1488 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.64 | 195.6063 | PTW295967
1489 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.64 | 195.6063 | PTW295967
1490 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS7 |  |  |  |  | Tx | 0 | 1 | IS7Tx | 16443 | 4.907% | IDT | IDT_Manual stop for LV Side Thermography | IDT manual stop for thermography work | 12:47 | 12:47 | 12:47 | 13:33 | 0 | 0 | 0.76667 | 0.76667 | After thermography work done IDT Charged. | Close | 0.037621 | 0.78542 | 10557.2033 | PTW296741
1491 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS7 |  |  |  |  | Tx | 0 | 1 | IS7Tx | 16443 | 4.907% | IDT | IDT_Manual stop for LV Side Thermography | IDT manual stop for thermography work | 14:10 | 14:10 | 14:10 | 14:41 | 0 | 0 | 0.51667 | 0.51667 | After thermography work done IDT Charged. | Close | 0.025353 | 0.48248 | 6485.3152 | PTW296741
1492 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS13 | INV3 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295805
1493 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS6 | INV3 | M2 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295805
1494 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS6 | INV3 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295805
1495 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS9 | INV3 | M1 | SCB6 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012389 | 7.6 | 196.3839 | PTW295805
1496 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0010116 | 7.6 | 160.3501 | PTW295805
1497 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0010116 | 7.6 | 160.3501 | PTW295805
1498 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS8 | INV4 | M1 | SCB1 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0010229 | 7.6 | 162.1518 | PTW295805
1499 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0010116 | 7.6 | 160.3501 | PTW295967
1500 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0010116 | 7.6 | 160.3501 | PTW295967
1501 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0010229 | 7.6 | 162.1518 | PTW295967
1502 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295967
1503 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295967
1504 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295967
1505 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295967
1506 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295967
1507 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.31 | 154.2315 | PTW295805
1508 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.31 | 154.2315 | PTW295805
1509 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.31 | 154.2315 | PTW295967
1510 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.31 | 154.2315 | PTW295967
1511 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0010203 | 7.31 | 155.9644 | PTW295967
1512 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.31 | 187.1573 | PTW295967
1513 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.31 | 187.1573 | PTW295967
1514 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.31 | 187.1573 | PTW295967
1515 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.31 | 187.1573 | PTW295967
1516 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.31 | 187.1573 | PTW295967
1517 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS15 | INV2 | M1 |  |  |  | 1 | 1 | IS15INV2M1 | 2004.48 | 0.5982% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:18 | 6:18 | 6:42 | 7:20 | 0 | 0.4 | 1.0333 | 1.0333 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.0061813 | 0.097872 | 160.3723 | PTW297021
1518 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS15 | INV2 | M2 |  |  |  | 1 | 1 | IS15INV2M2 | 1941.84 | 0.5795% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:02 | 7:02 | 7:02 | 7:20 | 0 | 0 | 0.3 | 0.3 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0017385 | 0.047683 | 75.6916 | PTW297021
1519 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.00095766 | 5.03 | 106.1265 | PTW295805
1520 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.00095766 | 5.03 | 106.1265 | PTW295805
1521 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.00095766 | 5.03 | 106.1265 | PTW295967
1522 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.00095766 | 5.03 | 106.1265 | PTW295967
1523 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.00096842 | 5.03 | 107.3189 | PTW295967
1524 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.0011621 | 5.03 | 128.7827 | PTW295967
1525 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.0011621 | 5.03 | 128.7827 | PTW295967
1526 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.0011621 | 5.03 | 128.7827 | PTW295967
1527 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.0011621 | 5.03 | 128.7827 | PTW295967
1528 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.0011621 | 5.03 | 128.7827 | PTW295967
1529 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS6 | INV3 | M2 | SCB10 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | String Affected Due to Wind Strom. | Close | 0.00061533 | 6.6 | 84.4896 | PTW297811
1530 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS14 | INV4 | M1 | SCB5 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | String Affected Due to Wind Strom. | Close | 0.00061533 | 6.6 | 84.4896 | PTW297811
1531 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS13 | INV1 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | String Affected Due to Wind Strom. | Close | 0.00061533 | 6.6 | 84.4896 | PTW297811
1532 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS12 | INV4 | M2 | SCB7 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | String Affected Due to Wind Strom. | Close | 0.00061533 | 6.6 | 84.4896 | PTW297811
1533 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS20 | INV4 | M2 | SCB7 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | String Affected Due to Wind Strom. | Close | 0.00061533 | 6.6 | 84.4896 | PTW297811
1534 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | Module Restored and Run | Close | 0.0012307 | 6.6 | 168.9793 | PTW297883
1535 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS6 | INV4 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | Module Restored and Run | Close | 0.0012307 | 6.6 | 168.9793 | PTW297883
1536 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | Module Restored and Run | Close | 0.0012307 | 6.6 | 168.9793 | PTW297883
1537 | 2025-05-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:26 | 19:28 | 13.0333 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:26 | 6:26 | 6:26 | 19:28 | 0 | 0 | 13.0333 | 13.0333 | Module Restored and Run | Close | 0.0012182 | 6.23 | 159.5062 | PTW297883
1538 | 2025-05-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:26 | 19:28 | 13.0333 | IS6 | INV4 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:26 | 6:26 | 6:26 | 19:28 | 0 | 0 | 13.0333 | 13.0333 | Module Restored and Run | Close | 0.0012182 | 6.23 | 159.5062 | PTW297883
1539 | 2025-05-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:26 | 19:28 | 13.0333 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:26 | 6:26 | 6:26 | 19:28 | 0 | 0 | 13.0333 | 13.0333 | Module Restored and Run | Close | 0.0012182 | 6.23 | 159.5062 | PTW297883
1540 | 2025-05-30 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:26 | 13.1167 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:26 | 0 | 0 | 13.1167 | 13.1167 | Module Restored and Run | Close | 0.001226 | 7.08 | 181.2687 | PTW297883
1541 | 2025-05-30 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:26 | 13.1167 | IS6 | INV4 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:26 | 0 | 0 | 13.1167 | 13.1167 | Module Restored and Run | Close | 0.001226 | 7.08 | 181.2687 | PTW297883
1542 | 2025-05-30 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:26 | 13.1167 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:26 | 0 | 0 | 13.1167 | 13.1167 | Module Restored and Run | Close | 0.001226 | 7.08 | 181.2687 | PTW297883
1543 | 2025-05-31 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS9 | INV1 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Manully stop due to IV Testing work | Manully stop due to IV Testing work | 10:35 | 10:35 | 10:35 | 13:26 | 0 | 0 | 2.85 | 2.85 | Manully stop due to IV Testing work | Close | 0.00026638 | 2.53 | 64.7754 | PTW298338
1544 | 2025-05-31 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS9 | INV1 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Manully stop due to IV Testing work | Manully stop due to IV Testing work | 10:35 | 10:35 | 10:35 | 13:26 | 0 | 0 | 2.85 | 2.85 | Manully stop due to IV Testing work | Close | 0.00026638 | 2.53 | 64.7754 | PTW298338
1545 | 2025-05-31 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS7 | INV1 | M1 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | MC4 connector damage | MC4 connector Replaced. | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | MC4 connector Replaced. | Close | 0.00061377 | 6.91 | 88.4581 | PTW298409
1546 | 2025-06-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:31 | 19:25 | 12.9 | [5 empty] | Power_Tx2 | 0 | 1 | Power_Tx2 | 167768.915 | 50.07% | PTR | Tripped due to the 87T Differential Protection operation. | R-Phase Cable End Termination Failure | 19:25 | 19:25 | 19:25 | 5:15 | 0 | 0 |  |  | R phase End termination replaced and Check IR Value then PTR Charged. | Close | 0 | 0 | 0 | PTW298610
1547 | 2025-06-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:26 | 13.1667 | IS4 | INV3 | M1 | SCB6 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:56 | 10:56 | 10:56 | 12:35 | 0 | 0 | 1.65 | 1.65 | String Manully shutdown for IV Testing work | Close | 0.00012852 | 1.49 | 32.2737 | PTW298884
1548 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS1 | INV3 | M2 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:46 | 10:46 | 10:46 | 11:06 | 0 | 0 | 0.33333 | 0.33333 | String Manully shutdown for IV Testing work | Close | 1.2837e-05 | 0.30154 | 3.2294 | PTW299319
1549 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS5 | INV3 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:15 | 11:15 | 11:15 | 11:30 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.24352 | 2.608 | PTW299319
1550 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:45 | 11:45 | 11:45 | 12:00 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1792e-05 | 0.25457 | 3.3391 | PTW299319
1551 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:20 | 12:20 | 12:20 | 12:35 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26092 | 3.3909 | PTW299319
1552 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS16 | INV3 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:45 | 12:45 | 12:45 | 13:00 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26183 | 3.4028 | PTW299319
1553 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS18 | INV4 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:10 | 13:10 | 13:10 | 13:30 | 0 | 0 | 0.33333 | 0.33333 | String Manully shutdown for IV Testing work | Close | 1.5578e-05 | 0.33905 | 4.4063 | PTW299319
1554 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS6 | INV2 | M1 | SCB2 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 14:45 | 14:45 | 14:45 | 15:03 | 0 | 0 | 0.3 | 0.3 | String Manully shutdown for IV Testing work | Close | 1.389e-05 | 0.25993 | 3.3467 | PTW299319
1555 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS1 | INV3 | M2 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:30 | 10:30 | 10:30 | 10:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.22043 | 2.3608 | PTW299485
1556 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS5 | INV3 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:00 | 11:00 | 11:00 | 11:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.2379 | 2.5479 | PTW299485
1557 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:30 | 11:30 | 11:30 | 11:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1792e-05 | 0.25215 | 3.3073 | PTW299485
1558 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:00 | 12:00 | 12:00 | 12:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26067 | 3.3877 | PTW299485
1559 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS16 | INV3 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:30 | 12:30 | 12:30 | 12:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26505 | 3.4446 | PTW299485
1560 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS18 | INV4 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:00 | 13:00 | 13:00 | 13:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26388 | 3.4295 | PTW299485
1561 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS6 | INV2 | M1 | SCB2 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:30 | 13:30 | 13:30 | 13:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1575e-05 | 0.25915 | 3.3368 | PTW299485
1562 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS9 | INV4 | M2 |  |  |  | 1 | 1 | IS9INV4M2 | 1959.82 | 0.5849% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:17 | 6:17 | 6:45 | 19:29 | 0 | 0.46667 | 13.2 | 13.2 | After Genration AC Breaker Replace with Sungrow Team. | Close | 0.077202 | 7.3191 | 11904.0443 | PTW299590
1563 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS9 | INV4 | M1 |  |  |  | 1 | 1 | IS9INV4M1 | 2244.31 | 0.6698% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:55 | 7:55 | 7:55 | 9:11 | 0 | 0 | 1.2667 | 1.2667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0084836 | 0.56024 | 1043.4672 | PTW299590
1564 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS9 | INV4 | M1 |  |  |  | 1 | 1 | IS9INV4M1 | 2244.31 | 0.6698% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 9:35 | 9:35 | 9:35 | 9:47 | 0 | 0 | 0.2 | 0.2 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0013395 | 0.14326 | 266.8238 | PTW299590
1565 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS16 | INV3 | M1 |  |  |  | 1 | 1 | IS16INV3M1 | 2129.76 | 0.6356% | Inverter | Inverter trip in GFDI falut | Inverter trip in GFDI falut | 14:28 | 14:45 | 14:45 | 15:22 | 0.28333 | 0.28333 | 0.9 | 0.9 | Inverter Auto Reset and Run | Close | 0.0057202 | 0.72991 | 1290.0983
1566 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS4 | INV2 | M1 |  |  |  | 1 | 1 | IS4INV2M1 | 2114.1 | 0.6309% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:20 | 6:20 | 7:05 | 7:40 | 0 | 0.75 | 1.3333 | 1.3333 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.008412 | 0.15156 | 265.9083 | PTW299810
1567 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS4 | INV2 | M2 |  |  |  | 1 | 1 | IS4INV2M2 | 2088 | 0.6231% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:25 | 7:25 | 7:25 | 7:40 | 0 | 0 | 0.25 | 0.25 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0015578 | 0.054265 | 94.0312 | PTW299810
1568 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS1 | INV3 | M2 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:30 | 10:30 | 10:30 | 10:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.2207 | 2.3636 | PTW299638
1569 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS5 | INV3 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:00 | 11:00 | 11:00 | 11:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.23875 | 2.557 | PTW299638
1570 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:30 | 11:30 | 11:30 | 11:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1792e-05 | 0.2523 | 3.3093 | PTW299638
1571 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:00 | 12:00 | 12:00 | 12:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26177 | 3.402 | PTW299638
1572 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS16 | INV3 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:30 | 12:30 | 12:30 | 12:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26597 | 3.4565 | PTW299638
1573 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS18 | INV4 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:00 | 13:00 | 13:00 | 13:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26517 | 3.4461 | PTW299638
1574 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS6 | INV2 | M1 | SCB2 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:30 | 13:30 | 13:30 | 13:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1575e-05 | 0.26072 | 3.3569 | PTW299638
1575 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS1 | INV3 | M2 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:31 | 10:31 | 10:31 | 10:45 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 8.9861e-06 | 0.21297 | 2.2808 | PTW299846
1576 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS5 | INV3 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:02 | 11:02 | 11:02 | 11:15 | 0 | 0 | 0.21667 | 0.21667 | String Manully shutdown for IV Testing work | Close | 8.3443e-06 | 0.21248 | 2.2756 | PTW299846
1577 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:31 | 11:31 | 11:31 | 11:45 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.1005e-05 | 0.2381 | 3.123 | PTW299846
1578 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:00 | 12:00 | 12:00 | 12:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.24873 | 3.2326 | PTW299846
1579 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS16 | INV3 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:30 | 12:30 | 12:30 | 12:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.25043 | 3.2547 | PTW299846
1580 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS18 | INV4 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:01 | 13:01 | 13:01 | 13:15 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.0905e-05 | 0.24678 | 3.2072 | PTW299846
1581 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS6 | INV2 | M1 | SCB2 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:30 | 13:30 | 13:30 | 13:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1575e-05 | 0.25177 | 3.2417 | PTW299846
1582 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS1 | INV3 | M2 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:30 | 10:30 | 10:30 | 10:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.20813 | 2.2291 | PTW300061
1583 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS5 | INV3 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:02 | 11:02 | 11:02 | 11:15 | 0 | 0 | 0.21667 | 0.21667 | String Manully shutdown for IV Testing work | Close | 8.3443e-06 | 0.21002 | 2.2492 | PTW300061
1584 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:31 | 11:31 | 11:31 | 11:45 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.1005e-05 | 0.23737 | 3.1134 | PTW300061
1585 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:00 | 12:00 | 12:00 | 12:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26255 | 3.4121 | PTW300061
1586 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS16 | INV3 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:30 | 12:30 | 12:30 | 12:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.25037 | 3.2538 | PTW300061
1587 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS18 | INV4 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:01 | 13:01 | 13:01 | 13:15 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.0905e-05 | 0.25013 | 3.2508 | PTW300061
1588 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS6 | INV2 | M1 | SCB2 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:31 | 13:31 | 13:31 | 13:45 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.0804e-05 | 0.24548 | 3.1608 | PTW300061
1589 | 2025-06-10 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:00 | 12:00 | 12:00 | 12:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1792e-05 | 0.25882 | 3.3948 | PTW300295
1590 | 2025-06-10 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:30 | 12:30 | 12:30 | 12:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26412 | 3.4325 | PTW300295
1591 | 2025-06-11 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:33 | 13.3167 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:15 | 12:15 | 12:15 | 12:37 | 0 | 0 | 0.36667 | 0.36667 | String Manully shutdown for IV Testing work | Close | 1.7294e-05 | 0.37892 | 4.97 | PTW300457
1592 | 2025-06-11 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:33 | 13.3167 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:54 | 12:54 | 12:54 | 13:08 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.0905e-05 | 0.24947 | 3.2421 | PTW300457
1593 | 2025-06-11 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:33 | 13.3167 | IS5 |  |  |  |  | Tx | 0 | 1 | IS5Tx | 16724.88 | 4.991% | IDT | IDT_Manual stop for LV Side Thermography | IDT manual stop for thermography work | 12:17 | 12:17 | 12:17 | 12:59 | 0 | 0 | 0.7 | 0.7 | After thermography work IDT Charged Sucessfully. | Close | 0.034938 | 0.71287 | 9894.4839 | PTW300540
1594 | 2025-06-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 13.2833 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:37 | 12:37 | 12:37 | 13:02 | 0 | 0 | 0.41667 | 0.41667 | String Manully shutdown for IV Testing work | Close | 1.9653e-05 | 0.43092 | 5.6521 | PTW300678
1595 | 2025-06-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 13.2833 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:15 | 13:15 | 13:15 | 13:32 | 0 | 0 | 0.28333 | 0.28333 | String Manully shutdown for IV Testing work | Close | 1.3241e-05 | 0.29373 | 3.8174 | PTW300678
1596 | 2025-06-13 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:29 | 13.1833 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:02 | 12:02 | 12:02 | 12:45 | 0 | 0 | 0.71667 | 0.71667 | String Manully shutdown for IV Testing work | Close | 3.3803e-05 | 0.69153 | 9.0705 | PTW300966
1597 | 2025-06-13 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:29 | 13.1833 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:06 | 13:06 | 13:06 | 13:32 | 0 | 0 | 0.43333 | 0.43333 | String Manully shutdown for IV Testing work | Close | 2.0251e-05 | 0.42897 | 5.5749 | PTW300966
1598 | 2025-06-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:48 | 19:26 | 12.6333 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:48 | 6:48 | 6:48 | 19:26 | 0 | 0 | 12.6333 | 12.6333 | Module Remove for damage module replacement work | Close | 0.00097307 | 1.79 | 38.3409 | PTW301070
1599 | 2025-06-15 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:39 | 19:31 | 12.8667 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:39 | 6:39 | 6:39 | 19:31 | 0 | 0 | 12.8667 | 12.8667 | Module Remove for damage module replacement work | Close | 0.00099104 | 2.95 | 63.1876 | PTW301312
1600 | 2025-06-16 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:40 | 13.4333 | IS4 | INV2 | M1 |  |  |  | 1 | 1 | IS4INV2M1 | 2114.1 | 0.6309% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:22 | 6:22 | 7:42 | 8:10 | 0 | 1.3333 | 1.8 | 1.8 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.011356 | 0.21953 | 385.1586 | PTW301465
1601 | 2025-06-16 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:40 | 13.4333 | IS4 | INV2 | M2 |  |  |  | 1 | 1 | IS4INV2M2 | 2088 | 0.6231% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:45 | 7:45 | 7:45 | 8:10 | 0 | 0 | 0.41667 | 0.41667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0025963 | 0.067603 | 117.1441 | PTW301465
1602 | 2025-06-16 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:40 | 13.4333 | IS9 | INV4 | M1 |  |  |  | 1 | 1 | IS9INV4M1 | 2244.31 | 0.6698% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:20 | 6:20 | 6:45 | 7:52 | 0 | 0.41667 | 1.5333 | 1.5333 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.01027 | 0.17218 | 320.6908 | PTW301465
1603 | 2025-06-16 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:40 | 13.4333 | IS9 | INV4 | M2 |  |  |  | 1 | 1 | IS9INV4M2 | 1959.82 | 0.5849% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:30 | 7:30 | 7:30 | 7:52 | 0 | 0 | 0.36667 | 0.36667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0021445 | 0.063402 | 103.119 | PTW301465
1604 | 2025-06-17 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:31 | 19:39 | 13.1333 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:31 | 6:31 | 6:31 | 19:39 | 0 | 0 | 13.1333 | 13.1333 | Module Remove for damage module replacement work | Close | 0.0010116 | 5.75 | 123.1623 | PTW301312
1605 | 2025-06-18 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:36 | 13.2333 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:22 | 6:22 | 6:22 | 19:36 | 0 | 0 | 13.2333 | 13.2333 | Module Remove for damage module replacement work | Close | 0.0010193 | 7.2 | 154.2206 | PTW301944
1606 | 2025-06-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:12 | 19:28 | 13.2667 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:12 | 6:12 | 6:12 | 19:28 | 0 | 0 | 13.2667 | 13.2667 | Module Remove for damage module replacement work | Close | 0.0010218 | 6.75 | 144.5818 | PTW302162
1607 | 2025-06-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:12 | 19:28 | 13.2667 | IS7 | INV2 | M1 |  |  |  | 1 | 1 | IS7INV2M1 | 2098.44 | 0.6262% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 17:46 | 17:46 | 17:46 | 19:28 | 0 | 0 | 1.7 | 1.7 | Auto Reset and Run. | Close | 0.010646 | 0.13604 | 236.905
1608 | 2025-06-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:12 | 19:28 | 13.2667 | IS7 | INV2 | M2 |  |  |  | 1 | 1 | IS7INV2M2 | 2004.48 | 0.5982% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 17:46 | 17:46 | 17:46 | 19:28 | 0 | 0 | 1.7 | 1.7 | Auto Reset and Run. | Close | 0.010169 | 0.13604 | 226.2973
1609 | 2025-06-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:12 | 19:28 | 13.2667 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 167322.75 | 49.93% | PTR | PTR-1 Trip in 87 Activated. | PTR-1 Trip in 87 Activated. | 19:32 | 19:32 | 20:02 | 22:49 | 0 | 0.5 | 3.2833 | 3.2833 | Cheack Related parameter and IR value after that disscuss with HT team then PTR charged. | Close | 1.6395 | 0 | 0 | PTW302345
1610 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS7 | INV2 | M1 |  |  |  | 1 | 1 | IS7INV2M1 | 2098.44 | 0.6262% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:18 | 6:18 | 6:40 | 19:35 | 0 | 0.36667 | 13.2833 | 13.2833 | After Genration OEM team replaced AC Breaker and inverter kept in observation | Close | 0.083184 | 6.58 | 11458.9356 | PTW302566
1611 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS7 | INV2 | M2 |  |  |  | 1 | 1 | IS7INV2M2 | 2004.48 | 0.5982% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:18 | 6:18 | 6:40 | 19:35 | 0 | 0.36667 | 13.2833 | 13.2833 | After Genration OEM team replaced AC Breaker and inverter kept in observation | Close | 0.07946 | 6.58 | 10945.849 | PTW302566
1612 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS18 | INV3 | M1 |  |  |  | 1 | 1 | IS18INV3M1 | 2223.72 | 0.6636% | Inverter | Inverter tripped in GFDI Fault | Inverter tripped in GFDI Fault | 6:18 | 6:18 | 7:00 | 8:15 | 0 | 0.7 | 1.95 | 1.95 | checked related connection and parameter then the inverter and start | Close | 0.012941 | 0.2264 | 417.8025 | PTW302616
1613 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS18 | INV3 | M2 |  |  |  | 1 | 1 | IS18INV3M2 | 1973.16 | 0.5888% | Inverter | Manually stop for Inv Unit_GFDI Fault rectification | Manually stop for Inv Unit_GFDI Fault rectification | 7:20 | 7:20 | 7:20 | 8:15 | 0 | 0 | 0.91667 | 0.91667 | Manually stop for Inv Unit_GFDI Fault rectification | Close | 0.0053977 | 0.16585 | 271.5839 | PTW302616
1614 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS18 | INV3 | M1 | SCB6 |  |  | 1 | 1 | IS18INV3M1SCB6 | 250.56 | 0.07477% | SCB | Manually stop SCB_GFDI Fault rectification | Manually stop SCB_GFDI Fault rectification | 8:15 | 8:15 | 8:15 | 8:55 | 0 | 0 | 0.66667 | 0.66667 | Manually stop SCB_GFDI Fault rectification | Close | 0.00049849 | 0.1619 | 33.6648 | PTW302616
1615 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS18 | INV3 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 8:55 | 8:55 | 8:55 | 19:35 | 0 | 0 | 10.6667 | 10.6667 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00049849 | 6.1941 | 80.499 | PTW302616
1616 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS18 | INV2 | M2 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:18 | 6:18 | 6:18 | 19:35 | 0 | 0 | 13.2833 | 13.2833 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00062078 | 6.58 | 85.5144 | PTW302616
1617 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:18 | 6:18 | 6:18 | 19:35 | 0 | 0 | 13.2833 | 13.2833 | Module Remove for damage module replacement work | Close | 0.0010231 | 6.58 | 140.9405 | PTW302441
1618 | 2025-06-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 19:28 | 13.0833 | IS7 | INV2 | M1 |  |  |  | 1 | 1 | IS7INV2M1 | 2098.44 | 0.6262% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:23 | 6:23 | 6:23 | 19:28 | 0 | 0 | 13.0833 | 13.0833 | After Genration OEM team attend inverter and found 20Amp. Fuse was blown, fuse arrenge other site and replaced in early morning then inverter reboot and run. | Close | 0.081932 | 2.13 | 3709.3515 | PTW302772
1619 | 2025-06-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 19:28 | 13.0833 | IS7 | INV2 | M2 |  |  |  | 1 | 1 | IS7INV2M2 | 2004.48 | 0.5982% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:23 | 6:23 | 6:23 | 19:28 | 0 | 0 | 13.0833 | 13.0833 | After Genration OEM team attend inverter and found 20Amp. Fuse was blown, fuse arrenge other site and replaced in early morning then inverter reboot and run. | Close | 0.078263 | 2.13 | 3543.2611 | PTW302772
1620 | 2025-06-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 19:28 | 13.0833 | IS18 | INV3 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:23 | 6:23 | 6:23 | 19:28 | 0 | 0 | 13.0833 | 13.0833 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00061143 | 2.13 | 27.6817 | PTW302616
1621 | 2025-06-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 19:28 | 13.0833 | IS18 | INV2 | M2 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:23 | 6:23 | 6:23 | 19:28 | 0 | 0 | 13.0833 | 13.0833 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00061143 | 2.13 | 27.6817 | PTW302616
1622 | 2025-06-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 19:28 | 13.0833 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:23 | 6:23 | 6:23 | 19:28 | 0 | 0 | 13.0833 | 13.0833 | Module Remove for damage module replacement work | Close | 0.0010077 | 2.13 | 45.6236 | PTW302441
1623 | 2025-06-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 13.2833 | IS18 | INV3 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:15 | 6:15 | 6:15 | 19:32 | 0 | 0 | 13.2833 | 13.2833 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00062078 | 7 | 90.9728 | PTW302616
1624 | 2025-06-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 13.2833 | IS18 | INV2 | M2 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:15 | 6:15 | 6:15 | 19:32 | 0 | 0 | 13.2833 | 13.2833 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00062078 | 7 | 90.9728 | PTW302616
1625 | 2025-06-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 13.2833 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:15 | 6:15 | 6:15 | 19:32 | 0 | 0 | 13.2833 | 13.2833 | Module Remove for damage module replacement work | Close | 0.0010231 | 7.04 | 150.7935 | PTW302441
1626 | 2025-06-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:26 | 19:28 | 13.0333 | IS18 | INV3 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:26 | 6:26 | 6:26 | 19:28 | 0 | 0 | 13.0333 | 13.0333 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00060909 | 5.7 | 74.0779 | PTW302616
1627 | 2025-06-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:26 | 19:28 | 13.0333 | IS18 | INV2 | M2 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:26 | 6:26 | 6:26 | 19:28 | 0 | 0 | 13.0333 | 13.0333 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00060909 | 5.7 | 74.0779 | PTW302616
1628 | 2025-06-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:26 | 19:28 | 13.0333 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:26 | 6:26 | 6:26 | 19:28 | 0 | 0 | 13.0333 | 13.0333 | Module Remove for damage module replacement work | Close | 0.0010039 | 5.74 | 122.9481 | PTW302441
1629 | 2025-06-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:29 | 19:31 | 13.0333 | IS18 | INV3 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:29 | 6:29 | 6:29 | 19:31 | 0 | 0 | 13.0333 | 13.0333 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00060909 | 6.51 | 84.6047 | PTW302616
1630 | 2025-06-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:29 | 19:31 | 13.0333 | IS18 | INV2 | M2 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:29 | 6:29 | 6:29 | 19:31 | 0 | 0 | 13.0333 | 13.0333 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00060909 | 6.51 | 84.6047 | PTW302616
1631 | 2025-06-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:29 | 19:31 | 13.0333 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:29 | 6:29 | 6:29 | 19:31 | 0 | 0 | 13.0333 | 13.0333 | Module Remove for damage module replacement work | Close | 0.0010039 | 6.44 | 137.9417 | PTW302441
1632 | 2025-06-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:23 | 13.0167 | IS18 | INV3 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:22 | 6:22 | 6:22 | 19:23 | 0 | 0 | 13.0167 | 13.0167 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00060832 | 6.16 | 80.0561 | PTW302616
1633 | 2025-06-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:23 | 13.0167 | IS18 | INV2 | M2 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:22 | 6:22 | 6:22 | 19:23 | 0 | 0 | 13.0167 | 13.0167 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00060832 | 6.16 | 80.0561 | PTW302616
1634 | 2025-06-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:23 | 13.0167 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:22 | 6:22 | 6:22 | 19:23 | 0 | 0 | 13.0167 | 13.0167 | Module Remove for damage module replacement work | Close | 0.0010026 | 6.13 | 131.3017 | PTW302441
1635 | 2025-06-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 18:15 | 11.8667 | IS18 | INV3 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:23 | 6:23 | 6:23 | 18:15 | 0 | 0 | 11.8667 | 11.8667 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00055457 | 5.23 | 67.9697 | PTW303787
1636 | 2025-06-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 18:15 | 11.8667 | IS18 | INV2 | M2 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:23 | 6:23 | 6:23 | 18:15 | 0 | 0 | 11.8667 | 11.8667 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00055457 | 5.23 | 67.9697 | PTW303787
1637 | 2025-06-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 18:15 | 11.8667 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:23 | 6:23 | 6:23 | 18:15 | 0 | 0 | 11.8667 | 11.8667 | Module Remove for damage module replacement work | Close | 0.00091402 | 5.54 | 118.6642 | PTW302441
1638 | 2025-06-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 18:15 | 11.8667 | IS6 | INV2 | M1 |  |  |  | 1 | 1 | IS6INV2M1 | 2203.13 | 0.6575% | Inverter | Inverter tripped in GFDI Fault | Inverter tripped in GFDI Fault | 17:32 | 17:32 | 17:32 | 18:15 | 0 | 0 | 0.71667 | 0.71667 | Auto Reset and Run. | Close | 0.0047119 | 0.015161 | 27.7204
1639 | 2025-06-27 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:15 | 12.8833 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:22 | 6:22 | 6:22 | 19:15 | 0 | 0 | 12.8833 | 12.8833 | Module Remove for damage module replacement work | Close | 0.00099232 | 4.25 | 91.033 | PTW302441
1640 | 2025-06-27 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:15 | 12.8833 | IS9 | INV4 | M1 |  |  |  | 1 | 1 | IS9INV4M1 | 2244.31 | 0.6698% | Inverter | Inverter tripped in GFDI Fault | Inverter tripped in GFDI Fault | 10:06 | 10:06 | 10:20 | 11:02 | 0 | 0.23333 | 0.93333 | 0.93333 | MC4 connector found burn, replace and Run. | Close | 0.0062511 | 0.66535 | 1239.2321 | PTW304064
1641 | 2025-06-27 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:15 | 12.8833 | IS9 | INV4 | M2 |  |  |  | 1 | 1 | IS9INV4M2 | 1959.82 | 0.5849% | Inverter | Manually stop for Inv Unit_GFDI Fault rectification | Manually stop for Inv Unit_GFDI Fault rectification | 10:20 | 10:20 | 10:20 | 11:02 | 0 | 0 | 0.7 | 0.7 | Manually stop for Inv Unit_GFDI Fault rectification | Close | 0.004094 | 0.50024 | 813.6157 | PTW304064
1642 | 2025-06-27 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:15 | 12.8833 | IS9 | INV4 | M1 | SCB8 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | MC4 connector damage | MC4 connector damage | 11:02 | 11:02 | 11:02 | 19:15 | 0 | 0 | 8.2167 | 8.2167 | MC4 Connector Replaced & Run. | Close | 0.00038755 | 2.4104 | 31.6162 | PTW304064
1643 | 2025-06-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:33 | 19:30 | 12.95 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:33 | 6:33 | 6:33 | 19:30 | 0 | 0 | 12.95 | 12.95 | Module Remove for damage module replacement work | Close | 0.00099746 | 5.92 | 126.8036 | PTW302441
1644 | 2025-06-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:32 | 13.1667 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:22 | 6:22 | 6:22 | 19:33 | 0 | 0 | 13.1833 | 13.1833 | Module Remove for damage module replacement work | Close | 0.0010154 | 5.18 | 110.9531 | PTW302441
1645 | 2025-06-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:32 | 13.1667 | IS16 | INV3 | M1 |  |  |  | 1 | 1 | IS16INV3M1 | 2129.76 | 0.6356% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:22 | 6:22 | 7:02 | 8:43 | 0 | 0.66667 | 2.35 | 2.35 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.014936 | 0.45257 | 799.9109 | PTW304339
1646 | 2025-06-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:32 | 13.1667 | IS16 | INV3 | M2 |  |  |  | 1 | 1 | IS16INV3M2 | 1879.2 | 0.5608% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 8:28 | 8:28 | 8:28 | 8:43 | 0 | 0 | 0.25 | 0.25 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.001402 | 0.10361 | 161.5807 | PTW304339
1647 | 2025-06-30 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:31 | 13.2333 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:17 | 6:17 | 6:17 | 19:31 | 0 | 0 | 13.2333 | 13.2333 | Module Remove for damage module replacement work | Close | 0.0010193 | 5.34 | 114.3803 | PTW302441
1648 | 2025-07-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:30 | 13.0333 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:28 | 6:28 | 6:28 | 19:30 | 0 | 0 | 13.0333 | 13.0333 | Module Remove for damage module replacement work | Close | 0.0010039 | 6.24 | 135.2882 | PTW302441
1649 | 2025-07-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:30 | 13.0333 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:28 | 6:28 | 6:28 | 19:30 | 0 | 0 | 13.0333 | 13.0333 | Module Remove for damage module replacement work | Close | 0.0012182 | 6.24 | 164.1699 | PTW304763
1650 | 2025-07-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:30 | 13.0333 | IS15 | INV1 | M1 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Y-connector fuse found damage | Y-connector fuse found damage | 6:28 | 6:28 | 6:28 | 19:30 | 0 | 0 | 13.0333 | 13.0333 | Fuse Replaced & Run. | Close | 0.0012182 | 6.24 | 164.1699 | PTW304900
1651 | 2025-07-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:30 | 13.0333 | IS16 | INV3 | M1 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | MC4 connector damage | MC4 connector damage | 6:28 | 6:28 | 6:28 | 19:30 | 0 | 0 | 13.0333 | 13.0333 | MC4 Connector Replaced & Run. | Close | 0.00060909 | 6.24 | 82.085 | PTW304900
1652 | 2025-07-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 18:46 | 12.3 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:28 | 6:28 | 6:28 | 18:46 | 0 | 0 | 12.3 | 12.3 | Module Remove for damage module replacement work | Close | 0.00094739 | 3.44 | 74.582 | PTW302441
1653 | 2025-07-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 18:46 | 12.3 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:28 | 6:28 | 6:28 | 18:46 | 0 | 0 | 12.3 | 12.3 | Module Remove for damage module replacement work | Close | 0.0011496 | 3.44 | 90.5039 | PTW304763
1654 | 2025-07-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 | 12.9833 | 12.9833 | Module Remove for damage module replacement work | Close | 0.001 | 2.617 | 56.7387 | PTW302441
1655 | 2025-07-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 | 12.9833 | 12.9833 | Module Remove for damage module replacement work | Close | 0.0012135 | 2.4948 | 65.6365 | PTW304763
1656 | 2025-07-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS7 | INV3 | M1 |  |  |  | 1 | 1 | IS7INV3M1 | 2223.72 | 0.6636% | Inverter | Inverter trip in GFDI falut | Inverter trip in GFDI falut | 6:27 | 6:27 | 7:00 | 7:37 | 0 | 0.55 | 1.1667 | 1.1667 | Inverter Reboot and Run | Close | 0.0077422 | 0.070914 | 132.4654 | PTW305128
1657 | 2025-07-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS4 | INV2 | M1 |  |  |  | 1 | 1 | IS4INV2M1 | 2114.1 | 0.6309% | Inverter | Inverter tripped in GFDI Fault | Inverter tripped in GFDI Fault | 6:27 | 6:27 | 7:00 | 8:02 | 0 | 0.55 | 1.5833 | 1.5833 | Module found damage, module bypass and run | Close | 0.0099893 | 0.14305 | 254.0324 | PTW305128
1658 | 2025-07-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS4 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS4INV2M1SCB3 | 234.9 | 0.0701% | SCB | Manually stop for Inv Unit_GFDI Fault rectification | Manually stop for Inv Unit_GFDI Fault rectification | 8:02 | 8:02 | 8:02 | 8:25 | 0 | 0 | 0.38333 | 0.38333 | Manually stop for Inv Unit_GFDI Fault rectification | Close | 0.00026872 | 0.054827 | 10.8184 | PTW305128
1659 | 2025-07-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS4 | INV2 | M1 | SCB3 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Connectors | Module found damage | Module found damage | 8:25 | 8:25 | 8:25 | 8:49 | 0 | 0 | 0.4 | 0.4 | Module found damage, module bypass and run | Close | 3.1156e-05 | 0.093073 | 2.0406 | PTW305128
1660 | 2025-07-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS4 |  |  |  |  | Tx | 0 | 1 | IS4Tx | 16547.4 | 4.938% | IDT | Manually stop due to IDT LV side thermography work | Manually stop due to IDT LV side thermography work | 12:45 | 12:45 | 12:45 | 13:42 | 0 | 0 | 0.95 | 0.95 | Manually stop due to IDT LV side thermography work | Close | 0.046913 | 0.14328 | 1991.6233 | PTW305276
1661 | 2025-07-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:31 | 19:31 | 13 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:31 | 6:31 | 6:31 | 19:31 | 0 | 0 | 13 | 13 | Module Remove for damage module replacement work | Close | 0.0010013 | 5.0858 | 110.265 | PTW302441
1662 | 2025-07-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:31 | 19:31 | 13 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:31 | 6:31 | 6:31 | 19:31 | 0 | 0 | 13 | 13 | Module Remove for damage module replacement work | Close | 0.0012151 | 5.0858 | 133.8048 | PTW304763
1663 | 2025-07-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:31 | 19:31 | 13 | IS20 | INV2 | M1 |  |  |  | 1 | 1 | IS20INV2M1 | 2255.04 | 0.673% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 8:15 | 8:20 | 8:55 | 11:00 | 0.083333 | 0.66667 | 2.75 | 2.75 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.018506 | 1.268 | 2401.8395 | PTW305457
1664 | 2025-07-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:31 | 19:31 | 13 | IS20 | INV2 | M2 |  |  |  | 1 | 1 | IS20INV2M2 | 2255.04 | 0.673% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 10:32 | 10:32 | 10:32 | 11:00 | 0 | 0 | 0.46667 | 0.46667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0031405 | 0.33314 | 631.0503 | PTW305457
1665 | 2025-07-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:31 | 19:31 | 13 | IS3 |  |  |  |  | Tx | 0 | 1 | IS3Tx | 16766.64 | 5.004% | IDT | Manually stop due to IDT LV side thermography work | Manually stop due to IDT LV side thermography work | 12:42 | 12:42 | 12:42 | 13:38 | 0 | 0 | 0.93333 | 0.93333 | Manually stop due to IDT LV side thermography work | Close | 0.0467 | 0.51797 | 7295.2127 | PTW305479
1665 | 2025-07-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:33 | 13.0833 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:28 | 6:28 | 6:28 | 19:33 | 0 | 0 | 13.0833 | 13.0833 | Module Remove for damage module replacement work | Close | 0.0010077 | 6.3045 | 136.687 | PTW302441
1665 | 2025-07-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:33 | 13.0833 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:28 | 6:28 | 6:28 | 19:33 | 0 | 0 | 13.0833 | 13.0833 | Module Remove for damage module replacement work | Close | 0.0012229 | 6.3045 | 165.8674 | PTW304763
1665 | 2025-07-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:33 | 13.0833 | IS11 |  |  |  |  | Tx | 0 | 1 | IS11Tx | 16595.25 | 4.952% | IDT | Manually stop due to IDT LV side thermography work | Manually stop due to IDT LV side thermography work | 12:22 | 12:22 | 12:22 | 13:05 | 0 | 0 | 0.71667 | 0.71667 | Manually stop due to IDT LV side thermography work | Close | 0.035493 | 0.7314 | 10195.935 | PTW305658
1666 | 2025-07-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:33 | 13.0833 | IS10 | INV4 | M2 | SCB10 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Junction Box Burn. | During String current checking found 8 nos. Module JB found. | 6:28 | 6:28 | 6:28 | 19:33 | 0 | 0 | 13.0833 | 13.0833 | During String current checking found 8 nos. Module JB found. | Close | 0.0012229 | 6.3045 | 165.8674 | PTW305652
1667 | 2025-07-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:27 | 12.75 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:42 | 6:42 | 6:42 | 19:27 | 0 | 0 | 12.75 | 12.75 | Module Remove for damage module replacement work | Close | 0.00098205 | 6.6503 | 144.1845 | PTW302441
1668 | 2025-07-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:27 | 12.75 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:42 | 6:42 | 6:42 | 19:27 | 0 | 0 | 12.75 | 12.75 | Module Remove for damage module replacement work | Close | 0.0011917 | 6.6503 | 174.9655 | PTW304763
1669 | 2025-07-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:27 | 12.75 | IS12 |  |  |  |  | Tx | 0 | 1 | IS12Tx | 16912.8 | 5.047% | IDT | Manually stop due to IDT LV side thermography work | Manually stop due to IDT LV side thermography work | 13:12 | 13:12 | 13:12 | 13:56 | 0 | 0 | 0.73333 | 0.73333 | Manually stop due to IDT LV side thermography work | Close | 0.037013 | 0.63879 | 9075.2752 | PTW305848
1670 | 2025-07-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:27 | 12.75 | IS10 | INV4 | M2 | SCB10 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Junction Box Burn. | During String current checking found 8 nos. Module JB found. | 6:42 | 6:42 | 6:42 | 19:27 | 0 | 0 | 12.75 | 12.75 | During String current checking found 8 nos. Module JB found. | Close | 0.0011917 | 6.6503 | 174.9655 | PTW305652
1671 | 2025-07-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:21 | 12.65 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:42 | 6:42 | 6:42 | 19:21 | 0 | 0 | 12.65 | 12.65 | Module Remove for damage module replacement work | Close | 0.00097435 | 5.5071 | 119.3986 | PTW302441
1672 | 2025-07-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:21 | 12.65 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:42 | 6:42 | 6:42 | 19:21 | 0 | 0 | 12.65 | 12.65 | Module Remove for damage module replacement work | Close | 0.0011824 | 5.5071 | 144.8881 | PTW304763
1673 | 2025-07-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:21 | 12.65 | IS13 |  |  |  |  | Tx | 0 | 1 | IS13Tx | 16599.6 | 4.954% | IDT | Manually stop due to IDT LV side thermography work | Manually stop due to IDT LV side thermography work | 12:34 | 12:34 | 12:34 | 13:15 | 0 | 0 | 0.68333 | 0.68333 | Manually stop due to IDT LV side thermography work | Close | 0.033851 | 0.51514 | 7183.0718 | PTW306053
1674 | 2025-07-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:21 | 12.65 | IS16 | INV3 | M1 |  |  |  | 1 | 1 | IS16INV3M1 | 2129.76 | 0.6356% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:42 | 6:42 | 7:08 | 7:46 | 0 | 0.43333 | 1.0667 | 1.0667 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.0067795 | 0.081427 | 145.6752 | PTW305917
1675 | 2025-07-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:21 | 12.65 | IS16 | INV3 | M2 |  |  |  | 1 | 1 | IS16INV3M2 | 1879.2 | 0.5608% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:32 | 7:32 | 7:32 | 7:46 | 0 | 0 | 0.23333 | 0.23333 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0013085 | 0.028347 | 44.7468 | PTW305917
1676 | 2025-07-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:21 | 12.65 | IS20 | INV2 | M1 |  |  |  | 1 | 1 | IS20INV2M1 | 2255.04 | 0.673% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:42 | 6:42 | 7:32 | 8:08 | 0 | 0.83333 | 1.4333 | 1.4333 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.0096458 | 0.14999 | 284.1122 | PTW305917
1677 | 2025-07-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:21 | 12.65 | IS20 | INV2 | M2 |  |  |  | 1 | 1 | IS20INV2M2 | 2255.04 | 0.673% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:55 | 7:55 | 7:55 | 8:08 | 0 | 0 | 0.21667 | 0.21667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0014581 | 0.045742 | 86.647 | PTW305917
1678 | 2025-07-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:25 | 19:32 | 13.1167 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:25 | 6:25 | 6:25 | 19:32 | 0 | 0 | 13.1167 | 13.1167 | Module Remove for damage module replacement work | Close | 0.0010103 | 5.0696 | 109.9125 | PTW302441
1679 | 2025-07-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:25 | 19:32 | 13.1167 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:25 | 6:25 | 6:25 | 19:32 | 0 | 0 | 13.1167 | 13.1167 | Module Remove for damage module replacement work | Close | 0.001226 | 5.0696 | 133.377 | PTW304763
1680 | 2025-07-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:25 | 19:32 | 13.1167 | IS15 | INV4 | M2 |  |  |  | 1 | 1 | IS15INV4M2 | 2004.48 | 0.5982% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:25 | 6:25 | 6:50 | 6:58 | 0 | 0.41667 | 0.55 | 0.55 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.00329 | 0.033194 | 55.8913 | PTW306126
1681 | 2025-07-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:25 | 19:32 | 13.1167 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 6:54 | 6:54 | 6:54 | 6:58 | 0 | 0 | 0.066667 | 0.066667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.00043618 | 0.0080383 | 14.8038 | PTW306126
1682 | 2025-07-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:25 | 19:32 | 13.1167 | IS20 | INV4 | M1 |  |  |  | 1 | 1 | IS20INV4M1 | 2255.04 | 0.673% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:25 | 6:25 | 6:25 | 6:37 | 0 | 0 | 0.2 | 0.2 | Auto Reboot and Run. | Close | 0.0013459 | 0.00657 | 12.4453 | PTW306126
1683 | 2025-07-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:37 | 19:31 | 12.9 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:37 | 6:37 | 6:37 | 19:31 | 0 | 0 | 12.9 | 12.9 | Module Remove for damage module replacement work | Close | 0.00099361 | 5.46 | 118.3772 | PTW302441
1684 | 2025-07-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:37 | 19:31 | 12.9 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:37 | 6:37 | 6:37 | 19:31 | 0 | 0 | 12.9 | 12.9 | Module Remove for damage module replacement work | Close | 0.0012057 | 5.46 | 143.6487 | PTW304763
1685 | 2025-07-10 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:26 | 19:24 | 12.9667 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:26 | 6:26 | 6:26 | 19:24 | 0 | 0 | 12.9667 | 12.9667 | Module Remove for damage module replacement work | Close | 0.00099874 | 5.56 | 120.5453 | PTW302441
1686 | 2025-07-10 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:26 | 19:24 | 12.9667 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:26 | 6:26 | 6:26 | 19:24 | 0 | 0 | 12.9667 | 12.9667 | Module Remove for damage module replacement work | Close | 0.001212 | 5.56 | 146.2796 | PTW304763
1687 | 2025-07-10 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:26 | 19:24 | 12.9667 | IS1 | INV1 | M1 |  |  |  | 1 | 1 | IS1INV1M1 | 2064.8 | 0.6162% | Inverter | Fan abnormal alarm | Running on half load due to fan failuer. | 14:00 | 14:00 | 14:00 | 19:24 | 0 | 0 | 5.4 | 5.4 | After Genration Fan Replace and issue resolve. | Close | 0.033274 | 2.0457 | 3548.198 | PTW306687
1688 | 2025-07-10 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:26 | 19:24 | 12.9667 | IS1 | INV1 | M2 |  |  |  | 1 | 1 | IS1INV1M2 | 2090.61 | 0.6239% | Inverter | Fan abnormal alarm | Running on half load due to fan failuer. | 14:00 | 14:00 | 14:00 | 19:24 | 0 | 0 | 5.4 | 5.4 | After Genration Fan Replace and issue resolve. | Close | 0.03369 | 2.0457 | 3592.5505 | PTW306687
[25 empty] | 377.6682 | 122742.17 | 2.0457
[25 empty] | 377.6682 | 122742.17 | 2.0457
Formulas:
Days = DAY(EOMONTH(PA[[#This Row],[Month Year]],0))

## GA
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
Sr. No. | Date | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Breakdown Description | Fault Time | Work Completion time on fault | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(Wh/m2) | Approximate Energy Loss (KWh)
1 | 2022-07-06 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 18:13 | 19:30 | 1.2833 | Restored plant post Grid resumed | Close | 1.2833
2 | 2022-07-07 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 17:50 | 18:37 | 0.78333 | Restored plant post Grid resumed | Close | 0.78333
3 | 2022-07-07 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 18:51 | 19:30 | 0.65 | Restored plant post Grid resumed | Close | 0.65
4 | 2022-07-08 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 16:59 | 17:34 | 0.58333 | Restored plant post Grid resumed | Close | 0.58333
5 | 2022-07-10 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 14:13 | 14:26 | 0.21667 | Restored plant post Grid resumed | Close | 0.21667
6 | 2022-07-17 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 16:00 | 16:15 | 0.25 | Restored plant post Grid resumed | Close | 0.25
7 | 2022-09-07 | FY22 | 2022 | Year_2 | Year_2 | 2022-09-01 | 30 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Line Shurt Down | 20:04 | 23:59 | 3.9167 | Restored plant post Grid resumed | Close | 3.9167
8 | 2022-09-12 | FY22 | 2022 | Year_2 | Year_2 | 2022-09-01 | 30 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Line tripped | 17:58 | 19:00 | 1.0333 | Restored plant post Grid resumed | Close | 1.0333
9 | 2023-01-22 | FY23 | 2023 | Year_2 | Year_2 | 2023-01-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Line tripped | 7:26 | 8:46 | 1.3333 | Restored plant post Grid resumed | Close | 1.3333
10 | 2023-05-18 | FY23 | 2023 | Year_2 | Year_2 | 2023-05-18 | 31 | 6:15 | 19:24 | 12.3833 | Grid | 335091.665 | 100% | Line Shurt Down | 19:46 | 23:25 | 3.65 | Restored plant post Grid resumed | Close | 3.65
11 | 2024-06-30 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-30 | 30 | 6:21 | 19:41 | 12.3833 | Grid | 335091.665 | 100% | Line Shurt Down | 19:47 | 5:29 | 9.42 | Restored plant post Grid resumed | Close | 9.42
12 | 2024-07-01 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:21 | 19:43 | 12.3833 | Grid | 335091.665 | 100% | Emergency Line Shutdown | 9:04 | 10:29 | 1.25 | Restored plant post Grid resumed | Close | 1.25
13 | 2024-07-01 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:21 | 19:43 | 12.3833 | Grid | 335091.665 | 100% | Line Shut Down | 20:42 | 2:26 | 5.44 | Restored plant post Grid resumed | Close
14 | 2024-07-02 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:13 | 19:40 | 12.3833 | Grid | 335091.665 | 100% | Line Shut Down | 21:06 | 3:05 | 5.59 | Restored plant post Grid resumed | Close
15 | 2024-07-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:19 | 19:39 | 12.3833 | Grid | 335091.665 | 100% | Line Shurt Down From GSS End due to Maintenance Work Purpose | 20:39 | 2:53 | 6.14 | Restored plant post Grid resumed | Close
16 | 2024-08-19 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:47 | 19:10 | 12.3833 | Grid | 335091.665 | 100% | Line Shurt Down From GSS End due to Maintenance Work Purpose | 21:00 | 6:00 |  | Restored plant post Grid resumed | Close | 0
17 | 2024-08-28 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:42 | 19:05 | 12.3833 | Grid | 335091.665 | 100% | Line Trip From GSS End due to Bus-1 fail | 10:20 | 13:35 | 3.25 | Restored plant post Grid resumed | Close | 3.25 | 2.18
18 | 2024-09-19 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 7:00 | 18:42 | 12.3833 | Grid | 335091.665 | 100% | 220KV Line trip due to GSS End ICT trip during load shifting. | 8:09 | 9:26 | 1.2833 | Restored plant post Grid resumed | Close | 1.2833
19 | 2024-09-20 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 6:53 | 18:37 | 12.3833 | Grid | 335091.665 | 100% | 220KV Line trip GSS End due to other line Y-phase Jumper Open. | 12:01 | 14:04 | 2.05 | Restored plant post Grid resumed | Close | 2.05
20 | 2024-09-21 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 7:34 | 18:38 | 12.3833 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Bus Jumper Replace Work. | 6:50 | 7:30 | 0.66667 | Restored plant post Grid resumed | Close | 0.66667
21 | 2024-12-11 | FY24 | 2024 | Year_3 | Year_3 | 2024-12-11 | 31 | 7:28 | 17:56 | 12.3833 | Grid | 335091.665 | 100% | 220KV Jaisalmer blackout occurred when the main line (Aakl-1 & 2) tripped. | 12:13 | 16:10 | 3.95 | Restored plant post Grid resumed | Close | 3.95 | 3.097 | 922015
22 | 2024-12-30 | FY24 | 2024 | Year_3 | Year_3 | 2024-12-11 | 31 | 7:36 | 18:07 | 12.3833 | Grid | 335091.665 | 100% | Line tripped from GSS End. | 18:11 | 21:00 |  | Restored plant post Grid resumed | Close | 0
23 | 2025-02-05 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:32 | 18:31 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to New T/F Jumper Work. | 18:52 | 22:13 |  | Restored plant post Grid resumed | Close | 0
24 | 2025-02-06 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:31 | 18:31 | 12.45 | Grid | 335091.665 | 100% | 220KV Line trip due to GSS End ICT trip during load shifting. | 11:30 | 12:28 | 0.96667 | Restored plant post Grid resumed | Close | 0.96667 | 0.92 | 262004
25 | 2025-02-25 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:18 | 18:23 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Aux. Bus Charge. | 18:25 | 18:46 |  | Restored plant post Grid resumed | Close | 0
26 | 2025-02-25 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:18 | 18:23 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Relay Inspection work. | 19:31 | 3:27 |  | Restored plant post Grid resumed | Close | 0
27 | 2025-03-03 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:18 | 18:50 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End For erection and stringing work in new 220 KV LV side bay-206 for ICT-2 of New 400/220 KV 500 MVA ICT2 | 19:15 | 4:34 |  | Restored plant post Grid resumed | Close | 0
28 | 2025-03-04 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:14 | 18:48 | 12.45 | Grid | 335091.665 | 100% | 220kV line manually tripped(S/D) from 400kV GSS Bhainsara for erection and stringing work in new 220 KV LV side bay-206 for ICT-2 of New 400/220 KV 500 MVA ICT3 at 400 kV GSS Bhainsara. | 19:15 | 5:37 |  | Restored plant post Grid resumed | Close | 0
29 | 2025-03-05 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:08 | 18:50 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End For erection and stringing work in new 220 KV LV side bay-206 for ICT-2 of New 400/220 KV 500 MVA ICT2 | 19:00 | 1:00 |  | Restored plant post Grid resumed | Close | 0
30 | 2025-03-07 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:11 | 18:50 | 12.45 | Grid | 335091.665 | 100% | 220kV Line manually tripped(S/D) by 400kV GSS, Bhainsara for erection and stringing work in new 220 KV LV side (for New 400/220 KV 500 MVA ICT2) | 19:15 | 0:15 |  | Restored plant post Grid resumed | Close | 0
31 | 2025-03-21 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:01 | 18:56 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Bay maintinance. | 20:01 | 5:20 |  | Restored plant post Grid resumed | Close | 0
32 | 2025-03-29 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 6:49 | 19:01 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Bay maintinance. | 21:50 | 4:29 |  | Restored plant post Grid resumed | Close | 0
33 | 2025-03-30 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 6:46 | 19:03 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Bay maintinance. | 19:30 | 6:52 |  | Restored plant post Grid resumed | Close | 0
34 | 2025-03-31 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 6:45 | 19:02 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Bay maintinance. | 6:45 | 7:18 | 0.55 | Restored plant post Grid resumed | Close | 0.55 | 0.025244 | 6940.6095
35 | 2025-04-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:38 | 19:06 | 12.45 | Grid | 335091.665 | 100% | Due to 220KV GSS End Line protection panel sparking issue, Load Down Zero. | 10:45 | 16:10 | 5.4167 | Restored plant post Grid resumed | Close | 5.4167 | 4.876 | 1317626.8056
36 | 2025-04-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:28 | 19:11 | 12.45 | Grid | 335091.665 | 100% | Line Shut-Down for Switchyard Maintinance work | 18:25 | 3:09 | 8.44 | Restored plant post Grid resumed | Close | 8.44
37 | 2025-05-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 7:28 | 19:13 | 12.45 | Grid | 335091.665 | 100% | SF6 Line CB tripped Due to Fault at GSS End. (NTPC Feeder R-Phase Jumper broken) | 11:52 | 14:12 | 2.3333 | Restored plant post Grid resumed | Close | 2.3333 | 1.9244 | 525936
38 | 2025-05-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:21 | 19:17 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Active Power. | 12:48 | 15:07 |  |  | Close | 0 | 2.125 | 82821.875
39 | 2025-05-13 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:16 | 19:18 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 12:03 | 13:53 |  |  | Close | 0 | 1.79 | 36077.45
40 | 2025-05-18 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:22 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 12:05 | 14:15 |  |  | Close | 0 | 2.08 | 41615.6
41 | 2025-05-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:17 | 19:23 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 10:15 | 15:04 |  |  | Close | 0 | 4.445 | 87255.35
42 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 11:21 | 13:34 |  |  | Close | 0 | 2.207 | 43891.7125
43 | 2025-05-31 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 11:45 | 13:50 |  |  | Close | 0 | 1.912 | 38345.16
44 | 2025-06-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:31 | 19:25 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Current Load. | 10:06 | 13:45 |  |  | Close | 0 | 3.1 | 196137
45 | 2025-06-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:27 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 11:50 | 14:10 |  |  | Close | 0 | 2.16 | 43178.4
46 | 2025-06-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:26 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 12:25 | 14:01 |  |  | Close | 0 | 1.46 | 29889.85
47 | 2025-06-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:25 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Active Power. | 10:31 | 12:59 |  |  | Close | 0 | 2.2 | 84524
48 | 2025-06-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:25 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 12:59 | 14:44 |  |  | Close | 0 | 1.55 | 29775.5
49 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Current Load. | 15:27 | 16:55 |  |  | Close | 0 | 0.881 | 29456.6755
50 | 2025-06-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Active Power due to 400KV Akal Line trip. | 13:49 | 14:43 |  |  | Close | 0 | 0.842 | 33309.52
51 | 2025-06-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 12.45 | Grid |  | 0% | Load Curtailment 30% of Active Power due to 400KV Akal Line trip. | 14:44 | 16:27 |  |  | Close | 0 | 1.24 | 68676.16
52 | 2025-06-13 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:29 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Current Load due to 400KV Akal Line trip.(PPC Set Point 155MW) | 9:33 | 16:07 |  |  | Close | 0 | 5.487 | 432597.8235
53 | 2025-06-17 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:31 | 19:39 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Current Load.(PPC Set Point 135MW) | 9:38 | 15:03 |  |  | Close | 0 | 2.56 | 244322.56
54 | 2025-06-18 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:36 | 12.45 | Grid |  | 0% | Load Curtailment @ 20% of Active Power due to heavy under drawl, high frequency. | 11:56 | 15:33 |  |  | Close | 0 | 3.22 | 133613.9
55 | 2025-06-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:12 | 19:28 | 12.45 | Grid |  | 0% | Load Curtailment @ 20% of Active Power due to heavy under drawl, high frequency. | 11:18 | 14:00 |  |  | Close | 0 | 2.46 | 102077.7
56 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 12.45 | Grid |  | 0% | Load Curtailment @ 20% of Active Power due to heavy under drawl, high frequency. | 12:32 | 13:30 |  |  | Close | 0 | 0.925 | 38382.875
57 | 2025-06-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 12.45 | Grid |  | 0% | Load Curtailment @ 20% of Active Power due to heavy under drawl, high frequency. | 10:14 | 11:33 |  |  | Close | 0 | 1.072 | 44482.64
58 | 2025-06-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 12.45 | Grid |  | 0% | Load Curtailment @ 40% of Active Power due to heavy under drawl, high frequency. | 11:34 | 14:05 |  |  | Close | 0 | 2.31 | 172536.21
59 | 2025-07-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:27 | 12.45 | Grid |  | 0% | Load Curtailment @ 20% of Active Power due to heavy under drawl, high frequency. | 11:21 | 14:58 |  |  | Close | 0 | 3.09 | 129780
Formulas:
Days = DAY(EOMONTH(GA[[#This Row],[Month Year]],0))

## Inv_SY
| 2013.18 | 2090.61 | 2090.61 | 2077.705 | 2090.61 | 2090.61 | 2090.61 | 2193.85 | 2090.61 | 2116.42 | 2064.8 | 2090.61 | 2064.8 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2111.49 | 2114.1 | 2061.9 | 2088 | 2088 | 1853.1 | 2111.49 | 2114.1 | 2114.1 | 2088 | 2061.9 | 2114.1 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2234.16 | 1985.92 | 2203.13 | 1954.89 | 2161.08 | 2442.96 | 1954.89 | 2234.16 | 1973.16 | 2020.14 | 2145.42 | 2004.48 | 2223.72 | 1973.16 | 2223.72 | 1973.16 | 1973.16 | 2270.7 | 1973.16 | 2239.38 | 2223.72 | 1973.16 | 2192.4 | 2088 | 2102.065 | 1991.43 | 2102.065 | 2212.7 | 2275.92 | 2023.04 | 2244.31 | 1959.82 | 2161.08 | 2129.76 | 1973.16 | 2239.38 | 1941.84 | 2255.04 | 1973.16 | 2223.72 | 2023.04 | 2196.895 | 2054.65 | 2275.92 | 2023.04 | 2181.09 | 2023.04 | 1785.965 | 2192.4 | 2129.76 | 1941.84 | 2255.04 | 2192.4 | 2004.48 | 2004.48 | 2208.06 | 1957.5 | 2035.8 | 2239.38 | 1941.84 | 2255.04 | 1941.84 | 2192.4 | 2004.48 | 2223.72 | 1910.52 | 2223.72 | 2004.48 | 2192.4 | 2004.48 | 2192.4 | 2004.48 | 1973.16 | 2192.4 | 2004.48 | 1941.84 | 2208.06 | 2223.72 | 2192.4 | 2004.48 | 2223.72 | 1973.16 | 2129.76 | 1973.16 | 2098.44 | 1847.88 | 2161.08 | 1973.16 | 2004.48 | 2004.48 | 1988.82 | 1722.6 | 1973.16 | 1753.92 | 2004.48 | 2004.48 | 2255.04 | 1941.84 | 2255.04 | 1973.16 | 2223.72 | 1973.16 | 2004.48 | 2004.48 | 2161.08 | 2255.04 | 2223.72 | 2223.72 | 2223.72 | 2255.04 | 2004.48 | 2223.72 | 2239.38 | 2255.04 | 2255.04 | 2255.04 | 2255.04 | 2004.48 | 2255.04 | 2004.48
Date | IS1_INV1_M1 | IS1_INV1_M2 | IS1_INV2_M1 | IS1_INV2_M2 | IS1_INV3_M1 | IS1_INV3_M2 | IS1_INV4_M1 | IS1_INV4_M2 | IS2_INV1_M1 | IS2_INV1_M2 | IS2_INV2_M1 | IS2_INV2_M2 | IS2_INV3_M1 | IS2_INV3_M2 | IS2_INV4_M1 | IS2_INV4_M2 | IS3_INV1_M1 | IS3_INV1_M2 | IS3_INV2_M1 | IS3_INV2_M2 | IS3_INV3_M1 | IS3_INV3_M2 | IS3_INV4_M1 | IS3_INV4_M2 | IS4_INV1_M1 | IS4_INV1_M2 | IS4_INV2_M1 | IS4_INV2_M2 | IS4_INV3_M1 | IS4_INV3_M2 | IS4_INV4_M1 | IS4_INV4_M2 | IS5_INV1_M1 | IS5_INV1_M2 | IS5_INV2_M1 | IS5_INV2_M2 | IS5_INV3_M1 | IS5_INV3_M2 | IS5_INV4_M1 | IS5_INV4_M2 | IS6_INV1_M1 | IS6_INV1_M2 | IS6_INV2_M1 | IS6_INV2_M2 | IS6_INV3_M1 | IS6_INV3_M2 | IS6_INV4_M1 | IS6_INV4_M2 | IS7_INV1_M1 | IS7_INV1_M2 | IS7_INV2_M1 | IS7_INV2_M2 | IS7_INV3_M1 | IS7_INV3_M2 | IS7_INV4_M1 | IS7_INV4_M2 | IS8_INV1_M1 | IS8_INV1_M2 | IS8_INV2_M1 | IS8_INV2_M2 | IS8_INV3_M1 | IS8_INV3_M2 | IS8_INV4_M1 | IS8_INV4_M2 | IS9_INV1_M1 | IS9_INV1_M2 | IS9_INV2_M1 | IS9_INV2_M2 | IS9_INV3_M1 | IS9_INV3_M2 | IS9_INV4_M1 | IS9_INV4_M2 | IS10_INV1_M1 | IS10_INV1_M2 | IS10_INV2_M1 | IS10_INV2_M2 | IS10_INV3_M1 | IS10_INV3_M2 | IS10_INV4_M1 | IS10_INV4_M2 | IS11_INV1_M1 | IS11_INV1_M2 | IS11_INV2_M1 | IS11_INV2_M2 | IS11_INV3_M1 | IS11_INV3_M2 | IS11_INV4_M1 | IS11_INV4_M2 | IS12_INV1_M1 | IS12_INV1_M2 | IS12_INV2_M1 | IS12_INV2_M2 | IS12_INV3_M1 | IS12_INV3_M2 | IS12_INV4_M1 | IS12_INV4_M2 | IS13_INV1_M1 | IS13_INV1_M2 | IS13_INV2_M1 | IS13_INV2_M2 | IS13_INV3_M1 | IS13_INV3_M2 | IS13_INV4_M1 | IS13_INV4_M2 | IS14_INV1_M1 | IS14_INV1_M2 | IS14_INV2_M1 | IS14_INV2_M2 | IS14_INV3_M1 | IS14_INV3_M2 | IS14_INV4_M1 | IS14_INV4_M2 | IS15_INV1_M1 | IS15_INV1_M2 | IS15_INV2_M1 | IS15_INV2_M2 | IS15_INV3_M1 | IS15_INV3_M2 | IS15_INV4_M1 | IS15_INV4_M2 | IS16_INV1_M1 | IS16_INV1_M2 | IS16_INV2_M1 | IS16_INV2_M2 | IS16_INV3_M1 | IS16_INV3_M2 | IS16_INV4_M1 | IS16_INV4_M2 | IS17_INV1_M1 | IS17_INV1_M2 | IS17_INV2_M1 | IS17_INV2_M2 | IS17_INV3_M1 | IS17_INV3_M2 | IS17_INV4_M1 | IS17_INV4_M2 | IS18_INV1_M1 | IS18_INV1_M2 | IS18_INV2_M1 | IS18_INV2_M2 | IS18_INV3_M1 | IS18_INV3_M2 | IS18_INV4_M1 | IS18_INV4_M2 | IS19_INV1_M1 | IS19_INV1_M2 | IS19_INV2_M1 | IS19_INV2_M2 | IS19_INV3_M1 | IS19_INV3_M2 | IS19_INV4_M1 | IS19_INV4_M2 | IS20_INV1_M1 | IS20_INV1_M2 | IS20_INV2_M1 | IS20_INV2_M2 | IS20_INV3_M1 | IS20_INV3_M2 | IS20_INV4_M1 | IS20_INV4_M2
2025-06-09 | 0.04794% | 0.8003% | 1.133% | 1.094% | 2.125% | 1.903% | 2.404% | 0.6449% | 1.476% | -0.4798% | 1.537% | 1.09% | 2.705% | 0.6515% | 1.69% | 2.166% | 1.132% | 1.299% | 1.429% | 2.243% | 0.5942% | 0.4426% | 1.108% | 0.6577% | -0.4622% | -1.868% | -1.873% | -1.987% | 0.2581% | 0.02482% | 1.498% | 0.6926% | 1.943% | 2.152% | 3.31% | 2.321% | 2.471% | 1.007% | 1.18% | 0.8943% | 0.9086% | 3.841% | 1.309% | 3.668% | -1.192% | -4.752% | 3.855% | 1.124% | 8.164% | 7.22% | -0.3665% | 1.014% | -1.277% | 9.958% | -1.946% | 9.559% | -1.66% | -2.633% | -1.33% | -1.429% | -1.7% | -1.557% | -2.728% | -2.741% | -1.092% | -2.027% | -1.934% | -2.877% | -3.449% | -1.736% | -3.299% | -2.603% | -2.021% | -2.343% | -0.5658% | -3.236% | -0.9613% | -1.88% | -0.3314% | -2.248% | -1.472% | -2.344% | -2.098% | -3.214% | -1.443% | -2.852% | -1.326% | -1.824% | -1.683% | -1.943% | -0.2866% | -1.549% | -1.327% | 0.3978% | -0.6997% | -1.462% | 0.3334% | 0.5947% | -1.547% | 0.8994% | -2.122% | 0.7583% | -1.335% | -0.1401% | -2.268% | -0.8425% | -1.693% | -0.8998% | -1.622% | -1.444% | -0.8461% | 0.5344% | -0.6486% | -1.569% | -0.7535% | 0.2105% | -1.647% | -1.719% | -1.566% | -0.8548% | -2.236% | -0.7014% | 0.09296% | 0.3546% | 0.1984% | -0.7133% | -1.426% | -0.6303% | -0.9143% | -0.3242% | -1.398% | -1.694% | -1.108% | -2.241% | -2.102% | -1.82% | 0.003548% | 3.743% | 0.408% | 4.259% | 0.9881% | 2.613% | 2.915% | 0.2957% | 2.07% | 0.9354% | 1.012% | 0.6584% | 0.5533% | -0.5582% | 3.705% | 1.174% | 0.7856% | 0.08573% | 0.2094% | -0.1194% | 0.1836% | 3.187% | 0.6131% | 3.741%
2025-06-10 | -0.19% | 0.6128% | 1.016% | 0.9352% | 2.114% | 1.798% | 2.181% | 0.8407% | 1.37% | -0.573% | 1.357% | 0.9622% | 2.628% | 0.4849% | 1.499% | 2.088% | 1.022% | 1.253% | 1.311% | 2.11% | 0.5308% | 0.3163% | 1.006% | 0.5438% | -0.5633% | -2.161% | -2.068% | -2.153% | 0.1921% | -0.09156% | 1.37% | 0.6933% | 1.687% | 1.932% | 3.14% | 2.063% | 2.475% | 0.9925% | 1.212% | 0.8925% | 1.087% | 3.594% | 1.459% | 3.424% | -1.173% | -4.488% | 3.558% | 1.348% | 8.081% | 7.128% | -0.5109% | 0.6828% | -1.306% | 9.809% | -1.976% | 9.573% | -1.921% | -2.662% | -1.571% | -1.463% | -1.792% | -1.819% | -2.575% | -2.623% | -1.081% | -2.283% | -2.164% | -2.912% | -3.447% | -1.978% | -3.342% | -2.857% | -2.156% | -2.548% | -0.9307% | -3.346% | -1.245% | -1.954% | -0.4603% | -2.23% | -1.667% | -2.412% | -2.191% | -3.054% | -1.586% | -2.76% | -1.368% | -1.961% | -1.526% | -1.95% | -0.5082% | -1.342% | -1.001% | 0.7563% | -0.215% | -0.9879% | 0.5703% | 0.4443% | -1.182% | 0.6556% | -1.748% | 0.5646% | -1.143% | -0.2029% | -2.04% | -0.9265% | -1.561% | -1.074% | -1.492% | -1.598% | -0.7521% | 0.4307% | -0.9088% | -1.523% | -0.9125% | 0.1175% | -1.268% | -1.55% | -1.482% | -1.253% | -2.121% | -0.9545% | 0.127% | 0.2343% | 0.479% | -0.8448% | -1.426% | -0.8633% | -1.229% | -0.7783% | -1.45% | -2.035% | -0.911% | -1.569% | -2.055% | -1.717% | 0.3449% | 3.586% | 0.7809% | 4.143% | 1.449% | 2.797% | 3.14% | 0.3684% | 2.223% | 1.132% | 1.41% | 0.9627% | 0.8615% | -0.201% | 3.666% | 1.546% | 1.246% | 0.5173% | 0.5877% | 0.3399% | 0.6085% | 3.217% | 0.9849% | 3.841%
2025-06-11 | 0.3521% | 1.056% | 1.457% | 1.595% | 2.477% | 2.325% | 2.955% | 1.016% | 2.078% | 0.08588% | 1.95% | 1.489% | 3.182% | 0.9482% | 2.056% | 2.534% | 1.554% | 1.732% | 1.94% | 2.74% | 1.166% | 0.9541% | 1.55% | 1.107% | -0.006345% | -1.553% | -1.526% | -1.592% | 0.8796% | 0.7962% | 2% | 1.24% | -7.254% | -7.081% | -6.024% | -6.895% | -6.246% | -7.529% | -7.397% | -7.846% | 1.189% | 4.266% | 1.736% | 4.113% | -0.3569% | -4.578% | 4.424% | 1.352% | 8.502% | 7.556% | 0.06777% | 1.375% | -0.9862% | 10.4% | -1.489% | 10.2% | -1.205% | -2.189% | -0.9546% | -1.128% | -1.448% | -1.23% | -2.16% | -2.031% | -0.6466% | -1.666% | -1.619% | -2.415% | -3.119% | -1.39% | -2.884% | -2.358% | -1.595% | -2.048% | -0.2909% | -2.949% | -0.729% | -1.69% | -0.02476% | -1.962% | -1.009% | -1.902% | -1.702% | -2.615% | -1.046% | -2.26% | -0.8135% | -1.324% | -1.346% | -1.411% | 0.06594% | -1.112% | -0.6212% | 1.109% | -0.04674% | -0.6666% | 1.096% | 1.097% | -0.8102% | 1.189% | -1.329% | 1.198% | -0.5719% | 0.2962% | -1.544% | -0.4484% | -1.114% | -0.512% | -0.8579% | -1.068% | -0.2257% | 1.034% | -0.3533% | -1.139% | -0.3079% | 0.6314% | -1.051% | -1.249% | -1.024% | -0.5366% | -1.692% | -0.3974% | 0.6855% | 0.914% | 0.9673% | -0.3953% | -0.8407% | -0.3336% | -0.789% | -0.4326% | -0.8312% | -1.635% | -0.6812% | -1.278% | -2.083% | -1.646% | 0.5277% | 4.072% | 1.025% | 4.696% | 1.715% | 3.391% | 3.708% | 0.8321% | 2.857% | 1.607% | 1.631% | 1.185% | 1.086% | -0.01145% | 4.114% | 1.742% | 1.449% | 0.709% | 0.8234% | 0.4987% | 0.8375% | 3.638% | 1.269% | 4.248%
2025-06-12 | 0.6381% | 0.2479% | 0.7241% | 1.113% | 1.632% | 1.636% | 1.534% | -1.049% | 1.137% | -0.9991% | 1.13% | 0.4852% | 2.4% | 0.0474% | 1.343% | 1.651% | 0.5851% | 0.8112% | 0.971% | 1.873% | 0.1101% | 0.1683% | 1.161% | 0.4876% | -0.3883% | 0.6204% | -1.762% | -1.944% | 0.08609% | 0.3444% | 1.453% | 0.1722% | 5.717% | 5.879% | 7.006% | 6.012% | 1.891% | 0.792% | 0.8503% | 0.4684% | -1.019% | 4.173% | -0.3922% | 4.368% | -1.314% | -6.857% | 4.447% | -0.957% | 7.561% | 6.425% | -0.7522% | 1.792% | -2.317% | 9.082% | -2.835% | 8.833% | -0.181% | -3.765% | 0.1771% | -2.581% | -2.7% | -0.1903% | -3.29% | -2.171% | -1.087% | -0.8426% | -1.645% | -3.542% | -4.78% | -0.877% | -4.287% | -1.007% | -2.447% | -2.3% | 0.536% | -4.214% | 0.6101% | -3.336% | 0.8145% | -3.219% | -0.408% | -2.925% | -1.256% | -4.282% | -0.4047% | -2.939% | -0.6854% | 1.304% | -2.417% | -2.047% | 1.281% | -2.922% | -1.999% | 1.505% | 0.2108% | -2.552% | 1.696% | 1.233% | -2.597% | 2.024% | -3.112% | 2.211% | -1.701% | 0.9658% | -3.059% | 1.067% | -2.57% | 0.1217% | -2.004% | -0.3258% | -1.688% | 1.572% | 0.6144% | -2.21% | 0.1842% | 1.766% | -2.352% | -2.701% | -2.325% | 0.2442% | -3.122% | 0.5648% | -0.3205% | 1.691% | 0.1676% | 1.771% | -1.611% | 0.817% | 0.18% | 0.4833% | -0.1213% | 1.594% | -0.512% | 1.332% | -1.008% | -0.6458% | -1.535% | 4.587% | -1.235% | 4.84% | -0.5401% | 3.577% | 3.341% | 1.421% | 1.105% | -0.986% | -0.1668% | -0.6588% | -0.7579% | -1.946% | 4.138% | -0.329% | -0.5882% | -1.365% | -1.346% | -1.527% | -1.24% | 3.775% | -0.8127% | 4.291%
2025-06-13 | 0.4047% | -1.345% | -0.9838% | -0.4507% | -0.2356% | -0.3128% | -0.4065% | -3.644% | -0.7811% | -3.262% | -0.2984% | -1.257% | 0.9583% | -1.547% | 0.05667% | 0.174% | -0.7667% | -0.5763% | -0.5495% | 0.6227% | -1.343% | -1.248% | 0.6307% | -0.4891% | -1.347% | 5.43% | -2.561% | -2.86% | -1.354% | -0.6663% | 0.735% | -1.405% | 29.4% | 29.93% | 31.37% | 29.98% | 0.1864% | -0.5135% | -0.5557% | -0.8778% | -3.78% | 4.034% | -3.005% | 5.002% | -2.486% | -9.886% | 4.507% | -3.922% | 5.761% | 4.24% | -2.22% | 2.24% | -4.441% | 6.855% | -4.867% | 6.74% | 1.929% | -6.288% | 2.688% | -5.085% | -5.032% | 1.967% | -5.448% | -2.847% | -2.022% | 1.072% | -2.296% | -5.381% | -7.447% | -0.00166% | -6.705% | 1.882% | -4.149% | -3.389% | 1.92% | -6.776% | 2.706% | -6.309% | 1.995% | -5.88% | 0.4855% | -4.763% | -0.6185% | -6.665% | 0.6429% | -4.191% | 0.11% | 8.626% | -4.053% | -2.837% | 3.744% | -5.222% | -3.91% | 2.131% | 1.272% | -4.519% | 3.667% | 1.508% | -4.707% | 4.351% | -5.012% | 4.742% | -2.812% | 2.732% | -4.475% | 5% | -3.972% | 1.991% | -3.107% | 1.911% | -2.822% | 3.383% | 2.78% | -3.629% | 2.142% | 4.641% | -3.663% | -4.192% | -3.449% | 2.35% | -4.537% | 3.133% | -1.044% | 3.75% | -0.2644% | 7.85% | -2.325% | 3.799% | 2.321% | 2.242% | 2.568% | 11.53% | 2.251% | 10.03% | 1.467% | 1.596% | -4.064% | 5.262% | -3.981% | 4.705% | -3.126% | 3.939% | 3.013% | 2.326% | -1.583% | -4.627% | -3.227% | -3.429% | -3.16% | -4.301% | 3.575% | -3.171% | -4.486% | -5.077% | -5.222% | -5.355% | -4.861% | 2.718% | -4.201% | 2.991%
2025-06-14 | -4.343% | -3.799% | -3.518% | -3.79% | -2.8% | -2.116% | -1.616% | -4.458% | -1.94% | -3.285% | -2.992% | -3.239% | -1.567% | -3.957% | -1.834% | -1.607% | -2.058% | -3.112% | -1.931% | -0.8111% | -1.777% | -3.518% | -1.827% | -2.16% | -3.655% | -5.09% | -5.338% | -5.631% | -1.991% | -1.466% | -0.7346% | -1.231% | 0.4271% | 0.9871% | 1.547% | 0.4119% | 0.7389% | -1.232% | -0.2208% | -1.029% | 0.8157% | 1.664% | 2.609% | 1.795% | -1.272% | -1.459% | 1.462% | 1.974% | 4.602% | 3.821% | -3.873% | -2.334% | -4.275% | 7.281% | -3.424% | 7.55% | -4.725% | -3.433% | -4.886% | -3.235% | -3.769% | -4.693% | -5.468% | -5.846% | -3.477% | -3.832% | -4.092% | -3.246% | -4.146% | -2.898% | -4.259% | -5.269% | -3.299% | -4.771% | -2.955% | -3.512% | -3.648% | -2.43% | -4.055% | -2.795% | -2.604% | -2.312% | -2.122% | -3.406% | -2.466% | -2.747% | -1.709% | -2.798% | 0.1206% | -1.395% | -0.9137% | 0.09838% | -0.7397% | -0.003361% | -1.307% | 0.5284% | 1.504% | 1.101% | 1.372% | 1.863% | 0.8197% | 1.733% | 0.6027% | 0.9281% | 1.349% | 0.6908% | 1.756% | 1.064% | 1.296% | 0.6629% | 3.059% | 2.242% | 1.238% | 1.677% | 1.263% | 1.866% | 2.512% | 2.188% | 2.329% | 1.837% | 2.243% | 2.495% | 3.722% | 2.713% | 4.043% | 2.35% | 2.4% | 3.149% | 2.478% | 3.814% | 2.76% | 1.52% | 1.42% | 1.713% | 0.8618% | 2.052% | 4.993% | 4.95% | 6.357% | 6.11% | 6.219% | 5.68% | 4.805% | 2.346% | 4.781% | 5.164% | 3.76% | 3.933% | 4.326% | 3.711% | 5.102% | 5.766% | 4.105% | 4.19% | 5.148% | 4.05% | 4.196% | 4.215% | 4.39% | 4.266%
2025-06-15 | -0.526% | 0.8596% | 0.8925% | 0.4382% | 2.04% | 2.117% | 2.579% | 0.7791% | 1.36% | -0.06817% | 0.1651% | -0.1178% | 1.826% | -1.066% | 1.963% | 1.925% | 1.514% | 0.7372% | 1.346% | 2.343% | 1.186% | -0.3387% | 1.216% | 0.6418% | -0.8838% | -2.478% | -2.632% | -2.715% | 0.4905% | 0.7369% | 1.166% | 0.9675% | 1.123% | 1.941% | 3.549% | 2.206% | 2.42% | 0.5417% | 1.198% | -0.01551% | 3.084% | 3.03% | 3.711% | 3.063% | 0.2501% | 0.4181% | 3.415% | 3.749% | 7.674% | 6.929% | -0.8875% | 0.1744% | -0.7034% | 10.81% | -0.949% | 9.989% | -2.461% | -1.447% | -1.89% | -0.9196% | -1.416% | -1.687% | -3.445% | -3.734% | -1.741% | -2.269% | -2.203% | -2.294% | -2.16% | -1.409% | -4.45% | -3.713% | -1.351% | -2.553% | -0.7616% | -1.565% | -1.496% | -0.2922% | -1.259% | -0.6501% | -2.138% | -1.541% | -2.405% | -3.37% | -2.51% | -3.221% | -1.407% | -3.192% | 0.2587% | -1.816% | -1.248% | -0.02799% | -1.142% | -0.3267% | -1.567% | 0.01986% | -0.5414% | -1.256% | -0.8554% | -0.4671% | -0.8613% | -0.2822% | -1.112% | -0.9098% | -0.9851% | -1.432% | -0.7927% | -1.821% | -1.18% | -2.005% | 0.09493% | -1.06% | -1.977% | -1.095% | -1.563% | -0.7621% | -0.8001% | -1.423% | -1.292% | -4.564% | -1.937% | -1.838% | -0.03855% | -0.9436% | 0.2066% | -2.376% | -2.053% | -1.861% | -2.215% | -1.266% | -2.196% | -3.074% | -3.39% | -3.05% | -2.825% | -2.053% | 1.862% | 1.592% | 2.728% | 2.047% | 1.885% | 0.7773% | 0.3707% | 0.1268% | 2.178% | 2.253% | 1.535% | 1.253% | 1.646% | 0.6919% | 1.933% | 2.55% | 2.199% | 2.562% | 3.471% | 2.24% | 2.56% | 1.964% | 2.279% | 2.295%
2025-06-16 | 1.188% | 2.674% | 2.742% | 2.351% | 3.696% | 4.224% | 4.094% | 1.583% | 3.296% | -0.01641% | 3.13% | 1.851% | 3.915% | 1.111% | 3.01% | 3.594% | 2.636% | 3.314% | 3.037% | 3.779% | 2.564% | 2.165% | 2.899% | 2.4% | 0.762% | -0.7852% | -5.35% | -2.667% | 2.512% | 2.019% | 2.83% | 2.336% | 2.463% | 3.879% | 4.515% | 3.624% | 3.953% | 2.213% | 2.34% | 1.837% | 2.809% | 4.871% | 3.332% | 4.65% | 0.7011% | -1.172% | 5.571% | 3.761% | 9.723% | 8.893% | 1.107% | 1.955% | 0.5248% | 11.31% | -0.2012% | 11.12% | -0.02682% | -0.353% | 0.675% | 0.4384% | 0.08428% | 0.5943% | -1.68% | -1.635% | -1.006% | -2.578% | -1.343% | -3.198% | -1.917% | -2.161% | -4.937% | -3.599% | -0.4825% | -2% | 1.114% | -1.887% | 0.2518% | 0.04571% | 0.8629% | -0.5674% | -2.189% | -2.525% | -2.95% | -3.059% | -2.266% | -3.528% | -2.102% | -2.111% | -0.7605% | -2.125% | 0.05771% | -0.7015% | -0.9692% | 1.01% | -0.09663% | -0.6939% | 0.1006% | 0.1228% | -0.4734% | 1.344% | -0.63% | 1.546% | -0.4001% | 0.7933% | -0.5303% | 0.2853% | 0.174% | -0.4828% | 0.2242% | -0.009148% | 0.8392% | 1.243% | -0.4227% | -1.495% | -1.847% | -0.126% | -1.138% | -2.06% | -1.749% | -1.659% | -2.746% | -1.717% | -0.1197% | 0.5115% | 0.05798% | -1.496% | -2.435% | -1.78% | -2.119% | -1.637% | -2.534% | -2.488% | -3.783% | -2.507% | -4.743% | -3.959% | -1.765% | -0.2662% | -2.154% | -0.5161% | -1.309% | -2.078% | -1.811% | -2.528% | -2.839% | -3.493% | -2.752% | -3.084% | -2.235% | -2.664% | -1.529% | -2.552% | -3.485% | -3.943% | -4.8% | -4.927% | -4.457% | -3.944% | -3.37% | -2.645%
2025-06-17 | -0.1562% | -1.091% | -1.281% | -0.7057% | -0.785% | -0.2978% | -0.3648% | -3.573% | -0.9603% | -3.591% | 2.465% | -1.878% | 2.981% | -1.701% | 0.8971% | 1.053% | -0.1212% | -0.06189% | 0.04639% | 1.473% | -0.9353% | -0.9301% | 0.2462% | -0.4635% | -1.728% | 4.907% | -2.134% | -2.564% | -1.666% | -1.9% | -0.2112% | -1.815% | 30.19% | 31.06% | 33.08% | 31.99% | -0.272% | -1.025% | -0.9913% | -1.366% | -2.988% | 3.75% | -2.389% | 4.647% | -2.969% | -9.384% | 3.863% | -3.2% | 6.471% | 4.729% | -1.448% | 1.733% | -3.425% | 7.808% | -4.554% | 7.306% | 0.9293% | -5.803% | 1.631% | -4.973% | -4.92% | 1.022% | -5.207% | -2.744% | -2.499% | -0.06572% | -2.82% | -5.666% | -7.022% | -1.054% | -6.73% | 0.4805% | -3.999% | -3.524% | 1.467% | -5.83% | 2.624% | -5.449% | 1.836% | -4.69% | -0.5762% | -4.89% | -1.154% | -6.599% | -0.2285% | -4.36% | -0.6108% | 6.853% | -2.987% | -2.48% | 3.348% | -4.7% | -3.618% | 1.693% | 0.6966% | -3.91% | 2.875% | 0.8656% | -4.763% | 2.947% | -5.226% | 2.799% | -4.055% | 0.9655% | -5.352% | 2.781% | -4.866% | 0.05669% | -4.262% | -0.04952% | -3.959% | 1.444% | 1.398% | -4.548% | -0.07237% | 2.375% | -4.944% | -5.471% | -5.015% | -0.1033% | -5.935% | 0.6739% | -2.74% | 1.577% | -1.865% | 4.813% | -4.093% | 1.394% | 0.6684% | 1.03% | -0.4169% | 8.093% | 0.947% | 8.643% | 1.892% | 2.436% | -2.812% | 5.188% | -1.985% | 5.406% | -1.153% | 4.585% | 3.821% | 3.237% | 1.08% | -1.553% | -0.5545% | -0.8126% | -1.033% | -2.585% | 4.742% | -0.5981% | -1.073% | -1.949% | -2.233% | -2.202% | -1.797% | 4.258% | -0.8291% | 4.882%
2025-06-18 | 0.3313% | -0.2069% | 0.2737% | 0.4685% | 1.107% | 1.451% | 1.16% | -1.725% | 0.7001% | -1.544% | 4.86% | -0.7558% | 7.882% | -0.9904% | 1.01% | 1.557% | 0.4007% | 0.4602% | 0.6747% | 1.369% | -0.209% | -0.2552% | 0.6528% | 0.03533% | -1.002% | 2.001% | -1.985% | -2.348% | -0.6266% | -0.9735% | 0.7912% | -0.2812% | 9.779% | 9.785% | 10.97% | 9.868% | 1.444% | 0.2746% | 0.4471% | 0.07415% | -1.501% | 3.187% | -0.9348% | 3.461% | -2.412% | -7.002% | 3.467% | -1.111% | 7.377% | 6.237% | -0.7781% | 1.77% | -2.288% | 8.597% | -2.69% | 8.494% | 0.9656% | -3.478% | 1.424% | -2.227% | -2.329% | 0.9675% | -3.503% | -2.32% | -1.264% | -0.01579% | -1.572% | -3.45% | -4.614% | -0.3956% | -4.286% | 0.002769% | -2.483% | -2.419% | 1.347% | -4.125% | 1.522% | -3.01% | 1.29% | -3.106% | 0.02504% | -3.004% | -0.7825% | -3.85% | 0.1218% | -3.019% | -0.1812% | 3.633% | -1.812% | -2.063% | 2.249% | -2.356% | -1.926% | 1.698% | 0.6207% | -2.077% | 2.11% | 0.7871% | -2.802% | 2.153% | -3.596% | 1.942% | -2.665% | 0.5102% | -3.773% | 1.374% | -3.158% | -0.2157% | -2.875% | -0.4686% | -2.397% | 1.21% | 0.6526% | -2.88% | 0.03267% | 1.783% | -2.924% | -3.331% | -3.14% | -0.1646% | -3.805% | 0.4351% | -1.161% | 1.456% | -0.6917% | 2.58% | -2.559% | 0.7273% | -0.1344% | -0.06229% | 3.305% | 4.735% | -1.256% | 3.591% | -0.7553% | -0.3106% | -1.5% | 4.008% | -1.263% | 4.027% | -0.5435% | 3.013% | 2.374% | 0.89% | 0.2628% | -1.514% | -0.6669% | -0.9673% | -0.7953% | -1.909% | 3.119% | -0.6225% | -1.093% | -1.91% | -1.969% | -2.288% | -2.041% | 2.192% | -1.438% | 2.68%
2025-06-19 | 0.09352% | -0.3977% | 0.3302% | 0.2955% | 1.598% | 1.625% | 0.658% | -2.376% | 0.4218% | -2.004% | 3.829% | -1.586% | 8.438% | -1.163% | 0.8842% | 1.51% | 0.2432% | 0.1736% | -0.009494% | 0.6754% | -1.037% | -1.169% | 0.3262% | -0.5089% | -1.807% | 0.7215% | -2.977% | -3.286% | -1.232% | -1.43% | 0.3587% | -0.8688% | 7.802% | 7.6% | 8.38% | 7.264% | 0.6196% | -0.9618% | 0.354% | 0.1334% | 1.059% | 4.625% | 1.468% | 5.429% | -0.7295% | -4.605% | 4.798% | 1.086% | 5.179% | 4.764% | -3.637% | -1.521% | -2.876% | 7.983% | -3.671% | 7.608% | -0.3853% | -4.127% | 0.7207% | -3.014% | -2.787% | 0.3977% | -3.78% | -2.539% | -2.322% | -1.209% | -2.75% | -4.395% | -5.13% | -1.564% | -4.835% | -0.9175% | -3.166% | -3.072% | 0.3947% | -4.483% | 0.7995% | -3.236% | 1.017% | -3.175% | -1.084% | -3.737% | -1.927% | -4.616% | -1.186% | -3.963% | -1.794% | 0.7229% | -2.842% | -2.953% | 0.9079% | -2.783% | -2.201% | 1.301% | 0.5432% | -2.111% | 1.76% | 0.7238% | -2.298% | 2.216% | -3.327% | 1.791% | -2.596% | 0.4592% | -3.668% | 1.107% | -3.206% | -0.4319% | -3.035% | -0.9705% | -2.192% | 1.181% | 0.9842% | -2.276% | 0.1096% | 1.955% | -2.588% | -2.883% | -2.76% | -0.04984% | -3.355% | 0.5674% | -1.104% | 1.48% | -0.3935% | 3.346% | -2.063% | 1.314% | 4.92% | 5.675% | 0.03739% | 3.813% | -0.2989% | 4.363% | 0.3264% | 0.6177% | 0.1955% | 4.96% | 0.8984% | 5.287% | -0.2605% | 3.686% | 3.617% | 1.812% | 1.57% | 0.1989% | 0.9344% | 0.5633% | 0.7166% | -0.0821% | 4.492% | 1.37% | 0.4431% | -0.178% | -0.1152% | -0.1551% | 0.05542% | 3.542% | 0.4315% | 4.237%
2025-06-20 | 1.454% | 3.038% | 2.699% | 2.461% | 3.633% | 4.192% | 4.843% | 2.568% | 3.221% | 1.654% | 9.49% | 3.447% | 12.39% | 2.588% | 3.516% | 3.395% | 2.68% | 2.409% | 2.805% | 3.271% | 1.976% | 1.574% | 2.072% | 1.641% | 0.3203% | 0.4375% | -1.008% | -1.228% | 2.003% | 2.884% | 2.455% | 1.845% | 6.647% | 6.222% | 7.046% | 6.369% | 4.228% | 2.535% | 3.054% | 2.599% | 2.302% | 2.687% | 2.594% | 4.181% | 0.04333% | -1.997% | 4.81% | 2.967% | 10.71% | 9.26% | -100% | -100% | 0.4999% | 12.33% | -0.04361% | 12.52% | 0.6464% | -0.3926% | 0.8339% | 0.3824% | -0.2708% | 0.3498% | -0.5155% | -0.7251% | -0.38% | -1.221% | -0.9939% | -2.803% | -2.073% | -1.102% | -2.285% | -1.521% | -0.8705% | -1.93% | 0.7498% | -2.274% | 0.3624% | -0.6846% | 0.6638% | -1.275% | -1.115% | -2.09% | -1.201% | -2.577% | -0.9861% | -2.479% | -1.105% | -0.06717% | -0.246% | -1.624% | 0.8934% | -0.03032% | 0.1062% | 2.127% | 1.3% | 0.05925% | 1.829% | 0.4205% | -0.3834% | 1.177% | -0.5849% | 1.226% | -0.7155% | 0.3254% | -1.369% | 0.3304% | -1.107% | -0.7702% | -1.169% | -0.9148% | -0.6955% | 0.235% | -1.127% | -1.722% | -0.3147% | 0.8581% | -1.373% | -1.869% | -2.261% | -1.994% | -2.29% | -0.7457% | -0.06702% | 0.2658% | 0.01828% | 0.3416% | -1.999% | -0.5486% | 0.08285% | 0.7828% | -0.308% | 1.017% | 0.3382% | 1.185% | -0.8558% | -0.4431% | 1.255% | 3.52% | 2.145% | 3.368% | -5.651% | 0.8406% | 2.982% | 1.124% | 3.131% | 2.508% | 2.483% | 2.115% | 1.865% | 0.8488% | 3.741% | 2.936% | 2.946% | 2.453% | 2.625% | 2.269% | 2.591% | 4.068% | 2.38% | 4.386%
2025-06-21 | 1.629% | 4.085% | 4.095% | 3.88% | 5.454% | 5.224% | 6.145% | 4.634% | 4.414% | 2.756% | 11.69% | 4.33% | 15.91% | 3.414% | 5.892% | 5.556% | 5.541% | 1.63% | 4.669% | 4.672% | 4.828% | 3.732% | 4.091% | 3.787% | 0.9711% | -0.6% | 0.3012% | -0.3024% | 3.925% | 5.504% | 4.222% | 3.445% | 5.164% | 5.088% | 6.283% | 5.231% | 5.419% | 3.164% | 4.877% | 3.219% | 8.351% | 6.536% | 8.827% | 8.225% | 4.769% | 4.335% | 7.923% | 8.942% | 6.426% | 5.147% | -100% | -100% | 0.3168% | 13.64% | -0.2999% | 11.88% | -0.6188% | 0.489% | 1.01% | 1.289% | -0.7117% | 0.522% | -1.281% | -1.961% | -0.6203% | -2.133% | -1.068% | -1.672% | -1.406% | -1.263% | -1.662% | -3.779% | 0.3104% | -3.14% | -0.4667% | -2.076% | -1.406% | 0.6836% | -3.91% | -3.439% | -1.905% | -1.34% | -1.397% | -2.252% | -1.639% | -2.366% | -0.2733% | -2.456% | 1.436% | -0.4741% | 0.5497% | 1.152% | 1.214% | 1.951% | 0.7895% | 1.57% | 2.333% | 0.7767% | 1.023% | 0.9628% | 1.156% | 1.005% | 0.5131% | -0.1425% | 1.464% | -0.02567% | 1.422% | -0.4936% | 1.089% | 0.1183% | 2.753% | -0.6975% | -0.3377% | -0.3909% | -0.6227% | -0.4096% | 0.2057% | -1.261% | -0.2446% | -2.151% | -1.294% | -1.143% | 1.608% | -1.495% | 1.963% | -1.831% | -1.708% | -1.109% | -1.144% | 0.7972% | -0.3163% | -1.845% | -0.548% | -2.048% | -3.576% | -3.351% | -0.5464% | -1.044% | 0.1535% | -1.128% | -0.6606% | -0.5375% | -1.281% | -1.552% | -1.533% | -1.35% | -1.871% | -1.74% | -1.196% | -2.231% | -1.531% | -0.7164% | -1.323% | -1.292% | -0.987% | -2.554% | -2.054% | -2.489% | -0.7391% | -1.753%
2025-06-22 | 0.6669% | 0.7081% | 0.09987% | 0.2391% | 0.9779% | 0.8359% | 1.516% | -1.526% | 1.098% | -0.5123% | 7.961% | 1.036% | 7.909% | -0.0479% | -0.5017% | 0.7215% | -0.2548% | -3.436% | -0.02884% | 0.4965% | -0.1547% | -2.457% | 1.364% | 0.1658% | -0.9568% | 0.9801% | -3.391% | -3.054% | 0.6828% | 1.787% | 1.788% | 0.6498% | 16.38% | 15.8% | 17.36% | 16.98% | 2.667% | 1.241% | 1.639% | -0.8878% | -0.2342% | 1.754% | 0.5775% | 1.67% | -1.149% | -6.535% | 4.735% | -0.1717% | 6.98% | 5.272% | -1.724% | 1.369% | -6.916% | 8.625% | -3.184% | 7.278% | -0.8025% | -4.127% | 0.85% | -2.766% | -4.885% | 0.3591% | -2.762% | -1.36% | -1.182% | 0.06993% | -3.13% | -4.917% | -4.611% | -0.4592% | -4.939% | -3.496% | -2.391% | -4.254% | 0.8238% | -3.955% | -1.138% | -3.225% | 1.013% | -2.742% | -0.1291% | -3.161% | -0.08928% | -7.86% | 0.393% | -6.102% | -0.1006% | 2.95% | -1.736% | -1.358% | 2.768% | -1.935% | -1.636% | 1.896% | 0.7409% | -1.775% | 2.053% | 0.9327% | -2.412% | 1.807% | -3.452% | 2.166% | -2.379% | 0.6067% | -3.467% | -0.2354% | -2.852% | -0.1093% | -2.427% | -1.054% | -1.797% | -2.498% | 0.6819% | -2.424% | -1.237% | 0.5234% | -2.186% | -2.69% | -2.204% | 0.5062% | -2.785% | 1.374% | -0.07066% | -1.733% | 0.642% | -0.01387% | -1.654% | 1.391% | -2.324% | 1.846% | 1.332% | 4.812% | 1.579% | 4.311% | -0.6034% | -0.3002% | -1.663% | 3.391% | -1.45% | 2.487% | -1.404% | 2.762% | 2.198% | 0.8821% | 0.4455% | -1.37% | -1.807% | -1.029% | -1.123% | -2.178% | 2.447% | -0.6738% | -0.5273% | -1.385% | -0.7443% | -2.66% | -1.46% | 2.462% | -1.486% | 2.406%
2025-06-23 | -0.9052% | 0.7285% | 0.08687% | -0.0913% | 1.148% | 1.368% | 1.937% | 0.462% | 1.347% | 0.009413% | 11.66% | 1.254% | 11.84% | -0.1342% | 0.4465% | 1.103% | 0.4701% | -0.8063% | 0.5939% | 1.035% | -0.06233% | -1.403% | -0.2998% | -0.5829% | -1.75% | -3.453% | -3.387% | -3.54% | -0.2868% | 0.8141% | 0.1864% | 0.02416% | 1.553% | 1.506% | 2.24% | 1.475% | 2.374% | 0.3256% | 0.982% | -0.4575% | 1.837% | 1.704% | 2.312% | 0.8979% | -1.991% | -2.126% | 2.185% | 2.438% | 7.363% | 6.378% | -1.672% | -0.6329% | -2.22% | 9.886% | -2.063% | 8.791% | -2.811% | -1.534% | -2.969% | -1.531% | -2.415% | -2.646% | -1.758% | -2.14% | -1.486% | -2.393% | -2.474% | -3.027% | -2.419% | -2.037% | -2.506% | -3.906% | -1.825% | -3.461% | -1.079% | -2.187% | -1.832% | -0.7637% | -1.723% | -1.497% | -1.938% | -2.057% | -2.252% | -2.202% | -2.145% | -2.928% | -1.767% | -2.675% | -0.1068% | -1.848% | -0.784% | 0.07432% | -0.6952% | -0.05696% | -1.154% | 0.06854% | 0.6291% | -0.07499% | 0.1302% | 0.07391% | -0.6945% | -0.1006% | -1.168% | -0.887% | -1.37% | -1.449% | -0.9909% | -1.699% | -1.517% | -2.535% | -0.3672% | -0.886% | -1.438% | -1.371% | -1.513% | -0.638% | -0.6096% | -1.283% | -1.43% | -1.994% | -1.884% | -1.791% | 0.04774% | -0.6484% | 0.1099% | -1.594% | -2.017% | -1.625% | -1.145% | -0.06414% | -1.516% | -1.945% | -0.5683% | -1.032% | -1.604% | -1.293% | 2.018% | 2.606% | 2.531% | 2.265% | 2.979% | 2.663% | 2.71% | 0.5569% | 2.104% | 2.076% | 1.817% | 1.814% | 1.936% | 0.9971% | 2.272% | 2.701% | 2.802% | 2.469% | 2.896% | 2.122% | 2.22% | 1.848% | 2.456% | 2.467%
2025-06-24 | -0.6391% | 1.147% | 1.178% | 1.054% | 2.055% | 1.95% | 2.369% | 0.5552% | 1.352% | 0.05619% | 11.63% | 1.086% | 11.78% | 0.213% | 1.056% | 1.323% | 0.3374% | 0.2421% | 0.4601% | 1.28% | -0.4346% | -0.8333% | -0.415% | -0.8008% | -2.252% | -3.897% | -3.548% | -3.809% | -0.1927% | 0.53% | 0.1551% | -0.2511% | 0.5501% | 0.6278% | 1.369% | 0.6313% | 1.93% | 0.07001% | 0.5704% | 0.02676% | 2.188% | 2.427% | 2.419% | 2.393% | -1.65% | -2.16% | 2.798% | 2.87% | 7.878% | 6.632% | -1.703% | -0.9875% | -1.746% | 9.563% | -2.777% | 9.272% | -3.376% | -2.731% | -2.586% | -1.344% | -1.83% | -2.762% | -2.309% | -2.619% | -3.015% | -3.688% | -3.537% | -3.569% | -3.868% | -2.872% | -3.898% | -3.71% | -3.223% | -3.227% | -1.9% | -2.84% | -1.681% | -1.164% | -1.198% | -1.832% | -2.325% | -2.503% | -2.653% | -2.613% | -2.678% | -3.657% | -3.199% | -3.711% | -1.396% | -3.232% | -1.897% | -1.222% | -1.914% | -1.286% | -2.404% | -1.335% | -0.1816% | -0.1824% | 0.1331% | 0.4295% | -0.2562% | 0.3991% | -0.5793% | -0.2585% | -1.206% | -0.9547% | -0.7648% | -1.397% | -1.34% | -2.437% | -0.4816% | -0.07896% | -1.078% | -0.958% | -1.69% | -0.2356% | -0.4128% | -0.7698% | -1.873% | -2.234% | -1.402% | -1.192% | 0.2552% | -0.02278% | 0.3877% | -0.8135% | -1.287% | -0.9186% | -0.6083% | 0.05635% | -1.233% | -1.508% | -0.4801% | -1.099% | -1.509% | -1.115% | 2.549% | 3.01% | 2.872% | 2.856% | 3.428% | 3.108% | 3.263% | 0.9732% | 2.902% | 2.822% | 2.589% | 2.354% | 2.681% | 1.704% | 2.57% | 3.298% | 3.389% | 2.86% | 3.501% | 2.889% | 3.013% | 2.902% | 1.117% | 3.182%
2025-06-25 | -1.201% | 0.03235% | -0.05439% | -0.2874% | 1.05% | 1.424% | 1.906% | 0.3229% | 0.9035% | -0.612% | 11.11% | 0.7781% | 12.16% | 0.5066% | 1.76% | 1.836% | 1.451% | -0.06099% | 1.665% | 2.095% | 1.134% | -1.698% | 1.155% | 0.854% | -0.2429% | -1.839% | -2.059% | -2.011% | 1.447% | 1.458% | 1.05% | 1.185% | 1.494% | 1.589% | 3.194% | 2.145% | 3.126% | 0.7102% | 1.32% | -0.5654% | 1.567% | 1.181% | 2.034% | 1.207% | -1.685% | -2.573% | 2.754% | 2.195% | 7.629% | 7.188% | -0.7731% | 0.2371% | -2.979% | 10.69% | -1.648% | 10.21% | -2.308% | -1.98% | -2.114% | -1.079% | -2.675% | -2.447% | -2.511% | -2.692% | -2.397% | -3.38% | -3.28% | -3.861% | -3.617% | -3.192% | -4.033% | -4.758% | -2.806% | -4.419% | -1.898% | -3.577% | -2.251% | -1.697% | -3.655% | -2.17% | -2.803% | -3.068% | -2.82% | -5.106% | -2.71% | -3.848% | -2.725% | -4.91% | -0.6338% | -2.461% | -0.7601% | -0.4354% | -1.014% | -0.5957% | -3.164% | -0.5191% | 0.03392% | -0.9013% | -0.8578% | -0.9884% | -1% | -0.6961% | -1.565% | -1.814% | -1.849% | -2.566% | -1.412% | -2.083% | -1.369% | -1.866% | -0.2437% | -2.911% | -3.074% | -2.52% | -2.791% | -1.683% | -1.236% | -1.993% | -2.102% | -2.336% | -2.033% | -1.575% | 0.1157% | -2.525% | 0.6763% | -2.799% | -1.616% | -1.441% | -4.053% | -0.7059% | -1.8% | -2.509% | -1.463% | -1.663% | -2.292% | -1.515% | 3.393% | 4.705% | 3.772% | 3.948% | 3.607% | 3.365% | 3.005% | 0.7986% | 4.634% | 4.117% | 1.881% | 3.411% | 3.556% | 2.41% | 3.822% | 3.967% | 2.903% | 4.1% | 4.68% | 2.293% | 4.058% | 4.694% | 2.72% | 4.775%
2025-06-26 | 1.323% | 1.687% | -0.249% | -0.005917% | 0.2492% | 0.5665% | 2.066% | 0.2237% | 3.028% | 1.889% | 11.72% | 2.555% | 10.97% | 1.375% | 0.1365% | 0.7442% | -0.7296% | -0.9746% | 0.5737% | 1.538% | -0.7831% | -0.6695% | -0.8156% | -0.8601% | -0.4865% | -1.264% | -1.91% | -2.594% | 0.4936% | 0.3724% | 0.6862% | 0.6101% | 3.425% | 3.434% | 3.793% | 2.686% | 3.373% | 1.235% | 1.6% | 1.882% | -1.393% | 0.0643% | -9.13% | 3.049% | -3.741% | -4.979% | 0.2489% | -0.9163% | 8.45% | 8.195% | 0.2936% | 2.174% | -0.5891% | 10.24% | 0.1076% | 11.6% | 0.4738% | 0.06762% | 0.07187% | 1.128% | 0.7499% | 0.1463% | -0.5004% | -0.6945% | 0.4615% | -0.01834% | -0.1882% | -0.5363% | -1.247% | 0.3185% | -1.112% | -0.6053% | -0.2292% | -0.3985% | 1.065% | -0.6156% | 1.102% | 0.2686% | 1.169% | 0.2155% | 0.4606% | 0.0247% | -0.6875% | -0.3656% | 0.05682% | -1.227% | 0.766% | -0.2831% | 1.511% | 0.2549% | 1.818% | 1.354% | 1.125% | 2.562% | 1.183% | 1.12% | 2.058% | 1.224% | 0.3561% | 1.036% | 0.4046% | 1.241% | 0.1343% | 0.3343% | -0.2772% | -0.06719% | -0.00508% | -0.5615% | 0.09191% | -0.3998% | 0.6576% | 1.066% | -2.806% | -1.358% | -1.157% | -0.08778% | -0.5436% | -1.117% | -1.361% | -1.651% | -1.794% | -1.164% | 0.4324% | 0.4781% | 0.6134% | -0.9956% | -1.582% | -1.283% | -1.27% | -0.4461% | -2.239% | -2.289% | -1.358% | -1.281% | -5.02% | -4.526% | -1.759% | -0.05218% | -2.152% | -0.7089% | -1.395% | -0.8535% | -0.8342% | -2.67% | -2.171% | -2.73% | -2.014% | -2.38% | -1.795% | -2.737% | -1.189% | -2.04% | -2.701% | -3.489% | -3.871% | -4.402% | -4.122% | -3.264% | -3.512% | -1.954%
2025-06-27 | 4.184% | 5.447% | 4.699% | 5.034% | 5.252% | 5.495% | 6.443% | 4.337% | 5.454% | 4.623% | 14.88% | 5.04% | 15.24% | 3.771% | 5.108% | 5.181% | 4.488% | 2.868% | 4.108% | 4.911% | 3.485% | 1.124% | 3.092% | 2.837% | 1.064% | 0.3278% | 0.03414% | -0.3693% | 3.247% | 3.987% | 3.063% | 2.407% | 3.058% | 2.841% | 5.062% | 3.878% | 4.431% | 2.289% | 1.47% | 1.086% | 3.167% | 4.058% | 3.091% | 15.78% | 0.02828% | -2.101% | 4.221% | 3.515% | 11.23% | 10.62% | 1.976% | 3.035% | 0.1884% | 14.21% | 0.9474% | 12.87% | 1.179% | 0.4981% | 1.905% | 1.641% | -0.1385% | 1.855% | 0.2457% | 0.2% | 0.09928% | -0.6263% | -0.4074% | -1.797% | -2.458% | -0.5703% | -17.61% | -5.095% | 0.1026% | -1.83% | 1.349% | -1.343% | 0.6316% | 0.6375% | 0.9707% | 0.4165% | -1.23% | -1.831% | -1.775% | -5.858% | -1.743% | -3.548% | -0.3126% | -2.704% | 0.6866% | -1.029% | 0.8565% | -0.1148% | -0.253% | 1.409% | 0.1662% | -0.08752% | 1.03% | -0.9083% | -1.588% | -0.8848% | -1.712% | -0.3479% | -1.879% | -1.601% | -1.939% | -1.801% | -1.767% | -2.62% | -3.88% | -3.59% | -0.8905% | -13.83% | -3.861% | -3.589% | -4.885% | -2.324% | -5.69% | -5.087% | -5.971% | -5.282% | -5.789% | -5.013% | -2.361% | -7.366% | -2.805% | -7.253% | -6.002% | -5.828% | -12.3% | -3.903% | -5.526% | -6.004% | -4.679% | -4.756% | -4.778% | -4.228% | -1.399% | -0.2753% | -1.296% | -2.819% | -1.088% | -0.9143% | -2.09% | -2.856% | -1.119% | -1.602% | -2.727% | -2.155% | -1.869% | -3.998% | -1.202% | -1.194% | -3.303% | -2.172% | -1.868% | -4.133% | -2.53% | -1.637% | -1.792% | -1.532%
2025-06-28 | -3.637% | -3.312% | -3.623% | -2.877% | -2.93% | -3.395% | -2.623% | -3.582% | -2.116% | -2.528% | 7.503% | -1.697% | 7.448% | -3.186% | -4.321% | -3.261% | -3.151% | -6.414% | -3.05% | -2.285% | -3.705% | -6.252% | -3.801% | -4.333% | -4.605% | -5.486% | -6.629% | -6.648% | -4.362% | -1.687% | -1.662% | -2.954% | 0.8593% | -0.9835% | -1.22% | -2.109% | -0.6704% | -2.24% | 0.2726% | -1.605% | 2.117% | 2.737% | 1.202% | 14.22% | -0.9307% | -2.225% | 4.661% | 2.656% | 4.956% | 3.835% | -4.017% | -2.262% | -6.694% | 6.521% | -4.858% | 4.698% | -5.119% | -4.459% | -4.489% | -3.917% | -4.736% | -4.505% | -3.962% | -3.579% | -3.907% | -3.959% | -5.229% | -5.72% | -5.376% | -3.25% | -5.043% | -4.604% | -3.818% | -4.831% | -1.967% | -4.248% | -2.546% | -2.28% | -2.463% | -2.504% | -2.789% | -3.627% | -3.475% | -5.285% | -3.613% | -5.889% | -3.574% | -5.046% | -0.7366% | -3.651% | -0.7485% | -0.9696% | -0.6568% | 1.245% | 0.5048% | 0.5606% | 4.028% | 3.062% | 1.866% | 3.776% | 1.514% | 3.623% | 1.713% | 2.706% | 0.9281% | 2.093% | 1.403% | 1.758% | 1.248% | 1.897% | 2.807% | 2.942% | 0.5376% | 1.906% | 2.196% | 3.834% | 2.345% | 1.39% | 1.801% | 2.325% | 1.085% | 3.127% | 3.637% | 3.018% | 3.481% | 2.855% | 2.047% | 3.308% | 3.205% | 5.042% | 4.278% | 3.581% | 4.978% | 4.811% | 1.856% | 2.017% | 3.705% | 5.637% | 4.259% | 5.755% | 4.421% | 4.823% | 4.629% | 3.333% | 6.091% | 4.572% | 3.871% | 4.811% | 4.642% | 3.25% | 5.136% | 5.006% | 3.489% | 3.786% | 4.429% | 3.643% | 4.246% | 5.973% | 3.673% | 7.008%
2025-06-29 | -0.6329% | 1.523% | 2.651% | 1.986% | 4.593% | 4.339% | 3.915% | 2.004% | 1.099% | 0.3425% | 11.31% | 0.5131% | 13.09% | 0.5818% | 3.846% | 4.013% | 3.578% | 1.343% | 2.585% | 2.714% | 2.67% | -0.1216% | 3.636% | 2.601% | -0.4773% | -2.459% | -2.615% | -1.819% | 2.646% | 4.826% | 4.501% | 2.296% | 2.325% | 1.643% | 2.531% | 1.918% | 3.821% | 3% | 3.982% | 2.428% | 5.542% | 18.22% | 5.431% | 18.98% | 3.869% | 1.639% | 8.534% | 5.971% | 7.87% | 6.416% | -1.382% | -0.7499% | -1.942% | 11.89% | -3.103% | 9.6% | -3.904% | -3.54% | -2.768% | -2.93% | -3.798% | -3.042% | -3.69% | -3.227% | -4.294% | -4.947% | -4.63% | -5.519% | -4.832% | -3.888% | -4.48% | -6.537% | -3.23% | -3.082% | -1.809% | -2.956% | -1.805% | -1.729% | -0.6987% | -1.509% | -3.897% | -3.752% | -4.009% | -7.285% | -4.189% | -5.814% | -4.013% | -6.58% | -1.799% | -3.606% | -1.294% | -1.218% | -0.6633% | 1.471% | 0.5059% | -0.5293% | 0.9728% | -0.9093% | -0.9979% | -0.09637% | -0.8563% | 0.4567% | -0.3908% | 0.1453% | -0.673% | -0.1713% | -0.2874% | -0.8034% | -0.7475% | -0.6088% | 1.736% | -1.009% | -3.247% | -1.74% | -1.91% | -0.5203% | -1.964% | -1.438% | -2.747% | -2.422% | -2.139% | -0.4145% | 0.2649% | -1.413% | -8.289% | -0.7568% | -1.258% | 0.1009% | -1.473% | 1.414% | 0.9316% | 0.4871% | 0.963% | 0.713% | -2.778% | -2.032% | -0.6561% | 1.583% | -0.5499% | 0.4973% | 0.6303% | 0.8555% | -1.354% | -1.156% | -0.1616% | -0.9311% | -1.999% | -1.285% | -0.9888% | -2.818% | -2.271% | -0.7304% | -2.419% | -1.642% | -1.776% | -3.559% | -2.615% | -0.6999% | -2.774% | -0.8079%
2025-06-30 | -3.441% | -1.903% | -2.254% | -2.628% | -0.8155% | -0.1761% | 0.3221% | -1.343% | -1.32% | -2.6% | 9.606% | -1.641% | 10.75% | -1.135% | 0.5706% | 0.3885% | 0.5778% | 0.5133% | 0.8478% | 1.051% | -0.1281% | -0.2535% | 0.4536% | -0.25% | -1.585% | -3.167% | -3.358% | -3.237% | 0.5103% | 1.564% | 1.191% | 0.5305% | 1.498% | 1.142% | 2.011% | 0.8489% | 2.565% | 0.9512% | 1.288% | 0.6514% | 5.42% | 19.2% | 4.113% | 19.69% | 2.821% | 1.377% | 20.42% | 5.206% | 6.911% | 5.854% | -2.156% | -1.726% | -1.751% | 9.572% | -3.543% | 9.58% | -4.345% | -3.816% | -4.136% | -3.117% | -3.816% | -4.661% | -4.05% | -3.86% | -4.196% | -4.464% | -4.025% | -4.323% | -4.33% | -3.168% | -3.735% | -3.436% | -3.902% | -3.478% | -2.581% | -3.182% | -1.771% | -2.49% | -1.828% | -2.605% | -3.181% | -2.884% | -3.485% | -3.959% | -3.704% | -4.095% | -3.525% | -3.632% | -0.6437% | -3.03% | -1.054% | -0.7273% | -0.9422% | 0.4708% | -0.6633% | -0.8166% | 0.4294% | -0.4782% | -0.7436% | -0.2199% | -0.7216% | 0.2316% | -0.8993% | -0.05945% | -0.7813% | -0.6326% | -0.09561% | -0.6804% | 0.3854% | 0.004563% | 1.612% | 1.659% | -3.155% | -1.447% | -1.089% | 0.2085% | 0.1509% | -0.6313% | -0.1764% | -0.4382% | -0.5361% | 0.06048% | 1.383% | 1.183% | 0.8333% | -0.2802% | -0.4427% | -0.2831% | 0.2916% | 0.8005% | 0.05327% | -0.1502% | -0.04031% | -0.9688% | -3.334% | -1.904% | 0.2191% | 1.218% | 1.119% | 1.785% | 1.727% | 1.025% | 1.044% | -0.627% | 1.48% | 1.087% | 1.566% | 1.197% | 1.117% | -0.09667% | 2.267% | 2.026% | 1.039% | 0.5662% | 1.152% | 0.7398% | 0.7891% | 1.11% | 1.247% | 1.928%
2025-07-01 | 0.407% | 2.072% | 1.727% | 1.682% | 2.547% | 2.7% | 3.345% | 1.03% | 2.463% | 0.8725% | 12.85% | 1.976% | 12.49% | 1.39% | 0.7214% | 1.426% | 0.08948% | -0.183% | 0.4543% | 1.158% | -0.6296% | -0.7594% | -0.7144% | -1.059% | -1.69% | -3.044% | -3.169% | -3.298% | -0.113% | 0.2617% | -0.1563% | -0.1784% | 1.283% | 1.134% | 2.039% | 0.8454% | 2.001% | -0.1504% | 0.4317% | 0.142% | -0.1014% | 12.66% | 0.4947% | 15.2% | -2.749% | -3.77% | 14.32% | 0.2663% | 8.162% | 8.128% | -0.3512% | 0.4556% | -0.7763% | 10.52% | -1.172% | 10.87% | -1.547% | -0.8574% | -1.102% | -0.06582% | -0.6001% | -1.217% | -1.139% | -1.625% | -1.544% | -2.53% | -1.989% | -2.879% | -2.217% | -2.21% | -2.274% | -3.347% | -1.551% | -2.787% | -0.7354% | -2.669% | -1.726% | -0.6428% | -1.109% | -2.122% | -2.598% | -2.761% | -3.039% | -2.653% | -2.623% | -3.372% | -2.439% | -3.124% | -0.6417% | -2.426% | -0.9024% | -0.1602% | -0.5821% | 0.07416% | -1.043% | -0.2569% | 0.226% | -0.294% | -0.4458% | -0.5194% | -2.267% | -0.6938% | -1.507% | -1.261% | -1.877% | -1.889% | -1.689% | -2.375% | -2.189% | -2.909% | -1.5% | -1.079% | -3.274% | -1.878% | -2.286% | -1.134% | -1.288% | -1.921% | -2.124% | -2.492% | -2.561% | -2.509% | -0.788% | -1.264% | -1.53% | -2.189% | -2.739% | -2.303% | -1.301% | -0.5103% | -2.137% | -2.237% | -1.063% | -1.825% | -4.506% | -3.18% | 1.129% | 1.735% | 1.882% | 2.542% | 1.981% | 1.089% | 1.051% | -1.393% | 1.237% | 1.221% | 1.228% | 1.016% | 1.305% | 0.3593% | 2.008% | 1.985% | 1.172% | 0.6774% | 1.195% | 0.6741% | 0.7765% | 0.754% | 0.1176% | 1.257%
2025-07-02 | -0.6478% | 0.8542% | 0.6505% | 0.462% | 1.709% | 1.964% | 2.197% | 0.2004% | 1.405% | -0.273% | 11.92% | 0.7261% | 12.36% | 0.4036% | 1.669% | 1.996% | 1.24% | 0.7384% | 1.047% | 1.555% | 0.6437% | -0.2191% | 0.5875% | 0.285% | -1.479% | -3.019% | -2.965% | -3.031% | 0.6415% | 1.326% | 0.8723% | 0.4767% | 1.277% | 1.316% | 2.427% | 1.096% | 2.018% | 0.04405% | 0.8526% | 0.1274% | 2.418% | 15.01% | 3.007% | 17.36% | 3.98% | -0.8448% | 17.14% | 2.977% | 7.793% | 7.472% | -0.8112% | -0.3003% | -0.9889% | 10.68% | -1.571% | 10.47% | -2.653% | -1.91% | -1.992% | -1.167% | -1.913% | -2.146% | -3.343% | -3.744% | -2.59% | -3.169% | -3.041% | -3.476% | -3.236% | -2.875% | -3.592% | -4.004% | -2.332% | -3.584% | -1.925% | -3.033% | -2.437% | -1.444% | -2.028% | -2.167% | -2.915% | -2.733% | -2.89% | -3.701% | -2.926% | -3.464% | -2.658% | -3.262% | -1.062% | -2.351% | -1.616% | -0.9191% | -1.293% | -0.5433% | -1.62% | -0.8024% | -0.1257% | -0.5949% | -0.5072% | -0.4549% | -2.531% | -0.7556% | -1.478% | -1.409% | -1.579% | -1.867% | -1.304% | -2.127% | -1.655% | -2.421% | -0.6795% | -1.694% | -2.662% | -1.601% | -1.932% | -0.9699% | -0.741% | -1.556% | -1.486% | -2.264% | -1.954% | -1.873% | -0.2742% | -1.271% | -0.174% | -1.792% | -2.127% | -1.754% | -1.728% | -0.6913% | -1.72% | -2.187% | -1.523% | -2.087% | -2.764% | -2.4% | 0.9477% | 1.291% | 1.59% | 1.719% | 1.853% | 0.4338% | 1.013% | -0.7798% | 1.109% | 0.9849% | 0.8985% | 0.7694% | 0.8855% | -0.0651% | 1.343% | 1.62% | 1.343% | 0.902% | 1.234% | 0.4785% | 0.6845% | 0.7539% | 0.5272% | 1.253%
2025-07-03 | 2.058% | 4.505% | 4.1% | 3.473% | 5.297% | 5.048% | 4.901% | 0.115% | 4.104% | 2.575% | 15.25% | 3.867% | 15.62% | 3.801% | -1.684% | 2.434% | 3.213% | -4.071% | 3.389% | 4.027% | 2.415% | -4.902% | 1.641% | 1.893% | -4.881% | -6.887% | -13.66% | -8.76% | -3.303% | -3.158% | -3.532% | -3.255% | 3.763% | 3.97% | 4.788% | 3.259% | 3.996% | -0.4302% | 2.465% | 0.5686% | 3.803% | 10.11% | 4.802% | 12.32% | 8.61% | -3.082% | 18.35% | 4.125% | 5.681% | 7.18% | 1.693% | 2.421% | -6.27% | 12.79% | 0.3402% | 5.828% | -3.373% | -0.2694% | -0.6551% | 1.121% | -5.546% | 0.4708% | -1.478% | -1.306% | -0.3448% | -1.493% | -5.413% | -4.864% | -2.225% | -1.495% | -0.7669% | -7.43% | 0.8265% | -4.137% | 1.364% | -0.3471% | -0.6729% | 1.496% | -2.734% | -0.9877% | -1.279% | -0.7408% | -1.325% | -7.679% | -1.795% | -7.773% | -1.561% | -8.631% | -2.615% | -2.328% | -1.277% | -4.602% | -0.532% | 0.4705% | -2.127% | -0.1293% | 0.2031% | -1.001% | -3.062% | -0.1234% | -4.044% | -0.2205% | -0.8111% | -1.487% | 0.003025% | -1.209% | 0.2864% | -0.7847% | -2.181% | -2.838% | 1.675% | -4.768% | -1.829% | -2.181% | -3.703% | -3.122% | -0.7771% | -2.183% | -2.278% | -5.135% | -2.38% | -1.473% | 1.333% | -5.839% | 2.206% | -6.37% | -1.4% | -1.278% | -8.249% | -1.113% | -1.969% | -3.235% | -2.014% | -3.08% | -3.137% | -1.999% | -0.1743% | 0.8217% | 1.694% | -1.525% | -0.845% | 0.3076% | -3.27% | -0.4405% | 2.74% | 2.722% | -3.195% | 0.9793% | 0.7228% | -3.248% | 1.092% | 2.307% | 0.723% | -0.2213% | 4.994% | 0.2356% | 4.048% | 3.715% | 1.898% | 2.832%
2025-07-04 | -2.529% | -0.7247% | -1.026% | -0.8269% | 0.01926% | 0.3924% | -0.3254% | -1.208% | -0.3766% | -4.535% | 11.09% | -0.05696% | 11.5% | 1.699% | 1.955% | 2.081% | -9.397% | -8.998% | -7.96% | -7.618% | -8.958% | -9.648% | -8.162% | -8.993% | -0.8785% | -2.538% | -2.308% | -2.709% | 0.7505% | 4.384% | 4.573% | 1.916% | 3.421% | 3.084% | 3.278% | 2.861% | 4.848% | 2.875% | 4.755% | 3.856% | 15.23% | 30.38% | 16.09% | 31.04% | 21.12% | 7.426% | 30.58% | 14.53% | 9.697% | 8.732% | 0.5545% | 0.9095% | -0.336% | 12.8% | -1.645% | 10.55% | -1.953% | -3.213% | -0.8888% | -0.865% | -3.733% | -2.55% | -4.29% | -3.936% | -4.934% | -8.138% | -6.89% | -10.45% | -8.343% | -10.48% | -11.01% | -12.78% | -6.2% | -11.65% | -6.109% | -10.66% | -8.679% | -6.107% | -6.997% | -9.849% | -10.82% | -11.53% | -9.723% | -11.7% | -8.847% | -9.551% | -7.184% | -8.232% | -2.529% | -5.888% | -3.277% | -2.756% | -1.764% | 0.8087% | 0.3875% | -0.7192% | 1.686% | 0.02995% | -0.8248% | 0.4012% | 0.5007% | 1.175% | 3.074% | 1.484% | 3.195% | 1.409% | 2.715% | 1.012% | 3.332% | 2.988% | 4.928% | 0.5156% | -1.585% | -3.202% | -2.92% | -1.517% | -1.186% | -3.149% | -2.311% | -3.568% | -2.575% | -1.306% | 1.693% | -0.1994% | 2.721% | -1.326% | -1.537% | -1.283% | -3.039% | -1.876% | -0.6504% | -2.037% | -2.771% | -3.056% | -3.917% | -3.174% | 1.985% | 1.506% | 5.695% | 3.649% | 1.263% | 1.613% | 0.8894% | -1.871% | 9.351% | 8.46% | 5.607% | 6.277% | 6.592% | 2.458% | 8.307% | 8.475% | 3.749% | 4.286% | -18.09% | -3.584% | 7.955% | 9.759% | 2.997% | 7.259%
2025-07-05 | -2.37% | -1.303% | -2.464% | -2.817% | -1.491% | -1.58% | -0.5894% | -3.286% | -0.3832% | -2.158% | 7.344% | -1.072% | 7.28% | -1.903% | 0.5692% | -0.3422% | 0.6674% | 0.4148% | 0.7156% | 1.074% | -0.2291% | -0.3328% | 0.688% | -0.2426% | -0.2632% | -1.648% | -2.741% | -2.637% | 0.9533% | 2.503% | 2.532% | 1.819% | 4.201% | 3.378% | 3.627% | 2.916% | 4.285% | 2.84% | 3.024% | 2.574% | 3.152% | 15.82% | 3.421% | 17.47% | 8.244% | -2.041% | 18.25% | 3.218% | 5.11% | 5.001% | -2.341% | 0.1806% | -2.671% | 8.305% | -1.935% | 10.47% | -2.126% | -2.546% | -3.837% | -3.061% | -3.853% | -3.854% | -2.917% | -3.36% | -3.356% | -3.89% | -2.526% | -3.548% | -3.621% | -2.183% | -3.538% | -2.768% | -2.443% | -2.617% | -1.331% | -3.425% | -1.481% | -2.984% | -1.853% | -4.531% | -12.5% | -13.17% | -11.41% | -13.23% | -11.74% | -12.69% | -12.5% | -12.16% | 0.5602% | -2.033% | 0.7099% | -0.06577% | 0.4955% | 3.004% | 2.411% | 1.3% | 4.591% | 3.115% | 0.6739% | 2.388% | -0.9157% | 2.1% | 0.05546% | 0.7588% | -0.9585% | 0.08787% | -1.037% | -0.8295% | -1.698% | -1.623% | -1.098% | 0.08847% | 0.4633% | -1.322% | -0.7569% | 0.7118% | -1.352% | -2.354% | -1.694% | -1.547% | -2.271% | -0.8953% | 0.2688% | 0.355% | 0.3851% | 0.1753% | -1.384% | -0.5813% | -0.8332% | 0.3249% | -0.5628% | -1.601% | -1.194% | -1.434% | -0.7271% | 0.09312% | 3.01% | 5.321% | 2.698% | 5.501% | 3.294% | 3.684% | 4.315% | 1.205% | 4.248% | 2.851% | 2.697% | 2.371% | 2.992% | 2.046% | 5.3% | 3.093% | 1.673% | 0.8255% | 0.7643% | 0.4349% | 1.067% | 3.504% | 1.428% | 4.533%
2025-07-06 | 2.084% | 1.894% | 1.029% | 1.376% | 1.601% | 1.577% | 2.415% | -0.9679% | 2.05% | 0.6116% | 8.957% | 1.663% | 8.63% | 0.711% | 0.9987% | 1.181% | 0.4919% | 0.1129% | 0.3768% | 1.169% | -0.4413% | -0.8749% | 0.2162% | -0.3572% | -1.371% | 1.602% | -2.225% | -2.694% | -0.6563% | 0.132% | 0.04585% | -1.055% | 6.253% | 6.269% | 7.858% | 6.366% | 0.5439% | -0.8642% | -0.4962% | -1.11% | -1.381% | 10.77% | -0.7577% | 11.99% | 3.635% | -6.421% | 12.7% | -1.118% | 6.822% | 6.525% | -0.9872% | 2.12% | -2.602% | 9.347% | -2.254% | 9.569% | 0.7497% | -3.054% | 1.198% | -2.404% | -2.429% | 1.171% | -1.801% | -0.1304% | -0.8068% | 0.7256% | -1.064% | -2.824% | -3.897% | 0.453% | -3.712% | -0.2185% | -1.483% | -2.048% | 2.245% | -3.417% | 1.882% | -2.014% | 1.71% | -2.699% | 0.5776% | -2.521% | -0.193% | -3.882% | 0.7748% | -2.219% | 0.8314% | 2.629% | -10.34% | -10.17% | -7.649% | -11.63% | -11.51% | -8.56% | -9.955% | -11.55% | 2.445% | 0.734% | -2.565% | 2.252% | -4.569% | 2.1% | -2.534% | 0.6289% | -3.341% | 1.359% | -3.075% | -0.1302% | -2.734% | -0.3321% | -1.807% | -0.7502% | 1.067% | -2.296% | -0.08829% | 1.855% | -2.788% | -4.06% | -3% | -0.5721% | -3.225% | 1.03% | -0.6096% | 0.1363% | 0.4881% | 2.492% | -1.738% | 1.64% | -0.5493% | 1.864% | 1.559% | 3.921% | 2.045% | 4.687% | 0.7812% | 1.116% | -0.4017% | 4.859% | 0.05372% | 4.895% | 1.046% | 3.987% | 3.708% | 2.198% | 1.039% | -0.6151% | -1.168% | 0.01464% | 0.4654% | -0.8665% | 3.824% | 0.6431% | -1.315% | -1.361% | -1.286% | -2.431% | -1.08% | 2.989% | -0.88% | 3.053%
2025-07-07 | 1.613% | 3.698% | 3.757% | 3.005% | 5.007% | 4.677% | 4.589% | 1.927% | 3.243% | 1.07% | 12.73% | 2.885% | 12.13% | 2.704% | 3.377% | 3.366% | 3.103% | 1.506% | 2.873% | 3.739% | 2.994% | 1.684% | 3.728% | 3.307% | 1.549% | 1.124% | -1.174% | -0.6758% | 2.917% | 2.975% | 2.281% | 1.902% | 1.713% | 1.606% | 4.171% | 2.481% | 2.934% | 1.284% | 2.037% | 1.256% | 2.741% | 16% | 3.856% | 17.67% | 9.053% | -1.9% | 17.88% | 3.609% | 8.415% | 8.742% | -0.1204% | 2.004% | -1.22% | 11.23% | -1.247% | 10.64% | -0.06605% | -1.612% | 1.26% | -0.5794% | -1.266% | 0.9038% | -1.223% | -0.04267% | -1.383% | -1.781% | -1.602% | -3.763% | -2.963% | -1.273% | -3.261% | -1.737% | -1.288% | -2.11% | 0.5836% | -2.607% | 0.4491% | -0.5965% | 0.9153% | -1.037% | -1.543% | -2.702% | -2.603% | -4.329% | -2.365% | -4.271% | -1.647% | -2.549% | -1.224% | -2.55% | -0.9566% | -1.878% | -1.249% | 1.401% | 0.1039% | -1.069% | -8.553% | -9.603% | -11.17% | -9.818% | -13.23% | -9.975% | -12.32% | -11.13% | -2.779% | -0.883% | -2.402% | -2.032% | -2.283% | -1.701% | -1.048% | -0.8406% | -1.221% | -3.342% | -2.166% | -1.098% | -3.091% | -4.147% | -3.688% | -1.98% | -3.35% | -0.4473% | -1.216% | 0.473% | -1.216% | -0.02845% | -1.74% | 0.2841% | -1.871% | -0.1626% | 0.3424% | -0.5026% | -0.06375% | -0.6544% | -2.332% | -2.112% | -2.463% | -0.417% | -2.402% | -0.513% | -1.092% | -0.4623% | 0.1515% | -0.6354% | 0.4053% | -0.9402% | -1.093% | -1.818% | -1.627% | -2.985% | -1.037% | -1.125% | -1.68% | -0.9825% | -3.737% | -2.515% | -1.137% | 0.2467% | -1.691% | 0.9894%
2025-07-08 | 4.97% | 5.608% | 5.372% | 5.52% | 6.812% | 7.185% | 7.313% | 4.542% | 5.884% | 5.486% | 15.93% | 4.961% | 16.14% | 4.502% | 5.032% | 5.839% | 2.996% | 1.975% | 2.429% | 3.653% | 1.162% | 1.073% | -0.2611% | -0.01522% | -1.702% | -2.083% | -1.654% | -2.322% | -0.09091% | -0.2083% | -0.822% | -0.723% | -1.153% | -0.653% | 1.67% | -0.225% | 0.3649% | -1.447% | -1.088% | -1.843% | -4.446% | 7.253% | -4.124% | 8.975% | 1.183% | -6.941% | 10.65% | -3.159% | 11.14% | 11.16% | 2.318% | 2.857% | 1.681% | 13.94% | 0.739% | 12.58% | 1.418% | 1.53% | 1.739% | 2.565% | 1.63% | 1.389% | 0.3462% | 0.6754% | 0.7767% | -0.3327% | 0.319% | -0.7371% | 0.1179% | 0.6597% | -0.6652% | -0.526% | 0.8124% | 0.02837% | 1.654% | 0.1277% | 1.495% | 1.8% | 2.261% | 1.672% | 0.01102% | 0.2004% | -0.4136% | -0.5943% | -0.3412% | -1.493% | -0.6436% | -1.347% | 0.5355% | -1.252% | -0.6403% | -1.156% | -2.601% | -2.299% | -3.575% | -2.846% | -3.238% | -3.418% | -4.204% | -3.784% | -6.227% | -4.467% | -5.991% | -5.842% | -7.118% | -6.939% | -6.883% | -7.498% | -7.498% | -8.373% | -6.709% | -6.872% | -4.627% | -5.48% | -7.435% | -5.768% | -6.077% | -6.313% | -7.226% | -8.608% | -7.012% | -6.545% | -5.941% | -6.31% | -5.979% | -7.086% | -6.997% | -6.419% | -5.538% | -3.836% | -5.871% | -6.03% | -4.198% | -3.859% | -3.462% | -3.101% | 1.634% | 1.883% | 2.566% | 2.466% | 1.757% | -0.09569% | 0.1399% | -1.74% | 3.359% | 2.922% | 3.379% | 2.713% | 2.666% | 1.218% | 2.868% | 3.141% | 3.834% | 3.4% | 2.838% | 2.04% | 2.476% | 2.95% | 3.52% | 4.089%
2025-07-09 | -0.8056% | 2.203% | 2.582% | 1.819% | 3.846% | 4.482% | 4.489% | 2.489% | 2.184% | -1.799% | 13.64% | 2.359% | 13.84% | 2.847% | 3.701% | 4.063% | 1.898% | 0.8436% | 1.165% | 2.668% | -0.07033% | -0.3673% | 0.5247% | -0.02575% | -1.602% | -2.371% | -2.323% | -3.336% | 0.5037% | 1.032% | 0.2317% | 0.4985% | 1.028% | 0.9456% | 2.157% | 1.086% | 2.095% | 0.01023% | -0.06228% | -0.4333% | 1.12% | 14.49% | 1.95% | 17.03% | 7.254% | -2.749% | 16% | 1.44% | 10.18% | 9.242% | 0.9116% | 1.688% | 0.4658% | 12.23% | -0.4798% | 11.97% | -0.1555% | -0.452% | 0.3689% | 0.4742% | -0.1893% | -0.2546% | -1.603% | -2.363% | -0.6445% | -1.6% | -1.248% | -2.504% | -1.979% | -1.692% | -2.432% | -2.883% | -1.156% | -2.519% | -0.5241% | -3.268% | -1.686% | -1.602% | -1.083% | -2.884% | -2.058% | -2.935% | -3.596% | -2.874% | -2.485% | -3.372% | -1.461% | -1.861% | -0.09731% | -1.295% | -0.4291% | -0.8887% | -1.537% | -0.4748% | -1.237% | -1.31% | 0.2088% | -0.3407% | -1.306% | -0.248% | -2.564% | -0.1745% | -1.638% | -0.7258% | -3.502% | -2.008% | -3.421% | -3.638% | -4.102% | -4.981% | -3.405% | -3.177% | -1.446% | -1.98% | -2.34% | -0.8896% | -1.936% | -2.132% | -3.118% | -2.873% | -3.579% | -3.337% | -2.629% | -3.129% | -2.576% | -3.19% | -4.051% | -3.232% | -1.301% | -0.5428% | -3.11% | -2.697% | -1.451% | -1.764% | -0.5833% | 0.06339% | 0.6089% | 2.874% | 0.9791% | 5.227% | 2.619% | 2.187% | 3.188% | 1.204% | -1.919% | -2.792% | -2.563% | -2.605% | -0.8414% | -0.9189% | 0.8252% | -1.174% | -1.934% | -2.691% | -2.414% | -2.845% | -2.831% | -2.188% | -3.011% | -1.687%
2025-07-10 | -13.78% | -13.04% | 1.193% | 0.3734% | 3.596% | 4.259% | 2.922% | 1.341% | 0.1439% | -4.424% | 11.37% | -0.08117% | 13.32% | 0.9822% | 4.115% | 4.132% | 3.717% | 2.978% | 3.81% | 4.054% | 2.18% | 2.13% | 1.669% | 1.65% | 0.8045% | -0.4946% | -1.188% | -0.6707% | 1.888% | 1.995% | 1.677% | 1.255% | 1.732% | 2.087% | 4.32% | 2.303% | 2.716% | 0.755% | 1.478% | 0.7296% | 4.866% | 18.53% | 5.768% | 20.65% | 11.1% | 1.249% | 21.02% | 5.9% | 8.288% | 6.59% | -0.4255% | -0.3609% | -0.1982% | 11.6% | -2.19% | 10.93% | -4.112% | -4.138% | -2.727% | -3.237% | -4.026% | -3.22% | -6.332% | -6.561% | -5.171% | -5.634% | -6.03% | -5.871% | -6.843% | -5.546% | -6.74% | -6.808% | -6.052% | -6.697% | -5.146% | -6.935% | -5.917% | -5.718% | -5.756% | -6.783% | -4.841% | -5.563% | -6.361% | -5.043% | -4.832% | -5.589% | -4.836% | -5.539% | -2.453% | -4.784% | -1.722% | -1.383% | -0.7809% | 0.7152% | -0.06772% | -0.3737% | 1.167% | 0.1311% | 0.7479% | 0.9913% | -0.8214% | 1.352% | 0.4651% | 0.7194% | -0.3657% | 0.3331% | -0.247% | -0.4884% | -1.376% | -2.318% | -1.032% | -0.1516% | -0.8681% | -0.7683% | -0.9091% | 0.2621% | -0.7942% | -1.356% | -0.9985% | -2.883% | -1.103% | -0.4002% | 1.002% | 0.8268% | 0.6013% | -0.1905% | -0.4741% | -0.3031% | -1.379% | -0.6647% | -0.7487% | -1.586% | -1.296% | -1.908% | -2.767% | -2.172% | 0.8283% | 2.187% | 0.9217% | 13.37% | 2.266% | 0.9412% | 1.311% | 0.4942% | 0.7496% | 0.511% | 0.06515% | -0.2796% | -0.2394% | -1.015% | 1.083% | 0.7% | 1.159% | 0.5166% | 0.7385% | 0.4241% | 0.4213% | 0.9191% | 0.3231% | 1.149%
2025-07-11 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Formulas:
Date = [Date, row above]+1

## ModellingYTD (hidden)
Year Number | Month | POA(kWh/m2) | GHI (kWh/m2) | Budgeted Energy (MWh) | Tmod | Irradiationce Losses (IAM+NearShadding+Solining) | Bifacial Gain | Temperature Loss | Mismatch Loss | DC Ohmic Loss | Inverter Conversion Loss | MPPT Mismatch Losse | AC Ohmic Loss | Clipping Loss | Plant Uptime | Grid Uptime | Tracker Uptime
Year-Apr | Apr | 215.9 | 208.9997 | 59637.6 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | May | 217.9 | 221.9002 | 61013.7 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | Jun | 192.8 | 200.2009 | 54806.4 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | Jul | 168.9 | 173.5997 | 48598.11 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | Aug | 174.2 | 172.6002 | 49476.24 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | Sep | 192.1 | 178.8993 | 53840.16 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | Oct | 202.3 | 174.6008 | 56487.42 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | Nov | 162.9 | 133.6994 | 47868.48 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | Dec | 158.6 | 124.4 | 47682.36 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | Jan | 169.0285 | 133.8993 | 50622.66 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | Feb | 172.5591 | 145.4008 | 49925.7 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | Mar | 215.7458 | 195.5989 | 59767.29 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2022-04-01 | 215.9 | 208.9997 | 59637.6 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2022-05-01 | 217.9 | 221.9002 | 61013.7 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2022-06-01 | 192.8 | 200.2009 | 54806.4 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2022-07-01 | 168.9 | 173.5997 | 48598.11 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2022-08-01 | 174.2 | 172.6002 | 49476.24 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2022-09-01 | 192.1 | 178.8993 | 53840.16 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2022-10-01 | 202.3 | 174.6008 | 56487.42 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2022-11-01 | 162.9 | 133.6994 | 47868.48 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2022-12-01 | 158.6 | 124.4 | 47682.36 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2023-01-01 | 169.0285 | 133.8993 | 50622.66 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2023-02-01 | 172.5591 | 145.4008 | 49925.7 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2023-03-01 | 215.7458 | 195.5989 | 59767.29 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2023-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2023-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2023-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2023-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2023-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2023-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2023-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2023-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2023-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2024-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2024-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2024-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2024-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2024-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2024-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2024-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2024-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2024-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2024-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2024-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2024-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2025-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2025-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2025-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2025-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2025-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2025-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2025-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2025-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2025-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2025-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2025-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2025-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2026-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2026-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2026-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2026-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2026-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2026-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2026-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2026-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2026-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2026-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2026-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2026-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2027-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2027-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2027-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2027-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2027-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2027-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2027-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2027-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2027-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2027-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2027-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2027-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2028-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2028-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2028-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2028-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2028-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2028-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2028-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2028-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2028-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2028-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2028-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2028-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2029-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2029-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2029-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2029-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2029-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2029-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2029-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2029-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2029-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2029-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2029-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2029-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2030-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2030-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2030-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2030-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2030-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2030-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2030-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2030-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2030-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2030-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2030-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2030-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2031-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2031-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2031-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2031-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2031-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2031-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2031-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2031-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2031-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2031-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2031-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2031-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2032-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2032-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2032-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2032-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2032-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2032-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2032-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2032-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2032-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2032-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2032-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2032-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2033-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2033-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2033-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2033-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2033-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2033-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2033-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2033-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2033-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2033-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2033-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2033-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2034-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2034-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2034-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2034-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2034-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2034-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2034-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2034-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2034-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2034-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2034-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2034-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2035-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2035-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2035-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2035-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2035-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2035-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2035-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2035-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2035-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2035-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2035-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2035-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2036-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2036-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2036-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2036-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2036-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2036-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2036-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2036-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2036-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2036-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2036-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2036-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2037-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2037-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2037-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2037-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2037-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2037-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2037-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2037-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2037-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2037-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2037-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2037-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2038-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2038-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2038-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2038-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2038-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2038-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2038-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2038-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2038-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2038-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2038-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2038-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2039-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2039-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2039-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2039-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2039-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2039-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2039-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2039-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2039-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2039-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2039-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2039-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2040-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2040-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2040-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2040-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2040-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2040-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2040-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2040-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2040-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2040-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2040-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2040-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2041-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2041-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2041-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2041-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2041-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2041-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2041-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2041-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2041-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2041-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2041-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2041-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2042-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2042-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2042-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2042-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2042-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2042-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2042-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2042-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2042-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2042-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2042-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2042-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2043-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2043-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2043-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2043-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2043-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2043-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2043-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2043-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2043-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2043-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2043-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2043-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2044-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2044-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2044-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2044-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2044-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2044-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2044-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2044-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2044-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2044-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2044-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2044-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2045-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2045-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2045-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2045-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2045-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2045-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2045-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2045-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2045-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2045-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2045-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2045-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2046-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2046-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2046-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2046-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2046-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2046-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2046-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2046-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2046-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2046-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2046-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2046-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2047-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2047-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2047-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Note on H26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear

## Basic Data (hidden)
Equipment | Affected DC Capacity | Plant Equivalent Weightage | Fault Category Plant BD sheet |  | IS Number |  | SCB Number |  | String Type | Equipment | Inverter Module Number |  | Status |  | Plant capacity | Month No. | Month Name
IS1INV1M1 | 2064.8 | 0.6162% | Module |  | IS1 |  | SCB1 |  | Str_Typ1(445*29) | Tx | M1 |  | Open |  | 335091
IS1INV1M2 | 2090.61 | 0.6239% | Cables |  | IS2 |  | SCB2 |  | Str_Typ2 (450*29) | MVP | M2 |  | Close
IS1INV2M1 | 2090.61 | 0.6239% | String Fuses |  | IS3 |  | SCB3 |  | Str_Typ3(535*29) | Aux_Tx
IS1INV2M2 | 2077.705 | 0.62% | SCB |  | IS4 |  | SCB4 |  | Str_Typ4(540*29) | MCR_MVP_Inc1
IS1INV3M1 | 2090.61 | 0.6239% | Inverter |  | IS5 |  | SCB5 |  | Str_Typ5(545*29) | MCR_MVP_Inc2
IS1INV3M2 | 2090.61 | 0.6239% | IDT |  | IS6 |  | SCB6 |  | Str_Typ6(445*58) | MCR_MVP_Inc3
IS1INV4M1 | 2090.61 | 0.6239% | PTR |  | IS7 |  | SCB7 |  | Str_Typ7(450*58) | MCR_MVP_Inc4
IS1INV4M2 | 2193.85 | 0.6547% | MV Panel |  | IS8 |  | SCB8 |  | Str_Typ8(535*58) | MCR_MVP_Inc5
IS2INV1M1 | 2090.61 | 0.6239% | Metering System Plant |  | IS9 |  | SCB9 |  | Str_Typ9(540*58) | MCR_MVP_Inc8
IS2INV1M2 | 2090.61 | 0.6239% | Grid System |  | IS10 |  | SCB10 |  | Str_Typ10(545*58) | MCR_MVP_Inc9
IS2INV2M1 | 2090.61 | 0.6239% | Metering System Grid |  | IS11 |  |  |  |  | MCR_MVP_Inc10
IS2INV2M2 | 2090.61 | 0.6239% | WMS |  | IS12 |  |  |  |  | MCR_MVP_Inc11
IS2INV3M1 | 2064.8 | 0.6162% | MMS |  | IS13 |  |  |  |  | MCR_MVP_Inc12
IS2INV3M2 | 2090.61 | 0.6239% | Battery Charger_MCR |  | IS14 |  |  |  |  | MCR_MVP_OG1
IS2INV4M1 | 2090.61 | 0.6239% | IC_UPS |  | IS15 |  |  |  |  | MCR_MVP_OG2
IS2INV4M2 | 2090.61 | 0.6239% | IC_Auxiliary Tranformer |  | IS16 |  |  |  |  | Power_Tx1
IS3INV1M1 | 2090.61 | 0.6239% | IC_Auxiliary DB |  | IS17 |  |  |  |  | Power_Tx2
IS3INV1M2 | 2090.61 | 0.6239% | IC_SCADA Panel |  | IS18 |  |  |  |  | Line_Bay1
IS3INV2M1 | 2090.61 | 0.6239% | Connectors |  | IS19
IS3INV2M2 | 2090.61 | 0.6239% |  |  | IS20
IS3INV3M1 | 2114.1 | 0.6309%
IS3INV3M2 | 2088 | 0.6231%
IS3INV4M1 | 2114.1 | 0.6309%
IS3INV4M2 | 2088 | 0.6231%
IS4INV1M1 | 2088 | 0.6231%
IS4INV1M2 | 1879.2 | 0.5608%
IS4INV2M1 | 2114.1 | 0.6309%
IS4INV2M2 | 2088 | 0.6231%
IS4INV3M1 | 2114.1 | 0.6309%
IS4INV3M2 | 2088 | 0.6231%
IS4INV4M1 | 2114.1 | 0.6309%
IS4INV4M2 | 2061.9 | 0.6153%
IS5INV1M1 | 2090.61 | 0.6239%
IS5INV1M2 | 2090.61 | 0.6239%
IS5INV2M1 | 2090.61 | 0.6239%
IS5INV2M2 | 2090.61 | 0.6239%
IS5INV3M1 | 2090.61 | 0.6239%
IS5INV3M2 | 2090.61 | 0.6239%
IS5INV4M1 | 2090.61 | 0.6239%
IS5INV4M2 | 2090.61 | 0.6239%
IS6INV1M1 | 2234.16 | 0.6667%
IS6INV1M2 | 1985.92 | 0.5927%
IS6INV2M1 | 2203.13 | 0.6575%
IS6INV2M2 | 1985.92 | 0.5927%
IS6INV3M1 | 2192.4 | 0.6543%
IS6INV3M2 | 2380.32 | 0.7104%
IS6INV4M1 | 2203.13 | 0.6575%
IS6INV4M2 | 1985.92 | 0.5927%
IS7INV1M1 | 1973.16 | 0.5888%
IS7INV1M2 | 1973.16 | 0.5888%
IS7INV2M1 | 2098.44 | 0.6262%
IS7INV2M2 | 2004.48 | 0.5982%
IS7INV3M1 | 2223.72 | 0.6636%
IS7INV3M2 | 1973.16 | 0.5888%
IS7INV4M1 | 2223.72 | 0.6636%
IS7INV4M2 | 1973.16 | 0.5888%
IS8INV1M1 | 2004.48 | 0.5982%
IS8INV1M2 | 2255.04 | 0.673%
IS8INV2M1 | 2255.04 | 0.673%
IS8INV2M2 | 2004.48 | 0.5982%
IS8INV3M1 | 2255.04 | 0.673%
IS8INV3M2 | 2004.48 | 0.5982%
IS8INV4M1 | 2088 | 0.6231%
IS8INV4M2 | 2061.9 | 0.6153%
IS9INV1M1 | 2102.065 | 0.6273%
IS9INV1M2 | 2023.04 | 0.6037%
IS9INV2M1 | 2102.065 | 0.6273%
IS9INV2M2 | 2212.7 | 0.6603%
IS9INV3M1 | 2275.33 | 0.679%
IS9INV3M2 | 2023.04 | 0.6037%
IS9INV4M1 | 2244.31 | 0.6698%
IS9INV4M2 | 1959.82 | 0.5849%
IS10INV1M1 | 2067.12 | 0.6169%
IS10INV1M2 | 2098.44 | 0.6262%
IS10INV2M1 | 1973.16 | 0.5888%
IS10INV2M2 | 2223.72 | 0.6636%
IS10INV3M1 | 1941.84 | 0.5795%
IS10INV3M2 | 2255.04 | 0.673%
IS10INV4M1 | 1973.16 | 0.5888%
IS10INV4M2 | 2223.72 | 0.6636%
IS11INV1M1 | 2023.04 | 0.6037%
IS11INV1M2 | 2212.7 | 0.6603%
IS11INV2M1 | 2275.92 | 0.6792%
IS11INV2M2 | 2038.845 | 0.6084%
IS11INV3M1 | 2023.04 | 0.6037%
IS11INV3M2 | 2212.7 | 0.6603%
IS11INV4M1 | 2023.04 | 0.6037%
IS11INV4M2 | 1785.965 | 0.533%
IS12INV1M1 | 2192.4 | 0.6543%
IS12INV1M2 | 2114.1 | 0.6309%
IS12INV2M1 | 1941.84 | 0.5795%
IS12INV2M2 | 2255.04 | 0.673%
IS12INV3M1 | 2192.4 | 0.6543%
IS12INV3M2 | 2004.48 | 0.5982%
IS12INV4M1 | 2004.48 | 0.5982%
IS12INV4M2 | 2208.06 | 0.6589%
IS13INV1M1 | 2004.48 | 0.5982%
IS13INV1M2 | 2004.48 | 0.5982%
IS13INV2M1 | 2192.4 | 0.6543%
IS13INV2M2 | 2004.48 | 0.5982%
IS13INV3M1 | 2192.4 | 0.6543%
IS13INV3M2 | 2004.48 | 0.5982%
IS13INV4M1 | 2192.4 | 0.6543%
IS13INV4M2 | 2004.48 | 0.5982%
IS14INV1M1 | 2223.72 | 0.6636%
IS14INV1M2 | 1910.52 | 0.5701%
IS14INV2M1 | 2223.72 | 0.6636%
IS14INV2M2 | 2004.48 | 0.5982%
IS14INV3M1 | 2192.4 | 0.6543%
IS14INV3M2 | 2004.48 | 0.5982%
IS14INV4M1 | 2192.4 | 0.6543%
IS14INV4M2 | 2004.48 | 0.5982%
IS15INV1M1 | 2004.48 | 0.5982%
IS15INV1M2 | 2192.4 | 0.6543%
IS15INV2M1 | 2004.48 | 0.5982%
IS15INV2M2 | 1941.84 | 0.5795%
IS15INV3M1 | 2223.72 | 0.6636%
IS15INV3M2 | 2192.4 | 0.6543%
IS15INV4M1 | 2192.4 | 0.6543%
IS15INV4M2 | 2004.48 | 0.5982%
IS16INV1M1 | 2192.4 | 0.6543%
IS16INV1M2 | 2004.48 | 0.5982%
IS16INV2M1 | 2161.08 | 0.6449%
IS16INV2M2 | 2004.48 | 0.5982%
IS16INV3M1 | 2129.76 | 0.6356%
IS16INV3M2 | 1879.2 | 0.5608%
IS16INV4M1 | 2129.76 | 0.6356%
IS16INV4M2 | 1973.16 | 0.5888%
IS17INV1M1 | 1973.16 | 0.5888%
IS17INV1M2 | 2004.48 | 0.5982%
IS17INV2M1 | 2004.48 | 0.5982%
IS17INV2M2 | 1753.92 | 0.5234%
IS17INV3M1 | 1957.5 | 0.5842%
IS17INV3M2 | 1753.92 | 0.5234%
IS17INV4M1 | 2004.48 | 0.5982%
IS17INV4M2 | 2004.48 | 0.5982%
IS18INV1M1 | 2255.04 | 0.673%
IS18INV1M2 | 1973.16 | 0.5888%
IS18INV2M1 | 2255.04 | 0.673%
IS18INV2M2 | 1973.16 | 0.5888%
IS18INV3M1 | 2223.72 | 0.6636%
IS18INV3M2 | 1973.16 | 0.5888%
IS18INV4M1 | 2004.48 | 0.5982%
IS18INV4M2 | 2004.48 | 0.5982%
IS19INV1M1 | 2161.08 | 0.6449%
IS19INV1M2 | 2255.04 | 0.673%
IS19INV2M1 | 2223.72 | 0.6636%
IS19INV2M2 | 2223.72 | 0.6636%
IS19INV3M1 | 2223.72 | 0.6636%
IS19INV3M2 | 2255.04 | 0.673%
IS19INV4M1 | 2004.48 | 0.5982%
IS19INV4M2 | 2223.72 | 0.6636%
IS20INV1M1 | 2255.04 | 0.673%
IS20INV1M2 | 2255.04 | 0.673%
IS20INV2M1 | 2255.04 | 0.673%
IS20INV2M2 | 2255.04 | 0.673%
IS20INV3M1 | 2255.04 | 0.673%
IS20INV3M2 | 2004.48 | 0.5982%
IS20INV4M1 | 2255.04 | 0.673%
IS20INV4M2 | 2004.48 | 0.5982%
IS1INV1M1SCB1 | 232.29 | 0.06932%
IS1INV1M1SCB2 | 232.29 | 0.06932%
IS1INV1M1SCB3 | 232.29 | 0.06932%
IS1INV1M1SCB4 | 232.29 | 0.06932%
IS1INV1M1SCB5 | 206.48 | 0.06162%
IS1INV1M1SCB6 | 232.29 | 0.06932%
IS1INV1M1SCB7 | 232.29 | 0.06932%
IS1INV1M1SCB8 | 232.29 | 0.06932%
IS1INV1M1SCB9 | 232.29 | 0.06932%
IS1INV1M1SCB10 | 0 | 0%
IS1INV1M2SCB1 | 232.29 | 0.06932%
IS1INV1M2SCB2 | 232.29 | 0.06932%
IS1INV1M2SCB3 | 232.29 | 0.06932%
IS1INV1M2SCB4 | 232.29 | 0.06932%
IS1INV1M2SCB5 | 232.29 | 0.06932%
IS1INV1M2SCB6 | 232.29 | 0.06932%
IS1INV1M2SCB7 | 232.29 | 0.06932%
IS1INV1M2SCB8 | 232.29 | 0.06932%
IS1INV1M2SCB9 | 232.29 | 0.06932%
IS1INV1M2SCB10 | 0 | 0%
IS1INV2M1SCB1 | 232.29 | 0.06932%
IS1INV2M1SCB2 | 232.29 | 0.06932%
IS1INV2M1SCB3 | 232.29 | 0.06932%
IS1INV2M1SCB4 | 232.29 | 0.06932%
IS1INV2M1SCB5 | 232.29 | 0.06932%
IS1INV2M1SCB6 | 232.29 | 0.06932%
IS1INV2M1SCB7 | 232.29 | 0.06932%
IS1INV2M1SCB8 | 232.29 | 0.06932%
IS1INV2M1SCB9 | 232.29 | 0.06932%
IS1INV2M1SCB10 | 0 | 0%
IS1INV2M2SCB1 | 232.29 | 0.06932%
IS1INV2M2SCB2 | 232.29 | 0.06932%
IS1INV2M2SCB3 | 232.29 | 0.06932%
IS1INV2M2SCB4 | 232.29 | 0.06932%
IS1INV2M2SCB5 | 232.29 | 0.06932%
IS1INV2M2SCB6 | 219.385 | 0.06547%
IS1INV2M2SCB7 | 232.29 | 0.06932%
IS1INV2M2SCB8 | 232.29 | 0.06932%
IS1INV2M2SCB9 | 232.29 | 0.06932%
IS1INV2M2SCB10 | 0 | 0%
IS1INV3M1SCB1 | 232.29 | 0.06932%
IS1INV3M1SCB2 | 232.29 | 0.06932%
IS1INV3M1SCB3 | 232.29 | 0.06932%
IS1INV3M1SCB4 | 232.29 | 0.06932%
IS1INV3M1SCB5 | 232.29 | 0.06932%
IS1INV3M1SCB6 | 232.29 | 0.06932%
IS1INV3M1SCB7 | 232.29 | 0.06932%
IS1INV3M1SCB8 | 232.29 | 0.06932%
IS1INV3M1SCB9 | 232.29 | 0.06932%
IS1INV3M1SCB10 | 0 | 0%
IS1INV3M2SCB1 | 232.29 | 0.06932%
IS1INV3M2SCB2 | 232.29 | 0.06932%
IS1INV3M2SCB3 | 232.29 | 0.06932%
IS1INV3M2SCB4 | 232.29 | 0.06932%
IS1INV3M2SCB5 | 232.29 | 0.06932%
IS1INV3M2SCB6 | 232.29 | 0.06932%
IS1INV3M2SCB7 | 232.29 | 0.06932%
IS1INV3M2SCB8 | 232.29 | 0.06932%
IS1INV3M2SCB9 | 232.29 | 0.06932%
IS1INV3M2SCB10 | 0 | 0%
IS1INV4M1SCB1 | 232.29 | 0.06932%
IS1INV4M1SCB2 | 232.29 | 0.06932%
IS1INV4M1SCB3 | 232.29 | 0.06932%
IS1INV4M1SCB4 | 232.29 | 0.06932%
IS1INV4M1SCB5 | 232.29 | 0.06932%
IS1INV4M1SCB6 | 232.29 | 0.06932%
IS1INV4M1SCB7 | 232.29 | 0.06932%
IS1INV4M1SCB8 | 232.29 | 0.06932%
IS1INV4M1SCB9 | 232.29 | 0.06932%
IS1INV4M1SCB10 | 0 | 0%
IS1INV4M2SCB1 | 232.29 | 0.06932%
IS1INV4M2SCB2 | 232.29 | 0.06932%
IS1INV4M2SCB3 | 232.29 | 0.06932%
IS1INV4M2SCB4 | 232.29 | 0.06932%
IS1INV4M2SCB5 | 206.48 | 0.06162%
IS1INV4M2SCB6 | 206.48 | 0.06162%
IS1INV4M2SCB7 | 206.48 | 0.06162%
IS1INV4M2SCB8 | 232.29 | 0.06932%
IS1INV4M2SCB9 | 206.48 | 0.06162%
IS1INV4M2SCB10 | 206.48 | 0.06162%
IS2INV1M1SCB1 | 232.29 | 0.06932%
IS2INV1M1SCB2 | 232.29 | 0.06932%
IS2INV1M1SCB3 | 232.29 | 0.06932%
IS2INV1M1SCB4 | 232.29 | 0.06932%
IS2INV1M1SCB5 | 232.29 | 0.06932%
IS2INV1M1SCB6 | 232.29 | 0.06932%
IS2INV1M1SCB7 | 232.29 | 0.06932%
IS2INV1M1SCB8 | 232.29 | 0.06932%
IS2INV1M1SCB9 | 232.29 | 0.06932%
IS2INV1M1SCB10 | 0 | 0%
IS2INV1M2SCB1 | 232.29 | 0.06932%
IS2INV1M2SCB2 | 232.29 | 0.06932%
IS2INV1M2SCB3 | 232.29 | 0.06932%
IS2INV1M2SCB4 | 232.29 | 0.06932%
IS2INV1M2SCB5 | 232.29 | 0.06932%
IS2INV1M2SCB6 | 232.29 | 0.06932%
IS2INV1M2SCB7 | 232.29 | 0.06932%
IS2INV1M2SCB8 | 232.29 | 0.06932%
IS2INV1M2SCB9 | 232.29 | 0.06932%
IS2INV1M2SCB10 | 0 | 0%
IS2INV2M1SCB1 | 232.29 | 0.06932%
IS2INV2M1SCB2 | 232.29 | 0.06932%
IS2INV2M1SCB3 | 232.29 | 0.06932%
IS2INV2M1SCB4 | 232.29 | 0.06932%
IS2INV2M1SCB5 | 232.29 | 0.06932%
IS2INV2M1SCB6 | 232.29 | 0.06932%
IS2INV2M1SCB7 | 232.29 | 0.06932%
IS2INV2M1SCB8 | 232.29 | 0.06932%
IS2INV2M1SCB9 | 232.29 | 0.06932%
IS2INV2M1SCB10 | 0 | 0%
IS2INV2M2SCB1 | 232.29 | 0.06932%
IS2INV2M2SCB2 | 232.29 | 0.06932%
IS2INV2M2SCB3 | 232.29 | 0.06932%
IS2INV2M2SCB4 | 232.29 | 0.06932%
IS2INV2M2SCB5 | 232.29 | 0.06932%
IS2INV2M2SCB6 | 232.29 | 0.06932%
IS2INV2M2SCB7 | 232.29 | 0.06932%
IS2INV2M2SCB8 | 232.29 | 0.06932%
IS2INV2M2SCB9 | 232.29 | 0.06932%
IS2INV2M2SCB10 | 0 | 0%
IS2INV3M1SCB1 | 232.29 | 0.06932%
IS2INV3M1SCB2 | 232.29 | 0.06932%
IS2INV3M1SCB3 | 232.29 | 0.06932%
IS2INV3M1SCB4 | 232.29 | 0.06932%
IS2INV3M1SCB5 | 206.48 | 0.06162%
IS2INV3M1SCB6 | 232.29 | 0.06932%
IS2INV3M1SCB7 | 232.29 | 0.06932%
IS2INV3M1SCB8 | 232.29 | 0.06932%
IS2INV3M1SCB9 | 232.29 | 0.06932%
IS2INV3M1SCB10 | 0 | 0%
IS2INV3M2SCB1 | 232.29 | 0.06932%
IS2INV3M2SCB2 | 232.29 | 0.06932%
IS2INV3M2SCB3 | 232.29 | 0.06932%
IS2INV3M2SCB4 | 232.29 | 0.06932%
IS2INV3M2SCB5 | 232.29 | 0.06932%
IS2INV3M2SCB6 | 232.29 | 0.06932%
IS2INV3M2SCB7 | 232.29 | 0.06932%
IS2INV3M2SCB8 | 232.29 | 0.06932%
IS2INV3M2SCB9 | 232.29 | 0.06932%
IS2INV3M2SCB10 | 0 | 0%
IS2INV4M1SCB1 | 232.29 | 0.06932%
IS2INV4M1SCB2 | 232.29 | 0.06932%
IS2INV4M1SCB3 | 232.29 | 0.06932%
IS2INV4M1SCB4 | 232.29 | 0.06932%
IS2INV4M1SCB5 | 232.29 | 0.06932%
IS2INV4M1SCB6 | 232.29 | 0.06932%
IS2INV4M1SCB7 | 232.29 | 0.06932%
IS2INV4M1SCB8 | 232.29 | 0.06932%
IS2INV4M1SCB9 | 232.29 | 0.06932%
IS2INV4M1SCB10 | 0 | 0%
IS2INV4M2SCB1 | 232.29 | 0.06932%
IS2INV4M2SCB2 | 232.29 | 0.06932%
IS2INV4M2SCB3 | 232.29 | 0.06932%
IS2INV4M2SCB4 | 232.29 | 0.06932%
IS2INV4M2SCB5 | 232.29 | 0.06932%
IS2INV4M2SCB6 | 232.29 | 0.06932%
IS2INV4M2SCB7 | 232.29 | 0.06932%
IS2INV4M2SCB8 | 232.29 | 0.06932%
IS2INV4M2SCB9 | 232.29 | 0.06932%
IS2INV4M2SCB10 | 0 | 0%
IS3INV1M1SCB1 | 232.29 | 0.06932%
IS3INV1M1SCB2 | 232.29 | 0.06932%
IS3INV1M1SCB3 | 232.29 | 0.06932%
IS3INV1M1SCB4 | 232.29 | 0.06932%
IS3INV1M1SCB5 | 232.29 | 0.06932%
IS3INV1M1SCB6 | 232.29 | 0.06932%
IS3INV1M1SCB7 | 232.29 | 0.06932%
IS3INV1M1SCB8 | 232.29 | 0.06932%
IS3INV1M1SCB9 | 232.29 | 0.06932%
IS3INV1M1SCB10 | 0 | 0%
IS3INV1M2SCB1 | 232.29 | 0.06932%
IS3INV1M2SCB2 | 232.29 | 0.06932%
IS3INV1M2SCB3 | 232.29 | 0.06932%
IS3INV1M2SCB4 | 232.29 | 0.06932%
IS3INV1M2SCB5 | 232.29 | 0.06932%
IS3INV1M2SCB6 | 232.29 | 0.06932%
IS3INV1M2SCB7 | 232.29 | 0.06932%
IS3INV1M2SCB8 | 232.29 | 0.06932%
IS3INV1M2SCB9 | 232.29 | 0.06932%
IS3INV1M2SCB10 | 0 | 0%
IS3INV2M1SCB1 | 232.29 | 0.06932%
IS3INV2M1SCB2 | 232.29 | 0.06932%
IS3INV2M1SCB3 | 232.29 | 0.06932%
IS3INV2M1SCB4 | 232.29 | 0.06932%
IS3INV2M1SCB5 | 232.29 | 0.06932%
IS3INV2M1SCB6 | 232.29 | 0.06932%
IS3INV2M1SCB7 | 232.29 | 0.06932%
IS3INV2M1SCB8 | 232.29 | 0.06932%
IS3INV2M1SCB9 | 232.29 | 0.06932%
IS3INV2M1SCB10 | 0 | 0%
IS3INV2M2SCB1 | 232.29 | 0.06932%
IS3INV2M2SCB2 | 232.29 | 0.06932%
IS3INV2M2SCB3 | 232.29 | 0.06932%
IS3INV2M2SCB4 | 232.29 | 0.06932%
IS3INV2M2SCB5 | 232.29 | 0.06932%
IS3INV2M2SCB6 | 232.29 | 0.06932%
IS3INV2M2SCB7 | 232.29 | 0.06932%
IS3INV2M2SCB8 | 232.29 | 0.06932%
IS3INV2M2SCB9 | 232.29 | 0.06932%
IS3INV2M2SCB10 | 0 | 0%
IS3INV3M1SCB1 | 234.9 | 0.0701%
IS3INV3M1SCB2 | 234.9 | 0.0701%
IS3INV3M1SCB3 | 234.9 | 0.0701%
IS3INV3M1SCB4 | 234.9 | 0.0701%
IS3INV3M1SCB5 | 234.9 | 0.0701%
IS3INV3M1SCB6 | 234.9 | 0.0701%
IS3INV3M1SCB7 | 234.9 | 0.0701%
IS3INV3M1SCB8 | 234.9 | 0.0701%
IS3INV3M1SCB9 | 234.9 | 0.0701%
IS3INV3M1SCB10 | 0 | 0%
IS3INV3M2SCB1 | 234.9 | 0.0701%
IS3INV3M2SCB2 | 234.9 | 0.0701%
IS3INV3M2SCB3 | 234.9 | 0.0701%
IS3INV3M2SCB4 | 234.9 | 0.0701%
IS3INV3M2SCB5 | 234.9 | 0.0701%
IS3INV3M2SCB6 | 234.9 | 0.0701%
IS3INV3M2SCB7 | 234.9 | 0.0701%
IS3INV3M2SCB8 | 234.9 | 0.0701%
IS3INV3M2SCB9 | 208.8 | 0.06231%
IS3INV3M2SCB10 | 0 | 0%
IS3INV4M1SCB1 | 234.9 | 0.0701%
IS3INV4M1SCB2 | 234.9 | 0.0701%
IS3INV4M1SCB3 | 234.9 | 0.0701%
IS3INV4M1SCB4 | 234.9 | 0.0701%
IS3INV4M1SCB5 | 234.9 | 0.0701%
IS3INV4M1SCB6 | 234.9 | 0.0701%
IS3INV4M1SCB7 | 234.9 | 0.0701%
IS3INV4M1SCB8 | 234.9 | 0.0701%
IS3INV4M1SCB9 | 234.9 | 0.0701%
IS3INV4M1SCB10 | 0 | 0%
IS3INV4M2SCB1 | 234.9 | 0.0701%
IS3INV4M2SCB2 | 234.9 | 0.0701%
IS3INV4M2SCB3 | 234.9 | 0.0701%
IS3INV4M2SCB4 | 234.9 | 0.0701%
IS3INV4M2SCB5 | 234.9 | 0.0701%
IS3INV4M2SCB6 | 234.9 | 0.0701%
IS3INV4M2SCB7 | 234.9 | 0.0701%
IS3INV4M2SCB8 | 234.9 | 0.0701%
IS3INV4M2SCB9 | 208.8 | 0.06231%
IS3INV4M2SCB10 | 0 | 0%
IS4INV1M1SCB1 | 234.9 | 0.0701%
IS4INV1M1SCB2 | 234.9 | 0.0701%
IS4INV1M1SCB3 | 234.9 | 0.0701%
IS4INV1M1SCB4 | 208.8 | 0.06231%
IS4INV1M1SCB5 | 234.9 | 0.0701%
IS4INV1M1SCB6 | 234.9 | 0.0701%
IS4INV1M1SCB7 | 234.9 | 0.0701%
IS4INV1M1SCB8 | 234.9 | 0.0701%
IS4INV1M1SCB9 | 234.9 | 0.0701%
IS4INV1M1SCB10 | 0 | 0%
IS4INV1M2SCB1 | 234.9 | 0.0701%
IS4INV1M2SCB2 | 234.9 | 0.0701%
IS4INV1M2SCB3 | 234.9 | 0.0701%
IS4INV1M2SCB4 | 0 | 0%
IS4INV1M2SCB5 | 234.9 | 0.0701%
IS4INV1M2SCB6 | 234.9 | 0.0701%
IS4INV1M2SCB7 | 234.9 | 0.0701%
IS4INV1M2SCB8 | 234.9 | 0.0701%
IS4INV1M2SCB9 | 234.9 | 0.0701%
IS4INV1M2SCB10 | 0 | 0%
IS4INV2M1SCB1 | 234.9 | 0.0701%
IS4INV2M1SCB2 | 234.9 | 0.0701%
IS4INV2M1SCB3 | 234.9 | 0.0701%
IS4INV2M1SCB4 | 234.9 | 0.0701%
IS4INV2M1SCB5 | 234.9 | 0.0701%
IS4INV2M1SCB6 | 234.9 | 0.0701%
IS4INV2M1SCB7 | 234.9 | 0.0701%
IS4INV2M1SCB8 | 234.9 | 0.0701%
IS4INV2M1SCB9 | 234.9 | 0.0701%
IS4INV2M1SCB10 | 0 | 0%
IS4INV2M2SCB1 | 234.9 | 0.0701%
IS4INV2M2SCB2 | 234.9 | 0.0701%
IS4INV2M2SCB3 | 234.9 | 0.0701%
IS4INV2M2SCB4 | 234.9 | 0.0701%
IS4INV2M2SCB5 | 234.9 | 0.0701%
IS4INV2M2SCB6 | 234.9 | 0.0701%
IS4INV2M2SCB7 | 234.9 | 0.0701%
IS4INV2M2SCB8 | 234.9 | 0.0701%
IS4INV2M2SCB9 | 208.8 | 0.06231%
IS4INV2M2SCB10 | 0 | 0%
IS4INV3M1SCB1 | 234.9 | 0.0701%
IS4INV3M1SCB2 | 234.9 | 0.0701%
IS4INV3M1SCB3 | 234.9 | 0.0701%
IS4INV3M1SCB4 | 234.9 | 0.0701%
IS4INV3M1SCB5 | 234.9 | 0.0701%
IS4INV3M1SCB6 | 234.9 | 0.0701%
IS4INV3M1SCB7 | 234.9 | 0.0701%
IS4INV3M1SCB8 | 234.9 | 0.0701%
IS4INV3M1SCB9 | 234.9 | 0.0701%
IS4INV3M1SCB10 | 0 | 0%
IS4INV3M2SCB1 | 234.9 | 0.0701%
IS4INV3M2SCB2 | 234.9 | 0.0701%
IS4INV3M2SCB3 | 234.9 | 0.0701%
IS4INV3M2SCB4 | 208.8 | 0.06231%
IS4INV3M2SCB5 | 234.9 | 0.0701%
IS4INV3M2SCB6 | 234.9 | 0.0701%
IS4INV3M2SCB7 | 234.9 | 0.0701%
IS4INV3M2SCB8 | 234.9 | 0.0701%
IS4INV3M2SCB9 | 234.9 | 0.0701%
IS4INV3M2SCB10 | 0 | 0%
IS4INV4M1SCB1 | 234.9 | 0.0701%
IS4INV4M1SCB2 | 234.9 | 0.0701%
IS4INV4M1SCB3 | 234.9 | 0.0701%
IS4INV4M1SCB4 | 234.9 | 0.0701%
IS4INV4M1SCB5 | 234.9 | 0.0701%
IS4INV4M1SCB6 | 234.9 | 0.0701%
IS4INV4M1SCB7 | 234.9 | 0.0701%
IS4INV4M1SCB8 | 234.9 | 0.0701%
IS4INV4M1SCB9 | 234.9 | 0.0701%
IS4INV4M1SCB10 | 0 | 0%
IS4INV4M2SCB1 | 234.9 | 0.0701%
IS4INV4M2SCB2 | 234.9 | 0.0701%
IS4INV4M2SCB3 | 234.9 | 0.0701%
IS4INV4M2SCB4 | 234.9 | 0.0701%
IS4INV4M2SCB5 | 208.8 | 0.06231%
IS4INV4M2SCB6 | 234.9 | 0.0701%
IS4INV4M2SCB7 | 234.9 | 0.0701%
IS4INV4M2SCB8 | 208.8 | 0.06231%
IS4INV4M2SCB9 | 234.9 | 0.0701%
IS4INV4M2SCB10 | 0 | 0%
IS5INV1M1SCB1 | 232.29 | 0.06932%
IS5INV1M1SCB2 | 232.29 | 0.06932%
IS5INV1M1SCB3 | 232.29 | 0.06932%
IS5INV1M1SCB4 | 232.29 | 0.06932%
IS5INV1M1SCB5 | 232.29 | 0.06932%
IS5INV1M1SCB6 | 232.29 | 0.06932%
IS5INV1M1SCB7 | 232.29 | 0.06932%
IS5INV1M1SCB8 | 232.29 | 0.06932%
IS5INV1M1SCB9 | 232.29 | 0.06932%
IS5INV1M1SCB10 | 0 | 0%
IS5INV1M2SCB1 | 232.29 | 0.06932%
IS5INV1M2SCB2 | 232.29 | 0.06932%
IS5INV1M2SCB3 | 232.29 | 0.06932%
IS5INV1M2SCB4 | 232.29 | 0.06932%
IS5INV1M2SCB5 | 232.29 | 0.06932%
IS5INV1M2SCB6 | 232.29 | 0.06932%
IS5INV1M2SCB7 | 232.29 | 0.06932%
IS5INV1M2SCB8 | 232.29 | 0.06932%
IS5INV1M2SCB9 | 232.29 | 0.06932%
IS5INV1M2SCB10 | 0 | 0%
IS5INV2M1SCB1 | 232.29 | 0.06932%
IS5INV2M1SCB2 | 232.29 | 0.06932%
IS5INV2M1SCB3 | 232.29 | 0.06932%
IS5INV2M1SCB4 | 232.29 | 0.06932%
IS5INV2M1SCB5 | 232.29 | 0.06932%
IS5INV2M1SCB6 | 232.29 | 0.06932%
IS5INV2M1SCB7 | 232.29 | 0.06932%
IS5INV2M1SCB8 | 232.29 | 0.06932%
IS5INV2M1SCB9 | 232.29 | 0.06932%
IS5INV2M1SCB10 | 0 | 0%
IS5INV2M2SCB1 | 232.29 | 0.06932%
IS5INV2M2SCB2 | 232.29 | 0.06932%
IS5INV2M2SCB3 | 232.29 | 0.06932%
IS5INV2M2SCB4 | 232.29 | 0.06932%
IS5INV2M2SCB5 | 232.29 | 0.06932%
IS5INV2M2SCB6 | 232.29 | 0.06932%
IS5INV2M2SCB7 | 232.29 | 0.06932%
IS5INV2M2SCB8 | 232.29 | 0.06932%
IS5INV2M2SCB9 | 232.29 | 0.06932%
IS5INV2M2SCB10 | 0 | 0%
IS5INV3M1SCB1 | 232.29 | 0.06932%
IS5INV3M1SCB2 | 232.29 | 0.06932%
IS5INV3M1SCB3 | 232.29 | 0.06932%
IS5INV3M1SCB4 | 232.29 | 0.06932%
IS5INV3M1SCB5 | 232.29 | 0.06932%
IS5INV3M1SCB6 | 232.29 | 0.06932%
IS5INV3M1SCB7 | 232.29 | 0.06932%
IS5INV3M1SCB8 | 232.29 | 0.06932%
IS5INV3M1SCB9 | 232.29 | 0.06932%
IS5INV3M1SCB10 | 0 | 0%
IS5INV3M2SCB1 | 232.29 | 0.06932%
IS5INV3M2SCB2 | 232.29 | 0.06932%
IS5INV3M2SCB3 | 232.29 | 0.06932%
IS5INV3M2SCB4 | 232.29 | 0.06932%
IS5INV3M2SCB5 | 232.29 | 0.06932%
IS5INV3M2SCB6 | 232.29 | 0.06932%
IS5INV3M2SCB7 | 232.29 | 0.06932%
IS5INV3M2SCB8 | 232.29 | 0.06932%
IS5INV3M2SCB9 | 232.29 | 0.06932%
IS5INV3M2SCB10 | 0 | 0%
IS5INV4M1SCB1 | 232.29 | 0.06932%
IS5INV4M1SCB2 | 232.29 | 0.06932%
IS5INV4M1SCB3 | 232.29 | 0.06932%
IS5INV4M1SCB4 | 232.29 | 0.06932%
IS5INV4M1SCB5 | 232.29 | 0.06932%
IS5INV4M1SCB6 | 232.29 | 0.06932%
IS5INV4M1SCB7 | 232.29 | 0.06932%
IS5INV4M1SCB8 | 232.29 | 0.06932%
IS5INV4M1SCB9 | 232.29 | 0.06932%
IS5INV4M1SCB10 | 0 | 0%
IS5INV4M2SCB1 | 232.29 | 0.06932%
IS5INV4M2SCB2 | 232.29 | 0.06932%
IS5INV4M2SCB3 | 232.29 | 0.06932%
IS5INV4M2SCB4 | 232.29 | 0.06932%
IS5INV4M2SCB5 | 232.29 | 0.06932%
IS5INV4M2SCB6 | 232.29 | 0.06932%
IS5INV4M2SCB7 | 232.29 | 0.06932%
IS5INV4M2SCB8 | 232.29 | 0.06932%
IS5INV4M2SCB9 | 232.29 | 0.06932%
IS5INV4M2SCB10 | 0 | 0%
IS6INV1M1SCB1 | 248.24 | 0.07408%
IS6INV1M1SCB2 | 248.24 | 0.07408%
IS6INV1M1SCB3 | 248.24 | 0.07408%
IS6INV1M1SCB4 | 248.24 | 0.07408%
IS6INV1M1SCB5 | 248.24 | 0.07408%
IS6INV1M1SCB6 | 248.24 | 0.07408%
IS6INV1M1SCB7 | 248.24 | 0.07408%
IS6INV1M1SCB8 | 248.24 | 0.07408%
IS6INV1M1SCB9 | 248.24 | 0.07408%
IS6INV1M1SCB10 | 0 | 0%
IS6INV1M2SCB1 | 248.24 | 0.07408%
IS6INV1M2SCB2 | 248.24 | 0.07408%
IS6INV1M2SCB3 | 248.24 | 0.07408%
IS6INV1M2SCB4 | 248.24 | 0.07408%
IS6INV1M2SCB5 | 248.24 | 0.07408%
IS6INV1M2SCB6 | 248.24 | 0.07408%
IS6INV1M2SCB7 | 248.24 | 0.07408%
IS6INV1M2SCB8 | 248.24 | 0.07408%
IS6INV1M2SCB9 | 0 | 0%
IS6INV1M2SCB10 | 0 | 0%
IS6INV2M1SCB1 | 217.21 | 0.06482%
IS6INV2M1SCB2 | 248.24 | 0.07408%
IS6INV2M1SCB3 | 248.24 | 0.07408%
IS6INV2M1SCB4 | 248.24 | 0.07408%
IS6INV2M1SCB5 | 248.24 | 0.07408%
IS6INV2M1SCB6 | 248.24 | 0.07408%
IS6INV2M1SCB7 | 248.24 | 0.07408%
IS6INV2M1SCB8 | 248.24 | 0.07408%
IS6INV2M1SCB9 | 248.24 | 0.07408%
IS6INV2M1SCB10 | 0 | 0%
IS6INV2M2SCB1 | 248.24 | 0.07408%
IS6INV2M2SCB2 | 248.24 | 0.07408%
IS6INV2M2SCB3 | 248.24 | 0.07408%
IS6INV2M2SCB4 | 248.24 | 0.07408%
IS6INV2M2SCB5 | 248.24 | 0.07408%
IS6INV2M2SCB6 | 248.24 | 0.07408%
IS6INV2M2SCB7 | 248.24 | 0.07408%
IS6INV2M2SCB8 | 248.24 | 0.07408%
IS6INV2M2SCB9 | 0 | 0%
IS6INV2M2SCB10 | 0 | 0%
IS6INV3M1SCB1 | 250.56 | 0.07477%
IS6INV3M1SCB2 | 250.56 | 0.07477%
IS6INV3M1SCB3 | 250.56 | 0.07477%
IS6INV3M1SCB4 | 219.24 | 0.06543%
IS6INV3M1SCB5 | 219.24 | 0.06543%
IS6INV3M1SCB6 | 250.56 | 0.07477%
IS6INV3M1SCB7 | 250.56 | 0.07477%
IS6INV3M1SCB8 | 250.56 | 0.07477%
IS6INV3M1SCB9 | 250.56 | 0.07477%
IS6INV3M1SCB10 | 0 | 0%
IS6INV3M2SCB1 | 250.56 | 0.07477%
IS6INV3M2SCB2 | 250.56 | 0.07477%
IS6INV3M2SCB3 | 219.24 | 0.06543%
IS6INV3M2SCB4 | 219.24 | 0.06543%
IS6INV3M2SCB5 | 219.24 | 0.06543%
IS6INV3M2SCB6 | 219.24 | 0.06543%
IS6INV3M2SCB7 | 250.56 | 0.07477%
IS6INV3M2SCB8 | 250.56 | 0.07477%
IS6INV3M2SCB9 | 250.56 | 0.07477%
IS6INV3M2SCB10 | 250.56 | 0.07477%
IS6INV4M1SCB1 | 248.24 | 0.07408%
IS6INV4M1SCB2 | 248.24 | 0.07408%
IS6INV4M1SCB3 | 248.24 | 0.07408%
IS6INV4M1SCB4 | 248.24 | 0.07408%
IS6INV4M1SCB5 | 248.24 | 0.07408%
IS6INV4M1SCB6 | 248.24 | 0.07408%
IS6INV4M1SCB7 | 248.24 | 0.07408%
IS6INV4M1SCB8 | 248.24 | 0.07408%
IS6INV4M1SCB9 | 217.21 | 0.06482%
IS6INV4M1SCB10 | 0 | 0%
IS6INV4M2SCB1 | 248.24 | 0.07408%
IS6INV4M2SCB2 | 248.24 | 0.07408%
IS6INV4M2SCB3 | 248.24 | 0.07408%
IS6INV4M2SCB4 | 248.24 | 0.07408%
IS6INV4M2SCB5 | 248.24 | 0.07408%
IS6INV4M2SCB6 | 248.24 | 0.07408%
IS6INV4M2SCB7 | 248.24 | 0.07408%
IS6INV4M2SCB8 | 248.24 | 0.07408%
IS6INV4M2SCB9 | 0 | 0%
IS6INV4M2SCB10 | 0 | 0%
IS7INV1M1SCB1 | 250.56 | 0.07477%
IS7INV1M1SCB2 | 250.56 | 0.07477%
IS7INV1M1SCB3 | 250.56 | 0.07477%
IS7INV1M1SCB4 | 250.56 | 0.07477%
IS7INV1M1SCB5 | 250.56 | 0.07477%
IS7INV1M1SCB6 | 250.56 | 0.07477%
IS7INV1M1SCB7 | 250.56 | 0.07477%
IS7INV1M1SCB8 | 219.24 | 0.06543%
IS7INV1M1SCB9 | 0 | 0%
IS7INV1M1SCB10 | 0 | 0%
IS7INV1M2SCB1 | 250.56 | 0.07477%
IS7INV1M2SCB2 | 250.56 | 0.07477%
IS7INV1M2SCB3 | 250.56 | 0.07477%
IS7INV1M2SCB4 | 250.56 | 0.07477%
IS7INV1M2SCB5 | 250.56 | 0.07477%
IS7INV1M2SCB6 | 250.56 | 0.07477%
IS7INV1M2SCB7 | 219.24 | 0.06543%
IS7INV1M2SCB8 | 250.56 | 0.07477%
IS7INV1M2SCB9 | 0 | 0%
IS7INV1M2SCB10 | 0 | 0%
IS7INV2M1SCB1 | 125.28 | 0.03739%
IS7INV2M1SCB2 | 250.56 | 0.07477%
IS7INV2M1SCB3 | 250.56 | 0.07477%
IS7INV2M1SCB4 | 250.56 | 0.07477%
IS7INV2M1SCB5 | 250.56 | 0.07477%
IS7INV2M1SCB6 | 250.56 | 0.07477%
IS7INV2M1SCB7 | 250.56 | 0.07477%
IS7INV2M1SCB8 | 250.56 | 0.07477%
IS7INV2M1SCB9 | 219.24 | 0.06543%
IS7INV2M1SCB10 | 0 | 0%
IS7INV2M2SCB1 | 250.56 | 0.07477%
IS7INV2M2SCB2 | 250.56 | 0.07477%
IS7INV2M2SCB3 | 250.56 | 0.07477%
IS7INV2M2SCB4 | 250.56 | 0.07477%
IS7INV2M2SCB5 | 250.56 | 0.07477%
IS7INV2M2SCB6 | 250.56 | 0.07477%
IS7INV2M2SCB7 | 250.56 | 0.07477%
IS7INV2M2SCB8 | 250.56 | 0.07477%
IS7INV2M2SCB9 | 0 | 0%
IS7INV2M2SCB10 | 0 | 0%
IS7INV3M1SCB1 | 250.56 | 0.07477%
IS7INV3M1SCB2 | 250.56 | 0.07477%
IS7INV3M1SCB3 | 250.56 | 0.07477%
IS7INV3M1SCB4 | 250.56 | 0.07477%
IS7INV3M1SCB5 | 250.56 | 0.07477%
IS7INV3M1SCB6 | 250.56 | 0.07477%
IS7INV3M1SCB7 | 250.56 | 0.07477%
IS7INV3M1SCB8 | 250.56 | 0.07477%
IS7INV3M1SCB9 | 219.24 | 0.06543%
IS7INV3M1SCB10 | 0 | 0%
IS7INV3M2SCB1 | 219.24 | 0.06543%
IS7INV3M2SCB2 | 250.56 | 0.07477%
IS7INV3M2SCB3 | 250.56 | 0.07477%
IS7INV3M2SCB4 | 250.56 | 0.07477%
IS7INV3M2SCB5 | 250.56 | 0.07477%
IS7INV3M2SCB6 | 250.56 | 0.07477%
IS7INV3M2SCB7 | 250.56 | 0.07477%
IS7INV3M2SCB8 | 250.56 | 0.07477%
IS7INV3M2SCB9 | 0 | 0%
IS7INV3M2SCB10 | 0 | 0%
IS7INV4M1SCB1 | 250.56 | 0.07477%
IS7INV4M1SCB2 | 250.56 | 0.07477%
IS7INV4M1SCB3 | 250.56 | 0.07477%
IS7INV4M1SCB4 | 250.56 | 0.07477%
IS7INV4M1SCB5 | 219.24 | 0.06543%
IS7INV4M1SCB6 | 250.56 | 0.07477%
IS7INV4M1SCB7 | 250.56 | 0.07477%
IS7INV4M1SCB8 | 250.56 | 0.07477%
IS7INV4M1SCB9 | 250.56 | 0.07477%
IS7INV4M1SCB10 | 0 | 0%
IS7INV4M2SCB1 | 250.56 | 0.07477%
IS7INV4M2SCB2 | 219.24 | 0.06543%
IS7INV4M2SCB3 | 250.56 | 0.07477%
IS7INV4M2SCB4 | 250.56 | 0.07477%
IS7INV4M2SCB5 | 250.56 | 0.07477%
IS7INV4M2SCB6 | 250.56 | 0.07477%
IS7INV4M2SCB7 | 250.56 | 0.07477%
IS7INV4M2SCB8 | 250.56 | 0.07477%
IS7INV4M2SCB9 | 0 | 0%
IS7INV4M2SCB10 | 0 | 0%
IS8INV1M1SCB1 | 250.56 | 0.07477%
IS8INV1M1SCB2 | 250.56 | 0.07477%
IS8INV1M1SCB3 | 250.56 | 0.07477%
IS8INV1M1SCB4 | 250.56 | 0.07477%
IS8INV1M1SCB5 | 250.56 | 0.07477%
IS8INV1M1SCB6 | 250.56 | 0.07477%
IS8INV1M1SCB7 | 250.56 | 0.07477%
IS8INV1M1SCB8 | 250.56 | 0.07477%
IS8INV1M1SCB9 | 0 | 0%
IS8INV1M1SCB10 | 0 | 0%
IS8INV1M2SCB1 | 250.56 | 0.07477%
IS8INV1M2SCB2 | 250.56 | 0.07477%
IS8INV1M2SCB3 | 250.56 | 0.07477%
IS8INV1M2SCB4 | 250.56 | 0.07477%
IS8INV1M2SCB5 | 250.56 | 0.07477%
IS8INV1M2SCB6 | 250.56 | 0.07477%
IS8INV1M2SCB7 | 250.56 | 0.07477%
IS8INV1M2SCB8 | 250.56 | 0.07477%
IS8INV1M2SCB9 | 250.56 | 0.07477%
IS8INV1M2SCB10 | 0 | 0%
IS8INV2M1SCB1 | 250.56 | 0.07477%
IS8INV2M1SCB2 | 250.56 | 0.07477%
IS8INV2M1SCB3 | 250.56 | 0.07477%
IS8INV2M1SCB4 | 250.56 | 0.07477%
IS8INV2M1SCB5 | 250.56 | 0.07477%
IS8INV2M1SCB6 | 250.56 | 0.07477%
IS8INV2M1SCB7 | 250.56 | 0.07477%
IS8INV2M1SCB8 | 250.56 | 0.07477%
IS8INV2M1SCB9 | 250.56 | 0.07477%
IS8INV2M1SCB10 | 0 | 0%
IS8INV2M2SCB1 | 250.56 | 0.07477%
IS8INV2M2SCB2 | 250.56 | 0.07477%
IS8INV2M2SCB3 | 250.56 | 0.07477%
IS8INV2M2SCB4 | 250.56 | 0.07477%
IS8INV2M2SCB5 | 250.56 | 0.07477%
IS8INV2M2SCB6 | 250.56 | 0.07477%
IS8INV2M2SCB7 | 250.56 | 0.07477%
IS8INV2M2SCB8 | 250.56 | 0.07477%
IS8INV2M2SCB9 | 0 | 0%
IS8INV2M2SCB10 | 0 | 0%
IS8INV3M1SCB1 | 250.56 | 0.07477%
IS8INV3M1SCB2 | 250.56 | 0.07477%
IS8INV3M1SCB3 | 250.56 | 0.07477%
IS8INV3M1SCB4 | 250.56 | 0.07477%
IS8INV3M1SCB5 | 250.56 | 0.07477%
IS8INV3M1SCB6 | 250.56 | 0.07477%
IS8INV3M1SCB7 | 250.56 | 0.07477%
IS8INV3M1SCB8 | 250.56 | 0.07477%
IS8INV3M1SCB9 | 250.56 | 0.07477%
IS8INV3M1SCB10 | 0 | 0%
IS8INV3M2SCB1 | 250.56 | 0.07477%
IS8INV3M2SCB2 | 250.56 | 0.07477%
IS8INV3M2SCB3 | 250.56 | 0.07477%
IS8INV3M2SCB4 | 250.56 | 0.07477%
IS8INV3M2SCB5 | 250.56 | 0.07477%
IS8INV3M2SCB6 | 250.56 | 0.07477%
IS8INV3M2SCB7 | 250.56 | 0.07477%
IS8INV3M2SCB8 | 250.56 | 0.07477%
IS8INV3M2SCB9 | 0 | 0%
IS8INV3M2SCB10 | 0 | 0%
IS8INV4M1SCB1 | 234.9 | 0.0701%
IS8INV4M1SCB2 | 234.9 | 0.0701%
IS8INV4M1SCB3 | 234.9 | 0.0701%
IS8INV4M1SCB4 | 234.9 | 0.0701%
IS8INV4M1SCB5 | 130.5 | 0.03894%
IS8INV4M1SCB6 | 156.6 | 0.04673%
IS8INV4M1SCB7 | 182.7 | 0.05452%
IS8INV4M1SCB8 | 234.9 | 0.0701%
IS8INV4M1SCB9 | 208.8 | 0.06231%
IS8INV4M1SCB10 | 234.9 | 0.0701%
IS8INV4M2SCB1 | 234.9 | 0.0701%
IS8INV4M2SCB2 | 234.9 | 0.0701%
IS8INV4M2SCB3 | 234.9 | 0.0701%
IS8INV4M2SCB4 | 234.9 | 0.0701%
IS8INV4M2SCB5 | 234.9 | 0.0701%
IS8INV4M2SCB6 | 208.8 | 0.06231%
IS8INV4M2SCB7 | 234.9 | 0.0701%
IS8INV4M2SCB8 | 234.9 | 0.0701%
IS8INV4M2SCB9 | 208.8 | 0.06231%
IS8INV4M2SCB10 | 0 | 0%
IS9INV1M1SCB1 | 268.685 | 0.08018%
IS9INV1M1SCB2 | 268.685 | 0.08018%
IS9INV1M1SCB3 | 0 | 0%
IS9INV1M1SCB4 | 268.685 | 0.08018%
IS9INV1M1SCB5 | 268.685 | 0.08018%
IS9INV1M1SCB6 | 268.685 | 0.08018%
IS9INV1M1SCB7 | 252.88 | 0.07547%
IS9INV1M1SCB8 | 252.88 | 0.07547%
IS9INV1M1SCB9 | 252.88 | 0.07547%
IS9INV1M1SCB10 | 0 | 0%
IS9INV1M2SCB1 | 252.88 | 0.07547%
IS9INV1M2SCB2 | 252.88 | 0.07547%
IS9INV1M2SCB3 | 252.88 | 0.07547%
IS9INV1M2SCB4 | 252.88 | 0.07547%
IS9INV1M2SCB5 | 252.88 | 0.07547%
IS9INV1M2SCB6 | 252.88 | 0.07547%
IS9INV1M2SCB7 | 252.88 | 0.07547%
IS9INV1M2SCB8 | 252.88 | 0.07547%
IS9INV1M2SCB9 | 0 | 0%
IS9INV1M2SCB10 | 0 | 0%
IS9INV2M1SCB1 | 268.685 | 0.08018%
IS9INV2M1SCB2 | 268.685 | 0.08018%
IS9INV2M1SCB3 | 268.685 | 0.08018%
IS9INV2M1SCB4 | 268.685 | 0.08018%
IS9INV2M1SCB5 | 268.685 | 0.08018%
IS9INV2M1SCB6 | 252.88 | 0.07547%
IS9INV2M1SCB7 | 252.88 | 0.07547%
IS9INV2M1SCB8 | 252.88 | 0.07547%
IS9INV2M1SCB9 | 0 | 0%
IS9INV2M1SCB10 | 0 | 0%
IS9INV2M2SCB1 | 252.88 | 0.07547%
IS9INV2M2SCB2 | 252.88 | 0.07547%
IS9INV2M2SCB3 | 252.88 | 0.07547%
IS9INV2M2SCB4 | 252.88 | 0.07547%
IS9INV2M2SCB5 | 221.27 | 0.06603%
IS9INV2M2SCB6 | 221.27 | 0.06603%
IS9INV2M2SCB7 | 252.88 | 0.07547%
IS9INV2M2SCB8 | 252.88 | 0.07547%
IS9INV2M2SCB9 | 252.88 | 0.07547%
IS9INV2M2SCB10 | 0 | 0%
IS9INV3M1SCB1 | 268.685 | 0.08018%
IS9INV3M1SCB2 | 252.88 | 0.07547%
IS9INV3M1SCB3 | 268.685 | 0.08018%
IS9INV3M1SCB4 | 252.88 | 0.07547%
IS9INV3M1SCB5 | 252.88 | 0.07547%
IS9INV3M1SCB6 | 252.88 | 0.07547%
IS9INV3M1SCB7 | 221.27 | 0.06603%
IS9INV3M1SCB8 | 252.88 | 0.07547%
IS9INV3M1SCB9 | 252.88 | 0.07547%
IS9INV3M1SCB10 | 0 | 0%
IS9INV3M2SCB1 | 252.88 | 0.07547%
IS9INV3M2SCB2 | 252.88 | 0.07547%
IS9INV3M2SCB3 | 252.88 | 0.07547%
IS9INV3M2SCB4 | 252.88 | 0.07547%
IS9INV3M2SCB5 | 252.88 | 0.07547%
IS9INV3M2SCB6 | 252.88 | 0.07547%
IS9INV3M2SCB7 | 252.88 | 0.07547%
IS9INV3M2SCB8 | 252.88 | 0.07547%
IS9INV3M2SCB9 | 0 | 0%
IS9INV3M2SCB10 | 0 | 0%
IS9INV4M1SCB1 | 221.27 | 0.06603%
IS9INV4M1SCB2 | 252.88 | 0.07547%
IS9INV4M1SCB3 | 252.88 | 0.07547%
IS9INV4M1SCB4 | 252.88 | 0.07547%
IS9INV4M1SCB5 | 252.88 | 0.07547%
IS9INV4M1SCB6 | 252.88 | 0.07547%
IS9INV4M1SCB7 | 252.88 | 0.07547%
IS9INV4M1SCB8 | 252.88 | 0.07547%
IS9INV4M1SCB9 | 252.88 | 0.07547%
IS9INV4M1SCB10 | 0 | 0%
IS9INV4M2SCB1 | 252.88 | 0.07547%
IS9INV4M2SCB2 | 252.88 | 0.07547%
IS9INV4M2SCB3 | 252.88 | 0.07547%
IS9INV4M2SCB4 | 252.88 | 0.07547%
IS9INV4M2SCB5 | 252.88 | 0.07547%
IS9INV4M2SCB6 | 221.27 | 0.06603%
IS9INV4M2SCB7 | 252.88 | 0.07547%
IS9INV4M2SCB8 | 221.27 | 0.06603%
IS9INV4M2SCB9 | 0 | 0%
IS9INV4M2SCB10 | 0 | 0%
IS10INV1M1SCB1 | 250.56 | 0.07477%
IS10INV1M1SCB2 | 250.56 | 0.07477%
IS10INV1M1SCB3 | 219.24 | 0.06543%
IS10INV1M1SCB4 | 219.24 | 0.06543%
IS10INV1M1SCB5 | 281.88 | 0.08412%
IS10INV1M1SCB6 | 281.88 | 0.08412%
IS10INV1M1SCB7 | 281.88 | 0.08412%
IS10INV1M1SCB8 | 281.88 | 0.08412%
IS10INV1M1SCB9 | 0 | 0%
IS10INV1M1SCB10 | 0 | 0%
IS10INV1M2SCB1 | 93.96 | 0.02804%
IS10INV1M2SCB2 | 250.56 | 0.07477%
IS10INV1M2SCB3 | 250.56 | 0.07477%
IS10INV1M2SCB4 | 250.56 | 0.07477%
IS10INV1M2SCB5 | 250.56 | 0.07477%
IS10INV1M2SCB6 | 250.56 | 0.07477%
IS10INV1M2SCB7 | 250.56 | 0.07477%
IS10INV1M2SCB8 | 250.56 | 0.07477%
IS10INV1M2SCB9 | 250.56 | 0.07477%
IS10INV1M2SCB10 | 0 | 0%
IS10INV2M1SCB1 | 250.56 | 0.07477%
IS10INV2M1SCB2 | 250.56 | 0.07477%
IS10INV2M1SCB3 | 250.56 | 0.07477%
IS10INV2M1SCB4 | 250.56 | 0.07477%
IS10INV2M1SCB5 | 250.56 | 0.07477%
IS10INV2M1SCB6 | 250.56 | 0.07477%
IS10INV2M1SCB7 | 219.24 | 0.06543%
IS10INV2M1SCB8 | 250.56 | 0.07477%
IS10INV2M1SCB9 | 0 | 0%
IS10INV2M1SCB10 | 0 | 0%
IS10INV2M2SCB1 | 250.56 | 0.07477%
IS10INV2M2SCB2 | 250.56 | 0.07477%
IS10INV2M2SCB3 | 250.56 | 0.07477%
IS10INV2M2SCB4 | 219.24 | 0.06543%
IS10INV2M2SCB5 | 250.56 | 0.07477%
IS10INV2M2SCB6 | 250.56 | 0.07477%
IS10INV2M2SCB7 | 250.56 | 0.07477%
IS10INV2M2SCB8 | 250.56 | 0.07477%
IS10INV2M2SCB9 | 250.56 | 0.07477%
IS10INV2M2SCB10 | 0 | 0%
IS10INV3M1SCB1 | 250.56 | 0.07477%
IS10INV3M1SCB2 | 250.56 | 0.07477%
IS10INV3M1SCB3 | 250.56 | 0.07477%
IS10INV3M1SCB4 | 250.56 | 0.07477%
IS10INV3M1SCB5 | 219.24 | 0.06543%
IS10INV3M1SCB6 | 250.56 | 0.07477%
IS10INV3M1SCB7 | 219.24 | 0.06543%
IS10INV3M1SCB8 | 250.56 | 0.07477%
IS10INV3M1SCB9 | 0 | 0%
IS10INV3M1SCB10 | 0 | 0%
IS10INV3M2SCB1 | 250.56 | 0.07477%
IS10INV3M2SCB2 | 250.56 | 0.07477%
IS10INV3M2SCB3 | 250.56 | 0.07477%
IS10INV3M2SCB4 | 250.56 | 0.07477%
IS10INV3M2SCB5 | 250.56 | 0.07477%
IS10INV3M2SCB6 | 250.56 | 0.07477%
IS10INV3M2SCB7 | 250.56 | 0.07477%
IS10INV3M2SCB8 | 250.56 | 0.07477%
IS10INV3M2SCB9 | 250.56 | 0.07477%
IS10INV3M2SCB10 | 0 | 0%
IS10INV4M1SCB1 | 250.56 | 0.07477%
IS10INV4M1SCB2 | 250.56 | 0.07477%
IS10INV4M1SCB3 | 250.56 | 0.07477%
IS10INV4M1SCB4 | 250.56 | 0.07477%
IS10INV4M1SCB5 | 250.56 | 0.07477%
IS10INV4M1SCB6 | 250.56 | 0.07477%
IS10INV4M1SCB7 | 250.56 | 0.07477%
IS10INV4M1SCB8 | 219.24 | 0.06543%
IS10INV4M1SCB9 | 0 | 0%
IS10INV4M1SCB10 | 0 | 0%
IS10INV4M2SCB1 | 250.56 | 0.07477%
IS10INV4M2SCB2 | 250.56 | 0.07477%
IS10INV4M2SCB3 | 250.56 | 0.07477%
IS10INV4M2SCB4 | 250.56 | 0.07477%
IS10INV4M2SCB5 | 250.56 | 0.07477%
IS10INV4M2SCB6 | 250.56 | 0.07477%
IS10INV4M2SCB7 | 250.56 | 0.07477%
IS10INV4M2SCB8 | 250.56 | 0.07477%
IS10INV4M2SCB9 | 219.24 | 0.06543%
IS10INV4M2SCB10 | 0 | 0%
IS11INV1M1SCB1 | 252.88 | 0.07547%
IS11INV1M1SCB2 | 252.88 | 0.07547%
IS11INV1M1SCB3 | 252.88 | 0.07547%
IS11INV1M1SCB4 | 252.88 | 0.07547%
IS11INV1M1SCB5 | 252.88 | 0.07547%
IS11INV1M1SCB6 | 252.88 | 0.07547%
IS11INV1M1SCB7 | 252.88 | 0.07547%
IS11INV1M1SCB8 | 252.88 | 0.07547%
IS11INV1M1SCB9 | 0 | 0%
IS11INV1M1SCB10 | 0 | 0%
IS11INV1M2SCB1 | 268.685 | 0.08018%
IS11INV1M2SCB2 | 268.685 | 0.08018%
IS11INV1M2SCB3 | 252.88 | 0.07547%
IS11INV1M2SCB4 | 252.88 | 0.07547%
IS11INV1M2SCB5 | 221.27 | 0.06603%
IS11INV1M2SCB6 | 221.27 | 0.06603%
IS11INV1M2SCB7 | 252.88 | 0.07547%
IS11INV1M2SCB8 | 252.88 | 0.07547%
IS11INV1M2SCB9 | 221.27 | 0.06603%
IS11INV1M2SCB10 | 0 | 0%
IS11INV2M1SCB1 | 252.88 | 0.07547%
IS11INV2M1SCB2 | 252.88 | 0.07547%
IS11INV2M1SCB3 | 252.88 | 0.07547%
IS11INV2M1SCB4 | 252.88 | 0.07547%
IS11INV2M1SCB5 | 252.88 | 0.07547%
IS11INV2M1SCB6 | 252.88 | 0.07547%
IS11INV2M1SCB7 | 252.88 | 0.07547%
IS11INV2M1SCB8 | 252.88 | 0.07547%
IS11INV2M1SCB9 | 252.88 | 0.07547%
IS11INV2M1SCB10 | 0 | 0%
IS11INV2M2SCB1 | 252.88 | 0.07547%
IS11INV2M2SCB2 | 252.88 | 0.07547%
IS11INV2M2SCB3 | 268.685 | 0.08018%
IS11INV2M2SCB4 | 252.88 | 0.07547%
IS11INV2M2SCB5 | 268.685 | 0.08018%
IS11INV2M2SCB6 | 252.88 | 0.07547%
IS11INV2M2SCB7 | 252.88 | 0.07547%
IS11INV2M2SCB8 | 237.075 | 0.07075%
IS11INV2M2SCB9 | 0 | 0%
IS11INV2M2SCB10 | 0 | 0%
IS11INV3M1SCB1 | 252.88 | 0.07547%
IS11INV3M1SCB2 | 252.88 | 0.07547%
IS11INV3M1SCB3 | 252.88 | 0.07547%
IS11INV3M1SCB4 | 252.88 | 0.07547%
IS11INV3M1SCB5 | 252.88 | 0.07547%
IS11INV3M1SCB6 | 252.88 | 0.07547%
IS11INV3M1SCB7 | 252.88 | 0.07547%
IS11INV3M1SCB8 | 252.88 | 0.07547%
IS11INV3M1SCB9 | 0 | 0%
IS11INV3M1SCB10 | 0 | 0%
IS11INV3M2SCB1 | 252.88 | 0.07547%
IS11INV3M2SCB2 | 252.88 | 0.07547%
IS11INV3M2SCB3 | 221.27 | 0.06603%
IS11INV3M2SCB4 | 252.88 | 0.07547%
IS11INV3M2SCB5 | 252.88 | 0.07547%
IS11INV3M2SCB6 | 221.27 | 0.06603%
IS11INV3M2SCB7 | 252.88 | 0.07547%
IS11INV3M2SCB8 | 252.88 | 0.07547%
IS11INV3M2SCB9 | 252.88 | 0.07547%
IS11INV3M2SCB10 | 0 | 0%
IS11INV4M1SCB1 | 252.88 | 0.07547%
IS11INV4M1SCB2 | 252.88 | 0.07547%
IS11INV4M1SCB3 | 252.88 | 0.07547%
IS11INV4M1SCB4 | 252.88 | 0.07547%
IS11INV4M1SCB5 | 252.88 | 0.07547%
IS11INV4M1SCB6 | 252.88 | 0.07547%
IS11INV4M1SCB7 | 252.88 | 0.07547%
IS11INV4M1SCB8 | 252.88 | 0.07547%
IS11INV4M1SCB9 | 0 | 0%
IS11INV4M1SCB10 | 0 | 0%
IS11INV4M2SCB1 | 252.88 | 0.07547%
IS11INV4M2SCB2 | 252.88 | 0.07547%
IS11INV4M2SCB3 | 221.27 | 0.06603%
IS11INV4M2SCB4 | 221.27 | 0.06603%
IS11INV4M2SCB5 | 221.27 | 0.06603%
IS11INV4M2SCB6 | 205.465 | 0.06132%
IS11INV4M2SCB7 | 252.88 | 0.07547%
IS11INV4M2SCB8 | 158.05 | 0.04717%
IS11INV4M2SCB9 | 0 | 0%
IS11INV4M2SCB10 | 0 | 0%
IS12INV1M1SCB1 | 266.22 | 0.07945%
IS12INV1M1SCB2 | 266.22 | 0.07945%
IS12INV1M1SCB3 | 250.56 | 0.07477%
IS12INV1M1SCB4 | 250.56 | 0.07477%
IS12INV1M1SCB5 | 250.56 | 0.07477%
IS12INV1M1SCB6 | 250.56 | 0.07477%
IS12INV1M1SCB7 | 250.56 | 0.07477%
IS12INV1M1SCB8 | 156.6 | 0.04673%
IS12INV1M1SCB9 | 250.56 | 0.07477%
IS12INV1M1SCB10 | 0 | 0%
IS12INV1M2SCB1 | 266.22 | 0.07945%
IS12INV1M2SCB2 | 266.22 | 0.07945%
IS12INV1M2SCB3 | 266.22 | 0.07945%
IS12INV1M2SCB4 | 266.22 | 0.07945%
IS12INV1M2SCB5 | 266.22 | 0.07945%
IS12INV1M2SCB6 | 266.22 | 0.07945%
IS12INV1M2SCB7 | 266.22 | 0.07945%
IS12INV1M2SCB8 | 250.56 | 0.07477%
IS12INV1M2SCB9 | 0 | 0%
IS12INV1M2SCB10 | 0 | 0%
IS12INV2M1SCB1 | 219.24 | 0.06543%
IS12INV2M1SCB2 | 250.56 | 0.07477%
IS12INV2M1SCB3 | 250.56 | 0.07477%
IS12INV2M1SCB4 | 250.56 | 0.07477%
IS12INV2M1SCB5 | 219.24 | 0.06543%
IS12INV2M1SCB6 | 250.56 | 0.07477%
IS12INV2M1SCB7 | 250.56 | 0.07477%
IS12INV2M1SCB8 | 250.56 | 0.07477%
IS12INV2M1SCB9 | 0 | 0%
IS12INV2M1SCB10 | 0 | 0%
IS12INV2M2SCB1 | 250.56 | 0.07477%
IS12INV2M2SCB2 | 250.56 | 0.07477%
IS12INV2M2SCB3 | 250.56 | 0.07477%
IS12INV2M2SCB4 | 250.56 | 0.07477%
IS12INV2M2SCB5 | 250.56 | 0.07477%
IS12INV2M2SCB6 | 250.56 | 0.07477%
IS12INV2M2SCB7 | 250.56 | 0.07477%
IS12INV2M2SCB8 | 250.56 | 0.07477%
IS12INV2M2SCB9 | 250.56 | 0.07477%
IS12INV2M2SCB10 | 0 | 0%
IS12INV3M1SCB1 | 250.56 | 0.07477%
IS12INV3M1SCB2 | 219.24 | 0.06543%
IS12INV3M1SCB3 | 219.24 | 0.06543%
IS12INV3M1SCB4 | 250.56 | 0.07477%
IS12INV3M1SCB5 | 250.56 | 0.07477%
IS12INV3M1SCB6 | 250.56 | 0.07477%
IS12INV3M1SCB7 | 250.56 | 0.07477%
IS12INV3M1SCB8 | 250.56 | 0.07477%
IS12INV3M1SCB9 | 250.56 | 0.07477%
IS12INV3M1SCB10 | 0 | 0%
IS12INV3M2SCB1 | 250.56 | 0.07477%
IS12INV3M2SCB2 | 250.56 | 0.07477%
IS12INV3M2SCB3 | 250.56 | 0.07477%
IS12INV3M2SCB4 | 250.56 | 0.07477%
IS12INV3M2SCB5 | 250.56 | 0.07477%
IS12INV3M2SCB6 | 250.56 | 0.07477%
IS12INV3M2SCB7 | 250.56 | 0.07477%
IS12INV3M2SCB8 | 250.56 | 0.07477%
IS12INV3M2SCB9 | 0 | 0%
IS12INV3M2SCB10 | 0 | 0%
IS12INV4M1SCB1 | 250.56 | 0.07477%
IS12INV4M1SCB2 | 250.56 | 0.07477%
IS12INV4M1SCB3 | 250.56 | 0.07477%
IS12INV4M1SCB4 | 250.56 | 0.07477%
IS12INV4M1SCB5 | 250.56 | 0.07477%
IS12INV4M1SCB6 | 250.56 | 0.07477%
IS12INV4M1SCB7 | 250.56 | 0.07477%
IS12INV4M1SCB8 | 250.56 | 0.07477%
IS12INV4M1SCB9 | 0 | 0%
IS12INV4M1SCB10 | 0 | 0%
IS12INV4M2SCB1 | 250.56 | 0.07477%
IS12INV4M2SCB2 | 250.56 | 0.07477%
IS12INV4M2SCB3 | 250.56 | 0.07477%
IS12INV4M2SCB4 | 250.56 | 0.07477%
IS12INV4M2SCB5 | 250.56 | 0.07477%
IS12INV4M2SCB6 | 187.92 | 0.05608%
IS12INV4M2SCB7 | 250.56 | 0.07477%
IS12INV4M2SCB8 | 250.56 | 0.07477%
IS12INV4M2SCB9 | 266.22 | 0.07945%
IS12INV4M2SCB10 | 0 | 0%
IS13INV1M1SCB1 | 250.56 | 0.07477%
IS13INV1M1SCB2 | 250.56 | 0.07477%
IS13INV1M1SCB3 | 250.56 | 0.07477%
IS13INV1M1SCB4 | 250.56 | 0.07477%
IS13INV1M1SCB5 | 250.56 | 0.07477%
IS13INV1M1SCB6 | 250.56 | 0.07477%
IS13INV1M1SCB7 | 250.56 | 0.07477%
IS13INV1M1SCB8 | 250.56 | 0.07477%
IS13INV1M1SCB9 | 0 | 0%
IS13INV1M1SCB10 | 0 | 0%
IS13INV1M2SCB1 | 250.56 | 0.07477%
IS13INV1M2SCB2 | 250.56 | 0.07477%
IS13INV1M2SCB3 | 250.56 | 0.07477%
IS13INV1M2SCB4 | 250.56 | 0.07477%
IS13INV1M2SCB5 | 250.56 | 0.07477%
IS13INV1M2SCB6 | 250.56 | 0.07477%
IS13INV1M2SCB7 | 250.56 | 0.07477%
IS13INV1M2SCB8 | 250.56 | 0.07477%
IS13INV1M2SCB9 | 0 | 0%
IS13INV1M2SCB10 | 0 | 0%
IS13INV2M1SCB1 | 250.56 | 0.07477%
IS13INV2M1SCB2 | 219.24 | 0.06543%
IS13INV2M1SCB3 | 250.56 | 0.07477%
IS13INV2M1SCB4 | 250.56 | 0.07477%
IS13INV2M1SCB5 | 250.56 | 0.07477%
IS13INV2M1SCB6 | 250.56 | 0.07477%
IS13INV2M1SCB7 | 250.56 | 0.07477%
IS13INV2M1SCB8 | 250.56 | 0.07477%
IS13INV2M1SCB9 | 219.24 | 0.06543%
IS13INV2M1SCB10 | 0 | 0%
IS13INV2M2SCB1 | 250.56 | 0.07477%
IS13INV2M2SCB2 | 250.56 | 0.07477%
IS13INV2M2SCB3 | 250.56 | 0.07477%
IS13INV2M2SCB4 | 250.56 | 0.07477%
IS13INV2M2SCB5 | 250.56 | 0.07477%
IS13INV2M2SCB6 | 250.56 | 0.07477%
IS13INV2M2SCB7 | 250.56 | 0.07477%
IS13INV2M2SCB8 | 250.56 | 0.07477%
IS13INV2M2SCB9 | 0 | 0%
IS13INV2M2SCB10 | 0 | 0%
IS13INV3M1SCB1 | 219.24 | 0.06543%
IS13INV3M1SCB2 | 250.56 | 0.07477%
IS13INV3M1SCB3 | 250.56 | 0.07477%
IS13INV3M1SCB4 | 250.56 | 0.07477%
IS13INV3M1SCB5 | 250.56 | 0.07477%
IS13INV3M1SCB6 | 250.56 | 0.07477%
IS13INV3M1SCB7 | 250.56 | 0.07477%
IS13INV3M1SCB8 | 219.24 | 0.06543%
IS13INV3M1SCB9 | 250.56 | 0.07477%
IS13INV3M1SCB10 | 0 | 0%
IS13INV3M2SCB1 | 250.56 | 0.07477%
IS13INV3M2SCB2 | 250.56 | 0.07477%
IS13INV3M2SCB3 | 250.56 | 0.07477%
IS13INV3M2SCB4 | 250.56 | 0.07477%
IS13INV3M2SCB5 | 250.56 | 0.07477%
IS13INV3M2SCB6 | 250.56 | 0.07477%
IS13INV3M2SCB7 | 250.56 | 0.07477%
IS13INV3M2SCB8 | 250.56 | 0.07477%
IS13INV3M2SCB9 | 0 | 0%
IS13INV3M2SCB10 | 0 | 0%
IS13INV4M1SCB1 | 250.56 | 0.07477%
IS13INV4M1SCB2 | 250.56 | 0.07477%
IS13INV4M1SCB3 | 219.24 | 0.06543%
IS13INV4M1SCB4 | 250.56 | 0.07477%
IS13INV4M1SCB5 | 250.56 | 0.07477%
IS13INV4M1SCB6 | 250.56 | 0.07477%
IS13INV4M1SCB7 | 250.56 | 0.07477%
IS13INV4M1SCB8 | 250.56 | 0.07477%
IS13INV4M1SCB9 | 219.24 | 0.06543%
IS13INV4M1SCB10 | 0 | 0%
IS13INV4M2SCB1 | 250.56 | 0.07477%
IS13INV4M2SCB2 | 250.56 | 0.07477%
IS13INV4M2SCB3 | 250.56 | 0.07477%
IS13INV4M2SCB4 | 250.56 | 0.07477%
IS13INV4M2SCB5 | 250.56 | 0.07477%
IS13INV4M2SCB6 | 250.56 | 0.07477%
IS13INV4M2SCB7 | 250.56 | 0.07477%
IS13INV4M2SCB8 | 250.56 | 0.07477%
IS13INV4M2SCB9 | 0 | 0%
IS13INV4M2SCB10 | 0 | 0%
IS14INV1M1SCB1 | 250.56 | 0.07477%
IS14INV1M1SCB2 | 250.56 | 0.07477%
IS14INV1M1SCB3 | 250.56 | 0.07477%
IS14INV1M1SCB4 | 250.56 | 0.07477%
IS14INV1M1SCB5 | 250.56 | 0.07477%
IS14INV1M1SCB6 | 250.56 | 0.07477%
IS14INV1M1SCB7 | 250.56 | 0.07477%
IS14INV1M1SCB8 | 219.24 | 0.06543%
IS14INV1M1SCB9 | 250.56 | 0.07477%
IS14INV1M1SCB10 | 0 | 0%
IS14INV1M2SCB1 | 219.24 | 0.06543%
IS14INV1M2SCB2 | 219.24 | 0.06543%
IS14INV1M2SCB3 | 219.24 | 0.06543%
IS14INV1M2SCB4 | 250.56 | 0.07477%
IS14INV1M2SCB5 | 250.56 | 0.07477%
IS14INV1M2SCB6 | 250.56 | 0.07477%
IS14INV1M2SCB7 | 250.56 | 0.07477%
IS14INV1M2SCB8 | 250.56 | 0.07477%
IS14INV1M2SCB9 | 0 | 0%
IS14INV1M2SCB10 | 0 | 0%
IS14INV2M1SCB1 | 250.56 | 0.07477%
IS14INV2M1SCB2 | 250.56 | 0.07477%
IS14INV2M1SCB3 | 250.56 | 0.07477%
IS14INV2M1SCB4 | 250.56 | 0.07477%
IS14INV2M1SCB5 | 250.56 | 0.07477%
IS14INV2M1SCB6 | 250.56 | 0.07477%
IS14INV2M1SCB7 | 219.24 | 0.06543%
IS14INV2M1SCB8 | 250.56 | 0.07477%
IS14INV2M1SCB9 | 250.56 | 0.07477%
IS14INV2M1SCB10 | 0 | 0%
IS14INV2M2SCB1 | 250.56 | 0.07477%
IS14INV2M2SCB2 | 250.56 | 0.07477%
IS14INV2M2SCB3 | 250.56 | 0.07477%
IS14INV2M2SCB4 | 250.56 | 0.07477%
IS14INV2M2SCB5 | 250.56 | 0.07477%
IS14INV2M2SCB6 | 250.56 | 0.07477%
IS14INV2M2SCB7 | 250.56 | 0.07477%
IS14INV2M2SCB8 | 250.56 | 0.07477%
IS14INV2M2SCB9 | 0 | 0%
IS14INV2M2SCB10 | 0 | 0%
IS14INV3M1SCB1 | 250.56 | 0.07477%
IS14INV3M1SCB2 | 250.56 | 0.07477%
IS14INV3M1SCB3 | 250.56 | 0.07477%
IS14INV3M1SCB4 | 219.24 | 0.06543%
IS14INV3M1SCB5 | 250.56 | 0.07477%
IS14INV3M1SCB6 | 250.56 | 0.07477%
IS14INV3M1SCB7 | 250.56 | 0.07477%
IS14INV3M1SCB8 | 219.24 | 0.06543%
IS14INV3M1SCB9 | 250.56 | 0.07477%
IS14INV3M1SCB10 | 0 | 0%
IS14INV3M2SCB1 | 250.56 | 0.07477%
IS14INV3M2SCB2 | 250.56 | 0.07477%
IS14INV3M2SCB3 | 250.56 | 0.07477%
IS14INV3M2SCB4 | 250.56 | 0.07477%
IS14INV3M2SCB5 | 250.56 | 0.07477%
IS14INV3M2SCB6 | 250.56 | 0.07477%
IS14INV3M2SCB7 | 250.56 | 0.07477%
IS14INV3M2SCB8 | 250.56 | 0.07477%
IS14INV3M2SCB9 | 0 | 0%
IS14INV3M2SCB10 | 0 | 0%
IS14INV4M1SCB1 | 219.24 | 0.06543%
IS14INV4M1SCB2 | 250.56 | 0.07477%
IS14INV4M1SCB3 | 250.56 | 0.07477%
IS14INV4M1SCB4 | 250.56 | 0.07477%
IS14INV4M1SCB5 | 250.56 | 0.07477%
IS14INV4M1SCB6 | 250.56 | 0.07477%
IS14INV4M1SCB7 | 250.56 | 0.07477%
IS14INV4M1SCB8 | 219.24 | 0.06543%
IS14INV4M1SCB9 | 250.56 | 0.07477%
IS14INV4M1SCB10 | 0 | 0%
IS14INV4M2SCB1 | 250.56 | 0.07477%
IS14INV4M2SCB2 | 250.56 | 0.07477%
IS14INV4M2SCB3 | 250.56 | 0.07477%
IS14INV4M2SCB4 | 250.56 | 0.07477%
IS14INV4M2SCB5 | 250.56 | 0.07477%
IS14INV4M2SCB6 | 250.56 | 0.07477%
IS14INV4M2SCB7 | 250.56 | 0.07477%
IS14INV4M2SCB8 | 250.56 | 0.07477%
IS14INV4M2SCB9 | 0 | 0%
IS14INV4M2SCB10 | 0 | 0%
IS15INV1M1SCB1 | 250.56 | 0.07477%
IS15INV1M1SCB2 | 250.56 | 0.07477%
IS15INV1M1SCB3 | 250.56 | 0.07477%
IS15INV1M1SCB4 | 250.56 | 0.07477%
IS15INV1M1SCB5 | 250.56 | 0.07477%
IS15INV1M1SCB6 | 250.56 | 0.07477%
IS15INV1M1SCB7 | 250.56 | 0.07477%
IS15INV1M1SCB8 | 250.56 | 0.07477%
IS15INV1M1SCB9 | 0 | 0%
IS15INV1M1SCB10 | 0 | 0%
IS15INV1M2SCB1 | 250.56 | 0.07477%
IS15INV1M2SCB2 | 250.56 | 0.07477%
IS15INV1M2SCB3 | 250.56 | 0.07477%
IS15INV1M2SCB4 | 250.56 | 0.07477%
IS15INV1M2SCB5 | 219.24 | 0.06543%
IS15INV1M2SCB6 | 250.56 | 0.07477%
IS15INV1M2SCB7 | 219.24 | 0.06543%
IS15INV1M2SCB8 | 250.56 | 0.07477%
IS15INV1M2SCB9 | 250.56 | 0.07477%
IS15INV1M2SCB10 | 0 | 0%
IS15INV2M1SCB1 | 250.56 | 0.07477%
IS15INV2M1SCB2 | 250.56 | 0.07477%
IS15INV2M1SCB3 | 250.56 | 0.07477%
IS15INV2M1SCB4 | 250.56 | 0.07477%
IS15INV2M1SCB5 | 250.56 | 0.07477%
IS15INV2M1SCB6 | 250.56 | 0.07477%
IS15INV2M1SCB7 | 250.56 | 0.07477%
IS15INV2M1SCB8 | 250.56 | 0.07477%
IS15INV2M1SCB9 | 0 | 0%
IS15INV2M1SCB10 | 0 | 0%
IS15INV2M2SCB1 | 219.24 | 0.06543%
IS15INV2M2SCB2 | 250.56 | 0.07477%
IS15INV2M2SCB3 | 250.56 | 0.07477%
IS15INV2M2SCB4 | 250.56 | 0.07477%
IS15INV2M2SCB5 | 250.56 | 0.07477%
IS15INV2M2SCB6 | 250.56 | 0.07477%
IS15INV2M2SCB7 | 250.56 | 0.07477%
IS15INV2M2SCB8 | 219.24 | 0.06543%
IS15INV2M2SCB9 | 0 | 0%
IS15INV2M2SCB10 | 0 | 0%
IS15INV3M1SCB1 | 250.56 | 0.07477%
IS15INV3M1SCB2 | 250.56 | 0.07477%
IS15INV3M1SCB3 | 250.56 | 0.07477%
IS15INV3M1SCB4 | 250.56 | 0.07477%
IS15INV3M1SCB5 | 250.56 | 0.07477%
IS15INV3M1SCB6 | 250.56 | 0.07477%
IS15INV3M1SCB7 | 219.24 | 0.06543%
IS15INV3M1SCB8 | 250.56 | 0.07477%
IS15INV3M1SCB9 | 250.56 | 0.07477%
IS15INV3M1SCB10 | 0 | 0%
IS15INV3M2SCB1 | 219.24 | 0.06543%
IS15INV3M2SCB2 | 250.56 | 0.07477%
IS15INV3M2SCB3 | 250.56 | 0.07477%
IS15INV3M2SCB4 | 250.56 | 0.07477%
IS15INV3M2SCB5 | 250.56 | 0.07477%
IS15INV3M2SCB6 | 250.56 | 0.07477%
IS15INV3M2SCB7 | 250.56 | 0.07477%
IS15INV3M2SCB8 | 250.56 | 0.07477%
IS15INV3M2SCB9 | 219.24 | 0.06543%
IS15INV3M2SCB10 | 0 | 0%
IS15INV4M1SCB1 | 250.56 | 0.07477%
IS15INV4M1SCB2 | 219.24 | 0.06543%
IS15INV4M1SCB3 | 250.56 | 0.07477%
IS15INV4M1SCB4 | 250.56 | 0.07477%
IS15INV4M1SCB5 | 250.56 | 0.07477%
IS15INV4M1SCB6 | 250.56 | 0.07477%
IS15INV4M1SCB7 | 219.24 | 0.06543%
IS15INV4M1SCB8 | 250.56 | 0.07477%
IS15INV4M1SCB9 | 250.56 | 0.07477%
IS15INV4M1SCB10 | 0 | 0%
IS15INV4M2SCB1 | 250.56 | 0.07477%
IS15INV4M2SCB2 | 250.56 | 0.07477%
IS15INV4M2SCB3 | 250.56 | 0.07477%
IS15INV4M2SCB4 | 250.56 | 0.07477%
IS15INV4M2SCB5 | 250.56 | 0.07477%
IS15INV4M2SCB6 | 250.56 | 0.07477%
IS15INV4M2SCB7 | 250.56 | 0.07477%
IS15INV4M2SCB8 | 250.56 | 0.07477%
IS15INV4M2SCB9 | 0 | 0%
IS15INV4M2SCB10 | 0 | 0%
IS16INV1M1SCB1 | 250.56 | 0.07477%
IS16INV1M1SCB2 | 219.24 | 0.06543%
IS16INV1M1SCB3 | 250.56 | 0.07477%
IS16INV1M1SCB4 | 250.56 | 0.07477%
IS16INV1M1SCB5 | 250.56 | 0.07477%
IS16INV1M1SCB6 | 250.56 | 0.07477%
IS16INV1M1SCB7 | 250.56 | 0.07477%
IS16INV1M1SCB8 | 219.24 | 0.06543%
IS16INV1M1SCB9 | 250.56 | 0.07477%
IS16INV1M1SCB10 | 0 | 0%
IS16INV1M2SCB1 | 250.56 | 0.07477%
IS16INV1M2SCB2 | 250.56 | 0.07477%
IS16INV1M2SCB3 | 250.56 | 0.07477%
IS16INV1M2SCB4 | 250.56 | 0.07477%
IS16INV1M2SCB5 | 250.56 | 0.07477%
IS16INV1M2SCB6 | 250.56 | 0.07477%
IS16INV1M2SCB7 | 250.56 | 0.07477%
IS16INV1M2SCB8 | 250.56 | 0.07477%
IS16INV1M2SCB9 | 0 | 0%
IS16INV1M2SCB10 | 0 | 0%
IS16INV2M1SCB1 | 250.56 | 0.07477%
IS16INV2M1SCB2 | 250.56 | 0.07477%
IS16INV2M1SCB3 | 250.56 | 0.07477%
IS16INV2M1SCB4 | 250.56 | 0.07477%
IS16INV2M1SCB5 | 219.24 | 0.06543%
IS16INV2M1SCB6 | 187.92 | 0.05608%
IS16INV2M1SCB7 | 250.56 | 0.07477%
IS16INV2M1SCB8 | 250.56 | 0.07477%
IS16INV2M1SCB9 | 250.56 | 0.07477%
IS16INV2M1SCB10 | 0 | 0%
IS16INV2M2SCB1 | 250.56 | 0.07477%
IS16INV2M2SCB2 | 250.56 | 0.07477%
IS16INV2M2SCB3 | 250.56 | 0.07477%
IS16INV2M2SCB4 | 250.56 | 0.07477%
IS16INV2M2SCB5 | 250.56 | 0.07477%
IS16INV2M2SCB6 | 250.56 | 0.07477%
IS16INV2M2SCB7 | 250.56 | 0.07477%
IS16INV2M2SCB8 | 250.56 | 0.07477%
IS16INV2M2SCB9 | 0 | 0%
IS16INV2M2SCB10 | 0 | 0%
IS16INV3M1SCB1 | 219.24 | 0.06543%
IS16INV3M1SCB2 | 219.24 | 0.06543%
IS16INV3M1SCB3 | 250.56 | 0.07477%
IS16INV3M1SCB4 | 250.56 | 0.07477%
IS16INV3M1SCB5 | 250.56 | 0.07477%
IS16INV3M1SCB6 | 250.56 | 0.07477%
IS16INV3M1SCB7 | 250.56 | 0.07477%
IS16INV3M1SCB8 | 250.56 | 0.07477%
IS16INV3M1SCB9 | 187.92 | 0.05608%
IS16INV3M1SCB10 | 0 | 0%
IS16INV3M2SCB1 | 219.24 | 0.06543%
IS16INV3M2SCB2 | 219.24 | 0.06543%
IS16INV3M2SCB3 | 219.24 | 0.06543%
IS16INV3M2SCB4 | 219.24 | 0.06543%
IS16INV3M2SCB5 | 250.56 | 0.07477%
IS16INV3M2SCB6 | 250.56 | 0.07477%
IS16INV3M2SCB7 | 250.56 | 0.07477%
IS16INV3M2SCB8 | 250.56 | 0.07477%
IS16INV3M2SCB9 | 0 | 0%
IS16INV3M2SCB10 | 0 | 0%
IS16INV4M1SCB1 | 219.24 | 0.06543%
IS16INV4M1SCB2 | 250.56 | 0.07477%
IS16INV4M1SCB3 | 187.92 | 0.05608%
IS16INV4M1SCB4 | 219.24 | 0.06543%
IS16INV4M1SCB5 | 250.56 | 0.07477%
IS16INV4M1SCB6 | 250.56 | 0.07477%
IS16INV4M1SCB7 | 250.56 | 0.07477%
IS16INV4M1SCB8 | 250.56 | 0.07477%
IS16INV4M1SCB9 | 250.56 | 0.07477%
IS16INV4M1SCB10 | 0 | 0%
IS16INV4M2SCB1 | 219.24 | 0.06543%
IS16INV4M2SCB2 | 250.56 | 0.07477%
IS16INV4M2SCB3 | 250.56 | 0.07477%
IS16INV4M2SCB4 | 250.56 | 0.07477%
IS16INV4M2SCB5 | 250.56 | 0.07477%
IS16INV4M2SCB6 | 250.56 | 0.07477%
IS16INV4M2SCB7 | 250.56 | 0.07477%
IS16INV4M2SCB8 | 250.56 | 0.07477%
IS16INV4M2SCB9 | 0 | 0%
IS16INV4M2SCB10 | 0 | 0%
IS17INV1M1SCB1 | 250.56 | 0.07477%
IS17INV1M1SCB2 | 250.56 | 0.07477%
IS17INV1M1SCB3 | 250.56 | 0.07477%
IS17INV1M1SCB4 | 250.56 | 0.07477%
IS17INV1M1SCB5 | 250.56 | 0.07477%
IS17INV1M1SCB6 | 250.56 | 0.07477%
IS17INV1M1SCB7 | 250.56 | 0.07477%
IS17INV1M1SCB8 | 219.24 | 0.06543%
IS17INV1M1SCB9 | 0 | 0%
IS17INV1M1SCB10 | 0 | 0%
IS17INV1M2SCB1 | 250.56 | 0.07477%
IS17INV1M2SCB2 | 250.56 | 0.07477%
IS17INV1M2SCB3 | 250.56 | 0.07477%
IS17INV1M2SCB4 | 250.56 | 0.07477%
IS17INV1M2SCB5 | 250.56 | 0.07477%
IS17INV1M2SCB6 | 250.56 | 0.07477%
IS17INV1M2SCB7 | 250.56 | 0.07477%
IS17INV1M2SCB8 | 250.56 | 0.07477%
IS17INV1M2SCB9 | 0 | 0%
IS17INV1M2SCB10 | 0 | 0%
IS17INV2M1SCB1 | 250.56 | 0.07477%
IS17INV2M1SCB2 | 250.56 | 0.07477%
IS17INV2M1SCB3 | 250.56 | 0.07477%
IS17INV2M1SCB4 | 250.56 | 0.07477%
IS17INV2M1SCB5 | 250.56 | 0.07477%
IS17INV2M1SCB6 | 250.56 | 0.07477%
IS17INV2M1SCB7 | 250.56 | 0.07477%
IS17INV2M1SCB8 | 250.56 | 0.07477%
IS17INV2M1SCB9 | 0 | 0%
IS17INV2M1SCB10 | 0 | 0%
IS17INV2M2SCB1 | 250.56 | 0.07477%
IS17INV2M2SCB2 | 250.56 | 0.07477%
IS17INV2M2SCB3 | 250.56 | 0.07477%
IS17INV2M2SCB4 | 250.56 | 0.07477%
IS17INV2M2SCB5 | 250.56 | 0.07477%
IS17INV2M2SCB6 | 250.56 | 0.07477%
IS17INV2M2SCB7 | 250.56 | 0.07477%
IS17INV2M2SCB8 | 0 | 0%
IS17INV2M2SCB9 | 0 | 0%
IS17INV2M2SCB10 | 0 | 0%
IS17INV3M1SCB1 | 250.56 | 0.07477%
IS17INV3M1SCB2 | 250.56 | 0.07477%
IS17INV3M1SCB3 | 250.56 | 0.07477%
IS17INV3M1SCB4 | 219.24 | 0.06543%
IS17INV3M1SCB5 | 250.56 | 0.07477%
IS17INV3M1SCB6 | 250.56 | 0.07477%
IS17INV3M1SCB7 | 234.9 | 0.0701%
IS17INV3M1SCB8 | 250.56 | 0.07477%
IS17INV3M1SCB9 | 0 | 0%
IS17INV3M1SCB10 | 0 | 0%
IS17INV3M2SCB1 | 250.56 | 0.07477%
IS17INV3M2SCB2 | 250.56 | 0.07477%
IS17INV3M2SCB3 | 250.56 | 0.07477%
IS17INV3M2SCB4 | 250.56 | 0.07477%
IS17INV3M2SCB5 | 250.56 | 0.07477%
IS17INV3M2SCB6 | 250.56 | 0.07477%
IS17INV3M2SCB7 | 250.56 | 0.07477%
IS17INV3M2SCB8 | 0 | 0%
IS17INV3M2SCB9 | 0 | 0%
IS17INV3M2SCB10 | 0 | 0%
IS17INV4M1SCB1 | 250.56 | 0.07477%
IS17INV4M1SCB2 | 250.56 | 0.07477%
IS17INV4M1SCB3 | 250.56 | 0.07477%
IS17INV4M1SCB4 | 250.56 | 0.07477%
IS17INV4M1SCB5 | 250.56 | 0.07477%
IS17INV4M1SCB6 | 250.56 | 0.07477%
IS17INV4M1SCB7 | 250.56 | 0.07477%
IS17INV4M1SCB8 | 250.56 | 0.07477%
IS17INV4M1SCB9 | 0 | 0%
IS17INV4M1SCB10 | 0 | 0%
IS17INV4M2SCB1 | 250.56 | 0.07477%
IS17INV4M2SCB2 | 250.56 | 0.07477%
IS17INV4M2SCB3 | 250.56 | 0.07477%
IS17INV4M2SCB4 | 250.56 | 0.07477%
IS17INV4M2SCB5 | 250.56 | 0.07477%
IS17INV4M2SCB6 | 250.56 | 0.07477%
IS17INV4M2SCB7 | 250.56 | 0.07477%
IS17INV4M2SCB8 | 250.56 | 0.07477%
IS17INV4M2SCB9 | 0 | 0%
IS17INV4M2SCB10 | 0 | 0%
IS18INV1M1SCB1 | 250.56 | 0.07477%
IS18INV1M1SCB2 | 250.56 | 0.07477%
IS18INV1M1SCB3 | 250.56 | 0.07477%
IS18INV1M1SCB4 | 250.56 | 0.07477%
IS18INV1M1SCB5 | 250.56 | 0.07477%
IS18INV1M1SCB6 | 250.56 | 0.07477%
IS18INV1M1SCB7 | 250.56 | 0.07477%
IS18INV1M1SCB8 | 250.56 | 0.07477%
IS18INV1M1SCB9 | 250.56 | 0.07477%
IS18INV1M1SCB10 | 0 | 0%
IS18INV1M2SCB1 | 250.56 | 0.07477%
IS18INV1M2SCB2 | 250.56 | 0.07477%
IS18INV1M2SCB3 | 219.24 | 0.06543%
IS18INV1M2SCB4 | 250.56 | 0.07477%
IS18INV1M2SCB5 | 250.56 | 0.07477%
IS18INV1M2SCB6 | 250.56 | 0.07477%
IS18INV1M2SCB7 | 250.56 | 0.07477%
IS18INV1M2SCB8 | 250.56 | 0.07477%
IS18INV1M2SCB9 | 0 | 0%
IS18INV1M2SCB10 | 0 | 0%
IS18INV2M1SCB1 | 250.56 | 0.07477%
IS18INV2M1SCB2 | 250.56 | 0.07477%
IS18INV2M1SCB3 | 250.56 | 0.07477%
IS18INV2M1SCB4 | 250.56 | 0.07477%
IS18INV2M1SCB5 | 250.56 | 0.07477%
IS18INV2M1SCB6 | 250.56 | 0.07477%
IS18INV2M1SCB7 | 250.56 | 0.07477%
IS18INV2M1SCB8 | 250.56 | 0.07477%
IS18INV2M1SCB9 | 250.56 | 0.07477%
IS18INV2M1SCB10 | 0 | 0%
IS18INV2M2SCB1 | 250.56 | 0.07477%
IS18INV2M2SCB2 | 250.56 | 0.07477%
IS18INV2M2SCB3 | 250.56 | 0.07477%
IS18INV2M2SCB4 | 250.56 | 0.07477%
IS18INV2M2SCB5 | 250.56 | 0.07477%
IS18INV2M2SCB6 | 250.56 | 0.07477%
IS18INV2M2SCB7 | 250.56 | 0.07477%
IS18INV2M2SCB8 | 219.24 | 0.06543%
IS18INV2M2SCB9 | 0 | 0%
IS18INV2M2SCB10 | 0 | 0%
IS18INV3M1SCB1 | 250.56 | 0.07477%
IS18INV3M1SCB2 | 250.56 | 0.07477%
IS18INV3M1SCB3 | 250.56 | 0.07477%
IS18INV3M1SCB4 | 250.56 | 0.07477%
IS18INV3M1SCB5 | 250.56 | 0.07477%
IS18INV3M1SCB6 | 250.56 | 0.07477%
IS18INV3M1SCB7 | 250.56 | 0.07477%
IS18INV3M1SCB8 | 219.24 | 0.06543%
IS18INV3M1SCB9 | 250.56 | 0.07477%
IS18INV3M1SCB10 | 0 | 0%
IS18INV3M2SCB1 | 250.56 | 0.07477%
IS18INV3M2SCB2 | 250.56 | 0.07477%
IS18INV3M2SCB3 | 250.56 | 0.07477%
IS18INV3M2SCB4 | 250.56 | 0.07477%
IS18INV3M2SCB5 | 250.56 | 0.07477%
IS18INV3M2SCB6 | 250.56 | 0.07477%
IS18INV3M2SCB7 | 250.56 | 0.07477%
IS18INV3M2SCB8 | 219.24 | 0.06543%
IS18INV3M2SCB9 | 0 | 0%
IS18INV3M2SCB10 | 0 | 0%
IS18INV4M1SCB1 | 0 | 0%
IS18INV4M1SCB2 | 250.56 | 0.07477%
IS18INV4M1SCB3 | 250.56 | 0.07477%
IS18INV4M1SCB4 | 250.56 | 0.07477%
IS18INV4M1SCB5 | 250.56 | 0.07477%
IS18INV4M1SCB6 | 250.56 | 0.07477%
IS18INV4M1SCB7 | 250.56 | 0.07477%
IS18INV4M1SCB8 | 250.56 | 0.07477%
IS18INV4M1SCB9 | 250.56 | 0.07477%
IS18INV4M1SCB10 | 0 | 0%
IS18INV4M2SCB1 | 250.56 | 0.07477%
IS18INV4M2SCB2 | 250.56 | 0.07477%
IS18INV4M2SCB3 | 250.56 | 0.07477%
IS18INV4M2SCB4 | 250.56 | 0.07477%
IS18INV4M2SCB5 | 250.56 | 0.07477%
IS18INV4M2SCB6 | 250.56 | 0.07477%
IS18INV4M2SCB7 | 250.56 | 0.07477%
IS18INV4M2SCB8 | 250.56 | 0.07477%
IS18INV4M2SCB9 | 0 | 0%
IS18INV4M2SCB10 | 0 | 0%
IS19INV1M1SCB1 | 219.24 | 0.06543%
IS19INV1M1SCB2 | 250.56 | 0.07477%
IS19INV1M1SCB3 | 250.56 | 0.07477%
IS19INV1M1SCB4 | 250.56 | 0.07477%
IS19INV1M1SCB5 | 219.24 | 0.06543%
IS19INV1M1SCB6 | 250.56 | 0.07477%
IS19INV1M1SCB7 | 219.24 | 0.06543%
IS19INV1M1SCB8 | 250.56 | 0.07477%
IS19INV1M1SCB9 | 250.56 | 0.07477%
IS19INV1M1SCB10 | 0 | 0%
IS19INV1M2SCB1 | 250.56 | 0.07477%
IS19INV1M2SCB2 | 250.56 | 0.07477%
IS19INV1M2SCB3 | 250.56 | 0.07477%
IS19INV1M2SCB4 | 250.56 | 0.07477%
IS19INV1M2SCB5 | 250.56 | 0.07477%
IS19INV1M2SCB6 | 250.56 | 0.07477%
IS19INV1M2SCB7 | 250.56 | 0.07477%
IS19INV1M2SCB8 | 250.56 | 0.07477%
IS19INV1M2SCB9 | 250.56 | 0.07477%
IS19INV1M2SCB10 | 0 | 0%
IS19INV2M1SCB1 | 250.56 | 0.07477%
IS19INV2M1SCB2 | 219.24 | 0.06543%
IS19INV2M1SCB3 | 250.56 | 0.07477%
IS19INV2M1SCB4 | 250.56 | 0.07477%
IS19INV2M1SCB5 | 250.56 | 0.07477%
IS19INV2M1SCB6 | 250.56 | 0.07477%
IS19INV2M1SCB7 | 250.56 | 0.07477%
IS19INV2M1SCB8 | 250.56 | 0.07477%
IS19INV2M1SCB9 | 250.56 | 0.07477%
IS19INV2M1SCB10 | 0 | 0%
IS19INV2M2SCB1 | 250.56 | 0.07477%
IS19INV2M2SCB2 | 250.56 | 0.07477%
IS19INV2M2SCB3 | 250.56 | 0.07477%
IS19INV2M2SCB4 | 250.56 | 0.07477%
IS19INV2M2SCB5 | 250.56 | 0.07477%
IS19INV2M2SCB6 | 250.56 | 0.07477%
IS19INV2M2SCB7 | 250.56 | 0.07477%
IS19INV2M2SCB8 | 250.56 | 0.07477%
IS19INV2M2SCB9 | 219.24 | 0.06543%
IS19INV2M2SCB10 | 0 | 0%
IS19INV3M1SCB1 | 250.56 | 0.07477%
IS19INV3M1SCB2 | 250.56 | 0.07477%
IS19INV3M1SCB3 | 250.56 | 0.07477%
IS19INV3M1SCB4 | 219.24 | 0.06543%
IS19INV3M1SCB5 | 250.56 | 0.07477%
IS19INV3M1SCB6 | 250.56 | 0.07477%
IS19INV3M1SCB7 | 250.56 | 0.07477%
IS19INV3M1SCB8 | 250.56 | 0.07477%
IS19INV3M1SCB9 | 250.56 | 0.07477%
IS19INV3M1SCB10 | 0 | 0%
IS19INV3M2SCB1 | 250.56 | 0.07477%
IS19INV3M2SCB2 | 250.56 | 0.07477%
IS19INV3M2SCB3 | 250.56 | 0.07477%
IS19INV3M2SCB4 | 250.56 | 0.07477%
IS19INV3M2SCB5 | 250.56 | 0.07477%
IS19INV3M2SCB6 | 250.56 | 0.07477%
IS19INV3M2SCB7 | 250.56 | 0.07477%
IS19INV3M2SCB8 | 250.56 | 0.07477%
IS19INV3M2SCB9 | 250.56 | 0.07477%
IS19INV3M2SCB10 | 0 | 0%
IS19INV4M1SCB1 | 250.56 | 0.07477%
IS19INV4M1SCB2 | 250.56 | 0.07477%
IS19INV4M1SCB3 | 250.56 | 0.07477%
IS19INV4M1SCB4 | 250.56 | 0.07477%
IS19INV4M1SCB5 | 250.56 | 0.07477%
IS19INV4M1SCB6 | 250.56 | 0.07477%
IS19INV4M1SCB7 | 250.56 | 0.07477%
IS19INV4M1SCB8 | 250.56 | 0.07477%
IS19INV4M1SCB9 | 0 | 0%
IS19INV4M1SCB10 | 0 | 0%
IS19INV4M2SCB1 | 219.24 | 0.06543%
IS19INV4M2SCB2 | 250.56 | 0.07477%
IS19INV4M2SCB3 | 250.56 | 0.07477%
IS19INV4M2SCB4 | 250.56 | 0.07477%
IS19INV4M2SCB5 | 250.56 | 0.07477%
IS19INV4M2SCB6 | 250.56 | 0.07477%
IS19INV4M2SCB7 | 250.56 | 0.07477%
IS19INV4M2SCB8 | 250.56 | 0.07477%
IS19INV4M2SCB9 | 250.56 | 0.07477%
IS19INV4M2SCB10 | 0 | 0%
IS20INV1M1SCB1 | 250.56 | 0.07477%
IS20INV1M1SCB2 | 250.56 | 0.07477%
IS20INV1M1SCB3 | 250.56 | 0.07477%
IS20INV1M1SCB4 | 250.56 | 0.07477%
IS20INV1M1SCB5 | 250.56 | 0.07477%
IS20INV1M1SCB6 | 250.56 | 0.07477%
IS20INV1M1SCB7 | 250.56 | 0.07477%
IS20INV1M1SCB8 | 250.56 | 0.07477%
IS20INV1M1SCB9 | 250.56 | 0.07477%
IS20INV1M1SCB10 | 0 | 0%
IS20INV1M2SCB1 | 250.56 | 0.07477%
IS20INV1M2SCB2 | 250.56 | 0.07477%
IS20INV1M2SCB3 | 250.56 | 0.07477%
IS20INV1M2SCB4 | 250.56 | 0.07477%
IS20INV1M2SCB5 | 250.56 | 0.07477%
IS20INV1M2SCB6 | 250.56 | 0.07477%
IS20INV1M2SCB7 | 250.56 | 0.07477%
IS20INV1M2SCB8 | 250.56 | 0.07477%
IS20INV1M2SCB9 | 250.56 | 0.07477%
IS20INV1M2SCB10 | 0 | 0%
IS20INV2M1SCB1 | 250.56 | 0.07477%
IS20INV2M1SCB2 | 250.56 | 0.07477%
IS20INV2M1SCB3 | 250.56 | 0.07477%
IS20INV2M1SCB4 | 250.56 | 0.07477%
IS20INV2M1SCB5 | 250.56 | 0.07477%
IS20INV2M1SCB6 | 250.56 | 0.07477%
IS20INV2M1SCB7 | 250.56 | 0.07477%
IS20INV2M1SCB8 | 250.56 | 0.07477%
IS20INV2M1SCB9 | 250.56 | 0.07477%
IS20INV2M1SCB10 | 0 | 0%
IS20INV2M2SCB1 | 250.56 | 0.07477%
IS20INV2M2SCB2 | 250.56 | 0.07477%
IS20INV2M2SCB3 | 250.56 | 0.07477%
IS20INV2M2SCB4 | 250.56 | 0.07477%
IS20INV2M2SCB5 | 250.56 | 0.07477%
IS20INV2M2SCB6 | 250.56 | 0.07477%
IS20INV2M2SCB7 | 250.56 | 0.07477%
IS20INV2M2SCB8 | 250.56 | 0.07477%
IS20INV2M2SCB9 | 250.56 | 0.07477%
IS20INV2M2SCB10 | 0 | 0%
IS20INV3M1SCB1 | 250.56 | 0.07477%
IS20INV3M1SCB2 | 250.56 | 0.07477%
IS20INV3M1SCB3 | 250.56 | 0.07477%
IS20INV3M1SCB4 | 250.56 | 0.07477%
IS20INV3M1SCB5 | 250.56 | 0.07477%
IS20INV3M1SCB6 | 250.56 | 0.07477%
IS20INV3M1SCB7 | 250.56 | 0.07477%
IS20INV3M1SCB8 | 250.56 | 0.07477%
IS20INV3M1SCB9 | 250.56 | 0.07477%
IS20INV3M1SCB10 | 0 | 0%
IS20INV3M2SCB1 | 250.56 | 0.07477%
IS20INV3M2SCB2 | 250.56 | 0.07477%
IS20INV3M2SCB3 | 250.56 | 0.07477%
IS20INV3M2SCB4 | 250.56 | 0.07477%
IS20INV3M2SCB5 | 250.56 | 0.07477%
IS20INV3M2SCB6 | 250.56 | 0.07477%
IS20INV3M2SCB7 | 250.56 | 0.07477%
IS20INV3M2SCB8 | 250.56 | 0.07477%
IS20INV3M2SCB9 | 0 | 0%
IS20INV3M2SCB10 | 0 | 0%
IS20INV4M1SCB1 | 250.56 | 0.07477%
IS20INV4M1SCB2 | 250.56 | 0.07477%
IS20INV4M1SCB3 | 250.56 | 0.07477%
IS20INV4M1SCB4 | 250.56 | 0.07477%
IS20INV4M1SCB5 | 250.56 | 0.07477%
IS20INV4M1SCB6 | 250.56 | 0.07477%
IS20INV4M1SCB7 | 250.56 | 0.07477%
IS20INV4M1SCB8 | 250.56 | 0.07477%
IS20INV4M1SCB9 | 250.56 | 0.07477%
IS20INV4M1SCB10 | 0 | 0%
IS20INV4M2SCB1 | 250.56 | 0.07477%
IS20INV4M2SCB2 | 250.56 | 0.07477%
IS20INV4M2SCB3 | 250.56 | 0.07477%
IS20INV4M2SCB4 | 250.56 | 0.07477%
IS20INV4M2SCB5 | 250.56 | 0.07477%
IS20INV4M2SCB6 | 250.56 | 0.07477%
IS20INV4M2SCB7 | 250.56 | 0.07477%
IS20INV4M2SCB8 | 250.56 | 0.07477%
IS20INV4M2SCB9 | 0 | 0%
IS20INV4M2SCB10 | 0 | 0%
IS1Tx | 16789.405 | 5.01%
IS2Tx | 16699.07 | 4.983%
IS3Tx | 16766.64 | 5.004%
IS4Tx | 16547.4 | 4.938%
IS5Tx | 16724.88 | 4.991%
IS6Tx | 17170.9 | 5.124%
IS7Tx | 16443 | 4.907%
IS8Tx | 16928.46 | 5.052%
IS9Tx | 16942.96 | 5.056%
IS10Tx | 16756.2 | 5%
IS11Tx | 16595.25 | 4.952%
IS12Tx | 16912.8 | 5.047%
IS13Tx | 16599.6 | 4.954%
IS14Tx | 16756.2 | 5%
IS15Tx | 16756.2 | 5%
IS16Tx | 16474.32 | 4.916%
IS17Tx | 15456.42 | 4.613%
IS18Tx | 16662.24 | 4.972%
IS19Tx | 17570.52 | 5.244%
IS20Tx | 17539.2 | 5.234%
IS1MVP | 16789.405 | 5.01%
IS2MVP | 16699.07 | 4.983%
IS3MVP | 16766.64 | 5.004%
IS4MVP | 16547.4 | 4.938%
IS5MVP | 16724.88 | 4.991%
IS6MVP | 17170.9 | 5.124%
IS7MVP | 16443 | 4.907%
IS8MVP | 16928.46 | 5.052%
IS9MVP | 16942.96 | 5.056%
IS10MVP | 16756.2 | 5%
IS11MVP | 16595.25 | 4.952%
IS12MVP | 16912.8 | 5.047%
IS13MVP | 16599.6 | 4.954%
IS14MVP | 16756.2 | 5%
IS15MVP | 16756.2 | 5%
IS16MVP | 16474.32 | 4.916%
IS17MVP | 15456.42 | 4.613%
IS18MVP | 16662.24 | 4.972%
IS19MVP | 17570.52 | 5.244%
IS20MVP | 17539.2 | 5.234%
IS1AuxTx | 16789.405 | 5.01%
IS2AuxTx | 16699.07 | 4.983%
IS3AuxTx | 16766.64 | 5.004%
IS4AuxTx | 16547.4 | 4.938%
IS5AuxTx | 16724.88 | 4.991%
IS6AuxTx | 17170.9 | 5.124%
IS7AuxTx | 16443 | 4.907%
IS8AuxTx | 16928.46 | 5.052%
IS9AuxTx | 16942.96 | 5.056%
IS10AuxTx | 16756.2 | 5%
IS11AuxTx | 16595.25 | 4.952%
IS12AuxTx | 16912.8 | 5.047%
IS13AuxTx | 16599.6 | 4.954%
IS14AuxTx | 16756.2 | 5%
IS15AuxTx | 16756.2 | 5%
IS16AuxTx | 16474.32 | 4.916%
IS17AuxTx | 15456.42 | 4.613%
IS18AuxTx | 16662.24 | 4.972%
IS19AuxTx | 17570.52 | 5.244%
IS20AuxTx | 17539.2 | 5.234%
MCR_MVP_Inc1 | 35109.72 | 10.48% | Incomer | Incomer 12 | Incomer 11 | Incomer 10 | Incomer 8 | Incomer 9 | Incomer 5 |  |  | Incomer 4 | Incomer 3 | Incomer 2 | Incomer 1
MCR_MVP_Inc2 | 32118.66 | 9.585% | DC Capacity (kwh) | 33307.805 | 33236.03 | 33870.55 | 33293.16 | 33667.26 | 33491.665 |  |  | 33340.14 | 33199.2 | 32103 | 35001.72
MCR_MVP_Inc3 | 33230.52 | 9.917% | Block | IR1-IR2 | IR3-IR4 | IR5-IR6 | IR8-IR7 | IR9-IR10 | IR12-IR11 |  |  | IR13-IR14 | IR15-IR16 | IR17-IR18 | IR19-IR20
MCR_MVP_Inc4 | 33355.8 | 9.954% | Full Load current | 613.4057 | 612.0839 | 623.7694 | 613.136 | 620.0256 | 616.7918 |  |  | 614.0012 | 611.4056 | 591.2177 | 644.6014
MCR_MVP_Inc5 | 33508.05 | 10%
MCR_MVP_Inc8 | 33371.46 | 9.959% | MCR_MVP_Inc1 | 35109.72 | Block | Full Load current
MCR_MVP_Inc9 | 33699.16 | 10.06% | MCR_MVP_Inc10 | 33895.78 | IR1-IR2 | 613.4057
MCR_MVP_Inc10 | 33895.78 | 10.12% | MCR_MVP_Inc11 | 33314.04 | IR3-IR4 | 612.0839
MCR_MVP_Inc11 | 33314.04 | 9.942% | MCR_MVP_Inc12 | 33488.475 | IR5-IR6 | 623.7694
MCR_MVP_Inc12 | 33488.475 | 9.994% | MCR_MVP_Inc2 | 32118.66 | IR8-IR7 | 613.136
MCR_MVP_OG1 | 167322.75 | 49.93% | MCR_MVP_Inc3 | 33230.52 | IR9-IR10 | 620.0256
MCR_MVP_OG2 | 167768.915 | 50.07% | MCR_MVP_Inc4 | 33355.8 | IR12-IR11 | 616.7918
Power_Tx1 | 167322.75 | 49.93% | MCR_MVP_Inc5 | 33508.05 | IR13-IR14 | 614.0012
Power_Tx2 | 167768.915 | 50.07% | MCR_MVP_Inc8 | 33371.46 | IR15-IR16 | 611.4056
Line_Bay1 | 335091.665 | 100% | MCR_MVP_Inc9 | 33699.16 | IR17-IR18 | 591.2177
Str_Typ1(445*29) | 12.905 | 0.003851% |  |  | IR19-IR20 | 644.6014
Str_Typ2 (450*29) | 13.05 | 0.003894%
Str_Typ3(535*29) | 15.515 | 0.00463%
Str_Typ4(540*29) | 15.66 | 0.004673%
Str_Typ5(545*29) | 15.805 | 0.004717%
Str_Typ6(445*58) | 25.81 | 0.007702%
Str_Typ7(450*58) | 26.1 | 0.007789%
Str_Typ8(535*58) | 31.03 | 0.00926%
Str_Typ9(540*58) | 31.32 | 0.009347%
Str_Typ10(545*58) | 31.61 | 0.009433%

## Inv_SY_B (hidden)
| 2013.18 | 2090.61 | 2090.61 | 2077.705 | 2090.61 | 2090.61 | 2090.61 | 2193.85 | 2090.61 | 2136.43 | 2064.8 | 2090.61 | 2064.8 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2111.49 | 2114.1 | 2061.9 | 2088 | 2088 | 1853.1 | 2111.49 | 2114.1 | 2114.1 | 2088 | 2061.9 | 2114.1 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2234.16 | 1985.92 | 2203.13 | 1954.89 | 2161.08 | 2442.96 | 1954.89 | 2234.16 | 1973.16 | 2020.14 | 2145.42 | 2004.48 | 2223.72 | 1973.16 | 2223.72 | 1973.16 | 1973.16 | 2270.84 | 1973.16 | 2239.52 | 2223.72 | 1973.16 | 2192.4 | 2088 | 2102.065 | 1991.43 | 2102.065 | 2212.7 | 2275.33 | 2023.04 | 2244.31 | 1959.82 | 2161.08 | 2129.76 | 1973.16 | 2239.38 | 1941.84 | 2255.04 | 1973.16 | 2223.72 | 2023.04 | 2196.595 | 2054.65 | 2275.92 | 2023.04 | 2181.09 | 2023.04 | 1785.965 | 2192.4 | 2129.76 | 1941.84 | 2255.04 | 2192.4 | 2004.48 | 2004.48 | 2208.06 | 1957.5 | 2035.8 | 2239.38 | 1941.84 | 2255.04 | 1941.84 | 2192.4 | 2004.48 | 2223.72 | 1910.52 | 2223.72 | 2004.48 | 2192.4 | 2004.48 | 2192.4 | 2004.48 | 1973.15 | 2192.4 | 2004.48 | 1941.84 | 2208.06 | 2223.72 | 2192.4 | 2004.48 | 2223.72 | 1973.16 | 2129.76 | 1973.16 | 2098.44 | 1847.88 | 2161.08 | 1973.16 | 2004.48 | 2004.48 | 1988.82 | 1722.6 | 1973.16 | 1753.92 | 2004.48 | 2004.48 | 2255.04 | 1941.84 | 2255.04 | 1973.16 | 2223.72 | 1973.16 | 2004.48 | 2004.48 | 2161.08 | 2255.04 | 2223.72 | 2223.72 | 2223.72 | 2255.04 | 2004.48 | 2223.72 | 2239.38 | 2255.04 | 2255.04 | 2255.04 | 2255.04 | 2004.48 | 2255.04 | 2004.48 | 335033.045
| 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 268
Date | IS1_INV1_M1 | IS1_INV1_M2 | IS1_INV2_M1 | IS1_INV2_M2 | IS1_INV3_M1 | IS1_INV3_M2 | IS1_INV4_M1 | IS1_INV4_M2 | IS2_INV1_M1 | IS2_INV1_M2 | IS2_INV2_M1 | IS2_INV2_M2 | IS2_INV3_M1 | IS2_INV3_M2 | IS2_INV4_M1 | IS2_INV4_M2 | IS3_INV1_M1 | IS3_INV1_M2 | IS3_INV2_M1 | IS3_INV2_M2 | IS3_INV3_M1 | IS3_INV3_M2 | IS3_INV4_M1 | IS3_INV4_M2 | IS4_INV1_M1 | IS4_INV1_M2 | IS4_INV2_M1 | IS4_INV2_M2 | IS4_INV3_M1 | IS4_INV3_M2 | IS4_INV4_M1 | IS4_INV4_M2 | IS5_INV1_M1 | IS5_INV1_M2 | IS5_INV2_M1 | IS5_INV2_M2 | IS5_INV3_M1 | IS5_INV3_M2 | IS5_INV4_M1 | IS5_INV4_M2 | IS6_INV1_M1 | IS6_INV1_M2 | IS6_INV2_M1 | IS6_INV2_M2 | IS6_INV3_M1 | IS6_INV3_M2 | IS6_INV4_M1 | IS6_INV4_M2 | IS7_INV1_M1 | IS7_INV1_M2 | IS7_INV2_M1 | IS7_INV2_M2 | IS7_INV3_M1 | IS7_INV3_M2 | IS7_INV4_M1 | IS7_INV4_M2 | IS8_INV1_M1 | IS8_INV1_M2 | IS8_INV2_M1 | IS8_INV2_M2 | IS8_INV3_M1 | IS8_INV3_M2 | IS8_INV4_M1 | IS8_INV4_M2 | IS9_INV1_M1 | IS9_INV1_M2 | IS9_INV2_M1 | IS9_INV2_M2 | IS9_INV3_M1 | IS9_INV3_M2 | IS9_INV4_M1 | IS9_INV4_M2 | IS10_INV1_M1 | IS10_INV1_M2 | IS10_INV2_M1 | IS10_INV2_M2 | IS10_INV3_M1 | IS10_INV3_M2 | IS10_INV4_M1 | IS10_INV4_M2 | IS11_INV1_M1 | IS11_INV1_M2 | IS11_INV2_M1 | IS11_INV2_M2 | IS11_INV3_M1 | IS11_INV3_M2 | IS11_INV4_M1 | IS11_INV4_M2 | IS12_INV1_M1 | IS12_INV1_M2 | IS12_INV2_M1 | IS12_INV2_M2 | IS12_INV3_M1 | IS12_INV3_M2 | IS12_INV4_M1 | IS12_INV4_M2 | IS13_INV1_M1 | IS13_INV1_M2 | IS13_INV2_M1 | IS13_INV2_M2 | IS13_INV3_M1 | IS13_INV3_M2 | IS13_INV4_M1 | IS13_INV4_M2 | IS14_INV1_M1 | IS14_INV1_M2 | IS14_INV2_M1 | IS14_INV2_M2 | IS14_INV3_M1 | IS14_INV3_M2 | IS14_INV4_M1 | IS14_INV4_M2 | IS15_INV1_M1 | IS15_INV1_M2 | IS15_INV2_M1 | IS15_INV2_M2 | IS15_INV3_M1 | IS15_INV3_M2 | IS15_INV4_M1 | IS15_INV4_M2 | IS16_INV1_M1 | IS16_INV1_M2 | IS16_INV2_M1 | IS16_INV2_M2 | IS16_INV3_M1 | IS16_INV3_M2 | IS16_INV4_M1 | IS16_INV4_M2 | IS17_INV1_M1 | IS17_INV1_M2 | IS17_INV2_M1 | IS17_INV2_M2 | IS17_INV3_M1 | IS17_INV3_M2 | IS17_INV4_M1 | IS17_INV4_M2 | IS18_INV1_M1 | IS18_INV1_M2 | IS18_INV2_M1 | IS18_INV2_M2 | IS18_INV3_M1 | IS18_INV3_M2 | IS18_INV4_M1 | IS18_INV4_M2 | IS19_INV1_M1 | IS19_INV1_M2 | IS19_INV2_M1 | IS19_INV2_M2 | IS19_INV3_M1 | IS19_INV3_M2 | IS19_INV4_M1 | IS19_INV4_M2 | IS20_INV1_M1 | IS20_INV1_M2 | IS20_INV2_M1 | IS20_INV2_M2 | IS20_INV3_M1 | IS20_INV3_M2 | IS20_INV4_M1 | IS20_INV4_M2 | Plant
2025-06-09 | 6.2082 | 6.2549 | 6.2755 | 6.2731 | 6.337 | 6.3233 | 6.3544 | 6.2452 | 6.2968 | 6.1754 | 6.3006 | 6.2729 | 6.3731 | 6.2456 | 6.3101 | 6.3396 | 6.2754 | 6.2858 | 6.2939 | 6.3444 | 6.2421 | 6.2327 | 6.274 | 6.246 | 6.1765 | 6.0893 | 6.089 | 6.0819 | 6.2212 | 6.2068 | 6.2982 | 6.2482 | 6.3258 | 6.3387 | 6.4106 | 6.3492 | 6.3586 | 6.2677 | 6.2784 | 6.2607 | 6.2616 | 6.4436 | 6.2864 | 6.4328 | 6.1312 | 5.9104 | 6.4444 | 6.275 | 6.7118 | 6.6533 | 6.1825 | 6.2681 | 6.126 | 6.8231 | 6.0845 | 6.7984 | 6.1022 | 6.0418 | 6.1227 | 6.1165 | 6.0997 | 6.1086 | 6.0359 | 6.0351 | 6.1374 | 6.0795 | 6.0852 | 6.0267 | 5.9912 | 6.0975 | 6.0005 | 6.0437 | 6.0798 | 6.0598 | 6.1701 | 6.0044 | 6.1456 | 6.0885 | 6.1846 | 6.0657 | 6.1139 | 6.0598 | 6.075 | 6.0057 | 6.1156 | 6.0283 | 6.1229 | 6.092 | 6.1008 | 6.0847 | 6.1874 | 6.1091 | 6.1229 | 6.2299 | 6.1618 | 6.1145 | 6.2259 | 6.2421 | 6.1092 | 6.261 | 6.0736 | 6.2523 | 6.1224 | 6.1965 | 6.0645 | 6.1529 | 6.1002 | 6.1494 | 6.1045 | 6.1156 | 6.1527 | 6.2384 | 6.165 | 6.1078 | 6.1585 | 6.2183 | 6.103 | 6.0986 | 6.108 | 6.1522 | 6.0665 | 6.1617 | 6.211 | 6.2272 | 6.2175 | 6.161 | 6.1167 | 6.1661 | 6.1485 | 6.1851 | 6.1185 | 6.1001 | 6.1365 | 6.0662 | 6.0748 | 6.0923 | 6.2054 | 6.4375 | 6.2305 | 6.4695 | 6.2665 | 6.3673 | 6.3861 | 6.2236 | 6.3337 | 6.2633 | 6.268 | 6.2461 | 6.2395 | 6.1706 | 6.4351 | 6.2781 | 6.254 | 6.2105 | 6.2182 | 6.1978 | 6.2166 | 6.403 | 6.2433 | 6.4373 | 6.2052
2025-06-10 | 6.1615 | 6.2111 | 6.236 | 6.231 | 6.3038 | 6.2842 | 6.3079 | 6.2252 | 6.2578 | 6.1379 | 6.257 | 6.2327 | 6.3355 | 6.2032 | 6.2658 | 6.3022 | 6.2364 | 6.2506 | 6.2542 | 6.3035 | 6.206 | 6.1928 | 6.2354 | 6.2068 | 6.1385 | 6.0399 | 6.0456 | 6.0404 | 6.1851 | 6.1676 | 6.2578 | 6.2161 | 6.2775 | 6.2926 | 6.3671 | 6.3006 | 6.326 | 6.2345 | 6.2481 | 6.2284 | 6.2404 | 6.3952 | 6.2633 | 6.3847 | 6.1008 | 5.8962 | 6.3929 | 6.2565 | 6.6721 | 6.6133 | 6.1417 | 6.2154 | 6.0926 | 6.7788 | 6.0513 | 6.7642 | 6.0547 | 6.0089 | 6.0763 | 6.083 | 6.0627 | 6.061 | 6.0143 | 6.0114 | 6.1066 | 6.0323 | 6.0397 | 5.9935 | 5.9605 | 6.0512 | 5.967 | 5.9969 | 6.0402 | 6.016 | 6.1158 | 5.9667 | 6.0964 | 6.0527 | 6.1449 | 6.0356 | 6.0704 | 6.0244 | 6.038 | 5.9847 | 6.0754 | 6.0029 | 6.0888 | 6.0522 | 6.079 | 6.0529 | 6.1419 | 6.0904 | 6.1115 | 6.22 | 6.16 | 6.1123 | 6.2085 | 6.2007 | 6.1003 | 6.2137 | 6.0654 | 6.2081 | 6.1027 | 6.1607 | 6.0473 | 6.1161 | 6.0769 | 6.107 | 6.0811 | 6.0746 | 6.1268 | 6.1999 | 6.1172 | 6.0793 | 6.1169 | 6.1805 | 6.095 | 6.0776 | 6.0818 | 6.0959 | 6.0424 | 6.1144 | 6.1811 | 6.1877 | 6.2028 | 6.1211 | 6.0852 | 6.12 | 6.0974 | 6.1252 | 6.0838 | 6.0477 | 6.117 | 6.0764 | 6.0464 | 6.0673 | 6.1946 | 6.3947 | 6.2215 | 6.429 | 6.2627 | 6.346 | 6.3671 | 6.196 | 6.3105 | 6.2432 | 6.2603 | 6.2327 | 6.2265 | 6.1609 | 6.3996 | 6.2687 | 6.2502 | 6.2052 | 6.2096 | 6.1943 | 6.2108 | 6.3719 | 6.2341 | 6.4104 | 6.1733
2025-06-11 | 6.3062 | 6.3504 | 6.3756 | 6.3843 | 6.4397 | 6.4302 | 6.4697 | 6.3479 | 6.4146 | 6.2895 | 6.4066 | 6.3776 | 6.484 | 6.3437 | 6.4132 | 6.4433 | 6.3817 | 6.3929 | 6.406 | 6.4562 | 6.3573 | 6.344 | 6.3815 | 6.3536 | 6.2837 | 6.1865 | 6.1882 | 6.184 | 6.3393 | 6.3341 | 6.4097 | 6.362 | 5.8283 | 5.8391 | 5.9055 | 5.8508 | 5.8915 | 5.8109 | 5.8193 | 5.791 | 6.3588 | 6.5521 | 6.3931 | 6.5425 | 6.2616 | 5.9964 | 6.5621 | 6.369 | 6.8184 | 6.7589 | 6.2883 | 6.3705 | 6.2221 | 6.9376 | 6.1905 | 6.9249 | 6.2084 | 6.1465 | 6.2241 | 6.2132 | 6.193 | 6.2067 | 6.1483 | 6.1564 | 6.2434 | 6.1794 | 6.1823 | 6.1323 | 6.088 | 6.1967 | 6.1029 | 6.1359 | 6.1838 | 6.1553 | 6.2658 | 6.0987 | 6.2383 | 6.1779 | 6.2825 | 6.1608 | 6.2207 | 6.1645 | 6.1771 | 6.1198 | 6.2183 | 6.142 | 6.2329 | 6.2008 | 6.1995 | 6.1954 | 6.2882 | 6.2142 | 6.245 | 6.3538 | 6.2811 | 6.2422 | 6.353 | 6.353 | 6.2332 | 6.3588 | 6.2006 | 6.3593 | 6.2481 | 6.3027 | 6.187 | 6.2559 | 6.2141 | 6.2519 | 6.2302 | 6.2169 | 6.2699 | 6.349 | 6.2619 | 6.2125 | 6.2647 | 6.3237 | 6.218 | 6.2056 | 6.2197 | 6.2503 | 6.1778 | 6.2591 | 6.3271 | 6.3415 | 6.3449 | 6.2592 | 6.2312 | 6.2631 | 6.2345 | 6.2569 | 6.2318 | 6.1813 | 6.2413 | 6.2038 | 6.1532 | 6.1807 | 6.3172 | 6.5399 | 6.3485 | 6.5792 | 6.3918 | 6.4971 | 6.5171 | 6.3364 | 6.4636 | 6.385 | 6.3866 | 6.3585 | 6.3523 | 6.2833 | 6.5426 | 6.3936 | 6.3751 | 6.3286 | 6.3358 | 6.3154 | 6.3367 | 6.5127 | 6.3638 | 6.551 | 6.2841
2025-06-12 | 6.0253 | 6.0019 | 6.0304 | 6.0537 | 6.0848 | 6.0851 | 6.0789 | 5.9243 | 6.0552 | 5.9273 | 6.0547 | 6.0161 | 6.1308 | 5.9899 | 6.0675 | 6.0859 | 6.0221 | 6.0357 | 6.0452 | 6.0992 | 5.9937 | 5.9972 | 6.0566 | 6.0163 | 5.9638 | 6.0242 | 5.8816 | 5.8707 | 5.9922 | 6.0077 | 6.0741 | 5.9974 | 6.3294 | 6.3391 | 6.4066 | 6.347 | 6.1003 | 6.0345 | 6.038 | 6.0151 | 5.9261 | 6.2369 | 5.9636 | 6.2486 | 5.9084 | 5.5766 | 6.2533 | 5.9298 | 6.4398 | 6.3717 | 5.9421 | 6.0943 | 5.8484 | 6.5308 | 5.8174 | 6.5159 | 5.9763 | 5.7617 | 5.9977 | 5.8326 | 5.8255 | 5.9757 | 5.7901 | 5.8571 | 5.922 | 5.9366 | 5.8886 | 5.775 | 5.7009 | 5.9346 | 5.7304 | 5.9268 | 5.8406 | 5.8494 | 6.0192 | 5.7348 | 6.0236 | 5.7873 | 6.0359 | 5.7944 | 5.9627 | 5.812 | 5.9119 | 5.7307 | 5.9629 | 5.8111 | 5.9461 | 6.0652 | 5.8424 | 5.8645 | 6.0638 | 5.8121 | 5.8674 | 6.0772 | 5.9997 | 5.8343 | 6.0886 | 6.0609 | 5.8316 | 6.1083 | 5.8008 | 6.1195 | 5.8852 | 6.0449 | 5.8039 | 6.051 | 5.8332 | 5.9944 | 5.8671 | 5.9676 | 5.886 | 6.0812 | 6.0239 | 5.8548 | 5.9981 | 6.0928 | 5.8463 | 5.8254 | 5.8479 | 6.0017 | 5.8001 | 6.0209 | 5.9679 | 6.0883 | 5.9971 | 6.0931 | 5.8907 | 6.036 | 5.9979 | 6.016 | 5.9798 | 6.0825 | 5.9564 | 6.0668 | 5.9267 | 5.9484 | 5.8952 | 6.2617 | 5.9132 | 6.2768 | 5.9548 | 6.2012 | 6.1871 | 6.0721 | 6.0532 | 5.9281 | 5.9771 | 5.9476 | 5.9417 | 5.8706 | 6.2348 | 5.9674 | 5.9519 | 5.9054 | 5.9065 | 5.8956 | 5.9128 | 6.2131 | 5.9384 | 6.244 | 5.9871
2025-06-13 | 4.6664 | 4.5851 | 4.6019 | 4.6266 | 4.6366 | 4.633 | 4.6287 | 4.4782 | 4.6113 | 4.496 | 4.6337 | 4.5892 | 4.6921 | 4.5757 | 4.6502 | 4.6557 | 4.612 | 4.6208 | 4.622 | 4.6765 | 4.5852 | 4.5896 | 4.6769 | 4.6249 | 4.585 | 4.9 | 4.5286 | 4.5147 | 4.5846 | 4.6166 | 4.6817 | 4.5823 | 6.0139 | 6.0388 | 6.1056 | 6.0412 | 4.6562 | 4.6237 | 4.6218 | 4.6068 | 4.4719 | 4.8351 | 4.5079 | 4.8801 | 4.532 | 4.1881 | 4.8571 | 4.4653 | 4.9153 | 4.8447 | 4.5444 | 4.7517 | 4.4412 | 4.9662 | 4.4214 | 4.9608 | 4.7372 | 4.3553 | 4.7725 | 4.4113 | 4.4137 | 4.739 | 4.3944 | 4.5153 | 4.5536 | 4.6974 | 4.5409 | 4.3975 | 4.3015 | 4.6475 | 4.336 | 4.7351 | 4.4548 | 4.4901 | 4.7368 | 4.3327 | 4.7734 | 4.3544 | 4.7403 | 4.3743 | 4.6701 | 4.4262 | 4.6188 | 4.3378 | 4.6775 | 4.4528 | 4.6527 | 5.0485 | 4.4592 | 4.5157 | 4.8216 | 4.4049 | 4.4659 | 4.7466 | 4.7067 | 4.4376 | 4.818 | 4.7177 | 4.4288 | 4.8498 | 4.4146 | 4.868 | 4.5169 | 4.7746 | 4.4396 | 4.88 | 4.463 | 4.7401 | 4.5032 | 4.7364 | 4.5164 | 4.8048 | 4.7768 | 4.4789 | 4.7471 | 4.8633 | 4.4774 | 4.4528 | 4.4873 | 4.7568 | 4.4367 | 4.7932 | 4.5991 | 4.8219 | 4.6353 | 5.0124 | 4.5395 | 4.8241 | 4.7554 | 4.7518 | 4.7669 | 5.1836 | 4.7522 | 5.1137 | 4.7158 | 4.7218 | 4.4587 | 4.8922 | 4.4626 | 4.8663 | 4.5023 | 4.8307 | 4.7876 | 4.7557 | 4.574 | 4.4326 | 4.4976 | 4.4882 | 4.5007 | 4.4477 | 4.8137 | 4.5002 | 4.4391 | 4.4116 | 4.4049 | 4.3987 | 4.4217 | 4.7739 | 4.4523 | 4.7866 | 4.6476
2025-06-14 | 1.5114 | 1.52 | 1.5244 | 1.5201 | 1.5358 | 1.5466 | 1.5545 | 1.5096 | 1.5494 | 1.5281 | 1.5327 | 1.5288 | 1.5553 | 1.5175 | 1.551 | 1.5546 | 1.5475 | 1.5308 | 1.5495 | 1.5672 | 1.5519 | 1.5244 | 1.5511 | 1.5459 | 1.5223 | 1.4996 | 1.4957 | 1.491 | 1.5486 | 1.5568 | 1.5684 | 1.5606 | 1.5868 | 1.5956 | 1.6045 | 1.5865 | 1.5917 | 1.5605 | 1.5765 | 1.5638 | 1.5929 | 1.6063 | 1.6212 | 1.6084 | 1.5599 | 1.557 | 1.6031 | 1.6112 | 1.6527 | 1.6404 | 1.5188 | 1.5431 | 1.5125 | 1.695 | 1.5259 | 1.6993 | 1.5054 | 1.5258 | 1.5028 | 1.5289 | 1.5205 | 1.5059 | 1.4936 | 1.4876 | 1.5251 | 1.5195 | 1.5154 | 1.5287 | 1.5145 | 1.5342 | 1.5127 | 1.4968 | 1.5279 | 1.5046 | 1.5333 | 1.5245 | 1.5224 | 1.5416 | 1.5159 | 1.5358 | 1.5389 | 1.5435 | 1.5465 | 1.5262 | 1.541 | 1.5366 | 1.553 | 1.5358 | 1.5819 | 1.558 | 1.5656 | 1.5816 | 1.5683 | 1.58 | 1.5594 | 1.5884 | 1.6038 | 1.5974 | 1.6017 | 1.6095 | 1.593 | 1.6074 | 1.5895 | 1.5947 | 1.6013 | 1.5909 | 1.6078 | 1.5968 | 1.6005 | 1.5905 | 1.6284 | 1.6154 | 1.5996 | 1.6065 | 1.6 | 1.6095 | 1.6197 | 1.6146 | 1.6168 | 1.609 | 1.6154 | 1.6194 | 1.6388 | 1.6229 | 1.6439 | 1.6172 | 1.6179 | 1.6298 | 1.6192 | 1.6403 | 1.6236 | 1.604 | 1.6025 | 1.6071 | 1.5936 | 1.6124 | 1.6589 | 1.6582 | 1.6805 | 1.6765 | 1.6783 | 1.6698 | 1.6559 | 1.6171 | 1.6556 | 1.6616 | 1.6394 | 1.6422 | 1.6484 | 1.6386 | 1.6606 | 1.6711 | 1.6449 | 1.6462 | 1.6613 | 1.644 | 1.6463 | 1.6466 | 1.6494 | 1.6474 | 1.58
2025-06-15 | 2.6044 | 2.6407 | 2.6415 | 2.6296 | 2.6716 | 2.6736 | 2.6857 | 2.6386 | 2.6538 | 2.6164 | 2.6225 | 2.6151 | 2.666 | 2.5902 | 2.6696 | 2.6686 | 2.6578 | 2.6375 | 2.6534 | 2.6795 | 2.6492 | 2.6093 | 2.65 | 2.635 | 2.595 | 2.5533 | 2.5492 | 2.5471 | 2.631 | 2.6375 | 2.6487 | 2.6435 | 2.6476 | 2.669 | 2.7111 | 2.6759 | 2.6815 | 2.6323 | 2.6495 | 2.6178 | 2.6989 | 2.6975 | 2.7153 | 2.6984 | 2.6247 | 2.6291 | 2.7076 | 2.7163 | 2.8191 | 2.7996 | 2.5949 | 2.6227 | 2.5997 | 2.9011 | 2.5933 | 2.8797 | 2.5537 | 2.5803 | 2.5687 | 2.5941 | 2.5811 | 2.574 | 2.528 | 2.5204 | 2.5726 | 2.5588 | 2.5605 | 2.5581 | 2.5616 | 2.5813 | 2.5017 | 2.5209 | 2.5828 | 2.5513 | 2.5982 | 2.5772 | 2.579 | 2.6105 | 2.5852 | 2.6011 | 2.5622 | 2.5778 | 2.5552 | 2.5299 | 2.5524 | 2.5338 | 2.5813 | 2.5346 | 2.6249 | 2.5706 | 2.5855 | 2.6174 | 2.5883 | 2.6096 | 2.5771 | 2.6187 | 2.604 | 2.5853 | 2.5958 | 2.6059 | 2.5956 | 2.6108 | 2.589 | 2.5943 | 2.5924 | 2.5807 | 2.5974 | 2.5705 | 2.5873 | 2.5657 | 2.6206 | 2.5904 | 2.5664 | 2.5895 | 2.5772 | 2.5982 | 2.5972 | 2.5809 | 2.5843 | 2.4987 | 2.5675 | 2.57 | 2.6171 | 2.5935 | 2.6236 | 2.556 | 2.5644 | 2.5694 | 2.5602 | 2.585 | 2.5607 | 2.5377 | 2.5294 | 2.5383 | 2.5442 | 2.5644 | 2.6669 | 2.6598 | 2.6896 | 2.6718 | 2.6675 | 2.6385 | 2.6279 | 2.6215 | 2.6752 | 2.6772 | 2.6583 | 2.651 | 2.6613 | 2.6363 | 2.6688 | 2.6849 | 2.6757 | 2.6852 | 2.709 | 2.6768 | 2.6852 | 2.6696 | 2.6778 | 2.6783 | 2.6182
2025-06-16 | 5.0201 | 5.0939 | 5.0972 | 5.0778 | 5.1446 | 5.1707 | 5.1643 | 5.0397 | 5.1247 | 4.9604 | 5.1165 | 5.053 | 5.1554 | 5.0163 | 5.1105 | 5.1395 | 5.092 | 5.1256 | 5.1119 | 5.1487 | 5.0884 | 5.0686 | 5.105 | 5.0803 | 4.999 | 4.9222 | 4.6958 | 4.8289 | 5.0858 | 5.0614 | 5.1016 | 5.0771 | 5.0834 | 5.1536 | 5.1852 | 5.141 | 5.1573 | 5.071 | 5.0773 | 5.0524 | 5.1006 | 5.2028 | 5.1265 | 5.1919 | 4.996 | 4.9031 | 5.2376 | 5.1478 | 5.4436 | 5.4024 | 5.0161 | 5.0582 | 4.9872 | 5.5224 | 4.9512 | 5.5126 | 4.9599 | 4.9437 | 4.9947 | 4.9829 | 4.9654 | 4.9907 | 4.8779 | 4.8801 | 4.9113 | 4.8333 | 4.8946 | 4.8025 | 4.8661 | 4.854 | 4.7162 | 4.7826 | 4.9373 | 4.862 | 5.0165 | 4.8676 | 4.9737 | 4.9635 | 5.004 | 4.933 | 4.8526 | 4.8359 | 4.8148 | 4.8094 | 4.8488 | 4.7861 | 4.8569 | 4.8565 | 4.9235 | 4.8558 | 4.9641 | 4.9264 | 4.9131 | 5.0113 | 4.9564 | 4.9268 | 4.9662 | 4.9673 | 4.9377 | 5.0279 | 4.9299 | 5.0379 | 4.9413 | 5.0005 | 4.9349 | 4.9753 | 4.9698 | 4.9372 | 4.9723 | 4.9607 | 5.0028 | 5.0228 | 4.9402 | 4.887 | 4.8695 | 4.9549 | 4.9047 | 4.859 | 4.8744 | 4.8789 | 4.825 | 4.876 | 4.9553 | 4.9866 | 4.9641 | 4.887 | 4.8404 | 4.8729 | 4.8561 | 4.88 | 4.8355 | 4.8377 | 4.7735 | 4.8368 | 4.7259 | 4.7648 | 4.8736 | 4.948 | 4.8543 | 4.9356 | 4.8963 | 4.8581 | 4.8713 | 4.8358 | 4.8204 | 4.7879 | 4.8247 | 4.8082 | 4.8503 | 4.829 | 4.8854 | 4.8346 | 4.7883 | 4.7656 | 4.7231 | 4.7168 | 4.74 | 4.7655 | 4.794 | 4.83 | 4.9612
2025-06-17 | 3.7051 | 3.6704 | 3.6633 | 3.6847 | 3.6817 | 3.6998 | 3.6973 | 3.5783 | 3.6752 | 3.5776 | 3.8024 | 3.6412 | 3.8215 | 3.6477 | 3.7442 | 3.75 | 3.7064 | 3.7086 | 3.7126 | 3.7656 | 3.6762 | 3.6764 | 3.72 | 3.6937 | 3.6467 | 3.893 | 3.6317 | 3.6157 | 3.6491 | 3.6404 | 3.703 | 3.6435 | 4.8313 | 4.8637 | 4.9386 | 4.8979 | 3.7008 | 3.6729 | 3.6741 | 3.6602 | 3.6 | 3.8501 | 3.6222 | 3.8833 | 3.6007 | 3.3626 | 3.8542 | 3.5921 | 3.951 | 3.8864 | 3.6571 | 3.7752 | 3.5838 | 4.0006 | 3.5419 | 3.982 | 3.7454 | 3.4955 | 3.7714 | 3.5263 | 3.5283 | 3.7488 | 3.5177 | 3.6091 | 3.6182 | 3.7084 | 3.6062 | 3.5006 | 3.4503 | 3.6718 | 3.4612 | 3.7287 | 3.5625 | 3.5801 | 3.7653 | 3.4945 | 3.8082 | 3.5087 | 3.779 | 3.5368 | 3.6895 | 3.5294 | 3.6681 | 3.466 | 3.7024 | 3.5491 | 3.6882 | 3.9652 | 3.6 | 3.6189 | 3.8351 | 3.5365 | 3.5766 | 3.7737 | 3.7367 | 3.5658 | 3.8176 | 3.743 | 3.5341 | 3.8202 | 3.517 | 3.8147 | 3.5604 | 3.7467 | 3.5123 | 3.8141 | 3.5303 | 3.713 | 3.5527 | 3.709 | 3.5639 | 3.7645 | 3.7628 | 3.5421 | 3.7082 | 3.799 | 3.5274 | 3.5079 | 3.5248 | 3.707 | 3.4906 | 3.7359 | 3.6092 | 3.7694 | 3.6417 | 3.8895 | 3.559 | 3.7626 | 3.7357 | 3.7491 | 3.6954 | 4.0112 | 3.746 | 4.0316 | 3.7811 | 3.8013 | 3.6065 | 3.9034 | 3.6372 | 3.9115 | 3.6681 | 3.881 | 3.8527 | 3.831 | 3.7509 | 3.6532 | 3.6903 | 3.6807 | 3.6725 | 3.615 | 3.8868 | 3.6887 | 3.6711 | 3.6386 | 3.628 | 3.6292 | 3.6442 | 3.8689 | 3.6801 | 3.892 | 3.7109
2025-06-18 | 5.482 | 5.4526 | 5.4789 | 5.4895 | 5.5244 | 5.5432 | 5.5273 | 5.3697 | 5.5022 | 5.3796 | 5.7295 | 5.4226 | 5.8946 | 5.4098 | 5.5191 | 5.549 | 5.4858 | 5.4891 | 5.5008 | 5.5387 | 5.4525 | 5.45 | 5.4996 | 5.4659 | 5.4091 | 5.5733 | 5.3555 | 5.3356 | 5.4297 | 5.4107 | 5.5072 | 5.4486 | 5.9982 | 5.9986 | 6.0632 | 6.0031 | 5.5428 | 5.4789 | 5.4884 | 5.468 | 5.3819 | 5.638 | 5.4128 | 5.653 | 5.3321 | 5.0813 | 5.6534 | 5.4032 | 5.867 | 5.8047 | 5.4214 | 5.5606 | 5.3389 | 5.9336 | 5.3169 | 5.928 | 5.5167 | 5.2739 | 5.5417 | 5.3423 | 5.3366 | 5.5168 | 5.2725 | 5.3372 | 5.3948 | 5.4631 | 5.378 | 5.2754 | 5.2118 | 5.4423 | 5.2297 | 5.4641 | 5.3283 | 5.3317 | 5.5375 | 5.2385 | 5.5471 | 5.2995 | 5.5344 | 5.2942 | 5.4653 | 5.2998 | 5.4212 | 5.2536 | 5.4706 | 5.299 | 5.454 | 5.6624 | 5.3649 | 5.3512 | 5.5868 | 5.3352 | 5.3587 | 5.5567 | 5.4978 | 5.3504 | 5.5792 | 5.5069 | 5.3108 | 5.5816 | 5.2674 | 5.57 | 5.3183 | 5.4918 | 5.2578 | 5.539 | 5.2914 | 5.4521 | 5.3068 | 5.4383 | 5.333 | 5.53 | 5.4996 | 5.3066 | 5.4657 | 5.5613 | 5.3042 | 5.2819 | 5.2923 | 5.4549 | 5.256 | 5.4877 | 5.4005 | 5.5435 | 5.4261 | 5.6049 | 5.3241 | 5.5037 | 5.4566 | 5.4605 | 5.6445 | 5.7226 | 5.3953 | 5.6601 | 5.4227 | 5.4469 | 5.3819 | 5.6829 | 5.3949 | 5.684 | 5.4342 | 5.6285 | 5.5936 | 5.5126 | 5.4783 | 5.3812 | 5.4275 | 5.4111 | 5.4205 | 5.3596 | 5.6343 | 5.4299 | 5.4042 | 5.3596 | 5.3563 | 5.3389 | 5.3524 | 5.5837 | 5.3854 | 5.6103 | 5.4639
2025-06-19 | 5.2286 | 5.2029 | 5.241 | 5.2391 | 5.3072 | 5.3086 | 5.2581 | 5.0996 | 5.2457 | 5.119 | 5.4237 | 5.1408 | 5.6645 | 5.1629 | 5.2699 | 5.3026 | 5.2364 | 5.2328 | 5.2232 | 5.259 | 5.1695 | 5.1626 | 5.2407 | 5.1971 | 5.1293 | 5.2614 | 5.0682 | 5.0521 | 5.1594 | 5.149 | 5.2424 | 5.1783 | 5.6313 | 5.6207 | 5.6615 | 5.6031 | 5.2561 | 5.1735 | 5.2422 | 5.2307 | 5.279 | 5.4653 | 5.3004 | 5.5073 | 5.1856 | 4.9831 | 5.4743 | 5.2804 | 5.4942 | 5.4725 | 5.0337 | 5.1443 | 5.0735 | 5.6407 | 5.0319 | 5.6211 | 5.2036 | 5.0081 | 5.2614 | 5.0663 | 5.0781 | 5.2445 | 5.0262 | 5.0911 | 5.1024 | 5.1606 | 5.0801 | 4.9941 | 4.9557 | 5.142 | 4.9711 | 5.1758 | 5.0584 | 5.0632 | 5.2443 | 4.9896 | 5.2655 | 5.0547 | 5.2768 | 5.0578 | 5.1671 | 5.0285 | 5.1231 | 4.9826 | 5.1617 | 5.0167 | 5.13 | 5.2615 | 5.0753 | 5.0694 | 5.2711 | 5.0783 | 5.1087 | 5.2916 | 5.2521 | 5.1134 | 5.3157 | 5.2615 | 5.1036 | 5.3395 | 5.0499 | 5.3173 | 5.0881 | 5.2477 | 5.0321 | 5.2815 | 5.0563 | 5.2011 | 5.0652 | 5.173 | 5.1092 | 5.2854 | 5.2751 | 5.1048 | 5.2294 | 5.3258 | 5.0885 | 5.0731 | 5.0795 | 5.2211 | 5.0485 | 5.2533 | 5.166 | 5.301 | 5.2032 | 5.3985 | 5.116 | 5.2924 | 5.4807 | 5.5201 | 5.2257 | 5.4229 | 5.2081 | 5.4516 | 5.2408 | 5.256 | 5.2339 | 5.4828 | 5.2706 | 5.4999 | 5.2101 | 5.4162 | 5.4126 | 5.3184 | 5.3057 | 5.2341 | 5.2725 | 5.2531 | 5.2611 | 5.2194 | 5.4584 | 5.2953 | 5.2469 | 5.2144 | 5.2177 | 5.2156 | 5.2266 | 5.4087 | 5.2462 | 5.4451 | 5.2237
2025-06-20 | 5.3221 | 5.4052 | 5.3874 | 5.3749 | 5.4364 | 5.4657 | 5.4999 | 5.3805 | 5.4148 | 5.3326 | 5.7437 | 5.4266 | 5.8956 | 5.3816 | 5.4303 | 5.4239 | 5.3864 | 5.3722 | 5.393 | 5.4174 | 5.3495 | 5.3284 | 5.3545 | 5.3319 | 5.2626 | 5.2688 | 5.193 | 5.1814 | 5.3509 | 5.3971 | 5.3746 | 5.3426 | 5.5945 | 5.5722 | 5.6154 | 5.58 | 5.4676 | 5.3788 | 5.4061 | 5.3822 | 5.3666 | 5.3868 | 5.3819 | 5.4652 | 5.2481 | 5.1411 | 5.4982 | 5.4015 | 5.8077 | 5.7316 | 0 | 0 | 5.2721 | 5.8926 | 5.2436 | 5.9029 | 5.2798 | 5.2252 | 5.2896 | 5.2659 | 5.2316 | 5.2642 | 5.2188 | 5.2078 | 5.2259 | 5.1818 | 5.1937 | 5.0988 | 5.1371 | 5.188 | 5.126 | 5.166 | 5.2002 | 5.1446 | 5.2852 | 5.1266 | 5.2649 | 5.2099 | 5.2807 | 5.1789 | 5.1873 | 5.1362 | 5.1828 | 5.1106 | 5.1941 | 5.1158 | 5.1879 | 5.2423 | 5.2329 | 5.1607 | 5.2927 | 5.2443 | 5.2514 | 5.3574 | 5.314 | 5.249 | 5.3418 | 5.2679 | 5.2257 | 5.3076 | 5.2152 | 5.3102 | 5.2083 | 5.2629 | 5.174 | 5.2632 | 5.1878 | 5.2054 | 5.1845 | 5.1979 | 5.2094 | 5.2582 | 5.1867 | 5.1555 | 5.2293 | 5.2909 | 5.1738 | 5.1478 | 5.1273 | 5.1412 | 5.1257 | 5.2067 | 5.2423 | 5.2598 | 5.2468 | 5.2638 | 5.141 | 5.2171 | 5.2502 | 5.2869 | 5.2297 | 5.2992 | 5.2636 | 5.308 | 5.2009 | 5.2226 | 5.3117 | 5.4305 | 5.3584 | 5.4225 | 4.9494 | 5.2899 | 5.4023 | 5.3048 | 5.4101 | 5.3774 | 5.3761 | 5.3568 | 5.3437 | 5.2904 | 5.4421 | 5.3999 | 5.4004 | 5.3745 | 5.3835 | 5.3649 | 5.3818 | 5.4592 | 5.3707 | 5.4759 | 5.2458
2025-06-21 | 1.9639 | 2.0114 | 2.0116 | 2.0074 | 2.0378 | 2.0334 | 2.0512 | 2.022 | 2.0177 | 1.9857 | 2.1584 | 2.0161 | 2.2399 | 1.9984 | 2.0463 | 2.0398 | 2.0395 | 1.9639 | 2.0227 | 2.0227 | 2.0257 | 2.0045 | 2.0115 | 2.0056 | 1.9512 | 1.9208 | 1.9383 | 1.9266 | 2.0083 | 2.0388 | 2.014 | 1.999 | 2.0322 | 2.0307 | 2.0539 | 2.0335 | 2.0372 | 1.9936 | 2.0267 | 1.9946 | 2.0938 | 2.0587 | 2.103 | 2.0914 | 2.0246 | 2.0162 | 2.0855 | 2.1052 | 2.0566 | 2.0319 | 0 | 0 | 1.9386 | 2.196 | 1.9266 | 2.162 | 1.9205 | 1.9419 | 1.9519 | 1.9573 | 1.9187 | 1.9425 | 1.9077 | 1.8945 | 1.9204 | 1.8912 | 1.9118 | 1.9001 | 1.9053 | 1.908 | 1.9003 | 1.8594 | 1.9384 | 1.8718 | 1.9234 | 1.8923 | 1.9053 | 1.9456 | 1.8569 | 1.866 | 1.8956 | 1.9065 | 1.9054 | 1.8889 | 1.9008 | 1.8867 | 1.9271 | 1.885 | 1.9602 | 1.9233 | 1.9431 | 1.9547 | 1.9559 | 1.9701 | 1.9477 | 1.9628 | 1.9775 | 1.9474 | 1.9522 | 1.951 | 1.9548 | 1.9519 | 1.9423 | 1.9297 | 1.9607 | 1.9319 | 1.9599 | 1.9229 | 1.9535 | 1.9347 | 1.9856 | 1.919 | 1.9259 | 1.9249 | 1.9204 | 1.9245 | 1.9364 | 1.9081 | 1.9277 | 1.8909 | 1.9074 | 1.9103 | 1.9635 | 1.9035 | 1.9704 | 1.897 | 1.8994 | 1.911 | 1.9103 | 1.9478 | 1.9263 | 1.8968 | 1.9218 | 1.8928 | 1.8633 | 1.8677 | 1.9219 | 1.9123 | 1.9354 | 1.9106 | 1.9197 | 1.922 | 1.9077 | 1.9024 | 1.9028 | 1.9064 | 1.8963 | 1.8988 | 1.9093 | 1.8893 | 1.9028 | 1.9186 | 1.9069 | 1.9075 | 1.9134 | 1.8831 | 1.8927 | 1.8843 | 1.9181 | 1.8985 | 1.9324
2025-06-22 | 5.0507 | 5.0528 | 5.0223 | 5.0293 | 5.0663 | 5.0592 | 5.0933 | 4.9407 | 5.0723 | 4.9916 | 5.4167 | 5.0692 | 5.4141 | 5.0149 | 4.9921 | 5.0535 | 5.0045 | 4.8449 | 5.0158 | 5.0422 | 5.0095 | 4.894 | 5.0857 | 5.0256 | 4.9693 | 5.0664 | 4.8471 | 4.864 | 5.0515 | 5.1069 | 5.107 | 5.0499 | 5.839 | 5.8099 | 5.8883 | 5.8694 | 5.1511 | 5.0795 | 5.0995 | 4.9727 | 5.0055 | 5.1052 | 5.0462 | 5.1011 | 4.9596 | 4.6894 | 5.2548 | 5.0086 | 5.3675 | 5.2818 | 4.9307 | 5.086 | 4.6702 | 5.45 | 4.8575 | 5.3824 | 4.977 | 4.8102 | 5.0599 | 4.8785 | 4.7722 | 5.0353 | 4.8787 | 4.949 | 4.9579 | 5.0208 | 4.8602 | 4.7706 | 4.7859 | 4.9942 | 4.7694 | 4.8419 | 4.8973 | 4.8038 | 5.0586 | 4.8188 | 4.9601 | 4.8554 | 5.0681 | 4.8797 | 5.0108 | 4.8587 | 5.0128 | 4.6229 | 5.037 | 4.7111 | 5.0122 | 5.1653 | 4.9302 | 4.9491 | 5.1561 | 4.9202 | 4.9352 | 5.1124 | 5.0544 | 4.9282 | 5.1203 | 5.0641 | 4.8962 | 5.1079 | 4.8441 | 5.1259 | 4.8979 | 5.0477 | 4.8433 | 5.0054 | 4.8742 | 5.0118 | 4.8955 | 4.9644 | 4.9271 | 4.8919 | 5.0515 | 4.8956 | 4.9552 | 5.0435 | 4.9076 | 4.8823 | 4.9067 | 5.0427 | 4.8775 | 5.0862 | 5.0137 | 4.9303 | 5.0495 | 5.0166 | 4.9343 | 5.0871 | 4.9007 | 5.1099 | 5.0841 | 5.2587 | 5.0965 | 5.2335 | 4.987 | 5.0022 | 4.9338 | 5.1874 | 4.9445 | 5.1421 | 4.9468 | 5.1558 | 5.1275 | 5.0615 | 5.0396 | 4.9485 | 4.9266 | 4.9656 | 4.9609 | 4.908 | 5.14 | 4.9835 | 4.9908 | 4.9478 | 4.9799 | 4.8838 | 4.944 | 5.1408 | 4.9427 | 5.138 | 5.0173
2025-06-23 | 4.8242 | 4.9037 | 4.8725 | 4.8638 | 4.9241 | 4.9348 | 4.9625 | 4.8907 | 4.9338 | 4.8687 | 5.436 | 4.9293 | 5.4445 | 4.8617 | 4.89 | 4.9219 | 4.8911 | 4.829 | 4.8971 | 4.9186 | 4.8652 | 4.7999 | 4.8536 | 4.8398 | 4.783 | 4.7001 | 4.7033 | 4.6959 | 4.8543 | 4.9079 | 4.8773 | 4.8694 | 4.9438 | 4.9415 | 4.9773 | 4.94 | 4.9838 | 4.8841 | 4.916 | 4.846 | 4.9577 | 4.9512 | 4.9808 | 4.9119 | 4.7713 | 4.7647 | 4.9746 | 4.9869 | 5.2267 | 5.1787 | 4.7868 | 4.8374 | 4.7601 | 5.3495 | 4.7678 | 5.2962 | 4.7314 | 4.7936 | 4.7237 | 4.7937 | 4.7506 | 4.7394 | 4.7827 | 4.764 | 4.7959 | 4.7517 | 4.7478 | 4.7209 | 4.7505 | 4.7691 | 4.7462 | 4.6781 | 4.7794 | 4.6997 | 4.8157 | 4.7618 | 4.779 | 4.831 | 4.7844 | 4.7953 | 4.7739 | 4.7681 | 4.7586 | 4.761 | 4.7638 | 4.7257 | 4.7822 | 4.738 | 4.863 | 4.7782 | 4.8301 | 4.8718 | 4.8344 | 4.8655 | 4.812 | 4.8716 | 4.8989 | 4.8646 | 4.8746 | 4.8718 | 4.8344 | 4.8633 | 4.8113 | 4.825 | 4.8015 | 4.7977 | 4.82 | 4.7855 | 4.7944 | 4.7448 | 4.8503 | 4.8251 | 4.7982 | 4.8015 | 4.7946 | 4.8372 | 4.8385 | 4.8058 | 4.7986 | 4.7712 | 4.7765 | 4.781 | 4.8705 | 4.8367 | 4.8736 | 4.7906 | 4.77 | 4.7891 | 4.8125 | 4.8651 | 4.7944 | 4.7735 | 4.8406 | 4.818 | 4.7901 | 4.8053 | 4.9665 | 4.9951 | 4.9914 | 4.9785 | 5.0133 | 4.9979 | 5.0001 | 4.8953 | 4.9707 | 4.9693 | 4.9567 | 4.9565 | 4.9625 | 4.9168 | 4.9788 | 4.9997 | 5.0046 | 4.9884 | 5.0092 | 4.9715 | 4.9763 | 4.9582 | 4.9878 | 4.9883 | 4.8682
2025-06-24 | 5.385 | 5.4817 | 5.4834 | 5.4767 | 5.531 | 5.5253 | 5.548 | 5.4497 | 5.4928 | 5.4226 | 6.0497 | 5.4784 | 6.0582 | 5.4311 | 5.4768 | 5.4913 | 5.4379 | 5.4327 | 5.4445 | 5.489 | 5.396 | 5.3744 | 5.3971 | 5.3762 | 5.2976 | 5.2084 | 5.2273 | 5.2132 | 5.4092 | 5.4483 | 5.428 | 5.406 | 5.4494 | 5.4536 | 5.4938 | 5.4538 | 5.5242 | 5.4234 | 5.4505 | 5.421 | 5.5382 | 5.5511 | 5.5507 | 5.5493 | 5.3302 | 5.3025 | 5.5713 | 5.5752 | 5.8466 | 5.779 | 5.3273 | 5.3661 | 5.325 | 5.9379 | 5.2691 | 5.9221 | 5.2366 | 5.2716 | 5.2795 | 5.3468 | 5.3204 | 5.2699 | 5.2945 | 5.2777 | 5.2562 | 5.2197 | 5.2279 | 5.2262 | 5.21 | 5.264 | 5.2083 | 5.2185 | 5.2449 | 5.2447 | 5.3166 | 5.2657 | 5.3285 | 5.3565 | 5.3547 | 5.3203 | 5.2936 | 5.284 | 5.2758 | 5.278 | 5.2744 | 5.2214 | 5.2462 | 5.2185 | 5.344 | 5.2444 | 5.3168 | 5.3534 | 5.3159 | 5.3499 | 5.2893 | 5.3472 | 5.4098 | 5.4097 | 5.4268 | 5.4429 | 5.4057 | 5.4412 | 5.3882 | 5.4056 | 5.3542 | 5.3679 | 5.3782 | 5.3439 | 5.347 | 5.2875 | 5.3935 | 5.4153 | 5.3612 | 5.3677 | 5.328 | 5.4068 | 5.3972 | 5.3779 | 5.3181 | 5.2985 | 5.3436 | 5.355 | 5.4334 | 5.4184 | 5.4406 | 5.3755 | 5.3498 | 5.3698 | 5.3866 | 5.4227 | 5.3528 | 5.3379 | 5.3936 | 5.3601 | 5.3378 | 5.3592 | 5.5577 | 5.5827 | 5.5752 | 5.5744 | 5.6054 | 5.588 | 5.5965 | 5.4723 | 5.5769 | 5.5725 | 5.5599 | 5.5472 | 5.5649 | 5.512 | 5.5589 | 5.5983 | 5.6032 | 5.5746 | 5.6093 | 5.5762 | 5.5829 | 5.5769 | 5.4801 | 5.592 | 5.4196
2025-06-25 | 5.0126 | 5.0752 | 5.0708 | 5.0589 | 5.1268 | 5.1458 | 5.1702 | 5.0899 | 5.1194 | 5.0425 | 5.6373 | 5.113 | 5.6906 | 5.0992 | 5.1628 | 5.1667 | 5.1472 | 5.0704 | 5.158 | 5.1798 | 5.1311 | 4.9874 | 5.1321 | 5.1169 | 5.0612 | 4.9802 | 4.9691 | 4.9715 | 5.1469 | 5.1475 | 5.1268 | 5.1336 | 5.1493 | 5.1541 | 5.2356 | 5.1824 | 5.2321 | 5.1096 | 5.1405 | 5.0448 | 5.153 | 5.1334 | 5.1767 | 5.1348 | 4.988 | 4.943 | 5.2132 | 5.1849 | 5.4606 | 5.4382 | 5.0343 | 5.0856 | 4.9224 | 5.6158 | 4.9899 | 5.5913 | 4.9564 | 4.973 | 4.9663 | 5.0188 | 4.9378 | 4.9494 | 4.9461 | 4.9369 | 4.9519 | 4.9021 | 4.9071 | 4.8777 | 4.89 | 4.9116 | 4.8689 | 4.8321 | 4.9311 | 4.8493 | 4.9772 | 4.8921 | 4.9593 | 4.9874 | 4.8881 | 4.9634 | 4.9313 | 4.9179 | 4.9305 | 4.8144 | 4.936 | 4.8783 | 4.9353 | 4.8244 | 5.0414 | 4.9487 | 5.035 | 5.0514 | 5.0221 | 5.0433 | 4.913 | 5.0472 | 5.0752 | 5.0278 | 5.03 | 5.0234 | 5.0228 | 5.0382 | 4.9941 | 4.9815 | 4.9797 | 4.9434 | 5.0019 | 4.9678 | 5.0041 | 4.9788 | 5.0612 | 4.9258 | 4.9176 | 4.9457 | 4.9319 | 4.9882 | 5.0108 | 4.9724 | 4.9669 | 4.955 | 4.9704 | 4.9936 | 5.0794 | 4.9454 | 5.1078 | 4.9315 | 4.9915 | 5.0004 | 4.8679 | 5.0377 | 4.9822 | 4.9462 | 4.9993 | 4.9892 | 4.9572 | 4.9967 | 5.2457 | 5.3122 | 5.2649 | 5.2738 | 5.2565 | 5.2442 | 5.226 | 5.114 | 5.3086 | 5.2824 | 5.169 | 5.2466 | 5.2539 | 5.1958 | 5.2675 | 5.2748 | 5.2208 | 5.2815 | 5.3109 | 5.1898 | 5.2794 | 5.3117 | 5.2115 | 5.3158 | 5.0735
2025-06-26 | 4.6892 | 4.706 | 4.6165 | 4.6277 | 4.6395 | 4.6542 | 4.7236 | 4.6383 | 4.7681 | 4.7154 | 5.1705 | 4.7462 | 5.1358 | 4.6916 | 4.6343 | 4.6624 | 4.5942 | 4.5829 | 4.6545 | 4.6992 | 4.5917 | 4.597 | 4.5902 | 4.5882 | 4.6055 | 4.5695 | 4.5396 | 4.5079 | 4.6508 | 4.6452 | 4.6597 | 4.6562 | 4.7865 | 4.7869 | 4.8035 | 4.7523 | 4.7841 | 4.6851 | 4.702 | 4.7151 | 4.5635 | 4.631 | 4.2054 | 4.7691 | 4.4549 | 4.3975 | 4.6395 | 4.5856 | 5.0191 | 5.0072 | 4.6416 | 4.7286 | 4.6007 | 5.1017 | 4.633 | 5.1649 | 4.6499 | 4.6311 | 4.6313 | 4.6802 | 4.6627 | 4.6347 | 4.6048 | 4.5958 | 4.6493 | 4.6271 | 4.6193 | 4.6032 | 4.5703 | 4.6427 | 4.5765 | 4.6 | 4.6174 | 4.6095 | 4.6773 | 4.5995 | 4.679 | 4.6404 | 4.6821 | 4.6379 | 4.6493 | 4.6291 | 4.5962 | 4.6111 | 4.6306 | 4.5712 | 4.6634 | 4.6149 | 4.6979 | 4.6398 | 4.7121 | 4.6906 | 4.68 | 4.7466 | 4.6827 | 4.6798 | 4.7232 | 4.6846 | 4.6445 | 4.6759 | 4.6467 | 4.6854 | 4.6342 | 4.6434 | 4.6151 | 4.6249 | 4.6277 | 4.602 | 4.6322 | 4.6095 | 4.6584 | 4.6773 | 4.4981 | 4.5651 | 4.5745 | 4.6239 | 4.6028 | 4.5763 | 4.565 | 4.5516 | 4.545 | 4.5741 | 4.648 | 4.6501 | 4.6564 | 4.5819 | 4.5548 | 4.5686 | 4.5692 | 4.6073 | 4.5243 | 4.5221 | 4.5651 | 4.5687 | 4.3957 | 4.4185 | 4.5466 | 4.6256 | 4.5284 | 4.5952 | 4.5634 | 4.5885 | 4.5894 | 4.5044 | 4.5275 | 4.5016 | 4.5348 | 4.5178 | 4.5449 | 4.5013 | 4.573 | 4.5336 | 4.503 | 4.4665 | 4.4488 | 4.4243 | 4.4372 | 4.4769 | 4.4655 | 4.5375 | 4.628
2025-06-27 | 3.6974 | 3.7422 | 3.7157 | 3.7275 | 3.7353 | 3.7439 | 3.7776 | 3.7028 | 3.7424 | 3.713 | 4.077 | 3.7278 | 4.0897 | 3.6827 | 3.7302 | 3.7327 | 3.7082 | 3.6507 | 3.6947 | 3.7232 | 3.6726 | 3.5888 | 3.6586 | 3.6496 | 3.5866 | 3.5605 | 3.5501 | 3.5358 | 3.6641 | 3.6904 | 3.6576 | 3.6343 | 3.6574 | 3.6497 | 3.7285 | 3.6865 | 3.7061 | 3.6301 | 3.6011 | 3.5874 | 3.6613 | 3.6929 | 3.6586 | 4.1089 | 3.5499 | 3.4743 | 3.6987 | 3.6736 | 3.9475 | 3.9257 | 3.619 | 3.6566 | 3.5556 | 4.0531 | 3.5825 | 4.0056 | 3.5907 | 3.5666 | 3.6165 | 3.6071 | 3.544 | 3.6147 | 3.5576 | 3.556 | 3.5524 | 3.5267 | 3.5344 | 3.4851 | 3.4617 | 3.5286 | 2.9238 | 3.3681 | 3.5525 | 3.484 | 3.5968 | 3.5012 | 3.5713 | 3.5715 | 3.5833 | 3.5637 | 3.5052 | 3.4839 | 3.4859 | 3.341 | 3.487 | 3.423 | 3.5378 | 3.4529 | 3.5733 | 3.5124 | 3.5793 | 3.5448 | 3.5399 | 3.5989 | 3.5548 | 3.5458 | 3.5854 | 3.5167 | 3.4925 | 3.5175 | 3.4881 | 3.5365 | 3.4822 | 3.4921 | 3.4801 | 3.485 | 3.4862 | 3.4559 | 3.4112 | 3.4215 | 3.5173 | 3.0581 | 3.4119 | 3.4215 | 3.3755 | 3.4664 | 3.347 | 3.3684 | 3.337 | 3.3614 | 3.3435 | 3.371 | 3.4651 | 3.2875 | 3.4493 | 3.2915 | 3.3359 | 3.3421 | 3.1123 | 3.4104 | 3.3528 | 3.3358 | 3.3828 | 3.3801 | 3.3793 | 3.3988 | 3.4992 | 3.5391 | 3.5029 | 3.4488 | 3.5103 | 3.5164 | 3.4747 | 3.4475 | 3.5092 | 3.492 | 3.4521 | 3.4724 | 3.4825 | 3.407 | 3.5062 | 3.5065 | 3.4317 | 3.4718 | 3.4826 | 3.4022 | 3.4591 | 3.4908 | 3.4853 | 3.4945 | 3.5489
2025-06-28 | 4.9024 | 4.9189 | 4.9032 | 4.9411 | 4.9384 | 4.9147 | 4.954 | 4.9053 | 4.9798 | 4.9589 | 5.4692 | 5.0011 | 5.4664 | 4.9254 | 4.8676 | 4.9216 | 4.9272 | 4.7611 | 4.9323 | 4.9712 | 4.899 | 4.7694 | 4.8941 | 4.867 | 4.8532 | 4.8084 | 4.7502 | 4.7493 | 4.8656 | 5.0016 | 5.0029 | 4.9372 | 5.1312 | 5.0374 | 5.0254 | 4.9802 | 5.0534 | 4.9735 | 5.1013 | 5.0058 | 5.1952 | 5.2267 | 5.1486 | 5.8109 | 5.0401 | 4.9743 | 5.3246 | 5.2226 | 5.3396 | 5.2826 | 4.8831 | 4.9724 | 4.7469 | 5.4192 | 4.8403 | 5.3265 | 4.827 | 4.8606 | 4.8591 | 4.8882 | 4.8465 | 4.8583 | 4.8859 | 4.9054 | 4.8887 | 4.886 | 4.8214 | 4.7964 | 4.814 | 4.9221 | 4.8309 | 4.8533 | 4.8932 | 4.8417 | 4.9874 | 4.8713 | 4.9579 | 4.9715 | 4.9621 | 4.9601 | 4.9456 | 4.903 | 4.9107 | 4.8186 | 4.9037 | 4.7879 | 4.9056 | 4.8308 | 5.05 | 4.9017 | 5.0494 | 5.0381 | 5.0541 | 5.1508 | 5.1131 | 5.116 | 5.2924 | 5.2432 | 5.1824 | 5.2796 | 5.1645 | 5.2718 | 5.1746 | 5.2251 | 5.1347 | 5.1939 | 5.1588 | 5.1769 | 5.151 | 5.184 | 5.2303 | 5.2371 | 5.1148 | 5.1845 | 5.1992 | 5.2825 | 5.2067 | 5.1582 | 5.1791 | 5.2057 | 5.1427 | 5.2466 | 5.2725 | 5.241 | 5.2646 | 5.2327 | 5.1916 | 5.2558 | 5.2505 | 5.344 | 5.3051 | 5.2697 | 5.3407 | 5.3322 | 5.1819 | 5.1901 | 5.276 | 5.3742 | 5.3042 | 5.3803 | 5.3124 | 5.3328 | 5.323 | 5.257 | 5.3973 | 5.3201 | 5.2844 | 5.3322 | 5.3236 | 5.2528 | 5.3488 | 5.3421 | 5.265 | 5.2801 | 5.3128 | 5.2728 | 5.3035 | 5.3913 | 5.2743 | 5.444 | 5.0875
2025-06-29 | 4.3579 | 4.4524 | 4.5019 | 4.4727 | 4.5871 | 4.5759 | 4.5573 | 4.4735 | 4.4338 | 4.4007 | 4.8816 | 4.4081 | 4.9596 | 4.4112 | 4.5543 | 4.5616 | 4.5425 | 4.4445 | 4.499 | 4.5047 | 4.5027 | 4.3803 | 4.5451 | 4.4997 | 4.3647 | 4.2778 | 4.271 | 4.3059 | 4.5017 | 4.5973 | 4.5831 | 4.4864 | 4.4876 | 4.4577 | 4.4966 | 4.4697 | 4.5532 | 4.5172 | 4.5603 | 4.4921 | 4.6287 | 5.1848 | 4.6238 | 5.2182 | 4.5553 | 4.4575 | 4.7599 | 4.6475 | 4.7308 | 4.667 | 4.325 | 4.3527 | 4.3005 | 4.9073 | 4.2495 | 4.8067 | 4.2144 | 4.2304 | 4.2642 | 4.2571 | 4.2191 | 4.2522 | 4.2238 | 4.2441 | 4.1973 | 4.1687 | 4.1826 | 4.1436 | 4.1737 | 4.2151 | 4.1892 | 4.0989 | 4.244 | 4.2505 | 4.3063 | 4.256 | 4.3065 | 4.3098 | 4.355 | 4.3195 | 4.2147 | 4.2211 | 4.2098 | 4.0661 | 4.2019 | 4.1306 | 4.2097 | 4.0971 | 4.3067 | 4.2275 | 4.3289 | 4.3322 | 4.3565 | 4.4501 | 4.4078 | 4.3624 | 4.4283 | 4.3458 | 4.3419 | 4.3814 | 4.3481 | 4.4057 | 4.3685 | 4.392 | 4.3561 | 4.3781 | 4.373 | 4.3504 | 4.3529 | 4.3589 | 4.4618 | 4.3414 | 4.2432 | 4.3093 | 4.3019 | 4.3628 | 4.2995 | 4.3226 | 4.2651 | 4.2794 | 4.2918 | 4.3675 | 4.3973 | 4.3237 | 4.0221 | 4.3524 | 4.3305 | 4.3901 | 4.321 | 4.4476 | 4.4265 | 4.407 | 4.4279 | 4.4169 | 4.2638 | 4.2965 | 4.3569 | 4.4551 | 4.3615 | 4.4074 | 4.4133 | 4.4232 | 4.3263 | 4.3349 | 4.3786 | 4.3448 | 4.298 | 4.3293 | 4.3423 | 4.2621 | 4.286 | 4.3536 | 4.2795 | 4.3136 | 4.3077 | 4.2295 | 4.271 | 4.3549 | 4.264 | 4.3502 | 4.3856
2025-06-30 | 4.5151 | 4.587 | 4.5706 | 4.5531 | 4.6379 | 4.6678 | 4.6911 | 4.6132 | 4.6143 | 4.5544 | 5.1252 | 4.5993 | 5.1789 | 4.623 | 4.7027 | 4.6942 | 4.703 | 4.7 | 4.7157 | 4.7252 | 4.67 | 4.6642 | 4.6972 | 4.6643 | 4.6019 | 4.5279 | 4.519 | 4.5247 | 4.6999 | 4.7491 | 4.7317 | 4.7008 | 4.7461 | 4.7294 | 4.77 | 4.7157 | 4.796 | 4.7205 | 4.7362 | 4.7065 | 4.9295 | 5.5738 | 4.8683 | 5.5967 | 4.8079 | 4.7404 | 5.631 | 4.9194 | 4.9992 | 4.9498 | 4.5752 | 4.5953 | 4.5941 | 5.1236 | 4.5103 | 5.124 | 4.4728 | 4.4976 | 4.4826 | 4.5303 | 4.4976 | 4.4581 | 4.4866 | 4.4955 | 4.4798 | 4.4673 | 4.4878 | 4.4739 | 4.4735 | 4.5279 | 4.5014 | 4.5154 | 4.4935 | 4.5134 | 4.5553 | 4.5272 | 4.5932 | 4.5596 | 4.5906 | 4.5542 | 4.5272 | 4.5412 | 4.513 | 4.4909 | 4.5028 | 4.4845 | 4.5112 | 4.5062 | 4.6459 | 4.5343 | 4.6267 | 4.642 | 4.632 | 4.698 | 4.645 | 4.6378 | 4.6961 | 4.6536 | 4.6412 | 4.6657 | 4.6423 | 4.6868 | 4.634 | 4.6732 | 4.6395 | 4.6464 | 4.6715 | 4.6442 | 4.694 | 4.6762 | 4.7514 | 4.7536 | 4.5285 | 4.6083 | 4.6251 | 4.6858 | 4.6831 | 4.6465 | 4.6678 | 4.6555 | 4.6509 | 4.6788 | 4.7407 | 4.7313 | 4.715 | 4.6629 | 4.6553 | 4.6628 | 4.6896 | 4.7134 | 4.6785 | 4.669 | 4.6741 | 4.6307 | 4.5201 | 4.587 | 4.6863 | 4.733 | 4.7283 | 4.7595 | 4.7568 | 4.7239 | 4.7248 | 4.6467 | 4.7452 | 4.7268 | 4.7492 | 4.732 | 4.7282 | 4.6715 | 4.782 | 4.7707 | 4.7246 | 4.7025 | 4.7299 | 4.7106 | 4.7129 | 4.7279 | 4.7343 | 4.7662 | 4.676
2025-07-01 | 5.305 | 5.393 | 5.3748 | 5.3724 | 5.4181 | 5.4262 | 5.4603 | 5.338 | 5.4137 | 5.3296 | 5.9623 | 5.3879 | 5.9436 | 5.357 | 5.3217 | 5.3589 | 5.2883 | 5.2739 | 5.3075 | 5.3447 | 5.2503 | 5.2434 | 5.2458 | 5.2276 | 5.1943 | 5.1227 | 5.1161 | 5.1093 | 5.2776 | 5.2974 | 5.2753 | 5.2741 | 5.3513 | 5.3435 | 5.3912 | 5.3282 | 5.3892 | 5.2756 | 5.3063 | 5.291 | 5.2782 | 5.9525 | 5.3097 | 6.0868 | 5.1383 | 5.0843 | 6.0399 | 5.2976 | 5.7148 | 5.713 | 5.265 | 5.3076 | 5.2425 | 5.8395 | 5.2216 | 5.858 | 5.2018 | 5.2382 | 5.2253 | 5.2801 | 5.2518 | 5.2192 | 5.2234 | 5.1977 | 5.202 | 5.1499 | 5.1784 | 5.1314 | 5.1664 | 5.1668 | 5.1634 | 5.1067 | 5.2016 | 5.1363 | 5.2447 | 5.1425 | 5.1923 | 5.2496 | 5.2249 | 5.1714 | 5.1463 | 5.1376 | 5.123 | 5.1434 | 5.1449 | 5.1054 | 5.1547 | 5.1185 | 5.2496 | 5.1554 | 5.2359 | 5.2751 | 5.2528 | 5.2875 | 5.2284 | 5.27 | 5.2955 | 5.268 | 5.26 | 5.2561 | 5.1638 | 5.2469 | 5.2039 | 5.2169 | 5.1844 | 5.1837 | 5.1943 | 5.158 | 5.1679 | 5.1299 | 5.2043 | 5.2265 | 5.1106 | 5.1843 | 5.1627 | 5.2236 | 5.2155 | 5.182 | 5.1713 | 5.1519 | 5.1482 | 5.151 | 5.2419 | 5.2168 | 5.2027 | 5.1679 | 5.1388 | 5.1619 | 5.2148 | 5.2566 | 5.1706 | 5.1653 | 5.2274 | 5.1871 | 5.0454 | 5.1155 | 5.3432 | 5.3752 | 5.383 | 5.4179 | 5.3882 | 5.3411 | 5.3391 | 5.2099 | 5.3489 | 5.3481 | 5.3484 | 5.3372 | 5.3525 | 5.3025 | 5.3896 | 5.3884 | 5.3455 | 5.3193 | 5.3467 | 5.3192 | 5.3246 | 5.3234 | 5.2898 | 5.35 | 5.2835
2025-07-02 | 3.0798 | 3.1263 | 3.12 | 3.1142 | 3.1528 | 3.1607 | 3.1679 | 3.106 | 3.1434 | 3.0914 | 3.4693 | 3.1223 | 3.4829 | 3.1123 | 3.1516 | 3.1617 | 3.1383 | 3.1227 | 3.1323 | 3.148 | 3.1198 | 3.093 | 3.118 | 3.1087 | 3.054 | 3.0063 | 3.0079 | 3.0059 | 3.1197 | 3.1409 | 3.1269 | 3.1146 | 3.1394 | 3.1406 | 3.1751 | 3.1338 | 3.1624 | 3.1012 | 3.1263 | 3.1038 | 3.1748 | 3.5652 | 3.193 | 3.638 | 3.2232 | 3.0736 | 3.6313 | 3.1921 | 3.3414 | 3.3315 | 3.0747 | 3.0905 | 3.0692 | 3.4308 | 3.0511 | 3.4245 | 3.0176 | 3.0406 | 3.0381 | 3.0636 | 3.0405 | 3.0333 | 2.9962 | 2.9838 | 3.0196 | 3.0016 | 3.0056 | 2.9921 | 2.9995 | 3.0107 | 2.9885 | 2.9757 | 3.0276 | 2.9887 | 3.0401 | 3.0058 | 3.0243 | 3.0551 | 3.037 | 3.0327 | 3.0095 | 3.0151 | 3.0102 | 2.9851 | 3.0091 | 2.9924 | 3.0174 | 2.9987 | 3.0669 | 3.027 | 3.0497 | 3.0713 | 3.0598 | 3.083 | 3.0496 | 3.075 | 3.0959 | 3.0814 | 3.0841 | 3.0857 | 3.0214 | 3.0764 | 3.054 | 3.0562 | 3.0509 | 3.0419 | 3.0594 | 3.0339 | 3.0485 | 3.0248 | 3.0788 | 3.0473 | 3.0173 | 3.0502 | 3.0399 | 3.0698 | 3.0769 | 3.0516 | 3.0538 | 3.0297 | 3.0393 | 3.0418 | 3.0913 | 3.0604 | 3.0944 | 3.0443 | 3.0339 | 3.0455 | 3.0463 | 3.0784 | 3.0465 | 3.032 | 3.0526 | 3.0351 | 3.0141 | 3.0254 | 3.1292 | 3.1399 | 3.1491 | 3.1531 | 3.1573 | 3.1133 | 3.1312 | 3.0757 | 3.1342 | 3.1304 | 3.1277 | 3.1237 | 3.1273 | 3.0978 | 3.1415 | 3.15 | 3.1414 | 3.1278 | 3.1381 | 3.1147 | 3.1211 | 3.1232 | 3.1162 | 3.1387 | 3.0998
2025-07-03 | 2.2189 | 2.2721 | 2.2633 | 2.2496 | 2.2893 | 2.2839 | 2.2807 | 2.1766 | 2.2634 | 2.2301 | 2.5057 | 2.2582 | 2.5137 | 2.2568 | 2.1375 | 2.2271 | 2.244 | 2.0856 | 2.2478 | 2.2617 | 2.2266 | 2.0675 | 2.2098 | 2.2153 | 2.068 | 2.0244 | 1.8772 | 1.9837 | 2.1023 | 2.1055 | 2.0973 | 2.1034 | 2.2559 | 2.2604 | 2.2782 | 2.245 | 2.261 | 2.1648 | 2.2277 | 2.1865 | 2.2568 | 2.3939 | 2.2785 | 2.4421 | 2.3613 | 2.1071 | 2.573 | 2.2638 | 2.2976 | 2.3302 | 2.2109 | 2.2268 | 2.0378 | 2.4521 | 2.1815 | 2.3008 | 2.1008 | 2.1683 | 2.1599 | 2.1985 | 2.0535 | 2.1844 | 2.142 | 2.1457 | 2.1666 | 2.1417 | 2.0565 | 2.0684 | 2.1258 | 2.1416 | 2.1575 | 2.0126 | 2.1921 | 2.0842 | 2.2038 | 2.1666 | 2.1595 | 2.2067 | 2.1147 | 2.1527 | 2.1463 | 2.158 | 2.1453 | 2.0072 | 2.1351 | 2.0051 | 2.1402 | 1.9865 | 2.1173 | 2.1235 | 2.1464 | 2.0741 | 2.1626 | 2.1844 | 2.1279 | 2.1713 | 2.1785 | 2.1524 | 2.1075 | 2.1714 | 2.0862 | 2.1693 | 2.1565 | 2.1418 | 2.1742 | 2.1478 | 2.1804 | 2.1571 | 2.1267 | 2.1124 | 2.2105 | 2.0705 | 2.1344 | 2.1267 | 2.0936 | 2.1062 | 2.1572 | 2.1267 | 2.1246 | 2.0625 | 2.1224 | 2.1421 | 2.2031 | 2.0472 | 2.2221 | 2.0356 | 2.1437 | 2.1464 | 1.9948 | 2.1499 | 2.1313 | 2.1038 | 2.1303 | 2.1072 | 2.1059 | 2.1307 | 2.1703 | 2.192 | 2.211 | 2.141 | 2.1558 | 2.1808 | 2.103 | 2.1646 | 2.2337 | 2.2333 | 2.1047 | 2.1954 | 2.1898 | 2.1035 | 2.1979 | 2.2243 | 2.1898 | 2.1693 | 2.2827 | 2.1793 | 2.2621 | 2.2549 | 2.2154 | 2.2357 | 2.1741
2025-07-04 | 4.0985 | 4.1744 | 4.1618 | 4.1701 | 4.2057 | 4.2214 | 4.1912 | 4.1541 | 4.1891 | 4.0142 | 4.6713 | 4.2025 | 4.6884 | 4.2764 | 4.2871 | 4.2924 | 3.8097 | 3.8265 | 3.8702 | 3.8846 | 3.8282 | 3.7992 | 3.8617 | 3.8268 | 4.168 | 4.0982 | 4.1079 | 4.091 | 4.2365 | 4.3892 | 4.3972 | 4.2855 | 4.3487 | 4.3346 | 4.3428 | 4.3252 | 4.4088 | 4.3258 | 4.4048 | 4.3671 | 4.8454 | 5.4822 | 4.8814 | 5.51 | 5.0931 | 4.5171 | 5.4908 | 4.8159 | 4.6127 | 4.5721 | 4.2282 | 4.2431 | 4.1908 | 4.7431 | 4.1357 | 4.6484 | 4.1228 | 4.0698 | 4.1675 | 4.1685 | 4.0479 | 4.0977 | 4.0245 | 4.0394 | 3.9975 | 3.8627 | 3.9152 | 3.7653 | 3.8541 | 3.764 | 3.7418 | 3.6675 | 3.9442 | 3.7152 | 3.948 | 3.7567 | 3.84 | 3.9481 | 3.9107 | 3.7908 | 3.75 | 3.7202 | 3.7961 | 3.713 | 3.8329 | 3.8033 | 3.9028 | 3.8588 | 4.0986 | 3.9573 | 4.0671 | 4.089 | 4.1307 | 4.2389 | 4.2212 | 4.1747 | 4.2758 | 4.2062 | 4.1702 | 4.2218 | 4.226 | 4.2543 | 4.3342 | 4.2673 | 4.3393 | 4.2641 | 4.3191 | 4.2474 | 4.345 | 4.3305 | 4.4121 | 4.2266 | 4.1383 | 4.0702 | 4.0821 | 4.1411 | 4.1551 | 4.0725 | 4.1077 | 4.0549 | 4.0966 | 4.15 | 4.2761 | 4.1965 | 4.3193 | 4.1491 | 4.1403 | 4.151 | 4.0771 | 4.126 | 4.1776 | 4.1192 | 4.0884 | 4.0764 | 4.0402 | 4.0714 | 4.2883 | 4.2682 | 4.4444 | 4.3583 | 4.258 | 4.2727 | 4.2423 | 4.1262 | 4.5981 | 4.5606 | 4.4407 | 4.4689 | 4.4821 | 4.3083 | 4.5542 | 4.5613 | 4.3625 | 4.3851 | 3.4441 | 4.0542 | 4.5394 | 4.6153 | 4.3309 | 4.5101 | 4.2049
2025-07-05 | 5.2316 | 5.2888 | 5.2266 | 5.2077 | 5.2787 | 5.2739 | 5.327 | 5.1825 | 5.3381 | 5.243 | 5.7521 | 5.3011 | 5.7487 | 5.2566 | 5.3891 | 5.3403 | 5.3944 | 5.3808 | 5.3969 | 5.4162 | 5.3463 | 5.3408 | 5.3955 | 5.3456 | 5.3445 | 5.2703 | 5.2117 | 5.2173 | 5.4097 | 5.4927 | 5.4943 | 5.4561 | 5.5837 | 5.5396 | 5.553 | 5.5148 | 5.5882 | 5.5108 | 5.5206 | 5.4965 | 5.5275 | 6.2065 | 5.5419 | 6.2945 | 5.8003 | 5.2492 | 6.3366 | 5.531 | 5.6324 | 5.6266 | 5.2331 | 5.3683 | 5.2154 | 5.8036 | 5.2549 | 5.9198 | 5.2447 | 5.2222 | 5.153 | 5.1946 | 5.1521 | 5.1521 | 5.2023 | 5.1785 | 5.1788 | 5.1502 | 5.2232 | 5.1685 | 5.1646 | 5.2416 | 5.169 | 5.2103 | 5.2277 | 5.2184 | 5.2873 | 5.175 | 5.2792 | 5.1987 | 5.2593 | 5.1158 | 4.6889 | 4.6527 | 4.7474 | 4.6495 | 4.7297 | 4.6783 | 4.6886 | 4.7069 | 5.3886 | 5.2497 | 5.3966 | 5.3551 | 5.3851 | 5.5196 | 5.4878 | 5.4282 | 5.6046 | 5.5255 | 5.3947 | 5.4865 | 5.3095 | 5.4712 | 5.3616 | 5.3993 | 5.3072 | 5.3633 | 5.303 | 5.3141 | 5.2676 | 5.2716 | 5.2998 | 5.3633 | 5.3834 | 5.2878 | 5.318 | 5.3967 | 5.2861 | 5.2324 | 5.2678 | 5.2757 | 5.2369 | 5.3106 | 5.373 | 5.3776 | 5.3792 | 5.368 | 5.2844 | 5.3274 | 5.3139 | 5.376 | 5.3284 | 5.2728 | 5.2946 | 5.2818 | 5.3196 | 5.3636 | 5.5199 | 5.6437 | 5.5032 | 5.6534 | 5.5351 | 5.556 | 5.5898 | 5.4232 | 5.5862 | 5.5113 | 5.5031 | 5.4856 | 5.519 | 5.4682 | 5.6426 | 5.5243 | 5.4482 | 5.4028 | 5.3995 | 5.3819 | 5.4158 | 5.5464 | 5.4351 | 5.6015 | 5.3586
2025-07-06 | 5.3474 | 5.3374 | 5.2921 | 5.3103 | 5.3221 | 5.3208 | 5.3647 | 5.1875 | 5.3456 | 5.2702 | 5.7074 | 5.3253 | 5.6903 | 5.2754 | 5.2905 | 5.3001 | 5.264 | 5.2441 | 5.2579 | 5.2994 | 5.2151 | 5.1924 | 5.2495 | 5.2195 | 5.1664 | 5.3221 | 5.1216 | 5.0971 | 5.2038 | 5.2451 | 5.2406 | 5.1829 | 5.5657 | 5.5666 | 5.6498 | 5.5717 | 5.2667 | 5.1929 | 5.2122 | 5.1801 | 5.1659 | 5.8022 | 5.1985 | 5.8662 | 5.4286 | 4.9019 | 5.9033 | 5.1797 | 5.5955 | 5.58 | 5.1865 | 5.3493 | 5.1019 | 5.7278 | 5.1201 | 5.7394 | 5.2775 | 5.0782 | 5.3009 | 5.1123 | 5.1109 | 5.2995 | 5.1439 | 5.2314 | 5.1959 | 5.2762 | 5.1825 | 5.0903 | 5.0341 | 5.2619 | 5.0438 | 5.2268 | 5.1605 | 5.1309 | 5.3558 | 5.0592 | 5.3368 | 5.1327 | 5.3278 | 5.0968 | 5.2685 | 5.1061 | 5.2281 | 5.0348 | 5.2788 | 5.122 | 5.2818 | 5.3759 | 4.6966 | 4.7054 | 4.8375 | 4.629 | 4.6352 | 4.7898 | 4.7167 | 4.6331 | 5.3663 | 5.2766 | 5.1039 | 5.3562 | 4.9988 | 5.3482 | 5.1055 | 5.2711 | 5.0632 | 5.3094 | 5.0771 | 5.2314 | 5.095 | 5.2208 | 5.1435 | 5.1989 | 5.2941 | 5.118 | 5.2336 | 5.3354 | 5.0922 | 5.0255 | 5.0811 | 5.2082 | 5.0693 | 5.2922 | 5.2063 | 5.2453 | 5.2638 | 5.3687 | 5.1471 | 5.3241 | 5.2094 | 5.3358 | 5.3199 | 5.4436 | 5.3453 | 5.4837 | 5.2791 | 5.2967 | 5.2172 | 5.4927 | 5.241 | 5.4946 | 5.293 | 5.447 | 5.4324 | 5.3534 | 5.2926 | 5.206 | 5.177 | 5.239 | 5.2626 | 5.1928 | 5.4385 | 5.2719 | 5.1693 | 5.1669 | 5.1708 | 5.1109 | 5.1816 | 5.3948 | 5.1921 | 5.3981 | 5.2382
2025-07-07 | 4.4709 | 4.5626 | 4.5652 | 4.5321 | 4.6202 | 4.6057 | 4.6018 | 4.4847 | 4.5426 | 4.447 | 4.96 | 4.5269 | 4.9338 | 4.5189 | 4.5485 | 4.548 | 4.5364 | 4.4662 | 4.5263 | 4.5644 | 4.5316 | 4.474 | 4.5639 | 4.5454 | 4.4681 | 4.4494 | 4.3483 | 4.3702 | 4.5283 | 4.5308 | 4.5003 | 4.4836 | 4.4753 | 4.4706 | 4.5834 | 4.5091 | 4.529 | 4.4564 | 4.4896 | 4.4552 | 4.5205 | 5.1039 | 4.5696 | 5.1772 | 4.7982 | 4.3163 | 5.1868 | 4.5587 | 4.7702 | 4.7846 | 4.3946 | 4.4881 | 4.3462 | 4.8939 | 4.3451 | 4.8682 | 4.397 | 4.329 | 4.4553 | 4.3744 | 4.3442 | 4.4397 | 4.3461 | 4.398 | 4.3391 | 4.3216 | 4.3294 | 4.2343 | 4.2695 | 4.3439 | 4.2565 | 4.3235 | 4.3432 | 4.3071 | 4.4256 | 4.2852 | 4.4197 | 4.3737 | 4.4402 | 4.3543 | 4.332 | 4.281 | 4.2854 | 4.2095 | 4.2959 | 4.212 | 4.3274 | 4.2878 | 4.3461 | 4.2877 | 4.3578 | 4.3173 | 4.345 | 4.4616 | 4.4045 | 4.3529 | 4.0236 | 3.9774 | 3.9084 | 3.9679 | 3.8179 | 3.961 | 3.858 | 3.9103 | 4.2777 | 4.3611 | 4.2942 | 4.3105 | 4.2994 | 4.3251 | 4.3538 | 4.3629 | 4.3462 | 4.2529 | 4.3046 | 4.3516 | 4.2639 | 4.2174 | 4.2376 | 4.3128 | 4.2525 | 4.3802 | 4.3464 | 4.4207 | 4.3464 | 4.3987 | 4.3233 | 4.4124 | 4.3176 | 4.3928 | 4.415 | 4.3778 | 4.3971 | 4.3711 | 4.2973 | 4.307 | 4.2915 | 4.3816 | 4.2942 | 4.3773 | 4.3519 | 4.3796 | 4.4066 | 4.372 | 4.4177 | 4.3585 | 4.3518 | 4.3199 | 4.3283 | 4.2686 | 4.3543 | 4.3504 | 4.326 | 4.3567 | 4.2355 | 4.2892 | 4.3499 | 4.4108 | 4.3255 | 4.4434 | 4.3999
2025-07-08 | 4.3752 | 4.4018 | 4.3919 | 4.3981 | 4.452 | 4.4675 | 4.4728 | 4.3573 | 4.4133 | 4.3967 | 4.832 | 4.3748 | 4.8409 | 4.3557 | 4.3778 | 4.4114 | 4.2929 | 4.2503 | 4.2693 | 4.3203 | 4.2165 | 4.2128 | 4.1571 | 4.1674 | 4.0971 | 4.0812 | 4.0991 | 4.0712 | 4.1642 | 4.1593 | 4.1338 | 4.1379 | 4.1199 | 4.1408 | 4.2376 | 4.1586 | 4.1832 | 4.1077 | 4.1227 | 4.0912 | 3.9827 | 4.4703 | 3.9961 | 4.5421 | 4.2173 | 3.8787 | 4.6121 | 4.0364 | 4.6323 | 4.633 | 4.2646 | 4.2871 | 4.2381 | 4.7491 | 4.1988 | 4.6922 | 4.2271 | 4.2318 | 4.2405 | 4.2749 | 4.236 | 4.2259 | 4.1824 | 4.1962 | 4.2004 | 4.1542 | 4.1813 | 4.1373 | 4.1729 | 4.1955 | 4.1403 | 4.1461 | 4.2019 | 4.1692 | 4.237 | 4.1733 | 4.2303 | 4.243 | 4.2622 | 4.2377 | 4.1685 | 4.1764 | 4.1508 | 4.1432 | 4.1538 | 4.1058 | 4.1412 | 4.1119 | 4.1903 | 4.1158 | 4.1413 | 4.1198 | 4.0596 | 4.0722 | 4.019 | 4.0494 | 4.0331 | 4.0255 | 3.9928 | 4.0103 | 3.9085 | 3.9818 | 3.9183 | 3.9245 | 3.8714 | 3.8788 | 3.8812 | 3.8555 | 3.8555 | 3.819 | 3.8884 | 3.8816 | 3.9752 | 3.9396 | 3.8581 | 3.9276 | 3.9147 | 3.9049 | 3.8669 | 3.8092 | 3.8758 | 3.8952 | 3.9204 | 3.905 | 3.9188 | 3.8727 | 3.8764 | 3.9005 | 3.9372 | 4.0081 | 3.9233 | 3.9167 | 3.993 | 4.0072 | 4.0237 | 4.0388 | 4.2361 | 4.2465 | 4.275 | 4.2708 | 4.2413 | 4.164 | 4.1739 | 4.0955 | 4.308 | 4.2898 | 4.3089 | 4.2811 | 4.2791 | 4.2188 | 4.2875 | 4.2989 | 4.3278 | 4.3097 | 4.2863 | 4.2531 | 4.2712 | 4.291 | 4.3147 | 4.3384 | 4.168
2025-07-09 | 4.5147 | 4.6516 | 4.6689 | 4.6342 | 4.7264 | 4.7554 | 4.7557 | 4.6646 | 4.6507 | 4.4695 | 5.1723 | 4.6587 | 5.1813 | 4.6809 | 4.7198 | 4.7363 | 4.6377 | 4.5898 | 4.6044 | 4.6728 | 4.5482 | 4.5346 | 4.5752 | 4.5502 | 4.4784 | 4.4435 | 4.4456 | 4.3995 | 4.5743 | 4.5983 | 4.5619 | 4.5741 | 4.5981 | 4.5944 | 4.6496 | 4.6008 | 4.6467 | 4.5518 | 4.5485 | 4.5316 | 4.6024 | 5.211 | 4.6401 | 5.3263 | 4.8815 | 4.4262 | 5.2795 | 4.6169 | 5.0148 | 4.972 | 4.5929 | 4.6282 | 4.5726 | 5.1078 | 4.5295 | 5.0963 | 4.5443 | 4.5308 | 4.5682 | 4.5729 | 4.5427 | 4.5398 | 4.4784 | 4.4438 | 4.522 | 4.4785 | 4.4946 | 4.4374 | 4.4613 | 4.4744 | 4.4407 | 4.4202 | 4.4988 | 4.4367 | 4.5275 | 4.4026 | 4.4746 | 4.4785 | 4.5021 | 4.4201 | 4.4577 | 4.4178 | 4.3877 | 4.4205 | 4.4383 | 4.3979 | 4.4849 | 4.4667 | 4.5469 | 4.4924 | 4.5318 | 4.5109 | 4.4814 | 4.5298 | 4.4951 | 4.4917 | 4.5609 | 4.5359 | 4.4919 | 4.5401 | 4.4347 | 4.5434 | 4.4768 | 4.5183 | 4.392 | 4.46 | 4.3957 | 4.3858 | 4.3647 | 4.3247 | 4.3964 | 4.4068 | 4.4856 | 4.4612 | 4.4448 | 4.5109 | 4.4632 | 4.4543 | 4.4095 | 4.4206 | 4.3885 | 4.3995 | 4.4317 | 4.409 | 4.4341 | 4.4062 | 4.367 | 4.4043 | 4.4921 | 4.5267 | 4.4098 | 4.4286 | 4.4853 | 4.4711 | 4.5248 | 4.5542 | 4.5791 | 4.6822 | 4.5959 | 4.7893 | 4.6706 | 4.6509 | 4.6965 | 4.6062 | 4.464 | 4.4243 | 4.4347 | 4.4328 | 4.5131 | 4.5095 | 4.5889 | 4.4979 | 4.4633 | 4.4289 | 4.4415 | 4.4219 | 4.4225 | 4.4518 | 4.4143 | 4.4746 | 4.5514
2025-07-10 | 4.0493 | 4.084 | 4.7523 | 4.7139 | 4.8652 | 4.8963 | 4.8336 | 4.7593 | 4.7031 | 4.4886 | 5.2301 | 4.6925 | 5.3221 | 4.7424 | 4.8896 | 4.8904 | 4.8709 | 4.8362 | 4.8752 | 4.8867 | 4.7987 | 4.7964 | 4.7747 | 4.7738 | 4.7341 | 4.6731 | 4.6405 | 4.6648 | 4.785 | 4.79 | 4.7751 | 4.7553 | 4.7776 | 4.7943 | 4.8992 | 4.8045 | 4.8239 | 4.7318 | 4.7657 | 4.7306 | 4.9248 | 5.5667 | 4.9672 | 5.6659 | 5.2174 | 4.755 | 5.6836 | 4.9734 | 5.0855 | 5.0058 | 4.6763 | 4.6794 | 4.687 | 5.2412 | 4.5935 | 5.2096 | 4.5032 | 4.502 | 4.5683 | 4.5443 | 4.5073 | 4.5451 | 4.399 | 4.3882 | 4.4535 | 4.4317 | 4.4131 | 4.4206 | 4.3749 | 4.4358 | 4.3798 | 4.3766 | 4.4121 | 4.3818 | 4.4546 | 4.3706 | 4.4184 | 4.4278 | 4.426 | 4.3778 | 4.469 | 4.435 | 4.3976 | 4.4595 | 4.4694 | 4.4338 | 4.4692 | 4.4362 | 4.5811 | 4.4716 | 4.6155 | 4.6314 | 4.6596 | 4.7299 | 4.6931 | 4.6788 | 4.7511 | 4.7025 | 4.7314 | 4.7429 | 4.6577 | 4.7598 | 4.7182 | 4.7301 | 4.6791 | 4.712 | 4.6847 | 4.6734 | 4.6317 | 4.5875 | 4.6478 | 4.6892 | 4.6556 | 4.6602 | 4.6536 | 4.7086 | 4.659 | 4.6326 | 4.6494 | 4.5609 | 4.6445 | 4.6775 | 4.7434 | 4.7351 | 4.7246 | 4.6874 | 4.6741 | 4.6821 | 4.6316 | 4.6651 | 4.6612 | 4.6219 | 4.6355 | 4.6067 | 4.5664 | 4.5943 | 4.7352 | 4.799 | 4.7396 | 5.3242 | 4.8027 | 4.7405 | 4.7579 | 4.7195 | 4.7315 | 4.7203 | 4.6994 | 4.6832 | 4.6851 | 4.6487 | 4.7472 | 4.7292 | 4.7507 | 4.7206 | 4.731 | 4.7162 | 4.7161 | 4.7395 | 4.7115 | 4.7503 | 4.6963
2025-07-11 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-12 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-13 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-15 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-16 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-17 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-18 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-19 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-21 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-24 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-25 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-26 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-27 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-28 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Formulas:
Date = [Date, row above]+1

## Curtailment records
Sr. No | Month | Date | Plant Name | Categoty | Equipment Name | Inverter No. | From | To | Duration in MIN | Total Breakdown Hrs. | Avg POA During BD time | Lost POA | Total POA | Net POA | Loss of Capacity in KWp | Estimated PR % (Pvsyst) | Loss of Generation kWh | Remark | Current Load befor Load Sheeding (AC MW) | Load to be maintain (AC Mw)
1 | Jun | 2022-06-10 | CSPPL | Load Shedding | All Block | All inverter | 11:08 | 13:08 | 2:00 | 47:59 | 1 | 1.89 | 7 | 5.11 | 40000 | 80 | 60480 | Load Shedding from 400 kv GSS side LD massage No. 287 | 218 | 198
2 | Sept | 2022-09-01 | CSPPL | Load Shedding | Block-5 | 1 | 12:29 | 14:19 | 1:50 | 43:59 |  | 1.81 | 7.2224 | 5.4124 | 4155.14 | 84.48 | 6353.5747 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
3 | Sept | 2022-09-01 | CSPPL | Load Shedding | Block-5 | 2 | 12:29 | 14:33 | 2:04 | 49:35 |  | 2.1 | 7.2224 | 5.1224 | 4181.22 | 84.48 | 7417.8188 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
4 | Sept | 2022-09-01 | CSPPL | Load Shedding | Block-5 | 3 | 12:29 | 14:48 | 2:19 | 55:35 |  | 2.28 | 7.2224 | 4.9424 | 4155.41 | 84.48 | 8003.918 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
5 | Sept | 2022-09-02 | CSPPL | Load Shedding | Block-5 | 1 | 12:55 | 13:17 | 0:22 | 8:48 |  | 0.4 | 7.0376 | 6.6376 | 4155.14 | 84.48 | 1404.1049 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
6 | Sept | 2022-09-02 | CSPPL | Load Shedding | Block-5 | 2 | 13:00 | 13:18 | 0:18 | 7:12 |  | 0.4 | 7.0376 | 6.6376 | 4181.22 | 84.48 | 1412.9179 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
7 | Sept | 2022-09-02 | CSPPL | Load Shedding | Block-5 | 3 | 13:01 | 13:19 | 0:18 | 7:12 |  | 0.4 | 7.0376 | 6.6376 | 4155.41 | 84.48 | 1404.1961 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
8 | Sept | 2022-09-03 | CSPPL | Load Shedding | Block-5 | 1 | 11:17 | 11:24 | 0:07 | 2:48 |  | 0.12 | 7.3589 | 7.2389 | 4155.14 | 84.48 | 421.2315 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
9 | Sept | 2022-09-03 | CSPPL | Load Shedding | Block-5 | 2 | 11:17 | 11:24 | 0:07 | 2:48 |  | 0.12 | 7.3589 | 7.2389 | 4181.22 | 84.48 | 423.8754 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
10 | Sept | 2022-09-03 | CSPPL | Load Shedding | Block-5 | 3 | 11:17 | 11:24 | 0:07 | 2:48 |  | 0.12 | 7.3589 | 7.2389 | 4155.41 | 84.48 | 421.2588 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
11 | Sept | 2022-09-03 | CSPPL | Load Shedding | Block-5 | 4 | 11:17 | 11:24 | 0:07 | 2:48 |  | 0.12 | 7.3589 | 7.2389 | 4129.6 | 84.48 | 418.6423 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
12 | Sept | 2022-09-07 | CSPPL | Load Shedding | Block-5 | 1 | 11:31 | 11:45 | 0:14 | 5:36 |  | 0.25 | 7.052 | 6.802 | 4155.14 | 84.48 | 877.5656 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
13 | Sept | 2022-09-07 | CSPPL | Load Shedding | Block-5 | 2 | 13:04 | 13:13 | 0:09 | 3:36 |  | 0.16 | 7.052 | 6.892 | 4181.22 | 84.48 | 565.1671 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
14 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-1_M1 | 11:40 | 12:36 | 0:56 | 22:24 |  | 0.89 | 7.0699 | 6.1799 | 4189.05 | 84.48 | 3149.6294 | Inverter manual stop for Load reducing at peak time | 256 | 250
15 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-2_M1 | 11:54 | 12:36 | 0:42 | 16:48 |  | 0.67 | 7.0699 | 6.3999 | 2203.13 | 84.48 | 1247.0068 | Inverter manual stop for Load reducing at peak time | 256 | 250
16 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-2_M2 | 11:54 | 12:36 | 0:42 | 16:48 |  | 0.67 | 7.0699 | 6.3999 | 1954.89 | 84.48 | 1106.499 | Inverter manual stop for Load reducing at peak time | 256 | 250
17 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-1_M1 | 12:58 | 13:21 | 0:23 | 9:12 |  | 0.53 | 7.0699 | 6.5399 | 2234.16 | 84.48 | 1000.3317 | Inverter manual stop for Load reducing at peak time | 256 | 250
18 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-1_M2 | 12:58 | 13:21 | 0:23 | 9:12 |  | 0.53 | 7.0699 | 6.5399 | 1954.89 | 84.48 | 875.2903 | Inverter manual stop for Load reducing at peak time | 256 | 250
19 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-2_M1 | 12:58 | 13:21 | 0:23 | 9:12 |  | 0.53 | 7.0699 | 6.5399 | 2203.13 | 84.48 | 986.4382 | Inverter manual stop for Load reducing at peak time | 256 | 250
20 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-2_M2 | 12:58 | 13:21 | 0:23 | 9:12 |  | 0.53 | 7.0699 | 6.5399 | 1954.89 | 84.48 | 875.2903 | Inverter manual stop for Load reducing at peak time | 256 | 250
21 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-3_M1 | 12:58 | 13:21 | 0:23 | 9:12 |  | 0.53 | 7.0699 | 6.5399 | 2192.4 | 84.48 | 981.6339 | Inverter manual stop for Load reducing at peak time | 256 | 250
22 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-3_M2 | 12:58 | 13:21 | 0:23 | 9:12 |  | 0.53 | 7.0699 | 6.5399 | 2442.96 | 84.48 | 1093.8207 | Inverter manual stop for Load reducing at peak time | 256 | 250
23 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-1_M1 | 12:10 | 12:14 | 0:04 | 1:36 |  | 0.07 | 6.89 | 6.82 | 1973.16 | 84.48 | 116.6848 | Inverter manual stop for Load reducing at peak time | 256 | 250
24 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-1_M2 | 12:10 | 12:14 | 0:04 | 1:36 |  | 0.07 | 6.89 | 6.82 | 2192.4 | 84.48 | 129.6498 | Inverter manual stop for Load reducing at peak time | 256 | 250
25 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-2_M1 | 12:37 | 12:56 | 0:19 | 7:36 |  | 0.3 | 6.89 | 6.59 | 1973.16 | 84.48 | 500.0777 | Inverter manual stop for Load reducing at peak time | 256 | 250
26 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-2_M2 | 12:37 | 12:56 | 0:19 | 7:36 |  | 0.3 | 6.89 | 6.59 | 2223.72 | 84.48 | 563.5796 | Inverter manual stop for Load reducing at peak time | 256 | 250
27 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-3_M1 | 12:44 | 12:58 | 0:14 | 5:36 |  | 0.24 | 6.89 | 6.65 | 2223.72 | 84.48 | 450.8637 | Inverter manual stop for Load reducing at peak time | 256 | 250
28 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-3_M2 | 12:44 | 12:58 | 0:14 | 5:36 |  | 0.24 | 6.89 | 6.65 | 1941.84 | 84.48 | 393.7119 | Inverter manual stop for Load reducing at peak time | 256 | 250
29 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-4_M1 | 13:07 | 13:32 | 0:25 | 10:00 |  | 0.42 | 6.89 | 6.47 | 2322.9 | 84.48 | 824.2021 | Inverter manual stop for Load reducing at peak time | 256 | 250
30 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-4_M2 | 13:07 | 13:32 | 0:25 | 10:00 |  | 0.42 | 6.89 | 6.47 | 2061.9 | 84.48 | 731.5951 | Inverter manual stop for Load reducing at peak time | 256 | 250
31 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-1 | Inv-2_M1 | 12:19 | 12:25 | 0:06 | 2:24 |  | 0.11 | 6.89 | 6.78 | 2090.61 | 84.48 | 194.2762 | Inverter manual stop for Load reducing at peak time | 256 | 250
32 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-1 | Inv-2_M2 | 12:19 | 12:25 | 0:06 | 2:24 |  | 0.11 | 6.89 | 6.78 | 2090.61 | 84.48 | 194.2762 | Inverter manual stop for Load reducing at peak time | 256 | 250
33 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-1_M1 | 12:15 | 12:22 | 0:07 | 2:48 |  | 0.12 | 6.08 | 5.96 | 2102.065 | 84.48 | 213.0989 | Inverter manual stop for Load reducing at peak time | 256 | 250
34 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-1_M2 | 12:15 | 12:22 | 0:07 | 2:48 |  | 0.12 | 6.08 | 5.96 | 2007.235 | 84.48 | 203.4855 | Inverter manual stop for Load reducing at peak time | 256 | 250
35 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-2_M1 | 12:36 | 12:40 | 0:04 | 1:36 |  | 0.07 | 6.08 | 6.01 | 2102.065 | 84.48 | 124.3077 | Inverter manual stop for Load reducing at peak time | 256 | 250
36 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-2_M2 | 12:36 | 12:40 | 0:04 | 1:36 |  | 0.07 | 6.08 | 6.01 | 2212.7 | 84.48 | 130.8502 | Inverter manual stop for Load reducing at peak time | 256 | 250
37 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-3_M1 | 12:38 | 12:44 | 0:06 | 2:24 |  | 0.07 | 6.08 | 6.01 | 2275.92 | 84.48 | 134.5888 | Inverter manual stop for Load reducing at peak time | 256 | 250
38 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-3_M2 | 12:38 | 12:44 | 0:06 | 2:24 |  | 0.07 | 6.08 | 6.01 | 1991.43 | 84.48 | 117.7652 | Inverter manual stop for Load reducing at peak time | 256 | 250
39 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-4_M1 | 12:42 | 12:46 | 0:04 | 1:36 |  | 0.07 | 6.08 | 6.01 | 2244.31 | 84.48 | 132.7195 | Inverter manual stop for Load reducing at peak time | 256 | 250
40 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-4_M2 | 12:42 | 12:46 | 0:04 | 1:36 |  | 0.07 | 6.08 | 6.01 | 1944.015 | 84.48 | 114.9613 | Inverter manual stop for Load reducing at peak time | 256 | 250
41 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-1 | Inv-2_M1 | 12:24 | 12:28 | 0:04 | 1:36 |  | 0.07 | 6.08 | 6.01 | 2090.61 | 84.48 | 123.6303 | Inverter manual stop for Load reducing at peak time | 256 | 250
42 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-1 | Inv-2_M2 | 12:24 | 12:28 | 0:04 | 1:36 |  | 0.07 | 6.08 | 6.01 | 2090.61 | 84.48 | 123.6303 | Inverter manual stop for Load reducing at peak time | 256 | 250
43 | Sept | 2022-09-11 | CSPPL | Load Shedding | Blk-11 | Inv-1_M1 | 13:10 | 13:18 | 0:08 | 3:12 |  | 0.14 | 5.72 | 5.58 | 2023.04 | 84.48 | 239.269 | Inverter manual stop for Load reducing at peak time | 256 | 250
44 | Sept | 2022-09-11 | CSPPL | Load Shedding | Blk-11 | Inv-1_M2 | 13:10 | 13:18 | 0:08 | 3:12 |  | 0.14 | 5.72 | 5.58 | 2228.505 | 84.48 | 263.5697 | Inverter manual stop for Load reducing at peak time | 256 | 250
45 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-1 | Inv-1_M1 | 12:21 | 12:23 | 0:02 | 0:48 |  | 0.02 | 6.38 | 6.36 | 1884.13 | 84.48 | 31.8343 | Inverter manual stop for Load reducing at peak time | 256 | 250
46 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-1 | Inv-1_M2 | 12:21 | 12:23 | 0:02 | 0:48 |  | 0.02 | 6.38 | 6.36 | 2090.61 | 84.48 | 35.3229 | Inverter manual stop for Load reducing at peak time | 256 | 250
47 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-1_M1 | 12:21 | 12:32 | 0:11 | 4:24 |  | 0.11 | 6.38 | 6.27 | 1973.16 | 84.48 | 183.3618 | Inverter manual stop for Load reducing at peak time | 256 | 250
48 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-1_M2 | 12:21 | 12:32 | 0:11 | 4:24 |  | 0.11 | 6.38 | 6.27 | 2192.4 | 84.48 | 203.7353 | Inverter manual stop for Load reducing at peak time | 256 | 250
49 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-2_M1 | 12:22 | 12:36 | 0:14 | 5:36 |  | 0.25 | 6.38 | 6.13 | 1973.16 | 84.48 | 416.7314 | Inverter manual stop for Load reducing at peak time | 256 | 250
50 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-2_M2 | 12:22 | 12:36 | 0:14 | 5:36 |  | 0.25 | 6.38 | 6.13 | 2223.72 | 84.48 | 469.6497 | Inverter manual stop for Load reducing at peak time | 256 | 250
51 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-3_M1 | 12:23 | 12:35 | 0:12 | 4:48 |  | 0.21 | 6.38 | 6.17 | 2223.72 | 84.48 | 394.5057 | Inverter manual stop for Load reducing at peak time | 256 | 250
52 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-3_M2 | 12:23 | 12:35 | 0:12 | 4:48 |  | 0.21 | 6.38 | 6.17 | 1941.84 | 84.48 | 344.498 | Inverter manual stop for Load reducing at peak time | 256 | 250
53 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-4_M1 | 12:53 | 12:56 | 0:03 | 1:12 |  | 0.06 | 6.38 | 6.32 | 2322.9 | 84.48 | 117.7432 | Inverter manual stop for Load reducing at peak time | 256 | 250
54 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-4_M2 | 12:54 | 12:57 | 0:03 | 1:12 |  | 0.06 | 6.38 | 6.32 | 2061.9 | 84.48 | 104.5136 | Inverter manual stop for Load reducing at peak time | 256 | 250
55 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-1_M1 | 12:18 | 12:24 | 0:06 | 2:24 |  | 0.07 | 6.12 | 6.05 | 2004.48 | 84.48 | 118.5369 | Inverter manual stop for Load reducing at peak time | 256 | 250
56 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-1_M2 | 12:18 | 12:24 | 0:06 | 2:24 |  | 0.07 | 6.12 | 6.05 | 2161.08 | 84.48 | 127.7976 | Inverter manual stop for Load reducing at peak time | 256 | 250
57 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-2_M1 | 12:18 | 12:24 | 0:06 | 2:24 |  | 0.07 | 6.12 | 6.05 | 1973.16 | 84.48 | 116.6848 | Inverter manual stop for Load reducing at peak time | 256 | 250
58 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-2_M2 | 12:18 | 12:24 | 0:06 | 2:24 |  | 0.07 | 6.12 | 6.05 | 2255.04 | 84.48 | 133.354 | Inverter manual stop for Load reducing at peak time | 256 | 250
59 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-3_M1 | 12:33 | 12:40 | 0:07 | 2:48 |  | 0.09 | 6.12 | 6.03 | 1973.16 | 84.48 | 150.0233 | Inverter manual stop for Load reducing at peak time | 256 | 250
60 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-3_M2 | 12:33 | 12:40 | 0:07 | 2:48 |  | 0.09 | 6.12 | 6.03 | 2255.04 | 84.48 | 171.4552 | Inverter manual stop for Load reducing at peak time | 256 | 250
61 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-4_M1 | 12:33 | 12:37 | 0:04 | 1:36 |  | 0.06 | 6.12 | 6.06 | 1973.16 | 84.48 | 100.0155 | Inverter manual stop for Load reducing at peak time | 256 | 250
62 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-4_M2 | 12:33 | 12:37 | 0:04 | 1:36 |  | 0.06 | 6.12 | 6.06 | 2192.4 | 84.48 | 111.1284 | Inverter manual stop for Load reducing at peak time | 256 | 250
63 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-11 | Inv-1_M1 | 12:35 | 12:40 | 0:05 | 2:00 |  | 0.07 | 6.12 | 6.05 | 2023.04 | 84.48 | 119.6345 | Inverter manual stop for Load reducing at peak time | 256 | 250
64 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-11 | Inv-1_M2 | 12:35 | 12:40 | 0:05 | 2:00 |  | 0.07 | 6.12 | 6.05 | 2228.505 | 84.48 | 131.7849 | Inverter manual stop for Load reducing at peak time | 256 | 250
65 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-1_M1 | 11:02 | 11:09 | 0:07 | 2:48 |  | 0.14652 | 6.45 | 6.3035 | 2023.04 | 84.48 | 250.4199 | Inverter manual stop for Load reducing at peak time | 256 | 250
66 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-1_M2 | 11:02 | 11:09 | 0:07 | 2:48 |  | 0.14652 | 6.45 | 6.3035 | 2228.505 | 84.48 | 275.8532 | Inverter manual stop for Load reducing at peak time | 256 | 250
67 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-2_M1 | 11:03 | 11:11 | 0:08 | 3:12 |  | 0.17831 | 6.45 | 6.2717 | 2054.65 | 84.48 | 309.5092 | Inverter manual stop for Load reducing at peak time | 256 | 250
68 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-2_M2 | 11:03 | 11:11 | 0:08 | 3:12 |  | 0.17831 | 6.45 | 6.2717 | 2275.92 | 84.48 | 342.8409 | Inverter manual stop for Load reducing at peak time | 256 | 250
69 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-3_M1 | 11:05 | 11:12 | 0:07 | 2:48 |  | 0.12889 | 6.45 | 6.3211 | 2023.04 | 84.48 | 220.2789 | Inverter manual stop for Load reducing at peak time | 256 | 250
70 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-3_M2 | 11:05 | 11:12 | 0:07 | 2:48 |  | 0.12889 | 6.45 | 6.3211 | 2133.675 | 84.48 | 232.3254 | Inverter manual stop for Load reducing at peak time | 256 | 250
71 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-4_M1 | 11:33 | 11:45 | 0:12 | 4:48 |  | 0.23231 | 6.45 | 6.2177 | 2023.04 | 84.48 | 397.0244 | Inverter manual stop for Load reducing at peak time | 256 | 250
72 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-4_M2 | 11:33 | 11:45 | 0:12 | 4:48 |  | 0.23231 | 6.45 | 6.2177 | 1754.355 | 84.48 | 344.2946 | Inverter manual stop for Load reducing at peak time | 256 | 250
73 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-1_M1 | 11:35 | 11:43 | 0:08 | 3:12 |  | 0.16475 | 6.45 | 6.2852 | 2302.02 | 84.48 | 320.4012 | Inverter manual stop for Load reducing at peak time | 256 | 250
74 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-1_M1 | 11:35 | 11:43 | 0:08 | 3:12 |  | 0.16475 | 6.45 | 6.2852 | 2145.42 | 84.48 | 298.6052 | Inverter manual stop for Load reducing at peak time | 256 | 250
75 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-2_M1 | 11:35 | 11:43 | 0:08 | 3:12 |  | 0.16475 | 6.45 | 6.2852 | 1910.52 | 84.48 | 265.9112 | Inverter manual stop for Load reducing at peak time | 256 | 250
76 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-2_M2 | 11:35 | 11:43 | 0:08 | 3:12 |  | 0.16475 | 6.45 | 6.2852 | 2192.4 | 84.48 | 305.144 | Inverter manual stop for Load reducing at peak time | 256 | 250
77 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-3_M1 | 11:36 | 11:44 | 0:08 | 3:12 |  | 0.16475 | 6.45 | 6.2852 | 2192.4 | 84.48 | 305.144 | Inverter manual stop for Load reducing at peak time | 256 | 250
78 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-3_M2 | 11:36 | 11:44 | 0:08 | 3:12 |  | 0.16475 | 6.45 | 6.2852 | 2004.48 | 84.48 | 278.9888 | Inverter manual stop for Load reducing at peak time | 256 | 250
79 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-4_M1 | 12:32 | 12:35 | 0:03 | 1:12 |  | 0.06389 | 6.45 | 6.3861 | 2004.48 | 84.48 | 108.1896 | Inverter manual stop for Load reducing at peak time | 256 | 250
80 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-4_M2 | 12:32 | 12:35 | 0:03 | 1:12 |  | 0.06389 | 6.45 | 6.3861 | 2223.72 | 84.48 | 120.0228 | Inverter manual stop for Load reducing at peak time | 256 | 250
81 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-2_M1 | 12:04 | 12:07 | 0:03 | 1:12 |  | 0.063414 | 6.45 | 6.3866 | 1910.52 | 84.48 | 102.3506 | Inverter manual stop for Load reducing at peak time | 256 | 250
82 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-2_M2 | 12:04 | 12:07 | 0:03 | 1:12 |  | 0.063414 | 6.45 | 6.3866 | 2192.4 | 84.48 | 117.4515 | Inverter manual stop for Load reducing at peak time | 256 | 250
83 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-3_M1 | 12:04 | 12:20 | 0:16 | 6:24 |  | 0.063414 | 6.45 | 6.3866 | 2192.4 | 84.48 | 117.4515 | Inverter manual stop for Load reducing at peak time | 256 | 250
84 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-3_M2 | 12:04 | 12:20 | 0:16 | 6:24 |  | 0.063414 | 6.45 | 6.3866 | 2004.48 | 84.48 | 107.3842 | Inverter manual stop for Load reducing at peak time | 256 | 250
85 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-1_M1 | 12:18 | 12:33 | 0:15 | 6:00 |  | 0.063414 | 6.45 | 6.3866 | 2004.48 | 84.48 | 107.3842 | Inverter manual stop for Load reducing at peak time | 256 | 250
86 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-1_M2 | 12:18 | 12:33 | 0:15 | 6:00 |  | 0.063414 | 6.45 | 6.3866 | 2004.48 | 84.48 | 107.3842 | Inverter manual stop for Load reducing at peak time | 256 | 250
87 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-2_M1 | 12:18 | 12:33 | 0:15 | 6:00 |  | 0.047746 | 6.45 | 6.4023 | 2239.38 | 84.48 | 90.3265 | Inverter manual stop for Load reducing at peak time | 256 | 250
88 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-2_M2 | 12:18 | 12:33 | 0:15 | 6:00 |  | 0.047746 | 6.45 | 6.4023 | 1941.84 | 84.48 | 78.3251 | Inverter manual stop for Load reducing at peak time | 256 | 250
89 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-3_M1 | 12:32 | 12:34 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2255.04 | 84.48 | 90.9581 | Inverter manual stop for Load reducing at peak time | 256 | 250
90 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-3_M2 | 12:32 | 12:34 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 1941.84 | 84.48 | 78.3251 | Inverter manual stop for Load reducing at peak time | 256 | 250
91 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-4_M1 | 12:41 | 12:43 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2192.4 | 84.48 | 88.4315 | Inverter manual stop for Load reducing at peak time | 256 | 250
92 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-4_M2 | 12:41 | 12:43 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2004.48 | 84.48 | 80.8517 | Inverter manual stop for Load reducing at peak time | 256 | 250
93 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-1_M1 | 12:42 | 12:45 | 0:03 | 1:12 |  | 0.069013 | 6.45 | 6.381 | 2223.72 | 84.48 | 129.6476 | Inverter manual stop for Load reducing at peak time | 256 | 250
94 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-1_M2 | 12:42 | 12:45 | 0:03 | 1:12 |  | 0.069013 | 6.45 | 6.381 | 1910.52 | 84.48 | 111.3874 | Inverter manual stop for Load reducing at peak time | 256 | 250
95 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-2_M1 | 12:44 | 12:46 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2223.72 | 84.48 | 89.6948 | Inverter manual stop for Load reducing at peak time | 256 | 250
96 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-2_M2 | 12:44 | 12:46 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2004.48 | 84.48 | 80.8517 | Inverter manual stop for Load reducing at peak time | 256 | 250
97 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-3_M1 | 12:50 | 12:52 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2192.4 | 84.48 | 88.4315 | Inverter manual stop for Load reducing at peak time | 256 | 250
98 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-3_M2 | 12:50 | 12:52 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2004.48 | 84.48 | 80.8517 | Inverter manual stop for Load reducing at peak time | 256 | 250
99 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-4_M1 | 12:55 | 13:01 | 0:06 | 2:24 |  | 0.10129 | 6.45 | 6.3487 | 2192.4 | 84.48 | 187.6105 | Inverter manual stop for Load reducing at peak time | 256 | 250
100 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-4_M2 | 12:55 | 13:01 | 0:06 | 2:24 |  | 0.10129 | 6.45 | 6.3487 | 2004.48 | 84.48 | 171.5296 | Inverter manual stop for Load reducing at peak time | 256 | 250
101 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-15 | Inv-1_M1 | 12:59 | 13:01 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 1973.16 | 84.48 | 79.5884 | Inverter manual stop for Load reducing at peak time | 256 | 250
102 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-15 | Inv-1_M2 | 12:59 | 13:01 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2192.4 | 84.48 | 88.4315 | Inverter manual stop for Load reducing at peak time | 256 | 250
103 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-15 | Inv-2_M1 | 13:06 | 13:12 | 0:06 | 2:24 |  | 0.1125 | 6.47 | 6.3575 | 1973.16 | 84.48 | 187.5239 | Inverter manual stop for Load reducing at peak time | 256 | 250
104 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-15 | Inv-2_M2 | 13:06 | 13:12 | 0:06 | 2:24 |  | 0.1125 | 6.47 | 6.3575 | 2223.72 | 84.48 | 211.3364 | Inverter manual stop for Load reducing at peak time | 256 | 250
105 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-15 | Inv-3_M1 | 13:08 | 13:14 | 0:06 | 2:24 |  | 0.11348 | 6.47 | 6.3565 | 1973.16 | 84.48 | 189.1633 | Inverter manual stop for Load reducing at peak time | 256 | 250
106 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-15 | Inv-3_M2 | 13:08 | 13:14 | 0:06 | 2:24 |  | 0.11348 | 6.47 | 6.3565 | 2192.4 | 84.48 | 210.1814 | Inverter manual stop for Load reducing at peak time | 256 | 250
107 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-1 | Inv-4_M1 | 13:27 | 13:30 | 0:03 | 1:12 |  | 0.064171 | 6.47 | 6.4058 | 2090.61 | 84.48 | 113.3359 | Inverter manual stop for Load reducing at peak time | 256 | 250
108 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-1 | Inv-4_M2 | 13:27 | 13:30 | 0:03 | 1:12 |  | 0.064171 | 6.47 | 6.4058 | 2193.85 | 84.48 | 118.9328 | Inverter manual stop for Load reducing at peak time | 256 | 250
109 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-16 | Inv-1_M1 | 13:28 | 13:36 | 0:08 | 3:12 |  | 0.1411 | 6.47 | 6.3289 | 2223.72 | 84.48 | 265.0705 | Inverter manual stop for Load reducing at peak time | 256 | 250
110 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-16 | Inv-2_M1 | 13:28 | 13:36 | 0:08 | 3:12 |  | 0.1411 | 6.47 | 6.3289 | 1941.84 | 84.48 | 231.47 | Inverter manual stop for Load reducing at peak time | 256 | 250
111 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-16 | Inv-2_M1 | 11:28 | 11:38 | 0:10 | 4:00 |  | 0.17162 | 6.9712 | 6.7996 | 2161.08 | 84.48 | 313.3163 | Inverter manual stop for Load reducing at peak time | 256 | 250
112 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-16 | Inv-2_M2 | 11:28 | 11:38 | 0:10 | 4:00 |  | 0.17162 | 6.9712 | 6.7996 | 1973.16 | 84.48 | 286.0714 | Inverter manual stop for Load reducing at peak time | 256 | 250
113 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-16 | Inv-3_M1 | 11:38 | 11:47 | 0:09 | 3:36 |  | 0.15838 | 6.9712 | 6.8128 | 2161.08 | 84.48 | 289.1539 | Inverter manual stop for Load reducing at peak time | 256 | 250
114 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-16 | Inv-3_M2 | 11:38 | 11:47 | 0:09 | 3:36 |  | 0.15838 | 6.9712 | 6.8128 | 1910.52 | 84.48 | 255.6288 | Inverter manual stop for Load reducing at peak time | 256 | 250
115 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-16 | Inv-4_M1 | 11:41 | 11:47 | 0:06 | 2:24 |  | 0.11114 | 6.9712 | 6.86 | 2161.08 | 84.48 | 202.8996 | Inverter manual stop for Load reducing at peak time | 256 | 250
116 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-16 | Inv-4_M2 | 11:41 | 11:47 | 0:06 | 2:24 |  | 0.11114 | 6.9712 | 6.86 | 1941.84 | 84.48 | 182.3155 | Inverter manual stop for Load reducing at peak time | 256 | 250
117 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-1_M1 | 11:48 | 11:52 | 0:04 | 1:36 |  | 0.079867 | 6.9712 | 6.8913 | 2004.48 | 84.48 | 135.2464 | Inverter manual stop for Load reducing at peak time | 256 | 250
118 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-1_M2 | 11:48 | 11:52 | 0:04 | 1:36 |  | 0.079867 | 6.9712 | 6.8913 | 2004.48 | 84.48 | 135.2464 | Inverter manual stop for Load reducing at peak time | 256 | 250
119 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-2_M1 | 11:48 | 11:52 | 0:04 | 1:36 |  | 0.079867 | 6.9712 | 6.8913 | 2004.48 | 84.48 | 135.2464 | Inverter manual stop for Load reducing at peak time | 256 | 250
120 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-2_M2 | 11:48 | 11:52 | 0:04 | 1:36 |  | 0.079867 | 6.9712 | 6.8913 | 1722.6 | 84.48 | 116.2274 | Inverter manual stop for Load reducing at peak time | 256 | 250
121 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-3_M1 | 12:22 | 12:40 | 0:18 | 7:12 |  | 0.30915 | 6.9712 | 6.662 | 1973.16 | 84.48 | 515.3291 | Inverter manual stop for Load reducing at peak time | 256 | 250
122 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-3_M2 | 12:22 | 12:40 | 0:18 | 7:12 |  | 0.30915 | 6.9712 | 6.662 | 1753.92 | 84.48 | 458.0703 | Inverter manual stop for Load reducing at peak time | 256 | 250
123 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-4_M1 | 12:22 | 12:41 | 0:19 | 7:36 |  | 0.32549 | 6.9712 | 6.6457 | 2004.48 | 84.48 | 551.1801 | Inverter manual stop for Load reducing at peak time | 256 | 250
124 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-4_M2 | 12:22 | 12:41 | 0:19 | 7:36 |  | 0.32549 | 6.9712 | 6.6457 | 2004.48 | 84.48 | 551.1801 | Inverter manual stop for Load reducing at peak time | 256 | 250
125 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-1_M1 | 12:39 | 12:46 | 0:07 | 2:48 |  | 0.13069 | 6.9712 | 6.8405 | 2255.04 | 84.48 | 248.9772 | Inverter manual stop for Load reducing at peak time | 256 | 250
126 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-1_M2 | 12:39 | 12:46 | 0:07 | 2:48 |  | 0.13069 | 6.9712 | 6.8405 | 1941.84 | 84.48 | 214.3971 | Inverter manual stop for Load reducing at peak time | 256 | 250
127 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-2_M1 | 12:41 | 12:46 | 0:05 | 2:00 |  | 0.11437 | 6.9712 | 6.8568 | 2255.04 | 84.48 | 217.8747 | Inverter manual stop for Load reducing at peak time | 256 | 250
128 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-2_M2 | 12:41 | 12:46 | 0:05 | 2:00 |  | 0.11437 | 6.9712 | 6.8568 | 1973.16 | 84.48 | 190.6403 | Inverter manual stop for Load reducing at peak time | 256 | 250
129 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-3_M1 | 13:12 | 13:28 | 0:16 | 6:24 |  | 0.27343 | 6.9712 | 6.6977 | 2223.72 | 84.48 | 513.6668 | Inverter manual stop for Load reducing at peak time | 256 | 250
130 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-3_M2 | 13:12 | 13:28 | 0:16 | 6:24 |  | 0.27343 | 6.9712 | 6.6977 | 1973.16 | 84.48 | 455.7888 | Inverter manual stop for Load reducing at peak time | 256 | 250
131 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-4_M1 | 13:12 | 13:38 | 0:26 | 10:24 |  | 0.43189 | 6.9712 | 6.5393 | 2004.48 | 84.48 | 731.3537 | Inverter manual stop for Load reducing at peak time | 256 | 250
132 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-4_M2 | 13:12 | 13:38 | 0:26 | 10:24 |  | 0.43189 | 6.9712 | 6.5393 | 2004.48 | 84.48 | 731.3537 | Inverter manual stop for Load reducing at peak time | 256 | 250
133 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-1_M1 | 11:07 | 11:26 | 0:19 | 7:36 |  | 0.30569 | 6.9425 | 6.6368 | 2161.08 | 84.48 | 558.085 | Inverter manual stop for Load reducing at peak time | 256 | 250
134 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-1_M2 | 11:07 | 11:26 | 0:19 | 7:36 |  | 0.30569 | 6.9425 | 6.6368 | 2255.04 | 84.48 | 582.3496 | Inverter manual stop for Load reducing at peak time | 256 | 250
135 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-2_M1 | 11:24 | 11:48 | 0:24 | 9:36 |  | 0.39293 | 6.9425 | 6.5496 | 2223.72 | 84.48 | 738.1656 | Inverter manual stop for Load reducing at peak time | 256 | 250
136 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-2_M2 | 11:24 | 11:48 | 0:24 | 9:36 |  | 0.39293 | 6.9425 | 6.5496 | 2223.72 | 84.48 | 738.1656 | Inverter manual stop for Load reducing at peak time | 256 | 250
137 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-3_M1 | 11:25 | 11:43 | 0:18 | 7:12 |  | 0.31392 | 6.9425 | 6.6286 | 2223.72 | 84.48 | 589.7284 | Inverter manual stop for Load reducing at peak time | 256 | 250
138 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-3_M2 | 11:25 | 11:43 | 0:18 | 7:12 |  | 0.31392 | 6.9425 | 6.6286 | 2255.04 | 84.48 | 598.0344 | Inverter manual stop for Load reducing at peak time | 256 | 250
139 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-4_M1 | 11:43 | 12:02 | 0:19 | 7:36 |  | 0.322 | 6.9425 | 6.6205 | 2004.48 | 84.48 | 545.275 | Inverter manual stop for Load reducing at peak time | 256 | 250
140 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-4_M2 | 11:43 | 12:02 | 0:19 | 7:36 |  | 0.322 | 6.9425 | 6.6205 | 2223.72 | 84.48 | 604.9144 | Inverter manual stop for Load reducing at peak time | 256 | 250
141 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-1_M1 | 11:46 | 12:16 | 0:30 | 12:00 |  | 0.50428 | 6.9425 | 6.4382 | 2255.04 | 84.48 | 960.6889 | Inverter manual stop for Load reducing at peak time | 256 | 250
142 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-1_M2 | 11:46 | 12:16 | 0:30 | 12:00 |  | 0.50428 | 6.9425 | 6.4382 | 2255.04 | 84.48 | 960.6889 | Inverter manual stop for Load reducing at peak time | 256 | 250
143 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-2_M1 | 11:47 | 12:23 | 0:36 | 14:24 |  | 0.60271 | 6.9425 | 6.3398 | 2223.72 | 84.48 | 1132.2485 | Inverter manual stop for Load reducing at peak time | 256 | 250
144 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-2_M2 | 11:47 | 12:23 | 0:36 | 14:24 |  | 0.60271 | 6.9425 | 6.3398 | 2161.08 | 84.48 | 1100.3541 | Inverter manual stop for Load reducing at peak time | 256 | 250
145 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-3_M1 | 11:56 | 12:35 | 0:39 | 15:36 |  | 0.65731 | 6.9425 | 6.2852 | 2223.72 | 84.48 | 1234.8134 | Inverter manual stop for Load reducing at peak time | 256 | 250
146 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-3_M2 | 11:56 | 12:35 | 0:39 | 15:36 |  | 0.65731 | 6.9425 | 6.2852 | 1816.56 | 84.48 | 1008.7208 | Inverter manual stop for Load reducing at peak time | 256 | 250
147 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-4_M1 | 12:02 | 12:35 | 0:33 | 13:12 |  | 0.55973 | 6.9425 | 6.3828 | 2176.74 | 84.48 | 1029.2939 | Inverter manual stop for Load reducing at peak time | 256 | 250
148 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-4_M2 | 12:02 | 12:35 | 0:33 | 13:12 |  | 0.55973 | 6.9425 | 6.3828 | 2004.48 | 84.48 | 947.839 | Inverter manual stop for Load reducing at peak time | 256 | 250
149 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-1_M1 | 12:18 | 12:55 | 0:37 | 14:48 |  | 0.62784 | 6.9425 | 6.3147 | 2064.8 | 84.48 | 1095.1641 | Inverter manual stop for Load reducing at peak time | 256 | 250
150 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-1_M2 | 12:18 | 12:55 | 0:37 | 14:48 |  | 0.62784 | 6.9425 | 6.3147 | 2142.23 | 84.48 | 1136.2328 | Inverter manual stop for Load reducing at peak time | 256 | 250
151 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-2_M1 | 12:24 | 13:04 | 0:40 | 16:00 |  | 0.67714 | 6.9425 | 6.2654 | 2064.8 | 84.48 | 1181.1616 | Inverter manual stop for Load reducing at peak time | 256 | 250
152 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-2_M2 | 12:24 | 13:04 | 0:40 | 16:00 |  | 0.67714 | 6.9425 | 6.2654 | 2090.61 | 84.48 | 1195.9261 | Inverter manual stop for Load reducing at peak time | 256 | 250
153 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-3_M1 | 12:34 | 13:11 | 0:37 | 14:48 |  | 0.62645 | 6.9425 | 6.3161 | 2090.61 | 84.48 | 1106.4084 | Inverter manual stop for Load reducing at peak time | 256 | 250
154 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-3_M2 | 12:34 | 13:11 | 0:37 | 14:48 |  | 0.62645 | 6.9425 | 6.3161 | 2077.705 | 84.48 | 1099.5787 | Inverter manual stop for Load reducing at peak time | 256 | 250
155 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-4_M1 | 12:38 | 13:18 | 0:40 | 16:00 |  | 0.67569 | 6.9425 | 6.2668 | 2090.61 | 84.48 | 1193.3743 | Inverter manual stop for Load reducing at peak time | 256 | 250
156 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-4_M2 | 12:38 | 13:18 | 0:40 | 16:00 |  | 0.67569 | 6.9425 | 6.2668 | 2064.8 | 84.48 | 1178.6413 | Inverter manual stop for Load reducing at peak time | 256 | 250
157 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-1_M1 | 12:56 | 13:32 | 0:36 | 14:24 |  | 0.60683 | 6.9425 | 6.3357 | 2064.8 | 84.48 | 1058.5131 | Inverter manual stop for Load reducing at peak time | 256 | 250
158 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-1_M2 | 12:56 | 13:32 | 0:36 | 14:24 |  | 0.60683 | 6.9425 | 6.3357 | 2090.61 | 84.48 | 1071.7445 | Inverter manual stop for Load reducing at peak time | 256 | 250
159 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-2_M1 | 13:06 | 13:45 | 0:39 | 15:36 |  | 0.65186 | 6.9425 | 6.2907 | 2090.61 | 84.48 | 1151.2787 | Inverter manual stop for Load reducing at peak time | 256 | 250
160 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-2_M2 | 13:06 | 13:45 | 0:39 | 15:36 |  | 0.65186 | 6.9425 | 6.2907 | 2090.61 | 84.48 | 1151.2787 | Inverter manual stop for Load reducing at peak time | 256 | 250
161 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-3_M1 | 13:11 | 13:49 | 0:38 | 15:12 |  | 0.63315 | 6.9425 | 6.3094 | 2114.1 | 84.48 | 1130.7931 | Inverter manual stop for Load reducing at peak time | 256 | 250
162 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-3_M2 | 13:11 | 13:49 | 0:38 | 15:12 |  | 0.63315 | 6.9425 | 6.3094 | 2088 | 84.48 | 1116.8327 | Inverter manual stop for Load reducing at peak time | 256 | 250
163 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-4_M1 | 13:19 | 13:49 | 0:30 | 12:00 |  | 0.50124 | 6.9425 | 6.4413 | 2114.1 | 84.48 | 895.2043 | Inverter manual stop for Load reducing at peak time | 256 | 250
164 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-4_M2 | 13:19 | 13:49 | 0:30 | 12:00 |  | 0.50124 | 6.9425 | 6.4413 | 2061.9 | 84.48 | 873.1005 | Inverter manual stop for Load reducing at peak time | 256 | 250
165 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-1_M1 | 12:00 | 12:17 | 0:17 | 6:48 |  | 0.29611 | 7.051 | 6.7549 | 2234.16 | 84.48 | 558.8908 | Inverter manual stop for Load reducing at peak time | 256 | 250
166 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-1_M2 | 12:00 | 12:17 | 0:17 | 6:48 |  | 0.29611 | 7.051 | 6.7549 | 1954.89 | 84.48 | 489.0295 | Inverter manual stop for Load reducing at peak time | 256 | 250
167 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-2_M1 | 12:03 | 12:18 | 0:15 | 6:00 |  | 0.26364 | 7.051 | 6.7873 | 2203.13 | 84.48 | 490.6797 | Inverter manual stop for Load reducing at peak time | 256 | 250
168 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-2_M2 | 12:03 | 12:18 | 0:15 | 6:00 |  | 0.26364 | 7.051 | 6.7873 | 1954.89 | 84.48 | 435.3918 | Inverter manual stop for Load reducing at peak time | 256 | 250
169 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-3_M1 | 12:20 | 12:27 | 0:07 | 2:48 |  | 0.12904 | 7.051 | 6.9219 | 2192.4 | 84.48 | 238.9966 | Inverter manual stop for Load reducing at peak time | 256 | 250
170 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-3_M2 | 12:20 | 12:27 | 0:07 | 2:48 |  | 0.12904 | 7.051 | 6.9219 | 2442.96 | 84.48 | 266.3105 | Inverter manual stop for Load reducing at peak time | 256 | 250
171 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-4_M1 | 12:38 | 12:48 | 0:10 | 4:00 |  | 0.18221 | 7.051 | 6.8688 | 1954.89 | 84.48 | 300.9216 | Inverter manual stop for Load reducing at peak time | 256 | 250
172 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-4_M2 | 12:38 | 12:48 | 0:10 | 4:00 |  | 0.18221 | 7.051 | 6.8688 | 2234.16 | 84.48 | 343.9104 | Inverter manual stop for Load reducing at peak time | 256 | 250
173 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-2_M1 | 12:32 | 12:44 | 0:12 | 4:48 |  | 0.21489 | 7.051 | 6.8361 | 2203.13 | 84.48 | 399.959 | Inverter manual stop for Load reducing at peak time | 256 | 250
174 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-2_M2 | 12:32 | 12:44 | 0:12 | 4:48 |  | 0.21489 | 7.051 | 6.8361 | 1954.89 | 84.48 | 354.8932 | Inverter manual stop for Load reducing at peak time | 256 | 250
175 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-3_M1 | 12:32 | 12:44 | 0:12 | 4:48 |  | 0.21489 | 7.051 | 6.8361 | 2192.4 | 84.48 | 398.011 | Inverter manual stop for Load reducing at peak time | 256 | 250
176 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-3_M2 | 12:32 | 12:44 | 0:12 | 4:48 |  | 0.21489 | 7.051 | 6.8361 | 2442.96 | 84.48 | 443.498 | Inverter manual stop for Load reducing at peak time | 256 | 250
177 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-1_M1 | 12:39 | 13:05 | 0:26 | 10:24 |  | 0.44717 | 7.051 | 6.6038 | 1973.16 | 84.48 | 745.3976 | Inverter manual stop for Load reducing at peak time | 256 | 250
178 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-1_M2 | 12:39 | 13:05 | 0:26 | 10:24 |  | 0.44717 | 7.051 | 6.6038 | 1910.52 | 84.48 | 721.7342 | Inverter manual stop for Load reducing at peak time | 256 | 250
179 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-2_M1 | 12:45 | 13:09 | 0:24 | 9:36 |  | 0.4151 | 7.051 | 6.6359 | 2098.44 | 84.48 | 735.8744 | Inverter manual stop for Load reducing at peak time | 256 | 250
180 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-2_M2 | 12:45 | 13:09 | 0:24 | 9:36 |  | 0.4151 | 7.051 | 6.6359 | 2004.48 | 84.48 | 702.9248 | Inverter manual stop for Load reducing at peak time | 256 | 250
181 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-3_M1 | 12:47 | 13:09 | 0:22 | 8:48 |  | 0.38165 | 7.051 | 6.6693 | 2223.72 | 84.48 | 716.9748 | Inverter manual stop for Load reducing at peak time | 256 | 250
182 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-3_M2 | 12:47 | 13:09 | 0:22 | 8:48 |  | 0.38165 | 7.051 | 6.6693 | 1973.16 | 84.48 | 636.1889 | Inverter manual stop for Load reducing at peak time | 256 | 250
183 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-4_M1 | 12:50 | 13:09 | 0:19 | 7:36 |  | 0.33148 | 7.051 | 6.7195 | 2223.72 | 84.48 | 622.7095 | Inverter manual stop for Load reducing at peak time | 256 | 250
184 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-4_M2 | 12:50 | 13:09 | 0:19 | 7:36 |  | 0.33148 | 7.051 | 6.7195 | 1973.16 | 84.48 | 552.545 | Inverter manual stop for Load reducing at peak time | 256 | 250
185 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-1_M1 | 13:16 | 13:24 | 0:08 | 3:12 |  | 0.14903 | 7.051 | 6.9019 | 1973.16 | 84.48 | 248.4161 | Inverter manual stop for Load reducing at peak time | 256 | 250
186 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-1_M2 | 13:16 | 13:24 | 0:08 | 3:12 |  | 0.14903 | 7.051 | 6.9019 | 2192.4 | 84.48 | 276.0179 | Inverter manual stop for Load reducing at peak time | 256 | 250
187 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-2_M1 | 13:16 | 13:24 | 0:08 | 3:12 |  | 0.14903 | 7.051 | 6.9019 | 1973.16 | 84.48 | 248.4161 | Inverter manual stop for Load reducing at peak time | 256 | 250
188 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-2_M2 | 13:16 | 13:24 | 0:08 | 3:12 |  | 0.14903 | 7.051 | 6.9019 | 2223.72 | 84.48 | 279.961 | Inverter manual stop for Load reducing at peak time | 256 | 250
189 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-3_M1 | 13:16 | 13:24 | 0:08 | 3:12 |  | 0.14903 | 7.051 | 6.9019 | 2223.72 | 84.48 | 279.961 | Inverter manual stop for Load reducing at peak time | 256 | 250
190 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-3_M2 | 13:16 | 13:24 | 0:08 | 3:12 |  | 0.14903 | 7.051 | 6.9019 | 1941.84 | 84.48 | 244.473 | Inverter manual stop for Load reducing at peak time | 256 | 250
191 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-4_M1 | 13:29 | 13:42 | 0:13 | 5:12 |  | 0.22805 | 7.051 | 6.8229 | 2322.9 | 84.48 | 447.522 | Inverter manual stop for Load reducing at peak time | 256 | 250
192 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-4_M2 | 13:29 | 13:42 | 0:13 | 5:12 |  | 0.22805 | 7.051 | 6.8229 | 2061.9 | 84.48 | 397.2386 | Inverter manual stop for Load reducing at peak time | 256 | 250
193 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-9 | Inv-1_M1 | 13:30 | 13:31 | 0:01 | 0:24 |  | 0.032811 | 7.051 | 7.0182 | 2102.065 | 84.48 | 58.2659 | Inverter manual stop for Load reducing at peak time | 256 | 250
194 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-9 | Inv-1_M2 | 13:30 | 13:31 | 0:01 | 0:24 |  | 0.032811 | 7.051 | 7.0182 | 2007.235 | 84.48 | 55.6374 | Inverter manual stop for Load reducing at peak time | 256 | 250
195 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-9 | Inv-2_M1 | 13:31 | 13:41 | 0:10 | 4:00 |  | 0.17929 | 7.051 | 6.8717 | 2102.065 | 84.48 | 318.383 | Inverter manual stop for Load reducing at peak time | 256 | 250
196 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-9 | Inv-2_M2 | 13:31 | 13:41 | 0:10 | 4:00 |  | 0.17929 | 7.051 | 6.8717 | 2212.7 | 84.48 | 335.14 | Inverter manual stop for Load reducing at peak time | 256 | 250
197 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-1_M1 | 11:11 | 11:20 | 0:09 | 3:36 |  | 0.15334 | 7.1588 | 7.0055 | 2102.065 | 84.48 | 272.3137 | Inverter manual stop for Load reducing at peak time | 256 | 250
198 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-1_M2 | 11:11 | 11:20 | 0:09 | 3:36 |  | 0.15334 | 7.1588 | 7.0055 | 2007.235 | 84.48 | 260.0289 | Inverter manual stop for Load reducing at peak time | 256 | 250
199 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-2_M1 | 11:20 | 11:49 | 0:29 | 11:36 |  | 0.47575 | 7.1588 | 6.6831 | 2102.065 | 84.48 | 844.8471 | Inverter manual stop for Load reducing at peak time | 256 | 250
200 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-2_M2 | 11:20 | 11:49 | 0:29 | 11:36 |  | 0.47575 | 7.1588 | 6.6831 | 2212.7 | 84.48 | 889.3128 | Inverter manual stop for Load reducing at peak time | 256 | 250
201 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-3_M1 | 11:23 | 11:56 | 0:33 | 13:12 |  | 0.54287 | 7.1588 | 6.616 | 2275.92 | 84.48 | 1043.7777 | Inverter manual stop for Load reducing at peak time | 256 | 250
202 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-3_M2 | 11:23 | 11:56 | 0:33 | 13:12 |  | 0.54287 | 7.1588 | 6.616 | 1991.43 | 84.48 | 913.3054 | Inverter manual stop for Load reducing at peak time | 256 | 250
203 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-4_M1 | 11:32 | 12:18 | 0:46 | 18:24 |  | 0.76227 | 7.1588 | 6.3966 | 2244.31 | 84.48 | 1445.2502 | Inverter manual stop for Load reducing at peak time | 256 | 250
204 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-4_M2 | 11:32 | 12:18 | 0:46 | 18:24 |  | 0.76227 | 7.1588 | 6.3966 | 1944.015 | 84.48 | 1251.8716 | Inverter manual stop for Load reducing at peak time | 256 | 250
205 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-1_M1 | 11:50 | 12:19 | 0:29 | 11:36 |  | 0.49072 | 7.1588 | 6.6681 | 2004.48 | 84.48 | 830.9695 | Inverter manual stop for Load reducing at peak time | 256 | 250
206 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-1_M2 | 11:50 | 12:19 | 0:29 | 11:36 |  | 0.49072 | 7.1588 | 6.6681 | 2161.08 | 84.48 | 895.889 | Inverter manual stop for Load reducing at peak time | 256 | 250
207 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-2_M1 | 11:53 | 12:21 | 0:28 | 11:12 |  | 0.47527 | 7.1588 | 6.6836 | 1973.16 | 84.48 | 792.2424 | Inverter manual stop for Load reducing at peak time | 256 | 250
208 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-2_M2 | 11:53 | 12:21 | 0:28 | 11:12 |  | 0.47527 | 7.1588 | 6.6836 | 2255.04 | 84.48 | 905.4199 | Inverter manual stop for Load reducing at peak time | 256 | 250
209 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-3_M1 | 11:57 | 12:22 | 0:25 | 10:00 |  | 0.42673 | 7.1588 | 6.7321 | 1973.16 | 84.48 | 711.3335 | Inverter manual stop for Load reducing at peak time | 256 | 250
210 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-3_M2 | 11:57 | 12:22 | 0:25 | 10:00 |  | 0.42673 | 7.1588 | 6.7321 | 2255.04 | 84.48 | 812.9526 | Inverter manual stop for Load reducing at peak time | 256 | 250
211 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-4_M1 | 12:10 | 12:25 | 0:15 | 6:00 |  | 0.26406 | 7.1588 | 6.8948 | 1973.16 | 84.48 | 440.1661 | Inverter manual stop for Load reducing at peak time | 256 | 250
212 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-4_M2 | 12:10 | 12:25 | 0:15 | 6:00 |  | 0.26406 | 7.1588 | 6.8948 | 2192.4 | 84.48 | 489.0734 | Inverter manual stop for Load reducing at peak time | 256 | 250
213 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-11 | Inv-1_M1 | 12:20 | 12:52 | 0:32 | 12:48 |  | 0.54738 | 7.1588 | 6.6115 | 2023.04 | 84.48 | 935.5122 | Inverter manual stop for Load reducing at peak time | 256 | 250
214 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-11 | Inv-1_M2 | 12:20 | 12:52 | 0:32 | 12:48 |  | 0.54738 | 7.1588 | 6.6115 | 2228.505 | 84.48 | 1030.5251 | Inverter manual stop for Load reducing at peak time | 256 | 250
215 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-11 | Inv-2_M1 | 12:20 | 12:55 | 0:35 | 14:00 |  | 0.54738 | 7.1588 | 6.6115 | 2054.65 | 84.48 | 950.1295 | Inverter manual stop for Load reducing at peak time | 256 | 250
216 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-11 | Inv-2_M2 | 12:20 | 12:55 | 0:35 | 14:00 |  | 0.54738 | 7.1588 | 6.6115 | 2275.92 | 84.48 | 1052.4512 | Inverter manual stop for Load reducing at peak time | 256 | 250
217 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-11 | Inv-3_M1 | 12:22 | 13:02 | 0:40 | 16:00 |  | 0.6802 | 7.1588 | 6.4787 | 2023.04 | 84.48 | 1162.5046 | Inverter manual stop for Load reducing at peak time | 256 | 250
218 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-11 | Inv-3_M2 | 12:22 | 13:02 | 0:40 | 16:00 |  | 0.6802 | 7.1588 | 6.4787 | 2133.675 | 84.48 | 1226.079 | Inverter manual stop for Load reducing at peak time | 256 | 250
219 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-1_M1 | 12:23 | 13:23 | 1:00 | 24:00 |  | 1.0085 | 7.1588 | 6.1504 | 2302.02 | 84.48 | 1961.2379 | Inverter manual stop for Load reducing at peak time | 256 | 250
220 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-1_M2 | 12:23 | 13:23 | 1:00 | 24:00 |  | 1.0085 | 7.1588 | 6.1504 | 2145.42 | 84.48 | 1827.8203 | Inverter manual stop for Load reducing at peak time | 256 | 250
221 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-2_M1 | 12:26 | 13:30 | 1:04 | 25:36 |  | 1.0722 | 7.1588 | 6.0867 | 1910.52 | 84.48 | 1730.4746 | Inverter manual stop for Load reducing at peak time | 256 | 250
222 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-2_M2 | 12:26 | 13:30 | 1:04 | 25:36 |  | 1.0722 | 7.1588 | 6.0867 | 2192.4 | 84.48 | 1985.7906 | Inverter manual stop for Load reducing at peak time | 256 | 250
223 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-3_M1 | 12:54 | 13:44 | 0:50 | 20:00 |  | 0.83196 | 7.1588 | 6.3269 | 2192.4 | 84.48 | 1540.9076 | Inverter manual stop for Load reducing at peak time | 256 | 250
224 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-3_M2 | 12:54 | 13:44 | 0:50 | 20:00 |  | 0.83196 | 7.1588 | 6.3269 | 2004.48 | 84.48 | 1408.8298 | Inverter manual stop for Load reducing at peak time | 256 | 250
225 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-4_M1 | 13:02 | 13:44 | 0:42 | 16:48 |  | 0.69914 | 7.1588 | 6.4597 | 2004.48 | 84.48 | 1183.9185 | Inverter manual stop for Load reducing at peak time | 256 | 250
226 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-4_M2 | 13:02 | 13:44 | 0:42 | 16:48 |  | 0.69914 | 7.1588 | 6.4597 | 2223.72 | 84.48 | 1313.4096 | Inverter manual stop for Load reducing at peak time | 256 | 250
227 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-13 | Inv-1_M1 | 13:29 | 13:59 | 0:30 | 12:00 |  | 0.49209 | 7.1588 | 6.6668 | 2004.48 | 84.48 | 833.292 | Inverter manual stop for Load reducing at peak time | 256 | 250
228 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-13 | Inv-1_M2 | 13:29 | 13:59 | 0:30 | 12:00 |  | 0.49209 | 7.1588 | 6.6668 | 2004.48 | 84.48 | 833.292 | Inverter manual stop for Load reducing at peak time | 256 | 250
228 | June | 2023-06-08 | CSPPL | Load Shedding | Plant |  | 11:48 | 14:42 | 2:54 | 69:36 |  | 2.77 | 7.5 | 4.73 | 25000 | 84.67 | 58633.975 | LD Msg No-230 for 250 to 225 and LD Msg No-236 for 225 to 250 | 250 | 225
229 | June | 2023-06-09 | CSPPL | Load Shedding | Plant |  | 10:30 | 11:00 | 0:30 | 12:00 |  | 0.41 | 7.0702 | 6.6602 | 50000 | 84.67 | 17357.35 | LD Msg No-261 for 250 to 200 | 250 | 200
230 | June | 2023-06-09 | CSPPL | Load Shedding | Plant |  | 11:00 | 15:42 | 4:42 | 112:48 |  | 4.05 | 7.0702 | 3.0202 | 100000 | 84.67 | 342913.5 | LD Msg No-262 for 250 to 150 and LD Msg No-265 for 225 to 250 | 200 | 150
231 | June | 2023-06-10 | CSPPL | Load Shedding | Plant |  | 10:00 | 15:19 | 5:19 | 127:36 |  | 4.1316 | 7.1785 | 3.0469 | 100000 | 84.67 | 349821.8218 | LD Msg No-282 for 250 to 150 and LD Msg No-287 for 150 to 250 | 250 | 150
232 | June | 2023-06-11 | CSPPL | Load Shedding | Plant |  | 10:38 | 15:30 | 4:52 | 116:48 |  | 3.67 | 7.7247 | 4.0547 | 100000 | 84.67 | 310738.9 | LD Msg No-323 for 250 to 150 and LD Msg No-329 for 150 to 251 | 250 | 150
233 | June | 2023-06-12 | CSPPL | Load Shedding | Plant |  | 10:58 | 15:10 | 4:12 | 100:48 |  | 3.7383 | 7.25 | 3.5117 | 100000 | 84.67 | 316525.9455 | LD Msg No-357 for 250 to 150 and LD Msg No-361 for 150 to 252 | 250 | 150
234 | June | 2023-06-13 | CSPPL | Load Shedding | Plant |  | 10:23 | 14:42 | 4:19 | 103:36 |  | 3.7343 | 7.2 | 3.4657 | 100000 | 84.67 | 316183.5606 | LD Msg No-386 for 250 to 150 and LD Msg No-392 for 150 to 252 | 250 | 150
235 | June | 2023-06-14 | CSPPL | Load Shedding | Plant |  | 11:05 | 11:09 | 0:04 | 1:36 |  | 0.064827 | 6.7454 | 6.6806 | 50000 | 84.67 | 2744.4601 | LD Msg No-420 for 250 to 200 | 250 | 200
236 | June | 2023-06-14 | CSPPL | Load Shedding | Plant |  | 11:09 | 13:50 | 2:41 | 64:24 |  | 2.2384 | 6.7454 | 4.507 | 75000 | 84.67 | 142144.8787 | LD Msg No-420 for 200 to 175 and LD Msg No-423 for 175 to 250 | 200 | 175
237 | June | 2023-06-15 | CSPPL | Load Shedding | Plant |  | 12:00 | 12:21 | 0:21 | 8:24 |  | 0.21266 | 4.9039 | 4.6912 | 50000 | 84.67 | 9003.0802 | LD Msg No-458 for 250 to 200 and LD Msg No-459 for 200 to 251 | 250 | 200
238 | June | 2023-06-20 | CSPPL | Load Shedding | Plant |  | 11:06 | 15:12 | 4:06 | 98:24 |  | 3.7045 | 7.3321 | 3.6275 | 50000 | 84.67 | 156831.8791 | LD Msg No-602 for 250 to 200 and LD Msg No-608 for 200 to 251 | 250 | 200
239 | June | 2023-06-22 | CSPPL | Load Shedding | Plant |  | 11:12 | 11:34 | 0:22 | 8:48 |  | 0.32748 | 7.0625 | 6.7351 | 25000 | 84.67 | 6931.8371 | LD Msg No-649 for 223 to 225 | 223 | 225
240 | June | 2023-06-22 | CSPPL | Load Shedding | Plant |  | 11:34 | 15:50 | 4:16 | 102:24 |  | 3.8191 | 7.0625 | 3.2434 | 45000 | 84.67 | 145514.9291 | LD Msg No-650 for 225 to 180 | 225 | 180
241 | June | 2023-06-23 | CSPPL | Load Shedding | Plant |  | 10:16 | 12:15 | 1:59 | 47:36 |  | 1.73 | 7.34 | 5.61 | 50000 | 84.67 | 73239.55 | LD Msg No- 670 for 200 | 198 | 200
242 | June | 2023-06-23 | CSPPL | Load Shedding | Plant |  | 12:15 | 13:46 | 1:31 | 36:24 |  | 1.49 | 7.34 | 5.85 | 75000 | 84.67 | 94618.725 | LD Msg No- 681 for 175 | 173 | 175
243 | June | 2023-06-23 | CSPPL | Load Shedding | Plant |  | 13:46 | 15:20 | 1:34 | 37:36 |  | 1.39 | 7.34 | 5.95 | 50000 | 84.67 | 58845.65 | LD Msg No- 683 for 200 | 189 | 200
244 | June | 2023-06-24 | CSPPL | Load Shedding | Plant |  | 12:35 | 14:00 | 1:25 | 34:00 |  | 1.35 | 7.1 | 5.75 | 25000 | 84.67 | 28576.125 | LD Msg No- 705 for 250 to 225 | 248 | 225
245 | July | 2023-07-01 | CSPPL | Load Shedding | Plant |  | 12:17 | 13:35 | 1:18 | 31:12 |  | 1.2627 | 7.22 | 5.9573 | 37000 | 85.6839 | 40031.7456 | LD Msg 13 for 250 to 213 and LD Msg 14 for 213 to 250 | 250 | 213
246 | July | 2023-07-13 | CSPPL | Load Shedding | Plant |  | 13:46 | 15:11 | 1:25 | 34:00 |  | 1.2594 | 7.39 | 6.1306 | 35000 | 85.6839 | 37769.5908 | LD Msg 301 for 250 to 215MW and LD Msg 308 for 250 | 250 | 215
247 | July | 2023-07-15 | CSPPL | Load Shedding | Plant |  | 10:56 | 12:33 | 1:37 | 38:48 |  | 1.4546 | 7.24 | 5.7854 | 50000 | 85.6839 | 62318.771 |  | 238 | 202
248 | July | 2023-07-15 | CSPPL | Load Shedding | Plant |  | 12:33 | 15:35 | 3:02 | 72:48 |  | 2.6247 | 7.24 | 4.6153 | 80000 | 85.6839 | 179913.2184 |  | 202 | 177
249 | Feb | 2024-02-19 | CSPPL | Load Shedding | Plant |  | 13:25 | 14:24 | 0:59 | 23:36 |  | 0.99456 | 5.72 | 4.7254 | 50000 | 87.08 | 43303.2875 | LD Msg 469 for 250 to 200Mw and LD Msg 472 for 250MW | 250 | 200
250 | April | 2024-04-07 | CSPPL | Load Shedding | Plant |  | 10:31 | 14:46 | 4:15 | 102:00 |  | 4.08 | 7.12 | 3.04 | 50000 | 80.7 | 164628 | LD Msg 178 for 250 to 200Mw and LD Msg 182 for 250MW | 250 | 200
251 | April | 2024-04-08 | CSPPL | Load Shedding | Plant |  | 10:34 | 15:15 | 4:41 | 112:24 |  | 4.31 | 7.45 | 3.14 | 50000 | 80.7 | 173908.5 | LD Msg 187 for 250 to 200Mw and LD Msg 191 for 250MW | 250 | 200
252 | April | 2024-04-19 | CSPPL | Load Shedding | Plant |  | 10:35 | 12:05 | 1:30 | 36:00 |  | 1.45 | 7.29 | 5.84 | 25000 | 80.7 | 29253.75 | LD Msg 466 for 250 to 225Mw | 250 | 225
253 | April | 2024-04-19 | CSPPL | Load Shedding | Plant |  | 12:05 | 14:49 | 2:44 | 65:36 |  | 2.679 | 7.29 | 4.611 | 50000 | 80.7 | 108097.65 | LD Msg 469 for 225 to 200Mw and LD Msg 474 for 250MW | 225 | 200
254 | Auguest | 2024-08-08 | CSPPL | Load Shedding | Plant |  | 11:57 | 13:30 | 1:33 | 37:12 |  | 0.53196 | 2.83 | 2.298 | 50000 | 86.32 | 22959.3936 | LD Msg 208 for 200Mw and LD Msg 210 for 250MW | 250 | 200
255 | Auguest | 2024-08-10 | CSPPL | Load Shedding | Plant |  | 11:08 | 14:54 | 3:46 | 18:24 |  | 2.71 | 5.42 | 2.71 | 17500 | 83.51 | 39567.82 | LD Msg 293 for 232.5MW and LD Msg 298 for 250MW | 250 | 232.5
256 | Auguest | 2024-08-11 | CSPPL | Load Shedding | Plant |  | 9:29 | 10:34 | 1:05 | 26:00 |  | 0.491 | 5.6774 | 5.1864 | 50000 | 62.87 | 15434.585 | LD Msg 320 for 250 to 200Mw | 250 | 200
257 | Auguest | 2024-08-11 | CSPPL | Load Shedding | Plant |  | 10:34 | 12:38 | 2:04 | 49:36 |  | 1.53 | 5.6774 | 4.1474 | 90000 | 62.87 | 86571.99 | LD Msg 324 for 200 to 160Mw | 200 | 160
258 | Auguest | 2024-08-11 | CSPPL | Load Shedding | Plant |  | 12:38 | 18:10 | 5:32 | 132:48 |  | 2.857 | 5.6774 | 2.8204 | 150000 | 62.87 | 269429.385 | LD Msg 331 for 160Mw and LD Msg 343 for 250MW | 250 | 100
259 | Auguest | 2024-08-15 | CSPPL | Load Shedding | Plant |  | 10:35 | 14:25 | 3:50 | 92:00 |  | 2.3275 | 3.54 | 1.2125 | 50000 | 85.61 | 99626.7113 | LD Msg 453 for 200Mw and LD Msg 454 for 250MW | 250 | 200
260 | Auguest | 2024-08-26 | CSPPL | Load Shedding | Plant |  | 12:00 | 14:50 | 2:50 | 68:00 |  | 1.96 | 5.24 | 3.28 | 38000 | 86.06 | 64097.488 | LD Msg 713 for 212Mw and LD Msg 736 for 250MW | 250 | 212
261 | Auguest | 2024-08-27 | CSPPL | Load Shedding | Plant |  | 9:53 | 13:00 | 3:07 | 74:48 |  | 0.7965 | 2.57 | 1.7735 | 18000 | 85.45 | 12250.9665 | LD Msg 768 for 250 to 232MW | 250 | 232
262 | Auguest | 2024-08-27 | CSPPL | Load Shedding | Plant |  | 13:00 | 13:20 | 0:20 | 8:00 |  | 0.1021 | 2.57 | 2.4679 | 36400 | 85.45 | 3175.698 | LD Msg 776 for 232 to 213.6MW | 232 | 213.6
263 | Auguest | 2024-08-27 | CSPPL | Load Shedding | Plant |  | 13:20 | 14:36 | 1:16 | 30:24 |  | 0.3402 | 2.57 | 2.2298 | 46400 | 85.45 | 13488.5218 | LD Msg 778 for 213 to 203.6MW | 213.6 | 203.6
264 | Auguest | 2024-08-27 | CSPPL | Load Shedding | Plant |  | 14:36 | 16:44 | 2:08 | 51:12 |  | 0.5023 | 2.57 | 2.0677 | 26000 | 85.45 | 11159.5991 | LD Msg 780 for 213.6 to 224MW | 213.6 | 224
265 | Auguest | 2024-08-29 | CSPPL | Load Shedding | Plant |  | 9:30 | 9:55 | 0:25 | 10:00 |  | 0.222 | 5.28 | 5.058 | 30000 | 83.48 | 5559.768 | LD Msg 837 for 220Mw and LD Msg 839 for 250MW | 250 | 220
266 | Auguest | 2024-08-29 | CSPPL | Load Shedding | Plant |  | 11:57 | 13:12 | 1:15 | 30:00 |  | 0.956 | 5.28 | 4.324 | 30000 | 83.48 | 23942.064 | LD Msg 844 for 250 to 220MW | 250 | 220
267 | Auguest | 2024-08-29 | CSPPL | Load Shedding | Plant |  | 13:12 | 13:55 | 0:43 | 17:12 |  | 0.545 | 5.28 | 4.735 | 99000 | 83.48 | 45041.634 | LD Msg 844 for 220 to 151MW and LD Msg 845 for 250MW | 220 | 151
268 | Sept. | 2024-09-05 | CSPPL | Load Shedding | Plant |  | 11:15 | 13:15 | 2:00 | 48:00 |  | 1.56 | 6.11 | 4.55 | 55000 | 84.33 | 72355.14 | LD Msg 96 for 250 to 195MW | 250 | 195
269 | Sept. | 2024-09-05 | CSPPL | Load Shedding | Plant |  | 13:15 | 14:45 | 1:30 | 36:00 |  | 1.46 | 6.11 | 4.65 | 75000 | 84.33 | 92341.35 | LD Msg 102 for 195 to 175MW and LD Msg 104 for 250MW | 195 | 175
270 | Sept. | 2024-09-08 | CSPPL | Load Shedding | Plant |  | 9:55 | 10:19 | 0:24 | 9:36 |  | 0.29764 | 6.78 | 6.4824 | 84000 | 81.63 | 20408.7272 | LD Msg 188 for 250 to 166MW | 250 | 166
271 | Sept. | 2024-09-08 | CSPPL | Load Shedding | Plant |  | 10:19 | 13:24 | 3:05 | 74:00 |  | 2.7376 | 6.78 | 4.0424 | 95000 | 81.63 | 212295.0934 | LD Msg 192 for 166 to 155MW | 166 | 155
272 | Sept. | 2024-09-08 | CSPPL | Load Shedding | Plant |  | 13:24 | 13:51 | 0:27 | 10:48 |  | 0.41255 | 6.78 | 6.3675 | 64000 | 81.63 | 21552.6855 | LD Msg 197 for 155 to 186MW and LD Msg 198 for 250MW | 155 | 186
273 | Sept. | 2024-09-11 | CSPPL | Load Shedding | Plant |  | 11:30 | 13:20 | 1:50 | 44:00 |  | 1.71 | 6 | 4.29 | 25000 | 84.03 | 35922.825 | LD Msg 263 for 250 to 225MW and LD Msg 266 for 250MW | 250 | 225
274 | Sept. | 2024-09-13 | CSPPL | Load Shedding | Plant |  | 10:20 | 11:10 | 0:50 | 20:00 |  | 0.7114 | 6.76 | 6.0486 | 38000 | 83.07 | 22456.6371 | LD Msg 318 for 250 to 212MW | 250 | 212
275 | Sept. | 2024-09-13 | CSPPL | Load Shedding | Plant |  | 11:10 | 14:30 | 3:20 | 80:00 |  | 2.933 | 6.76 | 3.827 | 30000 | 83.07 | 73093.293 | LD Msg 322 for 212 to 220MW | 212 | 220
276 | Sept. | 2024-09-13 | CSPPL | Load Shedding | Plant |  | 14:30 | 14:40 | 0:10 | 4:00 |  | 0.11965 | 6.76 | 6.6403 | 12000 | 83.07 | 1192.7191 | LD Msg 330 for 220 to 238MW and LD Msg 331 for 250MW | 220 | 238
277 | Sept. | 2024-09-14 | CSPPL | Load Shedding | Plant |  | 11:15 | 15:15 | 4:00 | 96:00 |  | 3.56 | 6.58 | 3.02 | 30000 | 81.67 | 87223.56 | LD Msg 357 for 250 to 220MW and LD Msg 363 for 250MW | 250 | 220
278 | Sept. | 2024-09-15 | CSPPL | Load Shedding | Plant |  | 11:00 | 15:20 | 4:20 | 104:00 |  | 3.83 | 6.73 | 2.9 | 30000 | 83.92 | 96424.08 | LD Msg 382 for 250 to 220MW and LD Msg 386 for 250MW | 250 | 220
279 | Sept. | 2024-09-16 | CSPPL | Load Shedding | Plant |  | 11:00 | 15:30 | 4:30 | 108:00 |  | 4.1 | 7.02 | 2.92 | 30000 | 79.35 | 97600.5 | LD Msg 397 for 250 to 220MW and LD Msg 404 for 250MW | 250 | 220
280 | Sept. | 2024-09-17 | CSPPL | Load Shedding | Plant |  | 10:05 | 14:40 | 4:35 | 110:00 |  | 4.2468 | 7.06 | 2.8132 | 30000 | 82.63 | 105272.9336 | LD Msg 430 for 250 to 220MW and LD Msg 435 for 250MW | 250 | 220
281 | Nov. | 2024-11-24 | CSPPL | Load Shedding | Plant |  | 12:50 | 17:50 | 5:00 | 120:00 |  | 2.35 | 5.19 | 2.84 | 25000 | 86.69 | 50930.375 | LD Msg 120 for 250 to 225MW | 250 | 225
282 | Nov. | 2024-11-25 | CSPPL | Load Shedding | Plant |  | 11:50 | 14:15 | 2:25 | 58:00 |  | 1.87 | 5.02 | 3.15 | 25000 | 86.78 | 40569.65 | LD Msg 123 for 250 to 225MW and LD Msg 124 for 250MW | 250 | 225
283 | Dec | 2024-12-08 | CSPPL | Load Shedding | Plant |  | 11:30 | 12:20 | 0:50 | 20:00 |  | 0.7219 | 5.41 | 4.6881 | 49000 | 85.76 | 30335.9706 | LD Msg 164 for 250 to 201MW and LD Msg 169 for 250MW | 250 | 201
284 | Jan | 2025-01-10 | CSPPL | Load Shedding | Plant |  | 11:06 | 14:58 | 3:52 | 92:48 |  | 3.0559 | 5.36 | 2.3041 | 25000 | 87.99 | 67222.2336 | LD Msg 186 for 250 to 225MW and LD Msg 189 for 250MW | 250 | 225
285 | Feb | 2025-02-23 | CSPPL | Load Shedding | Plant |  | 13:08 | 13:33 | 0:25 | 10:00 |  | 0.42483 | 6.8 | 6.3752 | 25000 | 85.12 | 9040.276 | LD Msg 579 for 250 to 225MW and LD Msg 580 for 250MW | 250 | 225
286 | April | 2025-04-06 | CSPPL | Load Shedding | Plant |  | 13:54 | 15:22 | 1:28 | 35:12 |  | 1.36 | 7.78 | 6.42 | 50000 | 79.15 | 53822 | LD Msg 110 for 250 to 200MW and LD Msg 118 for 250MW | 250 | 200
287 | April | 2025-04-07 | CSPPL | Load Shedding | Plant |  | 13:04 | 14:25 | 1:21 | 32:24 |  | 1.36 | 7.6 | 6.24 | 100000 | 75.61 | 102829.6 | LD Msg 148 for 250 to 150MW | 250 | 155
288 | April | 2025-04-07 | CSPPL | Load Shedding | Plant |  | 14:26 | 16:00 | 1:34 | 37:36 |  | 1.27 | 7.6 | 6.33 | 50000 | 75.61 | 48012.35 | LD Msg 157 for 150 to 200MW and LD Msg 160 for 250MW | 250 | 200
289 | April | 2025-04-12 | CSPPL | Load Shedding | Plant |  | 13:09 | 14:19 | 1:10 | 28:00 |  | 1.17 | 7.51 | 6.34 | 50000 | 78.05 | 45659.25 | LD Msg 276 for 250 to 200MW and LD Msg 278 for 250MW | 250 | 200
290 | April | 2025-04-18 | CSPPL | Load Shedding | Plant |  | 12:47 | 13:30 | 0:43 | 17:12 |  | 0.673 | 6.78 | 6.107 | 25000 | 81.53 | 13717.4225 | LD Msg 728 for 250 to 225MW and LD Msg 732 for 250MW | 250 | 225
291 | April | 2025-04-19 | CSPPL | Load Shedding | Plant |  | 11:28 | 12:24 | 0:56 | 22:24 |  | 0.898 | 7.12 | 6.222 | 38000 | 77.38 | 26405.1512 | LD Msg 764 for 250 to 212MW | 250 | 212
292 | April | 2025-04-19 | CSPPL | Load Shedding | Plant |  | 12:24 | 13:30 | 1:06 | 26:24 |  | 1.075 | 7.12 | 6.045 | 62000 | 77.38 | 51573.77 | LD Msg 768 for 212 to 188MW and LD Msg 771 for 250MW | 212 | 188
293 | May | 2025-05-12 | CSPPL | Load Shedding | Plant |  | 12:48 | 15:07 | 2:19 | 55:36 |  | 2.125 | 7.46 | 5.335 | 50000 | 77.95 | 82821.875 | LD Msg 366 for 250 to 200MW and LD Msg 373 for 250MW | 250 | 200
294 | May | 2025-05-13 | CSPPL | Load Shedding | Plant |  | 12:03 | 13:53 | 1:50 | 44:00 |  | 1.79 | 7.42 | 5.63 | 25000 | 80.62 | 36077.45 | LD Msg 401 for 250 to 225MW and LD Msg 404 for 250MW | 250 | 225
295 | May | 2025-05-18 | CSPPL | Load Shedding | Plant |  | 12:05 | 14:15 | 2:10 | 52:00 |  | 2.08 | 7.51 | 5.43 | 25000 | 80.03 | 41615.6 | LD Msg 603 for 250 to 225MW and LD Msg 605 for 250MW | 250 | 225
296 | May | 2025-05-19 | CSPPL | Load Shedding | Plant |  | 10:15 | 15:04 | 4:49 | 115:36 |  | 4.445 | 7.56 | 3.115 | 25000 | 78.52 | 87255.35 | LD Msg 622 for 250 to 225MW and LD Msg 627 for 250MW | 228 | 225
297 | May | 2025-05-23 | CSPPL | Load Shedding | Plant |  | 11:21 | 13:34 | 2:13 | 53:12 |  | 2.207 | 7.6 | 5.393 | 25000 | 79.55 | 43891.7125 | LD Msg 743 for 250 to 225MW and LD Msg 745 for 250MW | 250 | 225
298 | May | 2025-05-31 | CSPPL | Load Shedding | Plant |  | 11:45 | 13:50 | 2:05 | 50:00 |  | 1.912 | 6.9 | 4.988 | 25000 | 80.22 | 38345.16 | LD Msg 966 for 250 to 225MW and LD Msg 970 for 250MW | 250 | 225
299 | June | 2025-06-01 | CSPPL | Load Shedding | Plant |  | 10:06 | 13:45 | 3:39 | 87:36 |  | 3.1 | 6.75 | 3.65 | 90000 | 70.3 | 196137 | LD Msg 09 for 200 to 160MW and LD Msg 15 for 250MW | 200 | 160
300 | June | 2025-06-02 | CSPPL | Load Shedding | Plant |  | 11:50 | 14:10 | 2:20 | 56:00 |  | 2.16 | 7.23 | 5.07 | 25000 | 79.96 | 43178.4 | LD Msg 30 for 250 to 225MW and LD Msg 38 for 250MW | 250 | 225
301 | June | 2025-06-03 | CSPPL | Load Shedding | Plant |  | 12:25 | 14:01 | 1:36 | 38:24 |  | 1.46 | 6.97 | 5.51 | 25000 | 81.89 | 29889.85 | LD Msg 60 for 250 to 225MW and LD Msg 62 for 250MW | 250 | 225
302 | June | 2025-06-04 | CSPPL | Load Shedding | Plant |  | 10:31 | 12:59 | 2:28 | 59:12 |  | 2.2 | 7.26 | 5.06 | 50000 | 76.84 | 84524 | LD Msg 90 for 250 to 200MW | 250 | 200
303 | June | 2025-06-04 | CSPPL | Load Shedding | Plant |  | 12:59 | 14:44 | 1:45 | 42:00 |  | 1.55 | 7.26 | 5.71 | 25000 | 76.84 | 29775.5 | LD Msg 91 for 200 to 225MW and LD Msg 99 for 250MW | 200 | 225
304 | June | 2025-06-08 | CSPPL | Load Shedding | Plant |  | 15:27 | 16:55 | 1:28 | 35:12 |  | 0.881 | 7.75 | 6.869 | 41000 | 81.55 | 29456.6755 | LD Msg 211 for 207 to 166MW and LD Msg 213 for 250MW | 207 | 166
305 | June | 2025-06-12 | CSPPL | Load Shedding | Plant |  | 13:49 | 14:43 | 0:54 | 21:36 |  | 0.842 | 7.69 | 6.848 | 50000 | 79.12 | 33309.52 | LD Msg 313 for 250 to 200MW | 250 | 200
306 | June | 2025-06-12 | CSPPL | Load Shedding | Plant |  | 14:44 | 16:27 | 1:43 | 41:12 |  | 1.24 | 7.69 | 6.45 | 70000 | 79.12 | 68676.16 | LD Msg 316 for 200 to 180MW and LD Msg 317 for 250MW | 200 | 180
307 | June | 2025-06-13 | CSPPL | Load Shedding | Plant |  | 9:33 | 16:07 | 6:34 | 157:36 |  | 5.487 | 7.35 | 1.863 | 95000 | 82.99 | 432597.8235 | LD Msg 341 for 178.95 to 155MW and LD Msg 359 for 250MW | 178.95 | 155
308 | June | 2025-06-17 | CSPPL | Load Shedding | Plant |  | 9:38 | 15:03 | 5:25 | 130:00 |  | 2.56 | 5.75 | 3.19 | 115000 | 82.99 | 244322.56 | LD Msg 484 for 168 to 135MW and LD Msg 498 for 250MW | 168 | 135
309 | June | 2025-06-18 | CSPPL | Load Shedding | Plant |  | 11:56 | 15:33 | 3:37 | 86:48 |  | 3.22 | 7.2 | 3.98 | 50000 | 82.99 | 133613.9 | LD Msg 529 for 250 to 200MW and LD Msg 533 for 250MW | 250 | 200
310 | June | 2025-06-19 | CSPPL | Load Shedding | Plant |  | 11:18 | 14:00 | 2:42 | 64:48 |  | 2.46 | 6.79 | 4.33 | 50000 | 82.99 | 102077.7 | LD Msg 555 for 232 to 200MW and LD Msg 562 for 250MW | 232 | 200
311 | June | 2025-06-20 | CSPPL | Load Shedding | Plant |  | 12:32 | 13:30 | 0:58 | 23:12 |  | 0.925 | 6.62 | 5.695 | 50000 | 82.99 | 38382.875 | LD Msg 605 for 250 to 200MW and LD Msg 607 for 250MW | 250 | 200
312 | June | 2025-06-22 | CSPPL | Load Shedding | Plant |  | 10:14 | 11:33 | 1:19 | 31:36 |  | 1.072 | 7.04 | 5.968 | 50000 | 82.99 | 44482.64 | LD Msg 659 for 250 to 200MW | 202 | 200
313 | June | 2025-06-22 | CSPPL | Load Shedding | Plant |  | 11:34 | 14:05 | 2:31 | 60:24 |  | 2.31 | 7.04 | 4.73 | 90000 | 82.99 | 172536.21 | LD Msg for 663 to 160MW and LD Msg 659 for 250MW | 200 | 160
314 | July | 2025-07-06 | CSPPL | Load Shedding | Plant |  | 11:21 | 14:58 | 3:37 | 86:48 |  | 3.09 | 6.65 | 3.56 | 50000 | 84 | 129780 | LD Msg 162 for 250 to 200MW and LD Msg 164 for 250MW | 250 | 200

## WMS Graph
| POA UPWARD | POA DOWNWARD
180 | AMB. TEMP | WIND SPEED

## Modelling New (hidden)
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | CC*Bugt (MTD) | CC*Bugt (YTD) | Capacity | 335.091
1 | April | 4 | 2022-04-01 | 2022 | FY23 | 30 | 208.9997 | 215.9 |  | 29.1001 | 52.2965 | 59637.6 | 335.091 | 82.43% | 7.1967 | 27 | 194.31 | 194.31 | 1987.92 | 53673.84 | 53673.84 | 24.72% | 24.72% | 24.72% | 94.2319 | 94.2319 |  |  |  | 99.75% | 99.75%
2 | May | 5 | 2022-05-01 | 2022 | FY23 | 31 | 221.9002 | 217.9 |  | 33.4 | 55.4377 | 61013.7 | 335.091 | 83.56% | 7.029 | 31 | 217.9 | 412.21 | 1968.1839 | 61013.7 | 114687.54 | 24.47% | 24.47% | 24.59% | 228.4373 | 161.3346 |  |  |  | 99.75% | 99.75%
3 | June | 6 | 2022-06-01 | 2022 | FY23 | 30 | 200.2009 | 192.8 |  | 34.8001 | 54.6583 | 54806.4 | 335.091 | 84.83% | 6.4267 | 30 | 192.8 | 192.8 | 1826.88 | 54806.4 | 54806.4 | 22.72% | 22.72% | 7.744% | 312.8771 | 211.8488 |  |  |  | 99.75% | 99.75%
4 | July | 7 | 2022-07-01 | 2022 | FY23 | 31 | 173.5997 | 168.9 |  | 33.0999 | 51.5649 | 48598.11 | 335.091 | 85.87% | 5.4484 | 31 | 168.9 | 168.9 | 1567.681 | 48598.11 | 48598.11 | 19.49% | 19.49% | 5.078% | 330.6118 | 241.5395 |  |  |  | 99.75% | 99.75%
5 | August | 8 | 2022-08-01 | 2022 | FY23 | 31 | 172.6002 | 174.2 |  | 31.8 | 50.3366 | 49476.24 | 335.091 | 84.76% | 5.6194 | 31 | 174.2 | 174.2 | 1596.0077 | 49476.24 | 49476.24 | 19.85% | 19.85% | 4.101% | 333.3537 | 259.9024 |  |  |  | 99.75% | 99.75%
6 | September | 9 | 2022-09-01 | 2022 | FY23 | 30 | 178.8993 | 192.1 |  | 31.1999 | 52.2506 | 53840.16 | 335.091 | 83.64% | 6.4033 | 30 | 192.1 | 366.3 | 1794.672 | 53840.16 | 103316.4 | 22.32% | 22.32% | 7.137% | 334.1964 | 272.2847 |  |  |  | 99.75% | 99.75%
7 | October | 10 | 2022-10-01 | 2022 | FY23 | 31 | 174.6008 | 202.3 |  | 27.1001 | 49.7239 | 56487.42 | 335.091 | 83.33% | 6.5258 | 31 | 202.3 | 568.6 | 1822.1748 | 56487.42 | 159803.82 | 22.66% | 22.66% | 9.417% | 334.1957 | 281.1291 |  |  |  | 99.75% | 99.75%
8 | November | 11 | 2022-11-01 | 2022 | FY23 | 30 | 133.6994 | 162.9 |  | 20.9 | 42.1871 | 47868.48 | 335.091 | 87.69% | 5.43 | 30 | 162.9 | 731.5 | 1595.616 | 47868.48 | 207672.3 | 19.84% | 19.84% | 10.71% | 334.1957 | 287.7625 |  |  |  | 99.75% | 99.75%
9 | December | 12 | 2022-12-01 | 2022 | FY23 | 31 | 124.4 | 158.6 |  | 15.8915 | 36.0769 | 47682.36 | 335.091 | 89.72% | 5.1161 | 31 | 158.6 | 890.1 | 1538.1406 | 47682.36 | 255354.66 | 19.13% | 19.13% | 11.67% | 334.3514 | 292.939 |  |  |  | 99.75% | 99.75%
10 | January | 1 | 2023-01-01 | 2023 | FY23 | 31 | 133.8993 | 169.0285 |  | 14.3999 | 34.9703 | 50622.66 | 335.091 | 89.38% | 5.4525 | 31 | 169.0285 | 1059.1285 | 1632.989 | 50622.66 | 305977.32 | 20.31% | 20.31% | 12.56% | 334.7318 | 297.1183 |  |  |  | 99.75% | 99.75%
11 | February | 2 | 2023-02-01 | 2023 | FY23 | 28 | 145.4008 | 172.5591 |  | 17.8001 | 40.2521 | 49925.7 | 335.091 | 86.34% | 6.1628 | 28 | 172.5591 | 1231.6877 | 1783.0607 | 49925.7 | 355903.02 | 22.17% | 22.17% | 13.37% | 334.8139 | 300.5452 |  |  |  | 99.75% | 99.75%
12 | March | 3 | 2023-03-01 | 2023 | FY23 | 31 | 195.5989 | 215.7458 |  | 23.6002 | 47.1796 | 59767.29 | 335.091 | 82.67% | 6.9595 | 31 | 215.7458 | 1447.4334 | 1927.9771 | 59767.29 | 415670.31 | 23.97% | 23.97% | 14.28% | 335.0909 | 303.424 |  |  |  | 99.75% | 99.75%
13 | April | 4 | 2023-04-01 | 2023 | FY24 | 30 | 208.9997 | 215.9 |  | 29.1001 | 52.2965 | 58630 | 335.091 | 81.04% | 7.1967 | 30 | 215.9 | 215.9 | 1954.3333 | 58630 | 58630 | 24.3% | 24.3% | 24.3% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
14 | May | 5 | 2023-05-01 | 2023 | FY24 | 31 | 221.9002 | 217.9 |  | 33.4 | 55.4377 | 61780 | 335.091 | 84.61% | 7.029 | 31 | 217.9 | 433.8 | 1992.9032 | 61780 | 120410 | 24.78% | 24.78% | 24.54% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
15 | June | 6 | 2023-06-01 | 2023 | FY24 | 30 | 200.2009 | 192.8 |  | 34.8001 | 54.6583 | 53700 | 335.091 | 83.12% | 6.4267 | 30 | 192.8 | 626.6 | 1790 | 53700 | 637610 | 22.26% | 22.26% | 87.12% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
16 | July | 7 | 2023-07-01 | 2023 | FY24 | 31 | 173.5997 | 168.9 |  | 33.0999 | 51.5649 | 49210 | 335.091 | 86.95% | 5.4484 | 31 | 168.9 | 2242.9334 | 1587.4194 | 49210 | 637610 | 19.74% | 19.74% | 64.99% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
17 | August | 8 | 2023-08-01 | 2023 | FY24 | 31 | 172.6002 | 174.2 |  | 31.8 | 50.3366 | 50100 | 335.091 | 85.83% | 5.6194 | 31 | 174.2 | 969.7 | 1616.129 | 50100 | 273420 | 20.1% | 20.1% | 22.22% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
18 | September | 9 | 2023-09-01 | 2023 | FY24 | 30 | 178.8993 | 192.1 |  | 31.1999 | 52.2506 | 52760 | 335.091 | 81.96% | 6.4033 | 30 | 192.1 | 1161.8 | 1758.6667 | 52760 | 326180 | 21.87% | 21.87% | 22.16% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
19 | October | 10 | 2023-10-01 | 2023 | FY24 | 31 | 174.6008 | 202.3 |  | 27.1001 | 49.7239 | 57190 | 335.091 | 84.36% | 6.5258 | 31 | 202.3 | 1364.1 | 1844.8387 | 57190 | 383370 | 22.94% | 22.94% | 22.28% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
20 | November | 11 | 2023-11-01 | 2023 | FY24 | 30 | 133.6994 | 162.9 |  | 20.9 | 42.1871 | 46900 | 335.091 | 85.92% | 5.43 | 30 | 162.9 | 1527 | 1563.3333 | 46900 | 430270 | 19.44% | 19.44% | 21.93% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
21 | December | 12 | 2023-12-01 | 2023 | FY24 | 31 | 124.4 | 158.6 |  | 15.8915 | 36.0769 | 48280 | 335.091 | 90.85% | 5.1161 | 31 | 158.6 | 1685.6 | 1557.4194 | 48280 | 478550 | 19.37% | 19.37% | 21.64% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
22 | January | 1 | 2024-01-01 | 2024 | FY24 | 31 | 133.8993 | 169.0285 |  | 14.3999 | 34.9703 | 51260 | 335.091 | 90.5% | 5.4525 | 31 | 169.0285 | 1854.6285 | 1653.5484 | 51260 | 529810 | 20.56% | 20.56% | 21.53% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
23 | February | 2 | 2024-02-01 | 2024 | FY24 | 29 | 145.4008 | 172.5591 |  | 17.8001 | 40.2521 | 47290 | 335.091 | 81.78% | 5.9503 | 29 | 172.5591 | 2027.1877 | 1630.6897 | 47290 | 577100 | 20.28% | 20.28% | 21.42% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
24 | March | 3 | 2024-03-01 | 2024 | FY24 | 31 | 195.5989 | 215.7458 |  | 23.6002 | 47.1796 | 60510 | 335.091 | 83.7% | 6.9595 | 31 | 215.7458 | 2242.9334 | 1951.9355 | 60510 | 637610 | 24.27% | 24.27% | 21.66% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
25 | April | 4 | 2024-04-01 | 2024 | FY25 | 30 | 208.9997 | 215.9 |  | 29.1001 | 52.2965 | 59074 | 335.091 | 81.65% | 7.1967 | 30 | 215.9 | 215.9 | 1969.1333 | 59074 | 59074 | 24.49% | 24.49% | 24.49% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
26 | May | 5 | 2024-05-01 | 2024 | FY25 | 31 | 221.9002 | 217.9 |  | 33.4 | 55.4377 | 60423.7 | 335.091 | 82.75% | 7.029 | 31 | 217.9 | 433.8 | 1949.1516 | 60423.7 | 119497.7 | 24.24% | 24.24% | 24.36% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
27 | June | 6 | 2024-06-01 | 2024 | FY25 | 30 | 200.2009 | 192.8 |  | 34.8001 | 54.6583 | 54283.7 | 335.091 | 84.02% | 6.4267 | 30 | 192.8 | 626.6 | 1809.4567 | 54283.7 | 173781.4 | 22.5% | 22.5% | 23.75% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
28 | July | 7 | 2024-07-01 | 2024 | FY25 | 31 | 173.5997 | 168.9 |  | 33.0999 | 51.5649 | 48128.2 | 335.091 | 85.04% | 5.4484 | 31 | 168.9 | 2242.9334 | 1552.5226 | 48128.2 | 633273.4 | 19.3% | 19.3% | 64.54% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
29 | August | 8 | 2024-08-01 | 2024 | FY25 | 31 | 172.6002 | 174.2 |  | 31.8 | 50.3366 | 48997.8 | 335.091 | 83.94% | 5.6194 | 31 | 174.2 | 969.7 | 1580.5742 | 48997.8 | 270907.4 | 19.65% | 19.65% | 22.02% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
30 | September | 9 | 2024-09-01 | 2024 | FY25 | 30 | 178.8993 | 192.1 |  | 31.1999 | 52.2506 | 53326.7 | 335.091 | 82.84% | 6.4033 | 30 | 192.1 | 1161.8 | 1777.5567 | 53326.7 | 324234.1 | 22.1% | 22.1% | 22.03% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
31 | October | 10 | 2024-10-01 | 2024 | FY25 | 31 | 174.6008 | 202.3 |  | 27.1001 | 49.7239 | 55941.2 | 335.091 | 82.52% | 6.5258 | 31 | 202.3 | 1364.1 | 1804.5548 | 55941.2 | 380175.3 | 22.44% | 22.44% | 22.09% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
32 | November | 11 | 2024-11-01 | 2024 | FY25 | 30 | 133.6994 | 162.9 |  | 20.9 | 42.1871 | 47411.9 | 335.091 | 86.86% | 5.43 | 30 | 162.9 | 1527 | 1580.3967 | 47411.9 | 427587.2 | 19.65% | 19.65% | 21.79% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
33 | December | 12 | 2024-12-01 | 2024 | FY25 | 31 | 124.4 | 158.6 |  | 15.8915 | 36.0769 | 47221.3 | 335.091 | 88.85% | 5.1161 | 31 | 158.6 | 1685.6 | 1523.2677 | 47221.3 | 474808.5 | 18.94% | 18.94% | 21.47% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
34 | January | 1 | 2025-01-01 | 2025 | FY25 | 31 | 133.8993 | 169.0285 |  | 14.3999 | 34.9703 | 50133.1 | 335.091 | 88.51% | 5.4525 | 31 | 169.0285 | 1854.6285 | 1617.1968 | 50133.1 | 524941.6 | 20.11% | 20.11% | 21.33% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
35 | February | 2 | 2025-02-01 | 2025 | FY25 | 28 | 145.4008 | 172.5591 |  | 17.8001 | 40.2521 | 49142.5 | 335.091 | 84.99% | 6.1628 | 28 | 172.5591 | 2027.1877 | 1755.0893 | 49142.5 | 574084.1 | 21.82% | 21.82% | 21.37% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
36 | March | 3 | 2025-03-01 | 2025 | FY25 | 31 | 195.5989 | 215.7458 |  | 23.6002 | 47.1796 | 59189.3 | 335.091 | 81.87% | 6.9595 | 31 | 215.7458 | 2242.9334 | 1909.3323 | 59189.3 | 633273.4 | 23.74% | 23.74% | 21.57% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
37 | April | 4 | 2025-04-01 | 2025 | FY26 | 30 | 208.9997 | 215.9 |  | 29.1001 | 52.2965 | 58341.8915 | 335.091 | 80.64% | 7.1967 | 30 | 215.9 | 215.9 | 1944.7297 | 58341.8915 | 58341.8915 | 24.18% | 24.18% | 24.18% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
38 | May | 5 | 2025-05-01 | 2025 | FY26 | 31 | 221.9002 | 217.9 |  | 33.4 | 55.4377 | 59688.0938 | 335.091 | 81.75% | 7.029 | 31 | 217.9 | 433.8 | 1925.4224 | 59688.0938 | 118029.9853 | 23.94% | 23.94% | 24.06% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
39 | June | 6 | 2025-06-01 | 2025 | FY26 | 30 | 200.2009 | 192.8 |  | 34.8001 | 54.6583 | 53615.6559 | 335.091 | 82.99% | 6.4267 | 30 | 192.8 | 626.6 | 1787.1885 | 53615.6559 | 171645.6412 | 22.22% | 22.22% | 23.45% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
40 | July | 7 | 2025-07-01 | 2025 | FY26 | 31 | 173.5997 | 168.9 |  | 33.0999 | 51.5649 | 47542.2495 | 335.091 | 84% | 5.4484 | 10 | 54.4839 | 681.0839 | 1533.621 | 15336.2095 | 186981.8507 | 19.07% | 19.07% | 23.02% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
41 | August | 8 | 2025-08-01 | 2025 | FY26 | 31 | 172.6002 | 174.2 |  | 31.8 | 50.3366 | 48401.3009 | 335.091 | 82.92% | 5.6194 | 0 | 0 | 681.0839 | 1561.3323 | 0 | 186981.8507 | 19.41% |  | 23.02% |  | 335.0909 |  |  |  | 99.75% | 99.75%
42 | September | 9 | 2025-09-01 | 2025 | FY26 | 30 | 178.8993 | 192.1 |  | 31.1999 | 52.2506 | 52670.4088 | 335.091 | 81.82% | 6.4033 | 0 | 0 | 681.0839 | 1755.6803 | 0 | 186981.8507 | 21.83% |  | 23.02% |  | 335.0909 |  |  |  | 99.75% | 99.75%
43 | October | 10 | 2025-10-01 | 2025 | FY26 | 31 | 174.6008 | 202.3 |  | 27.1001 | 49.7239 | 55260.1534 | 335.091 | 81.52% | 6.5258 | 0 | 0 | 681.0839 | 1782.5856 | 0 | 186981.8507 | 22.17% |  | 23.02% |  | 335.0909 |  |  |  | 99.75% | 99.75%
44 | November | 11 | 2025-11-01 | 2025 | FY26 | 30 | 133.6994 | 162.9 |  | 20.9 | 42.1871 | 46828.4717 | 335.091 | 85.79% | 5.43 | 0 | 0 | 681.0839 | 1560.9491 | 0 | 186981.8507 | 19.41% |  | 23.02% |  | 335.0909 |  |  |  | 99.75% | 99.75%
45 | December | 12 | 2025-12-01 | 2025 | FY26 | 31 | 124.4 | 158.6 |  | 15.8915 | 36.0769 | 46646.3954 | 335.091 | 87.77% | 5.1161 | 0 | 0 | 681.0839 | 1504.7224 | 0 | 186981.8507 | 18.71% |  | 23.02% |  | 335.0909 |  |  |  | 99.75% | 99.75%
46 | January | 1 | 2026-01-01 | 2026 | FY26 | 31 | 133.8993 | 169.0285 |  | 14.3999 | 34.9703 | 49522.8134 | 335.091 | 87.43% | 5.4525 | 0 | 0 | 681.0839 | 1597.5101 | 0 | 186981.8507 | 19.86% |  | 23.02% |  | 335.0909 |  |  |  | 99.75% | 99.75%
47 | February | 2 | 2026-02-01 | 2026 | FY26 | 28 | 145.4008 | 172.5591 |  | 17.8001 | 40.2521 | 48840.9958 | 335.091 | 84.47% | 6.1628 | 0 | 0 | 681.0839 | 1744.3213 | 0 | 186981.8507 | 21.69% |  | 23.02% |  | 335.0909 |  |  |  | 99.75% | 99.75%
48 | March | 3 | 2026-03-01 | 2026 | FY26 | 31 | 195.5989 | 215.7458 |  | 23.6002 | 47.1796 | 58468.7638 | 335.091 | 80.88% | 6.9595 | 0 | 0 | 681.0839 | 1886.0892 | 0 | 186981.8507 | 23.45% |  | 23.02% |  | 335.0909 |  |  |  | 99.75% | 99.75%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## Sheet1 (hidden)
Generation loss Due to Load Shedding
Sr. No | Date | From | To | Generation loss(Kwh)
1 | 2023-06-08 | 11:48 | 14:42 | 58633.975
2 | 2023-06-09 | 10:30 | 11:00 | 17357.35
3 | 2023-06-09 | 11:00 | 15:42 | 342913.5
4 | 2023-06-10 | 10:00 | 15:19 | 349821.8218
5 | 2023-06-11 | 10:38 | 15:30 | 310738.9
6 | 2023-06-12 | 10:58 | 15:10 | 316525.9455
7 | 2023-06-13 | 10:23 | 14:42 | 316183.5606
8 | 2023-06-14 | 11:05 | 13:50 | 144889.3388
9 | 2023-06-15 | 12:00 | 12:21 | 9003.0802
10 | 2023-06-20 | 11:06 | 15:12 | 156831.8791
11 | 2023-06-22 | 11:12 | 11:34 | 6931.8371
12 | 2023-06-22 | 11:34 | 15:50 | 145514.9291
13 | 2023-06-23 | 10:16 | 12:15 | 73239.55
14 | 2023-06-23 | 12:15 | 13:46 | 94618.725
15 | 2023-06-23 | 13:46 | 15:20 | 58845.65
16 | 2023-06-24 | 12:35 | 14:00 | 28576.125
17 | 2023-07-01 | 12:17 | 13:35 | 40031.7456
18 | 2023-07-13 | 13:46 | 15:11 | 37769.5908
19 | 2023-07-15 | 10:56 | 12:33 | 62318.771
20 | 2023-07-15 | 12:33 | 15:35 | 179913.2184

## CSPPL_PVS (hidden)
Year Number | OP. year | Year Number | Month | POA(kWh/m2) | GHI (kWh/m2) | Budgeted Energy (MWh) | Tmod | Irradiationce Losses (IAM+NearShadding+Solining) | Bifacial Gain | Temperature Loss | Mismatch Loss | DC Ohmic Loss | Inverter Conversion Loss | MPPT Mismatch Losse | AC Ohmic Loss | Clipping Loss | Plant Uptime | Grid Uptime | Tracker Uptime
Year-0 | 0 | Year-0 | Apr | 215.9 | 208.9997 | 59637.6 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0% |  | YOY Degradation(2nd Year Onwards) | 0.45%
Year-0 | 0 | Year-0 | May | 217.9 | 221.9002 | 61013.7 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0% |  | DC Capacity | 335.096
Year-0 | 0 | Year-0 | Jun | 192.8 | 200.2009 | 54806.4 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Jul | 168.9 | 173.5997 | 48598.11 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Aug | 174.2 | 172.6002 | 49476.24 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Sep | 192.1 | 178.8993 | 53840.16 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Oct | 202.3 | 174.6008 | 56487.42 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Nov | 162.9 | 133.6994 | 47868.48 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Dec | 158.6 | 124.4 | 47682.36 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Jan | 169.0285 | 133.8993 | 50622.66 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Feb | 172.5591 | 145.4008 | 49925.7 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Mar | 215.7458 | 195.5989 | 59767.29 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-04-01 | 215.9 | 208.9997 | 59637.6 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-05-01 | 217.9 | 221.9002 | 61013.7 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-06-01 | 192.8 | 200.2009 | 54806.4 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-07-01 | 168.9 | 173.5997 | 48598.11 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-08-01 | 174.2 | 172.6002 | 49476.24 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-09-01 | 192.1 | 178.8993 | 53840.16 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-10-01 | 202.3 | 174.6008 | 56487.42 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-11-01 | 162.9 | 133.6994 | 47868.48 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-12-01 | 158.6 | 124.4 | 47682.36 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2023-01-01 | 169.0285 | 133.8993 | 50622.66 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2023-02-01 | 172.5591 | 145.4008 | 49925.7 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2023-03-01 | 215.7458 | 195.5989 | 59767.29 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0% | 1000
Year-2 | 2 | Year-2 | 2023-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2024-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2024-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2024-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-04-01 | 215.9 | 208.9997 | 58366.165 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-05-01 | 217.9 | 221.9002 | 61501.99 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-06-01 | 192.8 | 200.2009 | 53458.35 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-07-01 | 168.9 | 173.5997 | 48988.555 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-08-01 | 174.2 | 172.6002 | 49874.55 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-09-01 | 192.1 | 178.8993 | 52522.58 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-10-01 | 202.3 | 174.6008 | 56932.645 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-11-01 | 162.9 | 133.6994 | 46688.95 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-12-01 | 158.6 | 124.4 | 48062.74 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2025-01-01 | 169.0285 | 133.8993 | 51029.33 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2025-02-01 | 172.5591 | 145.4008 | 47077.195 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2025-03-01 | 215.7458 | 195.5989 | 60237.705 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-04-01 | 215.9 | 208.9997 | 58103.5173 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-05-01 | 217.9 | 221.9002 | 61225.231 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-06-01 | 192.8 | 200.2009 | 53217.7874 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-07-01 | 168.9 | 173.5997 | 48768.1065 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-08-01 | 174.2 | 172.6002 | 49650.1145 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-09-01 | 192.1 | 178.8993 | 52286.2284 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-10-01 | 202.3 | 174.6008 | 56676.4481 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-11-01 | 162.9 | 133.6994 | 46478.8497 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-12-01 | 158.6 | 124.4 | 47846.4577 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2026-01-01 | 169.0285 | 133.8993 | 50799.698 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2026-02-01 | 172.5591 | 145.4008 | 46865.3476 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2026-03-01 | 215.7458 | 195.5989 | 59966.6353 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-04-01 | 215.9 | 208.9997 | 57842.0514 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-05-01 | 217.9 | 221.9002 | 60949.7175 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-06-01 | 192.8 | 200.2009 | 52978.3074 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-07-01 | 168.9 | 173.5997 | 48548.65 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-08-01 | 174.2 | 172.6002 | 49426.689 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-09-01 | 192.1 | 178.8993 | 52050.9404 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-10-01 | 202.3 | 174.6008 | 56421.4041 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-11-01 | 162.9 | 133.6994 | 46269.6949 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-12-01 | 158.6 | 124.4 | 47631.1486 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2027-01-01 | 169.0285 | 133.8993 | 50571.0994 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2027-02-01 | 172.5591 | 145.4008 | 46654.4536 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2027-03-01 | 215.7458 | 195.5989 | 59696.7855 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-04-01 | 215.9 | 208.9997 | 57581.7622 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-05-01 | 217.9 | 221.9002 | 60675.4438 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-06-01 | 192.8 | 200.2009 | 52739.905 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-07-01 | 168.9 | 173.5997 | 48330.1811 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-08-01 | 174.2 | 172.6002 | 49204.2689 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-09-01 | 192.1 | 178.8993 | 51816.7111 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-10-01 | 202.3 | 174.6008 | 56167.5078 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-11-01 | 162.9 | 133.6994 | 46061.4813 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-12-01 | 158.6 | 124.4 | 47416.8084 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2028-01-01 | 169.0285 | 133.8993 | 50343.5294 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2028-02-01 | 172.5591 | 145.4008 | 46444.5085 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2028-03-01 | 215.7458 | 195.5989 | 59428.1499 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-04-01 | 215.9 | 208.9997 | 57322.6443 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-05-01 | 217.9 | 221.9002 | 60402.4043 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-06-01 | 192.8 | 200.2009 | 52502.5754 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-07-01 | 168.9 | 173.5997 | 48112.6953 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-08-01 | 174.2 | 172.6002 | 48982.8497 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-09-01 | 192.1 | 178.8993 | 51583.5359 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-10-01 | 202.3 | 174.6008 | 55914.754 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-11-01 | 162.9 | 133.6994 | 45854.2046 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-12-01 | 158.6 | 124.4 | 47203.4328 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2029-01-01 | 169.0285 | 133.8993 | 50116.9835 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2029-02-01 | 172.5591 | 145.4008 | 46235.5082 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2029-03-01 | 215.7458 | 195.5989 | 59160.7233 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-04-01 | 215.9 | 208.9997 | 57064.6924 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-05-01 | 217.9 | 221.9002 | 60130.5935 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-06-01 | 192.8 | 200.2009 | 52266.3138 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-07-01 | 168.9 | 173.5997 | 47896.1882 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-08-01 | 174.2 | 172.6002 | 48762.4269 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-09-01 | 192.1 | 178.8993 | 51351.41 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-10-01 | 202.3 | 174.6008 | 55663.1376 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-11-01 | 162.9 | 133.6994 | 45647.8607 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-12-01 | 158.6 | 124.4 | 46991.0174 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2030-01-01 | 169.0285 | 133.8993 | 49891.4571 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2030-02-01 | 172.5591 | 145.4008 | 46027.4484 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2030-03-01 | 215.7458 | 195.5989 | 58894.5 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-04-01 | 215.9 | 208.9997 | 56807.9013 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-05-01 | 217.9 | 221.9002 | 59860.0058 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-06-01 | 192.8 | 200.2009 | 52031.1154 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-07-01 | 168.9 | 173.5997 | 47680.6553 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-08-01 | 174.2 | 172.6002 | 48542.996 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-09-01 | 192.1 | 178.8993 | 51120.3287 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-10-01 | 202.3 | 174.6008 | 55412.6535 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-11-01 | 162.9 | 133.6994 | 45442.4453 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-12-01 | 158.6 | 124.4 | 46779.5578 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2031-01-01 | 169.0285 | 133.8993 | 49666.9456 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2031-02-01 | 172.5591 | 145.4008 | 45820.3249 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2031-03-01 | 215.7458 | 195.5989 | 58629.4748 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-04-01 | 215.9 | 208.9997 | 56552.2657 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-05-01 | 217.9 | 221.9002 | 59590.6358 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-06-01 | 192.8 | 200.2009 | 51796.9754 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-07-01 | 168.9 | 173.5997 | 47466.0924 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-08-01 | 174.2 | 172.6002 | 48324.5525 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-09-01 | 192.1 | 178.8993 | 50890.2872 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-10-01 | 202.3 | 174.6008 | 55163.2965 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-11-01 | 162.9 | 133.6994 | 45237.9543 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-12-01 | 158.6 | 124.4 | 46569.0498 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2032-01-01 | 169.0285 | 133.8993 | 49443.4443 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2032-02-01 | 172.5591 | 145.4008 | 45614.1335 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2032-03-01 | 215.7458 | 195.5989 | 58365.6421 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-04-01 | 215.9 | 208.9997 | 56297.7805 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-05-01 | 217.9 | 221.9002 | 59322.4779 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-06-01 | 192.8 | 200.2009 | 51563.889 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-07-01 | 168.9 | 173.5997 | 47252.4949 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-08-01 | 174.2 | 172.6002 | 48107.092 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-09-01 | 192.1 | 178.8993 | 50661.2809 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-10-01 | 202.3 | 174.6008 | 54915.0617 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-11-01 | 162.9 | 133.6994 | 45034.3835 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-12-01 | 158.6 | 124.4 | 46359.489 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2033-01-01 | 169.0285 | 133.8993 | 49220.9488 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2033-02-01 | 172.5591 | 145.4008 | 45408.8699 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2033-03-01 | 215.7458 | 195.5989 | 58102.9967 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-04-01 | 215.9 | 208.9997 | 56044.4405 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-05-01 | 217.9 | 221.9002 | 59055.5268 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-06-01 | 192.8 | 200.2009 | 51331.8515 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-07-01 | 168.9 | 173.5997 | 47039.8587 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-08-01 | 174.2 | 172.6002 | 47890.6101 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-09-01 | 192.1 | 178.8993 | 50433.3051 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-10-01 | 202.3 | 174.6008 | 54667.9439 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-11-01 | 162.9 | 133.6994 | 44831.7288 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-12-01 | 158.6 | 124.4 | 46150.8713 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2034-01-01 | 169.0285 | 133.8993 | 48999.4545 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2034-02-01 | 172.5591 | 145.4008 | 45204.5299 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2034-03-01 | 215.7458 | 195.5989 | 57841.5332 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-04-01 | 215.9 | 208.9997 | 55792.2405 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-05-01 | 217.9 | 221.9002 | 58789.7769 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-06-01 | 192.8 | 200.2009 | 51100.8582 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-07-01 | 168.9 | 173.5997 | 46828.1794 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-08-01 | 174.2 | 172.6002 | 47675.1023 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-09-01 | 192.1 | 178.8993 | 50206.3553 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-10-01 | 202.3 | 174.6008 | 54421.9382 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-11-01 | 162.9 | 133.6994 | 44629.986 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-12-01 | 158.6 | 124.4 | 45943.1924 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2035-01-01 | 169.0285 | 133.8993 | 48778.957 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2035-02-01 | 172.5591 | 145.4008 | 45001.1096 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2035-03-01 | 215.7458 | 195.5989 | 57581.2463 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-04-01 | 215.9 | 208.9997 | 55541.1754 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-05-01 | 217.9 | 221.9002 | 58525.2229 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-06-01 | 192.8 | 200.2009 | 50870.9043 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-07-01 | 168.9 | 173.5997 | 46617.4525 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-08-01 | 174.2 | 172.6002 | 47460.5644 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-09-01 | 192.1 | 178.8993 | 49980.4267 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-10-01 | 202.3 | 174.6008 | 54177.0394 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-11-01 | 162.9 | 133.6994 | 44429.1511 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-12-01 | 158.6 | 124.4 | 45736.4481 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2036-01-01 | 169.0285 | 133.8993 | 48559.4517 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2036-02-01 | 172.5591 | 145.4008 | 44798.6046 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2036-03-01 | 215.7458 | 195.5989 | 57322.1307 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-04-01 | 215.9 | 208.9997 | 55291.2401 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-05-01 | 217.9 | 221.9002 | 58261.8594 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-06-01 | 192.8 | 200.2009 | 50641.9853 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-07-01 | 168.9 | 173.5997 | 46407.674 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-08-01 | 174.2 | 172.6002 | 47246.9918 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-09-01 | 192.1 | 178.8993 | 49755.5147 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-10-01 | 202.3 | 174.6008 | 53933.2428 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-11-01 | 162.9 | 133.6994 | 44229.2199 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-12-01 | 158.6 | 124.4 | 45530.634 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2037-01-01 | 169.0285 | 133.8993 | 48340.9342 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2037-02-01 | 172.5591 | 145.4008 | 44597.0108 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2037-03-01 | 215.7458 | 195.5989 | 57064.1811 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-04-01 | 215.9 | 208.9997 | 55042.4296 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-05-01 | 217.9 | 221.9002 | 57999.681 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-06-01 | 192.8 | 200.2009 | 50414.0963 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-07-01 | 168.9 | 173.5997 | 46198.8395 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-08-01 | 174.2 | 172.6002 | 47034.3804 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-09-01 | 192.1 | 178.8993 | 49531.6149 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-10-01 | 202.3 | 174.6008 | 53690.5432 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-11-01 | 162.9 | 133.6994 | 44030.1884 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-12-01 | 158.6 | 124.4 | 45325.7462 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2038-01-01 | 169.0285 | 133.8993 | 48123.3999 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2038-02-01 | 172.5591 | 145.4008 | 44396.3243 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2038-03-01 | 215.7458 | 195.5989 | 56807.3923 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-04-01 | 215.9 | 208.9997 | 54794.7386 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-05-01 | 217.9 | 221.9002 | 57738.6825 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-06-01 | 192.8 | 200.2009 | 50187.2329 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-07-01 | 168.9 | 173.5997 | 45990.9447 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-08-01 | 174.2 | 172.6002 | 46822.7257 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-09-01 | 192.1 | 178.8993 | 49308.7227 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-10-01 | 202.3 | 174.6008 | 53448.9357 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-11-01 | 162.9 | 133.6994 | 43832.0526 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-12-01 | 158.6 | 124.4 | 45121.7803 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2039-01-01 | 169.0285 | 133.8993 | 47906.8446 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2039-02-01 | 172.5591 | 145.4008 | 44196.5408 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2039-03-01 | 215.7458 | 195.5989 | 56551.7591 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-04-01 | 215.9 | 208.9997 | 54548.1623 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-05-01 | 217.9 | 221.9002 | 57478.8584 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-06-01 | 192.8 | 200.2009 | 49961.3903 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-07-01 | 168.9 | 173.5997 | 45783.9854 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-08-01 | 174.2 | 172.6002 | 46612.0234 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-09-01 | 192.1 | 178.8993 | 49086.8334 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-10-01 | 202.3 | 174.6008 | 53208.4155 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-11-01 | 162.9 | 133.6994 | 43634.8083 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-12-01 | 158.6 | 124.4 | 44918.7323 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2040-01-01 | 169.0285 | 133.8993 | 47691.2638 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2040-02-01 | 172.5591 | 145.4008 | 43997.6564 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2040-03-01 | 215.7458 | 195.5989 | 56297.2762 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-04-01 | 215.9 | 208.9997 | 54302.6956 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-05-01 | 217.9 | 221.9002 | 57220.2035 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-06-01 | 192.8 | 200.2009 | 49736.5641 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-07-01 | 168.9 | 173.5997 | 45577.9575 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-08-01 | 174.2 | 172.6002 | 46402.2693 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-09-01 | 192.1 | 178.8993 | 48865.9427 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-10-01 | 202.3 | 174.6008 | 52968.9776 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-11-01 | 162.9 | 133.6994 | 43438.4517 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-12-01 | 158.6 | 124.4 | 44716.598 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2041-01-01 | 169.0285 | 133.8993 | 47476.6532 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2041-02-01 | 172.5591 | 145.4008 | 43799.667 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2041-03-01 | 215.7458 | 195.5989 | 56043.9384 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-04-01 | 215.9 | 208.9997 | 54058.3334 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-05-01 | 217.9 | 221.9002 | 56962.7126 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-06-01 | 192.8 | 200.2009 | 49512.7495 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-07-01 | 168.9 | 173.5997 | 45372.8567 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-08-01 | 174.2 | 172.6002 | 46193.4591 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-09-01 | 192.1 | 178.8993 | 48646.0459 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-10-01 | 202.3 | 174.6008 | 52730.6172 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-11-01 | 162.9 | 133.6994 | 43242.9787 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-12-01 | 158.6 | 124.4 | 44515.3733 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2042-01-01 | 169.0285 | 133.8993 | 47263.0082 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2042-02-01 | 172.5591 | 145.4008 | 43602.5685 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2042-03-01 | 215.7458 | 195.5989 | 55791.7407 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-04-01 | 215.9 | 208.9997 | 53815.0709 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-05-01 | 217.9 | 221.9002 | 56706.3804 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-06-01 | 192.8 | 200.2009 | 49289.9422 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-07-01 | 168.9 | 173.5997 | 45168.6788 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-08-01 | 174.2 | 172.6002 | 45985.5885 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-09-01 | 192.1 | 178.8993 | 48427.1387 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-10-01 | 202.3 | 174.6008 | 52493.3295 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-11-01 | 162.9 | 133.6994 | 43048.3852 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-12-01 | 158.6 | 124.4 | 44315.0542 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2043-01-01 | 169.0285 | 133.8993 | 47050.3247 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2043-02-01 | 172.5591 | 145.4008 | 43406.3569 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2043-03-01 | 215.7458 | 195.5989 | 55540.6779 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-04-01 | 215.9 | 208.9997 | 53572.9031 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-05-01 | 217.9 | 221.9002 | 56451.2017 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-06-01 | 192.8 | 200.2009 | 49068.1374 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-07-01 | 168.9 | 173.5997 | 44965.4198 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-08-01 | 174.2 | 172.6002 | 45778.6534 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-09-01 | 192.1 | 178.8993 | 48209.2166 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-10-01 | 202.3 | 174.6008 | 52257.1095 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-11-01 | 162.9 | 133.6994 | 42854.6675 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-12-01 | 158.6 | 124.4 | 44115.6364 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2044-01-01 | 169.0285 | 133.8993 | 46838.5982 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2044-02-01 | 172.5591 | 145.4008 | 43211.0283 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2044-03-01 | 215.7458 | 195.5989 | 55290.7448 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-04-01 | 215.9 | 208.9997 | 53331.8251 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-05-01 | 217.9 | 221.9002 | 56197.1713 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-06-01 | 192.8 | 200.2009 | 48847.3308 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-07-01 | 168.9 | 173.5997 | 44763.0754 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-08-01 | 174.2 | 172.6002 | 45572.6494 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-09-01 | 192.1 | 178.8993 | 47992.2751 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-10-01 | 202.3 | 174.6008 | 52021.9525 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-11-01 | 162.9 | 133.6994 | 42661.8215 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-12-01 | 158.6 | 124.4 | 43917.116 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2045-01-01 | 169.0285 | 133.8993 | 46627.8245 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2045-02-01 | 172.5591 | 145.4008 | 43016.5787 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2045-03-01 | 215.7458 | 195.5989 | 55041.9364 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-04-01 | 215.9 | 208.9997 | 53091.8318 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-05-01 | 217.9 | 221.9002 | 55944.284 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-06-01 | 192.8 | 200.2009 | 48627.5178 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-07-01 | 168.9 | 173.5997 | 44561.6416 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-08-01 | 174.2 | 172.6002 | 45367.5725 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-09-01 | 192.1 | 178.8993 | 47776.3099 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-10-01 | 202.3 | 174.6008 | 51787.8537 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-11-01 | 162.9 | 133.6994 | 42469.8433 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-12-01 | 158.6 | 124.4 | 43719.489 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2046-01-01 | 169.0285 | 133.8993 | 46417.9993 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2046-02-01 | 172.5591 | 145.4008 | 42823.0041 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2046-03-01 | 215.7458 | 195.5989 | 54794.2477 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-04-01 | 215.9 | 208.9997 | 52852.9186 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-05-01 | 217.9 | 221.9002 | 55692.5347 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-06-01 | 192.8 | 200.2009 | 48408.694 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-07-01 | 168.9 | 173.5997 | 44361.1142 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-08-01 | 174.2 | 172.6002 | 45163.4184 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-09-01 | 192.1 | 178.8993 | 47561.3165 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-10-01 | 202.3 | 174.6008 | 51554.8084 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-11-01 | 162.9 | 133.6994 | 42278.729 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-12-01 | 158.6 | 124.4 | 43522.7513 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2047-01-01 | 169.0285 | 133.8993 | 46209.1183 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2047-02-01 | 172.5591 | 145.4008 | 42630.3005 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2047-03-01 | 215.7458 | 195.5989 | 54547.6736 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%