## Dashboard
Performance Summary NTPC
Month | 2025-07-01
Date | 2025-07-16
Operation Year | 2025
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 2259.5352 | 1474.1615 | -34.76%
| E_Grid MTD(MWh) | 36152.5635 | 16886.587 | -53.29%
| E_Grid YTD (MWh) | 85336.0451 | 39923.0198 | -53.22%
2 | CUF Daily(%) | 17.43% | 11.37% | -34.76%
| CUF MTD(%) | 17.43% | 8.144% | -53.29%
| CUF YTD(%) | 6.154% | 2.879% | -53.22%
3 | PR_Daily (%) | 78.14% | 43.96% | -43.74%
| PR_MTD (%) | 78.14% | 35.44% | -54.65%
| PR_YTD (%) | 42.61% | 20.91% | -50.93%
4 | POA Daily (KWh/m2) | 5.3548 | 6.2096 | 15.96%
| POA MTD(KWh/m2) | 85.6774 | 88.2362 | 2.987%
| POA YTD(KWh/m2) | 370.8387 | 353.5391 | -4.665%
5 | PA Daily | 99.75% | 82.65% | -17.14%
| PA MTD | 99.75% | 84.29% | -15.49%
| PA YTD | 99.75% | 84.88% | -14.91%
6 | GA Daily | 99.75% | 63.35% | -36.49%
| GA MTD | 99.75% | 64.62% | -35.22%
| GA YTD | 99.75% | 74.94% | -24.88%
7 | WPR_Daily | 78.14%
| WPR_MTD | 78.14%
| WPR_YTD | 42.61%

## Annual_KPI
Till Date | 2025-07-16 | 2025-07-01
NTPC Performance Summary- YTD
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2026 | 107 | 370.8387 | 353.5391 | 85336.0451 | 39923.0198 | 42.61% | 20.91% | 6.154% | 2.879% | 99.75% | 74.94% | 99.75% | 84.88% | 0 | 0
NTPC Performance Summary- Monthwise
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-06-01 | 30 | 193.7 | 181.0527 | 34672.0237 | 21336.7105 | 66.3% | 43.65% | 17.84% | 10.98% | 99.75% | 69.58% | 99.75% | 83.44% | 0 | 0
2025-07-01 | 16 | 85.6774 | 88.2362 | 36152.5635 | 16886.587 | 78.14% | 35.44% | 17.43% | 8.144% | 99.75% | 64.62% | 99.75% | 84.29% | 0 | 0
2025-08-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0
2025-09-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0
2025-10-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0
2025-11-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0
2025-12-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0
2026-01-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0
2026-02-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0
2026-03-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0

## Monthly_KPI
Till Date | 2025-07-16
NTPC Performance Summary- MTD
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-07-01 | 16 | 85.6774 | 88.2362 | 36152.5635 | 16886.587 | 78.14% | 35.44% | 17.43% | 8.144% | 99.75% | 64.62% | 99.75% | 84.29% | 0 | 0
Start Date | 2025-07-10
End Date | 2025-07-16
NTPC Performance Summary- Weekly
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-07-01 | 7 | 37.4839 | 41.9358 | 15816.7465 | 8434.1037 | 78.14% | 37.24% | 17.43% | 9.297% | 99.75% | 65.83% | 99.75% | 82.72% | 0 | 0
Formulas:
Days = [Days, row below]-6

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 12 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 12 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 12 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 12 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 12 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 12 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 11.9833 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 12.2 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 12 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 12 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 12 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 12 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 12 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 12 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 12 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 12 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 11.9833 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 12.0167 | [22 empty] | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 12.8667 | 7.7618 |  | 7.6259 |  | 35.857 | 41.1 | 5.0604 | 10.78 | 95.1% |  |  | 100% |  |  | 15.29% |  | 4.859% | 170500.288 | 170500.288 | 9833.888 | 160666.4 | 137.763 | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 12.8333 | 7.6546 |  | 7.482 |  | 35.6211 | 45.9465 | 4.2815 | 10.52 | 97.15% |  |  | 100% |  |  | 15.32% |  | 4.775% | 442288.58 | 168630.98 | 10744.672 | 157886.308 | 137.763 | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 12.0167 | 7.126 |  | 6.9463 |  | 36.2954 | 41.6785 | 4.6258 | 9.89 | 96.5% |  |  | 100% |  |  | 16.75% |  | 4.848% | 458300.3 | 169928.2 | 9644.544 | 160283.656 | 137.763 | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 13.0167 | 7.5342 |  | 7.3569 |  | 36.8447 | 42.9947 | 4.6618 | 11.22 | 97.04% |  |  | 100% |  |  | 17.5% |  | 5.364% | 343723.5 | 188476.2 | 11118.368 | 177357.832 | 137.763 | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 12.9 | 7.253 |  | 7.0824 |  | 37.7718 | 45.8351 | 5.2482 | 12.87 | 94.23% |  |  | 100% |  |  | 16.94% |  | 4.998% | 366117 | 177453 | 12191.168 | 165261.832 | 137.763 | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 12.9 | 7.0135 |  | 6.8333 |  | 36.9701 | 51.8269 | 3.3899 | 8 | 93.24% |  |  | 100% |  |  | 18.31% |  | 5.213% | 462939.7 | 180820.8 | 8474.72 | 172346.08 | 137.763 | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 12.2833 | 3.3954 |  | 3.3064 |  | 38.2699 | 56.6182 | 2.4667 | 9.1 | 95.68% |  |  | 100% |  |  | 11.73% |  | 1.616% | 63500 | 63500 | 10079.072 | 53420.928 | 137.763 | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 12.8 | 5.8482 |  | 5.7493 |  | 37.3711 | 53.3461 | 3.1038 | 8.29 | 85.64% |  |  | 100% |  |  | 11.83% |  | 2.834% | 271442.6 | 102878.4 | 9176.576 | 93701.824 | 137.763 | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 12.55 | 6.1602 |  | 6.1228 |  | 38.7898 | 44.8871 | 2.1203 | 5.76 | 95.29% |  |  | 100% |  |  | 14.44% |  | 3.685% | 226497.5 | 131551.9 | 9712.384 | 121839.516 | 137.763 | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 12.7167 | 5.6167 |  | 5.5703 |  | 35.5238 | 41.6705 | 4.0971 | 16.3 | 94.01% |  |  | 100% |  |  | 12.42% |  | 2.884% | 105121 | 105121 | 9776.064 | 95344.936 | 137.763 | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 12.8833 | 6.6739 |  | 6.526 |  | 32.9638 | 38.8772 | 4.4773 | 11.05 | 95.17% |  |  | 100% |  |  | 15.34% |  | 4.172% | 147586.1 | 147586.1 | 9631.136 | 137954.964 | 137.763 | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 12.9833 | 6.983 |  | 6.7895 |  | 35.4178 | 41.3451 | 4.334 | 8.88 | 20.46% |  |  | 100% |  |  | 6.47% |  | 1.83% | 68893.6 | 68893.6 | 8379.776 | 60513.824 | 137.763 | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 13.05 | 7.01 |  | 6.8592 |  | 34.8947 | 40.3208 | 5.8005 | 11.92 | 96.25% |  |  | 100% |  |  | 15.15% |  | 4.329% | 154268.8 | 154268.8 | 11124.64 | 143144.16 | 137.763 | 7.0355 | 1116265.9961 | 58.76% | 17.23% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 13.0333 | 6.8687 |  | 6.681 |  | 33.2604 | 39.9561 | 4.543 | 10.15 | 94.44% |  |  | 48.01% |  |  | 33.88% |  | 9.433% | 649878.3 | 608806.912 | 9082.848 | 599724.064 | 264.9156 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 13.0833 | 7.268 |  | 7.1118 |  | 34.0127 | 40.5223 | 4.7648 | 10.5 | 86.61% |  |  | 51.94% |  |  | 36.08% |  | 10.69% | 700128.5 | 690206.592 | 10518.176 | 679688.416 | 264.9156 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 12.9833 | 7.0177 |  | 6.8708 |  | 33.8871 | 39.2627 | 5.3956 | 11.14 | 88.4% |  |  | 53.2% |  |  | 38.13% |  | 10.92% | 721455.92 | 704442.08 | 10387.584 | 694054.496 | 264.9156 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 13 | 7.4034 |  | 7.2337 |  | 33.8551 | 39.8859 | 4.2498 | 11.78 | 87.19% |  |  | 53.83% |  |  | 38.67% |  | 11.66% | 754563.1 | 751690.304 | 10564.288 | 741126.016 | 264.9156 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 13 | 7.4604 |  | 7.2688 |  | 34.3154 | 41.1154 | 4.3579 | 11.13 | 85.98% |  |  | 53.9% |  |  | 39.2% |  | 11.87% | 768153.4 | 764872.224 | 10058.944 | 754813.28 | 264.9156 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 13.0333 | 7.6926 |  | 7.5049 |  | 35.1499 | 43.2075 | 4.9429 | 10.91 | 89.46% |  |  | 53.88% |  |  | 38.46% |  | 12.03% | 779681.1 | 775087.232 | 10490.496 | 764596.736 | 264.9156 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 13.0333 | 7.8322 |  | 7.6045 |  | 35.4874 | 42.9734 | 4.7163 | 9.1 | 88.23% |  |  | 53.43% |  |  | 37.86% |  | 12% | 624424.1 | 773478.432 | 10724.832 | 762753.6 | 264.9156 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 13.2333 | 7.97 |  | 7.75 |  | 35.78 | 42.04 | 4.86 | 10.4 | 88.14% |  |  | 53.51% |  |  | 37.84% |  | 12.22% | 789309.4 | 782835.584 | 6000.64 | 776834.944 | 264.9156 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 13.0667 | 7.8259 |  | 7.6177 |  | 35.4855 | 42.6 | 5.5725 | 10.04 | 88.8% |  |  | 53.39% |  |  | 37.73% |  | 11.98% | 643809.3 | 777030.912 | 15542.176 | 761488.736 | 264.9156 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 13.1 | 7.7094 |  | 7.5036 |  | 35.0207 | 41.4598 | 5.1005 | 10.02 | 89.47% |  |  | 53.56% |  |  | 37.96% |  | 11.87% | 772587.3 | 765566.112 | 11070.4 | 754495.712 | 264.9156 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 13.1333 | 7.8878 |  | 7.6709 |  | 34.8011 | 40.956 | 4.2831 | 9.38 | 90.4% |  |  | 56.67% |  |  | 42.09% |  | 13.45% | 778521.2 | 866275.712 | 10856.8 | 855418.912 | 264.9156 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 13.0667 | 7.817 |  | 7.5953 |  | 35.2856 | 41.679 | 3.2931 | 7.73 | 77.47% |  |  | 49.18% |  |  | 31.99% |  | 10.12% | 755932.3 | 654355.552 | 10740.192 | 643615.36 | 264.9156 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 13.1833 | 7.2433 |  | 7.1236 |  | 37.9387 | 42.867 | 3.1106 | 8.13 | 77.93% |  |  | 52.62% |  |  | 37.05% |  | 11% | 720297.6 | 710010.24 | 10818.464 | 699191.776 | 264.9156 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 12.7833 | 1.4674 |  | 1.4336 |  | 33.4049 | 38.974 | 3.0313 | 10.39 | 84.2% |  |  | 70.23% |  |  | 55.94% |  | 3.342% | 214044.1 | 222762.848 | 10296.544 | 212466.304 | 264.9156 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 11.9 | 1.9756 |  | 1.9129 |  | 31.8905 | 35.9754 | 1.278 | 4.15 | 84.49% |  |  | 65.13% |  |  | 56.82% |  | 4.528% | 311234.8 | 299154.144 | 11232.864 | 287921.28 | 264.916 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 11.9833 | 3.6636 |  | 3.4422 |  | 35.8929 | 40.987 | 3.6599 | 8.35 | 88% |  |  | 83.13% |  |  | 86.43% |  | 12.4% | 553997.7 | 728092.48 | 10939.584 | 717152.896 | 241.0544 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 12.8833 | 5.8557 |  | 5.7667 |  | 33.5702 | 39.9877 | 2.7947 | 10.97 | 81.12% |  |  | 76.74% |  |  | 53.71% |  | 12.91% | 605280.6 | 757420.48 | 10822.976 | 746597.504 | 241.0544 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 13.1 | 7.4254 |  | 7.2151 |  | 35.1678 | 41.8979 | 2.5244 | 9.31 | 84.35% |  |  | 77.77% |  |  | 54.09% |  | 16.26% | 972754.6 | 951181.664 | 10413.536 | 940768.128 | 241.0544 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 13.6 | 7.4864 |  | 7.3007 |  | 34.807 | 40.9876 | 5.4483 | 11.7 | 91.68% |  |  | 78.29% |  |  | 54.49% |  | 16.58% | 986403.4 | 968779.328 | 9790.912 | 958988.416 | 241.0544 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 12.7833 | 6.5278 |  | 6.336 |  | 34.118 | 39.8877 | 5.3578 | 10.94 | 91.98% |  |  | 79.26% |  |  | 56.2% |  | 14.84% | 883585.4 | 868475.936 | 10188.544 | 858287.392 | 241.054 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 12.5 | 3.4647 |  | 3.4181 |  | 31.4815 | 37.9787 | 5.4005 | 11.49 | 74.12% |  |  | 79.76% |  |  | 52.77% |  | 7.516% | 449063.4 | 444469.632 | 9649.472 | 434820.16 | 241.054 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 13.15 | 6.9011 |  | 6.8287 |  | 34.2469 | 40.8976 | 4.0327 | 9.65 | 86.04% |  |  | 77.75% |  |  | 49.86% |  | 14.19% | 848244.8 | 831428.416 | 10654.048 | 820774.368 | 241.054 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 13.0333 | 5.9409 |  | 5.9192 |  | 34.3087 | 40.9865 | 3.8774 | 7.9 | 92.2% |  |  | 77.39% |  |  | 52.25% |  | 12.89% | 766742.24 | 756101.056 | 10501.824 | 745599.232 | 241.054 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 13.1833 | 6.8896 |  | 6.7475 |  | 35.2598 | 41.9899 | 4.5089 | 10.54 | 36.52% |  |  | 100% |  |  | 30.65% |  | 8.618% | 507601.4 | 508654.528 | 10053.792 | 498600.736 | 241.054 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 12.6 | 6.1945 |  | 6.0842 |  | 34.6453 | 41.9221 | 4.1952 | 9.07 | 81.62% |  |  | 76.51% |  |  | 50.27% |  | 12.74% | 761284.8 | 752698.272 | 15389.824 | 737308.448 | 241.054 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 11.6667 | 5.6114 |  | 5.5484 |  | 33.3947 | 39.7898 | 3.086 | 14.8 | 82.59% |  |  | 79.64% |  |  | 56.52% |  | 13.07% | 709762.3 | 772715.968 | 16803.776 | 755912.192 | 241.054 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 12.4833 | 4.1085 |  | 4.0081 |  | 29.777 | 35.7899 | 2.339 | 9.81 | 63.22% |  |  | 80.37% |  |  | 48.21% |  | 8.05% | 377237.4 | 480910.72 | 15165.728 | 465744.992 | 241.054 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 12.9 | 4.6658 |  | 4.3544 |  | 30.8834 | 35.88 | 3.3712 | 7.35 | 76.96% |  |  | 98.27% |  |  | 83.16% |  | 15.09% | 522414.6 | 887755.52 | 14861.088 | 872894.432 | 241.054 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 13.0333 | 4.2911 |  | 4.0604 |  | 30.4445 | 35.99 | 3.8201 | 8.7 | 79.78% |  |  | 100% |  |  | 77.48% |  | 13.11% | 257873.6 | 772887.488 | 14512.864 | 758374.624 | 241.054 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 12.0167 | 4.3656 |  | 5.14 |  | 31.6847 | 37.0123 | 4.2296 | 8.67 | 91.79% |  |  | 100% |  |  | 83.67% |  | 17.92% | 709323.3 | 1050239.936 | 13542.56 | 1036697.376 | 241.054 | 6.4567 | 1155734.1227 | 66.3% | 17.84% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 270
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | 12.9 | 6.2419 |  | 6.0782 |  | 32.3273 | 36.8766 | 4.7993 | 9.76 | 83.36% |  |  | 74.49% |  |  | 55.81% |  | 14.13% | 842223.7 | 830947.328 | 13208.032 | 817739.296 | 241.054 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | 12.55 | 3.6547 |  | 3.5404 |  | 31.5946 | 37.6566 | 3.9681 | 10.87 | 84.52% |  |  | 61.25% |  |  | 53.83% |  | 7.941% | 598021.69 | 650737.184 | 14169.248 | 636567.936 | 334 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | 12.4667 | 3.1467 |  | 3.1357 |  | 30.0325 | 36.9544 | 3.0713 | 7.12 | 87.38% |  |  | 48.49% |  |  | 51.68% |  | 6.752% | 495131.7 | 555122.304 | 13909.472 | 541212.832 | 334 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | 13.0167 | 5.8133 |  | 5.6918 |  | 30.8381 | 36.8877 | 2.8563 | 8.39 | 87.67% |  |  | 59.06% |  |  | 48.12% |  | 11.41% | 643096.9 | 923373.408 | 8545.952 | 914827.456 | 334 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | 12.9833 | 6.6631 |  | 6.4543 |  | 31.6394 | 38.3487 | 3.6162 | 10.43 | 86.33% |  |  | 63.88% |  |  | 54.87% |  | 14.76% | 986403.7 | 1189255.648 | 6445.472 | 1182810.176 | 334 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | 12.9167 | 5.9959 |  | 5.761 |  | 31.5823 | 37.8755 | 3.796 | 9.25 | 87.68% |  |  | 64.35% |  |  | 58.07% |  | 13.94% | 1136780.3 | 1132394.304 | 15106.4 | 1117287.904 | 334 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | 12.3 | 5.8486 |  | 5.6344 |  | 31.0807 | 37.9877 | 4.1355 | 8.83 | 80.82% |  |  | 61.79% |  |  | 55.41% |  | 13.01% | 1059589.16 | 1058056.864 | 15246.816 | 1042810.048 | 334 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | 12.9333 | 4.7119 |  | 4.6055 |  | 31.3505 | 37.7659 | 3.7157 | 7.51 | 84.66% |  |  | 68.02% |  |  | 61.53% |  | 11.81% | 1024729.2 | 1027397.28 | 14837.728 | 1012559.552 | 357.3265 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | 12.7667 | 5.5533 |  | 5.3991 |  | 31.8112 | 36.7899 | 4.5783 | 10.05 | 87.23% |  |  | 71.75% |  |  | 61.51% |  | 13.84% | 1206750.26 | 1203729.664 | 17061.504 | 1186668.16 | 357.3265 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | 12.9 | 5.7084 |  | 5.5468 |  | 31.8931 | 37.7899 | 3.8842 | 8.51 | 87.47% |  |  | 68.37% |  |  | 57.42% |  | 13.27% | 1183641.1 | 1170956.352 | 13269.056 | 1157687.296 | 363.512 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | 12.6833 | 6.0486 |  | 6.0011 |  | 31.3342 | 36.8899 | 3.8624 | 18.28 | 86.74% |  |  | 64.58% |  |  | 52.37% |  | 13.09% | 1186180.5 | 1157509.184 | 15096.064 | 1142413.12 | 363.512 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | 12.95 | 6.1713 |  | 6.0546 |  | 30.1634 | 35.9787 | 2.6214 | 8.35 | 78.47% |  |  | 69.2% |  |  | 52.94% |  | 13.35% | 1199189.2 | 1179714.496 | 14617.632 | 1165096.864 | 363.512 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | 13.0167 | 7.401 |  | 7.1413 |  | 37.7099 | 51.6433 | 2.2238 | 3.795 | 80.77% |  |  | 64.75% |  |  | 49.97% |  | 14.87% | 1330504.385 | 1311652.416 | 14445.344 | 1297207.072 | 363.512 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | 13 | 6.0364 |  | 5.7248 |  | 38.1813 | 48.4757 | 1.6616 | 3.03 | 82.02% |  |  | 65.39% |  |  | 54.8% |  | 13.07% | 1157069.1 | 1154352.704 | 13971.232 | 1140381.472 | 363.512 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | 12.7833 | 5.2716 |  | 5.2576 |  | 30.4039 | 36.9876 | 3.607 | 14.52 | 80.93% |  |  | 65.17% |  |  | 55.31% |  | 12.12% | 1068541.3 | 1071409.408 | 14253.024 | 1057156.384 | 363.512 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | 12.6167 | 6.3938 |  | 6.2096 |  | 31.4932 | 37.9766 | 3.6339 | 7.68 | 82.65% |  |  | 63.35% |  |  | 65.31% |  | 16.9% | 1492179.72 | 1482511.904 | 8350.432 | 1474161.472 | 363.512 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.3548 | 2259535.2171 | 78.14% | 17.43% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4903 | 2070717.3855 | 69.84% | 15.98% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2967 | 2530058.1967 | 74.41% | 19.52% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.4516 | 2951212.9577 | 84.71% | 22.77% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.4633 | 2514299.545 | 85.22% | 19.4% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.1613 | 2511049.6684 | 90.1% | 19.38% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 5.429 | 2646212.037 | 90.26% | 20.42% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.2 | 2632270.0663 | 78.62% | 20.31% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 6.9097 | 3116339.1887 | 83.52% | 24.05% | 99.75% | 99.75% |  |  |  | 0 | [5 empty] | 540
2026-04-01 | 2027 | 2026 | 2026-04-01 | 30 | [32 empty] | 0
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Basic Data
Equipment | Affected DC Capacity | Plant Equivalent Weightage | Fault Category Plant BD sheet |  | IS Number |  | Inverter Number | SCB Number |  | String Type | Equipment | Inverter Module Number |  | Status |  | Plant capacity | Month No. | Month Name
IS1Inv1M1 | 957 | 0.2633% | Module |  | IS1 |  | Inv1 | SCB1 |  | Str_Typ1(545*29) | Tx | M1 |  | Open |  | 363511.955
IS1Inv1M2 | 1084.6 | 0.2984% | Cables |  | IS2 |  | Inv2 | SCB2 |  | Str_Typ2 (550*29) | MVP | M2 |  | Close
IS1Inv1M3 | 829.4 | 0.2282% | String Fuses |  | IS3 |  |  | SCB3 |  |  | Aux_Tx | M3
IS1Inv1M4 | 1276 | 0.351% | SCB |  | IS4 |  |  | SCB4 |  |  | MCR_MVP_Inc1 | M4
IS1Inv2M1 | 1339.8 | 0.3686% | Inverter |  | IS5 |  |  | SCB5 |  |  | MCR_MVP_Inc2
IS1Inv2M2 | 1244.1 | 0.3422% | IDT |  | IS6 |  |  | SCB6 |  |  | MCR_MVP_Inc3
IS1Inv2M3 | 1116.5 | 0.3071% | PTR |  | IS7 |  |  | SCB7 |  |  | MCR_MVP_Inc4
IS1Inv2M4 | 1244.1 | 0.3422% | MV Panel |  | IS8 |  |  | SCB8 |  |  | MCR_MVP_Inc5
IS2Inv1M1 | 1180.3 | 0.3247% | Metering System Plant |  | IS9 |  |  | SCB9 |  |  | MCR_MVP_Inc8
IS2Inv1M2 | 1196.25 | 0.3291% | Grid System |  | IS10 |  |  | SCB10 |  |  | MCR_MVP_Inc9
IS2Inv1M3 | 1244.1 | 0.3422% | Metering System Grid |  | IS11 | [5 empty] | MCR_MVP_Inc10
IS2Inv1M4 | 1339.8 | 0.3686% | WMS |  | IS12 | [5 empty] | MCR_MVP_Inc11
IS2Inv2M1 | 1244.1 | 0.3422% | MMS |  | IS13 | [5 empty] | MCR_MVP_Inc12
IS2Inv2M2 | 781.55 | 0.215% | Battery Charger_MCR |  | IS14 | [5 empty] | MCR_MVP_OG1
IS2Inv2M3 | 430.65 | 0.1185% | IC_UPS |  | IS15 | [5 empty] | MCR_MVP_OG2
IS2Inv2M4 | 1228.15 | 0.3379% | IC_Auxiliary Tranformer |  | IS16 | [5 empty] | Power_Tx1
IS3Inv1M1 | 1264.4 | 0.3478% | IC_Auxiliary DB |  | IS17 | [5 empty] | Power_Tx2
IS3Inv1M2 | 1327.62 | 0.3652% | IC_SCADA Panel |  | IS18 | [5 empty] | Line_Bay1
IS3Inv1M3 | 1232.79 | 0.3391% | Connectors |  | IS19
IS3Inv1M4 | 1280.205 | 0.3522% |  |  | IS20
IS3Inv2M1 | 1296.01 | 0.3565% |  |  | IS21
IS3Inv2M2 | 1264.4 | 0.3478% |  |  | IS22
IS3Inv2M3 | 1296.01 | 0.3565% |  |  | IS23
IS3Inv2M4 | 1264.4 | 0.3478% |  |  | IS24
IS4Inv1M1 | 1180.3 | 0.3247% |  |  | IS25
IS4Inv1M2 | 1307.9 | 0.3598% |  |  | IS26
IS4Inv1M3 | 1307.9 | 0.3598% |  |  | IS27
IS4Inv1M4 | 1228.15 | 0.3379% |  |  | IS28
IS4Inv2M1 | 1323.85 | 0.3642% |  |  | IS29
IS4Inv2M2 | 1100.55 | 0.3028% |  |  | IS30
IS4Inv2M3 | 1036.75 | 0.2852% |  |  | IS31
IS4Inv2M4 | 1036.75 | 0.2852% |  |  | IS32
IS5Inv1M1 | 861.3 | 0.2369% |  |  | IS33
IS5Inv1M2 | 1212.2 | 0.3335% |  |  | IS34
IS5Inv1M3 | 797.5 | 0.2194% |  |  | IS35
IS5Inv1M4 | 893.2 | 0.2457% |  |  | IS36
IS5Inv2M1 | 1307.9 | 0.3598% |  |  | IS37
IS5Inv2M2 | 1307.9 | 0.3598% |  |  | IS38
IS5Inv2M3 | 893.2 | 0.2457% |  |  | IS39
IS5Inv2M4 | 829.4 | 0.2282% |  |  | IS40
IS6Inv1M1 | 1244.1 | 0.3422% |  |  | IS41
IS6Inv1M2 | 1276 | 0.351% |  |  | IS42
IS6Inv1M3 | 1307.9 | 0.3598% |  |  | IS43
IS6Inv1M4 | 1244.1 | 0.3422% |  |  | IS44
IS6Inv2M1 | 1244.1 | 0.3422% |  |  | IS45
IS6Inv2M2 | 1307.9 | 0.3598% |  |  | IS46
IS6Inv2M3 | 1276 | 0.351% |  |  | IS47
IS6Inv2M4 | 1276 | 0.351% |  |  | IS48
IS7Inv1M1 | 1276 | 0.351% |  |  | IS49
IS7Inv1M2 | 1291.95 | 0.3554% |  |  | IS50
IS7Inv1M3 | 1339.8 | 0.3686% |  |  | IS51
IS7Inv1M4 | 1276 | 0.351% |  |  | IS52
IS7Inv2M1 | 861.3 | 0.2369%
IS7Inv2M2 | 1276 | 0.351%
IS7Inv2M3 | 1244.1 | 0.3422%
IS7Inv2M4 | 1244.1 | 0.3422%
IS8Inv1M1 | 1244.1 | 0.3422%
IS8Inv1M2 | 1244.1 | 0.3422%
IS8Inv1M3 | 1276 | 0.351%
IS8Inv1M4 | 1244.1 | 0.3422%
IS8Inv2M1 | 1212.2 | 0.3335%
IS8Inv2M2 | 1244.1 | 0.3422%
IS8Inv2M3 | 1164.35 | 0.3203%
IS8Inv2M4 | 1339.8 | 0.3686%
IS9Inv1M1 | 1276 | 0.351%
IS9Inv1M2 | 1307.9 | 0.3598%
IS9Inv1M3 | 1244.1 | 0.3422%
IS9Inv1M4 | 1212.2 | 0.3335%
IS9Inv2M1 | 1084.6 | 0.2984%
IS9Inv2M2 | 1148.4 | 0.3159%
IS9Inv2M3 | 1180.3 | 0.3247%
IS9Inv2M4 | 1084.6 | 0.2984%
IS10Inv1M1 | 0 | 0%
IS10Inv1M2 | 0 | 0%
IS10Inv1M3 | 0 | 0%
IS10Inv1M4 | 0 | 0%
IS10Inv2M1 | 0 | 0%
IS10Inv2M2 | 0 | 0%
IS10Inv2M3 | 0 | 0%
IS10Inv2M4 | 0 | 0%
IS11Inv1M1 | 382.8 | 0.1053%
IS11Inv1M2 | 303.05 | 0.08337%
IS11Inv1M3 | 0 | 0%
IS11Inv1M4 | 0 | 0%
IS12Inv1M1 | 0 | 0%
IS12Inv1M2 | 0 | 0%
IS12Inv1M3 | 0 | 0%
IS12Inv1M4 | 0 | 0%
IS12Inv2M1 | 1339.8 | 0.3686%
IS12Inv2M2 | 1339.8 | 0.3686%
IS12Inv2M3 | 1307.9 | 0.3598%
IS12Inv2M4 | 1307.9 | 0.3598%
IS13Inv1M1 | 1339.8 | 0.3686%
IS13Inv1M2 | 1276 | 0.351%
IS13Inv1M3 | 1339.8 | 0.3686%
IS13Inv1M4 | 1307.9 | 0.3598%
IS13Inv2M1 | 1244.1 | 0.3422%
IS13Inv2M2 | 1148.4 | 0.3159%
IS13Inv2M3 | 1307.9 | 0.3598%
IS13Inv2M4 | 1307.9 | 0.3598%
IS14Inv1M1 | 1339.8 | 0.3686%
IS14Inv1M2 | 1260.05 | 0.3466%
IS14Inv1M3 | 1084.6 | 0.2984%
IS14Inv1M4 | 1307.9 | 0.3598%
IS14Inv2M1 | 1116.5 | 0.3071%
IS14Inv2M2 | 1276 | 0.351%
IS14Inv2M3 | 1228.15 | 0.3379%
IS14Inv2M4 | 1307.9 | 0.3598%
IS15Inv1M1 | 1020.8 | 0.2808%
IS15Inv1M2 | 1260.05 | 0.3466%
IS15Inv1M3 | 1276 | 0.351%
IS15Inv1M4 | 1164.35 | 0.3203%
IS15Inv2M1 | 1276 | 0.351%
IS15Inv2M2 | 1307.9 | 0.3598%
IS15Inv2M3 | 1276 | 0.351%
IS15Inv2M4 | 1307.9 | 0.3598%
IS16Inv1M1 | 1276 | 0.351%
IS16Inv1M2 | 1244.1 | 0.3422%
IS16Inv1M3 | 1307.9 | 0.3598%
IS16Inv1M4 | 1180.3 | 0.3247%
IS17Inv1M1 | 287.1 | 0.07898%
IS17Inv1M2 | 63.8 | 0.01755%
IS17Inv1M3 | 0 | 0%
IS17Inv1M4 | 0 | 0%
IS17Inv2M1 | 0 | 0%
IS17Inv2M2 | 0 | 0%
IS17Inv2M3 | 0 | 0%
IS17Inv2M4 | 0 | 0%
IS18Inv1M1 | 1291.95 | 0.3554%
IS18Inv1M2 | 1212.2 | 0.3335%
IS18Inv1M3 | 1339.8 | 0.3686%
IS18Inv1M4 | 1244.1 | 0.3422%
IS18Inv2M1 | 1307.9 | 0.3598%
IS18Inv2M2 | 1148.4 | 0.3159%
IS18Inv2M3 | 1052.7 | 0.2896%
IS18Inv2M4 | 1148.4 | 0.3159%
IS19Inv1M1 | 1148.4 | 0.3159%
IS19Inv1M2 | 1116.5 | 0.3071%
IS19Inv1M3 | 1276 | 0.351%
IS19Inv1M4 | 1212.2 | 0.3335%
IS19Inv2M1 | 957 | 0.2633%
IS19Inv2M2 | 797.5 | 0.2194%
IS19Inv2M3 | 765.6 | 0.2106%
IS19Inv2M4 | 1180.3 | 0.3247%
IS20Inv1M1 | 1291.95 | 0.3554%
IS20Inv1M2 | 1164.35 | 0.3203%
IS20Inv1M3 | 1276 | 0.351%
IS20Inv1M4 | 1339.8 | 0.3686%
IS20Inv2M1 | 1323.85 | 0.3642%
IS20Inv2M2 | 350.9 | 0.09653%
IS20Inv2M3 | 1212.2 | 0.3335%
IS20Inv2M4 | 1116.5 | 0.3071%
IS21Inv1M1 | 988.9 | 0.272%
IS21Inv1M2 | 765.6 | 0.2106%
IS21Inv1M3 | 510.4 | 0.1404%
IS21Inv1M4 | 861.3 | 0.2369%
IS21Inv2M1 | 1004.85 | 0.2764%
IS21Inv2M2 | 829.4 | 0.2282%
IS21Inv2M3 | 430.65 | 0.1185%
IS21Inv2M4 | 558.25 | 0.1536%
IS22Inv1M1 | 1116.5 | 0.3071%
IS22Inv1M2 | 1276 | 0.351%
IS22Inv1M3 | 1307.9 | 0.3598%
IS22Inv1M4 | 1339.8 | 0.3686%
IS22Inv2M1 | 797.5 | 0.2194%
IS22Inv2M2 | 988.9 | 0.272%
IS22Inv2M3 | 813.45 | 0.2238%
IS22Inv2M4 | 1244.1 | 0.3422%
IS23Inv1M1 | 1180.3 | 0.3247%
IS23Inv1M2 | 797.5 | 0.2194%
IS23Inv1M3 | 1244.1 | 0.3422%
IS23Inv1M4 | 1148.4 | 0.3159%
IS23Inv2M1 | 1260.05 | 0.3466%
IS23Inv2M2 | 1276 | 0.351%
IS23Inv2M3 | 1212.2 | 0.3335%
IS23Inv2M4 | 1180.3 | 0.3247%
IS24Inv1M1 | 0 | 0%
IS24Inv1M2 | 0 | 0%
IS24Inv1M3 | 0 | 0%
IS24Inv1M4 | 0 | 0%
IS24Inv2M1 | 0 | 0%
IS24Inv2M2 | 0 | 0%
IS24Inv2M3 | 0 | 0%
IS24Inv2M4 | 0 | 0%
IS25Inv1M1 | 0 | 0%
IS25Inv1M2 | 0 | 0%
IS25Inv1M3 | 0 | 0%
IS25Inv1M4 | 0 | 0%
IS25Inv2M1 | 0 | 0%
IS25Inv2M2 | 0 | 0%
IS25Inv2M3 | 0 | 0%
IS25Inv2M4 | 0 | 0%
IS26Inv1M1 | 0 | 0%
IS26Inv1M2 | 0 | 0%
IS26Inv1M3 | 0 | 0%
IS26Inv1M4 | 0 | 0%
IS26Inv2M1 | 0 | 0%
IS26Inv2M2 | 0 | 0%
IS26Inv2M3 | 0 | 0%
IS26Inv2M4 | 0 | 0%
IS27Inv1M1 | 0 | 0%
IS27Inv1M2 | 0 | 0%
IS27Inv1M3 | 0 | 0%
IS27Inv1M4 | 0 | 0%
IS27Inv2M1 | 0 | 0%
IS27Inv2M2 | 0 | 0%
IS27Inv2M3 | 0 | 0%
IS27Inv2M4 | 0 | 0%
IS28Inv1M1 | 1244.1 | 0.3422%
IS28Inv1M2 | 1180.3 | 0.3247%
IS28Inv1M3 | 733.7 | 0.2018%
IS28Inv1M4 | 669.9 | 0.1843%
IS28Inv2M1 | 861.3 | 0.2369%
IS28Inv2M2 | 0 | 0%
IS28Inv2M3 | 350.9 | 0.09653%
IS28Inv2M4 | 701.8 | 0.1931%
IS29Inv1M1 | 988.9 | 0.272%
IS29Inv1M2 | 733.7 | 0.2018%
IS29Inv1M3 | 861.3 | 0.2369%
IS29Inv1M4 | 988.9 | 0.272%
IS29Inv2M1 | 1180.3 | 0.3247%
IS29Inv2M2 | 1052.7 | 0.2896%
IS29Inv2M3 | 893.2 | 0.2457%
IS29Inv2M4 | 1164.35 | 0.3203%
IS30Inv1M1 | 1244.1 | 0.3422%
IS30Inv1M2 | 1276 | 0.351%
IS30Inv1M3 | 1116.5 | 0.3071%
IS30Inv1M4 | 1276 | 0.351%
IS30Inv2M1 | 1212.2 | 0.3335%
IS30Inv2M2 | 1084.6 | 0.2984%
IS30Inv2M3 | 1020.8 | 0.2808%
IS30Inv2M4 | 1339.8 | 0.3686%
IS31Inv1M1 | 1116.5 | 0.3071%
IS31Inv1M2 | 1307.9 | 0.3598%
IS31Inv1M3 | 1307.9 | 0.3598%
IS31Inv1M4 | 1339.8 | 0.3686%
IS31Inv2M1 | 1291.95 | 0.3554%
IS31Inv2M2 | 1339.8 | 0.3686%
IS31Inv2M3 | 1339.8 | 0.3686%
IS31Inv2M4 | 1339.8 | 0.3686%
IS32Inv1M1 | 1084.6 | 0.2984%
IS32Inv1M2 | 1244.1 | 0.3422%
IS32Inv1M3 | 1307.9 | 0.3598%
IS32Inv1M4 | 1339.8 | 0.3686%
IS32Inv2M1 | 1563.1 | 0.43%
IS32Inv2M2 | 1084.6 | 0.2984%
IS32Inv2M3 | 1276 | 0.351%
IS32Inv2M4 | 1212.2 | 0.3335%
IS33Inv1M1 | 1180.3 | 0.3247%
IS33Inv1M2 | 1244.1 | 0.3422%
IS33Inv1M3 | 925.1 | 0.2545%
IS33Inv1M4 | 1276 | 0.351%
IS33Inv2M1 | 1148.4 | 0.3159%
IS33Inv2M2 | 1116.5 | 0.3071%
IS33Inv2M3 | 1260.05 | 0.3466%
IS33Inv2M4 | 957 | 0.2633%
IS34Inv1M1 | 1084.6 | 0.2984%
IS34Inv1M2 | 893.2 | 0.2457%
IS34Inv1M3 | 1180.3 | 0.3247%
IS34Inv1M4 | 1180.3 | 0.3247%
IS34Inv2M1 | 1307.9 | 0.3598%
IS34Inv2M2 | 1307.9 | 0.3598%
IS34Inv2M3 | 1212.2 | 0.3335%
IS34Inv2M4 | 1276 | 0.351%
IS35Inv1M1 | 893.2 | 0.2457%
IS35Inv1M2 | 1180.3 | 0.3247%
IS35Inv1M3 | 1020.8 | 0.2808%
IS35Inv1M4 | 893.2 | 0.2457%
IS35Inv2M1 | 127.6 | 0.0351%
IS35Inv2M2 | 0 | 0%
IS35Inv2M3 | 797.5 | 0.2194%
IS35Inv2M4 | 1180.3 | 0.3247%
IS36Inv1M1 | 829.4 | 0.2282%
IS36Inv1M2 | 1020.8 | 0.2808%
IS36Inv1M3 | 957 | 0.2633%
IS36Inv1M4 | 893.2 | 0.2457%
IS36Inv2M1 | 1244.1 | 0.3422%
IS36Inv2M2 | 1052.7 | 0.2896%
IS36Inv2M3 | 1148.4 | 0.3159%
IS36Inv2M4 | 957 | 0.2633%
IS37Inv1M1 | 1228.15 | 0.3379%
IS37Inv1M2 | 1132.45 | 0.3115%
IS37Inv1M3 | 669.9 | 0.1843%
IS37Inv1M4 | 733.7 | 0.2018%
IS37Inv2M1 | 1084.6 | 0.2984%
IS37Inv2M2 | 1228.15 | 0.3379%
IS37Inv2M3 | 1291.95 | 0.3554%
IS37Inv2M4 | 1132.45 | 0.3115%
IS38Inv1M1 | 0 | 0%
IS38Inv1M2 | 0 | 0%
IS38Inv1M3 | 0 | 0%
IS38Inv1M4 | 0 | 0%
IS38Inv2M1 | 0 | 0%
IS38Inv2M2 | 0 | 0%
IS38Inv2M3 | 0 | 0%
IS38Inv2M4 | 0 | 0%
IS39Inv1M1 | 0 | 0%
IS39Inv1M2 | 0 | 0%
IS39Inv1M3 | 0 | 0%
IS39Inv1M4 | 191.4 | 0.05265%
IS39Inv2M1 | 0 | 0%
IS39Inv2M2 | 0 | 0%
IS39Inv2M3 | 223.3 | 0.06143%
IS39Inv2M4 | 0 | 0%
IS40Inv1M1 | 1291.95 | 0.3554%
IS40Inv1M2 | 1196.25 | 0.3291%
IS40Inv1M3 | 1228.15 | 0.3379%
IS40Inv1M4 | 287.1 | 0.07898%
IS40Inv2M1 | 0 | 0%
IS40Inv2M2 | 0 | 0%
IS40Inv2M3 | 0 | 0%
IS40Inv2M4 | 287.1 | 0.07898%
IS41Inv1M1 | 1036.75 | 0.2852%
IS41Inv1M2 | 909.15 | 0.2501%
IS41Inv1M3 | 1052.7 | 0.2896%
IS41Inv1M4 | 1084.6 | 0.2984%
IS41Inv2M1 | 1148.4 | 0.3159%
IS41Inv2M2 | 1244.1 | 0.3422%
IS41Inv2M3 | 1180.3 | 0.3247%
IS41Inv2M4 | 1068.65 | 0.294%
IS42Inv1M1 | 382.8 | 0.1053%
IS42Inv1M2 | 701.8 | 0.1931%
IS42Inv1M3 | 1100.55 | 0.3028%
IS42Inv1M4 | 430.65 | 0.1185%
IS42Inv2M1 | 1307.9 | 0.3598%
IS42Inv2M2 | 1196.25 | 0.3291%
IS42Inv2M3 | 1100.55 | 0.3028%
IS42Inv2M4 | 1116.5 | 0.3071%
IS43Inv1M1 | 1068.65 | 0.294%
IS43Inv1M2 | 845.35 | 0.2326%
IS43Inv1M3 | 1276 | 0.351%
IS43Inv1M4 | 1291.95 | 0.3554%
IS43Inv2M1 | 1307.9 | 0.3598%
IS43Inv2M2 | 1276 | 0.351%
IS43Inv2M3 | 1244.1 | 0.3422%
IS43Inv2M4 | 957 | 0.2633%
IS44Inv1M1 | 988.9 | 0.272%
IS44Inv1M2 | 638 | 0.1755%
IS44Inv1M3 | 0 | 0%
IS44Inv1M4 | 1081.41 | 0.2975%
IS44Inv2M1 | 797.5 | 0.2194%
IS44Inv2M2 | 781.55 | 0.215%
IS44Inv2M3 | 1164.35 | 0.3203%
IS44Inv2M4 | 925.1 | 0.2545%
IS45Inv1M1 | 797.5 | 0.2194%
IS45Inv1M2 | 510.4 | 0.1404%
IS45Inv1M3 | 1052.7 | 0.2896%
IS45Inv1M4 | 1020.8 | 0.2808%
IS45Inv2M1 | 861.3 | 0.2369%
IS45Inv2M2 | 797.5 | 0.2194%
IS45Inv2M3 | 893.2 | 0.2457%
IS45Inv2M4 | 701.8 | 0.1931%
IS46Inv1M1 | 1004.85 | 0.2764%
IS46Inv1M2 | 988.9 | 0.272%
IS46Inv1M3 | 1020.8 | 0.2808%
IS46Inv1M4 | 1116.5 | 0.3071%
IS46Inv2M1 | 1148.4 | 0.3159%
IS46Inv2M2 | 749.65 | 0.2062%
IS46Inv2M3 | 1212.2 | 0.3335%
IS46Inv2M4 | 1132.45 | 0.3115%
IS47Inv1M1 | 972.95 | 0.2677%
IS47Inv1M2 | 1068.65 | 0.294%
IS47Inv1M3 | 1148.4 | 0.3159%
IS47Inv1M4 | 1196.25 | 0.3291%
IS47Inv2M1 | 1084.6 | 0.2984%
IS47Inv2M2 | 1148.4 | 0.3159%
IS47Inv2M3 | 1180.3 | 0.3247%
IS47Inv2M4 | 988.9 | 0.272%
IS48Inv1M1 | 319 | 0.08776%
IS48Inv1M2 | 925.1 | 0.2545%
IS48Inv1M3 | 414.7 | 0.1141%
IS48Inv1M4 | 845.35 | 0.2326%
IS48Inv2M1 | 861.3 | 0.2369%
IS48Inv2M2 | 1228.15 | 0.3379%
IS48Inv2M3 | 542.3 | 0.1492%
IS48Inv2M4 | 925.1 | 0.2545%
IS49Inv1M1 | 1180.3 | 0.3247%
IS49Inv1M2 | 893.2 | 0.2457%
IS49Inv1M3 | 1164.35 | 0.3203%
IS49Inv1M4 | 1260.05 | 0.3466%
IS49Inv2M1 | 398.75 | 0.1097%
IS49Inv2M2 | 893.2 | 0.2457%
IS49Inv2M3 | 1084.6 | 0.2984%
IS49Inv2M4 | 1020.8 | 0.2808%
IS50Inv1M1 | 1196.25 | 0.3291%
IS50Inv1M2 | 1212.2 | 0.3335%
IS50Inv1M3 | 1339.8 | 0.3686%
IS50Inv1M4 | 1339.8 | 0.3686%
IS50Inv2M1 | 1339.8 | 0.3686%
IS50Inv2M2 | 1307.9 | 0.3598%
IS50Inv2M3 | 1244.1 | 0.3422%
IS50Inv2M4 | 1307.9 | 0.3598%
IS51Inv1M1 | 1084.6 | 0.2984%
IS51Inv1M2 | 1116.5 | 0.3071%
IS51Inv1M3 | 953.81 | 0.2624%
IS51Inv1M4 | 1116.5 | 0.3071%
IS51Inv2M1 | 1036.75 | 0.2852%
IS51Inv2M2 | 1084.6 | 0.2984%
IS51Inv2M3 | 1307.9 | 0.3598%
IS51Inv2M4 | 1244.1 | 0.3422%
IS52Inv1M1 | 1052.7 | 0.2896%
IS52Inv1M2 | 478.5 | 0.1316%
IS52Inv1M3 | 733.7 | 0.2018%
IS52Inv1M4 | 1339.8 | 0.3686%
IS52Inv2M1 | 861.3 | 0.2369%
IS52Inv2M2 | 893.2 | 0.2457%
IS52Inv2M3 | 893.2 | 0.2457%
IS52Inv2M4 | 1036.75 | 0.2852%
IS1Inv1 | 4147 | 1.141%
IS1Inv2 | 4944.5 | 1.36%
IS2Inv1 | 4960.45 | 1.365%
IS2Inv2 | 3684.45 | 1.014%
IS3Inv1 | 5105.015 | 1.404%
IS3Inv2 | 5120.82 | 1.409%
IS4Inv1 | 5024.25 | 1.382%
IS4Inv2 | 4497.9 | 1.237%
IS5Inv1 | 3764.2 | 1.036%
IS5Inv2 | 4338.4 | 1.193%
IS6Inv1 | 5072.1 | 1.395%
IS6Inv2 | 5104 | 1.404%
IS7Inv1 | 5183.75 | 1.426%
IS7Inv2 | 4625.5 | 1.272%
IS8Inv1 | 5008.3 | 1.378%
IS8Inv2 | 4960.45 | 1.365%
IS9Inv1 | 5040.2 | 1.387%
IS9Inv2 | 4497.9 | 1.237%
IS10Inv1 | 0 | 0%
IS10Inv2 | 0 | 0%
IS11Inv1 | 685.85 | 0.1887%
IS12Inv1 | 0 | 0%
IS12Inv2 | 5295.4 | 1.457%
IS13Inv1 | 5263.5 | 1.448%
IS13Inv2 | 5008.3 | 1.378%
IS14Inv1 | 4992.35 | 1.373%
IS14Inv2 | 4928.55 | 1.356%
IS15Inv1 | 4721.2 | 1.299%
IS15Inv2 | 5167.8 | 1.422%
IS16Inv1 | 5008.3 | 1.378%
IS17Inv1 | 350.9 | 0.09653%
IS17Inv2 | 0 | 0%
IS18Inv1 | 5088.05 | 1.4%
IS18Inv2 | 4657.4 | 1.281%
IS19Inv1 | 4753.1 | 1.308%
IS19Inv2 | 3700.4 | 1.018%
IS20Inv1 | 5072.1 | 1.395%
IS20Inv2 | 4003.45 | 1.101%
IS21Inv1 | 3126.2 | 0.86%
IS21Inv2 | 2823.15 | 0.7766%
IS22Inv1 | 5040.2 | 1.387%
IS22Inv2 | 3843.95 | 1.057%
IS23Inv1 | 4370.3 | 1.202%
IS23Inv2 | 4928.55 | 1.356%
IS24Inv1 | 0 | 0%
IS24Inv2 | 0 | 0%
IS25Inv1 | 0 | 0%
IS25Inv2 | 0 | 0%
IS26Inv1 | 0 | 0%
IS26Inv2 | 0 | 0%
IS27Inv1 | 0 | 0%
IS27Inv2 | 0 | 0%
IS28Inv1 | 3828 | 1.053%
IS28Inv2 | 1914 | 0.5265%
IS29Inv1 | 3572.8 | 0.9829%
IS29Inv2 | 4290.55 | 1.18%
IS30Inv1 | 4912.6 | 1.351%
IS30Inv2 | 4657.4 | 1.281%
IS31Inv1 | 5072.1 | 1.395%
IS31Inv2 | 5311.35 | 1.461%
IS32Inv1 | 4976.4 | 1.369%
IS32Inv2 | 5135.9 | 1.413%
IS33Inv1 | 4625.5 | 1.272%
IS33Inv2 | 4481.95 | 1.233%
IS34Inv1 | 4338.4 | 1.193%
IS34Inv2 | 5104 | 1.404%
IS35Inv1 | 3987.5 | 1.097%
IS35Inv2 | 2105.4 | 0.5792%
IS36Inv1 | 3700.4 | 1.018%
IS36Inv2 | 4402.2 | 1.211%
IS37Inv1 | 3764.2 | 1.036%
IS37Inv2 | 4737.15 | 1.303%
IS38Inv1 | 0 | 0%
IS38Inv2 | 0 | 0%
IS39Inv1 | 191.4 | 0.05265%
IS39Inv2 | 223.3 | 0.06143%
IS40Inv1 | 4003.45 | 1.101%
IS40Inv2 | 287.1 | 0.07898%
IS41Inv1 | 4083.2 | 1.123%
IS41Inv2 | 4641.45 | 1.277%
IS42Inv1 | 2615.8 | 0.7196%
IS42Inv2 | 4721.2 | 1.299%
IS43Inv1 | 4481.95 | 1.233%
IS43Inv2 | 4785 | 1.316%
IS44Inv1 | 2708.31 | 0.745%
IS44Inv2 | 3668.5 | 1.009%
IS45Inv1 | 3381.4 | 0.9302%
IS45Inv2 | 3253.8 | 0.8951%
IS46Inv1 | 4131.05 | 1.136%
IS46Inv2 | 4242.7 | 1.167%
IS47Inv1 | 4386.25 | 1.207%
IS47Inv2 | 4402.2 | 1.211%
IS48Inv1 | 2504.15 | 0.6889%
IS48Inv2 | 3556.85 | 0.9785%
IS49Inv1 | 4497.9 | 1.237%
IS49Inv2 | 3397.35 | 0.9346%
IS50Inv1 | 5088.05 | 1.4%
IS50Inv2 | 5199.7 | 1.43%
IS51Inv1 | 4271.41 | 1.175%
IS51Inv2 | 4673.35 | 1.286%
IS52Inv1 | 3604.7 | 0.9916%
IS52Inv2 | 3684.45 | 1.014%
IS1Inv1M1SCB1 | 159.5 | 0.04388%
IS1Inv1M1SCB2 | 191.4 | 0.05265%
IS1Inv1M1SCB3 | 191.4 | 0.05265%
IS1Inv1M1SCB4 | 95.7 | 0.02633%
IS1Inv1M1SCB5 | 191.4 | 0.05265%
IS1Inv1M1SCB6 | 127.6 | 0.0351%
IS1Inv1M2SCB1 | 223.3 | 0.06143%
IS1Inv1M2SCB2 | 191.4 | 0.05265%
IS1Inv1M2SCB3 | 223.3 | 0.06143%
IS1Inv1M2SCB4 | 95.7 | 0.02633%
IS1Inv1M2SCB5 | 191.4 | 0.05265%
IS1Inv1M2SCB6 | 159.5 | 0.04388%
IS1Inv1M3SCB1 | 191.4 | 0.05265%
IS1Inv1M3SCB2 | 159.5 | 0.04388%
IS1Inv1M3SCB3 | 159.5 | 0.04388%
IS1Inv1M3SCB4 | 191.4 | 0.05265%
IS1Inv1M3SCB5 | 95.7 | 0.02633%
IS1Inv1M3SCB6 | 31.9 | 0.008776%
IS1Inv1M4SCB1 | 255.2 | 0.0702%
IS1Inv1M4SCB2 | 223.3 | 0.06143%
IS1Inv1M4SCB3 | 191.4 | 0.05265%
IS1Inv1M4SCB4 | 159.5 | 0.04388%
IS1Inv1M4SCB5 | 223.3 | 0.06143%
IS1Inv1M4SCB6 | 223.3 | 0.06143%
IS1Inv2M1SCB1 | 223.3 | 0.06143%
IS1Inv2M1SCB2 | 223.3 | 0.06143%
IS1Inv2M1SCB3 | 223.3 | 0.06143%
IS1Inv2M1SCB4 | 223.3 | 0.06143%
IS1Inv2M1SCB5 | 223.3 | 0.06143%
IS1Inv2M1SCB6 | 223.3 | 0.06143%
IS1Inv2M2SCB1 | 191.4 | 0.05265%
IS1Inv2M2SCB2 | 223.3 | 0.06143%
IS1Inv2M2SCB3 | 191.4 | 0.05265%
IS1Inv2M2SCB4 | 223.3 | 0.06143%
IS1Inv2M2SCB5 | 191.4 | 0.05265%
IS1Inv2M2SCB6 | 223.3 | 0.06143%
IS1Inv2M3SCB1 | 95.7 | 0.02633%
IS1Inv2M3SCB2 | 127.6 | 0.0351%
IS1Inv2M3SCB3 | 223.3 | 0.06143%
IS1Inv2M3SCB4 | 223.3 | 0.06143%
IS1Inv2M3SCB5 | 223.3 | 0.06143%
IS1Inv2M3SCB6 | 223.3 | 0.06143%
IS1Inv2M4SCB1 | 223.3 | 0.06143%
IS1Inv2M4SCB2 | 159.5 | 0.04388%
IS1Inv2M4SCB3 | 223.3 | 0.06143%
IS1Inv2M4SCB4 | 191.4 | 0.05265%
IS1Inv2M4SCB5 | 223.3 | 0.06143%
IS1Inv2M4SCB6 | 223.3 | 0.06143%
IS2Inv1M1SCB1 | 223.3 | 0.06143%
IS2Inv1M1SCB2 | 191.4 | 0.05265%
IS2Inv1M1SCB3 | 95.7 | 0.02633%
IS2Inv1M1SCB4 | 223.3 | 0.06143%
IS2Inv1M1SCB5 | 223.3 | 0.06143%
IS2Inv1M1SCB6 | 223.3 | 0.06143%
IS2Inv1M2SCB1 | 223.3 | 0.06143%
IS2Inv1M2SCB2 | 207.35 | 0.05704%
IS2Inv1M2SCB3 | 223.3 | 0.06143%
IS2Inv1M2SCB4 | 159.5 | 0.04388%
IS2Inv1M2SCB5 | 223.3 | 0.06143%
IS2Inv1M2SCB6 | 159.5 | 0.04388%
IS2Inv1M3SCB1 | 223.3 | 0.06143%
IS2Inv1M3SCB2 | 223.3 | 0.06143%
IS2Inv1M3SCB3 | 223.3 | 0.06143%
IS2Inv1M3SCB4 | 191.4 | 0.05265%
IS2Inv1M3SCB5 | 159.5 | 0.04388%
IS2Inv1M3SCB6 | 223.3 | 0.06143%
IS2Inv1M4SCB1 | 223.3 | 0.06143%
IS2Inv1M4SCB2 | 223.3 | 0.06143%
IS2Inv1M4SCB3 | 223.3 | 0.06143%
IS2Inv1M4SCB4 | 223.3 | 0.06143%
IS2Inv1M4SCB5 | 223.3 | 0.06143%
IS2Inv1M4SCB6 | 223.3 | 0.06143%
IS2Inv2M1SCB1 | 223.3 | 0.06143%
IS2Inv2M1SCB2 | 223.3 | 0.06143%
IS2Inv2M1SCB3 | 191.4 | 0.05265%
IS2Inv2M1SCB4 | 223.3 | 0.06143%
IS2Inv2M1SCB5 | 159.5 | 0.04388%
IS2Inv2M1SCB6 | 223.3 | 0.06143%
IS2Inv2M2SCB1 | 207.35 | 0.05704%
IS2Inv2M2SCB2 | 175.45 | 0.04827%
IS2Inv2M2SCB3 | 175.45 | 0.04827%
IS2Inv2M2SCB4 | 223.3 | 0.06143%
IS2Inv2M2SCB5 | 0 | 0%
IS2Inv2M2SCB6 | 0 | 0%
IS2Inv2M3SCB1 | 191.4 | 0.05265%
IS2Inv2M3SCB2 | 127.6 | 0.0351%
IS2Inv2M3SCB3 | 0 | 0%
IS2Inv2M3SCB4 | 111.65 | 0.03071%
IS2Inv2M3SCB5 | 0 | 0%
IS2Inv2M3SCB6 | 0 | 0%
IS2Inv2M4SCB1 | 223.3 | 0.06143%
IS2Inv2M4SCB2 | 223.3 | 0.06143%
IS2Inv2M4SCB3 | 223.3 | 0.06143%
IS2Inv2M4SCB4 | 223.3 | 0.06143%
IS2Inv2M4SCB5 | 159.5 | 0.04388%
IS2Inv2M4SCB6 | 175.45 | 0.04827%
IS3Inv1M1SCB1 | 221.27 | 0.06087%
IS3Inv1M1SCB2 | 221.27 | 0.06087%
IS3Inv1M1SCB3 | 221.27 | 0.06087%
IS3Inv1M1SCB4 | 221.27 | 0.06087%
IS3Inv1M1SCB5 | 221.27 | 0.06087%
IS3Inv1M1SCB6 | 158.05 | 0.04348%
IS3Inv1M2SCB1 | 221.27 | 0.06087%
IS3Inv1M2SCB2 | 221.27 | 0.06087%
IS3Inv1M2SCB3 | 221.27 | 0.06087%
IS3Inv1M2SCB4 | 221.27 | 0.06087%
IS3Inv1M2SCB5 | 221.27 | 0.06087%
IS3Inv1M2SCB6 | 221.27 | 0.06087%
IS3Inv1M3SCB1 | 221.27 | 0.06087%
IS3Inv1M3SCB2 | 189.66 | 0.05217%
IS3Inv1M3SCB3 | 221.27 | 0.06087%
IS3Inv1M3SCB4 | 221.27 | 0.06087%
IS3Inv1M3SCB5 | 221.27 | 0.06087%
IS3Inv1M3SCB6 | 158.05 | 0.04348%
IS3Inv1M4SCB1 | 189.66 | 0.05217%
IS3Inv1M4SCB2 | 205.465 | 0.05652%
IS3Inv1M4SCB3 | 221.27 | 0.06087%
IS3Inv1M4SCB4 | 221.27 | 0.06087%
IS3Inv1M4SCB5 | 221.27 | 0.06087%
IS3Inv1M4SCB6 | 221.27 | 0.06087%
IS3Inv2M1SCB1 | 221.27 | 0.06087%
IS3Inv2M1SCB2 | 221.27 | 0.06087%
IS3Inv2M1SCB3 | 221.27 | 0.06087%
IS3Inv2M1SCB4 | 189.66 | 0.05217%
IS3Inv2M1SCB5 | 221.27 | 0.06087%
IS3Inv2M1SCB6 | 221.27 | 0.06087%
IS3Inv2M2SCB1 | 221.27 | 0.06087%
IS3Inv2M2SCB2 | 221.27 | 0.06087%
IS3Inv2M2SCB3 | 189.66 | 0.05217%
IS3Inv2M2SCB4 | 189.66 | 0.05217%
IS3Inv2M2SCB5 | 221.27 | 0.06087%
IS3Inv2M2SCB6 | 221.27 | 0.06087%
IS3Inv2M3SCB1 | 189.66 | 0.05217%
IS3Inv2M3SCB2 | 221.27 | 0.06087%
IS3Inv2M3SCB3 | 221.27 | 0.06087%
IS3Inv2M3SCB4 | 221.27 | 0.06087%
IS3Inv2M3SCB5 | 221.27 | 0.06087%
IS3Inv2M3SCB6 | 221.27 | 0.06087%
IS3Inv2M4SCB1 | 189.66 | 0.05217%
IS3Inv2M4SCB2 | 221.27 | 0.06087%
IS3Inv2M4SCB3 | 189.66 | 0.05217%
IS3Inv2M4SCB4 | 221.27 | 0.06087%
IS3Inv2M4SCB5 | 221.27 | 0.06087%
IS3Inv2M4SCB6 | 221.27 | 0.06087%
IS4Inv1M1SCB1 | 223.3 | 0.06143%
IS4Inv1M1SCB2 | 191.4 | 0.05265%
IS4Inv1M1SCB3 | 191.4 | 0.05265%
IS4Inv1M1SCB4 | 191.4 | 0.05265%
IS4Inv1M1SCB5 | 191.4 | 0.05265%
IS4Inv1M1SCB6 | 191.4 | 0.05265%
IS4Inv1M2SCB1 | 191.4 | 0.05265%
IS4Inv1M2SCB2 | 223.3 | 0.06143%
IS4Inv1M2SCB3 | 223.3 | 0.06143%
IS4Inv1M2SCB4 | 223.3 | 0.06143%
IS4Inv1M2SCB5 | 223.3 | 0.06143%
IS4Inv1M2SCB6 | 223.3 | 0.06143%
IS4Inv1M3SCB1 | 223.3 | 0.06143%
IS4Inv1M3SCB2 | 223.3 | 0.06143%
IS4Inv1M3SCB3 | 223.3 | 0.06143%
IS4Inv1M3SCB4 | 191.4 | 0.05265%
IS4Inv1M3SCB5 | 223.3 | 0.06143%
IS4Inv1M3SCB6 | 223.3 | 0.06143%
IS4Inv1M4SCB1 | 191.4 | 0.05265%
IS4Inv1M4SCB2 | 191.4 | 0.05265%
IS4Inv1M4SCB3 | 223.3 | 0.06143%
IS4Inv1M4SCB4 | 207.35 | 0.05704%
IS4Inv1M4SCB5 | 223.3 | 0.06143%
IS4Inv1M4SCB6 | 191.4 | 0.05265%
IS4Inv2M1SCB1 | 223.3 | 0.06143%
IS4Inv2M1SCB2 | 255.2 | 0.0702%
IS4Inv2M1SCB3 | 223.3 | 0.06143%
IS4Inv2M1SCB4 | 191.4 | 0.05265%
IS4Inv2M1SCB5 | 223.3 | 0.06143%
IS4Inv2M1SCB6 | 207.35 | 0.05704%
IS4Inv2M2SCB1 | 223.3 | 0.06143%
IS4Inv2M2SCB2 | 159.5 | 0.04388%
IS4Inv2M2SCB3 | 191.4 | 0.05265%
IS4Inv2M2SCB4 | 159.5 | 0.04388%
IS4Inv2M2SCB5 | 175.45 | 0.04827%
IS4Inv2M2SCB6 | 191.4 | 0.05265%
IS4Inv2M3SCB1 | 223.3 | 0.06143%
IS4Inv2M3SCB2 | 175.45 | 0.04827%
IS4Inv2M3SCB3 | 223.3 | 0.06143%
IS4Inv2M3SCB4 | 159.5 | 0.04388%
IS4Inv2M3SCB5 | 63.8 | 0.01755%
IS4Inv2M3SCB6 | 191.4 | 0.05265%
IS4Inv2M4SCB1 | 175.45 | 0.04827%
IS4Inv2M4SCB2 | 159.5 | 0.04388%
IS4Inv2M4SCB3 | 223.3 | 0.06143%
IS4Inv2M4SCB4 | 127.6 | 0.0351%
IS4Inv2M4SCB5 | 143.55 | 0.03949%
IS4Inv2M4SCB6 | 207.35 | 0.05704%
IS5Inv1M1SCB1 | 0 | 0%
IS5Inv1M1SCB2 | 0 | 0%
IS5Inv1M1SCB3 | 223.3 | 0.06143%
IS5Inv1M1SCB4 | 191.4 | 0.05265%
IS5Inv1M1SCB5 | 223.3 | 0.06143%
IS5Inv1M1SCB6 | 223.3 | 0.06143%
IS5Inv1M2SCB1 | 95.7 | 0.02633%
IS5Inv1M2SCB2 | 223.3 | 0.06143%
IS5Inv1M2SCB3 | 223.3 | 0.06143%
IS5Inv1M2SCB4 | 223.3 | 0.06143%
IS5Inv1M2SCB5 | 223.3 | 0.06143%
IS5Inv1M2SCB6 | 223.3 | 0.06143%
IS5Inv1M3SCB1 | 191.4 | 0.05265%
IS5Inv1M3SCB2 | 191.4 | 0.05265%
IS5Inv1M3SCB3 | 191.4 | 0.05265%
IS5Inv1M3SCB4 | 223.3 | 0.06143%
IS5Inv1M3SCB5 | 0 | 0%
IS5Inv1M3SCB6 | 0 | 0%
IS5Inv1M4SCB1 | 223.3 | 0.06143%
IS5Inv1M4SCB2 | 223.3 | 0.06143%
IS5Inv1M4SCB3 | 223.3 | 0.06143%
IS5Inv1M4SCB4 | 223.3 | 0.06143%
IS5Inv1M4SCB5 | 0 | 0%
IS5Inv1M4SCB6 | 0 | 0%
IS5Inv2M1SCB1 | 223.3 | 0.06143%
IS5Inv2M1SCB2 | 223.3 | 0.06143%
IS5Inv2M1SCB3 | 223.3 | 0.06143%
IS5Inv2M1SCB4 | 223.3 | 0.06143%
IS5Inv2M1SCB5 | 191.4 | 0.05265%
IS5Inv2M1SCB6 | 223.3 | 0.06143%
IS5Inv2M2SCB1 | 223.3 | 0.06143%
IS5Inv2M2SCB2 | 223.3 | 0.06143%
IS5Inv2M2SCB3 | 223.3 | 0.06143%
IS5Inv2M2SCB4 | 223.3 | 0.06143%
IS5Inv2M2SCB5 | 191.4 | 0.05265%
IS5Inv2M2SCB6 | 223.3 | 0.06143%
IS5Inv2M3SCB1 | 223.3 | 0.06143%
IS5Inv2M3SCB2 | 223.3 | 0.06143%
IS5Inv2M3SCB3 | 223.3 | 0.06143%
IS5Inv2M3SCB4 | 223.3 | 0.06143%
IS5Inv2M3SCB5 | 0 | 0%
IS5Inv2M3SCB6 | 0 | 0%
IS5Inv2M4SCB1 | 159.5 | 0.04388%
IS5Inv2M4SCB2 | 223.3 | 0.06143%
IS5Inv2M4SCB3 | 223.3 | 0.06143%
IS5Inv2M4SCB4 | 223.3 | 0.06143%
IS5Inv2M4SCB5 | 0 | 0%
IS5Inv2M4SCB6 | 0 | 0%
IS6Inv1M1SCB1 | 191.4 | 0.05265%
IS6Inv1M1SCB2 | 223.3 | 0.06143%
IS6Inv1M1SCB3 | 191.4 | 0.05265%
IS6Inv1M1SCB4 | 191.4 | 0.05265%
IS6Inv1M1SCB5 | 223.3 | 0.06143%
IS6Inv1M1SCB6 | 223.3 | 0.06143%
IS6Inv1M2SCB1 | 191.4 | 0.05265%
IS6Inv1M2SCB2 | 223.3 | 0.06143%
IS6Inv1M2SCB3 | 223.3 | 0.06143%
IS6Inv1M2SCB4 | 191.4 | 0.05265%
IS6Inv1M2SCB5 | 223.3 | 0.06143%
IS6Inv1M2SCB6 | 223.3 | 0.06143%
IS6Inv1M3SCB1 | 191.4 | 0.05265%
IS6Inv1M3SCB2 | 223.3 | 0.06143%
IS6Inv1M3SCB3 | 223.3 | 0.06143%
IS6Inv1M3SCB4 | 223.3 | 0.06143%
IS6Inv1M3SCB5 | 223.3 | 0.06143%
IS6Inv1M3SCB6 | 223.3 | 0.06143%
IS6Inv1M4SCB1 | 191.4 | 0.05265%
IS6Inv1M4SCB2 | 223.3 | 0.06143%
IS6Inv1M4SCB3 | 191.4 | 0.05265%
IS6Inv1M4SCB4 | 223.3 | 0.06143%
IS6Inv1M4SCB5 | 223.3 | 0.06143%
IS6Inv1M4SCB6 | 191.4 | 0.05265%
IS6Inv2M1SCB1 | 223.3 | 0.06143%
IS6Inv2M1SCB2 | 159.5 | 0.04388%
IS6Inv2M1SCB3 | 191.4 | 0.05265%
IS6Inv2M1SCB4 | 223.3 | 0.06143%
IS6Inv2M1SCB5 | 223.3 | 0.06143%
IS6Inv2M1SCB6 | 223.3 | 0.06143%
IS6Inv2M2SCB1 | 223.3 | 0.06143%
IS6Inv2M2SCB2 | 223.3 | 0.06143%
IS6Inv2M2SCB3 | 223.3 | 0.06143%
IS6Inv2M2SCB4 | 191.4 | 0.05265%
IS6Inv2M2SCB5 | 223.3 | 0.06143%
IS6Inv2M2SCB6 | 223.3 | 0.06143%
IS6Inv2M3SCB1 | 191.4 | 0.05265%
IS6Inv2M3SCB2 | 223.3 | 0.06143%
IS6Inv2M3SCB3 | 223.3 | 0.06143%
IS6Inv2M3SCB4 | 223.3 | 0.06143%
IS6Inv2M3SCB5 | 191.4 | 0.05265%
IS6Inv2M3SCB6 | 223.3 | 0.06143%
IS6Inv2M4SCB1 | 223.3 | 0.06143%
IS6Inv2M4SCB2 | 223.3 | 0.06143%
IS6Inv2M4SCB3 | 223.3 | 0.06143%
IS6Inv2M4SCB4 | 191.4 | 0.05265%
IS6Inv2M4SCB5 | 191.4 | 0.05265%
IS6Inv2M4SCB6 | 223.3 | 0.06143%
IS7Inv1M1SCB1 | 191.4 | 0.05265%
IS7Inv1M1SCB2 | 223.3 | 0.06143%
IS7Inv1M1SCB3 | 223.3 | 0.06143%
IS7Inv1M1SCB4 | 223.3 | 0.06143%
IS7Inv1M1SCB5 | 223.3 | 0.06143%
IS7Inv1M1SCB6 | 191.4 | 0.05265%
IS7Inv1M2SCB1 | 223.3 | 0.06143%
IS7Inv1M2SCB2 | 175.45 | 0.04827%
IS7Inv1M2SCB3 | 223.3 | 0.06143%
IS7Inv1M2SCB4 | 223.3 | 0.06143%
IS7Inv1M2SCB5 | 223.3 | 0.06143%
IS7Inv1M2SCB6 | 223.3 | 0.06143%
IS7Inv1M3SCB1 | 223.3 | 0.06143%
IS7Inv1M3SCB2 | 223.3 | 0.06143%
IS7Inv1M3SCB3 | 223.3 | 0.06143%
IS7Inv1M3SCB4 | 223.3 | 0.06143%
IS7Inv1M3SCB5 | 223.3 | 0.06143%
IS7Inv1M3SCB6 | 223.3 | 0.06143%
IS7Inv1M4SCB1 | 223.3 | 0.06143%
IS7Inv1M4SCB2 | 191.4 | 0.05265%
IS7Inv1M4SCB3 | 191.4 | 0.05265%
IS7Inv1M4SCB4 | 223.3 | 0.06143%
IS7Inv1M4SCB5 | 223.3 | 0.06143%
IS7Inv1M4SCB6 | 223.3 | 0.06143%
IS7Inv2M1SCB1 | 63.8 | 0.01755%
IS7Inv2M1SCB2 | 127.6 | 0.0351%
IS7Inv2M1SCB3 | 95.7 | 0.02633%
IS7Inv2M1SCB4 | 191.4 | 0.05265%
IS7Inv2M1SCB5 | 191.4 | 0.05265%
IS7Inv2M1SCB6 | 191.4 | 0.05265%
IS7Inv2M2SCB1 | 223.3 | 0.06143%
IS7Inv2M2SCB2 | 223.3 | 0.06143%
IS7Inv2M2SCB3 | 159.5 | 0.04388%
IS7Inv2M2SCB4 | 223.3 | 0.06143%
IS7Inv2M2SCB5 | 223.3 | 0.06143%
IS7Inv2M2SCB6 | 223.3 | 0.06143%
IS7Inv2M3SCB1 | 223.3 | 0.06143%
IS7Inv2M3SCB2 | 223.3 | 0.06143%
IS7Inv2M3SCB3 | 159.5 | 0.04388%
IS7Inv2M3SCB4 | 223.3 | 0.06143%
IS7Inv2M3SCB5 | 223.3 | 0.06143%
IS7Inv2M3SCB6 | 191.4 | 0.05265%
IS7Inv2M4SCB1 | 223.3 | 0.06143%
IS7Inv2M4SCB2 | 191.4 | 0.05265%
IS7Inv2M4SCB3 | 223.3 | 0.06143%
IS7Inv2M4SCB4 | 159.5 | 0.04388%
IS7Inv2M4SCB5 | 223.3 | 0.06143%
IS7Inv2M4SCB6 | 223.3 | 0.06143%
IS8Inv1M1SCB1 | 223.3 | 0.06143%
IS8Inv1M1SCB2 | 159.5 | 0.04388%
IS8Inv1M1SCB3 | 223.3 | 0.06143%
IS8Inv1M1SCB4 | 223.3 | 0.06143%
IS8Inv1M1SCB5 | 191.4 | 0.05265%
IS8Inv1M1SCB6 | 223.3 | 0.06143%
IS8Inv1M2SCB1 | 191.4 | 0.05265%
IS8Inv1M2SCB2 | 159.5 | 0.04388%
IS8Inv1M2SCB3 | 223.3 | 0.06143%
IS8Inv1M2SCB4 | 223.3 | 0.06143%
IS8Inv1M2SCB5 | 223.3 | 0.06143%
IS8Inv1M2SCB6 | 223.3 | 0.06143%
IS8Inv1M3SCB1 | 223.3 | 0.06143%
IS8Inv1M3SCB2 | 159.5 | 0.04388%
IS8Inv1M3SCB3 | 223.3 | 0.06143%
IS8Inv1M3SCB4 | 223.3 | 0.06143%
IS8Inv1M3SCB5 | 223.3 | 0.06143%
IS8Inv1M3SCB6 | 223.3 | 0.06143%
IS8Inv1M4SCB1 | 223.3 | 0.06143%
IS8Inv1M4SCB2 | 223.3 | 0.06143%
IS8Inv1M4SCB3 | 223.3 | 0.06143%
IS8Inv1M4SCB4 | 191.4 | 0.05265%
IS8Inv1M4SCB5 | 223.3 | 0.06143%
IS8Inv1M4SCB6 | 159.5 | 0.04388%
IS8Inv2M1SCB1 | 159.5 | 0.04388%
IS8Inv2M1SCB2 | 223.3 | 0.06143%
IS8Inv2M1SCB3 | 191.4 | 0.05265%
IS8Inv2M1SCB4 | 223.3 | 0.06143%
IS8Inv2M1SCB5 | 191.4 | 0.05265%
IS8Inv2M1SCB6 | 223.3 | 0.06143%
IS8Inv2M2SCB1 | 159.5 | 0.04388%
IS8Inv2M2SCB2 | 223.3 | 0.06143%
IS8Inv2M2SCB3 | 223.3 | 0.06143%
IS8Inv2M2SCB4 | 191.4 | 0.05265%
IS8Inv2M2SCB5 | 223.3 | 0.06143%
IS8Inv2M2SCB6 | 223.3 | 0.06143%
IS8Inv2M3SCB1 | 127.6 | 0.0351%
IS8Inv2M3SCB2 | 191.4 | 0.05265%
IS8Inv2M3SCB3 | 191.4 | 0.05265%
IS8Inv2M3SCB4 | 223.3 | 0.06143%
IS8Inv2M3SCB5 | 207.35 | 0.05704%
IS8Inv2M3SCB6 | 223.3 | 0.06143%
IS8Inv2M4SCB1 | 223.3 | 0.06143%
IS8Inv2M4SCB2 | 223.3 | 0.06143%
IS8Inv2M4SCB3 | 223.3 | 0.06143%
IS8Inv2M4SCB4 | 223.3 | 0.06143%
IS8Inv2M4SCB5 | 223.3 | 0.06143%
IS8Inv2M4SCB6 | 223.3 | 0.06143%
IS9Inv1M1SCB1 | 191.4 | 0.05265%
IS9Inv1M1SCB2 | 223.3 | 0.06143%
IS9Inv1M1SCB3 | 223.3 | 0.06143%
IS9Inv1M1SCB4 | 223.3 | 0.06143%
IS9Inv1M1SCB5 | 191.4 | 0.05265%
IS9Inv1M1SCB6 | 223.3 | 0.06143%
IS9Inv1M2SCB1 | 223.3 | 0.06143%
IS9Inv1M2SCB2 | 223.3 | 0.06143%
IS9Inv1M2SCB3 | 191.4 | 0.05265%
IS9Inv1M2SCB4 | 223.3 | 0.06143%
IS9Inv1M2SCB5 | 223.3 | 0.06143%
IS9Inv1M2SCB6 | 223.3 | 0.06143%
IS9Inv1M3SCB1 | 223.3 | 0.06143%
IS9Inv1M3SCB2 | 223.3 | 0.06143%
IS9Inv1M3SCB3 | 223.3 | 0.06143%
IS9Inv1M3SCB4 | 191.4 | 0.05265%
IS9Inv1M3SCB5 | 159.5 | 0.04388%
IS9Inv1M3SCB6 | 223.3 | 0.06143%
IS9Inv1M4SCB1 | 223.3 | 0.06143%
IS9Inv1M4SCB2 | 191.4 | 0.05265%
IS9Inv1M4SCB3 | 191.4 | 0.05265%
IS9Inv1M4SCB4 | 191.4 | 0.05265%
IS9Inv1M4SCB5 | 223.3 | 0.06143%
IS9Inv1M4SCB6 | 191.4 | 0.05265%
IS9Inv2M1SCB1 | 223.3 | 0.06143%
IS9Inv2M1SCB2 | 159.5 | 0.04388%
IS9Inv2M1SCB3 | 223.3 | 0.06143%
IS9Inv2M1SCB4 | 159.5 | 0.04388%
IS9Inv2M1SCB5 | 191.4 | 0.05265%
IS9Inv2M1SCB6 | 127.6 | 0.0351%
IS9Inv2M2SCB1 | 223.3 | 0.06143%
IS9Inv2M2SCB2 | 159.5 | 0.04388%
IS9Inv2M2SCB3 | 191.4 | 0.05265%
IS9Inv2M2SCB4 | 191.4 | 0.05265%
IS9Inv2M2SCB5 | 191.4 | 0.05265%
IS9Inv2M2SCB6 | 191.4 | 0.05265%
IS9Inv2M3SCB1 | 223.3 | 0.06143%
IS9Inv2M3SCB2 | 191.4 | 0.05265%
IS9Inv2M3SCB3 | 223.3 | 0.06143%
IS9Inv2M3SCB4 | 223.3 | 0.06143%
IS9Inv2M3SCB5 | 127.6 | 0.0351%
IS9Inv2M3SCB6 | 191.4 | 0.05265%
IS9Inv2M4SCB1 | 223.3 | 0.06143%
IS9Inv2M4SCB2 | 127.6 | 0.0351%
IS9Inv2M4SCB3 | 159.5 | 0.04388%
IS9Inv2M4SCB4 | 159.5 | 0.04388%
IS9Inv2M4SCB5 | 191.4 | 0.05265%
IS9Inv2M4SCB6 | 223.3 | 0.06143%
IS10Inv1M1SCB1 | 0 | 0%
IS10Inv1M1SCB2 | 0 | 0%
IS10Inv1M1SCB3 | 0 | 0%
IS10Inv1M1SCB4 | 0 | 0%
IS10Inv1M1SCB5 | 0 | 0%
IS10Inv1M1SCB6 | 0 | 0%
IS10Inv1M2SCB1 | 0 | 0%
IS10Inv1M2SCB2 | 0 | 0%
IS10Inv1M2SCB3 | 0 | 0%
IS10Inv1M2SCB4 | 0 | 0%
IS10Inv1M2SCB5 | 0 | 0%
IS10Inv1M2SCB6 | 0 | 0%
IS10Inv1M3SCB1 | 0 | 0%
IS10Inv1M3SCB2 | 0 | 0%
IS10Inv1M3SCB3 | 0 | 0%
IS10Inv1M3SCB4 | 0 | 0%
IS10Inv1M3SCB5 | 0 | 0%
IS10Inv1M3SCB6 | 0 | 0%
IS10Inv1M4SCB1 | 0 | 0%
IS10Inv1M4SCB2 | 0 | 0%
IS10Inv1M4SCB3 | 0 | 0%
IS10Inv1M4SCB4 | 0 | 0%
IS10Inv1M4SCB5 | 0 | 0%
IS10Inv1M4SCB6 | 0 | 0%
IS10Inv2M1SCB1 | 0 | 0%
IS10Inv2M1SCB2 | 0 | 0%
IS10Inv2M1SCB3 | 0 | 0%
IS10Inv2M1SCB4 | 0 | 0%
IS10Inv2M1SCB5 | 0 | 0%
IS10Inv2M1SCB6 | 0 | 0%
IS10Inv2M2SCB1 | 0 | 0%
IS10Inv2M2SCB2 | 0 | 0%
IS10Inv2M2SCB3 | 0 | 0%
IS10Inv2M2SCB4 | 0 | 0%
IS10Inv2M2SCB5 | 0 | 0%
IS10Inv2M2SCB5 | 0 | 0%
IS10Inv2M3SCB1 | 0 | 0%
IS10Inv2M3SCB2 | 0 | 0%
IS10Inv2M3SCB3 | 0 | 0%
IS10Inv2M3SCB4 | 0 | 0%
IS10Inv2M3SCB5 | 0 | 0%
IS10Inv2M3SCB6 | 0 | 0%
IS10Inv2M4SCB1 | 0 | 0%
IS10Inv2M4SCB2 | 0 | 0%
IS10Inv2M4SCB3 | 0 | 0%
IS10Inv2M4SCB4 | 0 | 0%
IS10Inv2M4SCB5 | 0 | 0%
IS10Inv2M4SCB6 | 0 | 0%
IS11Inv1M1SCB1 | 159.5 | 0.04388%
IS11Inv1M1SCB2 | 0 | 0%
IS11Inv1M1SCB3 | 223.3 | 0.06143%
IS11Inv1M1SCB4 | 0 | 0%
IS11Inv1M1SCB5 | 0 | 0%
IS11Inv1M1SCB6 | 0 | 0%
IS11Inv1M2SCB1 | 0 | 0%
IS11Inv1M2SCB2 | 0 | 0%
IS11Inv1M2SCB3 | 0 | 0%
IS11Inv1M2SCB4 | 0 | 0%
IS11Inv1M2SCB5 | 159.5 | 0.04388%
IS11Inv1M2SCB6 | 143.55 | 0.03949%
IS11Inv1M3SCB1 | 0 | 0%
IS11Inv1M3SCB2 | 0 | 0%
IS11Inv1M3SCB3 | 0 | 0%
IS11Inv1M3SCB4 | 0 | 0%
IS11Inv1M3SCB5 | 0 | 0%
IS11Inv1M3SCB6 | 0 | 0%
IS11Inv1M4SCB1 | 0 | 0%
IS11Inv1M4SCB2 | 0 | 0%
IS11Inv1M4SCB3 | 0 | 0%
IS11Inv1M4SCB4 | 0 | 0%
IS11Inv1M4SCB5 | 0 | 0%
IS11Inv1M4SCB6 | 0 | 0%
IS12Inv1M1SCB1 | 0 | 0%
IS12Inv1M1SCB2 | 0 | 0%
IS12Inv1M1SCB3 | 0 | 0%
IS12Inv1M1SCB4 | 0 | 0%
IS12Inv1M1SCB5 | 0 | 0%
IS12Inv1M1SCB6 | 0 | 0%
IS12Inv1M2SCB1 | 0 | 0%
IS12Inv1M2SCB2 | 0 | 0%
IS12Inv1M2SCB3 | 0 | 0%
IS12Inv1M2SCB4 | 0 | 0%
IS12Inv1M2SCB5 | 0 | 0%
IS12Inv1M2SCB6 | 0 | 0%
IS12Inv1M3SCB1 | 0 | 0%
IS12Inv1M3SCB2 | 0 | 0%
IS12Inv1M3SCB3 | 0 | 0%
IS12Inv1M3SCB4 | 0 | 0%
IS12Inv1M3SCB5 | 0 | 0%
IS12Inv1M3SCB6 | 0 | 0%
IS12Inv1M4SCB1 | 0 | 0%
IS12Inv1M4SCB2 | 0 | 0%
IS12Inv1M4SCB3 | 0 | 0%
IS12Inv1M4SCB4 | 0 | 0%
IS12Inv1M4SCB5 | 0 | 0%
IS12Inv1M4SCB6 | 0 | 0%
IS12Inv2M1SCB1 | 223.3 | 0.06143%
IS12Inv2M1SCB2 | 223.3 | 0.06143%
IS12Inv2M1SCB3 | 223.3 | 0.06143%
IS12Inv2M1SCB4 | 223.3 | 0.06143%
IS12Inv2M1SCB5 | 223.3 | 0.06143%
IS12Inv2M1SCB6 | 223.3 | 0.06143%
IS12Inv2M2SCB1 | 223.3 | 0.06143%
IS12Inv2M2SCB2 | 223.3 | 0.06143%
IS12Inv2M2SCB3 | 223.3 | 0.06143%
IS12Inv2M2SCB4 | 223.3 | 0.06143%
IS12Inv2M2SCB5 | 223.3 | 0.06143%
IS12Inv2M2SCB6 | 223.3 | 0.06143%
IS12Inv2M3SCB1 | 223.3 | 0.06143%
IS12Inv2M3SCB2 | 223.3 | 0.06143%
IS12Inv2M3SCB3 | 223.3 | 0.06143%
IS12Inv2M3SCB4 | 191.4 | 0.05265%
IS12Inv2M3SCB5 | 223.3 | 0.06143%
IS12Inv2M3SCB6 | 223.3 | 0.06143%
IS12Inv2M4SCB1 | 191.4 | 0.05265%
IS12Inv2M4SCB2 | 223.3 | 0.06143%
IS12Inv2M4SCB3 | 223.3 | 0.06143%
IS12Inv2M4SCB4 | 223.3 | 0.06143%
IS12Inv2M4SCB5 | 223.3 | 0.06143%
IS12Inv2M4SCB6 | 223.3 | 0.06143%
IS13Inv1M1SCB1 | 223.3 | 0.06143%
IS13Inv1M1SCB2 | 223.3 | 0.06143%
IS13Inv1M1SCB3 | 223.3 | 0.06143%
IS13Inv1M1SCB4 | 223.3 | 0.06143%
IS13Inv1M1SCB5 | 223.3 | 0.06143%
IS13Inv1M1SCB6 | 223.3 | 0.06143%
IS13Inv1M2SCB1 | 223.3 | 0.06143%
IS13Inv1M2SCB2 | 223.3 | 0.06143%
IS13Inv1M2SCB3 | 223.3 | 0.06143%
IS13Inv1M2SCB4 | 191.4 | 0.05265%
IS13Inv1M2SCB5 | 223.3 | 0.06143%
IS13Inv1M2SCB6 | 191.4 | 0.05265%
IS13Inv1M3SCB1 | 223.3 | 0.06143%
IS13Inv1M3SCB2 | 223.3 | 0.06143%
IS13Inv1M3SCB3 | 223.3 | 0.06143%
IS13Inv1M3SCB4 | 223.3 | 0.06143%
IS13Inv1M3SCB5 | 223.3 | 0.06143%
IS13Inv1M3SCB6 | 223.3 | 0.06143%
IS13Inv1M4SCB1 | 223.3 | 0.06143%
IS13Inv1M4SCB2 | 223.3 | 0.06143%
IS13Inv1M4SCB3 | 223.3 | 0.06143%
IS13Inv1M4SCB4 | 223.3 | 0.06143%
IS13Inv1M4SCB5 | 223.3 | 0.06143%
IS13Inv1M4SCB6 | 191.4 | 0.05265%
IS13Inv2M1SCB1 | 223.3 | 0.06143%
IS13Inv2M1SCB2 | 223.3 | 0.06143%
IS13Inv2M1SCB3 | 191.4 | 0.05265%
IS13Inv2M1SCB4 | 191.4 | 0.05265%
IS13Inv2M1SCB5 | 223.3 | 0.06143%
IS13Inv2M1SCB6 | 191.4 | 0.05265%
IS13Inv2M2SCB1 | 191.4 | 0.05265%
IS13Inv2M2SCB2 | 223.3 | 0.06143%
IS13Inv2M2SCB3 | 191.4 | 0.05265%
IS13Inv2M2SCB4 | 127.6 | 0.0351%
IS13Inv2M2SCB5 | 191.4 | 0.05265%
IS13Inv2M2SCB6 | 223.3 | 0.06143%
IS13Inv2M3SCB1 | 223.3 | 0.06143%
IS13Inv2M3SCB2 | 223.3 | 0.06143%
IS13Inv2M3SCB3 | 223.3 | 0.06143%
IS13Inv2M3SCB4 | 223.3 | 0.06143%
IS13Inv2M3SCB5 | 223.3 | 0.06143%
IS13Inv2M3SCB6 | 191.4 | 0.05265%
IS13Inv2M4SCB1 | 223.3 | 0.06143%
IS13Inv2M4SCB2 | 191.4 | 0.05265%
IS13Inv2M4SCB3 | 223.3 | 0.06143%
IS13Inv2M4SCB4 | 223.3 | 0.06143%
IS13Inv2M4SCB5 | 223.3 | 0.06143%
IS13Inv2M4SCB6 | 223.3 | 0.06143%
IS14Inv1M1SCB1 | 223.3 | 0.06143%
IS14Inv1M1SCB2 | 223.3 | 0.06143%
IS14Inv1M1SCB3 | 223.3 | 0.06143%
IS14Inv1M1SCB4 | 223.3 | 0.06143%
IS14Inv1M1SCB5 | 223.3 | 0.06143%
IS14Inv1M1SCB6 | 223.3 | 0.06143%
IS14Inv1M2SCB1 | 191.4 | 0.05265%
IS14Inv1M2SCB2 | 191.4 | 0.05265%
IS14Inv1M2SCB3 | 223.3 | 0.06143%
IS14Inv1M2SCB4 | 223.3 | 0.06143%
IS14Inv1M2SCB5 | 223.3 | 0.06143%
IS14Inv1M2SCB6 | 207.35 | 0.05704%
IS14Inv1M3SCB1 | 159.5 | 0.04388%
IS14Inv1M3SCB2 | 223.3 | 0.06143%
IS14Inv1M3SCB3 | 223.3 | 0.06143%
IS14Inv1M3SCB4 | 127.6 | 0.0351%
IS14Inv1M3SCB5 | 159.5 | 0.04388%
IS14Inv1M3SCB6 | 191.4 | 0.05265%
IS14Inv1M4SCB1 | 223.3 | 0.06143%
IS14Inv1M4SCB2 | 223.3 | 0.06143%
IS14Inv1M4SCB3 | 223.3 | 0.06143%
IS14Inv1M4SCB4 | 223.3 | 0.06143%
IS14Inv1M4SCB5 | 223.3 | 0.06143%
IS14Inv1M4SCB6 | 191.4 | 0.05265%
IS14Inv2M1SCB1 | 159.5 | 0.04388%
IS14Inv2M1SCB2 | 223.3 | 0.06143%
IS14Inv2M1SCB3 | 223.3 | 0.06143%
IS14Inv2M1SCB4 | 223.3 | 0.06143%
IS14Inv2M1SCB5 | 159.5 | 0.04388%
IS14Inv2M1SCB6 | 127.6 | 0.0351%
IS14Inv2M2SCB1 | 223.3 | 0.06143%
IS14Inv2M2SCB2 | 223.3 | 0.06143%
IS14Inv2M2SCB3 | 223.3 | 0.06143%
IS14Inv2M2SCB4 | 159.5 | 0.04388%
IS14Inv2M2SCB5 | 223.3 | 0.06143%
IS14Inv2M2SCB6 | 223.3 | 0.06143%
IS14Inv2M3SCB1 | 159.5 | 0.04388%
IS14Inv2M3SCB2 | 207.35 | 0.05704%
IS14Inv2M3SCB3 | 223.3 | 0.06143%
IS14Inv2M3SCB4 | 223.3 | 0.06143%
IS14Inv2M3SCB5 | 223.3 | 0.06143%
IS14Inv2M3SCB6 | 191.4 | 0.05265%
IS14Inv2M4SCB1 | 223.3 | 0.06143%
IS14Inv2M4SCB2 | 223.3 | 0.06143%
IS14Inv2M4SCB3 | 191.4 | 0.05265%
IS14Inv2M4SCB4 | 223.3 | 0.06143%
IS14Inv2M4SCB5 | 223.3 | 0.06143%
IS14Inv2M4SCB6 | 223.3 | 0.06143%
IS15Inv1M1SCB1 | 191.4 | 0.05265%
IS15Inv1M1SCB2 | 223.3 | 0.06143%
IS15Inv1M1SCB3 | 127.6 | 0.0351%
IS15Inv1M1SCB4 | 207.35 | 0.05704%
IS15Inv1M1SCB5 | 143.55 | 0.03949%
IS15Inv1M1SCB6 | 127.6 | 0.0351%
IS15Inv1M2SCB1 | 191.4 | 0.05265%
IS15Inv1M2SCB2 | 223.3 | 0.06143%
IS15Inv1M2SCB3 | 223.3 | 0.06143%
IS15Inv1M2SCB4 | 175.45 | 0.04827%
IS15Inv1M2SCB5 | 223.3 | 0.06143%
IS15Inv1M2SCB6 | 223.3 | 0.06143%
IS15Inv1M3SCB1 | 223.3 | 0.06143%
IS15Inv1M3SCB2 | 223.3 | 0.06143%
IS15Inv1M3SCB3 | 223.3 | 0.06143%
IS15Inv1M3SCB4 | 223.3 | 0.06143%
IS15Inv1M3SCB5 | 223.3 | 0.06143%
IS15Inv1M3SCB6 | 159.5 | 0.04388%
IS15Inv1M4SCB1 | 223.3 | 0.06143%
IS15Inv1M4SCB2 | 191.4 | 0.05265%
IS15Inv1M4SCB3 | 223.3 | 0.06143%
IS15Inv1M4SCB4 | 111.65 | 0.03071%
IS15Inv1M4SCB5 | 191.4 | 0.05265%
IS15Inv1M4SCB6 | 223.3 | 0.06143%
IS15Inv2M1SCB1 | 223.3 | 0.06143%
IS15Inv2M1SCB2 | 191.4 | 0.05265%
IS15Inv2M1SCB3 | 223.3 | 0.06143%
IS15Inv2M1SCB4 | 191.4 | 0.05265%
IS15Inv2M1SCB5 | 223.3 | 0.06143%
IS15Inv2M1SCB6 | 223.3 | 0.06143%
IS15Inv2M2SCB1 | 223.3 | 0.06143%
IS15Inv2M2SCB2 | 223.3 | 0.06143%
IS15Inv2M2SCB3 | 223.3 | 0.06143%
IS15Inv2M2SCB4 | 223.3 | 0.06143%
IS15Inv2M2SCB5 | 191.4 | 0.05265%
IS15Inv2M2SCB6 | 223.3 | 0.06143%
IS15Inv2M3SCB1 | 191.4 | 0.05265%
IS15Inv2M3SCB2 | 223.3 | 0.06143%
IS15Inv2M3SCB3 | 191.4 | 0.05265%
IS15Inv2M3SCB4 | 223.3 | 0.06143%
IS15Inv2M3SCB5 | 223.3 | 0.06143%
IS15Inv2M3SCB6 | 223.3 | 0.06143%
IS15Inv2M4SCB1 | 223.3 | 0.06143%
IS15Inv2M4SCB2 | 223.3 | 0.06143%
IS15Inv2M4SCB3 | 223.3 | 0.06143%
IS15Inv2M4SCB4 | 191.4 | 0.05265%
IS15Inv2M4SCB5 | 223.3 | 0.06143%
IS15Inv2M4SCB6 | 223.3 | 0.06143%
IS16Inv1M1SCB1 | 223.3 | 0.06143%
IS16Inv1M1SCB2 | 191.4 | 0.05265%
IS16Inv1M1SCB3 | 191.4 | 0.05265%
IS16Inv1M1SCB4 | 223.3 | 0.06143%
IS16Inv1M1SCB5 | 223.3 | 0.06143%
IS16Inv1M1SCB6 | 223.3 | 0.06143%
IS16Inv1M2SCB1 | 223.3 | 0.06143%
IS16Inv1M2SCB2 | 223.3 | 0.06143%
IS16Inv1M2SCB3 | 191.4 | 0.05265%
IS16Inv1M2SCB4 | 191.4 | 0.05265%
IS16Inv1M2SCB5 | 191.4 | 0.05265%
IS16Inv1M2SCB6 | 223.3 | 0.06143%
IS16Inv1M3SCB1 | 223.3 | 0.06143%
IS16Inv1M3SCB2 | 223.3 | 0.06143%
IS16Inv1M3SCB3 | 223.3 | 0.06143%
IS16Inv1M3SCB4 | 223.3 | 0.06143%
IS16Inv1M3SCB5 | 223.3 | 0.06143%
IS16Inv1M3SCB6 | 191.4 | 0.05265%
IS16Inv1M4SCB1 | 191.4 | 0.05265%
IS16Inv1M4SCB2 | 223.3 | 0.06143%
IS16Inv1M4SCB3 | 223.3 | 0.06143%
IS16Inv1M4SCB4 | 127.6 | 0.0351%
IS16Inv1M4SCB5 | 191.4 | 0.05265%
IS16Inv1M4SCB6 | 223.3 | 0.06143%
IS17Inv1M1SCB1 | 0 | 0%
IS17Inv1M1SCB2 | 0 | 0%
IS17Inv1M1SCB3 | 0 | 0%
IS17Inv1M1SCB4 | 95.7 | 0.02633%
IS17Inv1M1SCB5 | 95.7 | 0.02633%
IS17Inv1M1SCB6 | 95.7 | 0.02633%
IS17Inv1M2SCB1 | 63.8 | 0.01755%
IS17Inv1M2SCB2 | 0 | 0%
IS17Inv1M2SCB3 | 0 | 0%
IS17Inv1M2SCB4 | 0 | 0%
IS17Inv1M2SCB5 | 0 | 0%
IS17Inv1M2SCB6 | 0 | 0%
IS17Inv1M3SCB1 | 0 | 0%
IS17Inv1M3SCB2 | 0 | 0%
IS17Inv1M3SCB3 | 0 | 0%
IS17Inv1M3SCB4 | 0 | 0%
IS17Inv1M3SCB5 | 0 | 0%
IS17Inv1M3SCB6 | 0 | 0%
IS17Inv1M4SCB1 | 0 | 0%
IS17Inv1M4SCB2 | 0 | 0%
IS17Inv1M4SCB3 | 0 | 0%
IS17Inv1M4SCB4 | 0 | 0%
IS17Inv1M4SCB5 | 0 | 0%
IS17Inv1M4SCB6 | 0 | 0%
IS17Inv2M1SCB1 | 0 | 0%
IS17Inv2M1SCB2 | 0 | 0%
IS17Inv2M1SCB3 | 0 | 0%
IS17Inv2M1SCB4 | 0 | 0%
IS17Inv2M1SCB5 | 0 | 0%
IS17Inv2M1SCB6 | 0 | 0%
IS17Inv2M2SCB1 | 0 | 0%
IS17Inv2M2SCB2 | 0 | 0%
IS17Inv2M2SCB3 | 0 | 0%
IS17Inv2M2SCB4 | 0 | 0%
IS17Inv2M2SCB5 | 0 | 0%
IS17Inv2M2SCB6 | 0 | 0%
IS17Inv2M3SCB1 | 0 | 0%
IS17Inv2M3SCB2 | 0 | 0%
IS17Inv2M3SCB3 | 0 | 0%
IS17Inv2M3SCB4 | 0 | 0%
IS17Inv2M3SCB5 | 0 | 0%
IS17Inv2M3SCB6 | 0 | 0%
IS17Inv2M4SCB1 | 0 | 0%
IS17Inv2M4SCB2 | 0 | 0%
IS17Inv2M4SCB3 | 0 | 0%
IS17Inv2M4SCB4 | 0 | 0%
IS17Inv2M4SCB5 | 0 | 0%
IS17Inv2M4SCB6 | 0 | 0%
IS18Inv1M1SCB1 | 223.3 | 0.06143%
IS18Inv1M1SCB2 | 223.3 | 0.06143%
IS18Inv1M1SCB3 | 191.4 | 0.05265%
IS18Inv1M1SCB4 | 207.35 | 0.05704%
IS18Inv1M1SCB5 | 223.3 | 0.06143%
IS18Inv1M1SCB6 | 223.3 | 0.06143%
IS18Inv1M2SCB1 | 223.3 | 0.06143%
IS18Inv1M2SCB2 | 191.4 | 0.05265%
IS18Inv1M2SCB3 | 223.3 | 0.06143%
IS18Inv1M2SCB4 | 223.3 | 0.06143%
IS18Inv1M2SCB5 | 159.5 | 0.04388%
IS18Inv1M2SCB6 | 191.4 | 0.05265%
IS18Inv1M3SCB1 | 223.3 | 0.06143%
IS18Inv1M3SCB2 | 223.3 | 0.06143%
IS18Inv1M3SCB3 | 223.3 | 0.06143%
IS18Inv1M3SCB4 | 223.3 | 0.06143%
IS18Inv1M3SCB5 | 223.3 | 0.06143%
IS18Inv1M3SCB6 | 223.3 | 0.06143%
IS18Inv1M4SCB1 | 223.3 | 0.06143%
IS18Inv1M4SCB2 | 207.35 | 0.05704%
IS18Inv1M4SCB3 | 175.45 | 0.04827%
IS18Inv1M4SCB4 | 191.4 | 0.05265%
IS18Inv1M4SCB5 | 223.3 | 0.06143%
IS18Inv1M4SCB6 | 223.3 | 0.06143%
IS18Inv2M1SCB1 | 223.3 | 0.06143%
IS18Inv2M1SCB2 | 223.3 | 0.06143%
IS18Inv2M1SCB3 | 223.3 | 0.06143%
IS18Inv2M1SCB4 | 223.3 | 0.06143%
IS18Inv2M1SCB5 | 191.4 | 0.05265%
IS18Inv2M1SCB6 | 223.3 | 0.06143%
IS18Inv2M2SCB1 | 223.3 | 0.06143%
IS18Inv2M2SCB2 | 159.5 | 0.04388%
IS18Inv2M2SCB3 | 191.4 | 0.05265%
IS18Inv2M2SCB4 | 191.4 | 0.05265%
IS18Inv2M2SCB5 | 223.3 | 0.06143%
IS18Inv2M2SCB6 | 159.5 | 0.04388%
IS18Inv2M3SCB1 | 191.4 | 0.05265%
IS18Inv2M3SCB2 | 191.4 | 0.05265%
IS18Inv2M3SCB3 | 223.3 | 0.06143%
IS18Inv2M3SCB4 | 223.3 | 0.06143%
IS18Inv2M3SCB5 | 63.8 | 0.01755%
IS18Inv2M3SCB6 | 159.5 | 0.04388%
IS18Inv2M4SCB1 | 223.3 | 0.06143%
IS18Inv2M4SCB2 | 223.3 | 0.06143%
IS18Inv2M4SCB3 | 191.4 | 0.05265%
IS18Inv2M4SCB4 | 127.6 | 0.0351%
IS18Inv2M4SCB5 | 191.4 | 0.05265%
IS18Inv2M4SCB6 | 191.4 | 0.05265%
IS19Inv1M1SCB1 | 159.5 | 0.04388%
IS19Inv1M1SCB2 | 223.3 | 0.06143%
IS19Inv1M1SCB3 | 223.3 | 0.06143%
IS19Inv1M1SCB4 | 223.3 | 0.06143%
IS19Inv1M1SCB5 | 159.5 | 0.04388%
IS19Inv1M1SCB6 | 159.5 | 0.04388%
IS19Inv1M2SCB1 | 191.4 | 0.05265%
IS19Inv1M2SCB2 | 191.4 | 0.05265%
IS19Inv1M2SCB3 | 95.7 | 0.02633%
IS19Inv1M2SCB4 | 191.4 | 0.05265%
IS19Inv1M2SCB5 | 223.3 | 0.06143%
IS19Inv1M2SCB6 | 223.3 | 0.06143%
IS19Inv1M3SCB1 | 223.3 | 0.06143%
IS19Inv1M3SCB2 | 191.4 | 0.05265%
IS19Inv1M3SCB3 | 191.4 | 0.05265%
IS19Inv1M3SCB4 | 223.3 | 0.06143%
IS19Inv1M3SCB5 | 223.3 | 0.06143%
IS19Inv1M3SCB6 | 223.3 | 0.06143%
IS19Inv1M4SCB1 | 191.4 | 0.05265%
IS19Inv1M4SCB2 | 191.4 | 0.05265%
IS19Inv1M4SCB3 | 223.3 | 0.06143%
IS19Inv1M4SCB4 | 223.3 | 0.06143%
IS19Inv1M4SCB5 | 191.4 | 0.05265%
IS19Inv1M4SCB6 | 191.4 | 0.05265%
IS19Inv2M1SCB1 | 191.4 | 0.05265%
IS19Inv2M1SCB2 | 191.4 | 0.05265%
IS19Inv2M1SCB3 | 159.5 | 0.04388%
IS19Inv2M1SCB4 | 223.3 | 0.06143%
IS19Inv2M1SCB5 | 95.7 | 0.02633%
IS19Inv2M1SCB6 | 95.7 | 0.02633%
IS19Inv2M2SCB1 | 159.5 | 0.04388%
IS19Inv2M2SCB2 | 127.6 | 0.0351%
IS19Inv2M2SCB3 | 95.7 | 0.02633%
IS19Inv2M2SCB4 | 127.6 | 0.0351%
IS19Inv2M2SCB5 | 159.5 | 0.04388%
IS19Inv2M2SCB6 | 127.6 | 0.0351%
IS19Inv2M3SCB1 | 191.4 | 0.05265%
IS19Inv2M3SCB2 | 63.8 | 0.01755%
IS19Inv2M3SCB3 | 159.5 | 0.04388%
IS19Inv2M3SCB4 | 127.6 | 0.0351%
IS19Inv2M3SCB5 | 31.9 | 0.008776%
IS19Inv2M3SCB6 | 191.4 | 0.05265%
IS19Inv2M4SCB1 | 223.3 | 0.06143%
IS19Inv2M4SCB2 | 223.3 | 0.06143%
IS19Inv2M4SCB3 | 223.3 | 0.06143%
IS19Inv2M4SCB4 | 223.3 | 0.06143%
IS19Inv2M4SCB5 | 127.6 | 0.0351%
IS19Inv2M4SCB6 | 159.5 | 0.04388%
IS20Inv1M1SCB1 | 223.3 | 0.06143%
IS20Inv1M1SCB2 | 223.3 | 0.06143%
IS20Inv1M1SCB3 | 223.3 | 0.06143%
IS20Inv1M1SCB4 | 223.3 | 0.06143%
IS20Inv1M1SCB5 | 223.3 | 0.06143%
IS20Inv1M1SCB6 | 175.45 | 0.04827%
IS20Inv1M2SCB1 | 207.35 | 0.05704%
IS20Inv1M2SCB2 | 191.4 | 0.05265%
IS20Inv1M2SCB3 | 223.3 | 0.06143%
IS20Inv1M2SCB4 | 191.4 | 0.05265%
IS20Inv1M2SCB5 | 175.45 | 0.04827%
IS20Inv1M2SCB6 | 175.45 | 0.04827%
IS20Inv1M3SCB1 | 223.3 | 0.06143%
IS20Inv1M3SCB2 | 223.3 | 0.06143%
IS20Inv1M3SCB3 | 191.4 | 0.05265%
IS20Inv1M3SCB4 | 191.4 | 0.05265%
IS20Inv1M3SCB5 | 223.3 | 0.06143%
IS20Inv1M3SCB6 | 223.3 | 0.06143%
IS20Inv1M4SCB1 | 223.3 | 0.06143%
IS20Inv1M4SCB2 | 223.3 | 0.06143%
IS20Inv1M4SCB3 | 223.3 | 0.06143%
IS20Inv1M4SCB4 | 223.3 | 0.06143%
IS20Inv1M4SCB5 | 223.3 | 0.06143%
IS20Inv1M4SCB6 | 223.3 | 0.06143%
IS20Inv2M1SCB1 | 223.3 | 0.06143%
IS20Inv2M1SCB2 | 223.3 | 0.06143%
IS20Inv2M1SCB3 | 223.3 | 0.06143%
IS20Inv2M1SCB4 | 223.3 | 0.06143%
IS20Inv2M1SCB5 | 207.35 | 0.05704%
IS20Inv2M1SCB6 | 223.3 | 0.06143%
IS20Inv2M2SCB1 | 159.5 | 0.04388%
IS20Inv2M2SCB2 | 31.9 | 0.008776%
IS20Inv2M2SCB3 | 0 | 0%
IS20Inv2M2SCB4 | 0 | 0%
IS20Inv2M2SCB5 | 0 | 0%
IS20Inv2M2SCB6 | 159.5 | 0.04388%
IS20Inv2M3SCB1 | 223.3 | 0.06143%
IS20Inv2M3SCB2 | 223.3 | 0.06143%
IS20Inv2M3SCB3 | 255.2 | 0.0702%
IS20Inv2M3SCB4 | 223.3 | 0.06143%
IS20Inv2M3SCB5 | 127.6 | 0.0351%
IS20Inv2M3SCB6 | 159.5 | 0.04388%
IS20Inv2M4SCB1 | 223.3 | 0.06143%
IS20Inv2M4SCB2 | 223.3 | 0.06143%
IS20Inv2M4SCB3 | 207.35 | 0.05704%
IS20Inv2M4SCB4 | 175.45 | 0.04827%
IS20Inv2M4SCB5 | 191.4 | 0.05265%
IS20Inv2M4SCB6 | 95.7 | 0.02633%
IS21Inv1M1SCB1 | 127.6 | 0.0351%
IS21Inv1M1SCB2 | 159.5 | 0.04388%
IS21Inv1M1SCB3 | 127.6 | 0.0351%
IS21Inv1M1SCB4 | 223.3 | 0.06143%
IS21Inv1M1SCB5 | 127.6 | 0.0351%
IS21Inv1M1SCB6 | 223.3 | 0.06143%
IS21Inv1M2SCB1 | 159.5 | 0.04388%
IS21Inv1M2SCB2 | 159.5 | 0.04388%
IS21Inv1M2SCB3 | 223.3 | 0.06143%
IS21Inv1M2SCB4 | 0 | 0%
IS21Inv1M2SCB5 | 63.8 | 0.01755%
IS21Inv1M2SCB6 | 159.5 | 0.04388%
IS21Inv1M3SCB1 | 63.8 | 0.01755%
IS21Inv1M3SCB2 | 95.7 | 0.02633%
IS21Inv1M3SCB3 | 95.7 | 0.02633%
IS21Inv1M3SCB4 | 31.9 | 0.008776%
IS21Inv1M3SCB5 | 127.6 | 0.0351%
IS21Inv1M3SCB6 | 95.7 | 0.02633%
IS21Inv1M4SCB1 | 127.6 | 0.0351%
IS21Inv1M4SCB2 | 159.5 | 0.04388%
IS21Inv1M4SCB3 | 127.6 | 0.0351%
IS21Inv1M4SCB4 | 127.6 | 0.0351%
IS21Inv1M4SCB5 | 191.4 | 0.05265%
IS21Inv1M4SCB6 | 127.6 | 0.0351%
IS21Inv2M1SCB1 | 159.5 | 0.04388%
IS21Inv2M1SCB2 | 191.4 | 0.05265%
IS21Inv2M1SCB3 | 159.5 | 0.04388%
IS21Inv2M1SCB4 | 159.5 | 0.04388%
IS21Inv2M1SCB5 | 159.5 | 0.04388%
IS21Inv2M1SCB6 | 175.45 | 0.04827%
IS21Inv2M2SCB1 | 159.5 | 0.04388%
IS21Inv2M2SCB2 | 127.6 | 0.0351%
IS21Inv2M2SCB3 | 159.5 | 0.04388%
IS21Inv2M2SCB4 | 111.65 | 0.03071%
IS21Inv2M2SCB5 | 159.5 | 0.04388%
IS21Inv2M2SCB6 | 111.65 | 0.03071%
IS21Inv2M3SCB1 | 207.35 | 0.05704%
IS21Inv2M3SCB2 | 159.5 | 0.04388%
IS21Inv2M3SCB3 | 63.8 | 0.01755%
IS21Inv2M3SCB4 | 0 | 0%
IS21Inv2M3SCB5 | 0 | 0%
IS21Inv2M3SCB6 | 0 | 0%
IS21Inv2M4SCB1 | 207.35 | 0.05704%
IS21Inv2M4SCB2 | 191.4 | 0.05265%
IS21Inv2M4SCB3 | 127.6 | 0.0351%
IS21Inv2M4SCB4 | 31.9 | 0.008776%
IS21Inv2M4SCB5 | 0 | 0%
IS21Inv2M4SCB6 | 0 | 0%
IS22Inv1M1SCB1 | 191.4 | 0.05265%
IS22Inv1M1SCB2 | 159.5 | 0.04388%
IS22Inv1M1SCB3 | 207.35 | 0.05704%
IS22Inv1M1SCB4 | 159.5 | 0.04388%
IS22Inv1M1SCB5 | 191.4 | 0.05265%
IS22Inv1M1SCB6 | 207.35 | 0.05704%
IS22Inv1M2SCB1 | 223.3 | 0.06143%
IS22Inv1M2SCB2 | 223.3 | 0.06143%
IS22Inv1M2SCB3 | 191.4 | 0.05265%
IS22Inv1M2SCB4 | 223.3 | 0.06143%
IS22Inv1M2SCB5 | 223.3 | 0.06143%
IS22Inv1M2SCB6 | 191.4 | 0.05265%
IS22Inv1M3SCB1 | 223.3 | 0.06143%
IS22Inv1M3SCB2 | 223.3 | 0.06143%
IS22Inv1M3SCB3 | 223.3 | 0.06143%
IS22Inv1M3SCB4 | 191.4 | 0.05265%
IS22Inv1M3SCB5 | 223.3 | 0.06143%
IS22Inv1M3SCB6 | 223.3 | 0.06143%
IS22Inv1M4SCB1 | 223.3 | 0.06143%
IS22Inv1M4SCB2 | 223.3 | 0.06143%
IS22Inv1M4SCB3 | 223.3 | 0.06143%
IS22Inv1M4SCB4 | 223.3 | 0.06143%
IS22Inv1M4SCB5 | 223.3 | 0.06143%
IS22Inv1M4SCB6 | 223.3 | 0.06143%
IS22Inv2M1SCB1 | 191.4 | 0.05265%
IS22Inv2M1SCB2 | 223.3 | 0.06143%
IS22Inv2M1SCB3 | 0 | 0%
IS22Inv2M1SCB4 | 95.7 | 0.02633%
IS22Inv2M1SCB5 | 63.8 | 0.01755%
IS22Inv2M1SCB6 | 223.3 | 0.06143%
IS22Inv2M2SCB1 | 127.6 | 0.0351%
IS22Inv2M2SCB2 | 79.75 | 0.02194%
IS22Inv2M2SCB3 | 175.45 | 0.04827%
IS22Inv2M2SCB4 | 191.4 | 0.05265%
IS22Inv2M2SCB5 | 191.4 | 0.05265%
IS22Inv2M2SCB6 | 223.3 | 0.06143%
IS22Inv2M3SCB1 | 0 | 0%
IS22Inv2M3SCB2 | 143.55 | 0.03949%
IS22Inv2M3SCB3 | 63.8 | 0.01755%
IS22Inv2M3SCB4 | 191.4 | 0.05265%
IS22Inv2M3SCB5 | 191.4 | 0.05265%
IS22Inv2M3SCB6 | 223.3 | 0.06143%
IS22Inv2M4SCB1 | 223.3 | 0.06143%
IS22Inv2M4SCB2 | 223.3 | 0.06143%
IS22Inv2M4SCB3 | 223.3 | 0.06143%
IS22Inv2M4SCB4 | 159.5 | 0.04388%
IS22Inv2M4SCB5 | 223.3 | 0.06143%
IS22Inv2M4SCB6 | 191.4 | 0.05265%
IS23Inv1M1SCB1 | 223.3 | 0.06143%
IS23Inv1M1SCB2 | 191.4 | 0.05265%
IS23Inv1M1SCB3 | 191.4 | 0.05265%
IS23Inv1M1SCB4 | 191.4 | 0.05265%
IS23Inv1M1SCB5 | 223.3 | 0.06143%
IS23Inv1M1SCB6 | 159.5 | 0.04388%
IS23Inv1M2SCB1 | 223.3 | 0.06143%
IS23Inv1M2SCB2 | 127.6 | 0.0351%
IS23Inv1M2SCB3 | 63.8 | 0.01755%
IS23Inv1M2SCB4 | 95.7 | 0.02633%
IS23Inv1M2SCB5 | 127.6 | 0.0351%
IS23Inv1M2SCB6 | 159.5 | 0.04388%
IS23Inv1M3SCB1 | 191.4 | 0.05265%
IS23Inv1M3SCB2 | 223.3 | 0.06143%
IS23Inv1M3SCB3 | 223.3 | 0.06143%
IS23Inv1M3SCB4 | 223.3 | 0.06143%
IS23Inv1M3SCB5 | 223.3 | 0.06143%
IS23Inv1M3SCB6 | 159.5 | 0.04388%
IS23Inv1M4SCB1 | 223.3 | 0.06143%
IS23Inv1M4SCB2 | 223.3 | 0.06143%
IS23Inv1M4SCB3 | 223.3 | 0.06143%
IS23Inv1M4SCB4 | 191.4 | 0.05265%
IS23Inv1M4SCB5 | 127.6 | 0.0351%
IS23Inv1M4SCB6 | 159.5 | 0.04388%
IS23Inv2M1SCB1 | 223.3 | 0.06143%
IS23Inv2M1SCB2 | 159.5 | 0.04388%
IS23Inv2M1SCB3 | 223.3 | 0.06143%
IS23Inv2M1SCB4 | 223.3 | 0.06143%
IS23Inv2M1SCB5 | 223.3 | 0.06143%
IS23Inv2M1SCB6 | 207.35 | 0.05704%
IS23Inv2M2SCB1 | 223.3 | 0.06143%
IS23Inv2M2SCB2 | 223.3 | 0.06143%
IS23Inv2M2SCB3 | 223.3 | 0.06143%
IS23Inv2M2SCB4 | 191.4 | 0.05265%
IS23Inv2M2SCB5 | 191.4 | 0.05265%
IS23Inv2M2SCB6 | 223.3 | 0.06143%
IS23Inv2M3SCB1 | 223.3 | 0.06143%
IS23Inv2M3SCB2 | 191.4 | 0.05265%
IS23Inv2M3SCB3 | 159.5 | 0.04388%
IS23Inv2M3SCB4 | 223.3 | 0.06143%
IS23Inv2M3SCB5 | 191.4 | 0.05265%
IS23Inv2M3SCB6 | 223.3 | 0.06143%
IS23Inv2M4SCB1 | 191.4 | 0.05265%
IS23Inv2M4SCB2 | 159.5 | 0.04388%
IS23Inv2M4SCB3 | 223.3 | 0.06143%
IS23Inv2M4SCB4 | 191.4 | 0.05265%
IS23Inv2M4SCB5 | 191.4 | 0.05265%
IS23Inv2M4SCB6 | 223.3 | 0.06143%
IS24Inv1M1SCB1 | 0 | 0%
IS24Inv1M1SCB2 | 0 | 0%
IS24Inv1M1SCB3 | 0 | 0%
IS24Inv1M1SCB4 | 0 | 0%
IS24Inv1M1SCB5 | 0 | 0%
IS24Inv1M1SCB6 | 0 | 0%
IS24Inv1M2SCB1 | 0 | 0%
IS24Inv1M2SCB2 | 0 | 0%
IS24Inv1M2SCB3 | 0 | 0%
IS24Inv1M2SCB4 | 0 | 0%
IS24Inv1M2SCB5 | 0 | 0%
IS24Inv1M2SCB6 | 0 | 0%
IS24Inv1M3SCB1 | 0 | 0%
IS24Inv1M3SCB2 | 0 | 0%
IS24Inv1M3SCB3 | 0 | 0%
IS24Inv1M3SCB4 | 0 | 0%
IS24Inv1M3SCB5 | 0 | 0%
IS24Inv1M3SCB6 | 0 | 0%
IS24Inv1M4SCB1 | 0 | 0%
IS24Inv1M4SCB2 | 0 | 0%
IS24Inv1M4SCB3 | 0 | 0%
IS24Inv1M4SCB4 | 0 | 0%
IS24Inv1M4SCB5 | 0 | 0%
IS24Inv1M4SCB6 | 0 | 0%
IS24Inv2M1SCB1 | 0 | 0%
IS24Inv2M1SCB2 | 0 | 0%
IS24Inv2M1SCB3 | 0 | 0%
IS24Inv2M1SCB4 | 0 | 0%
IS24Inv2M1SCB5 | 0 | 0%
IS24Inv2M1SCB6 | 0 | 0%
IS24Inv2M2SCB1 | 0 | 0%
IS24Inv2M2SCB2 | 0 | 0%
IS24Inv2M2SCB3 | 0 | 0%
IS24Inv2M2SCB4 | 0 | 0%
IS24Inv2M2SCB5 | 0 | 0%
IS24Inv2M2SCB6 | 0 | 0%
IS24Inv2M3SCB1 | 0 | 0%
IS24Inv2M3SCB2 | 0 | 0%
IS24Inv2M3SCB3 | 0 | 0%
IS24Inv2M3SCB4 | 0 | 0%
IS24Inv2M3SCB5 | 0 | 0%
IS24Inv2M3SCB6 | 0 | 0%
IS24Inv2M4SCB1 | 0 | 0%
IS24Inv2M4SCB2 | 0 | 0%
IS24Inv2M4SCB3 | 0 | 0%
IS24Inv2M4SCB4 | 0 | 0%
IS24Inv2M4SCB5 | 0 | 0%
IS24Inv2M4SCB6 | 0 | 0%
IS25Inv1M1SCB1 | 0 | 0%
IS25Inv1M1SCB2 | 0 | 0%
IS25Inv1M1SCB3 | 0 | 0%
IS25Inv1M1SCB4 | 0 | 0%
IS25Inv1M1SCB5 | 0 | 0%
IS25Inv1M1SCB6 | 0 | 0%
IS25Inv1M2SCB1 | 0 | 0%
IS25Inv1M2SCB2 | 0 | 0%
IS25Inv1M2SCB3 | 0 | 0%
IS25Inv1M2SCB4 | 0 | 0%
IS25Inv1M2SCB5 | 0 | 0%
IS25Inv1M2SCB6 | 0 | 0%
IS25Inv1M3SCB1 | 0 | 0%
IS25Inv1M3SCB2 | 0 | 0%
IS25Inv1M3SCB3 | 0 | 0%
IS25Inv1M3SCB4 | 0 | 0%
IS25Inv1M3SCB5 | 0 | 0%
IS25Inv1M3SCB6 | 0 | 0%
IS25Inv1M4SCB1 | 0 | 0%
IS25Inv1M4SCB2 | 0 | 0%
IS25Inv1M4SCB3 | 0 | 0%
IS25Inv1M4SCB4 | 0 | 0%
IS25Inv1M4SCB5 | 0 | 0%
IS25Inv1M4SCB6 | 0 | 0%
IS25Inv2M1SCB1 | 0 | 0%
IS25Inv2M1SCB2 | 0 | 0%
IS25Inv2M1SCB3 | 0 | 0%
IS25Inv2M1SCB4 | 0 | 0%
IS25Inv2M1SCB5 | 0 | 0%
IS25Inv2M1SCB6 | 0 | 0%
IS25Inv2M2SCB1 | 0 | 0%
IS25Inv2M2SCB2 | 0 | 0%
IS25Inv2M2SCB3 | 0 | 0%
IS25Inv2M2SCB4 | 0 | 0%
IS25Inv2M2SCB5 | 0 | 0%
IS25Inv2M2SCB6 | 0 | 0%
IS25Inv2M3SCB1 | 0 | 0%
IS25Inv2M3SCB2 | 0 | 0%
IS25Inv2M3SCB3 | 0 | 0%
IS25Inv2M3SCB4 | 0 | 0%
IS25Inv2M3SCB5 | 0 | 0%
IS25Inv2M3SCB6 | 0 | 0%
IS25Inv2M4SCB1 | 0 | 0%
IS25Inv2M4SCB2 | 0 | 0%
IS25Inv2M4SCB3 | 0 | 0%
IS25Inv2M4SCB4 | 0 | 0%
IS25Inv2M4SCB5 | 0 | 0%
IS25Inv2M4SCB6 | 0 | 0%
IS26Inv1M1SCB1 | 0 | 0%
IS26Inv1M1SCB2 | 0 | 0%
IS26Inv1M1SCB3 | 0 | 0%
IS26Inv1M1SCB4 | 0 | 0%
IS26Inv1M1SCB5 | 0 | 0%
IS26Inv1M1SCB6 | 0 | 0%
IS26Inv1M2SCB1 | 0 | 0%
IS26Inv1M2SCB2 | 0 | 0%
IS26Inv1M2SCB3 | 0 | 0%
IS26Inv1M2SCB4 | 0 | 0%
IS26Inv1M2SCB5 | 0 | 0%
IS26Inv1M2SCB6 | 0 | 0%
IS26Inv1M3SCB1 | 0 | 0%
IS26Inv1M3SCB2 | 0 | 0%
IS26Inv1M3SCB3 | 0 | 0%
IS26Inv1M3SCB4 | 0 | 0%
IS26Inv1M3SCB5 | 0 | 0%
IS26Inv1M3SCB6 | 0 | 0%
IS26Inv1M4SCB1 | 0 | 0%
IS26Inv1M4SCB2 | 0 | 0%
IS26Inv1M4SCB3 | 0 | 0%
IS26Inv1M4SCB4 | 0 | 0%
IS26Inv1M4SCB5 | 0 | 0%
IS26Inv1M4SCB6 | 0 | 0%
IS26Inv2M1SCB1 | 0 | 0%
IS26Inv2M1SCB2 | 0 | 0%
IS26Inv2M1SCB3 | 0 | 0%
IS26Inv2M1SCB4 | 0 | 0%
IS26Inv2M1SCB5 | 0 | 0%
IS26Inv2M1SCB6 | 0 | 0%
IS26Inv2M2SCB1 | 0 | 0%
IS26Inv2M2SCB2 | 0 | 0%
IS26Inv2M2SCB3 | 0 | 0%
IS26Inv2M2SCB4 | 0 | 0%
IS26Inv2M2SCB5 | 0 | 0%
IS26Inv2M2SCB6 | 0 | 0%
IS26Inv2M3SCB1 | 0 | 0%
IS26Inv2M3SCB2 | 0 | 0%
IS26Inv2M3SCB3 | 0 | 0%
IS26Inv2M3SCB4 | 0 | 0%
IS26Inv2M3SCB5 | 0 | 0%
IS26Inv2M3SCB6 | 0 | 0%
IS26Inv2M4SCB1 | 0 | 0%
IS26Inv2M4SCB2 | 0 | 0%
IS26Inv2M4SCB3 | 0 | 0%
IS26Inv2M4SCB4 | 0 | 0%
IS26Inv2M4SCB5 | 0 | 0%
IS26Inv2M4SCB6 | 0 | 0%
IS27Inv1M1SCB1 | 0 | 0%
IS27Inv1M1SCB2 | 0 | 0%
IS27Inv1M1SCB3 | 0 | 0%
IS27Inv1M1SCB4 | 0 | 0%
IS27Inv1M1SCB5 | 0 | 0%
IS27Inv1M1SCB6 | 0 | 0%
IS27Inv1M2SCB1 | 0 | 0%
IS27Inv1M2SCB2 | 0 | 0%
IS27Inv1M2SCB3 | 0 | 0%
IS27Inv1M2SCB4 | 0 | 0%
IS27Inv1M2SCB5 | 0 | 0%
IS27Inv1M2SCB6 | 0 | 0%
IS27Inv1M3SCB1 | 0 | 0%
IS27Inv1M3SCB2 | 0 | 0%
IS27Inv1M3SCB3 | 0 | 0%
IS27Inv1M3SCB4 | 0 | 0%
IS27Inv1M3SCB5 | 0 | 0%
IS27Inv1M3SCB6 | 0 | 0%
IS27Inv1M4SCB1 | 0 | 0%
IS27Inv1M4SCB2 | 0 | 0%
IS27Inv1M4SCB3 | 0 | 0%
IS27Inv1M4SCB4 | 0 | 0%
IS27Inv1M4SCB5 | 0 | 0%
IS27Inv1M4SCB6 | 0 | 0%
IS27Inv2M1SCB1 | 0 | 0%
IS27Inv2M1SCB2 | 0 | 0%
IS27Inv2M1SCB3 | 0 | 0%
IS27Inv2M1SCB4 | 0 | 0%
IS27Inv2M1SCB5 | 0 | 0%
IS27Inv2M1SCB6 | 0 | 0%
IS27Inv2M2SCB1 | 0 | 0%
IS27Inv2M2SCB2 | 0 | 0%
IS27Inv2M2SCB3 | 0 | 0%
IS27Inv2M2SCB4 | 0 | 0%
IS27Inv2M2SCB5 | 0 | 0%
IS27Inv2M2SCB6 | 0 | 0%
IS27Inv2M3SCB1 | 0 | 0%
IS27Inv2M3SCB2 | 0 | 0%
IS27Inv2M3SCB3 | 0 | 0%
IS27Inv2M3SCB4 | 0 | 0%
IS27Inv2M3SCB5 | 0 | 0%
IS27Inv2M3SCB6 | 0 | 0%
IS27Inv2M4SCB1 | 0 | 0%
IS27Inv2M4SCB2 | 0 | 0%
IS27Inv2M4SCB3 | 0 | 0%
IS27Inv2M4SCB4 | 0 | 0%
IS27Inv2M4SCB5 | 0 | 0%
IS27Inv2M4SCB6 | 0 | 0%
IS28Inv1M1SCB1 | 223.3 | 0.06143%
IS28Inv1M1SCB2 | 207.35 | 0.05704%
IS28Inv1M1SCB3 | 223.3 | 0.06143%
IS28Inv1M1SCB4 | 175.45 | 0.04827%
IS28Inv1M1SCB5 | 223.3 | 0.06143%
IS28Inv1M1SCB6 | 191.4 | 0.05265%
IS28Inv1M2SCB1 | 223.3 | 0.06143%
IS28Inv1M2SCB2 | 223.3 | 0.06143%
IS28Inv1M2SCB3 | 175.45 | 0.04827%
IS28Inv1M2SCB4 | 143.55 | 0.03949%
IS28Inv1M2SCB5 | 191.4 | 0.05265%
IS28Inv1M2SCB6 | 223.3 | 0.06143%
IS28Inv1M3SCB1 | 95.7 | 0.02633%
IS28Inv1M3SCB2 | 63.8 | 0.01755%
IS28Inv1M3SCB3 | 0 | 0%
IS28Inv1M3SCB4 | 191.4 | 0.05265%
IS28Inv1M3SCB5 | 223.3 | 0.06143%
IS28Inv1M3SCB6 | 159.5 | 0.04388%
IS28Inv1M4SCB1 | 95.7 | 0.02633%
IS28Inv1M4SCB2 | 0 | 0%
IS28Inv1M4SCB3 | 191.4 | 0.05265%
IS28Inv1M4SCB4 | 191.4 | 0.05265%
IS28Inv1M4SCB5 | 95.7 | 0.02633%
IS28Inv1M4SCB6 | 95.7 | 0.02633%
IS28Inv2M1SCB1 | 0 | 0%
IS28Inv2M1SCB2 | 95.7 | 0.02633%
IS28Inv2M1SCB3 | 223.3 | 0.06143%
IS28Inv2M1SCB4 | 223.3 | 0.06143%
IS28Inv2M1SCB5 | 223.3 | 0.06143%
IS28Inv2M1SCB6 | 95.7 | 0.02633%
IS28Inv2M2SCB1 | 0 | 0%
IS28Inv2M2SCB2 | 0 | 0%
IS28Inv2M2SCB3 | 0 | 0%
IS28Inv2M2SCB4 | 0 | 0%
IS28Inv2M2SCB5 | 0 | 0%
IS28Inv2M2SCB6 | 0 | 0%
IS28Inv2M3SCB1 | 127.6 | 0.0351%
IS28Inv2M3SCB2 | 223.3 | 0.06143%
IS28Inv2M3SCB3 | 0 | 0%
IS28Inv2M3SCB4 | 0 | 0%
IS28Inv2M3SCB5 | 0 | 0%
IS28Inv2M3SCB6 | 0 | 0%
IS28Inv2M4SCB1 | 223.3 | 0.06143%
IS28Inv2M4SCB2 | 223.3 | 0.06143%
IS28Inv2M4SCB3 | 127.6 | 0.0351%
IS28Inv2M4SCB4 | 127.6 | 0.0351%
IS28Inv2M4SCB5 | 0 | 0%
IS28Inv2M4SCB6 | 0 | 0% | Incomer | Incomer 12 | Incomer 11 | Incomer 10 |  | Incomer 8 | Incomer 9 | Incomer 5 |  |  | Incomer 4 | Incomer 3 | Incomer 2 | Incomer 1
IS29Inv1M1SCB1 | 223.3 | 0.06143% | DC Capacity (kwh) | 33307.805 | 33236.03 | 33870.55 |  | 33293.16 | 33667.26 | 33491.665 |  |  | 33340.14 | 33199.2 | 32103 | 35001.72
IS29Inv1M1SCB2 | 63.8 | 0.01755% | Block | IR1-IR2 | IR3-IR4 | IR5-IR6 |  | IR8-IR7 | IR9-IR10 | IR12-IR11 |  |  | IR13-IR14 | IR15-IR16 | IR17-IR18 | IR19-IR20
IS29Inv1M1SCB3 | 191.4 | 0.05265% | Full Load current | 613.4057 | 612.0839 | 623.7694 |  | 613.136 | 620.0256 | 616.7918 |  |  | 614.0012 | 611.4056 | 591.2177 | 644.6014
IS29Inv1M1SCB4 | 191.4 | 0.05265%
IS29Inv1M1SCB5 | 223.3 | 0.06143% | MCR_MVP_Inc1 | 35109.72 | Block | Full Load current
IS29Inv1M1SCB6 | 95.7 | 0.02633% | MCR_MVP_Inc10 | 33895.78 | IR1-IR2 | 613.4057
IS29Inv1M2SCB1 | 127.6 | 0.0351% | MCR_MVP_Inc11 | 33314.04 | IR3-IR4 | 612.0839
IS29Inv1M2SCB2 | 127.6 | 0.0351% | MCR_MVP_Inc12 | 33488.475 | IR5-IR6 | 623.7694
IS29Inv1M2SCB3 | 127.6 | 0.0351% | MCR_MVP_Inc2 | 32118.66 | IR8-IR7 | 613.136
IS29Inv1M2SCB4 | 159.5 | 0.04388% | MCR_MVP_Inc3 | 33230.52 | IR9-IR10 | 620.0256
IS29Inv1M2SCB5 | 159.5 | 0.04388% | MCR_MVP_Inc4 | 33355.8 | IR12-IR11 | 616.7918
IS29Inv1M2SCB6 | 31.9 | 0.008776% | MCR_MVP_Inc5 | 33508.05 | IR13-IR14 | 614.0012
IS29Inv1M3SCB1 | 159.5 | 0.04388% | MCR_MVP_Inc8 | 33371.46 | IR15-IR16 | 611.4056
IS29Inv1M3SCB2 | 63.8 | 0.01755% | MCR_MVP_Inc9 | 33699.16 | IR17-IR18 | 591.2177
IS29Inv1M3SCB3 | 127.6 | 0.0351% |  |  | IR19-IR20 | 644.6014
IS29Inv1M3SCB4 | 191.4 | 0.05265%
IS29Inv1M3SCB5 | 159.5 | 0.04388%
IS29Inv1M3SCB6 | 159.5 | 0.04388%
IS29Inv1M4SCB1 | 191.4 | 0.05265%
IS29Inv1M4SCB2 | 127.6 | 0.0351%
IS29Inv1M4SCB3 | 0 | 0%
IS29Inv1M4SCB4 | 223.3 | 0.06143%
IS29Inv1M4SCB5 | 223.3 | 0.06143%
IS29Inv1M4SCB6 | 223.3 | 0.06143%
IS29Inv2M1SCB1 | 159.5 | 0.04388%
IS29INV2M1SCB2 | 191.4 | 0.05265%
IS29Inv2M1SCB3 | 223.3 | 0.06143%
IS29Inv2M1SCB4 | 191.4 | 0.05265%
IS29Inv2M1SCB5 | 223.3 | 0.06143%
IS29Inv2M1SCB6 | 191.4 | 0.05265%
IS29Inv2M2SCB1 | 127.6 | 0.0351%
IS29Inv2M2SCB2 | 159.5 | 0.04388%
IS29Inv2M2SCB3 | 191.4 | 0.05265%
IS29Inv2M2SCB4 | 223.3 | 0.06143%
IS29Inv2M2SCB5 | 223.3 | 0.06143%
IS29Inv2M2SCB6 | 127.6 | 0.0351%
IS29Inv2M3SCB1 | 159.5 | 0.04388%
IS29Inv2M3SCB2 | 191.4 | 0.05265%
IS29Inv2M3SCB3 | 95.7 | 0.02633%
IS29Inv2M3SCB4 | 223.3 | 0.06143%
IS29Inv2M3SCB5 | 95.7 | 0.02633%
IS29Inv2M3SCB6 | 127.6 | 0.0351%
IS29Inv2M4SCB1 | 95.7 | 0.02633%
IS29Inv2M4SCB2 | 223.3 | 0.06143%
IS29Inv2M4SCB3 | 207.35 | 0.05704%
IS29Inv2M4SCB4 | 223.3 | 0.06143%
IS29Inv2M4SCB5 | 223.3 | 0.06143%
IS29Inv2M4SCB6 | 191.4 | 0.05265%
IS30Inv1M1SCB1 | 191.4 | 0.05265%
IS30Inv1M1SCB2 | 223.3 | 0.06143%
IS30Inv1M1SCB3 | 223.3 | 0.06143%
IS30Inv1M1SCB4 | 223.3 | 0.06143%
IS30Inv1M1SCB5 | 159.5 | 0.04388%
IS30Inv1M1SCB6 | 223.3 | 0.06143%
IS30Inv1M2SCB1 | 223.3 | 0.06143%
IS30Inv1M2SCB2 | 223.3 | 0.06143%
IS30Inv1M2SCB3 | 223.3 | 0.06143%
IS30Inv1M2SCB4 | 191.4 | 0.05265%
IS30Inv1M2SCB5 | 223.3 | 0.06143%
IS30Inv1M2SCB6 | 191.4 | 0.05265%
IS30Inv1M3SCB1 | 223.3 | 0.06143%
IS30Inv1M3SCB2 | 191.4 | 0.05265%
IS30Inv1M3SCB3 | 191.4 | 0.05265%
IS30Inv1M3SCB4 | 223.3 | 0.06143%
IS30Inv1M3SCB5 | 159.5 | 0.04388%
IS30Inv1M3SCB6 | 127.6 | 0.0351%
IS30Inv1M4SCB1 | 223.3 | 0.06143%
IS30Inv1M4SCB2 | 223.3 | 0.06143%
IS30Inv1M4SCB3 | 223.3 | 0.06143%
IS30Inv1M4SCB4 | 223.3 | 0.06143%
IS30Inv1M4SCB5 | 159.5 | 0.04388%
IS30Inv1M4SCB6 | 223.3 | 0.06143%
IS30Inv2M1SCB1 | 223.3 | 0.06143%
IS30Inv2M1SCB2 | 223.3 | 0.06143%
IS30Inv2M1SCB3 | 223.3 | 0.06143%
IS30Inv2M1SCB4 | 223.3 | 0.06143%
IS30Inv2M1SCB5 | 127.6 | 0.0351%
IS30Inv2M1SCB6 | 191.4 | 0.05265%
IS30Inv2M2SCB1 | 223.3 | 0.06143%
IS30Inv2M2SCB2 | 159.5 | 0.04388%
IS30Inv2M2SCB3 | 95.7 | 0.02633%
IS30Inv2M2SCB4 | 191.4 | 0.05265%
IS30Inv2M2SCB5 | 223.3 | 0.06143%
IS30Inv2M2SCB6 | 191.4 | 0.05265%
IS30Inv2M3SCB1 | 159.5 | 0.04388%
IS30Inv2M3SCB2 | 223.3 | 0.06143%
IS30Inv2M3SCB3 | 223.3 | 0.06143%
IS30Inv2M3SCB4 | 191.4 | 0.05265%
IS30Inv2M3SCB5 | 159.5 | 0.04388%
IS30Inv2M3SCB6 | 63.8 | 0.01755%
IS30Inv2M4SCB1 | 223.3 | 0.06143%
IS30Inv2M4SCB2 | 223.3 | 0.06143%
IS30Inv2M4SCB3 | 223.3 | 0.06143%
IS30Inv2M4SCB4 | 223.3 | 0.06143%
IS30Inv2M4SCB5 | 223.3 | 0.06143%
IS30Inv2M4SCB6 | 223.3 | 0.06143%
IS31Inv1M1SCB1 | 223.3 | 0.06143%
IS31Inv1M1SCB2 | 223.3 | 0.06143%
IS31Inv1M1SCB3 | 191.4 | 0.05265%
IS31Inv1M1SCB4 | 127.6 | 0.0351%
IS31Inv1M1SCB5 | 127.6 | 0.0351%
IS31Inv1M1SCB6 | 223.3 | 0.06143%
IS31Inv1M2SCB1 | 223.3 | 0.06143%
IS31Inv1M2SCB2 | 223.3 | 0.06143%
IS31Inv1M2SCB3 | 223.3 | 0.06143%
IS31Inv1M2SCB4 | 191.4 | 0.05265%
IS31Inv1M2SCB5 | 223.3 | 0.06143%
IS31Inv1M2SCB6 | 223.3 | 0.06143%
IS31Inv1M3SCB1 | 223.3 | 0.06143%
IS31Inv1M3SCB2 | 223.3 | 0.06143%
IS31Inv1M3SCB3 | 223.3 | 0.06143%
IS31Inv1M3SCB4 | 223.3 | 0.06143%
IS31Inv1M3SCB5 | 223.3 | 0.06143%
IS31Inv1M3SCB6 | 191.4 | 0.05265%
IS31Inv1M4SCB1 | 223.3 | 0.06143%
IS31Inv1M4SCB2 | 223.3 | 0.06143%
IS31Inv1M4SCB3 | 223.3 | 0.06143%
IS31Inv1M4SCB4 | 223.3 | 0.06143%
IS31Inv1M4SCB5 | 223.3 | 0.06143%
IS31Inv1M4SCB6 | 223.3 | 0.06143%
IS31Inv2M1SCB1 | 223.3 | 0.06143%
IS31Inv2M1SCB2 | 223.3 | 0.06143%
IS31Inv2M1SCB3 | 223.3 | 0.06143%
IS31Inv2M1SCB4 | 223.3 | 0.06143%
IS31Inv2M1SCB5 | 207.35 | 0.05704%
IS31Inv2M1SCB6 | 191.4 | 0.05265%
IS31Inv2M2SCB1 | 223.3 | 0.06143%
IS31Inv2M2SCB2 | 223.3 | 0.06143%
IS31Inv2M2SCB3 | 223.3 | 0.06143%
IS31Inv2M2SCB4 | 223.3 | 0.06143%
IS31Inv2M2SCB5 | 223.3 | 0.06143%
IS31Inv2M2SCB6 | 223.3 | 0.06143%
IS31Inv2M3SCB1 | 223.3 | 0.06143%
IS31Inv2M3SCB2 | 223.3 | 0.06143%
IS31Inv2M3SCB3 | 223.3 | 0.06143%
IS31Inv2M3SCB4 | 223.3 | 0.06143%
IS31Inv2M3SCB5 | 223.3 | 0.06143%
IS31Inv2M3SCB6 | 223.3 | 0.06143%
IS31Inv2M4SCB1 | 223.3 | 0.06143%
IS31Inv2M4SCB2 | 223.3 | 0.06143%
IS31Inv2M4SCB3 | 223.3 | 0.06143%
IS31Inv2M4SCB4 | 223.3 | 0.06143%
IS31Inv2M4SCB5 | 223.3 | 0.06143%
IS31Inv2M4SCB6 | 223.3 | 0.06143%
IS32Inv2M1SCB1 | 223.3 | 0.06143%
IS32Inv1M1SCB2 | 223.3 | 0.06143%
IS32Inv1M1SCB3 | 223.3 | 0.06143%
IS32Inv1M1SCB4 | 191.4 | 0.05265%
IS32Inv1M1SCB5 | 223.3 | 0.06143%
IS32Inv1M1SCB6 | 223.3 | 0.06143%
IS32Inv1M2SCB1 | 191.4 | 0.05265%
IS32Inv1M2SCB2 | 223.3 | 0.06143%
IS32Inv1M2SCB3 | 223.3 | 0.06143%
IS32Inv1M2SCB4 | 207.35 | 0.05704%
IS32Inv1M2SCB5 | 191.4 | 0.05265%
IS32Inv1M2SCB6 | 207.35 | 0.05704%
IS32Inv1M3SCB1 | 191.4 | 0.05265%
IS32Inv1M3SCB2 | 223.3 | 0.06143%
IS32Inv1M3SCB3 | 223.3 | 0.06143%
IS32Inv1M3SCB4 | 223.3 | 0.06143%
IS32Inv1M3SCB5 | 223.3 | 0.06143%
IS32Inv1M3SCB6 | 223.3 | 0.06143%
IS32Inv1M4SCB1 | 223.3 | 0.06143%
IS32Inv1M4SCB2 | 223.3 | 0.06143%
IS32Inv1M4SCB3 | 223.3 | 0.06143%
IS32Inv1M4SCB4 | 223.3 | 0.06143%
IS32Inv1M4SCB5 | 223.3 | 0.06143%
IS32Inv1M4SCB6 | 223.3 | 0.06143%
IS32Inv2M1SCB1 | 223.3 | 0.06143%
IS32Inv2M1SCB2 | 223.3 | 0.06143%
IS32Inv2M1SCB3 | 223.3 | 0.06143%
IS32Inv2M1SCB4 | 223.3 | 0.06143%
IS32Inv2M1SCB5 | 223.3 | 0.06143%
IS32Inv2M1SCB6 | 223.3 | 0.06143%
IS32Inv2M2SCB1 | 191.4 | 0.05265%
IS32Inv2M2SCB2 | 127.6 | 0.0351%
IS32Inv2M2SCB3 | 223.3 | 0.06143%
IS32Inv2M2SCB4 | 223.3 | 0.06143%
IS32Inv2M2SCB5 | 159.5 | 0.04388%
IS32Inv2M2SCB6 | 159.5 | 0.04388%
IS32Inv2M3SCB1 | 223.3 | 0.06143%
IS32Inv2M3SCB2 | 223.3 | 0.06143%
IS32Inv2M3SCB3 | 223.3 | 0.06143%
IS32Inv2M3SCB4 | 159.5 | 0.04388%
IS32Inv2M3SCB5 | 223.3 | 0.06143%
IS32Inv2M3SCB6 | 223.3 | 0.06143%
IS32Inv2M4SCB1 | 223.3 | 0.06143%
IS32Inv2M4SCB2 | 191.4 | 0.05265%
IS32Inv2M4SCB3 | 223.3 | 0.06143%
IS32Inv2M4SCB4 | 159.5 | 0.04388%
IS32Inv2M4SCB5 | 223.3 | 0.06143%
IS32Inv2M4SCB6 | 191.4 | 0.05265%
IS33Inv1M1SCB1 | 191.4 | 0.05265%
IS33Inv1M1SCB2 | 191.4 | 0.05265%
IS33Inv1M1SCB3 | 191.4 | 0.05265%
IS33Inv1M1SCB4 | 223.3 | 0.06143%
IS33Inv1M1SCB5 | 191.4 | 0.05265%
IS33Inv1M1SCB6 | 191.4 | 0.05265%
IS33Inv1M2SCB1 | 223.3 | 0.06143%
IS33Inv1M2SCB2 | 223.3 | 0.06143%
IS33Inv1M2SCB3 | 191.4 | 0.05265%
IS33Inv1M2SCB4 | 223.3 | 0.06143%
IS33Inv1M2SCB5 | 223.3 | 0.06143%
IS33Inv1M2SCB6 | 159.5 | 0.04388%
IS33Inv1M3SCB1 | 0 | 0%
IS33Inv1M3SCB2 | 127.6 | 0.0351%
IS33Inv1M3SCB3 | 191.4 | 0.05265%
IS33Inv1M3SCB4 | 223.3 | 0.06143%
IS33Inv1M3SCB5 | 223.3 | 0.06143%
IS33Inv1M3SCB6 | 159.5 | 0.04388%
IS33Inv1M4SCB1 | 223.3 | 0.06143%
IS33Inv1M4SCB2 | 223.3 | 0.06143%
IS33Inv1M4SCB3 | 191.4 | 0.05265%
IS33Inv1M4SCB4 | 223.3 | 0.06143%
IS33Inv1M4SCB5 | 223.3 | 0.06143%
IS33Inv1M4SCB6 | 191.4 | 0.05265%
IS33Inv2M1SCB1 | 95.7 | 0.02633%
IS33Inv2M1SCB2 | 191.4 | 0.05265%
IS33Inv2M1SCB3 | 223.3 | 0.06143%
IS33Inv2M1SCB4 | 223.3 | 0.06143%
IS33Inv2M1SCB5 | 191.4 | 0.05265%
IS33Inv2M1SCB6 | 223.3 | 0.06143%
IS33Inv2M2SCB1 | 31.9 | 0.008776%
IS33Inv2M2SCB2 | 223.3 | 0.06143%
IS33Inv2M2SCB3 | 223.3 | 0.06143%
IS33Inv2M2SCB4 | 223.3 | 0.06143%
IS33Inv2M2SCB5 | 223.3 | 0.06143%
IS33Inv2M2SCB6 | 191.4 | 0.05265%
IS33Inv2M3SCB1 | 159.5 | 0.04388%
IS33Inv2M3SCB2 | 207.35 | 0.05704%
IS33Inv2M3SCB3 | 223.3 | 0.06143%
IS33Inv2M3SCB4 | 223.3 | 0.06143%
IS33Inv2M3SCB5 | 223.3 | 0.06143%
IS33Inv2M3SCB6 | 223.3 | 0.06143%
IS33Inv2M4SCB1 | 127.6 | 0.0351%
IS33Inv2M4SCB2 | 63.8 | 0.01755%
IS33Inv2M4SCB3 | 159.5 | 0.04388%
IS33Inv2M4SCB4 | 159.5 | 0.04388%
IS33Inv2M4SCB5 | 223.3 | 0.06143%
IS33Inv2M4SCB6 | 223.3 | 0.06143%
IS34Inv1M1SCB1 | 223.3 | 0.06143%
IS34Inv1M1SCB2 | 223.3 | 0.06143%
IS34Inv1M1SCB3 | 223.3 | 0.06143%
IS34Inv1M1SCB4 | 223.3 | 0.06143%
IS34Inv1M1SCB5 | 191.4 | 0.05265%
IS34Inv1M1SCB6 | 0 | 0%
IS34Inv1M2SCB1 | 95.7 | 0.02633%
IS34Inv1M2SCB2 | 159.5 | 0.04388%
IS34Inv1M2SCB3 | 191.4 | 0.05265%
IS34Inv1M2SCB4 | 127.6 | 0.0351%
IS34Inv1M2SCB5 | 127.6 | 0.0351%
IS34Inv1M2SCB6 | 191.4 | 0.05265%
IS34Inv1M3SCB1 | 127.6 | 0.0351%
IS34Inv1M3SCB2 | 223.3 | 0.06143%
IS34Inv1M3SCB3 | 191.4 | 0.05265%
IS34Inv1M3SCB4 | 223.3 | 0.06143%
IS34Inv1M3SCB5 | 191.4 | 0.05265%
IS34Inv1M3SCB6 | 223.3 | 0.06143%
IS34Inv1M4SCB1 | 223.3 | 0.06143%
IS34Inv1M4SCB2 | 159.5 | 0.04388%
IS34Inv1M4SCB3 | 223.3 | 0.06143%
IS34Inv1M4SCB4 | 223.3 | 0.06143%
IS34Inv1M4SCB5 | 159.5 | 0.04388%
IS34Inv1M4SCB6 | 191.4 | 0.05265%
IS34Inv2M1SCB1 | 223.3 | 0.06143%
IS34Inv2M1SCB2 | 223.3 | 0.06143%
IS34Inv2M1SCB3 | 223.3 | 0.06143%
IS34Inv2M1SCB4 | 191.4 | 0.05265%
IS34Inv2M1SCB5 | 223.3 | 0.06143%
IS34Inv2M1SCB6 | 223.3 | 0.06143%
IS34Inv2M2SCB1 | 223.3 | 0.06143%
IS34Inv2M2SCB2 | 223.3 | 0.06143%
IS34Inv2M2SCB3 | 223.3 | 0.06143%
IS34Inv2M2SCB4 | 223.3 | 0.06143%
IS34Inv2M2SCB5 | 191.4 | 0.05265%
IS34Inv2M2SCB6 | 223.3 | 0.06143%
IS34Inv2M3SCB1 | 159.5 | 0.04388%
IS34Inv2M3SCB2 | 223.3 | 0.06143%
IS34Inv2M3SCB3 | 191.4 | 0.05265%
IS34Inv2M3SCB4 | 223.3 | 0.06143%
IS34Inv2M3SCB5 | 223.3 | 0.06143%
IS34Inv2M3SCB6 | 191.4 | 0.05265%
IS34Inv2M4SCB1 | 223.3 | 0.06143%
IS34Inv2M4SCB2 | 223.3 | 0.06143%
IS34Inv2M4SCB3 | 191.4 | 0.05265%
IS34Inv2M4SCB4 | 191.4 | 0.05265%
IS34Inv2M4SCB5 | 223.3 | 0.06143%
IS34Inv2M4SCB6 | 223.3 | 0.06143%
IS35Inv1M1SCB1 | 95.7 | 0.02633%
IS35Inv1M1SCB2 | 127.6 | 0.0351%
IS35Inv1M1SCB3 | 127.6 | 0.0351%
IS35Inv1M1SCB4 | 223.3 | 0.06143%
IS35Inv1M1SCB5 | 223.3 | 0.06143%
IS35Inv1M1SCB6 | 95.7 | 0.02633%
IS35Inv1M2SCB1 | 191.4 | 0.05265%
IS35Inv1M2SCB2 | 223.3 | 0.06143%
IS35Inv1M2SCB3 | 191.4 | 0.05265%
IS35Inv1M2SCB4 | 223.3 | 0.06143%
IS35Inv1M2SCB5 | 223.3 | 0.06143%
IS35Inv1M2SCB6 | 127.6 | 0.0351%
IS35Inv1M3SCB1 | 0 | 0%
IS35Inv1M3SCB2 | 223.3 | 0.06143%
IS35Inv1M3SCB3 | 223.3 | 0.06143%
IS35Inv1M3SCB4 | 191.4 | 0.05265%
IS35Inv1M3SCB5 | 223.3 | 0.06143%
IS35Inv1M3SCB6 | 159.5 | 0.04388%
IS35Inv1M4SCB1 | 159.5 | 0.04388%
IS35Inv1M4SCB2 | 159.5 | 0.04388%
IS35Inv1M4SCB3 | 159.5 | 0.04388%
IS35Inv1M4SCB4 | 127.6 | 0.0351%
IS35Inv1M4SCB5 | 223.3 | 0.06143%
IS35Inv1M4SCB6 | 63.8 | 0.01755%
IS35Inv2M1SCB1 | 0 | 0%
IS35Inv2M1SCB2 | 0 | 0%
IS35Inv2M1SCB3 | 0 | 0%
IS35Inv2M1SCB4 | 0 | 0%
IS35Inv2M1SCB5 | 0 | 0%
IS35Inv2M1SCB6 | 127.6 | 0.0351%
IS35Inv2M2SCB1 | 0 | 0%
IS35Inv2M2SCB2 | 0 | 0%
IS35Inv2M2SCB3 | 0 | 0%
IS35Inv2M2SCB4 | 0 | 0%
IS35Inv2M2SCB5 | 0 | 0%
IS35Inv2M2SCB6 | 0 | 0%
IS35Inv2M3SCB1 | 191.4 | 0.05265%
IS35Inv2M3SCB2 | 223.3 | 0.06143%
IS35Inv2M3SCB3 | 223.3 | 0.06143%
IS35Inv2M3SCB4 | 0 | 0%
IS35Inv2M3SCB5 | 0 | 0%
IS35Inv2M3SCB6 | 159.5 | 0.04388%
IS35Inv2M4SCB1 | 223.3 | 0.06143%
IS35Inv2M4SCB2 | 223.3 | 0.06143%
IS35Inv2M4SCB3 | 159.5 | 0.04388%
IS35Inv2M4SCB4 | 223.3 | 0.06143%
IS35Inv2M4SCB5 | 191.4 | 0.05265%
IS35Inv2M4SCB6 | 159.5 | 0.04388%
IS36Inv1M1SCB1 | 95.7 | 0.02633%
IS36Inv1M1SCB2 | 159.5 | 0.04388%
IS36Inv1M1SCB3 | 223.3 | 0.06143%
IS36Inv1M1SCB4 | 223.3 | 0.06143%
IS36Inv1M1SCB5 | 127.6 | 0.0351%
IS36Inv1M1SCB6 | 0 | 0%
IS36Inv1M2SCB1 | 159.5 | 0.04388%
IS36Inv1M2SCB2 | 191.4 | 0.05265%
IS36Inv1M2SCB3 | 95.7 | 0.02633%
IS36Inv1M2SCB4 | 223.3 | 0.06143%
IS36Inv1M2SCB5 | 159.5 | 0.04388%
IS36Inv1M2SCB6 | 191.4 | 0.05265%
IS36Inv1M3SCB1 | 191.4 | 0.05265%
IS36Inv1M3SCB2 | 223.3 | 0.06143%
IS36Inv1M3SCB3 | 159.5 | 0.04388%
IS36Inv1M3SCB4 | 191.4 | 0.05265%
IS36Inv1M3SCB5 | 95.7 | 0.02633%
IS36Inv1M3SCB6 | 95.7 | 0.02633%
IS36Inv1M4SCB1 | 95.7 | 0.02633%
IS36Inv1M4SCB2 | 223.3 | 0.06143%
IS36Inv1M4SCB3 | 223.3 | 0.06143%
IS36Inv1M4SCB4 | 223.3 | 0.06143%
IS36Inv1M4SCB5 | 127.6 | 0.0351%
IS36Inv1M4SCB6 | 0 | 0%
IS36Inv2M1SCB1 | 159.5 | 0.04388%
IS36Inv2M1SCB2 | 191.4 | 0.05265%
IS36Inv2M1SCB3 | 223.3 | 0.06143%
IS36Inv2M1SCB4 | 223.3 | 0.06143%
IS36Inv2M1SCB5 | 223.3 | 0.06143%
IS36Inv2M1SCB6 | 223.3 | 0.06143%
IS36Inv2M2SCB1 | 223.3 | 0.06143%
IS36Inv2M2SCB2 | 191.4 | 0.05265%
IS36Inv2M2SCB3 | 223.3 | 0.06143%
IS36Inv2M2SCB4 | 223.3 | 0.06143%
IS36Inv2M2SCB5 | 127.6 | 0.0351%
IS36Inv2M2SCB6 | 63.8 | 0.01755%
IS36Inv2M3SCB1 | 191.4 | 0.05265%
IS36Inv2M3SCB2 | 191.4 | 0.05265%
IS36Inv2M3SCB3 | 223.3 | 0.06143%
IS36Inv2M3SCB4 | 223.3 | 0.06143%
IS36Inv2M3SCB5 | 127.6 | 0.0351%
IS36Inv2M3SCB6 | 191.4 | 0.05265%
IS36Inv2M4SCB1 | 95.7 | 0.02633%
IS36Inv2M4SCB2 | 159.5 | 0.04388%
IS36Inv2M4SCB3 | 159.5 | 0.04388%
IS36Inv2M4SCB4 | 127.6 | 0.0351%
IS36Inv2M4SCB5 | 223.3 | 0.06143%
IS36Inv2M4SCB6 | 191.4 | 0.05265%
IS37Inv1M1SCB1 | 223.3 | 0.06143%
IS37Inv1M1SCB2 | 223.3 | 0.06143%
IS37Inv1M1SCB3 | 223.3 | 0.06143%
IS37Inv1M1SCB4 | 159.5 | 0.04388%
IS37Inv1M1SCB5 | 207.35 | 0.05704%
IS37Inv1M1SCB6 | 191.4 | 0.05265%
IS37Inv1M2SCB1 | 223.3 | 0.06143%
IS37Inv1M2SCB2 | 159.5 | 0.04388%
IS37Inv1M2SCB3 | 127.6 | 0.0351%
IS37Inv1M2SCB4 | 175.45 | 0.04827%
IS37Inv1M2SCB5 | 223.3 | 0.06143%
IS37Inv1M2SCB6 | 223.3 | 0.06143%
IS37Inv1M3SCB1 | 223.3 | 0.06143%
IS37Inv1M3SCB2 | 159.5 | 0.04388%
IS37Inv1M3SCB3 | 159.5 | 0.04388%
IS37Inv1M3SCB4 | 95.7 | 0.02633%
IS37Inv1M3SCB5 | 31.9 | 0.008776%
IS37Inv1M3SCB6 | 0 | 0%
IS37Inv1M4SCB1 | 223.3 | 0.06143%
IS37Inv1M4SCB2 | 223.3 | 0.06143%
IS37Inv1M4SCB3 | 95.7 | 0.02633%
IS37Inv1M4SCB4 | 143.55 | 0.03949%
IS37Inv1M4SCB5 | 0 | 0%
IS37Inv1M4SCB6 | 47.85 | 0.01316%
IS37Inv2M1SCB1 | 191.4 | 0.05265%
IS37Inv2M1SCB2 | 223.3 | 0.06143%
IS37Inv2M1SCB3 | 191.4 | 0.05265%
IS37Inv2M1SCB4 | 191.4 | 0.05265%
IS37Inv2M1SCB5 | 95.7 | 0.02633%
IS37Inv2M1SCB6 | 191.4 | 0.05265%
IS37Inv2M2SCB1 | 223.3 | 0.06143%
IS37Inv2M2SCB2 | 191.4 | 0.05265%
IS37Inv2M2SCB3 | 143.55 | 0.03949%
IS37Inv2M2SCB4 | 223.3 | 0.06143%
IS37Inv2M2SCB5 | 223.3 | 0.06143%
IS37Inv2M2SCB6 | 223.3 | 0.06143%
IS37Inv2M3SCB1 | 207.35 | 0.05704%
IS37Inv2M3SCB2 | 223.3 | 0.06143%
IS37Inv2M3SCB3 | 223.3 | 0.06143%
IS37Inv2M3SCB4 | 191.4 | 0.05265%
IS37Inv2M3SCB5 | 223.3 | 0.06143%
IS37Inv2M3SCB6 | 223.3 | 0.06143%
IS37Inv2M4SCB1 | 223.3 | 0.06143%
IS37Inv2M4SCB2 | 191.4 | 0.05265%
IS37Inv2M4SCB3 | 191.4 | 0.05265%
IS37Inv2M4SCB4 | 175.45 | 0.04827%
IS37Inv2M4SCB5 | 191.4 | 0.05265%
IS37Inv2M4SCB6 | 159.5 | 0.04388%
IS38Inv1M1SCB1 | 0 | 0%
IS38Inv1M1SCB2 | 0 | 0%
IS38Inv1M1SCB3 | 0 | 0%
IS38Inv1M1SCB4 | 0 | 0%
IS38Inv1M1SCB5 | 0 | 0%
IS38Inv1M1SCB6 | 0 | 0%
IS38Inv1M2SCB1 | 0 | 0%
IS38Inv1M2SCB2 | 0 | 0%
IS38Inv1M2SCB3 | 0 | 0%
IS38Inv1M2SCB4 | 0 | 0%
IS38Inv1M2SCB5 | 0 | 0%
IS38Inv1M2SCB6 | 0 | 0%
IS38Inv1M3SCB1 | 0 | 0%
IS38Inv1M3SCB2 | 0 | 0%
IS38Inv1M3SCB3 | 0 | 0%
IS38Inv1M3SCB4 | 0 | 0%
IS38Inv1M3SCB5 | 0 | 0%
IS38Inv1M3SCB6 | 0 | 0%
IS38Inv1M4SCB1 | 0 | 0%
IS38Inv1M4SCB2 | 0 | 0%
IS38Inv1M4SCB3 | 0 | 0%
IS38Inv1M4SCB4 | 0 | 0%
IS38Inv1M4SCB5 | 0 | 0%
IS38Inv1M4SCB6 | 0 | 0%
IS38Inv2M1SCB1 | 0 | 0%
IS38Inv2M1SCB2 | 0 | 0%
IS38Inv2M1SCB3 | 0 | 0%
IS38Inv2M1SCB4 | 0 | 0%
IS38Inv2M1SCB5 | 0 | 0%
IS38Inv2M1SCB6 | 0 | 0%
IS38Inv2M2SCB1 | 0 | 0%
IS38Inv2M2SCB2 | 0 | 0%
IS38Inv2M2SCB3 | 0 | 0%
IS38Inv2M2SCB4 | 0 | 0%
IS38Inv2M2SCB5 | 0 | 0%
IS38Inv2M2SCB6 | 0 | 0%
IS38Inv2M3SCB1 | 0 | 0%
IS38Inv2M3SCB2 | 0 | 0%
IS38Inv2M3SCB3 | 0 | 0%
IS38Inv2M3SCB4 | 0 | 0%
IS38Inv2M3SCB5 | 0 | 0%
IS38Inv2M3SCB6 | 0 | 0%
IS38Inv2M4SCB1 | 0 | 0%
IS38Inv2M4SCB2 | 0 | 0%
IS38Inv2M4SCB3 | 0 | 0%
IS38Inv2M4SCB4 | 0 | 0%
IS38Inv2M4SCB5 | 0 | 0%
IS38Inv2M4SCB6 | 0 | 0%
IS39Inv1M1SCB1 | 0 | 0%
IS39Inv1M1SCB2 | 0 | 0%
IS39Inv1M1SCB3 | 0 | 0%
IS39Inv1M1SCB4 | 0 | 0%
IS39Inv1M1SCB5 | 0 | 0%
IS39Inv1M1SCB6 | 0 | 0%
IS39Inv1M2SCB1 | 0 | 0%
IS39Inv1M2SCB2 | 0 | 0%
IS39Inv1M2SCB3 | 0 | 0%
IS39Inv1M2SCB4 | 0 | 0%
IS39Inv1M2SCB5 | 0 | 0%
IS39Inv1M2SCB6 | 0 | 0%
IS39Inv1M3SCB1 | 0 | 0%
IS39Inv1M3SCB2 | 0 | 0%
IS39Inv1M3SCB3 | 0 | 0%
IS39Inv1M3SCB4 | 0 | 0%
IS39Inv1M3SCB5 | 0 | 0%
IS39Inv1M3SCB6 | 0 | 0%
IS39Inv1M4SCB1 | 63.8 | 0.01755%
IS39Inv1M4SCB2 | 63.8 | 0.01755%
IS39Inv1M4SCB3 | 63.8 | 0.01755%
IS39Inv1M4SCB4 | 0 | 0%
IS39Inv1M4SCB5 | 0 | 0%
IS39Inv1M4SCB6 | 0 | 0%
IS39Inv2M1SCB1 | 0 | 0%
IS39Inv2M1SCB2 | 0 | 0%
IS39Inv2M1SCB3 | 0 | 0%
IS39Inv2M1SCB4 | 0 | 0%
IS39Inv2M1SCB5 | 0 | 0%
IS39Inv2M1SCB6 | 0 | 0%
IS39Inv2M2SCB1 | 0 | 0%
IS39Inv2M2SCB2 | 0 | 0%
IS39Inv2M2SCB3 | 0 | 0%
IS39Inv2M2SCB4 | 0 | 0%
IS39Inv2M2SCB5 | 0 | 0%
IS39Inv2M2SCB6 | 0 | 0%
IS39Inv2M3SCB1 | 63.8 | 0.01755%
IS39Inv2M3SCB2 | 95.7 | 0.02633%
IS39Inv2M3SCB3 | 63.8 | 0.01755%
IS39Inv2M3SCB4 | 0 | 0%
IS39Inv2M3SCB5 | 0 | 0%
IS39Inv2M3SCB6 | 0 | 0%
IS39Inv2M4SCB1 | 0 | 0%
IS39Inv2M4SCB2 | 0 | 0%
IS39Inv2M4SCB3 | 0 | 0%
IS39Inv2M4SCB4 | 0 | 0%
IS39Inv2M4SCB5 | 0 | 0%
IS39Inv2M4SCB6 | 0 | 0%
IS40Inv1M1SCB1 | 223.3 | 0.06143%
IS40Inv1M1SCB2 | 223.3 | 0.06143%
IS40Inv1M1SCB3 | 207.35 | 0.05704%
IS40Inv1M1SCB4 | 223.3 | 0.06143%
IS40Inv1M1SCB5 | 223.3 | 0.06143%
IS40Inv1M1SCB6 | 191.4 | 0.05265%
IS40Inv1M2SCB1 | 191.4 | 0.05265%
IS40Inv1M2SCB2 | 223.3 | 0.06143%
IS40Inv1M2SCB3 | 191.4 | 0.05265%
IS40Inv1M2SCB4 | 223.3 | 0.06143%
IS40Inv1M2SCB5 | 223.3 | 0.06143%
IS40Inv1M2SCB6 | 143.55 | 0.03949%
IS40Inv1M3SCB1 | 223.3 | 0.06143%
IS40Inv1M3SCB2 | 223.3 | 0.06143%
IS40Inv1M3SCB3 | 223.3 | 0.06143%
IS40Inv1M3SCB4 | 191.4 | 0.05265%
IS40Inv1M3SCB5 | 207.35 | 0.05704%
IS40Inv1M3SCB6 | 159.5 | 0.04388%
IS40Inv1M4SCB1 | 0 | 0%
IS40Inv1M4SCB2 | 0 | 0%
IS40Inv1M4SCB3 | 0 | 0%
IS40Inv1M4SCB4 | 0 | 0%
IS40Inv1M4SCB5 | 191.4 | 0.05265%
IS40Inv1M4SCB6 | 95.7 | 0.02633%
IS40Inv2M1SCB1 | 0 | 0%
IS40Inv2M1SCB2 | 0 | 0%
IS40Inv2M1SCB3 | 0 | 0%
IS40Inv2M1SCB4 | 0 | 0%
IS40Inv2M1SCB5 | 0 | 0%
IS40Inv2M1SCB6 | 0 | 0%
IS40Inv2M2SCB1 | 0 | 0%
IS40Inv2M2SCB2 | 0 | 0%
IS40Inv2M2SCB3 | 0 | 0%
IS40Inv2M2SCB4 | 0 | 0%
IS40Inv2M2SCB5 | 0 | 0%
IS40Inv2M2SCB6 | 0 | 0%
IS40Inv2M3SCB1 | 0 | 0%
IS40Inv2M3SCB2 | 0 | 0%
IS40Inv2M3SCB3 | 0 | 0%
IS40Inv2M3SCB4 | 0 | 0%
IS40Inv2M3SCB5 | 0 | 0%
IS40Inv2M3SCB6 | 0 | 0%
IS40Inv2M4SCB1 | 0 | 0%
IS40Inv2M4SCB2 | 0 | 0%
IS40Inv2M4SCB3 | 0 | 0%
IS40Inv2M4SCB4 | 0 | 0%
IS40Inv2M4SCB5 | 191.4 | 0.05265%
IS40Inv2M4SCB6 | 95.7 | 0.02633%
IS41Inv1M1SCB1 | 207.35 | 0.05704%
IS41Inv1M1SCB2 | 159.5 | 0.04388%
IS41Inv1M1SCB3 | 159.5 | 0.04388%
IS41Inv1M1SCB4 | 191.4 | 0.05265%
IS41Inv1M1SCB5 | 223.3 | 0.06143%
IS41Inv1M1SCB6 | 95.7 | 0.02633%
IS41Inv1M2SCB1 | 159.5 | 0.04388%
IS41Inv1M2SCB2 | 223.3 | 0.06143%
IS41Inv1M2SCB3 | 0 | 0%
IS41Inv1M2SCB4 | 207.35 | 0.05704%
IS41Inv1M2SCB5 | 223.3 | 0.06143%
IS41Inv1M2SCB6 | 95.7 | 0.02633%
IS41Inv1M3SCB1 | 31.9 | 0.008776%
IS41Inv1M3SCB2 | 159.5 | 0.04388%
IS41Inv1M3SCB3 | 191.4 | 0.05265%
IS41Inv1M3SCB4 | 223.3 | 0.06143%
IS41Inv1M3SCB5 | 223.3 | 0.06143%
IS41Inv1M3SCB6 | 223.3 | 0.06143%
IS41Inv1M4SCB1 | 207.35 | 0.05704%
IS41Inv1M4SCB2 | 191.4 | 0.05265%
IS41Inv1M4SCB3 | 207.35 | 0.05704%
IS41Inv1M4SCB4 | 191.4 | 0.05265%
IS41Inv1M4SCB5 | 159.5 | 0.04388%
IS41Inv1M4SCB6 | 127.6 | 0.0351%
IS41Inv2M1SCB1 | 223.3 | 0.06143%
IS41Inv2M1SCB2 | 223.3 | 0.06143%
IS41Inv2M1SCB3 | 159.5 | 0.04388%
IS41Inv2M1SCB4 | 191.4 | 0.05265%
IS41Inv2M1SCB5 | 191.4 | 0.05265%
IS41Inv2M1SCB6 | 159.5 | 0.04388%
IS41Inv2M2SCB1 | 223.3 | 0.06143%
IS41Inv2M2SCB2 | 223.3 | 0.06143%
IS41Inv2M2SCB3 | 223.3 | 0.06143%
IS41Inv2M2SCB4 | 223.3 | 0.06143%
IS41Inv2M2SCB5 | 223.3 | 0.06143%
IS41Inv2M2SCB6 | 127.6 | 0.0351%
IS41Inv2M3SCB1 | 223.3 | 0.06143%
IS41Inv2M3SCB2 | 223.3 | 0.06143%
IS41Inv2M3SCB3 | 223.3 | 0.06143%
IS41Inv2M3SCB4 | 223.3 | 0.06143%
IS41Inv2M3SCB5 | 159.5 | 0.04388%
IS41Inv2M3SCB6 | 127.6 | 0.0351%
IS41Inv2M4SCB1 | 191.4 | 0.05265%
IS41Inv2M4SCB2 | 111.65 | 0.03071%
IS41Inv2M4SCB3 | 159.5 | 0.04388%
IS41Inv2M4SCB4 | 159.5 | 0.04388%
IS41Inv2M4SCB5 | 223.3 | 0.06143%
IS41Inv2M4SCB6 | 223.3 | 0.06143%
IS42Inv1M1SCB1 | 223.3 | 0.06143%
IS42Inv1M1SCB2 | 159.5 | 0.04388%
IS42Inv1M1SCB3 | 0 | 0%
IS42Inv1M1SCB4 | 0 | 0%
IS42Inv1M1SCB5 | 0 | 0%
IS42Inv1M1SCB6 | 0 | 0%
IS42Inv1M2SCB1 | 0 | 0%
IS42Inv1M2SCB2 | 159.5 | 0.04388%
IS42Inv1M2SCB3 | 127.6 | 0.0351%
IS42Inv1M2SCB4 | 0 | 0%
IS42Inv1M2SCB5 | 223.3 | 0.06143%
IS42Inv1M2SCB6 | 191.4 | 0.05265%
IS42Inv1M3SCB1 | 207.35 | 0.05704%
IS42Inv1M3SCB2 | 191.4 | 0.05265%
IS42Inv1M3SCB3 | 223.3 | 0.06143%
IS42Inv1M3SCB4 | 223.3 | 0.06143%
IS42Inv1M3SCB5 | 223.3 | 0.06143%
IS42Inv1M3SCB6 | 31.9 | 0.008776%
IS42Inv1M4SCB1 | 223.3 | 0.06143%
IS42Inv1M4SCB2 | 207.35 | 0.05704%
IS42Inv1M4SCB3 | 0 | 0%
IS42Inv1M4SCB4 | 0 | 0%
IS42Inv1M4SCB5 | 0 | 0%
IS42Inv1M4SCB6 | 0 | 0%
IS42Inv2M1SCB1 | 223.3 | 0.06143%
IS42Inv2M1SCB2 | 223.3 | 0.06143%
IS42Inv2M1SCB3 | 223.3 | 0.06143%
IS42Inv2M1SCB4 | 191.4 | 0.05265%
IS42Inv2M1SCB5 | 223.3 | 0.06143%
IS42Inv2M1SCB6 | 223.3 | 0.06143%
IS42Inv2M2SCB1 | 127.6 | 0.0351%
IS42Inv2M2SCB2 | 207.35 | 0.05704%
IS42Inv2M2SCB3 | 223.3 | 0.06143%
IS42Inv2M2SCB4 | 191.4 | 0.05265%
IS42Inv2M2SCB5 | 223.3 | 0.06143%
IS42Inv2M2SCB6 | 223.3 | 0.06143%
IS42Inv2M3SCB1 | 223.3 | 0.06143%
IS42Inv2M3SCB2 | 223.3 | 0.06143%
IS42Inv2M3SCB3 | 111.65 | 0.03071%
IS42Inv2M3SCB4 | 95.7 | 0.02633%
IS42Inv2M3SCB5 | 223.3 | 0.06143%
IS42Inv2M3SCB6 | 223.3 | 0.06143%
IS42Inv2M4SCB1 | 159.5 | 0.04388%
IS42Inv2M4SCB2 | 159.5 | 0.04388%
IS42Inv2M4SCB3 | 191.4 | 0.05265%
IS42Inv2M4SCB4 | 191.4 | 0.05265%
IS42Inv2M4SCB5 | 191.4 | 0.05265%
IS42Inv2M4SCB6 | 223.3 | 0.06143%
IS43Inv1M1SCB1 | 175.45 | 0.04827%
IS43Inv1M1SCB2 | 175.45 | 0.04827%
IS43Inv1M1SCB3 | 223.3 | 0.06143%
IS43Inv1M1SCB4 | 127.6 | 0.0351%
IS43Inv1M1SCB5 | 207.35 | 0.05704%
IS43Inv1M1SCB6 | 159.5 | 0.04388%
IS43Inv1M2SCB1 | 159.5 | 0.04388%
IS43Inv1M2SCB2 | 159.5 | 0.04388%
IS43Inv1M2SCB3 | 175.45 | 0.04827%
IS43Inv1M2SCB4 | 79.75 | 0.02194%
IS43Inv1M2SCB5 | 127.6 | 0.0351%
IS43Inv1M2SCB6 | 143.55 | 0.03949%
IS43Inv1M3SCB1 | 191.4 | 0.05265%
IS43Inv1M3SCB2 | 223.3 | 0.06143%
IS43Inv1M3SCB3 | 223.3 | 0.06143%
IS43Inv1M3SCB4 | 223.3 | 0.06143%
IS43Inv1M3SCB5 | 191.4 | 0.05265%
IS43Inv1M3SCB6 | 223.3 | 0.06143%
IS43Inv1M4SCB1 | 223.3 | 0.06143%
IS43Inv1M4SCB2 | 223.3 | 0.06143%
IS43Inv1M4SCB3 | 175.45 | 0.04827%
IS43Inv1M4SCB4 | 223.3 | 0.06143%
IS43Inv1M4SCB5 | 223.3 | 0.06143%
IS43Inv1M4SCB6 | 223.3 | 0.06143%
IS43Inv2M1SCB1 | 191.4 | 0.05265%
IS43Inv2M1SCB2 | 223.3 | 0.06143%
IS43Inv2M1SCB3 | 223.3 | 0.06143%
IS43Inv2M1SCB4 | 223.3 | 0.06143%
IS43Inv2M1SCB5 | 223.3 | 0.06143%
IS43Inv2M1SCB6 | 223.3 | 0.06143%
IS43Inv2M2SCB1 | 191.4 | 0.05265%
IS43Inv2M2SCB2 | 223.3 | 0.06143%
IS43Inv2M2SCB3 | 191.4 | 0.05265%
IS43Inv2M2SCB4 | 223.3 | 0.06143%
IS43Inv2M2SCB5 | 223.3 | 0.06143%
IS43Inv2M2SCB6 | 223.3 | 0.06143%
IS43Inv2M3SCB1 | 223.3 | 0.06143%
IS43Inv2M3SCB2 | 223.3 | 0.06143%
IS43Inv2M3SCB3 | 223.3 | 0.06143%
IS43Inv2M3SCB4 | 223.3 | 0.06143%
IS43Inv2M3SCB5 | 223.3 | 0.06143%
IS43Inv2M3SCB6 | 127.6 | 0.0351%
IS43Inv2M4SCB1 | 63.8 | 0.01755%
IS43Inv2M4SCB2 | 191.4 | 0.05265%
IS43Inv2M4SCB3 | 143.55 | 0.03949%
IS43Inv2M4SCB4 | 143.55 | 0.03949%
IS43Inv2M4SCB5 | 191.4 | 0.05265%
IS43Inv2M4SCB6 | 223.3 | 0.06143%
IS44Inv1M1SCB1 | 47.85 | 0.01316%
IS44Inv1M1SCB2 | 175.45 | 0.04827%
IS44Inv1M1SCB3 | 191.4 | 0.05265%
IS44Inv1M1SCB4 | 223.3 | 0.06143%
IS44Inv1M1SCB5 | 127.6 | 0.0351%
IS44Inv1M1SCB6 | 223.3 | 0.06143%
IS44Inv1M2SCB1 | 223.3 | 0.06143%
IS44Inv1M2SCB2 | 191.4 | 0.05265%
IS44Inv1M2SCB3 | 223.3 | 0.06143%
IS44Inv1M2SCB4 | 0 | 0%
IS44Inv1M2SCB5 | 0 | 0%
IS44Inv1M2SCB6 | 0 | 0%
IS44Inv1M3SCB1 | 0 | 0%
IS44Inv1M3SCB2 | 0 | 0%
IS44Inv1M3SCB3 | 0 | 0%
IS44Inv1M3SCB4 | 0 | 0%
IS44Inv1M3SCB5 | 0 | 0%
IS44Inv1M3SCB6 | 0 | 0%
IS44Inv1M4SCB1 | 191.4 | 0.05265%
IS44Inv1M4SCB2 | 191.4 | 0.05265%
IS44Inv1M4SCB3 | 191.4 | 0.05265%
IS44Inv1M4SCB4 | 223.3 | 0.06143%
IS44Inv1M4SCB5 | 143.55 | 0.03949%
IS44Inv1M4SCB6 | 140.36 | 0.03861%
IS44Inv2M1SCB1 | 111.65 | 0.03071%
IS44Inv2M1SCB2 | 159.5 | 0.04388%
IS44Inv2M1SCB3 | 127.6 | 0.0351%
IS44Inv2M1SCB4 | 175.45 | 0.04827%
IS44Inv2M1SCB5 | 63.8 | 0.01755%
IS44Inv2M1SCB6 | 159.5 | 0.04388%
IS44Inv2M2SCB1 | 143.55 | 0.03949%
IS44Inv2M2SCB2 | 159.5 | 0.04388%
IS44Inv2M2SCB3 | 0 | 0%
IS44Inv2M2SCB4 | 127.6 | 0.0351%
IS44Inv2M2SCB5 | 127.6 | 0.0351%
IS44Inv2M2SCB6 | 223.3 | 0.06143%
IS44Inv2M3SCB1 | 223.3 | 0.06143%
IS44Inv2M3SCB2 | 223.3 | 0.06143%
IS44Inv2M3SCB3 | 159.5 | 0.04388%
IS44Inv2M3SCB4 | 223.3 | 0.06143%
IS44Inv2M3SCB5 | 175.45 | 0.04827%
IS44Inv2M3SCB6 | 159.5 | 0.04388%
IS44Inv2M4SCB1 | 223.3 | 0.06143%
IS44Inv2M4SCB2 | 0 | 0%
IS44Inv2M4SCB3 | 159.5 | 0.04388%
IS44Inv2M4SCB4 | 191.4 | 0.05265%
IS44Inv2M4SCB5 | 143.55 | 0.03949%
IS44Inv2M4SCB6 | 207.35 | 0.05704%
IS45Inv1M1SCB1 | 223.3 | 0.06143%
IS45Inv1M1SCB2 | 223.3 | 0.06143%
IS45Inv1M1SCB3 | 223.3 | 0.06143%
IS45Inv1M1SCB4 | 63.8 | 0.01755%
IS45Inv1M1SCB5 | 0 | 0%
IS45Inv1M1SCB6 | 63.8 | 0.01755%
IS45Inv1M2SCB1 | 191.4 | 0.05265%
IS45Inv1M2SCB2 | 0 | 0%
IS45Inv1M2SCB3 | 31.9 | 0.008776%
IS45Inv1M2SCB4 | 0 | 0%
IS45Inv1M2SCB5 | 95.7 | 0.02633%
IS45Inv1M2SCB6 | 191.4 | 0.05265%
IS45Inv1M3SCB1 | 191.4 | 0.05265%
IS45Inv1M3SCB2 | 127.6 | 0.0351%
IS45Inv1M3SCB3 | 223.3 | 0.06143%
IS45Inv1M3SCB4 | 159.5 | 0.04388%
IS45Inv1M3SCB5 | 191.4 | 0.05265%
IS45Inv1M3SCB6 | 159.5 | 0.04388%
IS45Inv1M4SCB1 | 63.8 | 0.01755%
IS45Inv1M4SCB2 | 159.5 | 0.04388%
IS45Inv1M4SCB3 | 159.5 | 0.04388%
IS45Inv1M4SCB4 | 223.3 | 0.06143%
IS45Inv1M4SCB5 | 191.4 | 0.05265%
IS45Inv1M4SCB6 | 223.3 | 0.06143%
IS45Inv2M1SCB1 | 63.8 | 0.01755%
IS45Inv2M1SCB2 | 127.6 | 0.0351%
IS45Inv2M1SCB3 | 159.5 | 0.04388%
IS45Inv2M1SCB4 | 191.4 | 0.05265%
IS45Inv2M1SCB5 | 191.4 | 0.05265%
IS45Inv2M1SCB6 | 127.6 | 0.0351%
IS45Inv2M2SCB1 | 191.4 | 0.05265%
IS45Inv2M2SCB2 | 191.4 | 0.05265%
IS45Inv2M2SCB3 | 159.5 | 0.04388%
IS45Inv2M2SCB4 | 127.6 | 0.0351%
IS45Inv2M2SCB5 | 95.7 | 0.02633%
IS45Inv2M2SCB6 | 31.9 | 0.008776%
IS45Inv2M3SCB1 | 223.3 | 0.06143%
IS45Inv2M3SCB2 | 191.4 | 0.05265%
IS45Inv2M3SCB3 | 31.9 | 0.008776%
IS45Inv2M3SCB4 | 127.6 | 0.0351%
IS45Inv2M3SCB5 | 223.3 | 0.06143%
IS45Inv2M3SCB6 | 95.7 | 0.02633%
IS45Inv2M4SCB1 | 31.9 | 0.008776%
IS45Inv2M4SCB2 | 31.9 | 0.008776%
IS45Inv2M4SCB3 | 223.3 | 0.06143%
IS45Inv2M4SCB4 | 223.3 | 0.06143%
IS45Inv2M4SCB5 | 191.4 | 0.05265%
IS45Inv2M4SCB6 | 0 | 0%
IS46Inv1M1SCB1 | 127.6 | 0.0351%
IS46Inv1M1SCB2 | 191.4 | 0.05265%
IS46Inv1M1SCB3 | 191.4 | 0.05265%
IS46Inv1M1SCB4 | 223.3 | 0.06143%
IS46Inv1M1SCB5 | 159.5 | 0.04388%
IS46Inv1M1SCB6 | 111.65 | 0.03071%
IS46Inv1M2SCB1 | 127.6 | 0.0351%
IS46Inv1M2SCB2 | 127.6 | 0.0351%
IS46Inv1M2SCB3 | 223.3 | 0.06143%
IS46Inv1M2SCB4 | 159.5 | 0.04388%
IS46Inv1M2SCB5 | 191.4 | 0.05265%
IS46Inv1M2SCB6 | 159.5 | 0.04388%
IS46Inv1M3SCB1 | 159.5 | 0.04388%
IS46Inv1M3SCB2 | 223.3 | 0.06143%
IS46Inv1M3SCB3 | 223.3 | 0.06143%
IS46Inv1M3SCB4 | 191.4 | 0.05265%
IS46Inv1M3SCB5 | 223.3 | 0.06143%
IS46Inv1M3SCB6 | 0 | 0%
IS46Inv1M4SCB1 | 223.3 | 0.06143%
IS46Inv1M4SCB2 | 159.5 | 0.04388%
IS46Inv1M4SCB3 | 191.4 | 0.05265%
IS46Inv1M4SCB4 | 159.5 | 0.04388%
IS46Inv1M4SCB5 | 223.3 | 0.06143%
IS46Inv1M4SCB6 | 159.5 | 0.04388%
IS46Inv2M1SCB1 | 159.5 | 0.04388%
IS46Inv2M1SCB2 | 223.3 | 0.06143%
IS46Inv2M1SCB3 | 223.3 | 0.06143%
IS46Inv2M1SCB4 | 223.3 | 0.06143%
IS46Inv2M1SCB5 | 191.4 | 0.05265%
IS46Inv2M1SCB6 | 127.6 | 0.0351%
IS46Inv2M2SCB1 | 191.4 | 0.05265%
IS46Inv2M2SCB2 | 223.3 | 0.06143%
IS46Inv2M2SCB3 | 143.55 | 0.03949%
IS46Inv2M2SCB4 | 0 | 0%
IS46Inv2M2SCB5 | 0 | 0%
IS46Inv2M2SCB6 | 191.4 | 0.05265%
IS46Inv2M3SCB1 | 223.3 | 0.06143%
IS46Inv2M3SCB2 | 223.3 | 0.06143%
IS46Inv2M3SCB3 | 223.3 | 0.06143%
IS46Inv2M3SCB4 | 223.3 | 0.06143%
IS46Inv2M3SCB5 | 159.5 | 0.04388%
IS46Inv2M3SCB6 | 159.5 | 0.04388%
IS46Inv2M4SCB1 | 191.4 | 0.05265%
IS46Inv2M4SCB2 | 223.3 | 0.06143%
IS46Inv2M4SCB3 | 175.45 | 0.04827%
IS46Inv2M4SCB4 | 223.3 | 0.06143%
IS46Inv2M4SCB5 | 95.7 | 0.02633%
IS46Inv2M4SCB6 | 223.3 | 0.06143%
IS47Inv1M1SCB1 | 223.3 | 0.06143%
IS47Inv1M1SCB2 | 159.5 | 0.04388%
IS47Inv1M1SCB3 | 223.3 | 0.06143%
IS47Inv1M1SCB4 | 31.9 | 0.008776%
IS47Inv1M1SCB5 | 143.55 | 0.03949%
IS47Inv1M1SCB6 | 191.4 | 0.05265%
IS47Inv1M2SCB1 | 191.4 | 0.05265%
IS47Inv1M2SCB2 | 223.3 | 0.06143%
IS47Inv1M2SCB3 | 223.3 | 0.06143%
IS47Inv1M2SCB4 | 191.4 | 0.05265%
IS47Inv1M2SCB5 | 127.6 | 0.0351%
IS47Inv1M2SCB6 | 111.65 | 0.03071%
IS47Inv1M3SCB1 | 223.3 | 0.06143%
IS47Inv1M3SCB2 | 223.3 | 0.06143%
IS47Inv1M3SCB3 | 159.5 | 0.04388%
IS47Inv1M3SCB4 | 111.65 | 0.03071%
IS47Inv1M3SCB5 | 207.35 | 0.05704%
IS47Inv1M3SCB6 | 223.3 | 0.06143%
IS47Inv1M4SCB1 | 207.35 | 0.05704%
IS47Inv1M4SCB2 | 223.3 | 0.06143%
IS47Inv1M4SCB3 | 223.3 | 0.06143%
IS47Inv1M4SCB4 | 191.4 | 0.05265%
IS47Inv1M4SCB5 | 159.5 | 0.04388%
IS47Inv1M4SCB6 | 191.4 | 0.05265%
IS47Inv2M1SCB1 | 223.3 | 0.06143%
IS47Inv2M1SCB2 | 207.35 | 0.05704%
IS47Inv2M1SCB3 | 111.65 | 0.03071%
IS47Inv2M1SCB4 | 191.4 | 0.05265%
IS47Inv2M1SCB5 | 191.4 | 0.05265%
IS47Inv2M1SCB6 | 159.5 | 0.04388%
IS47Inv2M2SCB1 | 191.4 | 0.05265%
IS47Inv2M2SCB2 | 223.3 | 0.06143%
IS47Inv2M2SCB3 | 223.3 | 0.06143%
IS47Inv2M2SCB4 | 191.4 | 0.05265%
IS47Inv2M2SCB5 | 191.4 | 0.05265%
IS47Inv2M2SCB6 | 127.6 | 0.0351%
IS47Inv2M3SCB1 | 223.3 | 0.06143%
IS47Inv2M3SCB2 | 159.5 | 0.04388%
IS47Inv2M3SCB3 | 191.4 | 0.05265%
IS47Inv2M3SCB4 | 191.4 | 0.05265%
IS47Inv2M3SCB5 | 191.4 | 0.05265%
IS47Inv2M3SCB6 | 223.3 | 0.06143%
IS47Inv2M4SCB1 | 223.3 | 0.06143%
IS47Inv2M4SCB2 | 127.6 | 0.0351%
IS47Inv2M4SCB3 | 191.4 | 0.05265%
IS47Inv2M4SCB4 | 159.5 | 0.04388%
IS47Inv2M4SCB5 | 191.4 | 0.05265%
IS47Inv2M4SCB6 | 95.7 | 0.02633%
IS48Inv1M1SCB1 | 31.9 | 0.008776%
IS48Inv1M1SCB2 | 127.6 | 0.0351%
IS48Inv1M1SCB3 | 95.7 | 0.02633%
IS48Inv1M1SCB4 | 63.8 | 0.01755%
IS48Inv1M1SCB5 | 0 | 0%
IS48Inv1M1SCB6 | 0 | 0%
IS48Inv1M2SCB1 | 159.5 | 0.04388%
IS48Inv1M2SCB2 | 127.6 | 0.0351%
IS48Inv1M2SCB3 | 223.3 | 0.06143%
IS48Inv1M2SCB4 | 127.6 | 0.0351%
IS48Inv1M2SCB5 | 95.7 | 0.02633%
IS48Inv1M2SCB6 | 191.4 | 0.05265%
IS48Inv1M3SCB1 | 223.3 | 0.06143%
IS48Inv1M3SCB2 | 0 | 0%
IS48Inv1M3SCB3 | 31.9 | 0.008776%
IS48Inv1M3SCB4 | 63.8 | 0.01755%
IS48Inv1M3SCB5 | 31.9 | 0.008776%
IS48Inv1M3SCB6 | 63.8 | 0.01755%
IS48Inv1M4SCB1 | 207.35 | 0.05704%
IS48Inv1M4SCB2 | 223.3 | 0.06143%
IS48Inv1M4SCB3 | 223.3 | 0.06143%
IS48Inv1M4SCB4 | 191.4 | 0.05265%
IS48Inv1M4SCB5 | 0 | 0%
IS48Inv1M4SCB6 | 0 | 0%
IS48Inv2M1SCB1 | 63.8 | 0.01755%
IS48Inv2M1SCB2 | 31.9 | 0.008776%
IS48Inv2M1SCB3 | 159.5 | 0.04388%
IS48Inv2M1SCB4 | 223.3 | 0.06143%
IS48Inv2M1SCB5 | 223.3 | 0.06143%
IS48Inv2M1SCB6 | 159.5 | 0.04388%
IS48Inv2M2SCB1 | 191.4 | 0.05265%
IS48Inv2M2SCB2 | 223.3 | 0.06143%
IS48Inv2M2SCB3 | 223.3 | 0.06143%
IS48Inv2M2SCB4 | 207.35 | 0.05704%
IS48Inv2M2SCB5 | 159.5 | 0.04388%
IS48Inv2M2SCB6 | 223.3 | 0.06143%
IS48Inv2M3SCB1 | 159.5 | 0.04388%
IS48Inv2M3SCB2 | 159.5 | 0.04388%
IS48Inv2M3SCB3 | 95.7 | 0.02633%
IS48Inv2M3SCB4 | 31.9 | 0.008776%
IS48Inv2M3SCB5 | 0 | 0%
IS48Inv2M3SCB6 | 95.7 | 0.02633%
IS48Inv2M4SCB1 | 191.4 | 0.05265%
IS48Inv2M4SCB2 | 143.55 | 0.03949%
IS48Inv2M4SCB3 | 191.4 | 0.05265%
IS48Inv2M4SCB4 | 127.6 | 0.0351%
IS48Inv2M4SCB5 | 191.4 | 0.05265%
IS48Inv2M4SCB6 | 79.75 | 0.02194%
IS49Inv1M1SCB1 | 159.5 | 0.04388%
IS49Inv1M1SCB2 | 191.4 | 0.05265%
IS49Inv1M1SCB3 | 223.3 | 0.06143%
IS49Inv1M1SCB4 | 223.3 | 0.06143%
IS49Inv1M1SCB5 | 223.3 | 0.06143%
IS49Inv1M1SCB6 | 159.5 | 0.04388%
IS49Inv1M2SCB1 | 95.7 | 0.02633%
IS49Inv1M2SCB2 | 223.3 | 0.06143%
IS49Inv1M2SCB3 | 191.4 | 0.05265%
IS49Inv1M2SCB4 | 127.6 | 0.0351%
IS49Inv1M2SCB5 | 31.9 | 0.008776%
IS49Inv1M2SCB6 | 223.3 | 0.06143%
IS49Inv1M3SCB1 | 207.35 | 0.05704%
IS49Inv1M3SCB2 | 95.7 | 0.02633%
IS49Inv1M3SCB3 | 223.3 | 0.06143%
IS49Inv1M3SCB4 | 223.3 | 0.06143%
IS49Inv1M3SCB5 | 191.4 | 0.05265%
IS49Inv1M3SCB6 | 223.3 | 0.06143%
IS49Inv1M4SCB1 | 191.4 | 0.05265%
IS49Inv1M4SCB2 | 223.3 | 0.06143%
IS49Inv1M4SCB3 | 223.3 | 0.06143%
IS49Inv1M4SCB4 | 223.3 | 0.06143%
IS49Inv1M4SCB5 | 191.4 | 0.05265%
IS49Inv1M4SCB6 | 207.35 | 0.05704%
IS49Inv2M1SCB1 | 175.45 | 0.04827%
IS49Inv2M1SCB2 | 95.7 | 0.02633%
IS49Inv2M1SCB3 | 31.9 | 0.008776%
IS49Inv2M1SCB4 | 31.9 | 0.008776%
IS49Inv2M1SCB5 | 31.9 | 0.008776%
IS49Inv2M1SCB6 | 31.9 | 0.008776%
IS49Inv2M2SCB1 | 63.8 | 0.01755%
IS49Inv2M2SCB2 | 95.7 | 0.02633%
IS49Inv2M2SCB3 | 143.55 | 0.03949%
IS49Inv2M2SCB4 | 175.45 | 0.04827%
IS49Inv2M2SCB5 | 223.3 | 0.06143%
IS49Inv2M2SCB6 | 191.4 | 0.05265%
IS49Inv2M3SCB1 | 159.5 | 0.04388%
IS49Inv2M3SCB2 | 191.4 | 0.05265%
IS49Inv2M3SCB3 | 127.6 | 0.0351%
IS49Inv2M3SCB4 | 223.3 | 0.06143%
IS49Inv2M3SCB5 | 191.4 | 0.05265%
IS49Inv2M3SCB6 | 191.4 | 0.05265%
IS49Inv2M4SCB1 | 127.6 | 0.0351%
IS49Inv2M4SCB2 | 223.3 | 0.06143%
IS49Inv2M4SCB3 | 191.4 | 0.05265%
IS49Inv2M4SCB4 | 159.5 | 0.04388%
IS49Inv2M4SCB5 | 159.5 | 0.04388%
IS49Inv2M4SCB6 | 159.5 | 0.04388%
IS50Inv1M1SCB1 | 223.3 | 0.06143%
IS50Inv1M1SCB2 | 207.35 | 0.05704%
IS50Inv1M1SCB3 | 191.4 | 0.05265%
IS50Inv1M1SCB4 | 159.5 | 0.04388%
IS50Inv1M1SCB5 | 223.3 | 0.06143%
IS50Inv1M1SCB6 | 191.4 | 0.05265%
IS50Inv1M2SCB1 | 159.5 | 0.04388%
IS50Inv1M2SCB2 | 159.5 | 0.04388%
IS50Inv1M2SCB3 | 223.3 | 0.06143%
IS50Inv1M2SCB4 | 223.3 | 0.06143%
IS50Inv1M2SCB5 | 223.3 | 0.06143%
IS50Inv1M2SCB6 | 223.3 | 0.06143%
IS50Inv1M3SCB1 | 223.3 | 0.06143%
IS50Inv1M3SCB2 | 223.3 | 0.06143%
IS50Inv1M3SCB3 | 223.3 | 0.06143%
IS50Inv1M3SCB4 | 223.3 | 0.06143%
IS50Inv1M3SCB5 | 223.3 | 0.06143%
IS50Inv1M3SCB6 | 223.3 | 0.06143%
IS50Inv1M4SCB1 | 223.3 | 0.06143%
IS50Inv1M4SCB2 | 223.3 | 0.06143%
IS50Inv1M4SCB3 | 223.3 | 0.06143%
IS50Inv1M4SCB4 | 223.3 | 0.06143%
IS50Inv1M4SCB5 | 223.3 | 0.06143%
IS50Inv1M4SCB6 | 223.3 | 0.06143%
IS50Inv2M1SCB1 | 223.3 | 0.06143%
IS50Inv2M1SCB2 | 223.3 | 0.06143%
IS50Inv2M1SCB3 | 223.3 | 0.06143%
IS50Inv2M1SCB4 | 223.3 | 0.06143%
IS50Inv2M1SCB5 | 223.3 | 0.06143%
IS50Inv2M1SCB6 | 223.3 | 0.06143%
IS50Inv2M2SCB1 | 223.3 | 0.06143%
IS50Inv2M2SCB2 | 223.3 | 0.06143%
IS50Inv2M2SCB3 | 223.3 | 0.06143%
IS50Inv2M2SCB4 | 223.3 | 0.06143%
IS50Inv2M2SCB5 | 223.3 | 0.06143%
IS50Inv2M2SCB6 | 191.4 | 0.05265%
IS50Inv2M3SCB1 | 223.3 | 0.06143%
IS50Inv2M3SCB2 | 223.3 | 0.06143%
IS50Inv2M3SCB3 | 223.3 | 0.06143%
IS50Inv2M3SCB4 | 127.6 | 0.0351%
IS50Inv2M3SCB5 | 223.3 | 0.06143%
IS50Inv2M3SCB6 | 223.3 | 0.06143%
IS50Inv2M4SCB1 | 223.3 | 0.06143%
IS50Inv2M4SCB2 | 223.3 | 0.06143%
IS50Inv2M4SCB3 | 223.3 | 0.06143%
IS50Inv2M4SCB4 | 223.3 | 0.06143%
IS50Inv2M4SCB5 | 191.4 | 0.05265%
IS50Inv2M4SCB6 | 223.3 | 0.06143%
IS51Inv1M1SCB1 | 191.4 | 0.05265%
IS51Inv1M1SCB2 | 143.55 | 0.03949%
IS51Inv1M1SCB3 | 175.45 | 0.04827%
IS51Inv1M1SCB4 | 191.4 | 0.05265%
IS51Inv1M1SCB5 | 223.3 | 0.06143%
IS51Inv1M1SCB6 | 159.5 | 0.04388%
IS51Inv1M2SCB1 | 223.3 | 0.06143%
IS51Inv1M2SCB2 | 127.6 | 0.0351%
IS51Inv1M2SCB3 | 223.3 | 0.06143%
IS51Inv1M2SCB4 | 191.4 | 0.05265%
IS51Inv1M2SCB5 | 223.3 | 0.06143%
IS51Inv1M2SCB6 | 127.6 | 0.0351%
IS51Inv1M3SCB1 | 140.36 | 0.03861%
IS51Inv1M3SCB2 | 0 | 0%
IS51Inv1M3SCB3 | 175.45 | 0.04827%
IS51Inv1M3SCB4 | 223.3 | 0.06143%
IS51Inv1M3SCB5 | 191.4 | 0.05265%
IS51Inv1M3SCB6 | 223.3 | 0.06143%
IS51Inv1M4SCB1 | 191.4 | 0.05265%
IS51Inv1M4SCB2 | 223.3 | 0.06143%
IS51Inv1M4SCB3 | 223.3 | 0.06143%
IS51Inv1M4SCB4 | 127.6 | 0.0351%
IS51Inv1M4SCB5 | 159.5 | 0.04388%
IS51Inv1M4SCB6 | 191.4 | 0.05265%
IS51Inv2M1SCB1 | 175.45 | 0.04827%
IS51Inv2M1SCB2 | 223.3 | 0.06143%
IS51Inv2M1SCB3 | 191.4 | 0.05265%
IS51Inv2M1SCB4 | 63.8 | 0.01755%
IS51Inv2M1SCB5 | 223.3 | 0.06143%
IS51Inv2M1SCB6 | 159.5 | 0.04388%
IS51Inv2M2SCB1 | 191.4 | 0.05265%
IS51Inv2M2SCB2 | 127.6 | 0.0351%
IS51Inv2M2SCB3 | 223.3 | 0.06143%
IS51Inv2M2SCB4 | 223.3 | 0.06143%
IS51Inv2M2SCB5 | 191.4 | 0.05265%
IS51Inv2M2SCB6 | 127.6 | 0.0351%
IS51Inv2M3SCB1 | 223.3 | 0.06143%
IS51Inv2M3SCB2 | 223.3 | 0.06143%
IS51Inv2M3SCB3 | 191.4 | 0.05265%
IS51Inv2M3SCB4 | 223.3 | 0.06143%
IS51Inv2M3SCB5 | 223.3 | 0.06143%
IS51Inv2M3SCB6 | 223.3 | 0.06143%
IS51Inv2M4SCB1 | 191.4 | 0.05265%
IS51Inv2M4SCB2 | 223.3 | 0.06143%
IS51Inv2M4SCB3 | 191.4 | 0.05265%
IS51Inv2M4SCB4 | 191.4 | 0.05265%
IS51Inv2M4SCB5 | 223.3 | 0.06143%
IS51Inv2M4SCB6 | 223.3 | 0.06143%
IS52Inv1M1SCB1 | 223.3 | 0.06143%
IS52Inv1M1SCB2 | 191.4 | 0.05265%
IS52Inv1M1SCB3 | 223.3 | 0.06143%
IS52Inv1M1SCB4 | 95.7 | 0.02633%
IS52Inv1M1SCB5 | 95.7 | 0.02633%
IS52Inv1M1SCB6 | 223.3 | 0.06143%
IS52Inv1M2SCB1 | 159.5 | 0.04388%
IS52Inv1M2SCB2 | 31.9 | 0.008776%
IS52Inv1M2SCB3 | 31.9 | 0.008776%
IS52Inv1M2SCB4 | 127.6 | 0.0351%
IS52Inv1M2SCB5 | 31.9 | 0.008776%
IS52Inv1M2SCB6 | 95.7 | 0.02633%
IS52Inv1M3SCB1 | 127.6 | 0.0351%
IS52Inv1M3SCB2 | 95.7 | 0.02633%
IS52Inv1M3SCB3 | 127.6 | 0.0351%
IS52Inv1M3SCB4 | 127.6 | 0.0351%
IS52Inv1M3SCB5 | 127.6 | 0.0351%
IS52Inv1M3SCB6 | 127.6 | 0.0351%
IS52Inv1M4SCB1 | 223.3 | 0.06143%
IS52Inv1M4SCB2 | 223.3 | 0.06143%
IS52Inv1M4SCB3 | 223.3 | 0.06143%
IS52Inv1M4SCB4 | 223.3 | 0.06143%
IS52Inv1M4SCB5 | 223.3 | 0.06143%
IS52Inv1M4SCB6 | 223.3 | 0.06143%
IS52Inv2M1SCB1 | 159.5 | 0.04388%
IS52Inv2M1SCB2 | 0 | 0%
IS52Inv2M1SCB3 | 191.4 | 0.05265%
IS52Inv2M1SCB4 | 191.4 | 0.05265%
IS52Inv2M1SCB5 | 127.6 | 0.0351%
IS52Inv2M1SCB6 | 191.4 | 0.05265%
IS52Inv2M2SCB1 | 127.6 | 0.0351%
IS52Inv2M2SCB2 | 0 | 0%
IS52Inv2M2SCB3 | 223.3 | 0.06143%
IS52Inv2M2SCB4 | 159.5 | 0.04388%
IS52Inv2M2SCB5 | 191.4 | 0.05265%
IS52Inv2M2SCB6 | 191.4 | 0.05265%
IS52Inv2M3SCB1 | 191.4 | 0.05265%
IS52Inv2M3SCB2 | 63.8 | 0.01755%
IS52Inv2M3SCB3 | 31.9 | 0.008776%
IS52Inv2M3SCB4 | 191.4 | 0.05265%
IS52Inv2M3SCB5 | 223.3 | 0.06143%
IS52Inv2M3SCB6 | 191.4 | 0.05265%
IS52Inv2M4SCB1 | 223.3 | 0.06143%
IS52Inv2M4SCB2 | 223.3 | 0.06143%
IS52Inv2M4SCB3 | 207.35 | 0.05704%
IS52Inv2M4SCB4 | 159.5 | 0.04388%
IS52Inv2M4SCB5 | 191.4 | 0.05265%
IS52Inv2M4SCB6 | 31.9 | 0.008776%
IS1 | 9091.5 | 2.501%
IS2 | 8644.9 | 2.378%
IS3 | 10225.835 | 2.813%
IS4 | 9522.15 | 2.619%
IS5 | 8102.6 | 2.229%
IS6 | 10176.1 | 2.799%
IS7 | 9809.25 | 2.698%
IS8 | 9968.75 | 2.742%
IS9 | 9538.1 | 2.624%
IS10 | 0 | 0%
IS11 | 685.85 | 0.1887%
IS12 | 5295.4 | 1.457%
IS13 | 10271.8 | 2.826%
IS14 | 9920.9 | 2.729%
IS15 | 9889 | 2.72%
IS16 | 5008.3 | 1.378%
IS17 | 350.9 | 0.09653%
IS18 | 9745.45 | 2.681%
IS19 | 8453.5 | 2.326%
IS20 | 9075.55 | 2.497%
IS21 | 5949.35 | 1.637%
IS22 | 8884.15 | 2.444%
IS23 | 9298.85 | 2.558%
IS24 | 0 | 0%
IS25 | 0 | 0%
IS26 | 0 | 0%
IS27 | 0 | 0%
IS28 | 5742 | 1.58%
IS29 | 7863.35 | 2.163%
IS30 | 9570 | 2.633%
IS31 | 10383.45 | 2.856%
IS32 | 10112.3 | 2.782%
IS33 | 9107.45 | 2.505%
IS34 | 9442.4 | 2.598%
IS35 | 6092.9 | 1.676%
IS36 | 8102.6 | 2.229%
IS37 | 8501.35 | 2.339%
IS38 | 0 | 0%
IS39 | 414.7 | 0.1141%
IS40 | 4290.55 | 1.18%
IS41 | 8724.65 | 2.4%
IS42 | 7337 | 2.018%
IS43 | 9266.95 | 2.549%
IS44 | 6376.81 | 1.754%
IS45 | 6635.2 | 1.825%
IS46 | 8373.75 | 2.304%
IS47 | 8788.45 | 2.418%
IS48 | 6061 | 1.667%
IS49 | 7895.25 | 2.172%
IS50 | 10287.75 | 2.83%
IS51 | 8944.76 | 2.461%
IS52 | 7289.15 | 2.005%
Str_Typ1(545*29) | 15.805 | 0.004348%
Str_Typ2 (550*29) | 15.95 | 0.004388%
Tx | 0 | 0%
MVP | 0 | 0%
Aux_Tx | 0 | 0%
MCR_MVP_Inc1 | 25389.21 | 6.984%
MCR_MVP_Inc2 | 25232.9 | 6.941%
MCR_MVP_Inc3 | 26346.21 | 7.248%
MCR_MVP_Inc4 | 17226 | 4.739%
MCR_MVP_Inc5 | 685.85 | 0.1887%
MCR_MVP_Inc6 | 23637.9 | 6.503%
MCR_MVP_Inc7 | 12042.25 | 3.313%
MCR_MVP_Inc8 | 24722.5 | 6.801%
MCR_MVP_Inc9 | 26540.8 | 7.301%
MCR_MVP_Inc10 | 350.9 | 0.09653%
MCR_MVP_Inc11 | 29316.1 | 8.065%
MCR_MVP_Inc12 | 14817.55 | 4.076%
MCR_MVP_Inc13 | 26285.6 | 7.231%
MCR_MVP_Inc14 | 19747.985 | 5.433%
MCR_MVP_Inc15 | 5008.3 | 1.378%
MCR_MVP_Inc16 | 22840.4 | 6.283%
MCR_MVP_Inc17 | 23653.85 | 6.507%
MCR_MVP_Inc18 | 29395.85 | 8.087%
MCR_MVP_Inc19 | 0 | 0%
MCR_MVP_Inc20 | 10271.8 | 2.826%
MCR_MVP_OG1 | 94880.17 | 26.1%
MCR_MVP_OG2 | 87294.35 | 24.01%
MCR_MVP_OG3 | 95175.535 | 26.18%
MCR_MVP_OG4 | 86161.9 | 23.7%
Power_Tx1 | 182174.52 | 50.12%
Power_Tx2 | 181337.435 | 49.88%
Line_Bay1 | 363511.955 | 100%

## Inv_SY
| 957 | 1084.6 | 829.4 | 1276 | 1339.8 | 1244.1 | 1116.5 | 1244.1 | 1180.3 | 1196.25 | 1244.1 | 1339.8 | 1244.1 | 781.55 | 430.65 | 1228.15 | 1264.4 | 1327.62 | 1232.79 | 1280.205 | 1296.01 | 1264.4 | 1296.01 | 1264.4 | 1180.3 | 1307.9 | 1307.9 | 1228.15 | 1323.85 | 1100.55 | 1036.75 | 1036.75 | 861.3 | 1212.2 | 797.5 | 893.2 | 1307.9 | 1307.9 | 893.2 | 829.4 | 1244.1 | 1276 | 1307.9 | 1244.1 | 1244.1 | 1307.9 | 1276 | 1276 | 1276 | 1291.95 | 1339.8 | 1276 | 861.3 | 1276 | 1244.1 | 1244.1 | 1244.1 | 1244.1 | 1276 | 1244.1 | 1212.2 | 1244.1 | 1164.35 | 1339.8 | 1276 | 1307.9 | 1244.1 | 1212.2 | 1084.6 | 1148.4 | 1180.3 | 1084.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382.8 | 303.05 | 0 | 0 | 0 | 0 | 0 | 0 | 1339.8 | 1339.8 | 1307.9 | 1307.9 | 1339.8 | 1276 | 1339.8 | 1307.9 | 1244.1 | 1148.4 | 1307.9 | 1307.9 | 1339.8 | 1260.05 | 1084.6 | 1307.9 | 1116.5 | 1276 | 1228.15 | 1307.9 | 1020.8 | 1260.05 | 1276 | 1164.35 | 1276 | 1307.9 | 1276 | 1307.9 | 1276 | 1244.1 | 1307.9 | 1180.3 | 287.1 | 63.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1291.95 | 1212.2 | 1339.8 | 1244.1 | 1307.9 | 1148.4 | 1052.7 | 1148.4 | 1148.4 | 1116.5 | 1276 | 1212.2 | 957 | 797.5 | 765.6 | 1180.3 | 1291.95 | 1164.35 | 1276 | 1339.8 | 1323.85 | 350.9 | 1212.2 | 1116.5 | 988.9 | 765.6 | 510.4 | 861.3 | 1004.85 | 829.4 | 430.65 | 558.25 | 1116.5 | 1276 | 1307.9 | 1339.8 | 797.5 | 988.9 | 813.45 | 1244.1 | 1180.3 | 797.5 | 1244.1 | 1148.4 | 1260.05 | 1276 | 1212.2 | 1180.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1244.1 | 1180.3 | 733.7 | 669.9 | 861.3 | 0 | 350.9 | 701.8 | 988.9 | 733.7 | 861.3 | 988.9 | 1180.3 | 1052.7 | 893.2 | 1164.35 | 1244.1 | 1276 | 1116.5 | 1276 | 1212.2 | 1084.6 | 1020.8 | 1339.8 | 1116.5 | 1307.9 | 1307.9 | 1339.8 | 1291.95 | 1339.8 | 1339.8 | 1339.8 | 1084.6 | 1244.1 | 1307.9 | 1339.8 | 1563.1 | 1084.6 | 1276 | 1212.2 | 1180.3 | 1244.1 | 925.1 | 1276 | 1148.4 | 1116.5 | 1260.05 | 957 | 1084.6 | 893.2 | 1180.3 | 1180.3 | 1307.9 | 1307.9 | 1212.2 | 1276 | 893.2 | 1180.3 | 1020.8 | 893.2 | 127.6 | 0 | 797.5 | 1180.3 | 829.4 | 1020.8 | 957 | 893.2 | 1244.1 | 1052.7 | 1148.4 | 957 | 1228.15 | 1132.45 | 669.9 | 733.7 | 1084.6 | 1228.15 | 1291.95 | 1132.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191.4 | 0 | 0 | 223.3 | 0 | 1291.95 | 1196.25 | 1228.15 | 287.1 | 0 | 0 | 0 | 287.1 | 1036.75 | 909.15 | 1052.7 | 1084.6 | 1148.4 | 1244.1 | 1180.3 | 1068.65 | 382.8 | 701.8 | 1100.55 | 430.65 | 1307.9 | 1196.25 | 1100.55 | 1116.5 | 1068.65 | 845.35 | 1276 | 1291.95 | 1307.9 | 1276 | 1244.1 | 957 | 988.9 | 638 | 0 | 1081.41 | 797.5 | 781.55 | 1164.35 | 925.1 | 797.5 | 510.4 | 1052.7 | 1020.8 | 861.3 | 797.5 | 893.2 | 701.8 | 1004.85 | 988.9 | 1020.8 | 1116.5 | 1148.4 | 749.65 | 1212.2 | 1132.45 | 972.95 | 1068.65 | 1148.4 | 1196.25 | 1084.6 | 1148.4 | 1180.3 | 988.9 | 319 | 925.1 | 414.7 | 845.35 | 861.3 | 1228.15 | 542.3 | 925.1 | 1180.3 | 893.2 | 1164.35 | 1260.05 | 398.75 | 893.2 | 1084.6 | 1020.8 | 1196.25 | 1212.2 | 1339.8 | 1339.8 | 1339.8 | 1307.9 | 1244.1 | 1307.9 | 1084.6 | 1116.5 | 953.81 | 1116.5 | 1036.75 | 1084.6 | 1307.9 | 1244.1 | 1052.7 | 478.5 | 733.7 | 1339.8 | 861.3 | 893.2 | 893.2 | 1036.75
Date | IS1Inv1M1 | IS1Inv1M2 | IS1Inv1M3 | IS1Inv1M4 | IS1Inv2M1 | IS1Inv2M2 | IS1Inv2M3 | IS1Inv2M4 | IS2Inv1M1 | IS2Inv1M2 | IS2Inv1M3 | IS2Inv1M4 | IS2Inv2M1 | IS2Inv2M2 | IS2Inv2M3 | IS2Inv2M4 | IS3Inv1M1 | IS3Inv1M2 | IS3Inv1M3 | IS3Inv1M4 | IS3Inv2M1 | IS3Inv2M2 | IS3Inv2M3 | IS3Inv2M4 | IS4Inv1M1 | IS4Inv1M2 | IS4Inv1M3 | IS4Inv1M4 | IS4Inv2M1 | IS4Inv2M2 | IS4Inv2M3 | IS4Inv2M4 | IS5Inv1M1 | IS5Inv1M2 | IS5Inv1M3 | IS5Inv1M4 | IS5Inv2M1 | IS5Inv2M2 | IS5Inv2M3 | IS5Inv2M4 | IS6Inv1M1 | IS6Inv1M2 | IS6Inv1M3 | IS6Inv1M4 | IS6Inv2M1 | IS6Inv2M2 | IS6Inv2M3 | IS6Inv2M4 | IS7Inv1M1 | IS7Inv1M2 | IS7Inv1M3 | IS7Inv1M4 | IS7Inv2M1 | IS7Inv2M2 | IS7Inv2M3 | IS7Inv2M4 | IS8Inv1M1 | IS8Inv1M2 | IS8Inv1M3 | IS8Inv1M4 | IS8Inv2M1 | IS8Inv2M2 | IS8Inv2M3 | IS8Inv2M4 | IS9Inv1M1 | IS9Inv1M2 | IS9Inv1M3 | IS9Inv1M4 | IS9Inv2M1 | IS9Inv2M2 | IS9Inv2M3 | IS9Inv2M4 | IS10Inv1M1 | IS10Inv1M2 | IS10Inv1M3 | IS10Inv1M4 | IS10Inv2M1 | IS10Inv2M2 | IS10Inv2M3 | IS10Inv2M4 | IS11Inv1M1 | IS11Inv1M2 | IS11Inv1M3 | IS11Inv1M4 | IS12Inv1M1 | IS12Inv1M2 | IS12Inv1M3 | IS12Inv1M4 | IS12Inv2M1 | IS12Inv2M2 | IS12Inv2M3 | IS12Inv2M4 | IS13Inv1M1 | IS13Inv1M2 | IS13Inv1M3 | IS13Inv1M4 | IS13Inv2M1 | IS13Inv2M2 | IS13Inv2M3 | IS13Inv2M4 | IS14Inv1M1 | IS14Inv1M2 | IS14Inv1M3 | IS14Inv1M4 | IS14Inv2M1 | IS14Inv2M2 | IS14Inv2M3 | IS14Inv2M4 | IS15Inv1M1 | IS15Inv1M2 | IS15Inv1M3 | IS15Inv1M4 | IS15Inv2M1 | IS15Inv2M2 | IS15Inv2M3 | IS15Inv2M4 | IS16Inv1M1 | IS16Inv1M2 | IS16Inv1M3 | IS16Inv1M4 | IS17Inv1M1 | IS17Inv1M2 | IS17Inv1M3 | IS17Inv1M4 | IS17Inv2M1 | IS17Inv2M2 | IS17Inv2M3 | IS17Inv2M4 | IS18Inv1M1 | IS18Inv1M2 | IS18Inv1M3 | IS18Inv1M4 | IS18Inv2M1 | IS18Inv2M2 | IS18Inv2M3 | IS18Inv2M4 | IS19Inv1M1 | IS19Inv1M2 | IS19Inv1M3 | IS19Inv1M4 | IS19Inv2M1 | IS19Inv2M2 | IS19Inv2M3 | IS19Inv2M4 | IS20Inv1M1 | IS20Inv1M2 | IS20Inv1M3 | IS20Inv1M4 | IS20Inv2M1 | IS20Inv2M2 | IS20Inv2M3 | IS20Inv2M4 | IS21Inv1M1 | IS21Inv1M2 | IS21Inv1M3 | IS21Inv1M4 | IS21Inv2M1 | IS21Inv2M2 | IS21Inv2M3 | IS21Inv2M4 | IS22Inv1M1 | IS22Inv1M2 | IS22Inv1M3 | IS22Inv1M4 | IS22Inv2M1 | IS22Inv2M2 | IS22Inv2M3 | IS22Inv2M4 | IS23Inv1M1 | IS23Inv1M2 | IS23Inv1M3 | IS23Inv1M4 | IS23Inv2M1 | IS23Inv2M2 | IS23Inv2M3 | IS23Inv2M4 | IS24Inv1M1 | IS24Inv1M2 | IS24Inv1M3 | IS24Inv1M4 | IS24Inv2M1 | IS24Inv2M2 | IS24Inv2M3 | IS24Inv2M4 | IS25Inv1M1 | IS25Inv1M2 | IS25Inv1M3 | IS25Inv1M4 | IS25Inv2M1 | IS25Inv2M2 | IS25Inv2M3 | IS25Inv2M4 | IS26Inv1M1 | IS26Inv1M2 | IS26Inv1M3 | IS26Inv1M4 | IS26Inv2M1 | IS26Inv2M2 | IS26Inv2M3 | IS26Inv2M4 | IS27Inv1M1 | IS27Inv1M2 | IS27Inv1M3 | IS27Inv1M4 | IS27Inv2M1 | IS27Inv2M2 | IS27Inv2M3 | IS27Inv2M4 | IS28Inv1M1 | IS28Inv1M2 | IS28Inv1M3 | IS28Inv1M4 | IS28Inv2M1 | IS28Inv2M2 | IS28Inv2M3 | IS28Inv2M4 | IS29Inv1M1 | IS29Inv1M2 | IS29Inv1M3 | IS29Inv1M4 | IS29Inv2M1 | IS29Inv2M2 | IS29Inv2M3 | IS29Inv2M4 | IS30Inv1M1 | IS30Inv1M2 | IS30Inv1M3 | IS30Inv1M4 | IS30Inv2M1 | IS30Inv2M2 | IS30Inv2M3 | IS30Inv2M4 | IS31Inv1M1 | IS31Inv1M2 | IS31Inv1M3 | IS31Inv1M4 | IS31Inv2M1 | IS31Inv2M2 | IS31Inv2M3 | IS31Inv2M4 | IS32Inv1M1 | IS32Inv1M2 | IS32Inv1M3 | IS32Inv1M4 | IS32Inv2M1 | IS32Inv2M2 | IS32Inv2M3 | IS32Inv2M4 | IS33Inv1M1 | IS33Inv1M2 | IS33Inv1M3 | IS33Inv1M4 | IS33Inv2M1 | IS33Inv2M2 | IS33Inv2M3 | IS33Inv2M4 | IS34Inv1M1 | IS34Inv1M2 | IS34Inv1M3 | IS34Inv1M4 | IS34Inv2M1 | IS34Inv2M2 | IS34Inv2M3 | IS34Inv2M4 | IS35Inv1M1 | IS35Inv1M2 | IS35Inv1M3 | IS35Inv1M4 | IS35Inv2M1 | IS35Inv2M2 | IS35Inv2M3 | IS35Inv2M4 | IS36Inv1M1 | IS36Inv1M2 | IS36Inv1M3 | IS36Inv1M4 | IS36Inv2M1 | IS36Inv2M2 | IS36Inv2M3 | IS36Inv2M4 | IS37Inv1M1 | IS37Inv1M2 | IS37Inv1M3 | IS37Inv1M4 | IS37Inv2M1 | IS37Inv2M2 | IS37Inv2M3 | IS37Inv2M4 | IS38Inv1M1 | IS38Inv1M2 | IS38Inv1M3 | IS38Inv1M4 | IS38Inv2M1 | IS38Inv2M2 | IS38Inv2M3 | IS38Inv2M4 | IS39Inv1M1 | IS39Inv1M2 | IS39Inv1M3 | IS39Inv1M4 | IS39Inv2M1 | IS39Inv2M2 | IS39Inv2M3 | IS39Inv2M4 | IS40Inv1M1 | IS40Inv1M2 | IS40Inv1M3 | IS40Inv1M4 | IS40Inv2M1 | IS40Inv2M2 | IS40Inv2M3 | IS40Inv2M4 | IS41Inv1M1 | IS41Inv1M2 | IS41Inv1M3 | IS41Inv1M4 | IS41Inv2M1 | IS41Inv2M2 | IS41Inv2M3 | IS41Inv2M4 | IS42Inv1M1 | IS42Inv1M2 | IS42Inv1M3 | IS42Inv1M4 | IS42Inv2M1 | IS42Inv2M2 | IS42Inv2M3 | IS42Inv2M4 | IS43Inv1M1 | IS43Inv1M2 | IS43Inv1M3 | IS43Inv1M4 | IS43Inv2M1 | IS43Inv2M2 | IS43Inv2M3 | IS43Inv2M4 | IS44Inv1M1 | IS44Inv1M2 | IS44Inv1M3 | IS44Inv1M4 | IS44Inv2M1 | IS44Inv2M2 | IS44Inv2M3 | IS44Inv2M4 | IS45Inv1M1 | IS45Inv1M2 | IS45Inv1M3 | IS45Inv1M4 | IS45Inv2M1 | IS45Inv2M2 | IS45Inv2M3 | IS45Inv2M4 | IS46Inv1M1 | IS46Inv1M2 | IS46Inv1M3 | IS46Inv1M4 | IS46Inv2M1 | IS46Inv2M2 | IS46Inv2M3 | IS46Inv2M4 | IS47Inv1M1 | IS47Inv1M2 | IS47Inv1M3 | IS47Inv1M4 | IS47Inv2M1 | IS47Inv2M2 | IS47Inv2M3 | IS47Inv2M4 | IS48Inv1M1 | IS48Inv1M2 | IS48Inv1M3 | IS48Inv1M4 | IS48Inv2M1 | IS48Inv2M2 | IS48Inv2M3 | IS48Inv2M4 | IS49Inv1M1 | IS49Inv1M2 | IS49Inv1M3 | IS49Inv1M4 | IS49Inv2M1 | IS49Inv2M2 | IS49Inv2M3 | IS49Inv2M4 | IS50Inv1M1 | IS50Inv1M2 | IS50Inv1M3 | IS50Inv1M4 | IS50Inv2M1 | IS50Inv2M2 | IS50Inv2M3 | IS50Inv2M4 | IS51Inv1M1 | IS51Inv1M2 | IS51Inv1M3 | IS51Inv1M4 | IS51Inv2M1 | IS51Inv2M2 | IS51Inv2M3 | IS51Inv2M4 | IS52Inv1M1 | IS52Inv1M2 | IS52Inv1M3 | IS52Inv1M4 | IS52Inv2M1 | IS52Inv2M2 | IS52Inv2M3 | IS52Inv2M4
2025-06-15 | -63.92% | -17.73% | -14.7% | -16.62% | -14.78% | -13.87% | -39.88% | -22.5% | -12.35% | -15.61% | -12.32% | -14.83% | -14.28% | -12.06% | -23.53% | -5.34% | -14.6% | -18.77% | -19.69% | -15.05% | -18.5% | -15.71% | -26.13% | -15.52% | -20.81% | -14.46% | -15.66% | -13.93% | -24.06% | -22.34% | -22.86% | -16.91% | -29.01% | -20.38% | -29.49% | -26.22% | -22.76% | -22.06% | -20.11% | -14.1% | -26.45% | -15.1% | -28.12% | -33.13% | -75.58% | -75.7% | -19.56% | -22.27% | -30.15% | -57.75% | -29.7% | -15.04% | 11.67% | -33.89% | -15.01% | -20.71% | -32.39% | -30.56% | -23.95% | -36.19% | -45.3% | -74.17% | -17.21% | -30.71% | -43.46% | -26.34% | -38.84% | -25.22% | -33.38% | -28.31% | -23.41% | -24.26% | [8 empty] | -100% | -100% | [6 empty] | -22.18% | -25.38% | -21.95% | -20.33% | -20.62% | -19.97% | -20% | -20.82% | -8.998% | -29.63% | -43.91% | -18.3% | -52.33% | -20.15% | -11.15% | -59.7% | -15.73% | -35.69% | -16.64% | -28.38% | 3.996% | -12.99% | -15.92% | -3.101% | 728.5% | -21.56% | -13.02% | -19.58% | -100% | -100% | -100% | -100% | 257.1% | 1548% | [6 empty] | -24.2% | -26.39% | -20.61% | -21.71% | -24.43% | -35.25% | -18.73% | -20.92% | -100% | -100% | -100% | -100% | -15.32% | 24.48% | -58.94% | -3.976% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -67.52% | 34.23% | 97.51% | 2.502% | -33.99% | -22.21% | 52.61% | 95.97% | -38.73% | -75.19% | -19.78% | -33.91% | -9.012% | 5.364% | 19.27% | -29.01% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -18.91% | -6.227% | -43.55% | -86.57% | -87.31% | -60.92% | -63.87% | -34.34% | -86.02% | -80.8% | -72.71% | -100% | -96.01% | -100% | -100% | -54.05% | -7.941% | -22.07% | -14.15% | -22.5% | -29.1% | -65.43% | -20.16% | -23.08% | -25.97% | -17.54% | -27.88% | -20.03% | -28.56% | 0.8321% | -18.76% | -28.76% | -73.72% | -100% | -77.42% | -100% | -100% | -98.97% | -60.42% | -30.05% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-06-16 | -63.81% | -20.76% | -18.82% | -19.33% | -17.25% | -16.78% | -45.82% | -24.81% | -15.58% | -18.97% | -15.52% | -17.75% | -17.78% | -16.72% | -23.81% | -7.936% | -17.74% | -21.65% | -22.45% | -17.43% | -21% | -18.19% | -29.08% | -18.41% | -24.48% | -17.09% | -18.09% | -16.86% | -27.8% | -27.01% | -28.48% | -21.4% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [8 empty] | -100% | -100% | [6 empty] | -100% | -100% | -100% | -100% | -24.63% | -24.44% | -24.19% | -25.24% | -13.62% | -34.57% | -48.22% | -22.61% | -56.36% | -25.61% | -16.18% | -62.83% | -20.26% | -40.15% | -21.4% | -33.1% | -0.8829% | -18.86% | -21.95% | -9.042% | -22.67% | -27.01% | -17.62% | -24.26% | -100% | -100% | -100% | -100% | 223.1% | 1381% | [6 empty] | -31.08% | -33.24% | -27.06% | -28.05% | -30.73% | -41.92% | -26.94% | -28.3% | -100% | -100% | -100% | -100% | -16.92% | 22.69% | -57.62% | -5.279% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -68.95% | 26.18% | 84.94% | -5.157% | -40.03% | -29.41% | 39.62% | 81.82% | -43.95% | -76.65% | -24.51% | -50.77% | -21.53% | 1.284% | 15.44% | -23.27% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -25.1% | -15.4% | -48.25% | -85.66% | -86.69% | -64.08% | -67.56% | -45.91% | -85.24% | -81.19% | -73.87% | -100% | -94.56% | -100% | -100% | -57.65% | -15.02% | -27.76% | -19.78% | -27.65% | -34.28% | -68.17% | -25.8% | -28.62% | -33.72% | -25.18% | -34.55% | -25.83% | -33.74% | -5.925% | -24.81% | -34.76% | -74.72% | -100% | -77.27% | -100% | -100% | -97.71% | -64.25% | -36.78% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-06-17 | -63.57% | -20.73% | -18.79% | -19.5% | -17.58% | -16.97% | -42.37% | -24.78% | -15.71% | -18.76% | -15.36% | -17.86% | -17.8% | -15.96% | -23.06% | -8.371% | -17.69% | -21.54% | -22.41% | -17.28% | -20.55% | -17.74% | -28.72% | -18.16% | -23.19% | -16.4% | -17.3% | -15.9% | -27% | -25.66% | -26.63% | -19.49% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [8 empty] | -100% | -100% | [6 empty] | -100% | -100% | -100% | -100% | -23.72% | -23.44% | -23.06% | -24.14% | -12.52% | -33.36% | -47.3% | -22.19% | -55.5% | -24.35% | -15.03% | -62.34% | -19.13% | -39.19% | -20.31% | -31.73% | -34.94% | -46.52% | -48.54% | -40.27% | -49.8% | -52.42% | -46.59% | -50.98% | -100% | -100% | -100% | -100% | 248.6% | 1483% | [6 empty] | -26.54% | -28.74% | -22.16% | -23.53% | -26.35% | -38.25% | -22.35% | -23.83% | -100% | -100% | -100% | -100% | -15.39% | 24.12% | -56.65% | -3.75% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -68.02% | 28.41% | 89.02% | -2.79% | -38.15% | -26.75% | 44.65% | 88.15% | -42.41% | -76.6% | -22.72% | -55% | -33.32% | 2.813% | 16.76% | -23.15% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -26.25% | -13.07% | -46.51% | -84.88% | -86.06% | -62.88% | -65.47% | -44.49% | -84.59% | -80.51% | -73.03% | -100% | -94% | -100% | -100% | -56.35% | -11.96% | -25.14% | -17.08% | -25.19% | -32.01% | -66.88% | -23.12% | -26.05% | -30.6% | -22.45% | -31.58% | -22.96% | -31.35% | -2.83% | -22.32% | -32.34% | -73.79% | -100% | -76.3% | -100% | -100% | -97.15% | -63.11% | -34.83% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-06-18 | -55.44% | -3.388% | -0.8422% | -3.862% | -2.321% | -0.1583% | -29.23% | -8.19% | 2.667% | -1.584% | 1.383% | -2.196% | -0.3772% | 3.886% | -3.877% | 8.798% | -1.361% | -6.154% | -5.527% | -1.756% | -5.23% | -2.243% | -13.38% | -2.136% | -6.75% | -1.477% | -2.466% | 0.5922% | -10.31% | -9.391% | -10.46% | -1.976% | -29.86% | -43.36% | -26.27% | -30.99% | -47.04% | -47.01% | -28.89% | -23.31% | -69.8% | -68.76% | -46.96% | -44.62% | -45.59% | -46.26% | -46.58% | -48.12% | -46.25% | -48.3% | -48% | -45.92% | -21.6% | -54.77% | -45.09% | -43.3% | -50.21% | -68.98% | -46.6% | -45.37% | -45.49% | -46.43% | -41.3% | -51.43% | -49.91% | -49.87% | -45.53% | -45.44% | -41.19% | -41.08% | -45.16% | -37.56% | [8 empty] | -100% | -100% | [6 empty] | -47.8% | -48.26% | -46.88% | -46.65% | -8.125% | -7.061% | -7.582% | -8.194% | 3.652% | -18.45% | -35.23% | -5.732% | -45.67% | -8.275% | 3.705% | -53.61% | -1.091% | -25.64% | -3.255% | -17.06% | 27.88% | 4.948% | 0.9328% | 16.87% | -1.517% | -6.69% | 4.64% | -3.391% | -100% | -100% | -100% | -100% | 321.6% | 1812% | [6 empty] | -10.86% | -13.33% | -6.012% | -8.715% | 23.07% | -25.39% | -5.804% | -7.281% | 7.695% | -3.91% | -17.33% | -1.442% | 1.406% | 48.29% | -47.36% | 11.47% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -60.43% | 55.22% | 130.1% | 19% | -24.44% | -10.81% | 76.32% | 123.3% | -29.68% | -71.22% | -6.788% | -62.09% | -18.1% | 24.53% | 41.64% | -4.958% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -4.42% | 8.516% | -32.19% | -80.91% | -82.42% | -53.96% | -56.42% | -28.76% | -80.82% | -75.82% | -66.54% | -100% | -92.34% | -100% | -99.96% | -46.56% | 3.886% | -9.3% | -1.826% | -10.07% | -17.42% | -59.65% | -8.082% | -10.83% | -14.6% | -5.532% | -15.64% | -7.233% | -18.5% | 15.88% | -6.02% | -17.3% | -67.32% | -100% | -70.33% | -100% | -100% | -96.14% | -54.39% | -19.93% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-06-19 | -55.34% | -3.353% | -0.01468% | -2.447% | -0.9498% | 0.9276% | -29.66% | -8.476% | 3.138% | -1.612% | 2.666% | -0.8677% | 0.8128% | 3.181% | -4.366% | 10.79% | -0.3604% | -5.523% | -5.746% | -0.5017% | -4.321% | -2.102% | -13.71% | -1.01% | -7.368% | 0.003664% | -1.101% | 1.682% | -10.11% | -9.895% | -10.77% | -2.557% | -38.48% | -41.34% | -25.57% | -30.36% | -45.24% | -45.35% | -27.72% | -21.87% | -43.74% | -42.84% | -46.13% | -45.28% | -69.98% | -69.68% | -43.67% | -44.09% | -44.43% | -46.73% | -46.02% | -43.98% | -19.14% | -54.27% | -43.35% | -41.31% | -45.38% | -44.87% | -44.9% | -46.96% | -47.85% | -68.77% | -39.93% | -47.62% | -49.13% | -46.77% | -46.91% | -42.45% | -39.99% | -41.5% | -40.88% | -37.56% | [8 empty] | -100% | -100% | [6 empty] | -45.7% | -53.57% | -44.57% | -44.3% | -7.253% | -6.768% | -6.793% | -7.916% | 5.248% | -18.89% | -35.55% | -4.711% | -45.76% | -8.079% | 3.036% | -53.99% | -1.956% | -26.23% | -2.875% | -17% | 26.36% | 3.572% | -0.6473% | 15.08% | -2.603% | -7.886% | 3.651% | -4.359% | -100% | -100% | -100% | -100% | 314.8% | 1777% | [6 empty] | -11.88% | -14.42% | -6.946% | -11.09% | -12.14% | -26.04% | -6.599% | -8.441% | 14.48% | 0.9173% | -12.24% | 5.407% | 0.8161% | 55.04% | -47.64% | 13.13% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -60.66% | 54.32% | 130.2% | 18.14% | -24.64% | -11.08% | 75.7% | 125.6% | -29.92% | -71.21% | -5.876% | -65.38% | -18.43% | 25.76% | 39.29% | -4.769% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -7.714% | 6.951% | -32.25% | -81.04% | -85.27% | -53.97% | -56.44% | -40.79% | -80.96% | -76.01% | -66.6% | -100% | -92.49% | -100% | -62.35% | -46.92% | 3.319% | -9.405% | -0.4922% | -9.552% | -17.61% | -59.82% | -7.397% | -10.71% | -15.4% | -6.688% | -16.39% | -6.801% | -17.56% | 16.98% | -5.995% | -17.93% | -67.43% | -100% | -70.43% | -100% | -100% | -96.34% | -55.19% | -37.4% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-06-20 | -55.53% | -3.559% | -0.803% | -2.673% | -0.5463% | 0.533% | -30.06% | -8.731% | 2.673% | -1.817% | 2.7% | -0.3931% | 0.9425% | 3.188% | -4.622% | 11.57% | -0.2187% | -4.614% | -5.855% | -0.2582% | -4.437% | -2.217% | -13.55% | -0.6796% | -7.022% | 0.6926% | -0.6048% | 1.883% | -10.07% | -9.174% | -9.742% | -2.092% | -28.01% | -40.65% | -25.25% | -29.41% | -44.59% | -44.84% | -26.81% | -20.81% | -43.08% | -42.02% | -45.86% | -42.64% | -69.98% | -69.7% | -42.93% | -43.39% | -44.77% | -55.31% | -46.72% | -42.01% | -16.81% | -45.41% | -41.09% | -41.72% | -44.55% | -44.12% | -44.28% | -46.04% | -47.26% | -68.57% | -38.88% | -46.93% | -48.41% | -45.93% | -45.85% | -41.66% | -38.67% | -40.3% | -40.09% | -36.48% | [8 empty] | -100% | -100% | [6 empty] | -44.9% | -45.55% | -43.93% | -43.33% | -7.113% | -6.461% | -6.554% | -7.95% | 6.384% | -18.23% | -35.22% | -4.455% | -45.2% | -7.3% | 3.953% | -53.64% | -0.9572% | -25.34% | -1.778% | -15.97% | 23.56% | 1.251% | -2.875% | 12.3% | -3.991% | -9.359% | 1.645% | -5.985% | -100% | -100% | -100% | -100% | 309.8% | 1749% | [6 empty] | -12.87% | -15.42% | -8.351% | -12.01% | -13.06% | -26.81% | -7.729% | -9.635% | 14.44% | 0.2902% | -12.46% | 5.484% | 0.9719% | 49.14% | -47.93% | 13.39% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -60.68% | 54.07% | 129.9% | 18.21% | -24.64% | -10.89% | 75.57% | 125.4% | -29.46% | -71.05% | -5.694% | -65.57% | -18.45% | 25.8% | 39.22% | -4.645% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -8.925% | 8.107% | -31.63% | -81.03% | -85.23% | -53.72% | -56.24% | -42.65% | -80.94% | -75.98% | -66.55% | -100% | -99.02% | -100% | -62.43% | -46.92% | 2.385% | -10.13% | -0.4269% | -9.87% | -17.5% | -59.84% | -7.935% | -11.38% | -16.21% | -8.39% | -17.11% | -7.603% | -17.7% | 16.53% | -6.878% | -18.67% | -67.27% | -100% | -70.21% | -100% | -100% | -96.34% | -59.65% | -37.01% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-06-21 | -56.54% | -1.467% | 0.2615% | 0.5151% | 3.395% | 4.003% | -28.15% | -6.215% | 5.13% | 1.319% | 6.284% | 3.18% | 3.249% | 3.356% | -7.831% | 15.95% | 2.764% | -1.661% | -3.311% | 3.158% | -1.208% | 1.25% | -11.19% | 2.26% | -4.767% | 4.446% | 3.208% | 5.351% | -100% | -7.103% | -7.939% | -0.3327% | -19.35% | -13.92% | -19.27% | -19.02% | -18.73% | -19.74% | -10.39% | -3.774% | -19.94% | -12.04% | -22.52% | -26.47% | -70.74% | -70.73% | -15.34% | -17.26% | -22.87% | -53.5% | -24.36% | -12.01% | 17.9% | -25.41% | -12.5% | -16.18% | -25.43% | -23.54% | -18.85% | -28.84% | -36.58% | -69.05% | -11.65% | -24.61% | -38.28% | -24.19% | -31.09% | -17.79% | -23.8% | -21.57% | -15.87% | -15.7% | [8 empty] | -100% | -100% | [6 empty] | -15.31% | -18.98% | -16.5% | -14.02% | -5.4% | -4.984% | -4.851% | -5.409% | 9.17% | -17.86% | -35.4% | -2.824% | -45.33% | -6.03% | 5.053% | -54.07% | 0.6596% | -24.99% | -0.3732% | -15.2% | 5.989% | -13.17% | -18.95% | -3.157% | -17.17% | -22.17% | -14.46% | -19.44% | -100% | -100% | -100% | -100% | 245.3% | 1463% | [6 empty] | -57.61% | -58.99% | -55.02% | -57.23% | -57.59% | -64.46% | -55.34% | -55.98% | 19.18% | 3.017% | -9.93% | 9.764% | 3.792% | 54.19% | -48.57% | 18.59% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -67.5% | 32.25% | 96.75% | 0.4067% | -36.21% | -24.67% | 47.97% | 93.34% | -39.93% | -75.99% | -18.76% | -77.56% | -30.92% | 8.532% | 17.92% | -17.8% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -19.8% | -30.17% | -21.8% | -29.42% | -35.87% | -69.02% | -27.97% | -30.9% | -23.32% | -15.41% | -24.13% | -14.59% | -46.79% | -2.966% | -22.23% | -5.596% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-06-22 | -55.11% | -3.759% | -1.537% | -2.25% | 0.537% | 2.236% | -26.06% | -9.003% | -1.841% | -0.505% | 4.957% | 2.416% | 2.54% | 4.063% | -3.357% | 14.26% | 1.559% | -2.955% | -3.807% | 1.039% | -2.038% | 0.1962% | -13.15% | 0.1489% | -7.239% | 1.185% | 0.1197% | 1.899% | -36.98% | -19.55% | -19.5% | -12.59% | -29.16% | -41.74% | -25.87% | -30.88% | -45.62% | -45.8% | -28.04% | -22.89% | -44.14% | -42.9% | -43.78% | -45.9% | -69.78% | -69.52% | -43.96% | -44.42% | -46.07% | -55.69% | -47.9% | -42.96% | -19.13% | -46.68% | -42.24% | -43.59% | -46.09% | -45.53% | -45.32% | -47.31% | -48.56% | -68.66% | -40.08% | -48.4% | -50.47% | -47.64% | -50.78% | -43.49% | -40.9% | -42.56% | -41.96% | -38.61% | [8 empty] | -100% | -100% | [6 empty] | -45.56% | -46.73% | -45.25% | -44.55% | -5.295% | -5.053% | -5.006% | -5.152% | 8.351% | -17.52% | -34.47% | -2.725% | -45% | -6.577% | 1.356% | -53.78% | -0.8853% | -25.6% | -2.344% | -16.3% | 24.74% | 1.944% | -4.879% | 13.11% | -3.477% | -8.799% | 0.1417% | -5.429% | -100% | -100% | -100% | -100% | 316.3% | 1773% | [6 empty] | -12.43% | -15.22% | -7.635% | -11.71% | -12.41% | -26.54% | -6.904% | -8.694% | 16.79% | 5.917% | -11.9% | 7.039% | 1.807% | 50.58% | -47.11% | 16.16% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -57.96% | 57.58% | 134.9% | 20.56% | -23.25% | -9.33% | 79.43% | 130.2% | -28.94% | -70.95% | -5% | -75.17% | -17.28% | 28.38% | 39.91% | -3.067% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 3.585% | -8.415% | 2.176% | -7.8% | -16.15% | -59.22% | -6.557% | -10.15% | -14.92% | -5.743% | -16.16% | -5.944% | -15.69% | 19.33% | -4.897% | -16.97% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-06-23 | -56.56% | -1.371% | -2.195% | -3.211% | -0.8018% | -0.05633% | -28.73% | -10.74% | 0.1841% | -2.306% | 2.178% | -0.8797% | -0.3855% | 0.7826% | -6.883% | 11.22% | 2.164% | -5.051% | -3.758% | -0.6123% | -3.678% | -1.534% | -14.46% | -1.27% | -8.044% | 0.4466% | -0.9855% | 1.196% | -17.3% | -10.45% | -11.1% | -3.547% | -27.56% | -36.13% | -25.19% | -29.1% | -40.32% | -40.6% | -24.91% | -19.21% | -39.5% | -37.26% | -41.89% | -42.25% | -70.95% | -70.73% | -38.47% | -39.12% | -41.49% | -55.56% | -43.26% | -37.19% | -12.18% | -42.57% | -36.73% | -38.44% | -42.05% | -41.18% | -39.88% | -43.39% | -45.77% | -69.1% | -34.27% | -43.79% | -47.84% | -42.74% | -44.2% | -38.22% | -37.17% | -37.95% | -36.41% | -33.77% | [8 empty] | -100% | -100% | [6 empty] | -40% | -41.3% | -39.72% | -38.89% | -8.346% | -7.865% | -7.784% | -7.994% | 5.557% | -19.86% | -36.66% | -6.15% | -46.24% | -8.621% | -0.7062% | -54.37% | -2.144% | -26.7% | -3.317% | -17.37% | 23.46% | 1.153% | -8.064% | 12.29% | -4.441% | -9.839% | -1.046% | -6.454% | -100% | -100% | -100% | -100% | 305.4% | 1730% | [6 empty] | -13.68% | -16.34% | -8.641% | -13.13% | -13.95% | -27.83% | -8.643% | -10.34% | 12.78% | -1.92% | -14.41% | 3.9% | -1.121% | 46.31% | -49.34% | 12.13% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -60.12% | 51.61% | 125.5% | 15.42% | -26.46% | -12.95% | 71.95% | 122.1% | -30.85% | -68.57% | -7.025% | -75.75% | -20.07% | 24.01% | 35.06% | -8.623% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 1.026% | -11.66% | -1.816% | -11.34% | -19.64% | -60.93% | -8.998% | -12.52% | -16.94% | -7.642% | -18.09% | -9.008% | -18.3% | 14.7% | -8.371% | -20.33% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-06-24 | -42.2% | 34% | 31.82% | 30.85% | 34.7% | 35.7% | 0.7574% | 21.88% | 36.59% | 32.25% | 39.34% | 35.68% | 36.42% | 38.67% | 26.1% | 52.11% | 38.36% | 28.95% | 29.91% | 34.43% | 30.17% | 32.91% | 15.28% | 33.56% | 23.83% | 35.45% | 33.42% | 36.21% | 16.38% | 19.98% | 19.04% | 29.66% | -1.188% | -18.14% | 2.611% | -3.727% | -23.87% | -24.09% | 0.886% | 8.461% | -21.82% | -20.64% | -24.99% | -23.88% | -59.04% | -58.59% | -21.8% | -22.34% | -24.39% | -39.6% | 8.696% | -20.78% | 13.21% | -25.01% | -19.78% | -21.26% | -24.53% | -23.68% | -23.47% | -25.99% | -28.15% | -60.3% | -16.26% | -28.35% | -30.9% | -26.61% | -27% | -21.28% | -17.34% | -19.56% | -18.77% | -14.11% | [8 empty] | -100% | -100% | [6 empty] | -24.78% | -26% | -23.87% | -23.07% | 24.67% | 24.83% | 25.85% | 25.32% | 43.14% | 8.841% | -13.4% | 28.82% | -27.35% | 23.33% | 34.21% | -39.29% | 31.48% | -1.25% | 30.52% | 11.4% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [6 empty] | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -84.61% | -87.18% | -89.47% | -85.71% | 33.44% | 100.6% | -30.11% | 54.8% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-06-25 | -55.4% | 2.534% | 1.67% | 1.108% | -3.7% | -2.357% | -23.73% | -10.19% | 5.14% | 1.384% | 6.868% | -4.286% | -2.914% | 6.53% | -3.096% | 16.67% | 6.08% | -1.016% | 0.05202% | 3.447% | -0.1249% | 1.793% | -11.87% | 2.288% | -2.602% | 3.514% | 2.948% | -7.009% | -11.5% | -17.88% | -8.948% | -1.101% | -25.62% | -37.04% | -21.96% | -27.16% | -41.08% | -41.4% | -23.91% | -18.3% | -39.9% | -37.81% | -42.22% | -42.1% | -68.48% | -68.12% | -39.22% | -39.82% | -41.76% | -53.78% | -43.59% | -37.75% | -12.61% | -42.56% | -37.36% | -39.06% | -41.9% | -41.93% | -40.39% | -43.04% | -45.01% | -70.43% | -34.64% | -44.61% | -47.23% | -42.86% | -43.63% | -38.45% | -36.42% | -37.58% | -36.68% | -33.53% | [8 empty] | -100% | -100% | [6 empty] | -40.74% | -42% | -40.4% | -39.55% | -3.851% | -3.653% | -3.101% | -20.62% | 4.092% | -16.22% | -33.34% | -18.39% | -43.96% | -4.772% | 2.877% | -62.61% | -0.08247% | -24.31% | 0.08392% | -30.83% | 31.13% | 7.492% | -2.628% | 19.25% | 1.183% | -4.552% | 4.997% | -0.5548% | -100% | -100% | -100% | -100% | 323.6% | 1661% | [6 empty] | -17.95% | -13.4% | -5.305% | -9.838% | -9.886% | -25.28% | -5.104% | -12.18% | 21.3% | -6.749% | -39.55% | 11.29% | -15.92% | 56.4% | -54.5% | 20.07% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -68.98% | 45.15% | 82.3% | 21.93% | -24.76% | -8.099% | 81.7% | 91.39% | -27.43% | -77.58% | -11.09% | -77.87% | -16.33% | 22.86% | 42.27% | -26.07% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 5.326% | -3.253% | 5.761% | -4.581% | -13.17% | -57.62% | -2.811% | -4.384% | -12.07% | -1.817% | -12.72% | -2.753% | -12.64% | 23.41% | 0.001493% | -14.14% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-06-26 | -51.17% | 11.37% | 11.33% | 10.69% | 12.26% | 2.017% | -14.04% | 2.209% | -1.811% | -4.624% | -4.438% | -3.149% | -1.496% | 0.6495% | -9.152% | 8.66% | -23.01% | -28.62% | -27.97% | -25.65% | -28.28% | -25.82% | -35.63% | -25.52% | -6.988% | -1.669% | -1.455% | -0.3038% | -14.75% | -12.43% | -11.4% | -3.737% | -25.93% | -35.22% | -22.6% | -26.88% | -39.62% | -39.48% | -22.44% | -16.76% | -37.97% | -36.16% | -40.45% | -40.45% | -70.29% | -70.11% | -37.41% | -34.59% | -39.78% | -56.25% | -41.79% | -36.1% | -10.01% | -40.91% | -35.46% | -36.95% | -40.12% | -34.12% | -38.46% | -37.98% | -44.28% | -72.07% | -32.44% | -42.59% | -46.09% | -40.97% | -42.13% | -36.33% | -34.96% | -35.72% | -34.49% | -31.36% | [8 empty] | -100% | -100% | [6 empty] | -26.9% | -30.96% | -30.85% | -27.26% | -8.482% | -13.96% | -7.401% | -7.663% | 5.348% | -19.27% | -36.36% | -5.675% | -46.15% | -9.132% | -2.085% | -55.99% | -4.548% | -27.72% | -10.07% | -17.57% | 22.74% | 0.5409% | -8.593% | 11.93% | -5.247% | -10.23% | -1.346% | -6.798% | -100% | -100% | -100% | -100% | 304.4% | 1715% | [6 empty] | -14.67% | -17.15% | -10.1% | -14.99% | -15.74% | -29.87% | -10.57% | -11.15% | 35.08% | 3.798% | -33.34% | 23.35% | -6.737% | 73.53% | -49.2% | 33.27% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -70.82% | 51.59% | 127% | 15.95% | -26.74% | -13.35% | 71.99% | 123.2% | -32.92% | -72.23% | -5.902% | -78.94% | -28.4% | 24.72% | 35.16% | -11.3% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 0.3387% | -6.983% | 0.4737% | -9.592% | -21.48% | -59.65% | -6.776% | -7.982% | -16.58% | -5.714% | -16.76% | -7.294% | -16.82% | 17.44% | -4.054% | -21.47% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-06-27 | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 17.04% | 13.31% | 18.77% | 13.93% | 15.21% | 13.98% | 1.87% | 29.64% | 1.076% | -6.366% | -5.027% | -2.124% | -5.25% | -3.151% | -28.68% | -2.887% | 8.004% | 15.01% | 14.71% | 15.12% | -1.85% | 0.08552% | 0.9512% | 10.57% | -13.66% | -16.3% | -8.822% | 19.73% | -22.65% | -21.18% | -7.371% | -0.1131% | -23.3% | -17.85% | -24.89% | -27.9% | -60.86% | -66.16% | -45.05% | 5.705% | -24.98% | -48.73% | -26.77% | -16.63% | 13.56% | -95.85% | -16.84% | -20.39% | -96.94% | -26.8% | -96.66% | -30.19% | -36.43% | -69.31% | -15.01% | -30.14% | -36.23% | -37.04% | -31.15% | -22.59% | -23.46% | -23.35% | -19.47% | -17.09% | [8 empty] | -100% | -100% | [6 empty] | -100% | -100% | -100% | -100% | -22.26% | -21.92% | -21.46% | -22% | -9.98% | -32.17% | -46.87% | -20.63% | -38.69% | 2.91% | 7.645% | -49.46% | 11.64% | -15.4% | 11.98% | -6.02% | 2.042% | -16.55% | -24.63% | -7.462% | -21.47% | -25.65% | -18.1% | -22.5% | -100% | -100% | -100% | -100% | 238% | 1418% | [6 empty] | -29.17% | -31.69% | -24.8% | -29.61% | -29.25% | -41.22% | -25.46% | -25.93% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -84.18% | 26.04% | 87.76% | -4.762% | -41.49% | -30.97% | 40.83% | 84.99% | -44.89% | -78.07% | -49.88% | -83.47% | -41.56% | 4.193% | 13.04% | -26.06% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -32.78% | -37.76% | -30.95% | -37.73% | -44.38% | -72.61% | -37.68% | -38.63% | -30.74% | -21.21% | -30.12% | -21.59% | -30.29% | -1.232% | -20.99% | -47.18% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-06-28 | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 36.58% | 30.25% | 35.83% | 29.51% | 34.45% | 36.69% | 26.76% | 39.66% | 33.75% | 25.04% | 22.82% | 30.89% | 26.69% | 29.17% | 12.45% | 28.51% | -37.5% | -34.38% | -41.56% | -33.36% | -42.5% | -41.18% | -40.51% | -42.07% | -7.843% | -19.97% | -0.7295% | -8.832% | -26.05% | -25.37% | -5.485% | 2.824% | -24.24% | -21.58% | -27.54% | -27.43% | -59.83% | -59.01% | -23.26% | -23.98% | -27.03% | -44.81% | -29.06% | -21.47% | 9.226% | -28.44% | -21.21% | -23.29% | -61.98% | -43.06% | -27.69% | -38.54% | -34.11% | -63.82% | -17.51% | -31.44% | -31.18% | -28.26% | -30.31% | -23.32% | -21.71% | -23.31% | -20.9% | -17.94% | [8 empty] | -100% | -100% | [6 empty] | -100% | -100% | -100% | -100% | -64.45% | -64.39% | -64.01% | -64.55% | -59.1% | -69.23% | -75.74% | -63.59% | -29.02% | 18.16% | 24.78% | -40.25% | 28.31% | -2.835% | 26.67% | 6.999% | -46.03% | -55.91% | -59.71% | -50.44% | -57.99% | -60.24% | -56.65% | -59.33% | -100% | -100% | -100% | -100% | 116.3% | 1077% | [6 empty] | 20.14% | 16.2% | 27.4% | 22.37% | 20.44% | -0.5815% | 25.68% | 23.94% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -60.69% | 103.6% | 201.6% | -46.91% | -3.964% | 13.84% | 130.8% | 157.7% | -12.47% | -64.33% | 21.47% | -83.61% | -6.683% | 63.89% | 80.49% | 4.603% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 10.75% | 25.61% | 12.36% | 25.64% | 11.53% | 57.81% | 25.68% | 2.553% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-06-29 | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -30.05% | -30.67% | -29.49% | -30.51% | -36.04% | -34.96% | -24.14% | -17.99% | -33.65% | -29.01% | -35.85% | -37.72% | -73.49% | -73.16% | -30.87% | -32.03% | -38.35% | -61.52% | -39.8% | -31.56% | -6.514% | -37.75% | -31.64% | -34.53% | -48.79% | -39.77% | -39.19% | -43.64% | -50.36% | -77.48% | -30.38% | -43.05% | -49.6% | -40.51% | -44.85% | -37.43% | -39.55% | -38.73% | -34.58% | -33.09% | [8 empty] | -100% | -100% | [6 empty] | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -15.01% | -30.27% | -36.68% | -22.73% | -34.93% | -38.66% | -31.93% | -35.43% | -100% | -100% | -100% | -100% | 284.3% | 1678% | [6 empty] | -21.83% | -25.85% | -15.32% | -16.52% | -21.9% | -31.07% | -12.53% | -19.67% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -22.22% | -11.9% | -21.8% | -13.48% | -23.25% | 8.36% | -12.87% | -38.53% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-06-30 | -55.2% | 0.2418% | 0.1826% | -15.4% | 0.659% | -100% | -23.31% | -10.23% | 3.277% | 0.08229% | 4.73% | 0.6878% | 2.843% | 6.812% | -3.767% | 14.31% | 2.455% | -5.202% | -3.97% | -0.7706% | -3.647% | -1.084% | -14.53% | -1.678% | -3.699% | -0.538% | -1.056% | 0.5174% | -13.17% | -15.58% | -11.55% | -3.604% | -22.58% | -16.14% | -21.94% | -24.32% | -24.62% | -22.32% | -13.64% | -5.871% | -20.79% | -10.8% | -23.38% | -27.28% | -69.72% | -69.52% | -16.81% | -18.23% | -25.53% | -54.44% | -26.76% | -15.18% | 14.35% | -27.15% | -16.22% | -19.48% | -28.69% | -25.64% | -24.19% | -30.71% | -40.52% | -72.64% | -12.84% | -32.71% | -40.41% | -27.17% | -34.02% | -24.5% | -28.59% | -24.5% | -20.71% | -19.45% | [8 empty] | -100% | -100% | [6 empty] | -68.39% | -96.4% | -96.13% | -95.93% | -5.061% | -4.39% | -3.793% | -20.55% | 9.514% | -16.46% | -33.75% | -2.361% | -44.58% | -8.426% | -3.242% | -53.01% | 0.5241% | -24.28% | -0.6773% | -16.52% | 14.76% | -6.797% | -14.84% | 5.078% | -10.51% | -15.55% | -6.666% | -11.76% | -100% | -100% | -100% | -100% | 264.2% | 1544% | [6 empty] | -23.02% | -26.06% | -17.44% | -19.31% | -21.33% | -33.08% | -15.73% | -19.42% | 16.98% | -11.37% | -41.76% | 6.894% | -19.38% | 49.56% | -56.15% | 15.58% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -68.78% | 57.35% | 132.9% | -1.936% | -25.84% | -12.66% | 76.76% | 126.6% | -30.49% | -70.72% | -3.823% | -79.85% | -25.77% | 28.26% | 40.78% | -7.505% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -6.186% | -45.19% | -30.41% | -80.56% | -85.18% | -52.93% | -57.67% | -44.53% | -100% | -100% | -100% | -100% | -100% | -100% | -73.98% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -20.27% | -9.619% | -19.61% | -8.877% | -18.23% | 16.55% | -7.058% | -7.059% | -84.16% | -100% | -100% | -100% | -100% | -100% | -88.86% | -83.48% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-07-01 | -57.64% | -6.606% | -5.095% | -11.28% | -10.04% | -100% | -27.92% | -17.1% | -6.539% | -8.927% | -6.059% | -10.4% | -7.966% | 0.1392% | -9.891% | 1.08% | -6.531% | -12.73% | -10.55% | -6.999% | -10.23% | -9.44% | -22.71% | -11.45% | -11.57% | -8.57% | -8.693% | -7.194% | -19.2% | -19.3% | -15.45% | -9.011% | -17.53% | -10.18% | -21.63% | -20.95% | -17.15% | -14.57% | -11.62% | -4.18% | -71.69% | -70.73% | -14.09% | -12.24% | -18.36% | -9.598% | -18.6% | -27.76% | -21.63% | -56.02% | -22.73% | -7.11% | 20.42% | -23.82% | -8.893% | -14.81% | -27.94% | -24.37% | -21.78% | -29.83% | -41.6% | -74.22% | -9.41% | -21.33% | -40.26% | -23.35% | -33.36% | -20.66% | -26.3% | -23.89% | -15.23% | -15.64% | [8 empty] | -100% | -100% | [6 empty] | -10.86% | -19.21% | -13.22% | -10.01% | -15.18% | -14.34% | -14.61% | -27.27% | -3.533% | -23.32% | -39.03% | -12.88% | -48.81% | -17.18% | -11.97% | -56.84% | -8.752% | -30.75% | -11.52% | -23.97% | 13.14% | -7.538% | -15.02% | 2.399% | -13.7% | -16.26% | -8.659% | -13.47% | -100% | -100% | -100% | -100% | 278.6% | 1607% | [6 empty] | -19.21% | -20.71% | -15.81% | -18.06% | -19.31% | -30.2% | -12.72% | -15.21% | 4.257% | -17.5% | -45.34% | -3.395% | -23.23% | 38% | -58.37% | 3.226% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -70.78% | 42.08% | 111.6% | -8.493% | -30.94% | -18.55% | 65.16% | 105.2% | -36.16% | -73.18% | -14.29% | -81.41% | -30.92% | 14.95% | 27.41% | -16.78% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -22.78% | -56.58% | -36.75% | -82.22% | -86.42% | -56.92% | -61.18% | -49.37% | -100% | -100% | -100% | -100% | -100% | -100% | -75.79% | -99.69% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -22.88% | -12.82% | -22.43% | -12.97% | -22.34% | 10.04% | -12.2% | -28.52% | -85.63% | -100% | -100% | -100% | -100% | -100% | -100% | -91.37% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -100% | -100% | -100% | -100% |  |  |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-07-02 | -58.6% | -1.458% | -5.341% | -6.537% | -3.744% | -100% | -27.68% | -14.57% | -1.645% | -4.274% | 0.3618% | -3.891% | -3.262% | 0.4355% | -11.87% | 9.064% | -100% | -100% | -100% | -100% | -5.013% | -2.79% | -16.68% | -3.997% | -7.978% | -2.15% | -2.144% | -1.715% | -15.74% | -17.67% | -14.18% | -7.011% | -21.21% | -5.743% | -21.83% | -20.88% | -13.23% | -9.905% | -10.64% | -3.533% | -72.12% | -71.3% | -9.062% | -7.709% | -15.63% | -3.241% | -15.35% | -26.32% | -18.8% | -55.69% | -19.48% | -0.7457% | 24.54% | -22.31% | -3.501% | -10.97% | -26.58% | -21.66% | -19.31% | -28.92% | -41.08% | -74.72% | -4.954% | -25.35% | -38.57% | -20.08% | -32.15% | -18.22% | -24.76% | -22.4% | -12.4% | -15.62% | [8 empty] | -64.3% | -60.85% | [6 empty] | -4.896% | -15.91% | -8.283% | -4.146% | -10.3% | -9.901% | -9.437% | -25.38% | 3.642% | -21.96% | -38.44% | -7.769% | -48.12% | -13.47% | -9.334% | -56.36% | -4.976% | -29.1% | -8.9% | -21.2% | 19.63% | -2.064% | -11.24% | 9.113% | -9.389% | -12.38% | -2.886% | -8.488% | -100% | -93.39% | -100% | -100% | 294.5% | 1679% | [6 empty] | -15.93% | -18.79% | -11.03% | -15.43% | -15.94% | -29.59% | -10.96% | -12.44% | 10.97% | -16.77% | -45.55% | 1.941% | -23.71% | 42.92% | -60.18% | 10.3% | -100% | -100% | -100% | -94.69% | -94.59% | -96.57% | -100% | -100% | -72.73% | 49.25% | 121.4% | -7.249% | -29.93% | -17.51% | 67.12% | 119.6% | -35.22% | -73.42% | -9.154% | -81.96% | -30.32% | 21.77% | 32.67% | -13.15% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -76.73% | -100% | -39.96% | -36.89% | -38.33% |  | -100% | -100% | -29.77% | -100% | -35.93% | -83.06% | -87.15% | -56.75% | -61.45% | -48.68% | -100% | -88.33% | -100% | -100% | -100% | -100% | -76.45% | -68.9% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -20.77% | -100% | -100% | -10.75% | -20.41% | 12.89% | -9.691% | -28.59% | -86.52% | -100% | -100% | -100% | -100% | -100% | -100% | -92.56% | -47.45% | -100% | -100% | -100% | -100% | -68.03% | -52.96% | -66.88% | -60.01% | -57.73% | -52.08% | -40.92% | 106.2% |  | -100% | -100% | -29.68% | -39.94% | -36.32% | -100% | -70.25% | -69.68% | -49.46% | -35.13% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -54.66% | -57.66% | -49.5% | 116.3% |  |  |  | 123.5% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 16.22% | -42.19% | -45.38% | 4.2% | -60.8% | -81.38% | -50.34% | -58.49% | -100% | -100% | -100% | -100% | -89.03% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -42.38% | -27.57% | -22.15% | -28.14% | -40.17% | -3.548% | -39.21% | -43.28% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-07-03 | -52.4% | -1.566% | 1.112% | -9.311% | -8.315% | -78.11% | -25.41% | -14.19% | -3.713% | -5.939% | -3.596% | -8.073% | -7.292% | 6.945% | 1.015% | 3.3% | -19.35% | -13.28% | -10.81% | -9.811% | -8.53% | -6.396% | -17.28% | -7.742% | -9.061% | -7.079% | -6.502% | -4.792% | -16.77% | -14.75% | -11.22% | -5.003% | -14.98% | -7.421% | -14.31% | -14.46% | -14.62% | -12.36% | -5.472% | 2.007% | -68.25% | -67.22% | -12.83% | -9.244% | -15.05% | -6.743% | -15.8% | -24.14% | -18.65% | -51.53% | -20.21% | -5.148% | 23.84% | -21.54% | -5.894% | -11.71% | -24.45% | -17% | -18.95% | -26.39% | -36.96% | -71.21% | -4.44% | -22.06% | -33.53% | -17.98% | -29.22% | -16.36% | -20.71% | -19.31% | -12.59% | -14.11% | [8 empty] | -4.113% | 6.259% | [6 empty] | -8.498% | -16.69% | -10.54% | -7.49% | -13.34% | -11.99% | -12.87% | -24.11% | -1.49% | -8.717% | -35.25% | -11.19% | -44.26% | -14.36% | -8.192% | -52.36% | -6.046% | -26.83% | -10.7% | -20.95% | 13.92% | -7.111% | -13.57% | 3.162% | -11.74% | -14.3% | -7.356% | -12.32% | -100% | -82.85% | -100% | -100% | 278% | 1614% | [6 empty] | -18.11% | -18.92% | -15.09% | -16.46% | -17.67% | -4.963% | -10.05% | -13.4% | 6.548% | -13.71% | -41.18% | -1.898% | -17.65% | 40.5% | -53.75% | 5.187% | -100% | -100% | -100% | -86.44% | -86.23% | -88.3% | -100% | -100% | -67.44% | 46.01% | 115.5% | -2.948% | -25.77% | -12.54% | 76.66% | 107.4% | -30.77% | -69.48% | -12.06% | -79.29% | -23.82% | 17.1% | 31.49% | -13.74% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -15.72% | -100% | 26.72% | 46.92% | 23.27% |  | -100% | -100% | -36.8% | -61.61% | -30.43% | -80.42% | -85.08% | -52.38% | -57.04% | -44.58% | -96.65% | -86.42% | -100% | -100% | -100% | -100% | -73.32% | -65.51% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -12.56% | -23.06% | -31.75% | -1.035% | -11.55% | 25.19% | -0.4807% | -22.69% | -84.29% | -100% | -100% | -100% | -100% | -100% | -100% | -90.69% | -0.927% | -100% | -100% | -100% | -100% | -36.51% | -10.68% | -33.18% | -18.31% | -17.67% | -6.761% | 12.73% | 332.3% |  | -100% | -100% | 24.33% | 5.868% | 11.66% | -100% | -42.49% | -40.3% | -9.542% | 14.29% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -28.89% | -32.11% | -21.85% | 238.6% |  |  |  | 245.7% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 84.67% | -6.051% | -17.07% | 66.13% | -38.34% | -67.88% | -22.64% | -33.12% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -17.18% | 0.0626% | 4.867% | -3.453% | -15.43% | 34.93% | -15.69% | -18.78% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-07-04 | -58.96% | 1.706% | 3.797% | -2.817% | -1.653% | -87.6% | -22.98% | -37.93% | 1.773% | -28.04% | 1.151% | -3.201% | -4.988% | 9.571% | -13.17% | 9.908% | -15.06% | -6.841% | -0.6074% | 2.121% | -0.7031% | 1.283% | -12.02% | 0.2585% | -3.765% | 0.6257% | 0.9529% | 2.028% | -12.81% | -14.83% | -13.09% | -2.232% | -15.61% | -1.706% | -13.23% | -13.68% | -11.07% | -7.836% | -5.029% | 3.914% | -75.18% | -73.9% | -9.618% | -6.233% | -13.64% | -3.085% | -13.25% | -22.82% | -17.12% | -52.99% | -16.18% | 0.1564% | 28.33% | -20.11% | -3.685% | -11.56% | -21.72% | -16.1% | -17.22% | -24.62% | -36.54% | -79.55% | 1.915% | -18.61% | -31.73% | 6.284% | -25.88% | -11.67% | -17.8% | -17.54% | -5.015% | -11.53% | [8 empty] | -26.44% | -36.17% | [6 empty] | -35.97% | -42.97% | -35.06% | -43.09% | -7.784% | -5.753% | -5.741% | -21.17% | 5.38% | -15.98% | -33.07% | -6.917% | -42.3% | -9.111% | -3.983% | -52.05% | -1.325% | -24.68% | -5.812% | -20.03% | 22.43% | -2.414% | -7.886% | 12.84% | -6.764% | -9.891% | -0.9794% | -7.574% | -100% | -84.93% | -100% | -100% | 283.4% | 1642% | [6 empty] | -13.8% | -16.42% | -10.52% | -13.15% | -14.62% | -28.37% | -9.806% | -16.4% | 13.35% | -9.267% | -39.17% | 3.493% | -14.83% | 51.31% | -66.55% | 12.46% | -100% | -100% | -100% | -89.03% | -89.2% | -91.49% | -100% | -100% | -81.87% | 50.85% | 123.1% | -3.178% | -27.26% | -15.64% | 39.32% | 53.52% | -56.45% | -81.11% | -38.92% | -85.62% | -49.65% | -16.21% | -2.957% | -41.72% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -42.6% | -100% | -15.69% | 33.9% | -13.74% |  | -100% | -100% | -58.44% | -69.53% | -52.29% | -83.84% | -83.84% | -63.68% | -71.25% | -60.62% | -97.52% | -88.82% | -100% | -100% | -100% | -100% | -84.23% | -72.16% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -36.78% | -45.53% | -56.23% | -32.57% | -37.21% | -15.63% | -29.34% | -44.3% | -87.88% | -100% | -100% | -100% | -100% | -100% | -100% | -96.74% | -32.44% | -100% | -100% | -100% | -100% | -53.31% | -39.63% | -55.26% | -46.71% | -51.56% | -35.72% | -24.35% | 228.3% |  | -100% | -100% | -4.098% | -28.23% | -19.51% | -100% | -61.74% | -64.59% | -40.05% | -23.57% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -45.79% | -55.54% | -43.25% | 116.4% |  |  |  | 141.9% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 17.61% | -27.31% | -39.21% | 22.96% | -59.75% | -75.96% | -48.72% | -61.95% | -100% | -100% | -100% | -100% | -87.39% | -100% | -100% | -100% | -100% | -100% |  | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -39.41% | -29.17% | -24.87% | -31.08% | -41.2% | 4.468% | -41.21% | -37.87% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-07-05 | -46.57% | -4.463% | -0.1192% | -9.484% | -8.07% | -6.439% | -26.33% | -15.61% | -4.321% | -6.729% | -3.797% | -8.604% | -9.117% | 5.864% | 14.05% | 2.39% | -18.17% | -10.86% | -8.216% | -6.443% | -8.022% | -5.866% | -17.43% | -7.227% | -10.93% | -6.943% | -6.534% | -5.123% | -17.6% | -16.42% | -15.08% | -6.532% | -14.79% | -9.823% | -16.44% | -15.79% | -16.46% | -9.889% | -6.361% | 0.6306% | -62.68% | -62.38% | -15.28% | -11.23% | -17.04% | -8.354% | -17.24% | -25.5% | -19.51% | -49.77% | -22.17% | -6.958% | 21.2% | -22.52% | -7.547% | -13.41% | -25.49% | -20.46% | -20.65% | -26.51% | -36.11% | -64.17% | -6.277% | -24.04% | -35.14% | -22.1% | -31.4% | -18.72% | -21.86% | -20.55% | -13.66% | -15.52% | [8 empty] | -45.89% | -28.26% | [6 empty] | 41.4% | 23.47% | 36.35% | 41.66% | -15.51% | -14.53% | -15.12% | -27.45% | -4.137% | -21.77% | -36.04% | -12.66% | -44.62% | -17.14% | -10.3% | -50.04% | -7.419% | -28.72% | -13.07% | -26.75% | 7.257% | -13.75% | -18.76% | -1.485% | -16.85% | -20.49% | -8.507% | -18.2% | -100% | -100% | -100% | -100% | 258.6% | 1524% | [6 empty] | -22.92% | -23.87% | -20.64% | -21.91% | -23.64% | -30.12% | -14.95% | -18.03% | 5.816% | -16.03% | -42.01% | -1.976% | -16.87% | 47.56% | -43.43% | 5.654% | -100% | -100% | -100% | -92.08% | -78.23% | -83.03% | -100% | -100% | -59.7% | 41.53% | 110.1% | -4.334% | -25.38% | -11.22% | 78.34% | 103.7% | -31.07% | -63.93% | -16.74% | -72.62% | -24.01% | 19.15% | 27.56% | -18.03% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -9.918% | -30.78% | 22.79% | 67.3% | 18.27% |  | 20.48% | 25.9% | -24.98% | -34.17% | -26.46% | -72.09% | -78.8% | -47.32% | -47.8% | -42.79% | -93.6% | -80.7% | -100% | -100% | -100% | -100% | -64.49% | -60.78% | -55.46% | -54.64% | -50.79% | -52.04% | -100% | -100% | -100% | -100% | -1.255% | 8.798% | -2.545% | 7.874% | -4.057% | 35.64% | 8.944% | -11.77% | -78.65% | -100% | -100% | -100% | -100% | -100% | -100% | -86.74% | -3.011% | -100% | -100% | -100% | -100% | -35.92% | -12.76% | -33.31% | -16.72% | -41.32% | -8.371% | 6.724% | 471.3% |  | 15.92% | -34.69% | 3.72% | -10.58% | -5.641% | -100% | -42.83% | -40.01% | -13.15% | 11.17% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | 11.39% | 4.374% | 23.83% | 431.3% |  |  |  | 444.2% | -49.19% | 15.07% | 19.1% | -49.18% | 56.11% | 34.5% | 17.75% | 42.73% | 91.12% | -2.848% | -17.99% | 71.88% | -57.72% | -57.51% | -2.297% | -22.99% | 26.81% | -0.07142% | -100% | -12.37% | -74.12% | -100% | -100% | -100% | 15.3% | 3.469% |  | 27.32% | 54.25% | 32.44% | 8.683% | 1.27% | 66.05% | 154% | -16.99% | 51.9% | 83.24% | -100% | 83.91% | 125.6% | 28.16% | 60.76% | 74.15% | 59.21% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-07-06 | -42.93% | -4.415% | 2.321% | -11.38% | -10.62% | -7.654% | -24.47% | -16.21% | -6.055% | -8.759% | -6.393% | -10.92% | -9.901% | 8.79% | 22.08% | 0.6483% | -19.24% | -13.28% | -10.67% | -9.244% | -10.46% | -8.75% | -18.94% | -9.452% | -11.67% | -9.447% | -9.639% | -7.841% | -19.63% | -16.82% | -16.55% | -6.676% | -11.82% | -10.54% | -9.414% | -13.4% | -17.16% | -15.01% | -4.658% | 2.67% | -61.06% | -60.42% | -15.83% | -11.76% | -17.14% | -10.11% | -17.6% | -25.15% | -20.01% | -47.9% | -21.95% | -8.243% | 21.34% | -22.2% | -9.255% | -14.54% | -24.47% | -19.92% | -21.11% | -25.85% | -35.23% | -62.6% | -6.351% | -30.55% | -32.64% | -21.07% | -29.8% | -17.89% | -20.9% | -21.9% | -14.26% | -14.87% | [8 empty] | 4.552% | 33.49% | [6 empty] | -13.49% | -20.58% | -13.1% | -11.26% | -15.91% | -14.31% | -15.2% | -26.36% | -3.48% | -19.76% | -34.08% | -12.94% | -41.87% | -16.2% | -9.011% | -47.56% | -7.97% | -27.22% | -13.36% | -24.98% | 10.02% | -10.37% | -15.42% | 0.8018% | -14.37% | -18.86% | -10.4% | -14.76% | -100% | -78.9% | -100% | -100% | 274.7% | 1591% | [6 empty] | -19.36% | -21.53% | -17.22% | -17.86% | -20.61% | -26.02% | -10.6% | -14.25% | 2.411% | -15.81% | -41.03% | -5.473% | -16.15% | 37.29% | -41.28% | 1.539% | -100% | -100% | -100% | -58.43% | -49.12% | -83.96% | -100% | -100% | -58.94% | 41.86% | 85.74% | -1.152% | -22.16% | -7.177% | 85.27% | 104.2% | -28.56% | -62.52% | -17.58% | -73.15% | -29.9% | 11.69% | 28.16% | -17.69% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -9.508% | -28.89% | 25.64% | 67.85% | 21.97% |  | 26.08% | 29.49% | -78.45% | -31.4% | -79.6% | -74.03% | -80.21% | -44.15% | -46.06% | -39.67% | -94.09% | -81.95% | -98.03% | -100% | -100% | -100% | -17.7% | -59.12% | -25.41% | -24.24% | -18.44% | -19.39% | -100% | -100% | -100% | -100% | -18.3% | -14.24% | -22% | -16.06% | -25.91% | 5.544% | -14.03% | -26.62% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -1.994% | -100% | -100% | -100% | -100% | -33.15% | -11.15% | -31.46% | -5.876% | -100% | -4.913% | 13.44% | 593.2% |  | 20.79% | -30.58% | 22.57% | 4.118% | 10.69% | -100% | -39.53% | -35.21% | -10.5% | 12.73% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | 6.79% | 0.2752% | 19.32% | 408.5% |  |  |  | 416.5% | -50.89% | 19.73% | 30.81% | -51% | 51.46% | 30.49% | 13.77% | 38.3% | 105.1% | 4.358% | -11.76% | 86.88% | -28.91% | -16.72% | 4.581% | -19.85% | 22.78% | -4.05% | -100% | 6.081% | -73.72% | -100% | -100% | -100% | 11.28% | 0.1398% |  | 21.72% | 45.23% | 24.13% | 2.227% | -4.62% | 58.29% | 146.2% | -19.64% | 46.02% | 74.53% | 3.856% | 73.03% | 112.9% | -0.283% | 20.24% | 27.47% | 16.53% | 2.564% | 63.19% | 1.534% | -1.793% | -49.27% | -100% | -50.87% | -3.31% | 41.99% | 14.56% | -45.68% | 32.45% | 380.3% | 15.81% | 280% | 26.15% | -84.51% | -2.765% | 153.4% | 45.47% | 28.3% | 80.59% | 27.15% | 32.37% | 108.2% | 27.76% | 31.68% | 71.16% | 8.447% | 17.36% | 1.312% | -55.22% | -22.51% | -35.43% | -95.7% | -78.48% | -19.9% | -52.46% | -72.84% | 63.7% | 1.647% | 4.966% | 16.9% | 26.12% | 26.74% | 189.9% | 90.49% | 4.323% | -53.85% | -100% | -54.84% | 6.64%
2025-07-07 | -41.26% | -2.785% | 5.366% | -10.8% | -10.6% | -6.87% | -22.44% | -14.93% | -5.031% | -8.256% | -6.475% | -10.78% | -9.092% | 11.95% | 27% | 0.7159% | -18.95% | -13.73% | -10.3% | -9.549% | -11.39% | -9.261% | -18.41% | -10.04% | -9.991% | -9.407% | -9.324% | -6.633% | -17.56% | -13.52% | -11.11% | -3.88% | -8.193% | -8.458% | -5.867% | -10.47% | -15.8% | -13.78% | -1.638% | 6.174% | -59.56% | -58.39% | -14.72% | -10.64% | -15.78% | -9.918% | -16.85% | -23.53% | -19.65% | -46.21% | -22.29% | -9.336% | 21.98% | -20.61% | -8.729% | -13.94% | -23.81% | -19.94% | -21.05% | -25.05% | -33.23% | -62.97% | -6.508% | -24.37% | -30.5% | -20.37% | -28.29% | -15.65% | -17.16% | -18.11% | -11.77% | -12.01% | [8 empty] | 7.783% | 37.28% | [6 empty] | -11.67% | -18.91% | -12% | -9.881% | -16.77% | -14.93% | -16.03% | -25.65% | -15.24% | -16.85% | -18.12% | -23.84% | -40.08% | -16.11% | -7.507% | -44.77% | -5.551% | -25.16% | -12.8% | -23.84% | 11.9% | -8.728% | -13.51% | 2.673% | -11.93% | -16.04% | -8.081% | -12.26% | -100% | -78.11% | -100% | -100% | 282.4% | 1624% | [6 empty] | -16.69% | -18.49% | -14.78% | -14.75% | -17.65% | -22.53% | -7.663% | -11.73% | 5.199% | -11.79% | -37.5% | -2.567% | -11.76% | 47.64% | -41.11% | 3.92% | -82.77% | -100% | -100% | -51.86% | -43.52% | -78.23% | -93.94% | -93.03% | -58.47% | 41.79% | 89.1% | 1.873% | -20.69% | -4.016% | 91.05% | 104.1% | -26.14% | -61% | -16.88% | -72.97% | -26.19% | 11.98% | 28.82% | -17.06% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -7.887% | -26.4% | 29.5% | 69.98% | 24.8% |  | 28.9% | 34.93% | -22.81% | -25.23% | -20.06% | -73.1% | -79.47% | -39.83% | -42.76% | -35.56% | -94.09% | -81.81% | -74.67% | -100% | -100% | -100% | -64.69% | -52.44% | -23.21% | -23.7% | -18.99% | -18.82% | -100% | -100% | -100% | -100% | -15.8% | -12.97% | -20.39% | -15.54% | -26.07% | 5.319% | -13.39% | -24.65% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 0.6896% | -100% | -100% | -100% | -100% | -29.97% | -9.329% | -28.01% | -1.078% | -83.17% | -1.466% | 16.95% | 606.3% |  | 22.6% | -27.19% | 25.19% | 5.254% | 12.22% | -100% | -36.91% | -32.21% | -8.657% | 13.04% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -22.13% | -22.97% | -15.16% | 262.4% |  |  |  | 269.8% | -50.99% | -5.911% | -6.234% | -50.96% | 0.3069% | -11.46% | -16.99% | -3.189% | 158.1% | 9.07% | -2.948% | 135.5% | -21.68% | -13.5% | 6.511% | -16.79% | 18.34% | -7.148% | -100% | 2.403% | -74.77% | -100% | -100% | -100% | -13.77% | -6.615% |  | -11.1% | 11.58% | 1.314% | -22.07% | -19.97% | 17.78% | 82.59% | -31.58% | 2.506% | 21.43% | -2.146% | 20.65% | 49.83% | -7.96% | 6.826% | 11.51% | 1.534% | -8.529% | 44.24% | -10.66% | -11.6% | -49.56% | -100% | -50.68% | -25.67% | -1.018% | -12.3% | -48.2% | -3.191% | 235.8% | -6.77% | 162.8% | 1.794% | -83.84% | -25.18% | 84.01% | 6.811% | -9.483% | 24.23% | -9.943% | -10.58% | 85.15% | 12.62% | -4.826% | 14.74% | -19.23% | -15.51% | -25.7% | -55.24% | -37.17% | -43.23% | -95.46% | -77.84% | -21.67% | -49.57% | -69.63% | 7.118% | -18.56% | -19.18% | -18.94% | -12.98% | -7.219% | 109.5% | 35.79% | -25.02% | -52.94% | -100% | -54.03% | -15.79%
2025-07-08 | -49.38% | -2.196% | 5.284% | -9.633% | -9.403% | -6.058% | -22.78% | -14.25% | -4.071% | -6.205% | -4.452% | -9.304% | -8.236% | 11.72% | 9.446% | 1.609% | -16.7% | -11.48% | -8.537% | -7.676% | -9.187% | -6.97% | -16.63% | -7.569% | -8.654% | -7.601% | -7.861% | -5.837% | -17.05% | -13.62% | -12.38% | -3.002% | -10.1% | -8.828% | -9.382% | -12.07% | -15.32% | -13.06% | -1.265% | 5.834% | -64.88% | -64.32% | -13.9% | -9.956% | -1.279% | -25.57% | -29.59% | -10.59% | -17.46% | -48.24% | -19.41% | -6.104% | 25.91% | -19.13% | -7.024% | -11.93% | -21.74% | -17.26% | -18.46% | -23.23% | -33.29% | -67.8% | -3.635% | -21.8% | -29.57% | -18.4% | -26.82% | -13.84% | -16.81% | -17.35% | -10.38% | -10.44% | [8 empty] | 2.064% | 30.4% | [6 empty] | -12.3% | -19.09% | -12.04% | -10.3% | -13.61% | -11.78% | -13.01% | -22.93% | -1.279% | -15.24% | -31.31% | -12.77% | -39.61% | -13.26% | -9.408% | -47.1% | -3.62% | -23.67% | -10.67% | -23.24% | 11.42% | -10.69% | -15.43% | -2.046% | -13.76% | -15.78% | -10.11% | -14.37% | -100% | -81.19% | -100% | -100% | 282.1% | 1401% | [6 empty] | -18.84% | -19.91% | -16.55% | -16.69% | -19.45% | -24.24% | -9.573% | -13.49% | 3.631% | -13.62% | -40.88% | -4.222% | -14.94% | 38.82% | -51.15% | 2.485% | -27.49% | -35.76% | -57.16% | -41.7% | -33.11% | 104.9% | -66.02% | -53.58% | -63.7% | 45.91% | 93.41% | 3.109% | -20.78% | -4.331% | 91.47% | 108.5% | -25.54% | -65.51% | -15.41% | -76.18% | -32.77% | 14.91% | 32.34% | -14.82% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -8.666% | -26.84% | 29.48% | 68.74% | 23.21% |  | 8.144% | 32.5% | -70.89% | -35.31% | -21.05% | -77.24% | -82.58% | -45.17% | -50.02% | -38.08% | -95.1% | -84.31% | -78.11% | -100% | -100% | -100% | -69.57% | -52.96% | -21.16% | -21.19% | -15.73% | -17.27% | -100% | -100% | -100% | -100% | -15.91% | -13.05% | -20.53% | -15.05% | -24.89% | 7.255% | -11.79% | -24.12% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 1.595% | -100% | -100% | -100% | -100% | -32.09% | -11.65% | -30.67% | -2.817% | -11.39% | -0.5448% | 18.02% | 606.2% |  | 22.62% | -27.74% | 26.17% | 6.951% | 13.43% | -100% | -38.42% | -35.89% | -9.004% | 12.48% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -21.94% | -23.51% | -14.81% | 265.1% |  |  |  | 269.1% | -58.63% | -1.33% | -5.809% | -58.79% | 1.336% | -10.86% | -16.65% | -2.309% | 109.5% | 3.743% | -3.608% | 133.2% | -22.57% | -14.8% | 5.376% | -17.73% | 3.205% | -19.29% | -100% | -10.41% | -78.36% | -100% | -100% | -100% | -15.62% | -22.62% |  | -10.92% | 9.246% | -1.981% | -23.89% | -23.47% | 16.03% | 80.74% | -35.31% | 1.251% | 19.66% | -5.7% | 18% | 47.23% | -8.313% | 6.896% | 11.21% | 1.5% | -8.454% | 45.11% | -9.798% | -10.98% | -57.28% | -46.84% | -24.26% | -26.05% | -0.4297% | -11.44% | -54.4% | -3.719% | 236.7% | -8.671% | 164.7% | 0.1762% | -87.45% | -21.71% | 84.5% | 6.025% | -8.534% | 26.58% | -8.603% | -9.4% | 75.02% | -0.7896% | -5.039% | 15.48% | -18.76% | -14.9% | -25.16% | -61.21% | -38.21% | -46.28% | -96.73% | -81.61% | -0.9863% | -33.51% | -75.15% | 7.96% | -20.18% | -19.69% | -18.29% | -12.46% | -6.9% | 110.5% | 36.01% | -24.72% | -61.25% | -100% | -62.08% | -16.79%
2025-07-09 | -59.03% | -5.826% | 22.92% | 20.68% | -7.537% | -4.278% | -9.826% | 9.917% | -4.124% | -8.177% | 29.7% | 24.61% | -6.34% | 0.1627% | 17.35% | 41.23% | -41.18% | -33.83% | -31.99% | -31.25% | -18% | -16.34% | -28.46% | -17.15% | -66.24% | -34.53% | -34.96% | -35.8% | 5.918% | 0.9222% | 0.9414% | 13.42% | -40.71% | -29.73% | -41.67% | -42.31% | 12.56% | 16.84% | 17.01% | 26.25% | -78.88% | -78.28% | -34.06% | -31.41% | 9.829% | 25.55% | 10.32% | -3.365% | -41.53% | -68.86% | -41.98% | -33.2% | 62.27% | 3.092% | 25.14% | 15.13% | -47.32% | -42.28% | -42.48% | -49% | -24.82% | -66.45% | 25.72% | -1.157% | -55.76% | -43.46% | -53.9% | -41.51% | -4.052% | -1.653% | 12.01% | 5.238% | [8 empty] | -2.229% | 24.71% | [6 empty] | 19.74% | 5.197% | 16.82% | 22.5% | -33.53% | -33.58% | -33.01% | -44.76% | 35.19% | 2.878% | -19.62% | 17.06% | -61.94% | -36.68% | -38.3% | -68.9% | 19.82% | -8.338% | 14.11% | -5.676% | -7.056% | -26.34% | -31.17% | -14.81% | 20.24% | 17.73% | 27.75% | 20.34% | -100% | -81.02% | -100% | -100% | 214% | 1044% | [6 empty] | -33.35% | -36.65% | -29.5% | -31.47% | 9.471% | -2.75% | 16.42% | 14.07% | -12.59% | -33.89% | -59.02% | -20.89% | -1.261% | 83.22% | -46.98% | 42.34% | -46.08% | -51.87% | -67.99% | -58.08% | -20.77% | 165.3% | -45.18% | -40.54% | -63.75% | 83.68% | 127% | 14.89% | -10.43% | 11.23% | 113.9% | 184.2% | -48.17% | -78.5% | -32.89% | -85.39% | -30% | 52.87% | 71.89% | 9.181% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -20.35% | -44.73% | 2.82% | 41.93% | 66.2% |  | 20.85% | 67.25% | -27.55% | -34.35% | -16.92% | -76.72% | -82.16% | -43.33% | -49.15% | -33.49% | -94.78% | -83.8% | -77.45% | -100% | -100% | -100% | -68.03% | -49.52% | -7.95% | -1.207% | 9.863% | 9.089% | -100% | -100% | -100% | -100% | 2.999% | 16.94% | 1.272% | 15.87% | 3.184% | 46.6% | 18.1% | -8.553% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 32.11% | -100% | -100% | -100% | -100% | -26.81% | -7.888% | -34.37% | 9.484% | 9.44% | 23.06% | 49.98% | 731.4% |  | 51.29% | -17.2% | 63.57% | 41.26% | 50.22% | -100% | -28.67% | -27.45% | 20.99% | 51.41% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -6.145% | -12.05% | 4.487% | 348.7% |  |  |  | 368% | -55.93% | 8.057% | 18.01% | -56.01% | 36.68% | 15% | 2.162% | 23.85% | 135.1% | 14.42% | 30.57% | 229.9% | 14.94% | 12.54% | 28.6% | 3.113% | 13.9% | -10.26% | -100% | -0.6359% | -75.53% | -100% | -100% | -100% | 3.662% | -13.89% |  | 14.81% | 38.68% | 18.96% | 20.12% | -9.193% | 49.81% | 129.7% | -24.78% | 38.03% | 66.05% | 13.15% | 66.12% | 103.7% | 13.39% | 41.78% | 54.45% | 40.26% | -2.005% | 57.73% | -7.459% | -7.635% | -62.8% | -18.73% | -25.51% | -28.42% | 29.5% | 12.91% | -50.85% | 17.56% | 256.7% | -14.33% | 181% | -6.661% | -11.67% | -2.392% | 128.4% | 29.22% | -17.53% | 16.91% | -18.43% | -16.07% | 49.8% | -7.943% | -4.357% | 24.93% | -31.51% | -25.84% | -35.92% | -71.96% | -30.25% | -41.86% | -96.36% | -80.68% | -17.63% | -48.74% | -78.59% | -1.806% | -27.1% | -27.77% | -26.65% | -17.64% | -22.41% | 77.62% | 14.9% | -36.5% | -58.53% | -100% | -59.44% | -3.703%
2025-07-10 | -47.53% | -4.121% | 1.014% | -10.26% | -9.621% | -6.699% | -26.97% | -16.5% | -4.87% | -7.393% | -4.586% | -9.302% | -8.644% | 7.507% | 13.49% | 1.664% | -18.06% | 38.79% | -9.168% | -7.55% | -8.992% | -6.578% | -17.29% | -7.468% | -9.773% | -6.679% | -6.672% | -4.925% | -17.08% | -16.13% | -15.35% | -6.926% | -13.57% | -10.39% | -13.15% | -15.89% | -17.16% | -14.78% | -5.503% | 7.161% | -63.84% | -63.09% | -15.52% | -11.02% | -16.18% | -8.465% | -16.44% | -24.5% | -18.92% | -47.91% | -20.35% | -5.912% | 23.68% | -20.39% | -7.625% | -12.93% | -23.59% | -19.99% | -21.57% | -25.51% | -36.03% | -66.86% | -3.452% | -22.56% | -31.83% | -18.35% | -29.24% | -13.57% | -19.74% | -19.38% | -11.54% | -13.73% | [8 empty] | -8.326% | 17.05% | [6 empty] | -12.98% | -20.75% | -14.41% | -11.37% | -13.62% | -12.04% | -12.52% | -23.87% | -0.2342% | -17.27% | -37.33% | -12.73% | -36.15% | -13.66% | -12.55% | -48.66% | -5.531% | -26.35% | -11.16% | -24.41% | 12.8% | -10.08% | -15.05% | 1.887% | -13.97% | -17.04% | -9.068% | -13.16% | -100% | -80.93% | -100% | -100% | 285.7% | 1389% | [6 empty] | -17.75% | -19.58% | -15.49% | -15.32% | -18.93% | -23.11% | -10.33% | -13.78% | 3.839% | -15.56% | -42.53% | -3.733% | -18% | 36.71% | -48.17% | 2.371% | -29.34% | -33.24% | -54.16% | -42.52% | -34.3% | 122.7% | -22.67% | -35.13% | -62.73% | 46.45% | 90.32% | 1.787% | -22.35% | -3.372% | 86.75% | 110.2% | -28.39% | -65.17% | -16.02% | -75.57% | -31.55% | 16.25% | 35.44% | -15.45% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -9.125% | -29.64% | 26.37% | 64.5% | 23.85% |  | 16.17% | 30.43% | -22.66% | -34.14% | -22.49% | -76.2% | -81.74% | -44.45% | -52.34% | -39.1% | -95.85% | -83.44% | -77.05% | -100% | -100% | -100% | -67.59% | -52.4% | -13.04% | -23.63% | -18.35% | -16.84% | -100% | -100% | -100% | -100% | -18.05% | -13.23% | -23.12% | -14.26% | -40.88% | -0.5767% | -18.52% | -33.06% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 3.199% | -100% | -100% | -100% | -100% | -23.1% | -6.707% | -28.54% | -6.638% | -13.76% | -2.487% | 11.91% | 586.8% |  | 17.35% | -30.03% | 23.77% | 7.022% | 13.69% | -32.11% | -39.45% | -36.02% | -9.194% | 12.57% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -22.31% | -24.96% | -15.33% | 262.9% |  |  |  | 273.8% | -47.81% | 15.6% | 23.09% | -47.79% | 39.09% | 21.4% | 7.969% | 29.94% | 106.1% | 1.027% | 0.4996% | 152.1% | -11.76% | -12.02% | 7.442% | -19.36% | 6.02% | -16.82% | -100% | -8.266% | -44.53% | -100% | -100% | -100% | -18.6% | -0.6935% |  | -14.07% | 5.927% | -6.217% | -26.17% | -25.87% | 12.78% | 75.25% | -36.98% | 0.2801% | 20% | -9.339% | 17.67% | 46.22% | -11.16% | 6.309% | 12.13% | 2.284% | -9.239% | 44.56% | -11.02% | -12.9% | -55.31% | -17.93% | -24.93% | -28.55% | -0.808% | -12.16% | -53.48% | -5.781% | 240.4% | -10.3% | 166.6% | -3.008% | -8.554% | -22.52% | 80.97% | 4.745% | -6.114% | 30.74% | -6.108% | -6.141% | 73.22% | -1.806% | -4.015% | 19.75% | -19.41% | -13.5% | -25.27% | -60.87% | -40.47% | -47.95% | -96.41% | -80.81% | -11.35% | -41.25% | -76.03% | -2.307% | -30.26% | -31.73% | -28.19% | -21.31% | -11.49% | 105.1% | 32.41% | -29.72% | -60.77% | -100% | -61.61% | -21.39%
2025-07-11 | -43.13% | -3.49% | 3.413% | -9.959% | -9.705% | -7.419% | -14.57% | -15.79% | -5.551% | -7.264% | -9.812% | -10.36% | -10.08% | 8.591% | 17.16% | 0.25% | -17.98% | -16.31% | -8.542% | -7.18% | -8.449% | -6.235% | -16.51% | -7.484% | -9.934% | -6.182% | -5.614% | -3.601% | -15.42% | -13.45% | -7.933% | -5.017% | -11.86% | -11.03% | -9.726% | -13.61% | -17.57% | -15.58% | -5.067% | 1.892% | -60.68% | -60.05% | -16.23% | -12.31% | -17.22% | -5.992% | -17.96% | -25.48% | -19.43% | -47.77% | -21.34% | -7.753% | 21.2% | -21.7% | -8.669% | -13.69% | -23.7% | -20.96% | -21.88% | -24.88% | -34.3% | -65.2% | -6.579% | -23.35% | -31.61% | -18.54% | -27.73% | -12.63% | -17.62% | -17.16% | -10.66% | -12.17% | [8 empty] | 4.637% | 33.66% | [6 empty] | -12.58% | -20.25% | -14.88% | -11.18% | -15.29% | -13.57% | -14.5% | -25.36% | -2.013% | -18.18% | -37.94% | -15% | -41.35% | -14.75% | -13.4% | -47% | -4.929% | -27.67% | -11.71% | -25.04% | 13.08% | -9.558% | -14.56% | 2.638% | -12.44% | -16.19% | -8.77% | -13.28% | -100% | -78.57% | -100% | -100% | 288.8% | 1398% | [6 empty] | -17.79% | -19.63% | -15.92% | -15.91% | -19.06% | -46.38% | -10.03% | -13.78% | 3.717% | -14.8% | -40.63% | -3.631% | -15.28% | 38.13% | -40.92% | 2.7% | -29.41% | -29.42% | -50.75% | -41.91% | -34.18% | 146.3% | -32.4% | -34.08% | -62.31% | 40.53% | 85.23% | 0.1793% | -23.65% | -4.936% | 84.63% | 103.9% | -29.22% | -64.27% | -19.29% | -75% | -34.2% | 11.43% | 30.08% | -19.72% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -10.16% | -29.39% | 25.92% | 61.99% | 23.31% |  | 26.97% | 30.54% | -24.51% | -33.53% | -23.08% | -75.67% | -81.37% | -45.89% | -56.48% | -40.66% | -94.57% | -83.16% | -76.75% | -100% | -100% | -100% | -66.12% | -52.9% | -24.49% | -23.86% | -19.53% | -19.08% | -100% | -100% | -100% | -100% | -15.35% | -11.24% | -21.47% | -14.3% | -32.78% | 6.543% | -11.82% | -24.99% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 0.5161% | -100% | -100% | -100% | -100% | -24.22% | -8.686% | -29.59% | -6.919% | -14.64% | -2.752% | 16.62% | 595.9% |  | 19.85% | -28.64% | 21.47% | 4.392% | 11.55% | -3.649% | -38.73% | -34.67% | -9.908% | 10.72% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -21.74% | -23.8% | -14.88% | 265.8% |  |  |  | 272.8% | -52.32% | -7.973% | -31.29% | -52.21% | 3.438% | -9.94% | -17.27% | -1.679% | 168.8% | 21.16% | 2.489% | 129.7% | -7.724% | -5.461% | 9.913% | -16.61% | 21.54% | -3.805% | -100% | 7.148% | -6.383% | -99.55% | -100% | -100% | 27% | 25.02% |  | 44.43% | 79.85% | 54.19% | 20.19% | 16.15% | 86.84% | 182.7% | -6.389% | 73.35% | 110% | 44.15% | 50.56% | 160.5% | -9.069% | 7.877% | 13.36% | 3.851% | -100% | 43.15% | -10.41% | -11.76% | 33.55% | 11.82% | 1.058% | -2.852% | 43.19% | 24.45% | -45.92% | 31.11% | 383.3% | 16.8% | 136.5% | -22.21% | -6.046% | -27.24% | 153.4% | -30.82% | 29.62% | 83.44% | 30.09% | 35.66% | 114.9% | 30.04% | 30.72% | 73% | 12.51% | 21.35% | 5.166% | -53.55% | -20.52% | -33.9% | -97.72% | -77.75% | 23.22% | -5.797% | -69.97% | 63.75% | 1.128% | -0.7539% | 12.75% | 26.91% | 46.71% | 242.6% | 120.1% | 17.63% | 19.62% | 107.3% | -8.338% | 26%
2025-07-12 | -46.92% | 2.894% | 5.094% | -2.362% | -1.75% | 0.9978% | -10.95% | -9.505% | 2.539% | -1.572% | 2.767% | -2.942% | -3.482% | 12.23% | 3.999% | 10.01% | -13.45% | -5.533% | -4.13% | -0.9775% | -3.871% | -0.2464% | -12.74% | -1.522% | -5.917% | -0.3994% | -0.3349% | 0.8454% | -12.78% | -27.95% | -14.28% | -3.599% | -10.46% | -3.121% | -9.03% | -12.16% | -9.636% | -6.914% | -0.2196% | 7.767% | -64.43% | -63.83% | -10.11% | -5.978% | -12.17% | -1.738% | -11.86% | -21.09% | -15.97% | -48.61% | -16.34% | 0.5162% | 29.83% | -16.64% | -1.187% | -3.476% | -20.76% | -17.37% | -18.31% | -22.43% | -76.34% | -90% | -76.48% | -56.97% | -33.05% | -14.81% | -26.99% | -10.38% | -17.34% | -16.66% | -8.868% | -12.89% | [8 empty] | -100% | -100% | [6 empty] | -4.512% | -13.64% | -6.949% | -1.808% | -8.444% | -7.587% | -7.83% | -21.25% | 5.391% | -15.98% | -36.6% | -7.914% | -41.34% | -13.94% | -13.99% | -49.35% | -2.416% | -93.96% | -91.73% | -93.7% | 25.44% | -1.17% | -6.108% | 13.47% | -5.314% | -9.083% | 0.3861% | -4.56% | -100% | -79.29% | -100% | -100% | 323.9% | 1509% | [6 empty] | -11.33% | -98.86% | -7.427% | -8.801% | -12.26% | -19.16% | -4.714% | -8.437% | -30.81% | -8.919% | -40.13% | 6.339% | -13.11% | 49.56% | -46.23% | 13.58% | -4.043% | -3.623% | -42.65% | -28.49% | -13.64% | 181.9% | -6.214% | -5.129% | -65.08% | -98.7% | -98.47% | 0.2466% | -22.55% | -3.158% | 88.49% | 122.3% | -27.63% | -65.94% | -13.08% | -75.6% | -36.01% | 20.64% | 42.67% | -14.4% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | 29.35% | -8.748% | 70.44% | 135.6% | 76.33% |  | 27.22% | 75.16% | -32.78% | -97.33% | -30% | -80% | -81.35% | -47.26% | -58.59% | -42.61% | -94.37% | -88.48% | -76.78% | -100% | -100% | -100% | -67.76% | -53.42% | -19.9% | -17.48% | -10.75% | -15.31% | -100% | -100% | -100% | -100% | -14.19% | -6.637% | -18.31% | -10.78% | -30.45% | 15.65% | -7.891% | -24.12% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 41.5% | -100% | -100% | -100% | -100% | 1.921% | 30.38% | -11.66% | -9.125% | -8.879% | 10.1% | -31.39% | 775.1% |  | 46.67% | -18.91% | 97.87% | 79.57% | 88.05% | 47.23% | -13.41% | -25.54% | 42.24% | 79.48% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -6.592% | -14.72% | 13.35% | 390% |  |  |  | 397.5% | -58.23% | -42.88% | -18.25% | -58.51% | -11.07% | -43.58% | -29.39% | -1.486% | 186.6% | 60.57% | -10.05% | 132.6% | -3.59% | -1.543% | 15.38% | -9.828% | 38.02% | 17.64% | -68.18% | 19.23% | 2.929% | -22.77% | -14.27% | -16.83% | 9.309% | 11.81% |  | 20.98% | 45.84% | 16.53% | -4.846% | -3.914% | 54.22% | 140.2% | -21.07% | 44.55% | -47.45% | -18.22% | 70.67% | 112.7% | -10.76% | -100% | -15.53% | 5.412% | -100% | 5.393% | -100% | -38.95% | -55.6% | 6.88% | -2.852% | -7.004% | 32.93% | 19.83% | -47.2% | -100% | -100% | 10.39% | 112.4% | -25.75% | -10.01% | -30.48% | 140.7% | -33.46% | 26.23% | 78.27% | 25.16% | 29.82% | 98.75% | 24.53% | 24.41% | 68.05% | 5.968% | 15.03% | -2.885% | -57.78% | -24.85% | -37.62% | -96.08% | -79.9% | -100% | -27.48% | -84.81% | 49.52% | -100% | -12.74% | -4.832% | 6.09% | 9.894% | 145.5% | 53.47% | -100% | -100% | -71.86% | -20.68% | -4.797%
2025-07-13 | -47.01% | -6.96% | -4.263% | -12.26% | -11.94% | -9.314% | -18.79% | -18.34% | -7.675% | -12.54% | -7.684% | -12.57% | -12.54% | 4.757% | 4.163% | -1.51% | -21.37% | -14.87% | -13.61% | -11.03% | -12.56% | -10.5% | -21.16% | -11.23% | -14.72% | -10.72% | -10.81% | -9.374% | -21.22% | -33.43% | -20.39% | -11.62% | -15.2% | -11.48% | -13.23% | -16.81% | -17.72% | -15.46% | -7.132% | 0.4983% | -63.31% | -62.53% | -17.31% | -14.83% | -21.03% | -11.88% | -19.55% | -27.19% | -23.14% | -50.84% | -23.68% | -9.246% | 19.71% | -23.96% | -79.74% | -16.48% | -27% | -24.11% | -25.4% | -28.65% | -38.65% | -67.64% | -30.23% | -28.29% | -37.38% | -22.48% | -32.47% | -18.41% | -23.5% | -23.18% | -16.8% | -19.58% | [8 empty] | -100% | -100% | [6 empty] | -43.09% | -32.03% | -26.78% | -23.12% | -17.03% | -15.9% | -16.26% | -27.97% | -4.475% | -21.08% | -40.38% | -16.26% | -44.56% | -21.28% | -20.49% | -51.47% | -10.98% | -33.47% | -16.32% | -31.58% | 29.62% | 5.809% | 0.6831% | 21.32% | 1.976% | -2.108% | 7.774% | 1.098% | -100% | -93.3% | -100% | -100% | 355.4% | 1630% | [6 empty] | -4.29% | -7.372% | -0.6261% | -1.853% | -5.712% | -13.3% | 2.921% | -1.515% | 3.306% | -16.49% | -43.61% | -4.789% | -19.35% | 34.4% | -44.89% | 1.347% | -24.31% | -24.08% | -48.85% | -39.81% | -30.22% | 134.8% | -24.53% | -23.23% | -63.88% | 39.33% | 80.66% | -6.476% | -26.74% | -8.596% | 77.75% | 101.3% | -6.549% | -60.74% | 15.76% | -72.14% | -23.59% | 66.36% | 95.21% | 15.87% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -2.692% | -25.2% | 35.34% | 79.05% | 34.32% |  | 29.28% | 39.95% | -1.307% | -99.76% | -4.911% | -75.42% | -79.23% | -35.51% | -51.72% | -31.94% | -93.57% | -88.06% | -73.88% | -100% | -100% | -100% | -63.27% | -42.9% | -0.9447% | 5.695% | 14.4% | 14.39% | -100% | -100% | -100% | -100% | 14.27% | 27.87% | 10.44% | 21.8% | -6.562% | 59.12% | 25.67% | -0.1178% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 6.709% | -100% | -100% | -100% | 11.67% | 31.96% | 32.29% | -5.112% | -31.85% | -29.92% | -18.17% | -81.27% | 601.5% |  | 16.7% | -33.24% | 30.54% | 15.05% | 22.01% | 1.98% | -36.02% | -34.17% | -3.092% | 19.51% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -25.38% | -29.4% | -12.16% | 276.7% |  |  |  | 249.7% | -42.86% | -10.14% | -13.14% | -57.05% | -2.259% | -16.54% | -22.14% | -7.593% | 165.2% | 51.53% | -1.39% | 116.4% | -11.3% | -9.8% | 3.97% | -15.16% | 49.15% | 90.98% | 14.79% | 7.254% | -12.11% | -32.77% | -7.762% | -9.037% | 9.654% | 15.99% |  | 19.4% | 45.08% | 18.14% | -4.421% | 2.992% | 53.15% | 139.3% | -18.84% | 42.12% | -44.51% | -14.54% | 66.77% | 108.1% | -44.79% | -37.69% | 1.879% | -1.577% | -45.79% | 20.73% | -100% | -100% | -53.1% | 6.798% | -2.84% | -5.942% | 32.06% | 18.92% | -44.8% | -23.81% | 338% | 11.19% | 118.4% | -8.519% | -7.313% | -28.69% | 138.1% | -30.31% | 23.34% | 73.57% | 22.25% | 25.41% | 102.8% | 24.05% | 22.45% | 62.61% | 4.457% | 12.37% | -5.301% | -56.06% | -24.13% | -35.83% | -95.36% | -79.45% | -16.19% | -24.97% | -84.56% | 47.98% | -34.45% | -10.35% | -100% | -100% | 12.45% | 150.7% | 64.61% | -33.28% | -46.65% | -70.23% | -16.1% | -4.532%
2025-07-14 | -44.68% | -1.403% | 2.108% | -8.14% | -23.64% | -5.006% | -13.65% | -13.92% | -2.931% | -8.016% | -4.728% | -9.646% | -5.589% | 12.62% | 7.563% | 3.1% | -17.79% | -12.25% | -9.881% | -8.603% | -10.39% | -8.334% | -18.22% | -9.223% | -12.29% | -9.617% | -9.476% | -7.828% | -19.56% | -30.95% | -17.11% | -8.907% | -8.226% | -7.348% | -6.613% | -10.24% | -12.61% | -11.56% | -0.4038% | 7.788% | -61.32% | -60.16% | -9.773% | -10.7% | -16.15% | -8.931% | -15.91% | -22.92% | -19.35% | -47.26% | -21.32% | -7.591% | 24.16% | -19.96% | -23.51% | -12.55% | -24.46% | -21.35% | -21.89% | -25.15% | -35.25% | -67.12% | -27.65% | -26.27% | -34.83% | -20.57% | -29.76% | -16.48% | -20.87% | -21.21% | -15.19% | -17.38% | [8 empty] | -100% | -100% | [6 empty] | -13.64% | -20.61% | -13.02% | -9.679% | -17.07% | -14.28% | -15.18% | -24.68% | -4.406% | -17.35% | -37.17% | -14.3% | -41.94% | -19.18% | -17.99% | -49.38% | -9.925% | -31.21% | -15.55% | -29.57% | 12.18% | -8.445% | -12.89% | 3.809% | -11.87% | -14.36% | -6.654% | -12.55% | -100% | -94.27% | -100% | -100% | 295.1% | 1443% | [6 empty] | -15.35% | -17.27% | -13.38% | -12.85% | -16.75% | -20.82% | -6.941% | -11.61% | 6.417% | -12.09% | -40.36% | -1.987% | -14.63% | 38.6% | -45.25% | 1.85% | -26.49% | -20.32% | -38.58% | -38.84% | -31.51% | 132.6% | -30.68% | -23.87% | -63.03% | 43.58% | 89.24% | 0.9009% | -21.76% | -1.845% | 90.88% | 107.7% | -28.21% | -65.89% | -20.3% | -75.6% | -32.32% | 12.36% | 33.58% | -18.62% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -7.793% | -21.91% | 32.03% | 75.99% | 27.17% |  | 61.32% | 39.45% | -24.99% | -41.34% | -24.18% | -79.09% | -82.31% | -45.66% | -58.1% | -45.07% | -94.49% | -89.7% | -77.26% | -100% | -100% | -100% | -67.35% | -51.96% | -24.18% | -23.8% | -18.49% | -20.48% | -100% | -100% | -100% | -100% | -15.39% | -11.67% | -21.1% | -16.3% | -33.85% | 6.807% | -14.45% | -26.01% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 0.3137% | -100% | -100% | -100% | -38.12% | -25.01% | -6.975% | -32.27% | -20.64% | -21.93% | -13.77% | -36.7% | 541.5% |  | 8.801% | -36.4% | 25.13% | 7.599% | 14.17% | 6.758% | -23.35% | -22.38% | -7.924% | 13.67% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -30.47% | -34.57% | -18.59% | 253.5% |  |  |  | 252.1% | -28.32% | 3.635% | -12.69% | -29.98% | -4.562% | -18.33% | -22.57% | -9.223% | 169.9% | 51.96% | -0.9165% | 121.4% | -11.77% | -7.908% | 3.714% | -12.76% | 31.69% | 69.21% | 2.057% | -4.62% | -32.9% | -44.25% | -29.42% | -26.41% | -16.11% | -3.568% |  | -12.36% | 10.34% | -4.711% | -16.93% | 19.08% | 14.07% | 78.05% | -34.46% | 0.5509% | -52.27% | -26.46% | 18.42% | 48.28% | -12.99% | -3.606% | 2.611% | -2.04% | -13.78% | 21.79% | -100% | -83.12% | -60.37% | -21.95% | -28.22% | -26.92% | -8.772% | -16.31% | -53.33% | -15.79% | 127.8% | -19.34% | 62.94% | -27.06% | -26.57% | -44.56% | 68.97% | -41.88% | -16.14% | 16.07% | -3.372% | -16.74% | 60.86% | -9.569% | -14.62% | 6.043% | -25.58% | -21.62% | -33.78% | -63.42% | -43.39% | -49.99% | -96.5% | -83.17% | -13.9% | -40.06% | -87.34% | -2.884% | -28.03% | -31.12% | -100% | -100% | -20.09% | 78.75% | 17.9% | -89.56% | -14.32% | -71% | -32.19% | -28.84%
2025-07-15 | -46.79% | -4.421% | 0.03443% | -9.771% | -10.27% | -6.752% | -15.61% | -15.83% | -4.823% | -9.211% | -5.173% | -10.57% | -7.353% | 7.965% | -0.5805% | 0.9165% | -16.88% | -11.94% | -10.14% | -9.686% | -9.757% | -7.242% | -16.77% | -7.53% | -8.166% | -7.38% | -7.501% | -5.192% | -16.3% | -23.54% | -5.166% | -3.505% | -7.74% | -8.016% | -7.257% | -19.13% | -14.74% | -11.53% | 0.7476% | 7.619% | -61.77% | -61.14% | -10.9% | -11.81% | -16.98% | -9.113% | -15.01% | -22.5% | -18.58% | -46.04% | -19.22% | -5.325% | 27.23% | -18.7% | -60.44% | -12.04% | -21.25% | -18.13% | -20.19% | -23.21% | -32.85% | -66.88% | -23.57% | -22.32% | -30.58% | -16.95% | -26.28% | -12.1% | -15.69% | -64.68% | -10% | -12.06% | [8 empty] | -100% | -100% | [6 empty] | -43.43% | -49.95% | -43.28% | -40.22% | -15.09% | -10.11% | -11% | -20.59% | 0.8477% | -12.34% | -33.52% | -10.91% | -37.94% | -14.55% | -12.75% | -45.77% | -2.933% | -26.08% | -9.321% | -24.44% | 11.11% | -8.569% | -14.87% | 3.312% | -12.06% | -15.19% | -10.64% | -15.55% | -100% | -93.94% | -100% | -100% | 300% | 1457% | [6 empty] | -14.65% | -16.46% | -13.13% | -13.17% | -16.6% | -20.58% | -5.764% | -10.47% | 4.41% | -13.82% | -41.93% | -3.388% | -16.99% | 0.9498% | -48.42% | -0.4275% | -22.7% | -13.25% | -24.21% | -28.05% | -21.95% | 148% | -23.38% | -19.78% | -69.03% | 44.38% | 88.42% | 1.989% | -19.64% | 3.175% | 99.95% | 117.1% | -23.4% | -64.1% | -14.92% | -74.21% | -28.05% | 19.07% | 40.39% | -14.36% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -6.45% | -25.5% | 42.04% | 76.76% | 33.64% |  | 88.74% | 43.02% | -18.15% | -39.05% | -16.78% | -77.83% | -81.19% | -46.06% | -55.51% | -39.76% | -94.43% | -89.28% | -76.14% | -100% | -100% | -100% | -67.08% | -50.09% | -16.96% | -16.99% | -11.53% | -16.32% | -100% | -100% | -100% | -100% | -10.6% | -7.233% | -17.28% | -12.4% | -29.88% | 13.49% | -8.095% | -20.58% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 4.156% | -100% | -100% | -100% | -32.18% | -21.53% | -5.22% | -27.81% | -12.16% | -32.89% | -2.086% | 8.682% | 614% |  | 26.84% | -30.26% | 41.99% | 12.05% | 18.97% | 21.81% | -15.15% | -16.39% | -9.178% | 11.36% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -27.07% | -26.74% | -19.49% | 237.9% |  |  |  | 275.8% | -15.77% | 30.13% | 2.818% | -0.5283% | 6.659% | -7.585% | -12.67% | 3.558% | 198.5% | 68.35% | 9.483% | 144.3% | -2.926% | 0.8472% | 14.2% | -4.895% | 43.61% | 83.72% | 10.17% | 3.339% | -26.9% | -40.73% | -23.53% | -17.85% | -7.701% | 9.315% |  | -3.863% | 19.95% | 20.72% | -8.764% | 23.46% | 25.45% | 96.66% | -26.28% | 11.51% | -49.51% | -18.3% | 28.85% | 62.1% | -3.062% | 11.48% | 14.22% | 9.585% | -3.295% | 38.22% | -96.41% | -59.84% | -55.1% | -10.63% | -17.1% | -20.21% | 5.524% | -4.14% | -46.61% | 2.868% | 133.9% | -4.682% | 96.88% | -11.04% | -13.14% | -35.03% | 94.2% | -32.97% | -3.517% | 33.23% | -3.608% | -3.553% | 89.36% | 5.099% | -1.548% | 22.99% | -14.31% | -9.527% | -22.85% | -56.69% | -34.33% | -40.45% | -95.78% | -80.26% | 0.4294% | -39.09% | -84.92% | 15.61% | -14.46% | -24.65% | -80.45% | -54.51% | -0.6964% | 108% | 39.81% | -23.42% | 2.398% | -65.23% | -17.25% | -15.35%
2025-07-16 | -53.44% | 3.382% | -0.8419% | -0.5712% | 0.02739% | 2.7% | -10.88% | -7.615% | 4.099% | -3.866% | 4.229% | -1.15% | 2.423% | 6.685% | -15.41% | 12.59% | -23.39% | -16.22% | -15.44% | -13.72% | -13.51% | -12.32% | -23% | -11.67% | -14.74% | -12.01% | -12.55% | -10.85% | -22.25% | -37.82% | -64.68% | -13.17% | -23.84% | -13.4% | -29.36% | -35.85% | -20.43% | -17.09% | -14.01% | -7.125% | -68.34% | -67.37% | -2.307% | -4.686% | -11.85% | -0.2873% | -9.551% | -19.23% | -25.3% | -58.78% | -26.18% | -10.24% | 13.05% | -26.16% | -42.81% | -18.8% | -30.98% | -27.94% | -26.63% | -33.71% | -46.11% | -77.07% | -34.24% | -30.14% | -42.58% | -22.97% | -36.06% | -19.26% | -28.22% | -26.3% | -18.76% | -25.88% | [8 empty] | -100% | -100% | [6 empty] | -6.099% | -17.38% | -7.353% | -2.362% | -9.533% | -4.667% | -5.43% | -18.72% | 8.665% | -11.68% | -37.66% | -3.931% | -42.74% | -11.08% | -10.03% | -52.94% | 0.07656% | -27.54% | -6.18% | -24.51% | 18.36% | -2.518% | -11.81% | 11.61% | -5.694% | -9.297% | -3.857% | -10.1% | -100% | -100% | -100% | -100% | 316.4% | 1474% | [6 empty] | -14.03% | -18.13% | -10.91% | -11.61% | -15.1% | -23.88% | -7.532% | -13.13% | -30.6% | 7.365% | -72.71% | 8.214% | 38.3% | 26.69% | -6.92% | 9.172% | -33.97% | -25.55% | -35.37% | -37.91% | -30.66% | 109% | -34.25% | -34.66% | -89.01% | 56.8% | 99.77% | 1.387% | -29.63% | -4.587% | 84.43% | 123.6% | -28.96% | -71.26% | -12.79% | -79.3% | -43.12% | 24.18% | 45.05% | -12.94% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [32 empty] | -13.52% | -36.18% | 24.26% | 61.83% | 22.25% |  | 23.18% | 28.06% | -26.47% | -50.78% | -29.11% | -81.85% | -84.65% | -58.55% | -64.27% | -61.03% | -95.32% | -91.24% | -80.73% | -100% | -100% | -100% | -72.16% | -61.84% | -17.33% | -13.8% | -4.896% | -15.62% | -100% | -100% | -100% | -100% | -17.97% | -9.449% | -20.59% | -12.02% | -31.88% | 13.5% | -9.479% | -27.26% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | 6.642% | -100% | -100% | -100% | -39.4% | -22.03% | -2.754% | -31.7% | -22.6% | -84.15% | -3.986% | 4.724% | 557.9% |  | 12% | -38.18% | 48.88% | 16.73% | 22.45% | 22.92% | -3.271% | -17.5% | -1.688% | 22.19% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | [11 empty] | -100% |  |  | -100% |  | -33.23% | -32.36% | -20.17% | 244.2% |  |  |  | 69.1% | -30.43% | 23.63% | -9.368% | 5.926% | 3.295% | -12.1% | -18.98% | -4.222% | 193.6% | 66.16% | 8.081% | 129.9% | -2.134% | 1.09% | 16.69% | -7.591% | 3.875% | 32.59% | -20.48% | -25.23% | -35.42% | -53.18% | -31.99% | -36.13% | -22.36% | 16.94% |  | -9.98% | 27.51% | 32.31% | -5.99% | -5.792% | 3.04% | 81.88% | -40.26% | 7.416% | -59.28% | -37.21% | 27.1% | 57.84% | -12.71% | 6.13% | 11.82% | 8.924% | -7.109% | 29.02% | -40.75% | -70.24% | -67.72% | -22.04% | -28.96% | -31.16% | -3.411% | -11.61% | -37.53% | -6.846% | 222.4% | -20.5% | 57.02% | -32.49% | -34.4% | -51.35% | 60.69% | -38.51% | -16.6% | 16.51% | -18.13% | -17.52% | 31.13% | -18.3% | -17.51% | 6.307% | -54.65% | -25.28% | -38.91% | -72.73% | -50.74% | -58.43% | -97.29% | -87.4% | -91.15% | -63.36% | -96.12% | -8.926% | -30.65% | -46.1% | -74.12% | -36.86% | -13.39% | 71.41% | 21.68% | -89.15% | -16.9% | -75.51% | -39.72% | -34.66%
2025-07-17
Formulas:
Date = [Date, row above]+1

## Inv_SY_B
| 957 | 1084.6 | 829.4 | 1276 | 1339.8 | 1244.1 | 1116.5 | 1244.1 | 1180.3 | 1196.25 | 1244.1 | 1339.8 | 1244.1 | 781.55 | 430.65 | 1228.15 | 1264.4 | 1327.62 | 1232.79 | 1280.205 | 1296.01 | 1264.4 | 1296.01 | 1264.4 | 1180.3 | 1307.9 | 1307.9 | 1228.15 | 1323.85 | 1100.55 | 1036.75 | 1036.75 | 861.3 | 1212.2 | 797.5 | 893.2 | 1307.9 | 1307.9 | 893.2 | 829.4 | 1244.1 | 1276 | 1307.9 | 1244.1 | 1244.1 | 1307.9 | 1276 | 1276 | 1276 | 1291.95 | 1339.8 | 1276 | 861.3 | 1276 | 1244.1 | 1244.1 | 1244.1 | 1244.1 | 1276 | 1244.1 | 1212.2 | 1244.1 | 1164.35 | 1339.8 | 1276 | 1307.9 | 1244.1 | 1212.2 | 1084.6 | 1148.4 | 1180.3 | 1084.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382.8 | 303.05 | 0 | 0 | 0 | 0 | 0 | 0 | 1339.8 | 1339.8 | 1307.9 | 1307.9 | 1339.8 | 1276 | 1339.8 | 1307.9 | 1244.1 | 1148.4 | 1307.9 | 1307.9 | 1339.8 | 1260.05 | 1084.6 | 1307.9 | 1116.5 | 1276 | 1228.15 | 1307.9 | 1020.8 | 1260.05 | 1276 | 1164.35 | 1276 | 1307.9 | 1276 | 1307.9 | 1276 | 1244.1 | 1307.9 | 1180.3 | 287.1 | 63.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1291.95 | 1212.2 | 1339.8 | 1244.1 | 1307.9 | 1148.4 | 1052.7 | 1148.4 | 1148.4 | 1116.5 | 1276 | 1212.2 | 957 | 797.5 | 765.6 | 1180.3 | 1291.95 | 1164.35 | 1276 | 1339.8 | 1323.85 | 350.9 | 1212.2 | 1116.5 | 988.9 | 765.6 | 510.4 | 861.3 | 1004.85 | 829.4 | 430.65 | 558.25 | 1116.5 | 1276 | 1307.9 | 1339.8 | 797.5 | 988.9 | 813.45 | 1244.1 | 1180.3 | 797.5 | 1244.1 | 1148.4 | 1260.05 | 1276 | 1212.2 | 1180.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1244.1 | 1180.3 | 733.7 | 669.9 | 861.3 | 0 | 350.9 | 701.8 | 988.9 | 733.7 | 861.3 | 988.9 | 1180.3 | 1052.7 | 893.2 | 1164.35 | 1244.1 | 1276 | 1116.5 | 1276 | 1212.2 | 1084.6 | 1020.8 | 1339.8 | 1116.5 | 1307.9 | 1307.9 | 1339.8 | 1291.95 | 1339.8 | 1339.8 | 1339.8 | 1084.6 | 1244.1 | 1307.9 | 1339.8 | 1563.1 | 1084.6 | 1276 | 1212.2 | 1180.3 | 1244.1 | 925.1 | 1276 | 1148.4 | 1116.5 | 1260.05 | 957 | 1084.6 | 893.2 | 1180.3 | 1180.3 | 1307.9 | 1307.9 | 1212.2 | 1276 | 893.2 | 1180.3 | 1020.8 | 893.2 | 127.6 | 0 | 797.5 | 1180.3 | 829.4 | 1020.8 | 957 | 893.2 | 1244.1 | 1052.7 | 1148.4 | 957 | 1228.15 | 1132.45 | 669.9 | 733.7 | 1084.6 | 1228.15 | 1291.95 | 1132.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191.4 | 0 | 0 | 223.3 | 0 | 1291.95 | 1196.25 | 1228.15 | 287.1 | 0 | 0 | 0 | 287.1 | 1036.75 | 909.15 | 1052.7 | 1084.6 | 1148.4 | 1244.1 | 1180.3 | 1068.65 | 382.8 | 701.8 | 1100.55 | 430.65 | 1307.9 | 1196.25 | 1100.55 | 1116.5 | 1068.65 | 845.35 | 1276 | 1291.95 | 1307.9 | 1276 | 1244.1 | 957 | 988.9 | 638 | 0 | 1081.41 | 797.5 | 781.55 | 1164.35 | 925.1 | 797.5 | 510.4 | 1052.7 | 1020.8 | 861.3 | 797.5 | 893.2 | 701.8 | 1004.85 | 988.9 | 1020.8 | 1116.5 | 1148.4 | 749.65 | 1212.2 | 1132.45 | 972.95 | 1068.65 | 1148.4 | 1196.25 | 1084.6 | 1148.4 | 1180.3 | 988.9 | 319 | 925.1 | 414.7 | 845.35 | 861.3 | 1228.15 | 542.3 | 925.1 | 1180.3 | 893.2 | 1164.35 | 1260.05 | 398.75 | 893.2 | 1084.6 | 1020.8 | 1196.25 | 1212.2 | 1339.8 | 1339.8 | 1339.8 | 1307.9 | 1244.1 | 1307.9 | 1084.6 | 1116.5 | 953.81 | 1116.5 | 1036.75 | 1084.6 | 1307.9 | 1244.1 | 1052.7 | 478.5 | 733.7 | 1339.8 | 861.3 | 893.2 | 893.2 | 1036.75 | 363511.955
| 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 | 237 | 238 | 239 | 240 | 241 | 242 | 243 | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273 | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304 | 305 | 306 | 307 | 308 | 309 | 310 | 311 | 312 | 313 | 314 | 315 | 316 | 317 | 318 | 319 | 320 | 321 | 322 | 323 | 324 | 325 | 326 | 327 | 328 | 329 | 330 | 331 | 332 | 333 | 334 | 335 | 336 | 337 | 338 | 339 | 340 | 341 | 342 | 343 | 344 | 345 | 346 | 347 | 348 | 349 | 350 | 351 | 352 | 353 | 354 | 355 | 356 | 357 | 358 | 359 | 360 | 361 | 362 | 363 | 364 | 365 | 366 | 367 | 368 | 369 | 370 | 371 | 372 | 373 | 374 | 375 | 376 | 377 | 378 | 379 | 380 | 381 | 382 | 383 | 384 | 385 | 386 | 387 | 388 | 389 | 390 | 391 | 392 | 393 | 394 | 395 | 396 | 397 | 398 | 399 | 400 | 401 | 402 | 403 | 404 | 405 | 406 | 407 | 408 | 409 | 410 | 411 | 412 | 413 | 414 | 415 | 416 | 417 | 418
Date | IS1Inv1M1 | IS1Inv1M2 | IS1Inv1M3 | IS1Inv1M4 | IS1Inv2M1 | IS1Inv2M2 | IS1Inv2M3 | IS1Inv2M4 | IS2Inv1M1 | IS2Inv1M2 | IS2Inv1M3 | IS2Inv1M4 | IS2Inv2M1 | IS2Inv2M2 | IS2Inv2M3 | IS2Inv2M4 | IS3Inv1M1 | IS3Inv1M2 | IS3Inv1M3 | IS3Inv1M4 | IS3Inv2M1 | IS3Inv2M2 | IS3Inv2M3 | IS3Inv2M4 | IS4Inv1M1 | IS4Inv1M2 | IS4Inv1M3 | IS4Inv1M4 | IS4Inv2M1 | IS4Inv2M2 | IS4Inv2M3 | IS4Inv2M4 | IS5Inv1M1 | IS5Inv1M2 | IS5Inv1M3 | IS5Inv1M4 | IS5Inv2M1 | IS5Inv2M2 | IS5Inv2M3 | IS5Inv2M4 | IS6Inv1M1 | IS6Inv1M2 | IS6Inv1M3 | IS6Inv1M4 | IS6Inv2M1 | IS6Inv2M2 | IS6Inv2M3 | IS6Inv2M4 | IS7Inv1M1 | IS7Inv1M2 | IS7Inv1M3 | IS7Inv1M4 | IS7Inv2M1 | IS7Inv2M2 | IS7Inv2M3 | IS7Inv2M4 | IS8Inv1M1 | IS8Inv1M2 | IS8Inv1M3 | IS8Inv1M4 | IS8Inv2M1 | IS8Inv2M2 | IS8Inv2M3 | IS8Inv2M4 | IS9Inv1M1 | IS9Inv1M2 | IS9Inv1M3 | IS9Inv1M4 | IS9Inv2M1 | IS9Inv2M2 | IS9Inv2M3 | IS9Inv2M4 | IS10Inv1M1 | IS10Inv1M2 | IS10Inv1M3 | IS10Inv1M4 | IS10Inv2M1 | IS10Inv2M2 | IS10Inv2M3 | IS10Inv2M4 | IS11Inv1M1 | IS11Inv1M2 | IS11Inv1M3 | IS11Inv1M4 | IS12Inv1M1 | IS12Inv1M2 | IS12Inv1M3 | IS12Inv1M4 | IS12Inv2M1 | IS12Inv2M2 | IS12Inv2M3 | IS12Inv2M4 | IS13Inv1M1 | IS13Inv1M2 | IS13Inv1M3 | IS13Inv1M4 | IS13Inv2M1 | IS13Inv2M2 | IS13Inv2M3 | IS13Inv2M4 | IS14Inv1M1 | IS14Inv1M2 | IS14Inv1M3 | IS14Inv1M4 | IS14Inv2M1 | IS14Inv2M2 | IS14Inv2M3 | IS14Inv2M4 | IS15Inv1M1 | IS15Inv1M2 | IS15Inv1M3 | IS15Inv1M4 | IS15Inv2M1 | IS15Inv2M2 | IS15Inv2M3 | IS15Inv2M4 | IS16Inv1M1 | IS16Inv1M2 | IS16Inv1M3 | IS16Inv1M4 | IS17Inv1M1 | IS17Inv1M2 | IS17Inv1M3 | IS17Inv1M4 | IS17Inv2M1 | IS17Inv2M2 | IS17Inv2M3 | IS17Inv2M4 | IS18Inv1M1 | IS18Inv1M2 | IS18Inv1M3 | IS18Inv1M4 | IS18Inv2M1 | IS18Inv2M2 | IS18Inv2M3 | IS18Inv2M4 | IS19Inv1M1 | IS19Inv1M2 | IS19Inv1M3 | IS19Inv1M4 | IS19Inv2M1 | IS19Inv2M2 | IS19Inv2M3 | IS19Inv2M4 | IS20Inv1M1 | IS20Inv1M2 | IS20Inv1M3 | IS20Inv1M4 | IS20Inv2M1 | IS20Inv2M2 | IS20Inv2M3 | IS20Inv2M4 | IS21Inv1M1 | IS21Inv1M2 | IS21Inv1M3 | IS21Inv1M4 | IS21Inv2M1 | IS21Inv2M2 | IS21Inv2M3 | IS21Inv2M4 | IS22Inv1M1 | IS22Inv1M2 | IS22Inv1M3 | IS22Inv1M4 | IS22Inv2M1 | IS22Inv2M2 | IS22Inv2M3 | IS22Inv2M4 | IS23Inv1M1 | IS23Inv1M2 | IS23Inv1M3 | IS23Inv1M4 | IS23Inv2M1 | IS23Inv2M2 | IS23Inv2M3 | IS23Inv2M4 | IS24Inv1M1 | IS24Inv1M2 | IS24Inv1M3 | IS24Inv1M4 | IS24Inv2M1 | IS24Inv2M2 | IS24Inv2M3 | IS24Inv2M4 | IS25Inv1M1 | IS25Inv1M2 | IS25Inv1M3 | IS25Inv1M4 | IS25Inv2M1 | IS25Inv2M2 | IS25Inv2M3 | IS25Inv2M4 | IS26Inv1M1 | IS26Inv1M2 | IS26Inv1M3 | IS26Inv1M4 | IS26Inv2M1 | IS26Inv2M2 | IS26Inv2M3 | IS26Inv2M4 | IS27Inv1M1 | IS27Inv1M2 | IS27Inv1M3 | IS27Inv1M4 | IS27Inv2M1 | IS27Inv2M2 | IS27Inv2M3 | IS27Inv2M4 | IS28Inv1M1 | IS28Inv1M2 | IS28Inv1M3 | IS28Inv1M4 | IS28Inv2M1 | IS28Inv2M2 | IS28Inv2M3 | IS28Inv2M4 | IS29Inv1M1 | IS29Inv1M2 | IS29Inv1M3 | IS29Inv1M4 | IS29Inv2M1 | IS29Inv2M2 | IS29Inv2M3 | IS29Inv2M4 | IS30Inv1M1 | IS30Inv1M2 | IS30Inv1M3 | IS30Inv1M4 | IS30Inv2M1 | IS30Inv2M2 | IS30Inv2M3 | IS30Inv2M4 | IS31Inv1M1 | IS31Inv1M2 | IS31Inv1M3 | IS31Inv1M4 | IS31Inv2M1 | IS31Inv2M2 | IS31Inv2M3 | IS31Inv2M4 | IS32Inv1M1 | IS32Inv1M2 | IS32Inv1M3 | IS32Inv1M4 | IS32Inv2M1 | IS32Inv2M2 | IS32Inv2M3 | IS32Inv2M4 | IS33Inv1M1 | IS33Inv1M2 | IS33Inv1M3 | IS33Inv1M4 | IS33Inv2M1 | IS33Inv2M2 | IS33Inv2M3 | IS33Inv2M4 | IS34Inv1M1 | IS34Inv1M2 | IS34Inv1M3 | IS34Inv1M4 | IS34Inv2M1 | IS34Inv2M2 | IS34Inv2M3 | IS34Inv2M4 | IS35Inv1M1 | IS35Inv1M2 | IS35Inv1M3 | IS35Inv1M4 | IS35Inv2M1 | IS35Inv2M2 | IS35Inv2M3 | IS35Inv2M4 | IS36Inv1M1 | IS36Inv1M2 | IS36Inv1M3 | IS36Inv1M4 | IS36Inv2M1 | IS36Inv2M2 | IS36Inv2M3 | IS36Inv2M4 | IS37Inv1M1 | IS37Inv1M2 | IS37Inv1M3 | IS37Inv1M4 | IS37Inv2M1 | IS37Inv2M2 | IS37Inv2M3 | IS37Inv2M4 | IS38Inv1M1 | IS38Inv1M2 | IS38Inv1M3 | IS38Inv1M4 | IS38Inv2M1 | IS38Inv2M2 | IS38Inv2M3 | IS38Inv2M4 | IS39Inv1M1 | IS39Inv1M2 | IS39Inv1M3 | IS39Inv1M4 | IS39Inv2M1 | IS39Inv2M2 | IS39Inv2M3 | IS39Inv2M4 | IS40Inv1M1 | IS40Inv1M2 | IS40Inv1M3 | IS40Inv1M4 | IS40Inv2M1 | IS40Inv2M2 | IS40Inv2M3 | IS40Inv2M4 | IS41Inv1M1 | IS41Inv1M2 | IS41Inv1M3 | IS41Inv1M4 | IS41Inv2M1 | IS41Inv2M2 | IS41Inv2M3 | IS41Inv2M4 | IS42Inv1M1 | IS42Inv1M2 | IS42Inv1M3 | IS42Inv1M4 | IS42Inv2M1 | IS42Inv2M2 | IS42Inv2M3 | IS42Inv2M4 | IS43Inv1M1 | IS43Inv1M2 | IS43Inv1M3 | IS43Inv1M4 | IS43Inv2M1 | IS43Inv2M2 | IS43Inv2M3 | IS43Inv2M4 | IS44Inv1M1 | IS44Inv1M2 | IS44Inv1M3 | IS44Inv1M4 | IS44Inv2M1 | IS44Inv2M2 | IS44Inv2M3 | IS44Inv2M4 | IS45Inv1M1 | IS45Inv1M2 | IS45Inv1M3 | IS45Inv1M4 | IS45Inv2M1 | IS45Inv2M2 | IS45Inv2M3 | IS45Inv2M4 | IS46Inv1M1 | IS46Inv1M2 | IS46Inv1M3 | IS46Inv1M4 | IS46Inv2M1 | IS46Inv2M2 | IS46Inv2M3 | IS46Inv2M4 | IS47Inv1M1 | IS47Inv1M2 | IS47Inv1M3 | IS47Inv1M4 | IS47Inv2M1 | IS47Inv2M2 | IS47Inv2M3 | IS47Inv2M4 | IS48Inv1M1 | IS48Inv1M2 | IS48Inv1M3 | IS48Inv1M4 | IS48Inv2M1 | IS48Inv2M2 | IS48Inv2M3 | IS48Inv2M4 | IS49Inv1M1 | IS49Inv1M2 | IS49Inv1M3 | IS49Inv1M4 | IS49Inv2M1 | IS49Inv2M2 | IS49Inv2M3 | IS49Inv2M4 | IS50Inv1M1 | IS50Inv1M2 | IS50Inv1M3 | IS50Inv1M4 | IS50Inv2M1 | IS50Inv2M2 | IS50Inv2M3 | IS50Inv2M4 | IS51Inv1M1 | IS51Inv1M2 | IS51Inv1M3 | IS51Inv1M4 | IS51Inv2M1 | IS51Inv2M2 | IS51Inv2M3 | IS51Inv2M4 | IS52Inv1M1 | IS52Inv1M2 | IS52Inv1M3 | IS52Inv1M4 | IS52Inv2M1 | IS52Inv2M2 | IS52Inv2M3 | IS52Inv2M4 | Plant
2025-06-15 | 0.71076 | 1.6206 | 1.6804 | 1.6425 | 1.6787 | 1.6966 | 1.1842 | 1.5267 | 1.7265 | 1.6624 | 1.7273 | 1.6778 | 1.6885 | 1.7323 | 1.5063 | 1.8647 | 1.6823 | 1.6002 | 1.582 | 1.6733 | 1.6055 | 1.6603 | 1.4552 | 1.6641 | 1.5599 | 1.685 | 1.6614 | 1.6954 | 1.4959 | 1.5299 | 1.5196 | 1.6368 | 1.3984 | 1.5684 | 1.389 | 1.4534 | 1.5215 | 1.5354 | 1.5737 | 1.6922 | 1.4488 | 1.6723 | 1.4159 | 1.3172 | 0.48107 | 0.47863 | 1.5846 | 1.5312 | 1.3759 | 0.83231 | 1.3848 | 1.6735 | 2.1997 | 1.3022 | 1.6741 | 1.5619 | 1.3319 | 1.3678 | 1.4981 | 1.2569 | 1.0775 | 0.50888 | 1.6308 | 1.365 | 1.1138 | 1.451 | 1.2048 | 1.473 | 1.3123 | 1.4122 | 1.5088 | 1.4921 | [8 empty] | 0 | 0 | [6 empty] | 1.5329 | 1.4698 | 1.5374 | 1.5693 | 1.5636 | 1.5765 | 1.5758 | 1.5597 | 1.7926 | 1.3862 | 1.105 | 1.6095 | 0.93895 | 1.573 | 1.7501 | 0.79387 | 1.6599 | 1.2668 | 1.6421 | 1.4108 | 2.0486 | 1.7141 | 1.6563 | 1.9088 | 16.3205 | 1.5451 | 1.7135 | 1.5841 | 0 | 0 | 0 | 0 | 7.0334 | 32.4592 | [6 empty] | 1.4931 | 1.4501 | 1.564 | 1.5422 | 1.4886 | 1.2755 | 1.6008 | 1.5578 | 0 | 0 | 0 | 0 | 1.668 | 2.4522 | 0.80891 | 1.8916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6398 | 2.6441 | 3.8907 | 2.0192 | 1.3003 | 1.5324 | 3.0062 | 3.8603 | 1.207 | 0.48864 | 1.5803 | 1.3019 | 1.7924 | 2.0755 | 2.3494 | 1.3984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1.5973 | 1.8472 | 1.112 | 0.26464 | 0.24994 | 0.76973 | 0.71171 | 1.2935 | 0.2753 | 0.37829 | 0.53748 | 0 | 0.078617 | 0 | 0 | 0.90521 | 1.8134 | 1.5351 | 1.6911 | 1.5266 | 1.3966 | 0.68107 | 1.5728 | 1.5152 | 1.4582 | 1.6244 | 1.4206 | 1.5752 | 1.4072 | 1.9863 | 1.6003 | 1.4033 | 0.51775 | 0 | 0.44471 | 0 | 0 | 0.020331 | 0.77973 | 1.378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9699
2025-06-16 | 1.9855 | 4.3474 | 4.4541 | 4.4258 | 4.5397 | 4.5659 | 2.9722 | 4.1252 | 4.6314 | 4.4456 | 4.6351 | 4.5123 | 4.5109 | 4.5691 | 4.1802 | 5.0509 | 4.513 | 4.2983 | 4.2548 | 4.5298 | 4.3345 | 4.4882 | 3.8909 | 4.476 | 4.143 | 4.5487 | 4.4939 | 4.5613 | 3.9609 | 4.0046 | 3.9241 | 4.3125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 4.1352 | 4.1454 | 4.159 | 4.1018 | 4.7392 | 3.5899 | 2.8408 | 4.2461 | 2.3942 | 4.081 | 4.5987 | 2.0393 | 4.3747 | 3.2834 | 4.3121 | 3.6705 | 5.4379 | 4.4517 | 4.282 | 4.9903 | 4.2424 | 4.0047 | 4.5199 | 4.1556 | 0 | 0 | 0 | 0 | 17.728 | 81.2288 | [6 empty] | 3.7812 | 3.6625 | 4.0015 | 3.9473 | 3.8005 | 3.1867 | 4.0083 | 3.9339 | 0 | 0 | 0 | 0 | 4.5583 | 6.7309 | 2.325 | 5.1967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7035 | 6.9225 | 10.1464 | 5.2034 | 3.2902 | 3.8728 | 7.6598 | 9.9751 | 3.0751 | 1.2808 | 4.1414 | 2.701 | 4.3051 | 5.5568 | 6.3336 | 4.2094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 4.109 | 4.6417 | 2.8392 | 0.78663 | 0.72998 | 1.9708 | 1.7799 | 2.9677 | 0.8099 | 1.0317 | 1.4335 | 0 | 0.29863 | 0 | 0 | 2.3236 | 4.6625 | 3.9635 | 4.4011 | 3.9692 | 3.6058 | 1.7462 | 4.0711 | 3.916 | 3.6362 | 4.105 | 3.5908 | 4.0694 | 3.6354 | 5.1613 | 4.1254 | 3.5794 | 1.3868 | 0 | 1.2472 | 0 | 0 | 0.12539 | 1.9611 | 3.4683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4863
2025-06-17 | 2.1974 | 4.781 | 4.8981 | 4.8553 | 4.9709 | 5.0077 | 3.4759 | 4.5367 | 5.0834 | 4.8995 | 5.1051 | 4.9542 | 4.9573 | 5.0685 | 4.6407 | 5.5263 | 4.9644 | 4.7322 | 4.6793 | 4.9887 | 4.792 | 4.9612 | 4.2993 | 4.9361 | 4.6326 | 5.0423 | 4.9879 | 5.0719 | 4.4025 | 4.4833 | 4.425 | 4.8559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 4.6005 | 4.6173 | 4.6403 | 4.575 | 5.2759 | 4.0191 | 3.1787 | 4.6928 | 2.6841 | 4.5623 | 5.1246 | 2.2712 | 4.8774 | 3.6674 | 4.806 | 4.1174 | 3.9241 | 3.2253 | 3.1034 | 3.6026 | 3.0276 | 2.8696 | 3.2214 | 2.9563 | 0 | 0 | 0 | 0 | 21.0223 | 95.4687 | [6 empty] | 4.4307 | 4.2981 | 4.6948 | 4.6121 | 4.4419 | 3.7243 | 4.6832 | 4.5942 | 0 | 0 | 0 | 0 | 5.1032 | 7.4856 | 2.6147 | 5.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.929 | 7.7445 | 11.4003 | 5.8629 | 3.7301 | 4.4178 | 8.724 | 11.3478 | 3.4735 | 1.4115 | 4.6608 | 2.7141 | 4.0214 | 6.2008 | 7.0419 | 4.6347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 4.4481 | 5.2429 | 3.2258 | 0.91192 | 0.84046 | 2.2388 | 2.0828 | 3.3478 | 0.92959 | 1.1752 | 1.6267 | 0 | 0.36215 | 0 | 0 | 2.6323 | 5.3101 | 4.5146 | 5.0012 | 4.5121 | 4.1004 | 1.9973 | 4.6367 | 4.4599 | 4.1857 | 4.6772 | 4.1262 | 4.6466 | 4.1402 | 5.8605 | 4.6852 | 4.0806 | 1.5805 | 0 | 1.4296 | 0 | 0 | 0.17206 | 2.2249 | 3.9304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0312
2025-06-18 | 2.6838 | 5.8193 | 5.9726 | 5.7908 | 5.8836 | 6.0138 | 4.2627 | 5.53 | 6.184 | 5.9279 | 6.1067 | 5.8911 | 6.0006 | 6.2574 | 5.7899 | 6.5533 | 5.9414 | 5.6527 | 5.6904 | 5.9176 | 5.7084 | 5.8882 | 5.2172 | 5.8947 | 5.6168 | 5.9344 | 5.8748 | 6.059 | 5.4027 | 5.4577 | 5.3932 | 5.9043 | 4.225 | 3.4118 | 4.4411 | 4.1569 | 3.1897 | 3.1921 | 4.2829 | 4.6196 | 1.819 | 1.8816 | 3.1949 | 3.3355 | 3.2774 | 3.2371 | 3.2176 | 3.1252 | 3.2378 | 3.114 | 3.1319 | 3.2577 | 4.7222 | 2.7246 | 3.3077 | 3.415 | 2.9988 | 1.8682 | 3.2165 | 3.2907 | 3.2833 | 3.2267 | 3.5356 | 2.9255 | 3.0172 | 3.0198 | 3.2807 | 3.2866 | 3.5425 | 3.5489 | 3.3031 | 3.7609 | [8 empty] | 0 | 0 | [6 empty] | 3.1442 | 3.1166 | 3.1998 | 3.2132 | 5.534 | 5.598 | 5.5667 | 5.5298 | 6.2433 | 4.9118 | 3.9011 | 5.6781 | 3.2727 | 5.5249 | 6.2465 | 2.794 | 5.9576 | 4.4788 | 5.8273 | 4.9959 | 7.7029 | 6.3214 | 6.0795 | 7.0394 | 5.932 | 5.6204 | 6.3028 | 5.8191 | 0 | 0 | 0 | 0 | 25.3925 | 115.1567 | [6 empty] | 5.3694 | 5.2206 | 5.6612 | 5.4984 | 7.4128 | 4.4941 | 5.6738 | 5.5848 | 6.4869 | 5.7878 | 4.9798 | 5.9365 | 6.108 | 8.9319 | 3.171 | 6.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3835 | 9.3493 | 13.8617 | 7.1677 | 4.551 | 5.372 | 10.6207 | 13.4494 | 4.2359 | 1.7337 | 5.6145 | 2.2833 | 4.933 | 7.5009 | 8.5312 | 5.7247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 5.7571 | 6.5363 | 4.0846 | 1.15 | 1.0591 | 2.7732 | 2.6251 | 4.2909 | 1.1553 | 1.4564 | 2.0151 | 0 | 0.46164 | 0 | 0.002547 | 3.219 | 6.2574 | 5.4632 | 5.9134 | 5.4167 | 4.9741 | 2.4306 | 5.5366 | 5.3712 | 5.1439 | 5.6901 | 5.0814 | 5.5877 | 4.9091 | 6.9799 | 5.6607 | 4.9816 | 1.9685 | 0 | 1.7874 | 0 | 0 | 0.2326 | 2.747 | 4.8228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0234
2025-06-19 | 2.72 | 5.8866 | 6.0899 | 5.9418 | 6.033 | 6.1473 | 4.284 | 5.5746 | 6.282 | 5.9926 | 6.2532 | 6.038 | 6.1403 | 6.2846 | 5.8249 | 6.7483 | 6.0689 | 5.7544 | 5.7409 | 6.0603 | 5.8277 | 5.9628 | 5.2561 | 6.0293 | 5.642 | 6.0911 | 6.0238 | 6.1933 | 5.4752 | 5.4882 | 5.4348 | 5.9351 | 3.747 | 3.5727 | 4.5333 | 4.2417 | 3.3354 | 3.3284 | 4.4026 | 4.7589 | 3.4267 | 3.4815 | 3.2809 | 3.3328 | 1.8287 | 1.8469 | 3.431 | 3.4056 | 3.3848 | 3.2443 | 3.288 | 3.4123 | 4.9249 | 2.7852 | 3.4503 | 3.5745 | 3.3267 | 3.3576 | 3.356 | 3.2307 | 3.1766 | 1.9024 | 3.6586 | 3.1903 | 3.0981 | 3.2419 | 3.2336 | 3.5052 | 3.655 | 3.5629 | 3.6009 | 3.803 | [8 empty] | 0 | 0 | [6 empty] | 3.3073 | 2.828 | 3.3763 | 3.3928 | 5.6491 | 5.6786 | 5.6771 | 5.6087 | 6.4105 | 4.9404 | 3.9253 | 5.8039 | 3.3038 | 5.5987 | 6.2758 | 2.8021 | 5.9717 | 4.4931 | 5.9157 | 5.0557 | 7.6966 | 6.3084 | 6.0514 | 7.0091 | 5.9323 | 5.6105 | 6.3132 | 5.8254 | 0 | 0 | 0 | 0 | 25.2665 | 114.2994 | [6 empty] | 5.3675 | 5.2126 | 5.6678 | 5.4152 | 5.3516 | 4.5051 | 5.6889 | 5.5767 | 6.9729 | 6.1467 | 5.3452 | 6.4201 | 6.1405 | 9.4433 | 3.1893 | 6.8905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3964 | 9.3992 | 14.0229 | 7.1958 | 4.5903 | 5.416 | 10.7015 | 13.7424 | 4.2686 | 1.7536 | 5.7329 | 2.1085 | 4.968 | 7.6599 | 8.4841 | 5.8003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 5.621 | 6.5142 | 4.1264 | 1.1546 | 0.89706 | 2.8036 | 2.6533 | 3.6062 | 1.1594 | 1.4612 | 2.0345 | 0 | 0.45727 | 0 | 2.2933 | 3.2329 | 6.293 | 5.518 | 6.0609 | 5.509 | 5.0185 | 2.4471 | 5.6403 | 5.4384 | 5.1529 | 5.6835 | 5.0926 | 5.6766 | 5.0212 | 7.1249 | 5.7257 | 4.9989 | 1.9838 | 0 | 1.8009 | 0 | 0 | 0.22293 | 2.7294 | 3.8127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0908
2025-06-20 | 2.4266 | 5.2627 | 5.4131 | 5.3111 | 5.4271 | 5.486 | 3.8165 | 4.9805 | 5.6027 | 5.3577 | 5.6042 | 5.4354 | 5.5083 | 5.6309 | 5.2047 | 6.0884 | 5.445 | 5.2051 | 5.1374 | 5.4428 | 5.2148 | 5.3359 | 4.7172 | 5.4198 | 5.0737 | 5.4947 | 5.4239 | 5.5597 | 4.9073 | 4.9562 | 4.9253 | 5.3428 | 3.9286 | 3.2388 | 4.0789 | 3.852 | 3.0235 | 3.01 | 3.994 | 4.3211 | 3.106 | 3.1637 | 2.9545 | 3.13 | 1.6381 | 1.6534 | 3.114 | 3.0889 | 3.014 | 2.4387 | 2.9075 | 3.1645 | 4.5394 | 2.9791 | 3.2145 | 3.1802 | 3.0256 | 3.0493 | 3.0404 | 2.9445 | 2.8778 | 1.7151 | 3.335 | 2.8957 | 2.815 | 2.9505 | 2.9548 | 3.1836 | 3.3465 | 3.2576 | 3.2693 | 3.4663 | [8 empty] | 0 | 0 | [6 empty] | 3.0066 | 2.9712 | 3.0597 | 3.0922 | 5.0687 | 5.1043 | 5.0993 | 5.0231 | 5.8052 | 4.4622 | 3.5351 | 5.2138 | 2.9904 | 5.0585 | 5.6726 | 2.53 | 5.4047 | 4.0741 | 5.3599 | 4.5856 | 6.7428 | 5.5252 | 5.3 | 6.1281 | 5.2391 | 4.9462 | 5.5466 | 5.1303 | 0 | 0 | 0 | 0 | 22.3633 | 100.9044 | [6 empty] | 4.7545 | 4.6155 | 5.0012 | 4.8017 | 4.7445 | 3.994 | 5.0351 | 4.9311 | 6.2449 | 5.4727 | 4.777 | 5.7561 | 5.5099 | 8.1384 | 2.8416 | 6.1874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1457 | 8.4075 | 12.5478 | 6.4505 | 4.1124 | 4.8626 | 9.5804 | 12.3022 | 3.8493 | 1.58 | 5.1462 | 1.8789 | 4.4503 | 6.8649 | 7.597 | 5.2034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 4.9699 | 5.8993 | 3.7308 | 1.035 | 0.80624 | 2.5255 | 2.388 | 3.1295 | 1.0403 | 1.3107 | 1.8252 | 0 | 0.053457 | 0 | 2.0501 | 2.8967 | 5.587 | 4.9042 | 5.4336 | 4.9183 | 4.5022 | 2.1917 | 5.0239 | 4.8359 | 4.5725 | 4.999 | 4.5231 | 5.042 | 4.4909 | 6.3587 | 5.0816 | 4.4381 | 1.7862 | 0 | 1.6256 | 0 | 0 | 0.19964 | 2.2018 | 3.4371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4569
2025-06-21 | 1.2697 | 2.8788 | 2.9293 | 2.9368 | 3.0209 | 3.0387 | 2.0992 | 2.7401 | 3.0716 | 2.9603 | 3.1053 | 3.0146 | 3.0166 | 3.0198 | 2.6929 | 3.3878 | 3.0025 | 2.8732 | 2.825 | 3.014 | 2.8864 | 2.9582 | 2.5948 | 2.9877 | 2.7824 | 3.0516 | 3.0154 | 3.078 | 0 | 2.7142 | 2.6898 | 2.912 | 2.3564 | 2.5151 | 2.3586 | 2.3659 | 2.3745 | 2.3451 | 2.618 | 2.8114 | 2.339 | 2.5698 | 2.2637 | 2.1482 | 0.85475 | 0.85511 | 2.4735 | 2.4176 | 2.2534 | 1.3586 | 2.2101 | 2.5707 | 3.4446 | 2.1794 | 2.5565 | 2.4489 | 2.1787 | 2.2341 | 2.3708 | 2.0792 | 1.8531 | 0.90435 | 2.5814 | 2.2028 | 1.8034 | 2.2151 | 2.0133 | 2.4019 | 2.2264 | 2.2914 | 2.458 | 2.4629 | [8 empty] | 0 | 0 | [6 empty] | 2.4743 | 2.3671 | 2.4397 | 2.512 | 2.7639 | 2.7761 | 2.78 | 2.7637 | 3.1896 | 2.3999 | 1.8873 | 2.8392 | 1.5973 | 2.7455 | 3.0693 | 1.3418 | 2.941 | 2.1916 | 2.9108 | 2.4777 | 3.0967 | 2.537 | 2.3679 | 2.8295 | 2.4199 | 2.2741 | 2.4992 | 2.3538 | 0 | 0 | 0 | 0 | 10.0881 | 45.6755 | [6 empty] | 1.2385 | 1.1981 | 1.3142 | 1.2496 | 1.2392 | 1.0384 | 1.3049 | 1.2861 | 3.4821 | 3.0099 | 2.6316 | 3.207 | 3.0325 | 4.505 | 1.5027 | 3.4647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94964 | 3.8639 | 5.7484 | 2.9336 | 1.8637 | 2.201 | 4.3232 | 5.6489 | 1.755 | 0.70157 | 2.3736 | 0.65569 | 2.0184 | 3.171 | 3.4452 | 2.4017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3433 | 2.0402 | 2.2848 | 2.0622 | 1.8738 | 0.90528 | 2.1045 | 2.019 | 2.2404 | 2.4716 | 2.2168 | 2.4955 | 1.5545 | 2.8351 | 2.2722 | 2.7582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9217
2025-06-22 | 2.4771 | 5.3109 | 5.4336 | 5.3942 | 5.548 | 5.6417 | 4.0802 | 5.0215 | 5.4168 | 5.4905 | 5.7919 | 5.6517 | 5.6585 | 5.7426 | 5.3331 | 6.3054 | 5.6044 | 5.3553 | 5.3083 | 5.5757 | 5.4059 | 5.5292 | 4.7927 | 5.5266 | 5.1189 | 5.5838 | 5.525 | 5.6232 | 3.4775 | 4.4397 | 4.4425 | 4.8233 | 3.9091 | 3.2148 | 4.0909 | 3.8142 | 3.0011 | 2.9907 | 3.9708 | 4.2554 | 3.0825 | 3.1509 | 3.1026 | 2.9855 | 1.6675 | 1.6821 | 3.0923 | 3.067 | 2.976 | 2.445 | 2.8749 | 3.1476 | 4.4629 | 2.9422 | 3.1874 | 3.113 | 2.9752 | 3.006 | 3.0176 | 2.9076 | 2.8389 | 1.7292 | 3.3064 | 2.8473 | 2.733 | 2.8893 | 2.7163 | 3.1186 | 3.2615 | 3.1696 | 3.2027 | 3.3876 | [8 empty] | 0 | 0 | [6 empty] | 3.0043 | 2.9395 | 3.0213 | 3.0601 | 5.2262 | 5.2395 | 5.2421 | 5.234 | 5.9792 | 4.5515 | 3.6163 | 5.368 | 3.0351 | 5.1554 | 5.5932 | 2.5506 | 5.4695 | 4.1055 | 5.389 | 4.619 | 6.8835 | 5.6256 | 5.2491 | 6.2416 | 5.3265 | 5.0328 | 5.5262 | 5.2187 | 0 | 0 | 0 | 0 | 22.9756 | 103.3323 | [6 empty] | 4.8324 | 4.6787 | 5.097 | 4.8722 | 4.8334 | 4.054 | 5.1374 | 5.0386 | 6.445 | 5.8449 | 4.8619 | 5.9068 | 5.6181 | 8.3093 | 2.9189 | 6.4102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3197 | 8.6961 | 12.9639 | 6.653 | 4.2356 | 5.0035 | 9.9015 | 12.704 | 3.9213 | 1.6031 | 5.2424 | 1.3701 | 4.5646 | 7.0846 | 7.7208 | 5.3491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7162 | 5.054 | 5.6384 | 5.0879 | 4.6273 | 2.2506 | 5.1565 | 4.9584 | 4.6951 | 5.2014 | 4.6267 | 5.1903 | 4.6523 | 6.5852 | 5.2481 | 4.5822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5184
2025-06-23 | 2.1641 | 4.9131 | 4.8721 | 4.8215 | 4.9415 | 4.9786 | 3.5502 | 4.4462 | 4.9906 | 4.8665 | 5.0899 | 4.9376 | 4.9622 | 5.0204 | 4.6386 | 5.5405 | 5.0892 | 4.7298 | 4.7942 | 4.9509 | 4.7982 | 4.905 | 4.2613 | 4.9181 | 4.5807 | 5.0037 | 4.9323 | 5.041 | 4.1198 | 4.4607 | 4.4286 | 4.8047 | 3.6087 | 3.1815 | 3.7264 | 3.5317 | 2.9732 | 2.9591 | 3.7405 | 4.0246 | 3.0138 | 3.1255 | 2.8947 | 2.8765 | 1.4469 | 1.4578 | 3.0651 | 3.0326 | 2.9145 | 2.2139 | 2.8262 | 3.1288 | 4.3747 | 2.8608 | 3.1519 | 3.0666 | 2.8867 | 2.9298 | 2.9947 | 2.8202 | 2.7013 | 1.5392 | 3.2741 | 2.8003 | 2.5985 | 2.8523 | 2.7797 | 3.0777 | 3.13 | 3.0909 | 3.1676 | 3.2993 | [8 empty] | 0 | 0 | [6 empty] | 2.9891 | 2.924 | 3.0028 | 3.0442 | 4.5657 | 4.5897 | 4.5937 | 4.5832 | 5.2583 | 3.9923 | 3.1554 | 4.6751 | 2.678 | 4.552 | 4.9462 | 2.273 | 4.8746 | 3.6513 | 4.8162 | 4.1161 | 6.1503 | 5.0388 | 4.5797 | 5.5936 | 4.7602 | 4.4913 | 4.9293 | 4.6599 | 0 | 0 | 0 | 0 | 20.1961 | 91.1646 | [6 empty] | 4.2999 | 4.1673 | 4.551 | 4.3275 | 4.2864 | 3.595 | 4.5509 | 4.4661 | 5.6178 | 4.8858 | 4.2636 | 5.1757 | 4.9256 | 7.2885 | 2.5234 | 5.5855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9864 | 7.5522 | 11.2316 | 5.7497 | 3.6635 | 4.3365 | 8.5657 | 11.066 | 3.4444 | 1.5656 | 4.6315 | 1.2081 | 3.9814 | 6.1773 | 6.7278 | 4.5519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0325 | 4.4006 | 4.891 | 4.4167 | 4.003 | 1.9462 | 4.5332 | 4.3577 | 4.1377 | 4.6008 | 4.0802 | 4.5327 | 4.0697 | 5.7139 | 4.5644 | 3.9686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9814
2025-06-24 | 2.4057 | 5.5774 | 5.4866 | 5.4462 | 5.6065 | 5.6482 | 4.1938 | 5.0731 | 5.6852 | 5.5047 | 5.7995 | 5.6473 | 5.678 | 5.7717 | 5.2486 | 6.3312 | 5.7589 | 5.3671 | 5.4072 | 5.5955 | 5.4179 | 5.5322 | 4.7985 | 5.559 | 5.1542 | 5.6377 | 5.5532 | 5.6696 | 4.8441 | 4.9939 | 4.9548 | 5.397 | 4.1129 | 3.4071 | 4.271 | 4.0072 | 3.1689 | 3.1594 | 4.1992 | 4.5145 | 3.2542 | 3.3033 | 3.1223 | 3.1682 | 1.705 | 1.7235 | 3.2549 | 3.2325 | 3.1472 | 2.514 | 4.5243 | 3.2973 | 4.7123 | 3.1213 | 3.3388 | 3.2774 | 3.1412 | 3.1767 | 3.1853 | 3.0804 | 2.9906 | 1.6525 | 3.4856 | 2.9824 | 2.8761 | 3.0545 | 3.0384 | 3.2765 | 3.4404 | 3.348 | 3.3811 | 3.5751 | [8 empty] | 0 | 0 | [6 empty] | 3.1308 | 3.08 | 3.1687 | 3.202 | 5.1892 | 5.1958 | 5.2381 | 5.2161 | 5.958 | 4.5303 | 3.6046 | 5.362 | 3.0237 | 5.1334 | 5.5864 | 2.5267 | 5.4727 | 4.1103 | 5.4326 | 4.6367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64046 | 0.53381 | 0.43832 | 0.59479 | 5.5543 | 8.3512 | 2.9091 | 6.4434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1623
2025-06-25 | 2.1822 | 5.0174 | 4.9752 | 4.9476 | 4.7123 | 4.7781 | 3.7324 | 4.3947 | 5.145 | 4.9612 | 5.2295 | 4.6837 | 4.7508 | 5.213 | 4.7419 | 5.7089 | 5.1909 | 4.8437 | 4.896 | 5.0621 | 4.8873 | 4.9812 | 4.3124 | 5.0054 | 4.7661 | 5.0654 | 5.0377 | 4.5504 | 4.3306 | 4.0183 | 4.4556 | 4.8395 | 3.6396 | 3.0807 | 3.8189 | 3.5646 | 2.8831 | 2.8673 | 3.7236 | 3.9977 | 2.9408 | 3.0432 | 2.8275 | 2.8335 | 1.5426 | 1.5602 | 2.9741 | 2.9449 | 2.8501 | 2.2617 | 2.7604 | 3.0462 | 4.2762 | 2.8106 | 3.0652 | 2.9821 | 2.8429 | 2.8415 | 2.917 | 2.7872 | 2.6907 | 1.4469 | 3.1984 | 2.7103 | 2.5823 | 2.796 | 2.7585 | 3.0119 | 3.1112 | 3.0544 | 3.0987 | 3.2528 | [8 empty] | 0 | 0 | [6 empty] | 2.9 | 2.8384 | 2.9164 | 2.9583 | 4.705 | 4.7147 | 4.7417 | 3.8843 | 5.0936 | 4.0998 | 3.2622 | 3.9937 | 2.7421 | 4.6599 | 5.0342 | 1.8297 | 4.8894 | 3.7039 | 4.8975 | 3.3849 | 6.4166 | 5.26 | 4.7648 | 5.8354 | 4.9513 | 4.6707 | 5.1379 | 4.8663 | 0 | 0 | 0 | 0 | 20.7301 | 86.1959 | [6 empty] | 4.0149 | 4.2377 | 4.6338 | 4.412 | 4.4097 | 3.6562 | 4.6437 | 4.2976 | 5.9356 | 4.5632 | 2.9582 | 5.446 | 4.1144 | 7.6535 | 2.2266 | 5.8756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5178 | 7.1028 | 8.9207 | 5.9667 | 3.682 | 4.4971 | 8.8914 | 9.3655 | 3.5512 | 1.0973 | 4.3509 | 1.0831 | 4.0945 | 6.0118 | 6.9617 | 3.6178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1541 | 4.7342 | 5.1753 | 4.6693 | 4.2491 | 2.074 | 4.7559 | 4.6789 | 4.3029 | 4.8045 | 4.2709 | 4.7587 | 4.275 | 6.0388 | 4.8935 | 4.2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8934
2025-06-26 | 2.2455 | 5.1218 | 5.1198 | 5.0904 | 5.1628 | 4.6915 | 3.9532 | 4.7003 | 4.5155 | 4.3861 | 4.3947 | 4.4539 | 4.5299 | 4.6286 | 4.1779 | 4.997 | 3.5406 | 3.2827 | 3.3125 | 3.4193 | 3.2984 | 3.4113 | 2.9601 | 3.4252 | 4.2774 | 4.522 | 4.5318 | 4.5848 | 3.9202 | 4.0272 | 4.0744 | 4.4269 | 3.4064 | 2.979 | 3.5594 | 3.3624 | 2.7766 | 2.7831 | 3.5666 | 3.8279 | 2.8527 | 2.9359 | 2.7387 | 2.7384 | 1.3664 | 1.3746 | 2.8785 | 3.0082 | 2.7692 | 2.012 | 2.6768 | 2.9387 | 4.1385 | 2.7172 | 2.968 | 2.8993 | 2.7536 | 3.0298 | 2.83 | 2.8519 | 2.5624 | 1.2845 | 3.1068 | 2.6401 | 2.4792 | 2.7147 | 2.6614 | 2.9278 | 2.9911 | 2.956 | 3.0127 | 3.1566 | [8 empty] | 0 | 0 | [6 empty] | 3.3618 | 3.1752 | 3.1801 | 3.3449 | 4.2087 | 3.9569 | 4.2584 | 4.2463 | 4.8447 | 3.7124 | 2.9264 | 4.3378 | 2.4766 | 4.1788 | 4.5029 | 2.0239 | 4.3896 | 3.324 | 4.1357 | 3.7906 | 5.6447 | 4.6236 | 4.2036 | 5.1476 | 4.3574 | 4.1281 | 4.5368 | 4.2861 | 0 | 0 | 0 | 0 | 18.5991 | 83.4859 | [6 empty] | 3.9243 | 3.8103 | 4.1345 | 3.9095 | 3.8751 | 3.2249 | 4.1129 | 4.0859 | 6.2121 | 4.7734 | 3.0654 | 5.6726 | 4.2889 | 7.9803 | 2.3362 | 6.1288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3417 | 6.9714 | 10.4412 | 5.3321 | 3.3693 | 3.985 | 7.9092 | 10.2664 | 3.0846 | 1.2769 | 4.3273 | 0.96873 | 3.2925 | 5.7355 | 6.2159 | 4.0789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6143 | 4.2776 | 4.6205 | 4.1576 | 3.6111 | 1.8557 | 4.2871 | 4.2317 | 3.8362 | 4.336 | 3.8281 | 4.2633 | 3.825 | 5.401 | 4.4123 | 3.6115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5988
2025-06-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5083 | 3.3965 | 3.5601 | 3.415 | 3.4533 | 3.4167 | 3.0535 | 3.8859 | 3.0297 | 2.8067 | 2.8468 | 2.9338 | 2.8401 | 2.903 | 2.1379 | 2.9109 | 3.2374 | 3.4475 | 3.4384 | 3.4506 | 2.942 | 3 | 3.026 | 3.3144 | 2.5879 | 2.5087 | 2.733 | 3.5889 | 2.3185 | 2.3626 | 2.7765 | 2.9941 | 2.2989 | 2.4624 | 2.2515 | 2.1611 | 1.1731 | 1.0144 | 1.6471 | 3.1685 | 2.2487 | 1.5367 | 2.195 | 2.4991 | 3.4038 | 0.12437 | 2.4926 | 2.3862 | 0.091633 | 2.1941 | 0.10016 | 2.0925 | 1.9055 | 0.91986 | 2.5477 | 2.0941 | 1.9114 | 1.8871 | 2.0638 | 2.3202 | 2.2943 | 2.2976 | 2.414 | 2.4852 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 2.3303 | 2.3404 | 2.3543 | 2.3381 | 2.6983 | 2.0333 | 1.5926 | 2.379 | 1.8377 | 3.0847 | 3.2266 | 1.5149 | 3.3465 | 2.5357 | 3.3565 | 2.817 | 3.0587 | 2.5012 | 2.2592 | 2.7738 | 2.354 | 2.2288 | 2.4549 | 2.323 | 0 | 0 | 0 | 0 | 10.1317 | 45.5031 | [6 empty] | 2.1232 | 2.0477 | 2.2541 | 2.11 | 2.1206 | 1.762 | 2.2343 | 2.2201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.47406 | 3.7781 | 5.6279 | 2.8548 | 1.7537 | 2.0692 | 4.2213 | 5.5452 | 1.6519 | 0.65729 | 1.5024 | 0.4956 | 1.7516 | 3.1232 | 3.3884 | 2.2165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.015 | 1.8657 | 2.0697 | 1.8665 | 1.6673 | 0.82094 | 1.868 | 1.8395 | 2.0762 | 2.3616 | 2.0947 | 2.3504 | 2.0897 | 2.9605 | 2.3683 | 1.5832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9975
2025-06-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5466 | 5.2893 | 5.5161 | 5.2592 | 5.4602 | 5.5508 | 5.1476 | 5.6714 | 5.4317 | 5.078 | 4.9876 | 5.3153 | 5.145 | 5.2456 | 4.5664 | 5.2188 | 2.5382 | 2.6647 | 2.3733 | 2.7064 | 2.3352 | 2.3888 | 2.4157 | 2.3526 | 3.7425 | 3.2499 | 4.0313 | 3.7023 | 3.0032 | 3.0307 | 3.8382 | 4.1757 | 3.0766 | 3.1847 | 2.9427 | 2.9471 | 1.6314 | 1.6644 | 3.1163 | 3.0871 | 2.9634 | 2.2414 | 2.8807 | 3.1892 | 4.4356 | 2.906 | 3.1995 | 3.1153 | 1.5441 | 2.3123 | 2.9364 | 2.4958 | 2.6757 | 1.4693 | 3.35 | 2.7843 | 2.7948 | 2.9133 | 2.83 | 3.1138 | 3.1794 | 3.1143 | 3.2122 | 3.3323 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 1.4436 | 1.4462 | 1.4616 | 1.4397 | 1.6609 | 1.2496 | 0.98501 | 1.4784 | 2.8825 | 4.7985 | 5.0672 | 2.4263 | 5.2107 | 3.9458 | 5.1438 | 4.3452 | 2.1917 | 1.7903 | 1.636 | 2.0128 | 1.7062 | 1.6145 | 1.7605 | 1.6517 | 0 | 0 | 0 | 0 | 8.7823 | 47.7884 | [6 empty] | 4.8787 | 4.719 | 5.1738 | 4.9694 | 4.891 | 4.0374 | 5.1037 | 5.0331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5963 | 8.2662 | 12.2496 | 2.1559 | 3.9 | 4.6229 | 9.3712 | 10.4641 | 3.5545 | 1.4484 | 4.933 | 0.66555 | 3.7896 | 6.6555 | 7.3296 | 4.2479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4974 | 5.1009 | 4.5629 | 5.1021 | 4.5292 | 6.4087 | 5.1037 | 4.1647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.061
2025-06-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0316 | 3.0044 | 3.0554 | 3.0115 | 2.7716 | 2.8187 | 3.2873 | 3.5539 | 2.8753 | 3.0763 | 2.7799 | 2.6991 | 1.149 | 1.1631 | 2.996 | 2.9454 | 2.6715 | 1.6677 | 2.609 | 2.966 | 4.0513 | 2.6976 | 2.9624 | 2.8371 | 2.2192 | 2.61 | 2.6352 | 2.4422 | 2.1511 | 0.97597 | 3.0171 | 2.4681 | 2.184 | 2.5781 | 2.39 | 2.7115 | 2.6196 | 2.6553 | 2.8352 | 2.8996 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6833 | 3.0218 | 2.744 | 3.3486 | 2.8198 | 2.6584 | 2.9498 | 2.7981 | 0 | 0 | 0 | 0 | 16.6555 | 77.0658 | [6 empty] | 3.3877 | 3.2133 | 3.6695 | 3.6176 | 3.3847 | 2.9871 | 3.7905 | 3.4811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3707 | 3.8181 | 3.3887 | 3.7497 | 3.326 | 4.6959 | 3.7758 | 2.6637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3336
2025-06-30 | 2.0913 | 4.6799 | 4.6771 | 3.9497 | 4.6994 | 0 | 3.5805 | 4.191 | 4.8216 | 4.6724 | 4.8894 | 4.7007 | 4.8013 | 4.9866 | 4.4927 | 5.3369 | 4.7832 | 4.4257 | 4.4832 | 4.6326 | 4.4983 | 4.618 | 3.9902 | 4.5902 | 4.4959 | 4.6435 | 4.6193 | 4.6927 | 4.0537 | 3.9413 | 4.1293 | 4.5003 | 3.6145 | 3.9153 | 3.6443 | 3.5334 | 3.5192 | 3.6266 | 4.0319 | 4.3945 | 3.6982 | 4.1645 | 3.577 | 3.3951 | 1.4136 | 1.4229 | 3.884 | 3.8176 | 3.4765 | 2.127 | 3.4191 | 3.9597 | 5.3384 | 3.4013 | 3.9112 | 3.7593 | 3.3292 | 3.4714 | 3.5393 | 3.2348 | 2.7768 | 1.2775 | 4.0692 | 3.1415 | 2.7821 | 3.4 | 3.0804 | 3.5248 | 3.3339 | 3.5246 | 3.7018 | 3.7604 | [8 empty] | 0 | 0 | [6 empty] | 1.4759 | 0.16786 | 0.18075 | 0.19023 | 4.4323 | 4.4636 | 4.4915 | 3.7092 | 5.1128 | 3.9003 | 3.0927 | 4.5584 | 2.5871 | 4.2752 | 4.5172 | 2.1937 | 4.6931 | 3.5349 | 4.637 | 3.8972 | 5.3577 | 4.3513 | 3.9755 | 4.9057 | 4.178 | 3.9428 | 4.3574 | 4.1197 | 0 | 0 | 0 | 0 | 17.0017 | 76.7508 | [6 empty] | 3.594 | 3.4522 | 3.8543 | 3.7671 | 3.6726 | 3.1241 | 3.9342 | 3.7619 | 5.4614 | 4.1377 | 2.7188 | 4.9904 | 3.7638 | 6.9823 | 2.0473 | 5.3957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4576 | 7.3459 | 10.8723 | 4.5782 | 3.4624 | 4.0774 | 8.2522 | 10.5813 | 3.2452 | 1.3669 | 4.4901 | 0.94081 | 3.4656 | 5.9879 | 6.5723 | 4.3182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 4.3798 | 2.5588 | 3.2489 | 0.90757 | 0.69211 | 2.1973 | 1.976 | 2.5898 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7225 | 4.2195 | 3.753 | 4.2541 | 3.8177 | 5.4413 | 4.3391 | 4.3391 | 0.73947 | 0 | 0 | 0 | 0 | 0 | 0.5199 | 0.77137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6686
2025-07-01 | 2.3814 | 5.2505 | 5.3354 | 4.9875 | 5.0572 | 0 | 4.0524 | 4.6604 | 5.2543 | 5.12 | 5.2812 | 5.0372 | 5.174 | 5.6297 | 5.0658 | 5.6826 | 5.2547 | 4.9062 | 5.0289 | 5.2284 | 5.0466 | 5.0912 | 4.345 | 4.978 | 4.9716 | 5.1401 | 5.1332 | 5.2174 | 4.5427 | 4.5367 | 4.7531 | 5.1153 | 4.6364 | 5.0495 | 4.4058 | 4.4439 | 4.6576 | 4.8027 | 4.9685 | 5.3869 | 1.5917 | 1.6453 | 4.8295 | 4.9338 | 4.5899 | 5.0823 | 4.5764 | 4.0615 | 4.4058 | 2.4728 | 4.3438 | 5.2222 | 6.7699 | 4.2828 | 5.1219 | 4.7892 | 4.0509 | 4.2519 | 4.3975 | 3.9449 | 3.2834 | 1.4492 | 5.0929 | 4.423 | 3.3587 | 4.3091 | 3.7466 | 4.4604 | 4.1432 | 4.2788 | 4.7659 | 4.7427 | [8 empty] | 0 | 0 | [6 empty] | 5.0113 | 4.5417 | 4.8788 | 5.0594 | 4.7685 | 4.8157 | 4.8006 | 4.0887 | 5.4233 | 4.311 | 3.4274 | 4.8979 | 2.8776 | 4.6563 | 4.9492 | 2.4266 | 5.1299 | 3.8933 | 4.9741 | 4.2742 | 6.3605 | 5.1981 | 4.7774 | 5.7568 | 4.8516 | 4.7079 | 5.1351 | 4.8646 | 0 | 0 | 0 | 0 | 21.2835 | 95.9514 | [6 empty] | 4.542 | 4.4574 | 4.733 | 4.6064 | 4.5361 | 3.9241 | 4.9066 | 4.7667 | 5.8612 | 4.6378 | 3.0731 | 5.431 | 4.3162 | 7.7581 | 2.3404 | 5.8033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6426 | 7.9873 | 11.8964 | 5.1444 | 3.8827 | 4.579 | 9.2853 | 11.5366 | 3.5892 | 1.5078 | 4.8188 | 1.0449 | 3.8835 | 6.4622 | 7.1626 | 4.6786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 4.3412 | 2.4411 | 3.5559 | 0.9998 | 0.76353 | 2.4222 | 2.1823 | 2.8464 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3612 | 0.017391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3356 | 4.9011 | 4.3608 | 4.8926 | 4.3662 | 6.1862 | 4.9359 | 4.0186 | 0.80785 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6219
2025-07-02 | 1.4052 | 3.3445 | 3.2127 | 3.1721 | 3.2669 | 0 | 2.4544 | 2.8994 | 3.3381 | 3.2489 | 3.4062 | 3.2619 | 3.2833 | 3.4087 | 2.9911 | 3.7016 | 0 | 0 | 0 | 0 | 3.2238 | 3.2993 | 2.8278 | 3.2583 | 3.1232 | 3.321 | 3.3212 | 3.3357 | 2.8598 | 2.7941 | 2.9129 | 3.156 | 2.6741 | 3.1991 | 2.653 | 2.6854 | 2.9449 | 3.0578 | 3.0328 | 3.2741 | 0.94639 | 0.97406 | 3.0864 | 3.1323 | 2.8634 | 3.284 | 2.873 | 2.5006 | 2.7559 | 1.5037 | 2.7326 | 3.3687 | 4.2268 | 2.6366 | 3.2751 | 3.0215 | 2.4919 | 2.6589 | 2.7385 | 2.4123 | 1.9997 | 0.85789 | 3.2258 | 2.5334 | 2.0848 | 2.7123 | 2.3029 | 2.7756 | 2.5538 | 2.6338 | 2.9732 | 2.8639 | [8 empty] | 1.2116 | 1.3288 | [6 empty] | 3.2278 | 2.854 | 3.1129 | 3.2532 | 3.0443 | 3.0579 | 3.0737 | 2.5327 | 3.5176 | 2.6487 | 2.0892 | 3.1303 | 1.7608 | 2.9366 | 3.0772 | 1.481 | 3.2251 | 2.4064 | 3.0919 | 2.6745 | 4.0601 | 3.3239 | 3.0125 | 3.7033 | 3.0753 | 2.9738 | 3.296 | 3.1059 | 0 | 0.22434 | 0 | 0 | 13.3891 | 60.373 | [6 empty] | 2.8534 | 2.7561 | 3.0195 | 2.8702 | 2.8529 | 2.3898 | 3.0221 | 2.9717 | 3.7663 | 2.8248 | 1.848 | 3.4598 | 2.5892 | 4.8507 | 1.3516 | 3.7436 | 0 | 0 | 0 | 0.1801 | 0.18348 | 0.11656 | 0 | 0 | 0.92547 | 5.0656 | 7.5145 | 3.1479 | 2.3781 | 2.7997 | 5.6719 | 7.4529 | 2.1985 | 0.90204 | 3.0833 | 0.61233 | 2.3648 | 4.1328 | 4.5028 | 2.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0.78981 | 0 | 2.0378 | 2.142 | 2.0931 |  | 0 | 0 | 2.3836 | 0 | 2.1744 | 0.57478 | 0.43625 | 1.468 | 1.3082 | 1.7417 | 0 | 0.39608 | 0 | 0 | 0 | 0 | 0.79928 | 1.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6891 | 0 | 0 | 3.029 | 2.7013 | 3.8313 | 3.065 | 2.4238 | 0.4576 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25256 | 1.7836 | 0 | 0 | 0 | 0 | 1.0849 | 1.5964 | 1.1241 | 1.3571 | 1.4346 | 1.6263 | 2.0052 | 7 |  | 0 | 0 | 2.3865 | 2.0385 | 2.1613 | 0 | 1.0097 | 1.0291 | 1.7153 | 2.2018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 1.5389 | 1.4372 | 1.7138 | 7.3403 |  |  |  | 7.5869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9446 | 1.9621 | 1.8536 | 3.5365 | 1.3304 | 0.63197 | 1.6855 | 1.4089 | 0 | 0 | 0 | 0 | 0.37235 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9555 | 2.4583 | 2.642 | 2.4389 | 2.0307 | 3.2735 | 2.0632 | 1.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.394
2025-07-03 | 1.1606 | 2.3999 | 2.4652 | 2.2111 | 2.2353 | 0.53372 | 1.8185 | 2.0921 | 2.3475 | 2.2932 | 2.3504 | 2.2412 | 2.2603 | 2.6074 | 2.4628 | 2.5185 | 1.9662 | 2.1143 | 2.1746 | 2.1989 | 2.2301 | 2.2821 | 2.0168 | 2.2493 | 2.2171 | 2.2655 | 2.2795 | 2.3212 | 2.0292 | 2.0785 | 2.1645 | 2.3161 | 2.0728 | 2.2571 | 2.0892 | 2.0854 | 2.0817 | 2.1367 | 2.3046 | 2.487 | 0.77405 | 0.79914 | 2.1252 | 2.2127 | 2.0712 | 2.2736 | 2.0529 | 1.8495 | 1.9833 | 1.1816 | 1.9453 | 2.3125 | 3.0194 | 1.9129 | 2.2943 | 2.1526 | 1.8421 | 2.0236 | 1.9761 | 1.7946 | 1.537 | 0.70187 | 2.3298 | 1.9002 | 1.6205 | 1.9998 | 1.7257 | 2.0392 | 1.9332 | 1.9672 | 2.1312 | 2.094 | [8 empty] | 2.3378 | 2.5907 | [6 empty] | 2.2309 | 2.0312 | 2.1811 | 2.2554 | 2.1129 | 2.1457 | 2.1243 | 1.8501 | 2.4017 | 2.2255 | 1.5786 | 2.1652 | 1.3591 | 2.088 | 2.2383 | 1.1614 | 2.2906 | 1.7839 | 2.1771 | 1.9274 | 2.7775 | 2.2647 | 2.1072 | 2.5151 | 2.1519 | 2.0895 | 2.2587 | 2.1377 | 0 | 0.41813 | 0 | 0 | 9.217 | 41.7947 | [6 empty] | 1.9964 | 1.9767 | 2.0701 | 2.0367 | 2.0073 | 2.317 | 2.1931 | 2.1115 | 2.5977 | 2.1037 | 1.4341 | 2.3918 | 2.0077 | 3.4256 | 1.1275 | 2.5645 | 0 | 0 | 0 | 0.33065 | 0.33561 | 0.28527 | 0 | 0 | 0.79371 | 3.5597 | 5.2549 | 2.3662 | 1.8097 | 2.1323 | 4.307 | 5.0554 | 1.688 | 0.74404 | 2.144 | 0.50493 | 1.8574 | 2.855 | 3.2059 | 2.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.0548 | 0 | 3.0895 | 3.5819 | 3.0053 |  | 0 | 0 | 1.5408 | 0.93594 | 1.6962 | 0.4774 | 0.36372 | 1.161 | 1.0475 | 1.3512 | 0.081746 | 0.33103 | 0 | 0 | 0 | 0 | 0.65057 | 0.84087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1318 | 1.8758 | 1.6639 | 2.4128 | 2.1565 | 3.0522 | 2.4263 | 1.8849 | 0.38295 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22696 | 2.4155 | 0 | 0 | 0 | 0 | 1.5479 | 2.1776 | 1.629 | 1.9916 | 2.0072 | 2.2732 | 2.7484 | 10.54 |  | 0 | 0 | 3.0312 | 2.5811 | 2.7224 | 0 | 1.4021 | 1.4555 | 2.2054 | 2.7864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 1.7338 | 1.6552 | 1.9053 | 8.255 |  |  |  | 8.4291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5024 | 2.2905 | 2.0218 | 4.0504 | 1.5034 | 0.7832 | 1.886 | 1.6305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0191 | 2.4396 | 2.5567 | 2.3539 | 2.0619 | 3.2897 | 2.0554 | 1.9803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4381
2025-07-04 | 1.4387 | 3.5649 | 3.6382 | 3.4063 | 3.4472 | 0.43469 | 2.6995 | 2.1757 | 3.5672 | 2.5224 | 3.5455 | 3.3929 | 3.3303 | 3.8406 | 3.0433 | 3.8524 | 2.9774 | 3.2653 | 3.4838 | 3.5794 | 3.4805 | 3.5501 | 3.0838 | 3.5142 | 3.3731 | 3.527 | 3.5385 | 3.5762 | 3.0562 | 2.9851 | 3.0463 | 3.4269 | 2.9579 | 3.4453 | 3.0415 | 3.0258 | 3.1171 | 3.2304 | 3.3288 | 3.6423 | 0.86995 | 0.91473 | 3.168 | 3.2866 | 3.027 | 3.397 | 3.0405 | 2.7052 | 2.9049 | 1.6479 | 2.9381 | 3.5106 | 4.4981 | 2.8004 | 3.3759 | 3.0998 | 2.7438 | 2.9409 | 2.9016 | 2.6423 | 2.2242 | 0.71682 | 3.5722 | 2.8529 | 2.3928 | 3.7254 | 2.598 | 3.0961 | 2.8813 | 2.8905 | 3.3293 | 3.1009 | [8 empty] | 2.5784 | 2.2373 | [6 empty] | 2.2444 | 1.9988 | 2.2762 | 1.9948 | 3.2323 | 3.3034 | 3.3039 | 2.7631 | 3.6937 | 2.9451 | 2.3461 | 3.2626 | 2.0225 | 3.1857 | 3.3655 | 1.6806 | 3.4587 | 2.6402 | 3.3014 | 2.8031 | 4.2912 | 3.4205 | 3.2287 | 3.9553 | 3.268 | 3.1584 | 3.4708 | 3.2396 | 0 | 0.52809 | 0 | 0 | 13.4375 | 61.058 | [6 empty] | 3.0213 | 2.9297 | 3.1365 | 3.0442 | 2.9925 | 2.5106 | 3.1614 | 2.9302 | 3.973 | 3.1803 | 2.1321 | 3.6275 | 2.9854 | 5.3034 | 1.1724 | 3.9418 | 0 | 0 | 0 | 0.38468 | 0.37844 | 0.29838 | 0 | 0 | 0.63555 | 5.2875 | 7.8197 | 3.3937 | 2.5496 | 2.957 | 4.8833 | 5.3811 | 1.5265 | 0.66223 | 2.141 | 0.50411 | 1.7648 | 2.937 | 3.4014 | 2.0428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.012 | 0 | 2.9553 | 4.6932 | 3.0233 |  | 0 | 0 | 1.4566 | 1.068 | 1.6724 | 0.56659 | 0.5663 | 1.2732 | 1.0077 | 1.3803 | 0.087051 | 0.39193 | 0 | 0 | 0 | 0 | 0.5529 | 0.97582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2159 | 1.9093 | 1.5341 | 2.3633 | 2.2008 | 2.9572 | 2.4768 | 1.9525 | 0.42472 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11432 | 2.3681 | 0 | 0 | 0 | 0 | 1.6365 | 2.116 | 1.5683 | 1.8678 | 1.698 | 2.2532 | 2.6515 | 11.5078 |  | 0 | 0 | 3.3615 | 2.5157 | 2.8213 | 0 | 1.341 | 1.241 | 2.1014 | 2.6788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 1.9002 | 1.5582 | 1.9892 | 7.5862 |  |  |  | 8.4779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1223 | 2.5477 | 2.1308 | 4.3098 | 1.4107 | 0.84263 | 1.7973 | 1.3336 | 0 | 0 | 0 | 0 | 0.44193 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1237 | 2.4826 | 2.6332 | 2.4156 | 2.0611 | 3.6617 | 2.0607 | 2.1776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5051
2025-07-05 | 2.0703 | 3.7022 | 3.8705 | 3.5076 | 3.5624 | 3.6256 | 2.8546 | 3.2704 | 3.7077 | 3.6144 | 3.728 | 3.5417 | 3.5218 | 4.1024 | 4.4196 | 3.9678 | 3.171 | 3.4543 | 3.5567 | 3.6254 | 3.5642 | 3.6478 | 3.1998 | 3.5951 | 3.4514 | 3.6061 | 3.6219 | 3.6766 | 3.1932 | 3.2387 | 3.2906 | 3.622 | 3.3021 | 3.4945 | 3.238 | 3.2632 | 3.2373 | 3.4919 | 3.6286 | 3.8996 | 1.4463 | 1.4579 | 3.2828 | 3.4401 | 3.2147 | 3.5514 | 3.207 | 2.8871 | 3.1193 | 1.9467 | 3.016 | 3.6055 | 4.6966 | 3.0024 | 3.5827 | 3.3554 | 2.8873 | 3.0824 | 3.0748 | 2.848 | 2.4758 | 1.3884 | 3.6319 | 2.9437 | 2.5132 | 3.0189 | 2.6585 | 3.1498 | 3.028 | 3.0788 | 3.3458 | 3.2738 | [8 empty] | 2.0969 | 2.7801 | [6 empty] | 5.4793 | 4.7844 | 5.2837 | 5.4896 | 3.2739 | 3.3121 | 3.2891 | 2.8114 | 3.7148 | 3.0313 | 2.4787 | 3.3847 | 2.1461 | 3.2109 | 3.4761 | 1.9359 | 3.5876 | 2.7621 | 3.3686 | 2.8384 | 4.1563 | 3.3425 | 3.1481 | 3.8176 | 3.2221 | 3.0812 | 3.5455 | 3.1697 | 0 | 0 | 0 | 0 | 13.8962 | 62.9404 | [6 empty] | 2.9871 | 2.9501 | 3.0754 | 3.026 | 2.959 | 2.7078 | 3.2956 | 3.1765 | 4.1005 | 3.254 | 2.2473 | 3.7985 | 3.2215 | 5.718 | 2.1923 | 4.0942 | 0 | 0 | 0 | 0.30684 | 0.84345 | 0.65745 | 0 | 0 | 1.5617 | 5.4846 | 8.1411 | 3.7072 | 2.8917 | 3.4404 | 6.9107 | 7.8934 | 2.6709 | 1.3976 | 3.2265 | 1.061 | 2.9448 | 4.6173 | 4.9433 | 3.1764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 3.4908 | 2.6825 | 4.7582 | 6.4832 | 4.5833 |  | 4.6686 | 4.8786 | 2.9071 | 2.5512 | 2.8499 | 1.0816 | 0.82149 | 2.0414 | 2.0227 | 2.2168 | 0.24789 | 0.74796 | 0 | 0 | 0 | 0 | 1.3761 | 1.5198 | 1.7261 | 1.7577 | 1.9068 | 1.8584 | 0 | 0 | 0 | 0 | 3.8265 | 4.2161 | 3.7765 | 4.1803 | 3.7179 | 5.2561 | 4.2217 | 3.4191 | 0.82716 | 0 | 0 | 0 | 0 | 0 | 0 | 0.514 | 3.7584 | 0 | 0 | 0 | 0 | 2.4832 | 3.3806 | 2.5843 | 3.2272 | 2.274 | 3.5507 | 4.1357 | 22.1379 |  | 4.492 | 2.531 | 4.0193 | 3.4651 | 3.6565 | 0 | 2.2153 | 2.3247 | 3.3654 | 4.3078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 4.3163 | 4.0446 | 4.7986 | 20.5876 |  |  |  | 21.0892 | 1.9691 | 4.4591 | 4.6153 | 1.9692 | 6.0493 | 5.2122 | 4.563 | 5.5311 | 7.4062 | 3.7647 | 3.1781 | 6.6606 | 1.6383 | 1.6467 | 3.7861 | 2.9841 | 4.9141 | 3.8724 | 0 | 3.3956 | 1.0028 | 0 | 0 | 0 | 4.4682 | 4.0096 |  | 4.9337 | 5.9773 | 5.1322 | 4.2116 | 3.9243 | 6.4347 | 9.8435 | 3.2168 | 5.8863 | 7.1009 | 0 | 7.1268 | 8.7432 | 4.9665 | 6.2298 | 6.7484 | 6.1695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8751
2025-07-06 | 2.1144 | 3.5416 | 3.7912 | 3.2834 | 3.3117 | 3.4216 | 2.7984 | 3.1047 | 3.4808 | 3.3806 | 3.4683 | 3.3004 | 3.3383 | 4.0308 | 4.5232 | 3.7292 | 2.9924 | 3.2131 | 3.3099 | 3.3627 | 3.3175 | 3.381 | 3.0033 | 3.355 | 3.2728 | 3.3551 | 3.348 | 3.4146 | 2.9778 | 3.0818 | 3.0918 | 3.4578 | 3.2674 | 3.3147 | 3.3564 | 3.2088 | 3.0695 | 3.1489 | 3.5326 | 3.8041 | 1.4427 | 1.4664 | 3.1187 | 3.2693 | 3.07 | 3.3305 | 3.0532 | 2.7732 | 2.9638 | 1.9303 | 2.8917 | 3.3998 | 4.4959 | 2.8827 | 3.3623 | 3.1665 | 2.7985 | 2.967 | 2.923 | 2.7474 | 2.3997 | 1.3857 | 3.4698 | 2.5731 | 2.4959 | 2.9245 | 2.6012 | 3.0423 | 2.9308 | 2.8936 | 3.1768 | 3.1543 | [8 empty] | 3.8738 | 4.946 | [6 empty] | 3.2052 | 2.9428 | 3.2197 | 3.288 | 3.1155 | 3.175 | 3.1418 | 2.7284 | 3.5762 | 2.973 | 2.4424 | 3.2257 | 2.1538 | 3.1048 | 3.3713 | 1.9429 | 3.4099 | 2.6967 | 3.2102 | 2.7797 | 4.0763 | 3.3209 | 3.1338 | 3.7349 | 3.1729 | 3.0063 | 3.3199 | 3.1584 | 0 | 0.78193 | 0 | 0 | 13.8837 | 62.6646 | [6 empty] | 2.9877 | 2.9076 | 3.0672 | 3.0432 | 2.9414 | 2.741 | 3.3123 | 3.1773 | 3.7945 | 3.1195 | 2.185 | 3.5024 | 3.1068 | 5.0868 | 2.1758 | 3.7622 | 0 | 0 | 0 | 1.5402 | 1.885 | 0.59447 | 0 | 0 | 1.5213 | 5.2561 | 6.8821 | 3.6625 | 2.8842 | 3.4392 | 6.8647 | 7.5669 | 2.6471 | 1.3887 | 3.0537 | 0.99478 | 2.5975 | 4.1384 | 4.7484 | 3.0496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 3.3529 | 2.6347 | 4.6552 | 6.2191 | 4.5193 |  | 4.6714 | 4.7978 | 0.79846 | 2.5419 | 0.75583 | 0.96208 | 0.73337 | 2.0694 | 1.9984 | 2.2352 | 0.21887 | 0.66897 | 0.072996 | 0 | 0 | 0 | 3.0494 | 1.5146 | 2.7636 | 2.8071 | 3.022 | 2.9867 | 0 | 0 | 0 | 0 | 3.027 | 3.1777 | 2.89 | 3.1102 | 2.7452 | 3.9106 | 3.1854 | 2.7189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6313 | 0 | 0 | 0 | 0 | 2.4769 | 3.2919 | 2.5394 | 3.4875 | 0 | 3.5231 | 4.2032 | 25.6834 |  | 4.4755 | 2.5722 | 4.5414 | 3.8578 | 4.1013 | 0 | 2.2403 | 2.4004 | 3.316 | 4.1768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 3.9567 | 3.7154 | 4.421 | 18.8391 |  |  |  | 19.1379 | 1.8196 | 4.4362 | 4.8466 | 1.8156 | 5.612 | 4.835 | 4.2155 | 5.1243 | 7.6008 | 3.8666 | 3.2695 | 6.9242 | 2.6338 | 3.0858 | 3.8749 | 2.9696 | 4.5492 | 3.5551 | 0 | 3.9305 | 0.9737 | 0 | 0 | 0 | 4.123 | 3.7103 |  | 4.51 | 5.3812 | 4.5992 | 3.7877 | 3.534 | 5.865 | 9.1219 | 2.9774 | 5.4102 | 6.4665 | 3.848 | 6.4112 | 7.888 | 3.6947 | 4.4551 | 4.7232 | 4.3176 | 3.8002 | 6.0466 | 3.762 | 3.6387 | 1.8795 | 0 | 1.8202 | 3.5825 | 5.261 | 4.2447 | 2.0128 | 4.9074 | 17.7956 | 4.2911 | 14.0781 | 4.6742 | 0.5739 | 3.6027 | 9.3898 | 5.3899 | 4.7539 | 6.6912 | 4.7112 | 4.9046 | 7.7131 | 4.7335 | 4.8791 | 6.3416 | 4.0181 | 4.3484 | 3.7538 | 1.6591 | 2.871 | 2.3924 | 0.15915 | 0.79723 | 2.9677 | 1.7616 | 1.0064 | 6.0652 | 3.7662 | 3.8892 | 4.3312 | 4.6731 | 4.6958 | 10.7425 | 7.0581 | 3.8654 | 1.71 | 0 | 1.6731 | 3.9512 | 3.7052
2025-07-07 | 2.1634 | 3.5802 | 3.8804 | 3.285 | 3.2925 | 3.4298 | 2.8563 | 3.133 | 3.4975 | 3.3787 | 3.4443 | 3.2859 | 3.348 | 4.123 | 4.6771 | 3.7092 | 2.9847 | 3.1773 | 3.3033 | 3.3311 | 3.2632 | 3.3417 | 3.0049 | 3.3131 | 3.3148 | 3.3363 | 3.3394 | 3.4385 | 3.0361 | 3.185 | 3.2738 | 3.5399 | 3.3811 | 3.3713 | 3.4667 | 3.2974 | 3.1011 | 3.1752 | 3.6225 | 3.9102 | 1.4893 | 1.5324 | 3.1405 | 3.2909 | 3.1016 | 3.3175 | 3.0621 | 2.8161 | 2.959 | 1.981 | 2.8618 | 3.3389 | 4.4924 | 2.9238 | 3.3613 | 3.1693 | 2.806 | 2.9484 | 2.9076 | 2.7602 | 2.4589 | 1.3639 | 3.4431 | 2.7852 | 2.5596 | 2.9326 | 2.6411 | 3.1063 | 3.0509 | 3.0158 | 3.2492 | 3.2405 | [8 empty] | 3.9694 | 5.0556 | [6 empty] | 3.253 | 2.9863 | 3.2409 | 3.3189 | 3.065 | 3.1331 | 3.0924 | 2.738 | 3.1216 | 3.0623 | 3.0154 | 2.8048 | 2.2067 | 3.0896 | 3.4063 | 2.0339 | 3.4784 | 2.7561 | 3.2113 | 2.8048 | 4.121 | 3.3614 | 3.1852 | 3.7813 | 3.2433 | 3.0921 | 3.3852 | 3.2314 | 0 | 0.80621 | 0 | 0 | 14.0836 | 63.4781 | [6 empty] | 3.0682 | 3.0019 | 3.1384 | 3.1395 | 3.033 | 2.8532 | 3.4006 | 3.251 | 3.8743 | 3.2485 | 2.3018 | 3.5883 | 3.2496 | 5.4371 | 2.1688 | 3.8272 | 0.63439 | 0 | 0 | 1.773 | 2.0799 | 0.80165 | 0.22307 | 0.25687 | 1.5294 | 5.2218 | 6.9643 | 3.7518 | 2.9208 | 3.5349 | 7.0361 | 7.5178 | 2.72 | 1.4363 | 3.0612 | 0.9953 | 2.7181 | 4.1241 | 4.7442 | 3.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 3.3923 | 2.7107 | 4.7694 | 6.2602 | 4.596 |  | 4.7472 | 4.9694 | 2.8428 | 2.7537 | 2.9439 | 0.9908 | 0.75625 | 2.2158 | 2.108 | 2.3731 | 0.21759 | 0.66983 | 0.933 | 0 | 0 | 0 | 1.3004 | 1.7517 | 2.8281 | 2.8102 | 2.9836 | 2.9897 | 0 | 0 | 0 | 0 | 3.1009 | 3.2053 | 2.932 | 3.1105 | 2.7227 | 3.8787 | 3.1896 | 2.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7082 | 0 | 0 | 0 | 0 | 2.579 | 3.3392 | 2.6513 | 3.6431 | 0.61976 | 3.6288 | 4.3071 | 26.0125 |  | 4.5152 | 2.6815 | 4.6106 | 3.8763 | 4.1329 | 0 | 2.3235 | 2.4967 | 3.364 | 4.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 2.8677 | 2.8368 | 3.1245 | 13.3469 |  |  |  | 13.6207 | 1.8049 | 3.4651 | 3.4532 | 1.8059 | 3.6941 | 3.2607 | 3.0571 | 3.5653 | 9.5037 | 4.0168 | 3.5742 | 8.672 | 2.8844 | 3.1856 | 3.9226 | 3.0643 | 4.3583 | 3.4195 | 0 | 3.7713 | 0.92905 | 0 | 0 | 0 | 3.1759 | 3.4392 |  | 3.2742 | 4.1093 | 3.7312 | 2.8699 | 2.9474 | 4.3376 | 6.7245 | 2.5197 | 3.7751 | 4.4721 | 3.6038 | 4.4432 | 5.5178 | 3.3897 | 3.9342 | 4.1066 | 3.7393 | 3.3687 | 5.3121 | 3.2904 | 3.2555 | 1.8576 | 0 | 1.8162 | 2.7373 | 3.6453 | 3.2297 | 1.9078 | 3.5653 | 12.3661 | 3.4335 | 9.6778 | 3.7489 | 0.59515 | 2.7556 | 6.7767 | 3.9336 | 3.3336 | 4.575 | 3.3166 | 3.2932 | 6.8188 | 4.1474 | 3.5051 | 4.2257 | 2.9746 | 3.1115 | 2.7362 | 1.6483 | 2.3139 | 2.0908 | 0.16727 | 0.81627 | 2.8846 | 1.8571 | 1.1185 | 3.9449 | 2.9991 | 2.9766 | 2.9852 | 3.2047 | 3.4169 | 7.7172 | 5.0007 | 2.7614 | 1.7332 | 0 | 1.693 | 3.1014 | 3.6828
2025-07-08 | 1.7862 | 3.451 | 3.715 | 3.1886 | 3.1967 | 3.3148 | 2.7248 | 3.0258 | 3.3849 | 3.3096 | 3.3714 | 3.2003 | 3.2379 | 3.9419 | 3.8618 | 3.5853 | 2.9394 | 3.1233 | 3.2273 | 3.2577 | 3.2044 | 3.2826 | 2.9417 | 3.2615 | 3.2232 | 3.2603 | 3.2512 | 3.3226 | 2.9269 | 3.0479 | 3.0917 | 3.4226 | 3.1722 | 3.217 | 3.1975 | 3.1026 | 2.988 | 3.0678 | 3.4839 | 3.7344 | 1.2392 | 1.2589 | 3.0382 | 3.1772 | 3.4834 | 2.6262 | 2.4844 | 3.1549 | 2.9126 | 1.8265 | 2.8435 | 3.3132 | 4.4427 | 2.8534 | 3.2807 | 3.1077 | 2.7614 | 2.9195 | 2.8771 | 2.7089 | 2.3539 | 1.1361 | 3.4003 | 2.7594 | 2.485 | 2.8793 | 2.5822 | 3.0403 | 2.9355 | 2.9165 | 3.1622 | 3.1602 | [8 empty] | 3.6014 | 4.6012 | [6 empty] | 3.0946 | 2.8549 | 3.1036 | 3.1652 | 3.0481 | 3.1127 | 3.0696 | 2.7194 | 3.4834 | 2.9909 | 2.4238 | 3.078 | 2.1308 | 3.0607 | 3.1966 | 1.8664 | 3.4008 | 2.6934 | 3.1521 | 2.7084 | 3.9316 | 3.1513 | 2.9839 | 3.4563 | 3.0429 | 2.9717 | 3.1716 | 3.0215 | 0 | 0.66377 | 0 | 0 | 13.4824 | 52.9734 | [6 empty] | 2.8637 | 2.8259 | 2.9445 | 2.9397 | 2.8422 | 2.6731 | 3.1907 | 3.0524 | 3.6567 | 3.0481 | 2.0859 | 3.3796 | 3.0013 | 4.8982 | 1.7236 | 3.6162 | 2.5587 | 2.2667 | 1.5118 | 2.0572 | 2.3602 | 7.2288 | 1.1991 | 1.6378 | 1.2807 | 5.1484 | 6.8246 | 3.6382 | 2.7952 | 3.3757 | 6.7561 | 7.358 | 2.6274 | 1.2169 | 2.9846 | 0.84057 | 2.3723 | 4.0548 | 4.6695 | 3.0055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 3.2227 | 2.5815 | 4.5688 | 5.9542 | 4.3474 |  | 3.8159 | 4.6754 | 1.0272 | 2.2827 | 2.7859 | 0.80311 | 0.61484 | 1.9348 | 1.7634 | 2.1849 | 0.17298 | 0.55368 | 0.77241 | 0 | 0 | 0 | 1.0736 | 1.6597 | 2.7817 | 2.7808 | 2.9735 | 2.9191 | 0 | 0 | 0 | 0 | 2.9671 | 3.0679 | 2.804 | 2.9973 | 2.6504 | 3.7845 | 3.1125 | 2.6776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5848 | 0 | 0 | 0 | 0 | 2.3963 | 3.1173 | 2.4462 | 3.4291 | 3.1266 | 3.5093 | 4.1644 | 24.9201 |  | 4.3265 | 2.5499 | 4.4519 | 3.7738 | 4.0025 | 0 | 2.1727 | 2.262 | 3.2108 | 3.9689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 2.7542 | 2.6991 | 3.006 | 12.8837 |  |  |  | 13.023 | 1.4598 | 3.4816 | 3.3235 | 1.4542 | 3.5757 | 3.1453 | 2.9411 | 3.4471 | 7.3932 | 3.6606 | 3.4012 | 8.2297 | 2.7321 | 3.0062 | 3.7182 | 2.9031 | 3.6416 | 2.8481 | 0 | 3.1612 | 0.76344 | 0 | 0 | 0 | 2.9772 | 2.7304 |  | 3.1433 | 3.8548 | 3.4586 | 2.6854 | 2.7004 | 4.0942 | 6.3774 | 2.2826 | 3.5727 | 4.2223 | 3.3274 | 4.1638 | 5.1949 | 3.2352 | 3.7719 | 3.924 | 3.5815 | 3.2302 | 5.1204 | 3.1828 | 3.141 | 1.5075 | 1.8759 | 2.6725 | 2.6095 | 3.5134 | 3.1248 | 1.6089 | 3.3973 | 11.8821 | 3.2226 | 9.3417 | 3.5347 | 0.4427 | 2.7625 | 6.5102 | 3.7411 | 3.2274 | 4.4663 | 3.225 | 3.1969 | 6.1755 | 3.5007 | 3.3507 | 4.0746 | 2.8665 | 3.0026 | 2.6407 | 1.3686 | 2.1802 | 1.8956 | 0.11534 | 0.6489 | 3.4937 | 2.3462 | 0.87701 | 3.8094 | 2.8166 | 2.8337 | 2.8831 | 3.0887 | 3.2851 | 7.4286 | 4.7992 | 2.6563 | 1.3672 | 0 | 1.3381 | 2.936 | 3.5285
2025-07-09 | 1.5606 | 3.5871 | 4.6822 | 4.5969 | 3.5219 | 3.6461 | 3.4348 | 4.1868 | 3.652 | 3.4976 | 4.9404 | 4.7465 | 3.5676 | 3.8152 | 4.47 | 5.3794 | 2.2404 | 2.5203 | 2.5904 | 2.6186 | 3.1235 | 3.1865 | 2.7251 | 3.1559 | 1.2859 | 2.4938 | 2.4773 | 2.4455 | 4.0344 | 3.8442 | 3.8449 | 4.3202 | 2.2584 | 2.6765 | 2.2219 | 2.1975 | 4.2876 | 4.4505 | 4.4569 | 4.8089 | 0.8046 | 0.82743 | 2.5117 | 2.6127 | 4.1834 | 4.7821 | 4.2023 | 3.6809 | 2.2272 | 1.186 | 2.2102 | 2.5446 | 6.181 | 3.9268 | 4.7666 | 4.3855 | 2.0068 | 2.1986 | 2.1908 | 1.9426 | 2.8635 | 1.2778 | 4.7888 | 3.765 | 1.6853 | 2.1535 | 1.7558 | 2.2278 | 3.6547 | 3.7461 | 4.2665 | 4.0086 | [8 empty] | 3.7241 | 4.7504 | [6 empty] | 4.5611 | 4.007 | 4.4499 | 4.6662 | 2.5319 | 2.5298 | 2.5516 | 2.1041 | 5.1495 | 3.9187 | 3.0616 | 4.4588 | 1.4497 | 2.4119 | 2.3503 | 1.1848 | 4.5642 | 3.4915 | 4.3465 | 3.5929 | 3.5403 | 2.8057 | 2.6218 | 3.2448 | 4.58 | 4.4844 | 4.8661 | 4.5839 | 0 | 0.72301 | 0 | 0 | 11.9592 | 43.5925 | [6 empty] | 2.5387 | 2.4129 | 2.6853 | 2.6104 | 4.1698 | 3.7043 | 4.4346 | 4.345 | 3.3295 | 2.5182 | 1.5608 | 3.0134 | 3.761 | 6.9788 | 2.0196 | 5.4218 | 2.0539 | 1.8335 | 1.2191 | 1.5968 | 3.0178 | 10.1046 | 2.0879 | 2.265 | 1.3807 | 6.9966 | 8.6448 | 4.3763 | 3.4117 | 4.2368 | 8.1468 | 10.8242 | 1.9744 | 0.81904 | 2.5564 | 0.55665 | 2.6663 | 5.8228 | 6.5474 | 4.1587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 3.0338 | 2.1054 | 3.9165 | 5.4062 | 6.3308 |  | 4.6033 | 6.3708 | 2.7595 | 2.5005 | 3.1644 | 0.88684 | 0.6794 | 2.1584 | 1.9369 | 2.5333 | 0.19886 | 0.61708 | 0.85911 | 0 | 0 | 0 | 1.2179 | 1.9228 | 3.5062 | 3.7631 | 4.1847 | 4.1552 | 0 | 0 | 0 | 0 | 3.9233 | 4.4544 | 3.8575 | 4.4136 | 3.9303 | 5.5839 | 4.4985 | 3.4833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0323 | 0 | 0 | 0 | 0 | 2.788 | 3.5086 | 2.4997 | 4.1703 | 4.1686 | 4.6874 | 5.7127 | 31.6669 |  | 5.7628 | 3.1539 | 6.2303 | 5.3806 | 5.722 | 0 | 2.7171 | 2.7633 | 4.6085 | 5.7672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 3.575 | 3.35 | 3.98 | 17.0906 |  |  |  | 17.8269 | 1.6787 | 4.1159 | 4.4951 | 1.6756 | 5.2062 | 4.3804 | 3.8914 | 4.7174 | 8.9532 | 4.3582 | 4.9735 | 12.5645 | 4.3781 | 4.2866 | 4.8983 | 3.9276 | 4.3384 | 3.4183 | 0 | 3.7848 | 0.93226 | 0 | 0 | 0 | 3.9485 | 3.2798 |  | 4.373 | 5.2823 | 4.5311 | 4.5756 | 3.4589 | 5.7062 | 8.7494 | 2.8651 | 5.2574 | 6.3251 | 4.3098 | 6.3277 | 7.7589 | 4.3192 | 5.4003 | 5.8831 | 5.3427 | 3.7327 | 6.008 | 3.5249 | 3.5182 | 1.4171 | 3.0955 | 2.8374 | 2.7264 | 4.9329 | 4.3009 | 1.872 | 4.4778 | 13.585 | 3.2633 | 10.7039 | 3.5553 | 3.3647 | 3.7179 | 8.7004 | 4.9221 | 3.1415 | 4.4531 | 3.107 | 3.1968 | 5.7061 | 3.5065 | 3.6431 | 4.7586 | 2.6088 | 2.8248 | 2.441 | 1.0682 | 2.6567 | 2.2146 | 0.13873 | 0.73591 | 3.1375 | 1.9524 | 0.81568 | 3.7403 | 2.7769 | 2.7512 | 2.7938 | 3.1372 | 2.9553 | 6.7657 | 4.3767 | 2.4186 | 1.5795 | 0 | 1.5449 | 3.668 | 3.809
2025-07-10 | 2.1117 | 3.8589 | 4.0656 | 3.6119 | 3.6376 | 3.7552 | 2.9394 | 3.3607 | 3.8288 | 3.7272 | 3.8402 | 3.6504 | 3.6769 | 4.3269 | 4.5677 | 4.0918 | 3.2979 | 5.5862 | 3.6558 | 3.7209 | 3.6629 | 3.76 | 3.3288 | 3.7242 | 3.6314 | 3.7559 | 3.7563 | 3.8266 | 3.3373 | 3.3758 | 3.4069 | 3.746 | 3.4788 | 3.6067 | 3.4955 | 3.3851 | 3.3343 | 3.4298 | 3.8033 | 4.313 | 1.4553 | 1.4855 | 3.4 | 3.5812 | 3.3734 | 3.6841 | 3.3631 | 3.0389 | 3.2635 | 2.0966 | 3.2059 | 3.7868 | 4.9778 | 3.2041 | 3.7179 | 3.5044 | 3.0754 | 3.2202 | 3.1567 | 2.9981 | 2.5747 | 1.334 | 3.8859 | 3.1167 | 2.7438 | 3.2864 | 2.8478 | 3.4787 | 3.2302 | 3.2446 | 3.5602 | 3.4723 | [8 empty] | 3.6897 | 4.7111 | [6 empty] | 3.5024 | 3.1895 | 3.4448 | 3.5672 | 3.4768 | 3.5404 | 3.5209 | 3.0641 | 4.0154 | 3.3297 | 2.5225 | 3.5124 | 2.5696 | 3.4751 | 3.5197 | 2.0663 | 3.8021 | 2.9641 | 3.5755 | 3.0424 | 4.5401 | 3.6189 | 3.419 | 4.1007 | 3.4625 | 3.3389 | 3.6598 | 3.495 | 0 | 0.76762 | 0 | 0 | 15.5221 | 59.9451 | [6 empty] | 3.3104 | 3.2366 | 3.4015 | 3.4081 | 3.263 | 3.0947 | 3.609 | 3.4703 | 4.1793 | 3.3985 | 2.3131 | 3.8745 | 3.3003 | 5.5023 | 2.0861 | 4.1202 | 2.8439 | 2.6871 | 1.8451 | 2.3133 | 2.6443 | 8.9635 | 3.1122 | 2.6109 | 1.5002 | 5.8943 | 7.6601 | 4.0967 | 3.125 | 3.8891 | 7.5161 | 8.4618 | 2.8822 | 1.4017 | 3.38 | 0.98328 | 2.755 | 4.6787 | 5.4511 | 3.4031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 3.6575 | 2.8317 | 5.0863 | 6.6207 | 4.9847 |  | 4.6757 | 5.2494 | 3.1129 | 2.6508 | 3.1196 | 0.95793 | 0.7349 | 2.2356 | 1.9182 | 2.4511 | 0.16711 | 0.66654 | 0.9236 | 0 | 0 | 0 | 1.3045 | 1.9159 | 3.5 | 3.0738 | 3.2862 | 3.347 | 0 | 0 | 0 | 0 | 3.2982 | 3.4922 | 3.0941 | 3.4507 | 2.3794 | 4.0016 | 3.2795 | 2.6944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1535 | 0 | 0 | 0 | 0 | 3.095 | 3.7548 | 2.8762 | 3.7576 | 3.4709 | 3.9247 | 4.5043 | 27.6418 |  | 4.7233 | 2.816 | 4.9813 | 4.3074 | 4.5758 | 2.7324 | 2.437 | 2.5752 | 3.6547 | 4.5306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 3.1267 | 3.0202 | 3.4076 | 14.6043 |  |  |  | 15.0435 | 2.1006 | 4.6525 | 4.9539 | 2.1012 | 5.5982 | 4.8863 | 4.3455 | 5.23 | 8.2957 | 4.0661 | 4.0449 | 10.1461 | 3.5516 | 3.5409 | 4.3243 | 3.2455 | 4.2671 | 3.3477 | 0 | 3.6921 | 2.2326 | 0 | 0 | 0 | 3.2764 | 3.9969 |  | 3.4584 | 4.2633 | 3.7746 | 2.9716 | 2.9835 | 4.5392 | 7.0533 | 2.5363 | 4.0361 | 4.8299 | 3.6489 | 4.7358 | 5.8849 | 3.5757 | 4.2787 | 4.5128 | 4.1167 | 3.6529 | 5.8182 | 3.5813 | 3.5054 | 1.7987 | 3.3032 | 3.0216 | 2.8757 | 3.9923 | 3.5354 | 1.8724 | 3.7921 | 13.6991 | 3.6104 | 10.7306 | 3.9037 | 3.6805 | 3.1185 | 7.2838 | 4.2158 | 3.7787 | 5.262 | 3.7789 | 3.7776 | 6.9718 | 3.9521 | 3.8632 | 4.8197 | 3.2435 | 3.4813 | 3.0079 | 1.5749 | 2.3959 | 2.095 | 0.14468 | 0.77223 | 3.5681 | 2.3645 | 0.96455 | 3.9319 | 2.8068 | 2.7476 | 2.8901 | 3.1669 | 3.5623 | 8.255 | 5.3292 | 2.8288 | 1.579 | 0 | 1.545 | 3.1637 | 4.0248
2025-07-11 | 2.1139 | 3.5874 | 3.844 | 3.3469 | 3.3564 | 3.4414 | 3.1756 | 3.1301 | 3.5108 | 3.4471 | 3.3524 | 3.3321 | 3.3424 | 4.0365 | 4.3548 | 3.7264 | 3.0486 | 3.1108 | 3.3996 | 3.4502 | 3.4031 | 3.4854 | 3.1036 | 3.4389 | 3.3479 | 3.4873 | 3.5084 | 3.5833 | 3.1438 | 3.2172 | 3.4222 | 3.5306 | 3.2762 | 3.3073 | 3.3556 | 3.2112 | 3.0638 | 3.1379 | 3.5288 | 3.7874 | 1.4617 | 1.4851 | 3.1138 | 3.2597 | 3.0772 | 3.4944 | 3.0496 | 2.7699 | 2.9947 | 1.9414 | 2.9238 | 3.4289 | 4.5051 | 2.9106 | 3.3949 | 3.2082 | 2.8362 | 2.9379 | 2.904 | 2.7921 | 2.4421 | 1.2934 | 3.4726 | 2.849 | 2.5422 | 3.0281 | 2.6862 | 3.2475 | 3.0622 | 3.0792 | 3.321 | 3.2648 | [8 empty] | 3.8895 | 4.9682 | [6 empty] | 3.2495 | 2.9643 | 3.1639 | 3.3015 | 3.1488 | 3.2129 | 3.178 | 2.7744 | 3.6423 | 3.0414 | 2.3068 | 3.1597 | 2.1803 | 3.1688 | 3.219 | 1.9703 | 3.5339 | 2.6886 | 3.2818 | 2.7863 | 4.2032 | 3.3619 | 3.176 | 3.8152 | 3.2547 | 3.1153 | 3.3911 | 3.2233 | 0 | 0.79656 | 0 | 0 | 14.4525 | 55.6818 | [6 empty] | 3.0558 | 2.9873 | 3.1254 | 3.1258 | 3.0086 | 1.9929 | 3.3444 | 3.2048 | 3.8553 | 3.1671 | 2.2068 | 3.5822 | 3.1492 | 5.1344 | 2.1962 | 3.8175 | 2.6239 | 2.6235 | 1.8308 | 2.1593 | 2.4466 | 9.1553 | 2.5128 | 2.4504 | 1.4008 | 5.2236 | 6.8854 | 3.7238 | 2.8381 | 3.5336 | 6.8629 | 7.5808 | 2.631 | 1.328 | 3.0002 | 0.92924 | 2.4458 | 4.1419 | 4.8352 | 2.9841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 3.3395 | 2.6246 | 4.6807 | 6.0212 | 4.5834 |  | 4.7196 | 4.8524 | 2.8061 | 2.4709 | 2.8594 | 0.90424 | 0.69245 | 2.0115 | 1.6177 | 2.2057 | 0.20183 | 0.62602 | 0.86413 | 0 | 0 | 0 | 1.2592 | 1.7507 | 2.8067 | 2.8303 | 2.9911 | 3.0079 | 0 | 0 | 0 | 0 | 3.1466 | 3.2994 | 2.919 | 3.1854 | 2.4988 | 3.9604 | 3.2776 | 2.7883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7363 | 0 | 0 | 0 | 0 | 2.817 | 3.3942 | 2.6172 | 3.4599 | 3.1728 | 3.6148 | 4.335 | 25.8691 |  | 4.4548 | 2.6524 | 4.5153 | 3.8804 | 4.1463 | 3.5815 | 2.2776 | 2.4282 | 3.3488 | 4.1158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 2.909 | 2.8324 | 3.1639 | 13.5987 |  |  |  | 13.8589 | 1.7722 | 3.4208 | 2.5542 | 1.7764 | 3.8449 | 3.3476 | 3.0752 | 3.6547 | 9.9906 | 4.5038 | 3.8096 | 8.5376 | 3.43 | 3.5141 | 4.0856 | 3.0997 | 4.5177 | 3.5757 | 0 | 3.9828 | 3.4799 | 0.016771 | 0 | 0 | 4.7208 | 4.647 |  | 5.3688 | 6.6854 | 5.7313 | 4.4677 | 4.3175 | 6.9451 | 10.5098 | 3.4796 | 6.4436 | 7.8055 | 5.3581 | 5.5966 | 9.6825 | 3.38 | 4.0099 | 4.2136 | 3.8603 | 0 | 5.321 | 3.3301 | 3.2801 | 4.9642 | 4.1566 | 3.7564 | 3.6111 | 5.3224 | 4.626 | 2.0103 | 4.8734 | 17.9646 | 4.3417 | 8.7924 | 2.8917 | 3.4924 | 2.7046 | 9.4206 | 2.5715 | 4.8183 | 6.8187 | 4.8355 | 5.0427 | 7.9895 | 4.8336 | 4.8592 | 6.4304 | 4.1823 | 4.5106 | 3.9092 | 1.7267 | 2.9542 | 2.4571 | 0.08472 | 0.82697 | 4.5804 | 3.5017 | 1.1163 | 6.0869 | 3.7591 | 3.6891 | 4.1911 | 4.7175 | 5.4532 | 12.7344 | 8.1809 | 4.3724 | 4.4464 | 7.7059 | 3.4072 | 4.6835 | 3.7171
2025-07-12 | 2.0134 | 3.9028 | 3.9863 | 3.7034 | 3.7267 | 3.8309 | 3.3776 | 3.4325 | 3.8894 | 3.7334 | 3.898 | 3.6814 | 3.661 | 4.2571 | 3.9447 | 4.1725 | 3.2827 | 3.5832 | 3.6364 | 3.756 | 3.6462 | 3.7837 | 3.3099 | 3.7353 | 3.5686 | 3.7779 | 3.7803 | 3.8251 | 3.3082 | 2.7329 | 3.2515 | 3.6565 | 3.3964 | 3.6746 | 3.4505 | 3.3317 | 3.4276 | 3.5308 | 3.7847 | 4.0877 | 1.3491 | 1.3721 | 3.4095 | 3.5663 | 3.3313 | 3.7271 | 3.3433 | 2.9931 | 3.1874 | 1.9493 | 3.1732 | 3.8126 | 4.9244 | 3.1619 | 3.748 | 3.6612 | 3.0056 | 3.1341 | 3.0984 | 2.9422 | 0.89738 | 0.37939 | 0.89217 | 1.6321 | 2.5396 | 3.2314 | 2.7695 | 3.3992 | 3.1353 | 3.1611 | 3.4567 | 3.304 | [8 empty] | 0 | 0 | [6 empty] | 3.6219 | 3.2758 | 3.5295 | 3.7244 | 3.4728 | 3.5053 | 3.496 | 2.9868 | 3.9975 | 3.1869 | 2.4047 | 3.4929 | 2.225 | 3.2645 | 3.2625 | 1.9211 | 3.7014 | 0.22892 | 0.31356 | 0.23878 | 4.7581 | 3.7487 | 3.5614 | 4.3038 | 3.5915 | 3.4485 | 3.8077 | 3.6201 | 0 | 0.78555 | 0 | 0 | 16.0805 | 61.0408 | [6 empty] | 3.3632 | 0.04331 | 3.5113 | 3.4592 | 3.3279 | 3.0664 | 3.6142 | 3.473 | 2.6243 | 3.4547 | 2.2708 | 4.0335 | 3.2959 | 5.673 | 2.0396 | 4.3081 | 3.6397 | 3.6556 | 2.1752 | 2.7124 | 3.2755 | 10.6942 | 3.5573 | 3.5985 | 1.3244 | 0.049373 | 0.057994 | 3.8024 | 2.9379 | 3.6733 | 7.1497 | 8.4321 | 2.745 | 1.2919 | 3.2969 | 0.92566 | 2.4272 | 4.5759 | 5.4115 | 3.2468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 4.9061 | 3.4612 | 6.465 | 8.9381 | 6.6881 |  | 4.8256 | 6.6441 | 2.5498 | 0.10113 | 2.6553 | 0.75852 | 0.70753 | 2.0003 | 1.5705 | 2.1768 | 0.21357 | 0.43715 | 0.88061 | 0 | 0 | 0 | 1.2229 | 1.7668 | 3.0381 | 3.1301 | 3.3854 | 3.2123 | 0 | 0 | 0 | 0 | 3.2549 | 3.5413 | 3.0987 | 3.384 | 2.6379 | 4.3865 | 3.4937 | 2.8781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3671 | 0 | 0 | 0 | 0 | 3.8659 | 4.9453 | 3.3506 | 3.4469 | 3.4562 | 4.1762 | 2.6023 | 33.1936 |  | 5.5633 | 3.0758 | 7.5054 | 6.8113 | 7.1327 | 5.5844 | 3.2843 | 2.8242 | 5.3953 | 6.8077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 3.543 | 3.2349 | 4.2994 | 18.5869 |  |  |  | 18.8708 | 1.5842 | 2.1667 | 3.1008 | 1.5739 | 3.3733 | 2.1401 | 2.6783 | 3.7367 | 10.8696 | 6.0905 | 3.4117 | 8.8239 | 3.6569 | 3.7345 | 4.3764 | 3.4202 | 5.2352 | 4.4622 | 1.2071 | 4.5225 | 3.9041 | 2.9295 | 3.2517 | 3.1546 | 4.1461 | 4.2411 |  | 4.5886 | 5.5318 | 4.4202 | 3.6092 | 3.6446 | 5.8497 | 9.1091 | 2.994 | 5.4828 | 1.9931 | 3.1019 | 6.4736 | 8.0665 | 3.3848 | 0 | 3.204 | 3.9983 | 0 | 3.9976 | 0 | 2.3158 | 1.6842 | 4.054 | 3.6849 | 3.5274 | 5.0422 | 4.5451 | 2.0027 | 0 | 0 | 4.187 | 8.0559 | 2.8163 | 3.4132 | 2.6371 | 9.1285 | 2.5239 | 4.7881 | 6.7618 | 4.7475 | 4.9239 | 7.5388 | 4.7234 | 4.7188 | 6.374 | 4.0194 | 4.363 | 3.6836 | 1.6013 | 2.8504 | 2.3661 | 0.14878 | 0.76237 | 0 | 2.7507 | 0.57601 | 5.6715 | 0 | 3.3099 | 3.6098 | 4.024 | 4.1683 | 9.311 | 5.8213 | 0 | 0 | 1.0675 | 3.0085 | 3.6111 | 3.793
2025-07-13 | 2.2582 | 3.9649 | 4.0798 | 3.7389 | 3.7529 | 3.8646 | 3.4605 | 3.4799 | 3.9344 | 3.7271 | 3.934 | 3.7258 | 3.727 | 4.4642 | 4.4389 | 4.1971 | 3.351 | 3.6278 | 3.6816 | 3.7913 | 3.7264 | 3.8138 | 3.3599 | 3.7829 | 3.6342 | 3.8047 | 3.8009 | 3.862 | 3.357 | 2.8368 | 3.3927 | 3.7662 | 3.6136 | 3.7724 | 3.6977 | 3.5449 | 3.5062 | 3.6025 | 3.9576 | 4.2827 | 1.5636 | 1.597 | 3.524 | 3.6293 | 3.3651 | 3.7553 | 3.4286 | 3.1027 | 3.2754 | 2.0951 | 3.2525 | 3.8675 | 5.1013 | 3.2403 | 0.86327 | 3.5591 | 3.1108 | 3.2341 | 3.1792 | 3.0406 | 2.6144 | 1.379 | 2.9732 | 3.056 | 2.6685 | 3.3035 | 2.8777 | 3.4768 | 3.26 | 3.2737 | 3.5457 | 3.427 | [8 empty] | 0 | 0 | [6 empty] | 2.4254 | 2.8963 | 3.1202 | 3.2761 | 3.5357 | 3.5839 | 3.5685 | 3.0694 | 4.0708 | 3.3633 | 2.5406 | 3.5687 | 2.3628 | 3.3546 | 3.3881 | 2.0682 | 3.7935 | 2.8352 | 3.5662 | 2.9156 | 5.5236 | 4.509 | 4.2906 | 5.1701 | 4.3457 | 4.1717 | 4.5928 | 4.3083 | 0 | 0.28545 | 0 | 0 | 19.4064 | 73.7218 | [6 empty] | 4.0787 | 3.9473 | 4.2348 | 4.1825 | 4.0181 | 3.6949 | 4.386 | 4.1969 | 4.4024 | 3.559 | 2.4032 | 4.0574 | 3.4367 | 5.7273 | 2.3485 | 4.3189 | 3.2257 | 3.2353 | 2.1797 | 2.5649 | 2.9738 | 10.005 | 3.2161 | 3.2714 | 1.5394 | 5.9376 | 7.6987 | 3.9855 | 3.1221 | 3.8952 | 7.5746 | 8.5783 | 3.9824 | 1.6731 | 4.9331 | 1.1873 | 3.2562 | 7.0893 | 8.3186 | 4.9378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 4.1468 | 3.1874 | 5.7677 | 7.6302 | 5.7239 |  | 5.5091 | 5.9638 | 4.2058 | 0.010372 | 4.0522 | 1.0476 | 0.88531 | 2.7481 | 2.0575 | 2.9003 | 0.27406 | 0.50889 | 1.1131 | 0 | 0 | 0 | 1.5651 | 2.4333 | 4.2212 | 4.5042 | 4.8751 | 4.8748 | 0 | 0 | 0 | 0 | 4.8695 | 5.4493 | 4.7066 | 5.1903 | 3.9818 | 6.781 | 5.3555 | 4.2565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5474 | 0 | 0 | 0 | 4.7588 | 5.6233 | 5.6374 | 4.0436 | 2.9043 | 2.9865 | 3.4873 | 0.79825 | 29.894 |  | 4.973 | 2.845 | 5.5631 | 4.903 | 5.1996 | 4.3459 | 2.7263 | 2.8055 | 4.1297 | 5.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 3.18 | 3.0085 | 3.7432 | 16.0529 |  |  |  | 14.9023 | 2.4351 | 3.8295 | 3.7016 | 1.8303 | 4.1652 | 3.5565 | 3.318 | 3.9379 | 11.3022 | 6.4574 | 4.2023 | 9.2215 | 3.7801 | 3.8439 | 4.4307 | 3.6153 | 6.3562 | 8.1385 | 4.8917 | 4.5706 | 3.7456 | 2.8651 | 3.9307 | 3.8764 | 4.6729 | 4.9429 |  | 5.0881 | 6.1827 | 5.0347 | 4.0731 | 4.389 | 6.5265 | 10.1979 | 3.4587 | 6.0562 | 2.3647 | 3.6417 | 7.1067 | 8.8685 | 2.3526 | 2.6555 | 4.3415 | 4.1943 | 2.3102 | 5.1451 | 0 | 0 | 1.9986 | 4.5512 | 4.1405 | 4.0083 | 5.6279 | 5.0676 | 2.3522 | 3.2468 | 18.6656 | 4.7383 | 9.3075 | 3.8984 | 3.9498 | 3.039 | 10.1474 | 2.9699 | 5.256 | 7.3965 | 5.2095 | 5.3442 | 8.6431 | 5.2864 | 5.2184 | 6.9294 | 4.4514 | 4.7887 | 4.0356 | 1.8723 | 3.2333 | 2.7346 | 0.19759 | 0.87572 | 3.5716 | 3.1972 | 0.6579 | 6.306 | 2.7935 | 3.8206 | 0 | 0 | 4.792 | 10.6818 | 7.0148 | 2.8433 | 2.2735 | 1.2687 | 3.5752 | 4.0683 | 4.2615
2025-07-14 | 2.2253 | 3.9661 | 4.1073 | 3.6951 | 3.0715 | 3.8212 | 3.4733 | 3.4624 | 3.9046 | 3.7001 | 3.8323 | 3.6345 | 3.7977 | 4.5301 | 4.3267 | 4.1472 | 3.3071 | 3.5299 | 3.625 | 3.6764 | 3.6046 | 3.6873 | 3.2898 | 3.6515 | 3.528 | 3.6357 | 3.6413 | 3.7076 | 3.2358 | 2.7774 | 3.3342 | 3.6642 | 3.6916 | 3.7269 | 3.7565 | 3.6107 | 3.5153 | 3.5574 | 4.0063 | 4.3358 | 1.5559 | 1.6026 | 3.6294 | 3.5919 | 3.3727 | 3.6633 | 3.3824 | 3.1005 | 3.2442 | 2.1213 | 3.1649 | 3.7172 | 4.9942 | 3.2197 | 3.0768 | 3.5178 | 3.0387 | 3.1637 | 3.1422 | 3.0109 | 2.6045 | 1.3226 | 2.9101 | 2.9657 | 2.6214 | 3.1952 | 2.8253 | 3.3594 | 3.1831 | 3.1695 | 3.4113 | 3.3235 | [8 empty] | 0 | 0 | [6 empty] | 3.474 | 3.1934 | 3.4988 | 3.6332 | 3.3359 | 3.4483 | 3.4121 | 3.0296 | 3.8453 | 3.3248 | 2.5274 | 3.4473 | 2.3353 | 3.251 | 3.2989 | 2.0364 | 3.6233 | 2.7672 | 3.397 | 2.8329 | 4.5123 | 3.6828 | 3.5042 | 4.1757 | 3.5452 | 3.4447 | 3.7549 | 3.5177 | 0 | 0.23061 | 0 | 0 | 15.891 | 62.0674 | [6 empty] | 3.4052 | 3.3278 | 3.4841 | 3.5056 | 3.3487 | 3.1849 | 3.7433 | 3.5554 | 4.2807 | 3.5361 | 2.3991 | 3.9426 | 3.4341 | 5.5752 | 2.2025 | 4.0969 | 2.957 | 3.2051 | 2.4708 | 2.4603 | 2.7549 | 9.3571 | 2.7886 | 3.0625 | 1.4873 | 5.7756 | 7.6123 | 4.0587 | 3.147 | 3.9483 | 7.6782 | 8.3559 | 2.8877 | 1.3722 | 3.2058 | 0.98164 | 2.7223 | 4.5196 | 5.3733 | 3.2736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 3.709 | 3.1411 | 5.3109 | 7.0793 | 5.1155 |  | 6.4893 | 5.6093 | 3.0171 | 2.3595 | 3.05 | 0.84104 | 0.7116 | 2.186 | 1.6855 | 2.2094 | 0.22161 | 0.41418 | 0.91491 | 0 | 0 | 0 | 1.3132 | 1.9326 | 3.0498 | 3.0651 | 3.2787 | 3.1988 | 0 | 0 | 0 | 0 | 3.4034 | 3.5532 | 3.1739 | 3.3668 | 2.661 | 4.2963 | 3.4411 | 2.9764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 0 | 2.489 | 3.0164 | 3.742 | 2.7246 | 3.1925 | 3.1403 | 3.4685 | 2.5462 | 25.8049 |  | 4.3766 | 2.5582 | 5.0334 | 4.3282 | 4.5926 | 4.2943 | 3.0834 | 3.1222 | 3.7038 | 4.5724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 2.7969 | 2.6321 | 3.2749 | 14.2215 |  |  |  | 14.163 | 2.8832 | 4.1687 | 3.5119 | 2.8167 | 3.839 | 3.2852 | 3.1145 | 3.6515 | 10.8558 | 6.1126 | 3.9856 | 8.9056 | 3.5492 | 3.7044 | 4.1719 | 3.5094 | 5.2974 | 6.8064 | 4.1053 | 3.8367 | 2.699 | 2.2427 | 2.8389 | 2.9603 | 3.3746 | 3.879 |  | 3.5254 | 4.4384 | 3.833 | 3.3416 | 4.7899 | 4.5886 | 7.162 | 2.6363 | 4.0447 | 1.92 | 2.958 | 4.7633 | 5.9647 | 3.4999 | 3.8774 | 4.1275 | 3.9404 | 3.4684 | 4.899 | 0 | 0.67897 | 1.5942 | 3.1397 | 2.8873 | 2.9395 | 3.6696 | 3.3665 | 1.8775 | 3.3872 | 9.163 | 3.2447 | 6.5541 | 2.9339 | 2.9539 | 2.2299 | 6.7968 | 2.3377 | 3.3731 | 4.6688 | 3.8869 | 3.3491 | 6.4705 | 3.6376 | 3.4344 | 4.2656 | 2.9937 | 3.1527 | 2.6637 | 1.4716 | 2.2771 | 2.0119 | 0.14091 | 0.67704 | 3.4632 | 2.4112 | 0.50912 | 3.9065 | 2.8952 | 2.7708 | 0 | 0 | 3.2143 | 7.1904 | 4.7427 | 0.41999 | 3.4463 | 1.1664 | 2.7275 | 2.8623 | 4.0225
2025-07-15 | 1.8852 | 3.3865 | 3.5444 | 3.1969 | 3.1794 | 3.3039 | 2.9901 | 2.9823 | 3.3723 | 3.2168 | 3.3599 | 3.1687 | 3.2826 | 3.8253 | 3.5226 | 3.5756 | 2.9451 | 3.1202 | 3.1839 | 3.2 | 3.1974 | 3.2865 | 2.9491 | 3.2763 | 3.2538 | 3.2817 | 3.2774 | 3.3592 | 2.9656 | 2.709 | 3.3601 | 3.419 | 3.2689 | 3.2591 | 3.286 | 2.8654 | 3.0209 | 3.1347 | 3.5696 | 3.8131 | 1.3546 | 1.377 | 3.1571 | 3.1248 | 2.9416 | 3.2203 | 3.0114 | 2.7458 | 2.885 | 1.9118 | 2.862 | 3.3545 | 4.5078 | 2.8804 | 1.4018 | 3.1167 | 2.7903 | 2.9009 | 2.8277 | 2.7208 | 2.3792 | 1.1734 | 2.7082 | 2.7522 | 2.4598 | 2.9424 | 2.6118 | 3.1143 | 2.9872 | 1.2515 | 3.1889 | 3.1159 | [8 empty] | 0 | 0 | [6 empty] | 2.0043 | 1.7732 | 2.0096 | 2.1182 | 3.0086 | 3.1851 | 3.1535 | 2.8137 | 3.5732 | 3.1059 | 2.3555 | 3.1566 | 2.1988 | 3.0276 | 3.0914 | 1.9213 | 3.4392 | 2.619 | 3.2129 | 2.677 | 3.9368 | 3.2396 | 3.0165 | 3.6605 | 3.1157 | 3.005 | 3.1662 | 2.9922 | 0 | 0.21485 | 0 | 0 | 14.1742 | 55.1536 | [6 empty] | 3.0241 | 2.9599 | 3.0778 | 3.0764 | 2.955 | 2.8138 | 3.3389 | 3.1722 | 3.6994 | 3.0535 | 2.0576 | 3.4231 | 2.9412 | 3.5768 | 1.8276 | 3.528 | 2.739 | 3.0738 | 2.6852 | 2.5494 | 2.7655 | 8.7863 | 2.7147 | 2.8422 | 1.0975 | 5.1157 | 6.6759 | 3.6136 | 2.8474 | 3.6557 | 7.0844 | 7.6912 | 2.7141 | 1.272 | 3.0146 | 0.91394 | 2.5492 | 4.2189 | 4.9742 | 3.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 3.3146 | 2.6396 | 5.0326 | 6.2627 | 4.7349 |  | 6.6874 | 5.0675 | 2.9002 | 2.1595 | 2.9486 | 0.78562 | 0.66636 | 1.9111 | 1.5764 | 2.1344 | 0.19749 | 0.37986 | 0.84532 | 0 | 0 | 0 | 1.1662 | 1.7685 | 2.9423 | 2.9412 | 3.1345 | 2.9651 | 0 | 0 | 0 | 0 | 3.1676 | 3.2869 | 2.931 | 3.1037 | 2.4845 | 4.0211 | 3.2563 | 2.8141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6904 | 0 | 0 | 0 | 2.4029 | 2.7803 | 3.3582 | 2.5578 | 3.1123 | 2.3777 | 3.4692 | 3.8508 | 25.2978 |  | 4.494 | 2.4711 | 5.0309 | 3.97 | 4.2153 | 4.3159 | 3.0063 | 2.9624 | 3.218 | 3.9458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 2.5838 | 2.5957 | 2.8524 | 11.9721 |  |  |  | 13.3166 | 2.9843 | 4.6107 | 3.643 | 3.5244 | 3.7791 | 3.2744 | 3.0942 | 3.6692 | 10.5778 | 5.9649 | 3.8792 | 8.6544 | 3.4395 | 3.5732 | 4.0462 | 3.3697 | 5.0885 | 6.5095 | 3.9035 | 3.6614 | 2.5901 | 2.1 | 2.7094 | 2.9109 | 3.2703 | 3.8732 |  | 3.4063 | 4.2499 | 4.2771 | 3.2326 | 4.3744 | 4.4448 | 6.9679 | 2.612 | 3.9511 | 1.789 | 2.8948 | 4.5654 | 5.7435 | 3.4346 | 3.9498 | 4.047 | 3.8828 | 3.4264 | 4.8972 | 0.12721 | 1.4228 | 1.5908 | 3.1666 | 2.9373 | 2.8271 | 3.7389 | 3.3965 | 1.8916 | 3.6448 | 8.2865 | 3.3773 | 6.9759 | 3.1521 | 3.0776 | 2.3019 | 6.8809 | 2.3749 | 3.4185 | 4.7207 | 3.4153 | 3.4172 | 6.7095 | 3.7238 | 3.4883 | 4.3579 | 3.0362 | 3.2056 | 2.7335 | 1.5346 | 2.3269 | 2.1101 | 0.14959 | 0.69937 | 3.5584 | 2.1582 | 0.53428 | 4.0964 | 3.0307 | 2.6698 | 0.69279 | 1.6116 | 3.5185 | 7.3682 | 4.9537 | 2.7135 | 3.6281 | 1.2319 | 2.9319 | 2.9992 | 3.5431
2025-07-16 | 2.4313 | 5.398 | 5.1775 | 5.1916 | 5.2229 | 5.3624 | 4.6532 | 4.8238 | 5.4355 | 5.0196 | 5.4422 | 5.1614 | 5.348 | 5.5705 | 4.4168 | 5.8789 | 4.0002 | 4.3744 | 4.4154 | 4.5053 | 4.5162 | 4.5783 | 4.0207 | 4.6119 | 4.4517 | 4.5943 | 4.5662 | 4.6547 | 4.0595 | 3.2466 | 1.8441 | 4.5337 | 3.9768 | 4.522 | 3.6884 | 3.3495 | 4.1547 | 4.329 | 4.4898 | 4.8494 | 1.6532 | 1.7037 | 5.101 | 4.9768 | 4.6027 | 5.2064 | 4.7227 | 4.2172 | 3.9002 | 2.152 | 3.8546 | 4.6865 | 5.9028 | 3.8553 | 2.9863 | 4.24 | 3.6041 | 3.7627 | 3.8311 | 3.4611 | 2.8141 | 1.1973 | 3.4334 | 3.6476 | 2.9982 | 4.0222 | 3.3387 | 4.2159 | 3.7482 | 3.8483 | 4.2418 | 3.8704 | [8 empty] | 0 | 0 | [6 empty] | 4.903 | 4.3139 | 4.8375 | 5.0981 | 4.7237 | 4.9777 | 4.9379 | 4.2442 | 5.6739 | 4.6117 | 3.2553 | 5.0162 | 2.99 | 4.6427 | 4.6976 | 2.4572 | 5.2254 | 3.7832 | 4.8988 | 3.9417 | 6.1799 | 5.09 | 4.6045 | 5.8275 | 4.9241 | 4.736 | 5.0201 | 4.6941 | 0 | 0 | 0 | 0 | 21.7405 | 82.1928 | [6 empty] | 4.4888 | 4.275 | 4.652 | 4.615 | 4.4331 | 3.9743 | 4.8282 | 4.5356 | 3.6238 | 5.606 | 1.4252 | 5.6503 | 7.2212 | 6.6152 | 4.8601 | 5.7003 | 3.4479 | 3.8871 | 3.3747 | 3.2421 | 3.6204 | 10.9134 | 3.4332 | 3.4117 | 0.57407 | 8.187 | 10.4308 | 5.2939 | 3.6742 | 4.9819 | 9.6299 | 11.6761 | 3.7094 | 1.5008 | 4.5537 | 1.0808 | 2.9702 | 6.4842 | 7.5738 | 4.5457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 4.5153 | 3.3324 | 6.4879 | 8.4501 | 6.383 |  | 6.4317 | 6.6864 | 3.8391 | 2.57 | 3.7013 | 0.94772 | 0.80132 | 2.1642 | 1.8654 | 2.035 | 0.24451 | 0.4576 | 1.0061 | 0 | 0 | 0 | 1.4536 | 1.9926 | 4.3165 | 4.5008 | 4.9658 | 4.4059 | 0 | 0 | 0 | 0 | 4.2831 | 4.7281 | 4.1463 | 4.5937 | 3.5568 | 5.9262 | 4.7265 | 3.7983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5682 | 0 | 0 | 0 | 3.1643 | 4.071 | 5.0776 | 3.5665 | 4.0416 | 0.82776 | 5.0133 | 5.4681 | 34.3511 |  | 5.848 | 3.2279 | 7.7738 | 6.095 | 6.3936 | 6.4183 | 5.0506 | 4.3078 | 5.1333 | 6.3798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 3.4863 | 3.5315 | 4.1684 | 17.9711 |  |  |  | 8.8297 | 3.6325 | 6.4555 | 4.7323 | 5.5309 | 5.3935 | 4.5899 | 4.2304 | 5.001 | 15.3323 | 8.6758 | 5.6434 | 12.0033 | 5.11 | 5.2783 | 6.093 | 4.8251 | 5.4238 | 6.9232 | 4.1521 | 3.9043 | 3.3719 | 2.4447 | 3.5511 | 3.3348 | 4.0541 | 6.1058 |  | 4.7003 | 6.6581 | 6.9085 | 4.9087 | 4.919 | 5.3802 | 9.4969 | 3.1195 | 5.6086 | 2.1262 | 3.2786 | 6.6363 | 8.2415 | 4.5579 | 5.5415 | 5.8386 | 5.6874 | 4.8502 | 6.7365 | 3.0935 | 1.5542 | 1.6856 | 4.0706 | 3.7095 | 3.5946 | 5.0433 | 4.6151 | 3.2619 | 4.864 | 16.8339 | 4.1509 | 8.1987 | 3.5252 | 3.4251 | 2.5404 | 8.3902 | 3.2105 | 4.3547 | 6.0834 | 4.2748 | 4.3069 | 6.8469 | 4.2659 | 4.3073 | 5.5507 | 2.3681 | 3.9016 | 3.1898 | 1.4241 | 2.5719 | 2.1707 | 0.14163 | 0.65815 | 0.46201 | 1.9133 | 0.20245 | 4.7554 | 3.6213 | 2.8143 | 1.3513 | 3.297 | 4.5222 | 8.9503 | 6.3533 | 0.5665 | 4.3391 | 1.2787 | 3.1472 | 3.4116 | 5.2214
2025-07-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Formulas:
Date = [Date, row above]+1

## Raw_Data
[478 empty] | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 | 237 | 238 | 239 | 240 | 241 | 242 | 243 | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273 | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304 | 305 | 306 | 307 | 308 | 309 | 310 | 311 | 312 | 313 | 314 | 315 | 316 | 317 | 318 | 319 | 320 | 321 | 322 | 323 | 324 | 325 | 326 | 327 | 328 | 329 | 330 | 331 | 332 | 333 | 334 | 335 | 336 | 337 | 338 | 339 | 340 | 341 | 342 | 343 | 344 | 345 | 346 | 347 | 348 | 349 | 350 | 351 | 352 | 353 | 354 | 355 | 356 | 357 | 358 | 359 | 360 | 361 | 362 | 363 | 364 | 365 | 366 | 367 | 368 | 369 | 370 | 371 | 372 | 373 | 374 | 375 | 376 | 377 | 378 | 379 | 380 | 381 | 382 | 383 | 384 | 385 | 386 | 387 | 388 | 389 | 390 | 391 | 392 | 393 | 394 | 395 | 396 | 397 | 398 | 399 | 400 | 401 | 402 | 403 | 404 | 405 | 406 | 407 | 408 | 409 | 410 | 411 | 412 | 413 | 414 | 415 | 416 | 417 | 418 | 419 | 420 | 421 | 422 | 423 | 424 | 425 | 426 | 427 | 428 | 429 | 430 | 431 | 432 | 433 | 434 | 435 | 436 | 437 | 438 | 439 | 440 | 441 | 442 | 443 | 444 | 445 | 446 | 447 | 448 | 449 | 450 | 451 | 452 | 453 | 454 | 455 | 456 | 457 | 458 | 459 | 460 | 461 | 462 | 463 | 464 | 465 | 466 | 467 | 468 | 469 | 470 | 471 | 472 | 473 | 474 | 475 | 476 | 477 | 478 | 479 | 480 | 481 | 482 | 483 | 484 | 485 | 486 | 487 | 488 | 489 | 490 | 491 | 492 | 493 | 494 | 495 | 496 | 497 | 498 | 499 | 500 | 501 | 502 | 503 | 504 | 505 | 506 | 507 | 508 | 509 | 510 | 511 | 512 | 513 | 514 | 515 | 516 | 517 | 518 | 519 | 520 | 521
[8 empty] | hh:MM | hh:MM
Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Plant DC Capcity (kW) | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | IS1Inv1M1 | IS1Inv1M2 | IS1Inv1M3 | IS1Inv1M4 | IS1Inv2M1 | IS1Inv2M2 | IS1Inv2M3 | IS1Inv2M4 | IS2Inv1M1 | IS2Inv1M2 | IS2Inv1M3 | IS2Inv1M4 | IS2Inv2M1 | IS2Inv2M2 | IS2Inv2M3 | IS2Inv2M4 | IS3Inv1M1 | IS3Inv1M2 | IS3Inv1M3 | IS3Inv1M4 | IS3Inv2M1 | IS3Inv2M2 | IS3Inv2M3 | IS3Inv2M4 | IS4Inv1M1 | IS4Inv1M2 | IS4Inv1M3 | IS4Inv1M4 | IS4Inv2M1 | IS4Inv2M2 | IS4Inv2M3 | IS4Inv2M4 | IS5Inv1M1 | IS5Inv1M2 | IS5Inv1M3 | IS5Inv1M4 | IS5Inv2M1 | IS5Inv2M2 | IS5Inv2M3 | IS5Inv2M4 | IS6Inv1M1 | IS6Inv1M2 | IS6Inv1M3 | IS6Inv1M4 | IS6Inv2M1 | IS6Inv2M2 | IS6Inv2M3 | IS6Inv2M4 | IS7Inv1M1 | IS7Inv1M2 | IS7Inv1M3 | IS7Inv1M4 | IS7Inv2M1 | IS7Inv2M2 | IS7Inv2M3 | IS7Inv2M4 | IS8Inv1M1 | IS8Inv1M2 | IS8Inv1M3 | IS8Inv1M4 | IS8Inv2M1 | IS8Inv2M2 | IS8Inv2M3 | IS8Inv2M4 | IS9Inv1M1 | IS9Inv1M2 | IS9Inv1M3 | IS9Inv1M4 | IS9Inv2M1 | IS9Inv2M2 | IS9Inv2M3 | IS9Inv2M4 | IS10Inv1M1 | IS10Inv1M2 | IS10Inv1M3 | IS10Inv1M4 | IS10Inv2M1 | IS10Inv2M2 | IS10Inv2M3 | IS10Inv2M4 | IS11Inv1M1 | IS11Inv1M2 | IS11Inv1M3 | IS11Inv1M4 | IS12Inv1M1 | IS12Inv1M2 | IS12Inv1M3 | IS12Inv1M4 | IS12Inv2M1 | IS12Inv2M2 | IS12Inv2M3 | IS12Inv2M4 | IS13Inv1M1 | IS13Inv1M2 | IS13Inv1M3 | IS13Inv1M4 | IS13Inv2M1 | IS13Inv2M2 | IS13Inv2M3 | IS13Inv2M4 | IS14Inv1M1 | IS14Inv1M2 | IS14Inv1M3 | IS14Inv1M4 | IS14Inv2M1 | IS14Inv2M2 | IS14Inv2M3 | IS14Inv2M4 | IS15Inv1M1 | IS15Inv1M2 | IS15Inv1M3 | IS15Inv1M4 | IS15Inv2M1 | IS15Inv2M2 | IS15Inv2M3 | IS15Inv2M4 | IS16Inv1M1 | IS16Inv1M2 | IS16Inv1M3 | IS16Inv1M4 | IS17Inv1M1 | IS17Inv1M2 | IS17Inv1M3 | IS17Inv1M4 | IS17Inv2M1 | IS17Inv2M2 | IS17Inv2M3 | IS17Inv2M4 | IS18Inv1M1 | IS18Inv1M2 | IS18Inv1M3 | IS18Inv1M4 | IS18Inv2M1 | IS18Inv2M2 | IS18Inv2M3 | IS18Inv2M4 | IS19Inv1M1 | IS19Inv1M2 | IS19Inv1M3 | IS19Inv1M4 | IS19Inv2M1 | IS19Inv2M2 | IS19Inv2M3 | IS19Inv2M4 | IS20Inv1M1 | IS20Inv1M2 | IS20Inv1M3 | IS20Inv1M4 | IS20Inv2M1 | IS20Inv2M2 | IS20Inv2M3 | IS20Inv2M4 | IS21Inv1M1 | IS21Inv1M2 | IS21Inv1M3 | IS21Inv1M4 | IS21Inv2M1 | IS21Inv2M2 | IS21Inv2M3 | IS21Inv2M4 | IS22Inv1M1 | IS22Inv1M2 | IS22Inv1M3 | IS22Inv1M4 | IS22Inv2M1 | IS22Inv2M2 | IS22Inv2M3 | IS22Inv2M4 | IS23Inv1M1 | IS23Inv1M2 | IS23Inv1M3 | IS23Inv1M4 | IS23Inv2M1 | IS23Inv2M2 | IS23Inv2M3 | IS23Inv2M4 | IS24Inv1M1 | IS24Inv1M2 | IS24Inv1M3 | IS24Inv1M4 | IS24Inv2M1 | IS24Inv2M2 | IS24Inv2M3 | IS24Inv2M4 | IS25Inv1M1 | IS25Inv1M2 | IS25Inv1M3 | IS25Inv1M4 | IS25Inv2M1 | IS25Inv2M2 | IS25Inv2M3 | IS25Inv2M4 | IS26Inv1M1 | IS26Inv1M2 | IS26Inv1M3 | IS26Inv1M4 | IS26Inv2M1 | IS26Inv2M2 | IS26Inv2M3 | IS26Inv2M4 | IS27Inv1M1 | IS27Inv1M2 | IS27Inv1M3 | IS27Inv1M4 | IS27Inv2M1 | IS27Inv2M2 | IS27Inv2M3 | IS27Inv2M4 | IS28Inv1M1 | IS28Inv1M2 | IS28Inv1M3 | IS28Inv1M4 | IS28Inv2M1 | IS28Inv2M2 | IS28Inv2M3 | IS28Inv2M4 | IS29Inv1M1 | IS29Inv1M2 | IS29Inv1M3 | IS29Inv1M4 | IS29Inv2M1 | IS29Inv2M2 | IS29Inv2M3 | IS29Inv2M4 | IS30Inv1M1 | IS30Inv1M2 | IS30Inv1M3 | IS30Inv1M4 | IS30Inv2M1 | IS30Inv2M2 | IS30Inv2M3 | IS30Inv2M4 | IS31Inv1M1 | IS31Inv1M2 | IS31Inv1M3 | IS31Inv1M4 | IS31Inv2M1 | IS31Inv2M2 | IS31Inv2M3 | IS31Inv2M4 | IS32Inv1M1 | IS32Inv1M2 | IS32Inv1M3 | IS32Inv1M4 | IS32Inv2M1 | IS32Inv2M2 | IS32Inv2M3 | IS32Inv2M4 | IS33Inv1M1 | IS33Inv1M2 | IS33Inv1M3 | IS33Inv1M4 | IS33Inv2M1 | IS33Inv2M2 | IS33Inv2M3 | IS33Inv2M4 | IS34Inv1M1 | IS34Inv1M2 | IS34Inv1M3 | IS34Inv1M4 | IS34Inv2M1 | IS34Inv2M2 | IS34Inv2M3 | IS34Inv2M4 | IS35Inv1M1 | IS35Inv1M2 | IS35Inv1M3 | IS35Inv1M4 | IS35Inv2M1 | IS35Inv2M2 | IS35Inv2M3 | IS35Inv2M4 | IS36Inv1M1 | IS36Inv1M2 | IS36Inv1M3 | IS36Inv1M4 | IS36Inv2M1 | IS36Inv2M2 | IS36Inv2M3 | IS36Inv2M4 | IS37Inv1M1 | IS37Inv1M2 | IS37Inv1M3 | IS37Inv1M4 | IS37Inv2M1 | IS37Inv2M2 | IS37Inv2M3 | IS37Inv2M4 | IS38Inv1M1 | IS38Inv1M2 | IS38Inv1M3 | IS38Inv1M4 | IS38Inv2M1 | IS38Inv2M2 | IS38Inv2M3 | IS38Inv2M4 | IS39Inv1M1 | IS39Inv1M2 | IS39Inv1M3 | IS39Inv1M4 | IS39Inv2M1 | IS39Inv2M2 | IS39Inv2M3 | IS39Inv2M4 | IS40Inv1M1 | IS40Inv1M2 | IS40Inv1M3 | IS40Inv1M4 | IS40Inv2M1 | IS40Inv2M2 | IS40Inv2M3 | IS40Inv2M4 | IS41Inv1M1 | IS41Inv1M2 | IS41Inv1M3 | IS41Inv1M4 | IS41Inv2M1 | IS41Inv2M2 | IS41Inv2M3 | IS41Inv2M4 | IS42Inv1M1 | IS42Inv1M2 | IS42Inv1M3 | IS42Inv1M4 | IS42Inv2M1 | IS42Inv2M2 | IS42Inv2M3 | IS42Inv2M4 | IS43Inv1M1 | IS43Inv1M2 | IS43Inv1M3 | IS43Inv1M4 | IS43Inv2M1 | IS43Inv2M2 | IS43Inv2M3 | IS43Inv2M4 | IS44Inv1M1 | IS44Inv1M2 | IS44Inv1M3 | IS44Inv1M4 | IS44Inv2M1 | IS44Inv2M2 | IS44Inv2M3 | IS44Inv2M4 | IS45Inv1M1 | IS45Inv1M2 | IS45Inv1M3 | IS45Inv1M4 | IS45Inv2M1 | IS45Inv2M2 | IS45Inv2M3 | IS45Inv2M4 | IS46Inv1M1 | IS46Inv1M2 | IS46Inv1M3 | IS46Inv1M4 | IS46Inv2M1 | IS46Inv2M2 | IS46Inv2M3 | IS46Inv2M4 | IS47Inv1M1 | IS47Inv1M2 | IS47Inv1M3 | IS47Inv1M4 | IS47Inv2M1 | IS47Inv2M2 | IS47Inv2M3 | IS47Inv2M4 | IS48Inv1M1 | IS48Inv1M2 | IS48Inv1M3 | IS48Inv1M4 | IS48Inv2M1 | IS48Inv2M2 | IS48Inv2M3 | IS48Inv2M4 | IS49Inv1M1 | IS49Inv1M2 | IS49Inv1M3 | IS49Inv1M4 | IS49Inv2M1 | IS49Inv2M2 | IS49Inv2M3 | IS49Inv2M4 | IS50Inv1M1 | IS50Inv1M2 | IS50Inv1M3 | IS50Inv1M4 | IS50Inv2M1 | IS50Inv2M2 | IS50Inv2M3 | IS50Inv2M4 | IS51Inv1M1 | IS51Inv1M2 | IS51Inv1M3 | IS51Inv1M4 | IS51Inv2M1 | IS51Inv2M2 | IS51Inv2M3 | IS51Inv2M4 | IS52Inv1M1 | IS52Inv1M2 | IS52Inv1M3 | IS52Inv1M4 | IS52Inv2M1 | IS52Inv2M2 | IS52Inv2M3 | IS52Inv2M4 | Amb_Temp_IS2_W1 | Amb_Temp_IS4_W2 | Amb_Temp_IS6_W3 | Amb_Temp_IS9_W4 | Amb_Temp_IS15_W5 | Amb_Temp_IS19_W6 | MT_Temp_IS2_W1 | MT_Temp_IS4_W2 | MT_Temp_IS6_W3 | MT_Temp_IS9_W4 | MT_Temp_IS15_W5 | MT_Temp_IS19_W6 | WS_Avg_IS2_W1 | WS_Avg_IS4_W2 | WS_Avg_IS6_W3 | WS_Avg_IS9_W4 | WS_Avg_IS15_W5 | WS_Avg_IS19_W6 | WS_Max_IS2_W1 | WS_Max_IS4_W2 | WS_Max_IS6_W3 | WS_Max_IS9_W4 | WS_Max_IS15_W5 | WS_Max_IS19_W6 | GHI_Up_IS2_W1 | GHI_Up_IS4_W2 | GHI_Up_IS6_W3 | GHI_Up_IS9_W4 | GHI_Up_IS15_W5 | GHI_Up_IS19_W6 | GHI_Down_IS2_W1 | GHI_Down_IS4_W2 | GHI_Down_IS6_W3 | GHI_Down_IS9_W4 | GHI_Down_IS15_W5 | GHI_Down_IS19_W6 | POA_Up_IS2_W1 | POA_Up_IS4_W2 | POA_Up_IS6_W3 | POA_Up_IS9_W4 | POA_Up_IS15_W5 | POA_Up_IS19_W6 | POA_Down_IS2_W1 | POA_Down_IS4_W2 | POA_Down_IS6_W3 | POA_Down_IS9_W4 | POA_Down_IS15_W5 | POA_Down_IS19_W6 | GHI_UP_Lost_IS2_W1 | GHI_UP_Lost_IS4_W2 | GHI_UP_Lost_IS6_W3 | GHI_UP_Lost_IS9_W4 | GHI_UP_Lost_IS15_W5 | GHI_UP_Lost_IS19_W6 | POA_UP_Lost_IS2_W1 | POA_UP_Lost_IS4_W2 | POA_UP_Lost_IS6_W3 | POA_UP_Lost_IS9_W4 | POA_UP_Lost_IS15_W5 | POA_UP_Lost_IS19_W6 | 33kV_OG2_Ex | 33kV_OG2_Im | 33kV_OG1_Ex | 33kV_OG1_Im | 220kV_PQM_Ex | 220kV_PQM_Im | GHI_UP_Net_IS2_W1 | GHI_UP_Net_IS4_W2 | GHI_UP_Net_IS6_W3 | GHI_UP_Net_IS9_W4 | GHI_UP_Net_IS15_W5 | GHI_UP_Net_IS19_W6 | POA_UP_Net_IS2_W1 | POA_UP_Net_IS4_W2 | POA_UP_Net_IS6_W3 | POA_UP_Net_IS9_W4 | POA_UP_Net_IS15_W5 | POA_UP_Net_IS19_W6 | 33kV_OG2_EX (KWh) | 33kV_OG2_Im (KWh) | 33kV_OG1_Ex(KWh) | 33kV_OG1_Im(KWh) | 220kV_PQM_Ex(KWh) | 220kV_PQM_Im(KWh) | 33kV_Net_Ex (kWh) | 220kV_Net_Ex (kWh) | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Albedo GHI (%) | Albedo POA (%) | Amm_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | Inv_Exp(KWh) | WPR_Eac | WPR_Edc | WPR | Forecasting Data count received on Forecasting Portal | Forecasting Penalties (INR) | Generator Export Commisioned Capacity | Meter Export Commisioned Capacity | Meter Import Commisioned Capacity | Net Export Commisioned Capacity
2025-04-28 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-04-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 137763 | 0.28958 | 0.78889 | 1833 | 3154 | 2073 | 3492 | 4007 | 3666 | 2976 | 3518 | [8 empty] | 2943 | 3312 | 3435 | 3513 | 3532 | 3225 | 2325 | 2996 | [16 empty] | 2709 | 2641 | 2483 | 3081 | 3532 | 3225 | 2325 | 2996 | 3307 | 2966 | 3401 | 2926 | 2367 | 3063 | 3487 | 3139 | 3443 | 1403 | 2425 | 2719 | 3192 | 2642 | 3246 | 2907 | [20 empty] | 697 | 3008 | 3539 | 2556 | 3739 | 3186 | 3452 | 3667 | [16 empty] | 3625 | 3690 | 3598 | 3822 | 3271 | 3362 | 3001 | 3026 |  |  |  |  | 3168 | 3038 | 3755 | 2953 | 3765 | 3387 | 2992 | 3328 | 0 | 3755 | 3701 | 3447 | 3433 | 2546 | 3128 | 3473 | [80 empty] | 3583 | 3467 | 3067 | 3243 | 3063 | 3195 | 3392 | 3597 | 3602 | 2791 | 3296 | 2251 | 2394 | 2964 | 2618 | 2102 | 2397 | 616 | 3257 | 1844 | 3303 | 1840 | 1188 | 1982 | [8 empty] | 2641 | 2339 | 2497 | 2815 | 756 | 2764 | 3380 | 3451 | [152 empty] | 35.6 | [5 empty] | 40.87 | [5 empty] | 2.7639 | [5 empty] | 7.77 | [5 empty] | 2.591 | [11 empty] | 2.314 | [27 empty] | 1401.322 | 81.7108 | 2.591 | 0 | 0 | 0 | 0 | 0 | 2.314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140132.2048 | 4171.0752 | 0 | 135961.1296 | 11.9833 | 2.591 |  | 2.314 |  |  |  | 35.6 | 40.87 | 2.7639 | 7.77 | 306428 | [6 empty] | 0 |  | 0
2025-04-30 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 137763 | 0.27917 | 0.77917 | 1140 |  | 60160 | 76660 | 39.07 | 363.45 | 295.81 | 347.84 | [8 empty] | 2420 | 2770 | 2820 | 2850 | 2890 | 3000 | 2200 | 2610 | [16 empty] | 2310 | 2280 | 2420 | 2700 | 2290 | 2760 | 2140 | 2630 | 2780 | 2590 | 2880 | 2530 | 1960 | 2960 | 3060 | 2750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2820 | 2270 | 2530 | 2310 | 2650 | 2210 | 2710 | 2470 | [12 empty] | 1230 | 1320 | 1400 | 970 | 1420 | 1300 | 1460 | 1370 | [16 empty] | 2880 | 3000 | 3010 | 3110 | 2680 | 2800 | 2490 | 2510 |  |  |  |  | 3090 | 2900 | 2490 | 2780 | 0 | 0 | 0 | 0 | 100 | 3120 | 3090 | 2100 | 2070 | 2090 | 2590 | 2880 | [80 empty] | 1040 | 1250 | 400 | 1700 | 2500 | 2660 | 2840 | 2990 | 2910 | 2300 | 2770 | 1890 | 2160 | 2470 | 2150 | 1690 | 2730 | 1490 | 2730 | 2060 | 2690 | 1780 | 2570 | 2390 | [12 empty] | 510 | 2270 | 2810 | 2870 | [152 empty] | 35.754 | [5 empty] | 49.936 | [5 empty] | 3.27 | [5 empty] | 7.12 | [5 empty] | 2.405 | [11 empty] | 2.466 | [27 empty] | 1544 | 85.76 | 2.405 | 0 | 0 | 0 | 0 | 0 | 2.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142677.952 | 4049.248 | 0 | 138628.704 | 12 | 2.405 |  | 2.466 |  |  |  | 35.754 | 49.936 | 3.27 | 7.12 | 344446.17 | [6 empty] | 0 |  | 0
2025-05-01 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.27917 | 0.77917 | 1406 | 2679.1 | 1920.7 | 3037.3 | 3339.8 | 3053.7 | 2593 | 2926.9 | [8 empty] | 3339.8 | 3055.7 | 2595 | 2920.9 | 2955 | 2915 | 2509 | 2743 | [16 empty] | 2739.8 | 2941 | 2732.4 | 2746.8 | 2377.6 | 2780.8 | 2064 | 2716 | 2818.3 | 2547.9 | 2838.4 | 2515.8 | 1943.4 | 2918.8 | 3001.4 | 2788 | 2887 | 2554.5 | 2836.2 | 2610.6 |  |  |  |  | 2887 | 2554.5 | 2836.2 | 2610.6 | 2619 | 2119.3 | 2627.1 | 2370.3 | [12 empty] | 1755.9 | 2905.9 | 3143.8 | 2025.5 | 3191.8 | 2887.6 | 3333.3 | 3130 | [16 empty] | 2768.6 | 2830.2 | 2831.6 | 2946.8 | 2668 | 2745.4 | 2428.6 | 2450.1 |  |  |  |  | 2599.1 | 2482.5 | 3156.9 | 2377.6 | 3120.2 | 2838.5 | 2425.1 | 2707.2 | 2646.3 | 3049.9 | 3048.1 | 2825.9 | 2792.8 | 2009.3 | 2521.4 | 2817.8 | [80 empty] | 2599.1 | 2482.5 | 3156.9 | 2377.6 | 3120.2 | 2838.5 | 2425.1 | 2707.2 | 2646.3 | 3049.9 | 3048.1 | 2825.9 | 2792.8 | 2009.3 | 2521.4 | 2817.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [152 empty] | 34.297 | [5 empty] | 39.0963 | [5 empty] | 4.2859 | [5 empty] | 15.16 | [5 empty] | 4.9066 | [11 empty] | 4.5988 | [27 empty] | 1669.7456 | 88.8649 | 4.9066 | 0 | 0 | 0 | 0 | 0 | 4.5988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125745.632 | 3104.864 | 0 | 122640.768 | 12 | 4.9066 |  | 4.5988 |  |  |  | 34.297 | 39.0963 | 4.2859 | 15.16 | 248852.9 | [6 empty] | 0 |  | 0
2025-05-02 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.28194 | 0.78194 | 902.5 | 1716.1 | 1260.8 | 2110.7 | 2303.6 | 2091.2 | 1773.1 | 1966.2 | [8 empty] | 2151.1 | 2381.9 | 2234.1 | 2238.2 | 2420.1 | 2440.1 | 2091.5 | 2257.9 | [16 empty] | 2822.8 | 3030.8 | 2880.8 | 2931.8 | 2767.4 | 3071.6 | 2896.1 | 2944.2 | 2339.9 | 2227.5 | 2423 | 2387.6 | 1713.9 | 2436.7 | 2377.2 | 2250.6 | [8 empty] | 1991.8 | 1989 | 1821.7 | 1898.3 | 1695.7 | 1653.5 | 1788.1 | 1562.8 | [12 empty] | 2183.8 | 1955.6 | 2080.2 | 1373.4 | 2081.4 | 1886.5 | 2143.4 | 2129.9 | [16 empty] | 2098.3 | 2167.6 | 2151.5 | 2250.8 | 1963.9 | 2081.1 | 1884.1 | 1772.2 |  |  |  |  | 1745.1 | 1674.8 | 2124.7 | 1630.5 | 2134.9 | 1930.4 | 1650 | 1833.2 | [280 empty] | 34.2029 | [5 empty] | 39.9772 | [5 empty] | 2.8763 | [5 empty] | 10.26 | [5 empty] | 6.6614 | [11 empty] | 6.6845 | [27 empty] | 1863.8234 | 94.6437 | 6.6614 | 0 | 0 | 0 | 0 | 0 | 6.6845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194077.76 | 5778.816 | 0 | 188298.944 | 12 | 6.6614 |  | 6.6845 |  |  |  | 34.2029 | 39.9772 | 2.8763 | 10.26 | 135169.2 | [6 empty] | 0 |  | 0
2025-05-03 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.27014 | 0.77014 | 751.3 | 2479.4 | 1044.3 | 2886.9 | 3185.9 | 2874.8 | 2431.8 | 2697 | [8 empty] | 2730.9 | 2967 | 2713.8 | 2780.2 | 3007.4 | 3030.2 | 2523.3 | 2786.7 | [16 empty] | 1258.6 | 1324.4 | 1239.7 | 1269.7 | 1167.2 | 1361.9 | 1251.6 | 1282.7 | 2976.8 | 2787.1 | 3156.8 | 3019.3 | 2424.7 | 3367.6 | 3286.3 | 3124.2 | [8 empty] | 4228.2 | 4283.4 | 4246.4 | 4159.2 | 3797.5 | 3715.8 | 3972.9 | 3574.2 | [12 empty] | 3071.6 | 2624.9 | 2950.7 | 1972.6 | 2945 | 2673.7 | 3013.5 | 2997 | [16 empty] | 2954.7 | 3049.7 | 3018.2 | 3156.2 | 2743 | 2878.2 | 2641.5 | 2503 |  |  |  |  | 2390.2 | 2297 | 2915 | 3335.8 | 2941.9 | 2637.6 | 2263.7 | 2516.2 | 1570.4 | 1820.7 | 1821.3 | 1771.7 | 1719.5 | 1321.2 | 1596.4 | 1726.4 | [80 empty] | 2760.7 | 2871.5 | 2674.9 | 2569.2 | 2527.9 | 2597.1 | 2656 | 2795.8 | 3082 | 2272.4 | 2783.6 | 2723.9 | 2809.4 | 2472.5 | 2440.7 | 1747 | 2794 | 1990.2 | 2768.8 | 2417.8 | 2972.2 | 2175.9 | 2504.9 | 2399.9 | [8 empty] | 2414.9 | 2221.1 | 2759.3 | 2927.1 | 2963.3 | 3047.1 | 2771.6 | 2729.9 | [152 empty] | 34.9701 | [5 empty] | 43.522 | [5 empty] | 3.336 | [5 empty] | 12.89 | [5 empty] | 6.957 | [11 empty] | 6.9533 | [27 empty] | 2127.3831 | 100.3137 | 6.957 | 0 | 0 | 0 | 0 | 0 | 6.9533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263559.744 | 5670.048 | 0 | 257889.696 | 12 | 6.957 |  | 6.9533 |  |  |  | 34.9701 | 43.522 | 3.336 | 12.89 | 270648.2 | [6 empty] | 0 |  | 0
2025-05-04 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.28056 | 0.78056 | 0 | 1422.1 | 0 | 0 | 1625.1 | 1576.5 | 1375.2 | 1496.1 | [8 empty] | 1524.7 | 1661.7 | 309.1 | 1535.6 | 1629 | 1640 | 1457 | 1572.1 | [16 empty] | 1011.5 | 1053.1 | 1013.9 | 1029.6 | 971.6 | 1072.7 | 1016.5 | 1002.9 | 1613.6 | 1534.5 | 1663.2 | 1622.3 | 1272.4 | 1662.5 | 1630.2 | 1555.8 | [8 empty] | 1522.7 | 1528.2 | 1524.1 | 1489.5 | 1349.7 | 1314.8 | 1425.7 | 1248.4 | [12 empty] | 1600.4 | 1442.6 | 1542.6 | 1156.2 | 1559.3 | 1447.4 | 1579.4 | 1566.8 | [16 empty] | 1688.2 | 1729.6 | 1707.2 | 1686.3 | 1498.5 | 1557 | 1457.3 | 1387.6 |  |  |  |  | 1397.2 | 1340.6 | 1606.3 | 1320.9 | 1604.5 | 1499.8 | 1334.6 | 1450.8 | 1394.7 | 1594 | 1602.1 | 1515 | 1511 | 1170 | 1379 | 1523.1 | [80 empty] | 1578.9 | 1567.3 | 1547.4 | 1447.3 | 1442.1 | 1475.3 | 1502.5 | 1565.6 | 1715 | 1326.8 | 1545 | 1513.8 | 1560.7 | 1484.6 | 1159.9 | 1152.3 | 1590.3 | 1306.2 | 1544.6 | 1415.5 | 108.1 | 1313.4 | 1461.6 | 1405.9 | [8 empty] | 1402.4 | 1177.6 | 1454.4 | 1493.4 | 1549.6 | 1618.3 | 1473.7 | 1475.8 | [152 empty] | 31.1 | [5 empty] | 31.1228 | [5 empty] | 5.8533 | [5 empty] | 17.25 | [5 empty] | 6.8413 | [39 empty] | 2274.9159 | 106.0155 | 6.8413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147532.768 | 5701.792 | 0 | 141830.976 | 12 | 6.8413 | [5 empty] | 31.1 | 31.1228 | 5.8533 | 17.25 | 144178.9 | [6 empty] | 0 |  | 0
2025-05-05 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.29097 | 0.79097 | 839.7 | 1374.1 | 1032.9 | 1508 | 1676.1 | 1543.1 | 1337.3 | 1472.8 | [8 empty] | 1540.3 | 1615.2 | 1417 | 1503.4 | 1595.9 | 1571.9 | 1386.7 | 1529.6 | [16 empty] | 1448 | 1524.8 | 1455.8 | 1483.8 | 1380.2 | 1577.5 | 1469.4 | 1257.8 | 1560.2 | 1490.4 | 1652.7 | 1577.7 | 1211.2 | 1628.4 | 1588.9 | 1506.5 | [8 empty] | 1459.6 | 1462.3 | 1492.6 | 1459.8 | 1305.6 | 583.9 | 1337.3 | 1186.2 | [12 empty] | 1584.2 | 1383.4 | 1528.8 | 1108.4 | 1546.4 | 1427.9 | 1570.1 | 1557.6 | [16 empty] | 1603.3 | 1646.6 | 1632.1 | 0 | 1448.8 | 268.1 | 1393.1 | 1313.5 |  |  |  |  | 1234.5 | 1261.2 | 1546 | 1236.8 | 1535.9 | 1426.8 | 1248.9 | 1370.9 | 1319.3 | 1533.8 | 1530 | 1442.5 | 1445.2 | 1085.8 | 1306.1 | 1458.4 | [80 empty] | 1535.4 | 1547.7 | 1513.6 | 1408.2 | 1402.6 | 1418 | 1462.1 | 1513.3 | 1698.5 | 1281.5 | 1514.3 | 1483.3 | 1522.4 | 0 | 1409 | 1074.3 | 1564.1 | 1144.2 | 1509.7 | 1367.5 | 1607 | 1261.4 | 1422.6 | 1363.6 | [8 empty] | 1337.1 | 1127.1 | 1411.4 | 1459.3 | 1617.2 | 1686.1 | 1526 | 16.8 | [152 empty] | 35.108 | [5 empty] | 40.109 | [5 empty] | 1.79 | [5 empty] | 10.52 | [5 empty] | 6.0953 | [11 empty] | 6.0014 | [27 empty] | 2420.2084 | 111.7805 | 6.0953 | 0 | 0 | 0 | 0 | 0 | 6.0014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145292.448 | 5764.96 | 0 | 139527.488 | 12 | 6.0953 |  | 6.0014 |  |  |  | 35.108 | 40.109 | 1.79 | 10.52 | 143244.3 | [6 empty] | 0 |  | 0
2025-05-06 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.28194 | 0.78194 | 100.8 | 113.4 | 105.1 | 116.7 | 120.1 | 118.3 | 106.4 | 115.7 | [8 empty] | 118.7 | 123.7 | 117.9 | 120 | 119.6 | 121 | 116.7 | 119.2 | [16 empty] | 660 | 680.5 | 661.1 | 668.6 | 637.7 | 677.6 | 665.5 | 570.7 | 675.6 | 665.9 | 509.5 | 681 | 566.5 | 508.1 | 641.2 | 624.1 | [8 empty] | 123.8 | 122.3 | 123 | 122 | 119.7 | 118.3 | 118.4 | 116.9 | [12 empty] | 124.5 | 120.5 | 121.1 | 116 | 126.3 | 123.7 | 126.8 | 126 | [16 empty] | 153.5 | 154.4 | 145.3 | 0 | 127.4 | 126.8 | 129.5 | 122.4 |  |  |  |  | 127.4 | 127.4 | 132.5 | 125.8 | 133.3 | 130 | 125 | 129.4 | 128.9 | 133.3 | 133.7 | 132.8 | 134.6 | 121.7 | 128.7 | 136.3 | [80 empty] | 978.1 | 953.3 | 975.4 | 949.6 | 926.2 | 930.3 | 940.6 | 831.7 | 163.3 | 144.9 | 147.4 | 143.4 | 147.7 | 0 | 159.3 | 156.9 | 154.2 | 147.5 | 157.5 | 153.1 | 157.5 | 155.2 | 155.1 | 151.8 | [8 empty] | 2500.3 | 2339.9 | 2529.5 | 2423.4 | 2570.5 | 2617.2 | 2390.5 | 2423.1 | [152 empty] | 30.349 | [5 empty] | 42.3927 | [5 empty] | 1.1886 | [5 empty] | 9.16 | [5 empty] | 6.235 | [11 empty] | 6.2207 | [27 empty] | 2463.8727 | 117.2278 | 6.235 | 0 | 0 | 0 | 0 | 0 | 6.2207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43664.352 | 5447.296 | 0 | 38217.056 | 12 | 6.235 |  | 6.2207 |  |  |  | 30.349 | 42.3927 | 1.1886 | 9.16 | 46510.7 | [6 empty] | 0 |  | 0
2025-05-07 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.28125 | 0.78056 | 1236.2 | 2134 | 1541.3 | 2366.9 | 2630.3 | 2384.9 | 1681.3 | 2227 | [8 empty] | 2393.4 | 2514.2 | 2237.6 | 2428.4 | 2478 | 2429.4 | 2109.4 | 2397 | [16 empty] | 2286.9 | 2435.9 | 2177.9 | 1970.3 | 2094.8 | 2393.1 | 2295 | 1573.3 | 2429.7 | 2329.8 | 2623 | 2329 | 1844.5 | 2587.1 | 2497 | 2350.4 | [8 empty] | 2243.6 | 2236.2 | 2290.3 | 2207.7 | 1943.6 | 1823.7 | 2010.7 | 1776.7 | [12 empty] | 2482.7 | 2156.4 | 2406.5 | 1670.4 | 2420.4 | 2226.9 | 2426.5 | 2474.2 | [16 empty] | 572.6 | 574.2 | 567.1 | 0 | 2456.6 | 2347.9 | 2483 | 2149 |  |  |  |  | 2054.8 | 1686.8 | 2435.1 | 1905.9 | 2449.9 | 2239.8 | 1934.3 | 2143.2 | 2202.2 | 2438.6 | 2422.4 | 3222.6 | 2291.1 | 1720.3 | 2084.6 | 2299.2 | [80 empty] | 2234.1 | 2380.8 | 2247.4 | 2181 | 460.3 | 465.8 | 474.9 | 473 | 2531.8 | 2478.3 | 2323.8 | 2275.5 | 2385.2 | 2204.5 | 2260.8 | 2011.9 | 2430.7 | 1723.2 | 2612.9 | 2300.8 | 2523.6 | 2261.5 | 2170.5 | 2097.8 | [8 empty] | 2000.5 | 1671.1 | 2122 | 1836.9 | 2503.7 | 2584 | 2262.7 | 33.6 | [152 empty] | 28.97 | [5 empty] | 38.74 | [5 empty] | 2.05 | [5 empty] | 7.17 | [5 empty] | 7.294 | [11 empty] | 7.2484 | [27 empty] | 2677.9714 | 120.3311 | 7.294 | 0 | 0 | 0 | 0 | 0 | 7.2484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214098.688 | 3103.296 | 0 | 210995.392 | 11.9833 | 7.294 |  | 7.2484 |  |  |  | 28.97 | 38.74 | 2.05 | 7.17 | 215409.3 | [6 empty] | 0 |  | 0
2025-05-08 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.27708 | 0.78542 | 773.9 | 1410.4 | 1002.4 | 1602.9 | 1787.3 | 1622.3 | 1075.7 | 1079.6 | [8 empty] | 1583.4 | 1642.7 | 1446.4 | 1567.4 | 1633.4 | 1597.2 | 1378.8 | 1568.3 | [16 empty] | 1493.9 | 1574.8 | 1480.8 | 1521.5 | 1358 | 1572.7 | 1497.8 | 969.2 | 1382.3 | 1469.5 | 1664 | 1586.8 | 1124.5 | 1598.8 | 1601.6 | 1501.9 | [8 empty] | 1432.4 | 1415.2 | 1346.2 | 1427.5 | 1248.9 | 1071.7 | 1181.3 | 1119.2 | [12 empty] | 1642.4 | 1442 | 1582.6 | 1052 | 1590.4 | 1445.6 | 1588.7 | 1616.3 | [16 empty] | 396.3 | 400.7 | 403.7 | 0 | 1574.2 | 1520.7 | 1582.3 | 1540.3 |  |  |  |  | 1311 | 1200.9 | 1581.3 | 1202.7 | 1570.8 | 1423.4 | 1225.8 | 1377.6 | 1443 | 1574.5 | 1564.4 | 1445.6 | 1451.6 | 1095.9 | 1289.5 | 1452.9 | [80 empty] | 1311.3 | 1200.9 | 1581.3 | 1202.7 | 359.3 | 335.2 | 343.2 | 356.9 | 1632.6 | 1640.8 | 1505.4 | 1468.5 | 1543.2 | 1248.4 | 0 | 1252.8 | 1594.5 | 996.4 | 1676.8 | 1469.6 | 1618.9 | 1490.8 | 1548.5 | 1589 | [8 empty] | 1231.6 | 1121 | 1425.7 | 1188.5 | 1625 | 1669.8 | 1546.9 | 0 | [152 empty] | 33.3027 | [5 empty] | 34.0745 | [5 empty] | 3.1715 | [5 empty] | 16.28 | [5 empty] | 3.9392 | [11 empty] | 3.8596 | [27 empty] | 2815.5359 | 130.0767 | 3.9392 | 0 | 0 | 0 | 0 | 0 | 3.8596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137564.544 | 9745.664 | 0 | 127818.88 | 12.2 | 3.9392 |  | 3.8596 |  |  |  | 33.3027 | 34.0745 | 3.1715 | 16.28 | 136777.2 | [6 empty] | 0 |  | 0
2025-05-09 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.28542 | 0.78542 | 3769.7 | 5039 | 3983.9 | 6291.3 | 6857.9 | 4340.7 | 4117.2 | 5718.5 | [8 empty] | 6230.6 | 6470.3 | 5696.6 | 6308.6 | 6409.4 | 6382.2 | 6461.9 | 6170.2 | [16 empty] | 5903.7 | 6072.6 | 6075.7 | 5951.3 | 5287 | 6094.2 | 5827.9 | 4950.7 | 6145.1 | 5970.6 | 5701.5 | 6582.5 | 4608.9 | 6662.4 | 6464.6 | 6062.2 | [8 empty] | 5630.5 | 5688 | 4639.8 | 5342 | 5010.4 | 4440.5 | 4934.9 | 457.6 | [12 empty] | 6697.1 | 6066.5 | 6295.1 | 5266.2 | 6257.3 | 6126.6 | 6264.1 | 6447.8 | [16 empty] | 6325.2 | 6483.2 | 6462.2 | 6251.2 | 6345.8 | 6069.2 | 6346.2 | 6223.7 |  |  |  |  | 6137 | 6175.8 | 6362.7 | 5212.1 | 6392.3 | 5767.1 | 4884.2 | 5681 | 5809.5 | 6302.8 | 6258.7 | 5760.4 | 5817.5 | 4398.6 | 5221.4 | 5808.6 | [80 empty] | 5769 | 6272.6 | 6187.4 | 6489.6 | 1357.4 | 3911.2 | 5746.4 | 5920.6 | 6499.4 | 6530.3 | 6039.1 | 5912.3 | 6195.9 | 5406.6 | 0 | 5049.5 | 6380.7 | 4385.9 | 6691.5 | 5881.6 | 6544.2 | 5904.7 | 6185.8 | 6414.4 | [8 empty] | 4984.8 | 4473.7 | 5705.3 | 4768.5 | 6502.2 | 6665.4 | 6218 | 4405.3 | [152 empty] | 28.0071 | [5 empty] | 33.4041 | [5 empty] | 2.8703 | [5 empty] | 12.32 | [5 empty] | 6.0254 | [11 empty] | 5.874 | [27 empty] | 3395.268 | 135.1522 | 6.0254 | 0 | 0 | 0 | 0 | 0 | 5.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 579732.064 | 5075.424 | 0 | 574656.64 | 12 | 6.0254 |  | 5.874 |  |  |  | 28.0071 | 33.4041 | 2.8703 | 12.32 | 588069 | [6 empty] | 0 |  | 0
2025-05-10 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.27431 | 0.77431 | 1020.7 | 1034.4 | 1073.5 | 1647.6 | 1790.6 | 1669.3 | 1111.5 | 1519.4 | [8 empty] | 1636.5 | 1698.5 | 1510.4 | 1643.9 | 1677.9 | 1664.5 | 1448.4 | 1614.7 | [16 empty] | 1551.3 | 1599.7 | 535.7 | 836.2 | 1405.2 | 1614.2 | 1522.3 | 1315.3 | 1606.8 | 1544.2 | 1495.7 | 1723.6 | 1229 | 1603.9 | 1701.3 | 1603.9 | [8 empty] | 1483.4 | 1480.1 | 1242.3 | 1414.8 | 1339.5 | 1267 | 1340.7 | 1221.6 | [12 empty] | 1747.4 | 1586.9 | 1629.3 | 1670.7 | 1652.8 | 1625.6 | 1651.8 | 1693.5 | [16 empty] | 1725.2 | 1757.5 | 1752.9 | 1760.9 | 1667.6 | 1619.4 | 1671.2 | 1629.3 |  |  |  |  | 1624.4 | 1632.7 | 1698.3 | 1402.6 | 1685 | 1545.9 | 1352.4 | 1543.3 | 1537.1 | 1670.1 | 1657.7 | 1510.3 | 1546.1 | 1187.4 | 1377.6 | 1550.7 | [80 empty] | 1551.1 | 1655.8 | 1644.6 | 1725.7 | 1142.8 | 1515.3 | 1522.8 | 0.2 | 1737.7 | 1733.6 | 1602.7 | 1564.7 | 1637.8 | 0.2 | 0 | 1264.7 | 1690.1 | 1218.5 | 1770.2 | 1568.8 | 1714 | 1568.3 | 1644.2 | 1702.7 | [8 empty] | 1338.1 | 1210.2 | 1490.1 | 1268.1 | 1675.1 | 1766.9 | 1230.3 | 1289 | [152 empty] | 31.5324 | [5 empty] | 38.2776 | [5 empty] | 1.4798 | [5 empty] | 8.01 | [5 empty] | 7.06 | [11 empty] | 6.9639 | [27 empty] | 3548.057 | 138.5732 | 7.06 | 0 | 0 | 0 | 0 | 0 | 6.9639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152788.96 | 3421.024 | 0 | 149367.936 | 12 | 7.06 |  | 6.9639 |  |  |  | 31.5324 | 38.2776 | 1.4798 | 8.01 | 153247.4 | [6 empty] | 0 |  | 0
2025-05-11 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.29028 | 0.79028 | [8 empty] | 1400 | 1610 | 1740 | 1920 | 1530 | 1130 | 710 | 1680 | [8 empty] | 0 | 1880 | 0 | 0 | 1360 | 1040 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 950 | 1040 | [16 empty] | 180 | 990 | 360 | 1070 | 1670 | 1430 | 1270 | 1590 | [28 empty] | 1810 | 1690 | 1500 | 740 | 1470 | 0 | 780 | 1830 | 550 | 0 | 750 | 220 | 0 | 0 | 0 | 0 | [28 empty] | 1120 | 1200 | 280 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 750 | 330 | 1240 | 1310 | 0 | 0 | 0 | 0 | 1100 | 750 | 190 | 1500 | 1760 | 1500 | 160 | 170 | [72 empty] | 0 | 0 | 0 | 0 | 460 | 1190 | 1390 | 1210 | [128 empty] | 1880 | 1570 | 1680 | 1450 | 0 | 1260 | 0 | 1810 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 33.32 | [5 empty] | 40.1661 | [5 empty] | 2.4157 | [5 empty] | 6.55 | [5 empty] | 6.0742 | [11 empty] | 6.1296 | [27 empty] | 3618.6762 | 146.0182 | 6.0742 | 0 | 0 | 0 | 0 | 0 | 6.1296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70619.2 | 7444.992 | 0 | 63174.208 | 12 | 6.0742 |  | 6.1296 |  |  |  | 33.32 | 40.1661 | 2.4157 | 6.55 | 66870 | [6 empty] | 0 |  | 0
2025-05-12 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.29028 | 0.79028 | [8 empty] | 2922.9 | 3424.4 | 3692.1 | 4051.5 | 3171.6 | 2352.6 | 1416.7 | 3513.1 | [8 empty] | 1946.1 | 3912.6 | 2396.6 | 2310 | 2867.9 | 2212.9 | 2790.3 | 1633.9 | 258.7 | 2552.5 | 1912.6 | 1807.1 | 1890.1 | 3804.4 | 2044.7 | 2142.1 | [16 empty] | 323 | 2058.9 | 796.9 | 2204.2 | 3194.7 | 3020.2 | 2719.8 | 3441.1 | [28 empty] | 3920.2 | 3658.1 | 3248.2 | 1550.9 | 3184.1 | 1875.8 | 1621.3 | 3931.8 | 2366.8 | 223.4 | 2436.7 | 843.5 | 1405.9 | 3444.3 | 574.5 | 3153.3 | [28 empty] | 2245.6 | 2434.8 | 662.1 | 0 | 0 | 0 | 0 | 1724.8 | [8 empty] | 1586.4 | 600.6 | 2724.2 | 2963.4 | 185.4 | 0 | 0 | 0 | 2432.5 | 1602.8 | 1655.3 | 3323.3 | 3947.2 | 3673.2 | 1784.5 | 1680.8 | [72 empty] | 0 | 0 | 0 | 1374.2 | 1064.7 | 2713.6 | 3095.9 | 2696.7 | [128 empty] | 3958.7 | 3335.2 | 3542.1 | 3032.8 | 1668.4 | 2733.3 | 475.1 | 3800.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 34.5785 | [5 empty] | 47.5256 | [5 empty] | 4.2741 | [5 empty] | 10.06 | [5 empty] | 7.7969 | [11 empty] | 7.6949 | [27 empty] | 3800.818 | 155.8024 | 7.7969 | 0 | 0 | 0 | 0 | 0 | 7.6949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182141.824 | 9784.192 | 0 | 172357.632 | 12 | 7.7969 |  | 7.6949 |  |  |  | 34.5785 | 47.5256 | 4.2741 | 10.06 | 184943 | [6 empty] | 0 |  | 0
2025-05-13 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.27917 | 0.77917 | 2283.9 | 3134.4 | 2416 | 3836 | 4176.9 | 3866.2 | 2516.7 | 3526.1 | [8 empty] | 3901.5 | 3918.7 | 3468.2 | 3811.8 | 3865.6 | 3827.7 | 3320.5 | 0 | [16 empty] | 3594 | 3653 | 3649.8 | 3593.1 | 3201 | 3793.5 | 3535.1 | 3086.7 | 3684 | 3535.8 | 3410.2 | 3913.9 | 2790.8 | 3930.8 | 3844.4 | 3619.3 | [8 empty] | 3363 | 3373.9 | 2809.1 | 3188.6 | 2999.7 | 2726.4 | 3021.1 | 2756.3 | [12 empty] | 3945 | 3581.3 | 3702 | 3838 | 3135 | 3691.8 | 3700.5 | 3816.9 | [16 empty] | 3750.9 | 3822.1 | 3820.9 | 0 | 3724.3 | 3569.5 | 3736.7 | 3660.2 |  |  |  |  | 3604.4 | 3618.9 | 3737.6 | 3092 | 3740.9 | 3410.9 | 2981.1 | 3402.1 | 3417.3 | 3687.2 | 3659.8 | 3395.8 | 3420.4 | 2636.1 | 3085.6 | 3415.1 | [80 empty] | 3411.4 | 2938.5 | 2548.4 | 771.8 | 768.4 | 2732.9 | 3360.2 | 3585.1 | 3783 | 3774.1 | 3521.8 | 3435.4 | 3596.5 | 3270.4 | 0 | 2966.5 | 3770.3 | 3461.3 | 3859.9 | 3419.7 | 3773.1 | 2822.4 | 3710.5 | 3798.1 | [8 empty] | 2918 | 2630.8 | 3150.2 | 1060.7 | 1933.6 | 2353.3 | 3571.7 | 2801.9 | [152 empty] | 34.5501 | [5 empty] | 42.2984 | [5 empty] | 4.5099 | [5 empty] | 10.75 | [5 empty] | 7.7369 | [11 empty] | 7.6363 | [27 empty] | 4210.8811 | 163.3086 | 7.7369 | 0 | 0 | 0 | 0 | 0 | 7.6363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410063.104 | 7506.24 | 0 | 402556.864 | 12 | 7.7369 |  | 7.6363 |  |  |  | 34.5501 | 42.2984 | 4.5099 | 10.75 | 336243.9 | [6 empty] | 0 |  | 0
2025-05-14 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.28542 | 0.78542 | [8 empty] | 5681.8 | 6738.6 | 7278.9 | 8034.7 | 6243.6 | 4489.1 | 2608.1 | 6879.8 | [8 empty] | 6056.4 | 7951.1 | 8008.9 | 7571.1 | 5839.2 | 4879.4 | 5633.7 | 5656.8 | 3715.7 | 6176.6 | 3837.6 | 3893.2 | 7030.8 | 7634.5 | 5262.8 | 4760.6 | [16 empty] | 6868.8 | 5453.6 | 4285.5 | 4193.2 | 6243.9 | 5850.9 | 5268.6 | 6750.6 | [28 empty] | 3874.8 | 5637.8 | 6403.6 | 3545.2 | 6156.1 | 7434.3 | 4404.2 | 3765.7 | 4574.2 | 490.8 | 6590.3 | 7210.9 | 5355.7 | 6826.9 | 6504.1 | 6232.5 | [28 empty] | 6578.6 | 5765.4 | 1986.8 | 713 | 0 | 0 | 0 | 2899 | [8 empty] | 2366.9 | 829.6 | 4017.5 | 3496.6 | 0 | 0 | 0 | 0 | 949.7 | 743.7 | 1313.9 | 1231.7 | 1499.4 | 1363.7 | 1295.8 | 1129.6 | [72 empty] | 0 | 0 | 0 | 2806.3 | 2448.9 | 6094.6 | 7228.4 | 5287.2 | [128 empty] | 7647 | 7504.3 | 6815.6 | 6939.2 | 6564 | 6447.9 | 2334.1 | 7713.6 | 0.9 | 0 | 0 | 0 | 3051.9 | 2372.4 | 683.3 | 96.4 | [16 empty] | 33.0666 | [5 empty] | 49.9424 | [5 empty] | 3.2686 | [5 empty] | 8.91 | [5 empty] | 6.7067 | [11 empty] | 6.7515 | [27 empty] | 4607.2815 | 170.93 | 6.7067 | 0 | 0 | 0 | 0 | 0 | 6.7515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396400.448 | 7621.408 | 0 | 388779.04 | 12 | 6.7067 |  | 6.7515 |  |  |  | 33.0666 | 49.9424 | 3.2686 | 8.91 | 392002.1 | [6 empty] | 0 |  | 0
2025-05-15 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.27847 | 0.77847 | [8 empty] | 311.2 | 367.5 | 392.9 | 427.4 | 332.9 | 260.2 | 168.1 | 374.1 | [8 empty] | 332.7 | 426.8 | 429.9 | 405.7 | 328.2 | 267.3 | 305.5 | 313.4 | 240.9 | 377.7 | 229.4 | 233.4 | 390.1 | 414 | 300.7 | 290.6 | [16 empty] | 387.1 | 316.3 | 255 | 250.9 | 346.9 | 325 | 295.9 | 376.1 | [28 empty] | 1609.8 | 2296.1 | 2965.6 | 2170.9 | 2491.3 | 2947.8 | 2301.4 | 1576.8 | 3461.3 | 349.3 | 3801.4 | 3911.7 | 3377.8 | 3830.9 | 3778.7 | 3736.9 | [28 empty] | 375.7 | 332 | 150.8 | 217 | 0 | 0 | 0 | 432 | [8 empty] | 207.6 | 109.6 | 313.6 | 278.9 | 177.9 | 0 | 0 | 0 | 435.8 | 289.1 | 425.7 | 407.2 | 481.7 | 447.8 | 427.8 | 400.7 | [72 empty] | 0 | 0 | 0 | 1.5 | 202.8 | 387.7 | 446.2 | 346.3 | [128 empty] | 467.8 | 463.5 | 425.3 | 432.6 | 419.7 | 404.8 | 203.3 | 475.2 | 127.3 | 0 | 0 | 0 | 403.4 | 333.3 | 293.8 | 231.5 | [16 empty] | 35.9319 | [5 empty] | 42.9914 | [5 empty] | 3.0187 | [5 empty] | 9.88 | [5 empty] | 7.924 | [11 empty] | 7.7875 | [27 empty] | 4669.1697 | 178.228 | 7.924 | 0 | 0 | 0 | 0 | 0 | 7.7875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61888.128 | 7297.984 | 0 | 54590.144 | 12 | 7.924 |  | 7.7875 |  |  |  | 35.9319 | 42.9914 | 3.0187 | 9.88 | 67058.4 | [6 empty] | 0 |  | 0
2025-05-16 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.27083 | 0.77083 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [28 empty] | 97.8 | 141.1 | 186.7 | 136.6 | 159 | 189.9 | 144.1 | 94.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1344.5 | 863.4 | 1312.9 | 1261.6 | 1306.7 | 1164.7 | 1347.5 | 894.3 | [48 empty] | 5090.5 | 3857.8 | 2792 | 971.9 | 945.1 | 2352.7 | 4519.3 | 5384.4 | 310.3 | 310.4 | 294.1 | 239.9 | 300.4 | 285.2 | 0 | 249.3 | 312.8 | 295.4 | 319.7 | 295.6 | 311.2 | 245 | 313.8 | 318.4 | 0 | 0 | 0 | 3943.2 | 0 | 0 | 0 | 0 | [128 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 36.4273 | [5 empty] | 42.2396 | [5 empty] | 4.1783 | [5 empty] | 9.76 | [5 empty] | 7.8278 | [11 empty] | 7.7046 | [27 empty] | 4709.1493 | 185.3326 | 7.8278 | 0 | 0 | 0 | 0 | 0 | 7.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39979.616 | 7104.64 | 0 | 32874.976 | 12 | 7.8278 |  | 7.7046 |  |  |  | 36.4273 | 42.2396 | 4.1783 | 9.76 | 44903.7 | [6 empty] | 0 |  | 0
2025-05-17 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.28542 | 0.78472 | [8 empty] | 1319.6 | 1499.8 | 1637.8 | 1800.3 | 1671.3 | 1031.5 | 664.2 | 1570.2 | [8 empty] | 1469.4 | 1801.7 | 1793.4 | 1694.2 | 1310.9 | 1106.2 | 1323.3 | 1282.8 | 1000.4 | 1606.6 | 962.1 | 913.2 | 1604.2 | 1689.9 | 1167.9 | 1103.9 | [16 empty] | 1542.6 | 1336.8 | 1197.9 | 982 | 1399.4 | 1355.1 | 1206 | 1499.9 | [28 empty] | 1139.7 | 1257.1 | 1702.8 | 1233.6 | 1415.4 | 1689.7 | 1310.5 | 1450.9 | 1374.7 | 193.8 | 1460.9 | 1634.3 | 1221.1 | 1596.1 | 1480 | 1415.2 | [28 empty] | 1489.8 | 1333.9 | 1106.5 | 1337.1 | 0 | 1502.5 | 0 | 1699.1 | [8 empty] | 2162.4 | 849.3 | 2898.4 | 2640.5 | 2534.3 | 1039.9 | 997.6 | 2184.8 | 3017.1 | 2347.7 | 2939.7 | 2887.8 | 2742.5 | 2628.7 | 2862.4 | 2325.3 | [48 empty] | 1305.8 | 1033 | 816.4 | 297.1 | 86.3 | 237.2 | 488.5 | 595.2 | [16 empty] | 0 | 0 | 0 | 2352 | 114.8 | 0 | 229.7 | 144.7 | [128 empty] | 1678 | 1681.3 | 1541.8 | 1714.5 | 1408.3 | 1561.8 | 1593.1 | 1723.5 | 1266.1 | 603.5 | 281.8 | 0 | 1374 | 1404.1 | 1054.2 | 298.9 | [16 empty] | 35.0725 | [5 empty] | 43.0013 | [5 empty] | 4.3015 | [5 empty] | 11.37 | [5 empty] | 7.9324 | [11 empty] | 7.7632 | [27 empty] | 4842.4412 | 192.2361 | 7.9324 | 0 | 0 | 0 | 0 | 0 | 7.7632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133291.936 | 6903.488 | 0 | 126388.448 | 11.9833 | 7.9324 |  | 7.7632 |  |  |  | 35.0725 | 43.0013 | 4.3015 | 11.37 | 137533.2 | [6 empty] | 0 |  | 0
2025-05-18 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.28958 | 0.79028 | [8 empty] | 834.3 | 992.5 | 1073.5 | 1182.6 | 1077.9 | 638.3 | 370.3 | 985.7 | [8 empty] | 952.4 | 1187.6 | 1188.9 | 1115.7 | 851.5 | 694.1 | 846.2 | 820.6 | 630.3 | 1049.7 | 594.1 | 566.3 | 1058.7 | 1136.2 | 742.7 | 701.2 | [16 empty] | 968.2 | 858.8 | 769 | 600.6 | 879 | 864.9 | 754.5 | 997.1 | [28 empty] | 897.4 | 1081.1 | 1134.6 | 799.6 | 936 | 1139 | 848.3 | 985.4 | 915.5 | 61.6 | 946.2 | 1083.2 | 788.2 | 1046.8 | 961.4 | 947.1 | [28 empty] | 944 | 843.4 | 684.6 | 875.8 | 59.8 | 1029.5 | 16.3 | 1131.6 | [8 empty] | 446.9 | 144.9 | 769.6 | 629.5 | 582.9 | 233.1 | 483.9 | 812.1 | 1064.4 | 629.6 | 1044.9 | 989.6 | 1032.1 | 925.5 | 1089 | 701.9 | [72 empty] | 0 | 0 | 0 | 854.1 | 640.5 | 0.8 | 1100.6 | 669.9 | [128 empty] | 4432.6 | 4444 | 4287.8 | 4463.6 | 4167 | 4295.8 | 4345.4 | 4487.9 | 4016.1 | 3249.1 | 1008 | 0 | 4119,1 | 4149.1 | 3742.5 | 1146.7 | [16 empty] | 35.3332 | [5 empty] | 42.7665 | [5 empty] | 4.8627 | [5 empty] | 10.67 | [5 empty] | 7.7847 | [11 empty] | 7.6161 | [27 empty] | 4956.5112 | 199.7585 | 7.7847 | 0 | 0 | 0 | 0 | 0 | 7.6161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114069.952 | 7522.4 | 0 | 106547.552 | 12.0167 | 7.7847 |  | 7.6161 |  |  |  | 35.3332 | 42.7665 | 4.8627 | 10.67 | 115221.2 | [6 empty] | 0 |  | 0
2025-05-19 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 0.25833 | 0.79444 | 455.7 | 1751.9 | 1316.5 | 2049.9 | 2413.2 | 2222.1 | 1294.3 | 1987.7 | [8 empty] | 2225.7 | 2189.7 | 1982.2 | 2161.3 | 2200.8 | 2180.9 | 1939.6 | 0 | [16 empty] | 0 | 679.2 | 2079.7 | 2099.5 | 1823.8 | 2247.6 | 1979.2 | 1723.4 | 2123.8 | 2046.1 | 2359.3 | 2294.9 | 1603.4 | 2273.1 | 2233.6 | 2098.5 | [8 empty] | 1934.2 | 1922.6 | 1500.7 | 1797.9 | 1716 | 1530.4 | 1723.6 | 1551.8 | [12 empty] | 2301 | 2073.7 | 2140.9 | 2269.4 | 1834 | 2168 | 2110.3 | 2208.5 | [16 empty] | 2142.6 | 2215.7 | 2218.3 | 2260.3 | 2171.5 | 2079.9 | 2155 | 2111.8 |  |  |  |  | 2115.7 | 2126.7 | 0 | 0 | 2138.4 | 1980.6 | 1701.5 | 1991.8 | 1985.4 | 2167.8 | 2148.1 | 1964.8 | 1983.9 | 1499.2 | 1746.5 | 1998.3 | [80 empty] | 1959.7 | 1460.2 | 1046.5 | 307.8 | 341.8 | 892.7 | 1770.5 | 2121.6 | 2201.5 | 1501.9 | 1202.6 | 0 | 489.7 | 1523.6 | 0 | 1505.3 | 0 | 2047.2 | 2331.5 | 2048.8 | 2265 | 1406.2 | 2222.4 | 2282 | [8 empty] | 0 | 0 | 0 | 0 | 228.4 | 997 | 2148.8 | 1658.8 | [152 empty] | 35.857 | [5 empty] | 41.1 | [5 empty] | 5.0604 | [5 empty] | 10.78 | [5 empty] | 7.7618 | [11 empty] | 7.6259 | [27 empty] | 5127.0115 | 209.5924 | 7.7618 | 0 | 0 | 0 | 0 | 0 | 7.6259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170500.288 | 9833.888 | 0 | 160666.4 | 12.8667 | 7.7618 |  | 7.6259 |  |  |  | 35.857 | 41.1 | 5.0604 | 10.78 | 171684.9 | [5 empty] | 170500.288 | 170500.288 | 9833.888 | 160666.4
2025-05-20 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 6:16 | 19:06 | 453.2 | 1768.8 | 1321.9 | 2066.4 | 2459.3 | 2256.2 | 1296.8 | 2011.5 | 3380 | 3247.6 | 3523.9 | 3882.9 | 3571.9 | 2086.2 | 1230 | 3280.9 | 2275.2 | 2237.2 | 2015.4 | 2227 | 2269.2 | 2243.2 | 2015.9 | 0 | 1910.3 | 3749.1 | 3770.1 | 3690.5 | 2769.4 | 2423.5 | 2777.3 | 2596.9 | 1864 | 3057.4 | 1725.7 | 1635.5 | 3035.2 | 2717.2 | 0 | 2048.5 | 0 | 262.1 | 850.9 | 863.1 | 744.4 | 911.2 | 808.6 | 691.9 | 2173.7 | 2058.8 | 2433.2 | 2361 | 1631 | 2337.7 | 2277.8 | 2137.4 | 3484.1 | 3146.5 | 3301.5 | 3461.1 | 3010 | 3485.7 | 2602 | 3379.2 | 1996.2 | 1968.1 | 1520.2 | 1830.1 | 1702.5 | 1554.7 | 1748.9 | 1583.8 | [12 empty] | 2358.4 | 2116.7 | 2187.3 | 2321 | 1860.2 | 2213.2 | 2151.8 | 2257.88 | 3809.9 | 3533.6 | 3736.7 | 2972.3 | 3171.2 | 3629.1 | 3142.7 | 3767.7 | 2960.2 | 2461.8 | 3331.3 | 3599.1 | 3339.1 | 3465.6 | 3501.6 | 3064.4 | 2174.6 | 2250.9 | 2257.3 | 2297.4 | 2211.5 | 2110.8 | 2164.3 | 2118.2 |  |  |  |  | 2150.4 | 2163.8 | 0 | 0 | 2143.8 | 2011.2 | 2694.1 | 2015.2 | 2017 | 2098.9 | 2183.6 | 2001.3 | 1507.1 | 1507 | 1763.4 | 2019.7 | 3689.3 | 3244.7 | 2678 | 3404.8 | 3374.8 | 3491.1 | 667.7 | 3814.3 | [8 empty] | 1884.9 | 3320.4 | 3453.1 | 2112.4 | 2017.9 | 2246.5 | 2067.9 | 3086.8 | 3395.4 | 2037.2 | 3251.8 | 3180.1 | 3257.9 | 2975.5 | 3469 | 2238.1 | [48 empty] | 1980.4 | 1472.8 | 1001.9 | 304.2 | 337.2 | 891.1 | 1791.4 | 2153.1 | 2203.1 | 1484 | 1176.7 | 0 | 483.1 | 1527.1 | 0 | 1496.3 | 172.7 | 1841.5 | 2086.9 | 1833.5 | 2039.1 | 1246.6 | 2005.4 | 2064.6 | 2801.1 | 2124.1 | 2041.1 | 3202.3 | 2497.6 | 3015.9 | 3516 | 2114.3 | 1231.7 | 1131.9 | 776.3 | 171.7 | 223.1 | 985.5 | 2163.7 | 1661.9 | [120 empty] | 3500.8 | 3471 | 3369.4 | 3758.1 | 2062.2 | 3418.1 | 3494.5 | 3813.7 | 2791.6 | 2424.9 | 2033.6 | 2166.4 | 1106.6 | 1138.7 | 1422.2 | 683.4 | [16 empty] | 35.6211 | [5 empty] | 45.9465 | [5 empty] | 4.2815 | [5 empty] | 10.52 | [5 empty] | 7.6546 | [11 empty] | 7.482 | [27 empty] | 5566.0076 | 220.3371 | 7.6546 | 0 | 0 | 0 | 0 | 0 | 7.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 438996.096 | 10744.672 | 0 | 428251.424 | 12.8333 | 7.6546 |  | 7.482 |  |  |  | 35.6211 | 45.9465 | 4.2815 | 10.52 | 442288.58 | [5 empty] | 168630.98 | 168630.98 | 10744.672 | 157886.308
2025-05-21 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 6:14 | 18:15 | 473.8 | 1850.4 | 1382.5 | 2141.1 | 2571.5 | 2356.4 | 1360.3 | 2100.9 | 3425.3 | 3254.9 | 3032.7 | 3232.1 | 3335.8 | 2653.1 | 2415.1 | 3196 | 2357.1 | 2315.6 | 2078.3 | 2306.6 | 2350.6 | 2322.9 | 2069.7 | 0 | 1990.5 | 3633.6 | 3654.7 | 3470.8 | 2736.7 | 2347.1 | 2826.2 | 2545.1 | 2797.9 | 3027.8 | 2505.3 | 2876.4 | 3046.7 | 3226.3 | 2456.2 | 2866 | 0 | 0 | 0 | 0 | 85 | 1041.7 | 921.6 | 780.1 | 2280 | 2132.5 | 2548.2 | 2476.2 | 1797.6 | 2457.6 | 2392.4 | 2244 | 1027 | 3096.2 | 3076.4 | 3207.9 | 2824.3 | 3281.3 | 2607.8 | 3678.1 | 2101.8 | 2072.7 | 1599.3 | 1913.4 | 1800.7 | 1627.4 | 1848.5 | 1672.6 | [12 empty] | 2441.3 | 0 | 1481.5 | 0 | 1939.7 | 2297.5 | 2232.6 | 2342.3 | 3593.4 | 3323.5 | 3525.3 | 3087 | 3349.9 | 3415.9 | 2962.2 | 3534.8 | 2795.5 | 3322.4 | 3229.3 | 3350.9 | 3086.7 | 3335.2 | 3399.5 | 3151.6 | 2271.2 | 2346.1 | 2355.3 | 2388.2 | 2301 | 2210.5 | 2261.5 | 2211.8 |  |  |  |  | 2244.3 | 2260 | 0 | 0 | 2205.7 | 2093.8 | 1765.8 | 2109.5 | 2107.4 | 2181.4 | 2279.4 | 2088.4 | 2111.3 | 1584.9 | 1845.6 | 2093.1 | 3642.5 | 3268.1 | 2891.1 | 3452.4 | 3175.7 | 3062.1 | 2460.8 | 3581.8 | [8 empty] | 2449.9 | 3365.7 | 3329.7 | 2094.2 | 2221.9 | 2622.7 | 2068.8 | 3376.8 | 3225.3 | 1946.7 | 3096.9 | 3019.6 | 3103.5 | 2832.4 | 3297.2 | 2139.9 | [48 empty] | 2048.6 | 1518.1 | 990.4 | 315.9 | 350.4 | 919 | 1846.9 | 2220.1 | 2279.1 | 1544.1 | 1230.5 | 0 | 490.9 | 1536.1 | 0 | 1487 | 2114.6 | 2056.8 | 2299.9 | 2018.2 | 2232.1 | 1367.6 | 2227.2 | 2297.1 | 3234.1 | 3085.5 | 2967.1 | 3247.5 | 2932.4 | 3377.1 | 3388.2 | 2366.2 | 1616.9 | 1498.8 | 502.5 | 217.8 | 212.8 | 947.1 | 2071.6 | 1588 | [120 empty] | 3328 | 3301.9 | 3201.3 | 3566.7 | 1981.4 | 3250.9 | 3328 | 3623.7 | 3020.6 | 2758.3 | 2172.6 | 3063.6 | 2690.5 | 2514.5 | 3552.5 | 2879.4 | [16 empty] | 36.2954 | [5 empty] | 41.6785 | [5 empty] | 4.6258 | [5 empty] | 9.89 | [5 empty] | 7.126 | [11 empty] | 6.9463 | [27 empty] | 6019.5079 | 229.9816 | 7.126 | 0 | 0 | 0 | 0 | 0 | 6.9463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453500.384 | 9644.544 | 0 | 443855.84 | 12.0167 | 7.126 |  | 6.9463 |  |  |  | 36.2954 | 41.6785 | 4.6258 | 9.89 | 458300.3 | [5 empty] | 169928.2 | 169928.2 | 9644.544 | 160283.656
2025-05-22 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 6:13 | 19:14 | 499.6 | 1921.2 | 1440.8 | 2208.9 | 2639.8 | 2426.1 | 1418 | 2135.8 | 1678 | 1575.1 | 1663.3 | 1782.9 | 1685.5 | 1562 | 1452.6 | 1748.4 | 2426 | 2382.6 | 2143.4 | 2373.2 | 2419.4 | 2391.9 | 2120 | 1801.7 | 1647.5 | 2165.3 | 2195.1 | 2082.4 | 1890.3 | 1626.2 | 1691.5 | 1617.5 | 1612.4 | 1633.4 | 1692.1 | 1746.8 | 1665.2 | 1661.8 | 1695.1 | 1698.8 | 0 | 0 | 0 | 0 | 1323.8 | 2474.1 | 2192.3 | 1858.8 | 2348.2 | 2165.6 | 2605.4 | 2536.8 | 1762.2 | 2545.5 | 2471.9 | 2302.1 | 1581.2 | 1546 | 1561 | 1692.4 | 1416.8 | 1656.8 | 1475.1 | 1834.3 | 2146.1 | 2134.5 | 1661.7 | 1980.1 | 1872 | 1695.8 | 1911.3 | 1712 | [12 empty] | 2516.6 | 0 | 1594 | 0 | 2014.7 | 2376.4 | 2308.6 | 2419 | 1807.8 | 1666.2 | 1766.5 | 1685.8 | 1850.7 | 1706.7 | 1492.8 | 1775.3 | 1362.2 | 1639.6 | 1605.9 | 1667.4 | 1544.3 | 1664.8 | 1704.6 | 1566.1 | 2335.2 | 2413.6 | 2420.2 | 2466.8 | 2406.5 | 2305.6 | 2357.2 | 2302.9 |  |  |  |  | 2295.1 | 2309.8 | 2036.3 | 1697.4 | 2258.5 | 2143 | 1814.7 | 2158.4 | 2164.9 | 2236.2 | 2340.2 | 2147.1 | 2161.8 | 1631.8 | 1893.9 | 2114.1 | 1823.7 | 1273.6 | 1552.5 | 1740.2 | 1598.7 | 1727.1 | 1344.4 | 1815.6 | [8 empty] | 2339.4 | 1703.3 | 1662.9 | 1565.8 | 1073.3 | 1259.3 | 987.1 | 1563.5 | 1628 | 1046 | 1610.3 | 1519.3 | 1433.5 | 1374.7 | 1631.9 | 1486.7 | [48 empty] | 2138.2 | 1592.2 | 1044.4 | 335.5 | 372.4 | 969.8 | 1930.8 | 2315.9 | 2404.2 | 1637 | 1309.6 | 0 | 552.7 | 1696.2 | 0 | 1643.7 | 2344.4 | 2305.1 | 2548 | 2244.3 | 2482.9 | 1535.5 | 2491.1 | 2563.8 | 1611.6 | 1700 | 1509.3 | 1617.7 | 1763.1 | 1679.7 | 1712.2 | 1341.9 | 1833.6 | 1701.7 | 640.1 | 254.1 | 250.4 | 1088.1 | 2349.6 | 1811.8 | [120 empty] | 1667.9 | 1649.2 | 1536.6 | 1797.2 | 1044.2 | 1636.1 | 1667.3 | 1815.7 | 1490.3 | 1501.2 | 1448.4 | 1522 | 1342.1 | 1381.5 | 1607.5 | 1704.3 | [16 empty] | 36.8447 | [5 empty] | 42.9947 | [5 empty] | 4.6618 | [5 empty] | 11.22 | [5 empty] | 7.5342 | [11 empty] | 7.3569 | [27 empty] | 6362.1 | 241.1 | 7.5342 | 0 | 0 | 0 | 0 | 0 | 7.3569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342592.064 | 11118.368 | 0 | 331473.696 | 13.0167 | 7.5342 |  | 7.3569 |  |  |  | 36.8447 | 42.9947 | 4.6618 | 11.22 | 343723.5 | [5 empty] | 188476.2 | 188476.2 | 11118.368 | 177357.832
2025-05-23 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 6:13 | 19:07 | 440.3 | 1811.7 | 1349.8 | 2079.1 | 2491.8 | 2284.9 | 1324.4 | 1987.5 | 2263 | 2163.3 | 2246.5 | 2408.6 | 2236.4 | 2109 | 1945 | 2293.6 | 2216.2 | 2227.1 | 2033.2 | 2256 | 2313.3 | 2288.1 | 2024 | 2210 | 1987.8 | 2352.3 | 2364.5 | 2231 | 2154.1 | 1905.8 | 1881.6 | 1785.6 | 2069.8 | 2051.3 | 1928.8 | 2244.3 | 2136.2 | 2257.3 | 2159.1 | 2172.9 | 0 | 0 | 0 | 0 | 1236.9 | 2324.5 | 2053.5 | 1777.1 | 2212.9 | 2008.5 | 2455.8 | 2391.2 | 1635.4 | 2358.6 | 2312.1 | 2138.9 | 2027.3 | 1966.5 | 2017.9 | 2115.1 | 1853.8 | 2189.3 | 1888.6 | 2343.1 | 1963 | 1950.1 | 1520.4 | 1790.2 | 1716.8 | 1558 | 1753.9 | 1563.9 | [12 empty] | 2400.5 | 0 | 1520.8 | 0 | 1878 | 2221.7 | 2150.4 | 2260.4 | 2301.8 | 2135.4 | 2253.6 | 2152.6 | 2361.7 | 2179.9 | 1938.6 | 2284.4 | 1777.2 | 2115.9 | 2073.5 | 2143.7 | 2000 | 2153.7 | 2199 | 2020.4 | 2176.1 | 2249.9 | 2258.7 | 2301 | 2218.6 | 2122.8 | 2176.2 | 2127.2 |  |  |  |  | 2156.4 | 2170.1 | 2200.6 | 1818.4 | 2131.1 | 2019.4 | 1706.4 | 2002.4 | 2047.3 | 2116 | 2216.5 | 2029.4 | 2053.9 | 1542.7 | 1792.8 | 2006.8 | 2356.5 | 2167.1 | 2050.2 | 2245.7 | 1971.5 | 2269.8 | 1750.5 | 2342.2 | [8 empty] | 1691.9 | 2197 | 2142.7 | 2001.2 | 1408.9 | 1775.4 | 1513.3 | 2209.6 | 2109.7 | 1283.9 | 2077.3 | 2020.5 | 0 | 1933.7 | 1779.9 | 1827.4 | [48 empty] | 2040.1 | 1411.5 | 985.6 | 314.2 | 349.8 | 917.5 | 1839.8 | 2214.1 | 2332.9 | 1578.9 | 1259.3 | 0 | 525.6 | 1642.4 | 0 | 1591 | 2261.7 | 2231.2 | 2485.7 | 2169.2 | 2411.9 | 1482.1 | 2401.9 | 2493.1 | 2063 | 2144.7 | 1939.4 | 2086.6 | 2252.3 | 2178 | 2190.2 | 1733.1 | 1793.9 | 1663.7 | 1137.8 | 245.4 | 240.4 | 675.1 | 1204.3 | 1421.3 | [120 empty] | 1690 | 1670 | 1520 | 1810 | 1630 | 1510 | 1670 | 1820 | 1500 | 1510 | 1480 | 1310 | 1200 | 1270 | 1820 | 1700 | [16 empty] | 37.7718 | [5 empty] | 45.8351 | [5 empty] | 5.2482 | [5 empty] | 12.87 | [5 empty] | 7.253 | [11 empty] | 7.0824 | [27 empty] | 6731.4684 | 253.2912 | 7.253 | 0 | 0 | 0 | 0 | 0 | 7.0824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369368.448 | 12191.168 | 0 | 357177.28 | 12.9 | 7.253 |  | 7.0824 |  |  |  | 37.7718 | 45.8351 | 5.2482 | 12.87 | 366117 | [5 empty] | 177453 | 177453 | 12191.168 | 165261.832
2025-05-24 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 6:12 | 19:06 | 401.1 | 1789 | 1335.7 | 2046.3 | 2462.2 | 2258 | 1302.5 | 1968.2 | 3180.6 | 3013.8 | 3174 | 3409.8 | 3218.3 | 2085.9 | 2835.4 | 3279.5 | 2276.1 | 2156.2 | 1993.2 | 2208.2 | 2253.8 | 2227.8 | 1971.1 | 2159.9 | 2870.4 | 3384.7 | 3386.5 | 3216.2 | 3102.3 | 2713 | 2671 | 2565.9 | 2919.4 | 2907.5 | 2772.2 | 3233.8 | 3070.6 | 3242.5 | 3096.4 | 3115.3 | 0 | 0 | 0 | 0 | 1246.7 | 2307.5 | 2035.7 | 1783.1 | 2187.2 | 1984.6 | 2426.6 | 2362.5 | 1628.2 | 2347.6 | 2309.4 | 2131.2 | 2916.6 | 2887.2 | 2890.7 | 3031.3 | 2640.2 | 3117.5 | 2918.1 | 3366.4 | 1960.4 | 1980.2 | 1546.9 | 1798.1 | 1733.8 | 1569.6 | 1770.7 | 1572.9 | [12 empty] | 2340.9 | 0 | 1486.3 | 0 | 8175 | 2218.3 | 2050.2 | 2259.9 | 3298 | 3057.1 | 3229.5 | 3097.8 | 3390.3 | 3139.5 | 2783.4 | 3253.2 | 2561.6 | 3033.4 | 2942.1 | 3046.7 | 2851.4 | 3021.5 | 3121 | 2896.8 | 2172.8 | 2246.1 | 2260.9 | 2298.6 | 2207.5 | 2117.3 | 2165 | 2117 |  |  |  |  | 2149.7 | 2166.5 | 2194.9 | 1816.9 | 2117.3 | 2001.3 | 1619.6 | 1927.1 | 2014.6 | 2078.8 | 2176.1 | 1999.5 | 2017.3 | 1514.6 | 1759.3 | 1967.9 | 3332.5 | 2993.9 | 2934.9 | 3202.9 | 2563.7 | 2804.9 | 2192.1 | 2772.2 | [8 empty] | 2373.6 | 3139.5 | 3074.4 | 2866.5 | 1989 | 2517.2 | 2173.6 | 3152.3 | 3018.2 | 1851.3 | 3005.5 | 2893.4 | 3273.1 | 3245.9 | 2986.3 | 3054.7 | [48 empty] | 1987.1 | 1472.8 | 959 | 303.9 | 339.8 | 893.1 | 1793 | 2155.8 | 2247.5 | 1522.5 | 1212.3 | 0 | 438.6 | 1575 | 0 | 1526.2 | 2186.5 | 2154.5 | 2429.8 | 2105.3 | 2328.3 | 1394.4 | 2300.1 | 2400.4 | 2923 | 3035.9 | 2763.3 | 3016.4 | 3217.2 | 3112.7 | 3317.3 | 2552.4 | 1703.4 | 1581.2 | 1078.4 | 230.9 | 226.7 | 642.2 | 1147.2 | 1355.5 | [120 empty] | 2998 | 2972.3 | 2711.7 | 3226 | 2932.5 | 2679.1 | 2993.6 | 3260.8 | 2738.4 | 2749.2 | 2851.8 | 2438.2 | 2501.8 | 2326 | 3342.2 | 3091.2 | [16 empty] | 36.9701 | [5 empty] | 51.8269 | [5 empty] | 3.3899 | [5 empty] | 8 | [5 empty] | 7.0135 | [11 empty] | 6.8333 | [27 empty] | 7185.3688 | 261.7659 | 7.0135 | 0 | 0 | 0 | 0 | 0 | 6.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453900.384 | 8474.72 | 0 | 445425.664 | 12.9 | 7.0135 |  | 6.8333 |  |  |  | 36.9701 | 51.8269 | 3.3899 | 8 | 462939.7 | [5 empty] | 180820.8 | 180820.8 | 8474.72 | 172346.08
2025-05-25 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 6:45 | 19:02 | 120.4 | 651.5 | 479.8 | 763.5 | 928 | 848.6 | 487.2 | 755.7 | [8 empty] | 854.5 | 805.2 | 740.1 | 830.3 | 860.1 | 860.9 | 745.9 | 804.3 | [16 empty] | 0 | 0 | 0 | 0 | 455.5 | 860.6 | 757.9 | 653.1 | 824.5 | 745.2 | 910 | 878.2 | 597.6 | 888.2 | 873.1 | 806.4 | [8 empty] | 711.6 | 750.9 | 567.4 | 656.3 | 636.9 | 578.7 | 646.5 | 560.8 | [12 empty] | 879.7 | 0 | 544.1 | 0 | 728.1 | 850.1 | 778.3 | 864.8 | [16 empty] | 788.9 | 817.6 | 829.9 | 571 | 815.2 | 777.5 | 802.3 | 781.6 |  |  |  |  | 802.5 | 797.1 | 809.2 | 663.9 | 793.9 | 758.3 | 625.1 | 689.8 | 750.1 | 768.2 | 817.1 | 742.2 | 744.3 | 556.4 | 653.5 | 713.5 | [80 empty] | 709.5 | 527.1 | 314.1 | 79 | 91.9 | 302.2 | 652.7 | 773.3 | 613.1 | 510 | 357.9 | 0 | 86 | 467.3 | 0 | 536.6 | 793.8 | 798 | 903 | 773.7 | 861.9 | 482.6 | 851.3 | 885.9 | [8 empty] | 605.5 | 565 | 377.5 | 51 | 50.1 | 194.5 | 392.7 | 483.2 | [152 empty] | 38.2699 | [5 empty] | 56.6182 | [5 empty] | 2.4667 | [5 empty] | 9.1 | [5 empty] | 3.3954 | [11 empty] | 3.3064 | [27 empty] | 7250.3204 | 271.845 | 3.3954 | 0 | 0 | 0 | 0 | 0 | 3.3064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64951.584 | 10079.072 | 0 | 54872.512 | 12.2833 | 3.3954 |  | 3.3064 |  |  |  | 38.2699 | 56.6182 | 2.4667 | 9.1 | 63500 | [5 empty] | 63500 | 63500 | 10079.072 | 53420.928
2025-05-26 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 6:17 | 19:05 | 269 | 1080.8 | 825.3 | 1242 | 1488.8 | 1370 | 845.2 | 1218.8 | 1970.9 | 1845.7 | 1929.5 | 2127.3 | 2040.9 | 1913.7 | 1709.7 | 1943.8 | 1400.3 | 1307.7 | 1228 | 1350.8 | 1403.2 | 1433.6 | 1266.8 | 1344.8 | 1781.3 | 2142.2 | 2211.8 | 2140.6 | 1900.2 | 1622.6 | 1682.7 | 1587.5 | 1755.5 | 1743.5 | 1579.8 | 1921.6 | 1798.7 | 1969.4 | 1926.3 | 1864.4 | 0 | 0 | 0 | 0 | 797.5 | 1400.3 | 1245.1 | 1076.1 | 1333.9 | 1203.2 | 1449.6 | 1420.6 | 1120.3 | 1492.8 | 1458.8 | 1360.3 | 1872.6 | 1803.7 | 1793.8 | 1849.4 | 1723.1 | 1887.9 | 1796.9 | 2009.3 | 1173 | 1198.6 | 958.2 | 1089.2 | 1071.1 | 948.3 | 1082.2 | 947.5 | [12 empty] | 1429.7 | 0 | 913.4 | 0 | 1240.8 | 1391.2 | 1261.4 | 1383.9 | 1976.9 | 1826.5 | 1900.5 | 1840.1 | 2010.7 | 1860.8 | 1673.6 | 1974.3 | 1541.4 | 1845.2 | 1806.3 | 1892 | 1768 | 1855.1 | 1933.6 | 1805.8 | 1247.2 | 1294.3 | 1305.6 | 1278.5 | 1241 | 1198.4 | 1226.8 | 1207.1 |  |  |  |  | 1263.4 | 1258 | 1273 | 1052.6 | 1232 | 1174 | 986 | 1093 | 1154.7 | 1164.8 | 1262.8 | 1146.8 | 1157.1 | 886.2 | 1023.9 | 1112.6 | 1996.7 | 1743 | 1733.3 | 1926.6 | 1763.6 | 1946.1 | 1492.1 | 1970.2 | [8 empty] | 620.2 | 1862.6 | 1811.7 | 1700.5 | 1021.1 | 0 | 1267 | 2002.1 | 1840.6 | 1189 | 1805.4 | 1788.6 | 1986.7 | 1914.9 | 1801.4 | 1817.8 | [48 empty] | 1159.6 | 884.5 | 568.1 | 173 | 190.9 | 534.2 | 1043.8 | 1190.9 | 915.8 | 919.4 | 631 | 0 | 190 | 748.7 | 0 | 878.1 | 1262.5 | 1283.5 | 1455.3 | 1267.3 | 1379.1 | 819.6 | 1360.2 | 1398 | 1820.9 | 1876.4 | 1735.1 | 1976.8 | 2045.4 | 2055.7 | 2037.7 | 1554.5 | 998.9 | 117.5 | 636.5 | 123 | 119.2 | 375 | 680 | 812.9 | [120 empty] | 0 | 1765.3 | 1636.4 | 1926.8 | 1756 | 1815.2 | 1763.3 | 1933.8 | 1718.7 | 1717.9 | 1665.3 | 1363.1 | 1357.8 | 1156.8 | 1850 | 1677 | [16 empty] | 37.3711 | [5 empty] | 53.3461 | [5 empty] | 3.1038 | [5 empty] | 8.29 | [5 empty] | 5.8482 | [11 empty] | 5.7493 | [27 empty] | 7523.5786 | 281.0215 | 5.8482 | 0 | 0 | 0 | 0 | 0 | 5.7493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273258.208 | 9176.576 | 0 | 264081.632 | 12.8 | 5.8482 |  | 5.7493 |  |  |  | 37.3711 | 53.3461 | 3.1038 | 8.29 | 271442.6 | [5 empty] | 102878.4 | 102878.4 | 9176.576 | 93701.824
2025-05-27 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 6:17 | 18:50 | 324.9 | 1288.9 | 964.8 | 1539.5 | 1845.6 | 1693.6 | 1000 | 1446.5 | 1151.3 | 1081.7 | 1111.7 | 1238.3 | 1182.4 | 1104.4 | 976.6 | 1142.7 | 1748.2 | 1551.8 | 1532.1 | 1677 | 1757.4 | 1790.9 | 1576.7 | 1685.3 | 1008.8 | 1234.2 | 1265.8 | 1216.1 | 1080.9 | 908.9 | 955.4 | 890.2 | 997.5 | 984.1 | 865 | 1091.6 | 1021.3 | 1117.7 | 1087.5 | 1050.5 | 0 | 0 | 0 | 0 | 921.9 | 1698.7 | 1493.1 | 1274.6 | 1613.7 | 1439.6 | 1770.1 | 1735.6 | 1390.7 | 1760.8 | 1716.9 | 1592.5 | 1045.9 | 1010.7 | 1005.9 | 1032 | 957.9 | 1061.2 | 1003.8 | 1129.4 | 1417.8 | 1414 | 1134.5 | 1297.3 | 1294.7 | 1116.9 | 1311.7 | 1135.6 | [12 empty] | 1810.7 | 0 | 1125.9 | 0 | 1555.5 | 1759 | 1574.7 | 1743.9 | 1111.5 | 1023.1 | 1068.6 | 1034.3 | 1130 | 1048.5 | 933.5 | 1109.6 | 866.1 | 1031.8 | 1007.3 | 1082.3 | 1004.1 | 1043.4 | 1095.6 | 1031 | 1515.9 | 1582 | 1597.3 | 1587.1 | 1520.6 | 1470 | 1503.3 | 1482.8 |  |  |  |  | 1585.3 | 1572.2 | 1605.4 | 1285 | 1544.8 | 1464.3 | 1233 | 1385.2 | 1440.8 | 1420.4 | 1588.8 | 1424.7 | 1448.2 | 1091.4 | 1265.4 | 1391.8 | 1120.8 | 968.9 | 944.1 | 1080.6 | 996.2 | 1091.9 | 875.8 | 1109.8 | [8 empty] | 333.3 | 1040.4 | 1010.3 | 944.5 | 650.9 | 0 | 713.8 | 1132.4 | 1042.5 | 664.1 | 1118.9 | 999.6 | 1142.6 | 1108.9 | 1003 | 1012.4 | [48 empty] | 1585.3 | 1572.2 | 1605.4 | 1285 | 1544.8 | 1464.3 | 1233 | 1385.2 | 1440.8 | 1420.4 | 1588.8 | 1224.7 | 1448.2 | 1091.4 | 1265.4 | 1391.8 | 1120.8 | 968.9 | 944.1 | 1080.6 | 996.2 | 1091.9 | 875.8 | 1109.8 | 1002.1 | 1029.8 | 949.1 | 1131.4 | 1155.8 | 1168.2 | 1136.6 | 858.6 | 1276.2 | 150.9 | 514.7 | 0 | 0 | 459.9 | 854.1 | 1032 | [120 empty] | 0 | 977.4 | 902.1 | 1069.1 | 972.2 | 999.7 | 975.1 | 1073.1 | 959.4 | 942.5 | 911.2 | 683 | 705 | 786.9 | 926.6 | 892.9 | [16 empty] | 38.7898 | [5 empty] | 44.8871 | [5 empty] | 2.1203 | [5 empty] | 5.76 | [5 empty] | 6.1602 | [11 empty] | 6.1228 | [27 empty] | 7743.565 | 290.7339 | 6.1602 | 0 | 0 | 0 | 0 | 0 | 6.1228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219986.336 | 9712.384 | 0 | 210273.952 | 12.55 | 6.1602 |  | 6.1228 |  |  |  | 38.7898 | 44.8871 | 2.1203 | 5.76 | 226497.5 | [5 empty] | 131551.9 | 131551.9 | 9712.384 | 121839.516
2025-05-28 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 6:15 | 18:58 | 286.8 | 1137.6 | 840.7 | 1383.8 | 1665 | 1522.4 | 927.3 | 1273.5 | [8 empty] | 1592.7 | 1381.5 | 1382.6 | 1515.1 | 1568.4 | 1596.8 | 1443.7 | 1549.6 | [16 empty] | 0 | 0 | 0 | 0 | 793.8 | 1464.1 | 1289.3 | 1103.5 | 1399 | 1249.6 | 1541.5 | 1500.7 | 1360 | 1518.5 | 1458.7 | 1370 | [8 empty] | 1223.7 | 1211.5 | 973.5 | 1099.5 | 1109.5 | 962.7 | 1123.8 | 976.2 | [12 empty] | 1637.8 | 0 | 1027.4 | 0 | 1353.7 | 1527.1 | 1398.9 | 1522.1 | [16 empty] | 1299.5 | 1354.2 | 1368.8 | 632.3 | 1307.8 | 1252.6 | 1286.2 | 1270.8 |  |  |  |  | 1359.7 | 1342.2 | 1373.4 | 1094.7 | 1318.9 | 1243.3 | 1057.6 | 1176.5 | 1223.7 | 1184.4 | 1350.7 | 1210.8 | 1222.9 | 921 | 1072.8 | 1179.4 | [80 empty] | 1183.2 | 909.5 | 570.8 | 172.9 | 187.1 | 543.7 | 639.3 | 1068.4 | 345.9 | 315.9 | 393.5 | 0 | 75.4 | 8.7 | 0 | 880.3 | 1365.3 | 1419.2 | 1703.8 | 1486.2 | 1280.6 | 595.7 | 1510.5 | 1553.3 | [8 empty] | 1056.9 | 122.7 | 436.2 | 0 | 0 | 373.7 | 701.8 | 852.7 | [152 empty] | 35.5238 | [5 empty] | 41.6705 | [5 empty] | 4.0971 | [5 empty] | 16.3 | [5 empty] | 5.6167 | [11 empty] | 5.5703 | [27 empty] | 7849.1215 | 300.51 | 5.6167 | 0 | 0 | 0 | 0 | 0 | 5.5703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105556.544 | 9776.064 | 0 | 95780.48 | 12.7167 | 5.6167 |  | 5.5703 |  |  |  | 35.5238 | 41.6705 | 4.0971 | 16.3 | 105121 | [5 empty] | 105121 | 105121 | 9776.064 | 95344.936
2025-05-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 6:16 | 19:09 | 337.2 | 1545.2 | 1131.8 | 1775.1 | 2139.3 | 1964.7 | 1150.6 | 1701.1 | [8 empty] | 1952.3 | 1775.9 | 1739.4 | 1904.8 | 1947.5 | 1945.2 | 1718 | 1877.4 | [16 empty] | 0 | 0 | 0 | 0 | 1101.1 | 2008.3 | 1771.6 | 1550.1 | 1921.1 | 1751.9 | 2121.2 | 2094.7 | 1899.8 | 2085.6 | 2006.2 | 1874 | [8 empty] | 1710.1 | 1715.8 | 1363.4 | 1539.7 | 1528.8 | 1399.5 | 1570 | 1359.7 | [12 empty] | 2097.8 | 667.2 | 1640.8 | 0 | 1656.3 | 1974.3 | 1832.6 | 1979.8 | [16 empty] | 1973.5 | 2034.1 | 2043.7 | 2048.5 | 2017.7 | 1922.4 | 1943.9 | 1935 |  |  |  |  | 1951.9 | 2008.9 | 2035.6 | 1687.1 | 1978.7 | 1893.2 | 1594.8 | 1770.7 | 1896.5 | 1781.5 | 2051.4 | 1870.3 | 1892.2 | 1425.8 | 1670.3 | 1809.9 | [80 empty] | 1658.8 | 1300.7 | 853.4 | 278.6 | 308.8 | 824.9 | 805 | 1539.2 | 519.6 | 478.5 | 589.2 | 0 | 120.7 | 0 | 0 | 1342.3 | 1930.7 | 1922.8 | 2159.7 | 1994.8 | 1743.5 | 863.3 | 2075.1 | 2132.4 | [8 empty] | 1560.3 | 206.5 | 664 | 0 | 0 | 42 | 918.8 | 688 | [152 empty] | 32.9638 | [5 empty] | 38.8772 | [5 empty] | 4.4773 | [5 empty] | 11.05 | [5 empty] | 6.6739 | [11 empty] | 6.526 | [27 empty] | 7996.1052 | 310.1411 | 6.6739 | 0 | 0 | 0 | 0 | 0 | 6.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146983.648 | 9631.136 | 0 | 137352.512 | 12.8833 | 6.6739 |  | 6.526 |  |  |  | 32.9638 | 38.8772 | 4.4773 | 11.05 | 147586.1 | [5 empty] | 147586.1 | 147586.1 | 9631.136 | 137954.964
2025-05-30 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 6:12 | 19:11 | 173.1 | 802.6 | 589.4 | 916.6 | 1103.9 | 1022.4 | 591 | 874.8 | [8 empty] | 1009.6 | 919.7 | 901.8 | 977 | 1004.3 | 1006.2 | 890.4 | 994.6 | [16 empty] | 0 | 0 | 0 | 0 | 566 | 1031.4 | 908.6 | 791.5 | 977.8 | 891.2 | 1081.4 | 1075.2 | 974.3 | 1060.9 | 1028.1 | 966 | [28 empty] | 1052 | 612.7 | 968.7 | 0 | 838.3 | 991.6 | 924.2 | 995.7 | [16 empty] | 993.3 | 1028.8 | 1025.8 | 1049.2 | 1008.5 | 974.9 | 973.5 | 963.6 |  |  |  |  | 952 | 985.5 | 1003.4 | 831.5 | 963.5 | 927.8 | 783.2 | 872.6 | 925.1 | 876.2 | 1004.9 | 904.3 | 927.8 | 701.1 | 813.7 | 893.1 | [80 empty] | 835.7 | 648.3 | 428.2 | 139.1 | 154.3 | 411.5 | 399.8 | 762.7 | 261.5 | 238.9 | 295.7 | 0 | 60 | 0 | 0 | 669.3 | 970.3 | 962.7 | 1087.1 | 991.5 | 854.2 | 429.4 | 1034.4 | 1062.9 | [8 empty] | 775.7 | 103.2 | 323.2 | 0 | 0 | 22.3 | 456.8 | 618.6 | [152 empty] | 35.4178 | [5 empty] | 41.3451 | [5 empty] | 4.334 | [5 empty] | 8.88 | [5 empty] | 6.983 | [11 empty] | 6.7895 | [27 empty] | 8070.6933 | 318.5209 | 6.983 | 0 | 0 | 0 | 0 | 0 | 6.7895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74588.192 | 8379.776 | 0 | 66208.416 | 12.9833 | 6.983 |  | 6.7895 |  |  |  | 35.4178 | 41.3451 | 4.334 | 8.88 | 68893.6 | [5 empty] | 68893.6 | 68893.6 | 8379.776 | 60513.824
2025-05-31 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 137763 | 6:15 | 19:18 | 432.9 | 1794.7 | 1311.7 | 2024.4 | 2448.8 | 2258.4 | 1382.1 | 1971.9 | [8 empty] | 2152 | 1970.3 | 1919.9 | 2095.3 | 2136.3 | 2121.5 | 1858.7 | 2118.6 | [16 empty] | 0 | 326.9 | 1028.3 | 997.4 | 901.4 | 2147.3 | 1868.7 | 1638.4 | 2109 | 1881.2 | 2323 | 2298.7 | 2083.9 | 2289.2 | 2199 | 2059.5 | [8 empty] | 1744.4 | 1752.6 | 1397.2 | 1576.8 | 1549.5 | 1419.1 | 1587.8 | 1379.4 | [12 empty] | 2333.1 | 1363.6 | 2145.2 | 1309.3 | 1802.5 | 2181.8 | 2019.1 | 2185.8 | [16 empty] | 1860.1 | 2002.8 | 1999.2 | 2043.3 | 1970.4 | 1876.4 | 1892.9 | 1865.6 |  |  |  |  | 1731.7 | 1790.3 | 1813 | 1502.7 | 1759.3 | 1672.2 | 1402.1 | 1558 | 2048.3 | 1923.1 | 2217.5 | 2024.4 | 2045.5 | 1536.2 | 1799.3 | 1953.6 | [80 empty] | 1168.7 | 908.3 | 593.3 | 186.2 | 205.2 | 562.5 | 547.5 | 1028.6 | 374.3 | 342.5 | 424.9 | 0 | 79.1 | 0 | 0 | 979.4 | 2080.3 | 2096.8 | 2361.8 | 2155.3 | 1876 | 929.4 | 2240.1 | 2301 | [8 empty] | 1068 | 27.5 | 280.5 | 0 | 0 | 26.7 | 527.8 | 712.6 | [152 empty] | 34.8947 | [5 empty] | 40.3208 | [5 empty] | 5.8005 | [5 empty] | 11.92 | [5 empty] | 7.01 | [11 empty] | 6.8592 | [27 empty] | 8229.2023 | 329.6455 | 7.01 | 0 | 0 | 0 | 0 | 0 | 6.8592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158508.992 | 11124.64 | 0 | 147384.352 | 13.05 | 7.01 |  | 6.8592 |  |  |  | 34.8947 | 40.3208 | 5.8005 | 11.92 | 154268.8 | [5 empty] | 154268.8 | 154268.8 | 11124.64 | 143144.16
2025-06-01 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 264915.58 | 6:15 | 19:17 | 1444.5 | 4939.3 | 4581.5 | 6859.9 | 6767 | 6373.9 | 4320.8 | 6587.8 | 1886.2 | 1798.9 | 1921.6 | 2040.7 | 1932.4 | 0 | 0 | 1918.9 | 7211.3 | 6648.5 | 6460.8 | 7069.1 | 7189.6 | 7002.5 | 6262.8 | 7123.4 | 1704 | 2033.7 | 2001.7 | 1903.4 | 430 | 823 | 564.1 | 576 | 1057.9 | 1765 | 958.1 | 1216.4 | 1759.9 | 1870.3 | 1273.1 | 1210.7 | 0 | 2298.7 | 6984.8 | 6758.6 | 6176.1 | 7422.1 | 6458.5 | 5683.7 | 7055.2 | 6313.6 | 7689.8 | 7610.8 | 6936.3 | 7620.7 | 7324.8 | 6889.8 | 704.3 | 831.9 | 849.3 | 875.7 | 796.6 | 885.3 | 809.2 | 809 | 6001.6 | 6264.9 | 5005.7 | 5649.6 | 5573.5 | 5161.4 | 5691.8 | 4948 | [12 empty] | 7657.4 | 4517.5 | 7066.9 | 7379.1 | 5929.9 | 7182.5 | 6633.8 | 7170.1 | 575 | 468 | 467 | 591 | 441 | 903 | 663 | 800 | 522 | 831 | 790 | 852 | 800 | 828 | 852 | 791 | 6979 | 7261.5 | 7225.5 | 7350.8 | 7119.7 | 6796.7 | 6847.3 | 6809 |  |  |  |  | 6747 | 6959.6 | 7141.6 | 5860.1 | 6718.3 | 6589.9 | 5546.1 | 6146.2 | 6568.8 | 6169.5 | 7072.7 | 6456.5 | 6528.2 | 4911.7 | 5784.7 | 6253.1 | 2037 | 1832 | 1722 | 1938.7 | 734 | 691 | 656 | 551 | [8 empty] | 475 | 611 | 416 | 668 | 576 | 0 | 489 | 522 | 1342 | 535.8 | 1817.7 | 1674.1 | 717 | 911 | 697 | 524 | [48 empty] | 5832.2 | 4596.7 | 3060.3 | 1076.3 | 1179.6 | 2964.4 | 2892.4 | 0 | 1915.1 | 1750.8 | 2137.8 | 0 | 520.5 | 0 | 0 | 4738.3 | 6783.4 | 6780.2 | 7603.8 | 6959.4 | 6119.4 | 3087.5 | 7252.6 | 7425.8 | 856 | 467 | 533 | 353 | 1882.8 | 1885.3 | 1905 | 1472.3 | 4159 | 255.2 | 1558.4 | 0 | 0 | 160 | 2129.6 | 3086.9 | [120 empty] | 754.9 | 1741.9 | 1575.6 | 1870.1 | 1665.1 | 1162.5 | 1634.3 | 1867.4 | 1538.1 | 1551 | 1485.8 | 672.9 | 1069 | 968.5 | 444.3 | 234.9 | [16 empty] | 33.2604 | [5 empty] | 39.9561 | [5 empty] | 4.543 | [5 empty] | 10.15 | [5 empty] | 6.8687 | [11 empty] | 6.681 | [27 empty] | 8838.0092 | 338.7284 | 6.8687 | 0 | 0 | 0 | 0 | 0 | 6.681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608806.912 | 9082.848 | 0 | 599724.064 | 13.0333 | 6.8687 |  | 6.681 |  |  |  | 33.2604 | 39.9561 | 4.543 | 10.15 | 649878.3 | [5 empty] | 608806.912 | 608806.912 | 9082.848 | 599724.064
2025-06-02 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 264915.58 | 6:14 | 19:19 | 1068.9 | 3893.3 | 5037.7 | 7694.4 | 6162.7 | 5774.9 | 4241.1 | 6950.6 | 1549 | 1455.7 | 1567.7 | 1670.7 | 1609 | 0 | 0 | 1594.4 | 6120.6 | 5470.8 | 6741 | 7445.7 | 7544 | 7342.4 | 6555.8 | 7460.3 | 1386.6 | 1615 | 1644.1 | 1576.5 | 1543.5 | 1326.3 | 1275.1 | 1249.9 | 860.8 | 1430 | 785.8 | 996.9 | 1437.2 | 1521.9 | 1033.8 | 983.9 | 0 | 2408.9 | 7212.6 | 7080.7 | 6480 | 7795.2 | 6772.7 | 5958.5 | 7539.5 | 7109.7 | 8096.2 | 8001.1 | 7289.2 | 7993.5 | 7740 | 7321.5 | 1247.3 | 1469.2 | 1475.6 | 1527.3 | 1441.5 | 546.7 | 1498.4 | 1521 | 6298.3 | 6541.1 | 5279.7 | 5946.6 | 5906.6 | 5464.3 | 5995.1 | 5194 | [12 empty] | 7996.5 | 4720.6 | 7384.5 | 7745.7 | 6228.7 | 7494.4 | 6931.1 | 7485.9 | 1613.9 | 1499.3 | 1588.6 | 1523.7 | 1674.9 | 1168.2 | 1204.8 | 1611.7 | 939.7 | 1495.5 | 1394.6 | 1492.1 | 1389.9 | 1451.7 | 1484.3 | 1413.1 | 7397.3 | 7687 | 7663.1 | 7810.8 | 7556.4 | 7078.3 | 7266.5 | 7191.5 |  |  |  |  | 7136.8 | 7353.9 | 7418.2 | 6197.6 | 7216.5 | 6963.5 | 5861.6 | 6500.4 | 6955.4 | 6532.9 | 7481.7 | 6826.4 | 6922.4 | 5204.8 | 6121.9 | 6515.1 | 1649 | 1487.7 | 1388.8 | 1564.2 | 643.6 | 849 | 255.8 | 910.6 | [8 empty] | 464.2 | 1507 | 1471.5 | 1412.3 | 977.4 | 0 | 929.2 | 1574.3 | 1114.6 | 455.9 | 1560.7 | 1423.1 | 1289.1 | 1565 | 1470.2 | 1486.6 | [48 empty] | 6185.7 | 4880.8 | 3253.8 | 1148.3 | 1258.1 | 3154.1 | 3071.6 | 5185.2 | 2035.1 | 1858.1 | 2271.4 | 0 | 558.4 | 0 | 0 | 5016.6 | 7241.1 | 7221 | 8068.1 | 7374.3 | 6472.5 | 3273.7 | 6799.1 | 7496.2 | 1428.9 | 1463.3 | 1342.8 | 1461.1 | 1592 | 1595.8 | 1603.5 | 1239.4 | 4426.7 | 271.4 | 1671.3 | 0 | 0 | 253.4 | 3469.8 | 4631.9 | [120 empty] | 1540.2 | 1534 | 1383 | 1629.3 | 1496.4 | 1047.1 | 1450.1 | 1694.6 | 1358.8 | 1354.6 | 1303.4 | 598.7 | 964.8 | 871.4 | 400.9 | 213.5 | [16 empty] | 34.0127 | [5 empty] | 40.5223 | [5 empty] | 4.7648 | [5 empty] | 10.5 | [5 empty] | 7.268 | [11 empty] | 7.1118 | [27 empty] | 9528.2158 | 349.2466 | 7.268 | 0 | 0 | 0 | 0 | 0 | 7.1118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690206.592 | 10518.176 | 0 | 679688.416 | 13.0833 | 7.268 |  | 7.1118 |  |  |  | 34.0127 | 40.5223 | 4.7648 | 10.5 | 700128.5 | [5 empty] | 690206.592 | 690206.592 | 10518.176 | 679688.416
2025-06-03 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 264915.58 | 6:14 | 19:13 | 1543.4 | 5816.7 | 4931.7 | 7339.9 | 7752.3 | 7390 | 4694 | 6787 | 1856 | 1746.4 | 1871.5 | 1988 | 1886.7 | 0 | 0 | 1877.1 | 7327.6 | 6156.7 | 6935.7 | 7471.8 | 7354.6 | 7101.9 | 6458.8 | 7112.3 | 1670.2 | 9081.2 | 1964.6 | 1877.1 | 1818.1 | 1559.9 | 1512.5 | 1483.9 | 1041 | 1711.6 | 923.5 | 1195.8 | 1705.1 | 1802.3 | 1229 | 1181.6 | 0 | 2360.3 | 7101.7 | 6977.4 | 6354.6 | 7433 | 6610.8 | 5816.4 | 7326.9 | 7319.6 | 7641.6 | 7517.4 | 7006.6 | 7477.6 | 7396.4 | 7133.6 | 1477 | 1730.3 | 1739.8 | 1778.6 | 1636.12 | 560 | 1702.9 | 1727.9 | 6123.7 | 6230.8 | 5153.4 | 5777.2 | 5756.1 | 5308.1 | 5843.5 | 5068 | [12 empty] | 7534.1 | 4618.8 | 7102 | 7263 | 6079.4 | 7194.5 | 6756.7 | 7182.6 | 1907.2 | 1771.3 | 1869.6 | 1795.7 | 1980 | 1384.1 | 1434.1 | 1913.4 | 1128.3 | 1773.3 | 1663.1 | 1777.6 | 1672 | 1735.7 | 1777.8 | 1691.9 | 7096.5 | 7291.8 | 7270.9 | 7389 | 7212.2 | 6817.2 | 6965.2 | 6673 |  |  |  |  | 6888.3 | 7046.4 | 7102.8 | 6028.3 | 6968.2 | 6755.5 | 5709.5 | 6313.6 | 6749.8 | 6353.8 | 7153.6 | 6661.5 | 6737.3 | 5000.4 | 5970.7 | 6259.5 | 1971.8 | 1790.3 | 1676.6 | 1884.7 | 1436.5 | 1876.2 | 573 | 2008.4 | [8 empty] | 556.1 | 1770 | 1727.5 | 1661 | 1160.9 | 0 | 1115.8 | 1870.5 | 1229.5 | 547.6 | 1825.6 | 1669.8 | 1525.9 | 1842.7 | 1733.7 | 1760.3 | [48 empty] | 5922 | 4656 | 3155.5 | 1107.6 | 1214.1 | 2860 | 2985.4 | 5437.6 | 1975.2 | 1800.4 | 2200 | 0 | 538.2 | 0 | 0 | 4867 | 6946.3 | 6936.6 | 7557.7 | 7071.2 | 6271.8 | 3176.6 | 7293 | 7143.9 | 1717.8 | 1743.5 | 1608.2 | 1761 | 1893.7 | 1876.7 | 1877 | 1472.9 | 4290.3 | 258.1 | 1616 | 0 | 0 | 242.6 | 3356.9 | 4493.8 | [120 empty] | 1790.4 | 1778.6 | 1608.2 | 1881 | 1118.1 | 1225.9 | 1687.5 | 1960.7 | 1580.8 | 1532.6 | 1519.7 | 704.7 | 1118.3 | 1017.4 | 472.7 | 254.3 | [16 empty] | 33.8871 | [5 empty] | 39.2627 | [5 empty] | 5.3956 | [5 empty] | 11.14 | [5 empty] | 7.0177 | [11 empty] | 6.8708 | [27 empty] | 10232.6579 | 359.6341 | 7.0177 | 0 | 0 | 0 | 0 | 0 | 6.8708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 704442.08 | 10387.584 | 0 | 694054.496 | 12.9833 | 7.0177 |  | 6.8708 |  |  |  | 33.8871 | 39.2627 | 5.3956 | 11.14 | 721455.92 | [5 empty] | 704442.08 | 704442.08 | 10387.584 | 694054.496
2025-06-04 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 264915.58 | 6:13 | 19:13 | 1469.9 | 4565.8 | 4077.1 | 5398 | 5662 | 5436.3 | 3987.2 | 5070.1 | 3762.1 | 3632.3 | 3774.7 | 3893.9 | 3846.8 | 0 | 0 | 3869.7 | 5403.6 | 4758.5 | 5177.5 | 5795.9 | 5347.9 | 4318 | 4946.7 | 5191.8 | 3311.9 | 3933.9 | 3922 | 3835.2 | 4369 | 4000.3 | 3890.5 | 3888.9 | 2798.4 | 3564.3 | 2636.6 | 2974.9 | 3342.3 | 3640.9 | 3009.6 | 2960.5 | 0 | 2455.3 | 5421.7 | 5338 | 5043.4 | 5618.3 | 5015.4 | 4593.9 | 5410.6 | 5409.7 | 5599.5 | 5533 | 5179.2 | 5420 | 5353.2 | 5258.1 | 3297.3 | 3580.2 | 3563.1 | 3250.3 | 2956.2 | 1886.8 | 3570.8 | 3463 | 4753.8 | 4791.2 | 4255.4 | 4579.1 | 4516.7 | 4272.8 | 4576.4 | 4159.8 | [12 empty] | 5519 | 3667.5 | 5259.4 | 5430.5 | 4721.1 | 5330.4 | 5079.3 | 5331.3 | 3804.9 | 3652.9 | 3769.4 | 3689.8 | 3972.2 | 3280.2 | 3347.5 | 3908.3 | 2950.9 | 3730.5 | 3616.2 | 3738.1 | 3621.4 | 3697 | 3744.3 | 3632.2 | 4990 | 5119 | 5087.6 | 3697.7 | 5353.7 | 5118.5 | 5184.8 | 5017.6 |  |  |  |  | 5148 | 5244.1 | 5219.4 | 4694.5 | 5182 | 5051.4 | 4517.2 | 4842 | 5055.3 | 4853.5 | 5289.7 | 4997.9 | 5039.3 | 4147.8 | 4632.8 | 4811.9 | 3968.3 | 3758.4 | 3595.9 | 3874 | 3042.6 | 3601.4 | 1968.4 | 3696 | [8 empty] | 1904.5 | 3738.6 | 3693.4 | 3612.8 | 2969.7 | 0 | 2973.7 | 3852.5 | 3064.5 | 1865.5 | 3806.8 | 3619 | 3445.7 | 3832.2 | 3702 | 3724.6 | [48 empty] | 4608.4 | 3976 | 3182 | 1151.1 | 1262.5 | 2943.5 | 3055.7 | 4400.3 | 2049.1 | 1870 | 2281.4 | 0 | 562.6 | 0 | 0 | 4119.1 | 5183.6 | 5174.9 | 5556.1 | 5255.4 | 4806.2 | 2175.7 | 5393.6 | 5296.2 | 3691.6 | 3726.5 | 3580.9 | 3792 | 3909.3 | 3874.5 | 3876.6 | 3389.4 | 3821.6 | 272.5 | 1676.8 | 0 | 0 | 255.5 | 3295.7 | 3913.4 | [120 empty] | 3768.6 | 3752.7 | 3545.1 | 3873.4 | 2844.7 | 3089 | 3646.5 | 3966.6 | 3526.3 | 3471.2 | 3455.7 | 2360.3 | 2971.5 | 2828 | 1470.4 | 925.7 | [16 empty] | 33.8551 | [5 empty] | 39.8859 | [5 empty] | 4.2498 | [5 empty] | 11.78 | [5 empty] | 7.4034 | [11 empty] | 7.2337 | [27 empty] | 10984.3482 | 370.1984 | 7.4034 | 0 | 0 | 0 | 0 | 0 | 7.2337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 751690.304 | 10564.288 | 0 | 741126.016 | 13 | 7.4034 |  | 7.2337 |  |  |  | 33.8551 | 39.8859 | 4.2498 | 11.78 | 754563.1 | [5 empty] | 751690.304 | 751690.304 | 10564.288 | 741126.016
2025-06-05 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 264915.58 | 6:13 | 19:13 | 1481.5 | 4140.5 | 3855.5 | 4666.9 | 4843.4 | 4682.3 | 3775.2 | 4448.4 | 4622.6 | 4490.5 | 4638.7 | 4766.5 | 4632.3 | 2801.2 | 1953.7 | 4670.3 | 4671.9 | 4269.4 | 4524.4 | 4736.7 | 4659.3 | 4636.3 | 4410.1 | 4566.6 | 4423.9 | 4769 | 4756.3 | 4659.5 | 4589.2 | 4277.3 | 4138.1 | 4186 | 3618.6 | 4470.4 | 3420.9 | 3808.4 | 4447.3 | 4556.6 | 3857.7 | 3811.6 | 61.5 | 2507.1 | 4656.2 | 4593.6 | 4413.5 | 4747.5 | 4405.4 | 4141.3 | 4328.7 | 3573.7 | 4400.9 | 4740.4 | 4497.4 | 4617.1 | 4670.3 | 4542 | 4207.8 | 4523.7 | 4487 | 4120.1 | 3752.7 | 2427 | 4456.8 | 4330.5 | 4269 | 4365.7 | 3952.4 | 4143.1 | 4139.9 | 3978.9 | 4188.4 | 4050.9 | [12 empty] | 4714.8 | 3756.1 | 4514.6 | 4657.7 | 4227.7 | 4600.5 | 4436 | 4596.7 | 4660.4 | 4509.9 | 4626.7 | 4541.4 | 4777.3 | 4063.1 | 4125.3 | 4686.6 | 3709.6 | 4526.9 | 4414.5 | 4532.5 | 4420.4 | 4494.7 | 4540 | 4425.6 | 1340.6 | 1237.9 | 1279 | 1031.3 | 4669.9 | 4505.7 | 4554.1 | 4453.1 |  |  |  |  | 4485.2 | 4576.6 | 4539.8 | 4240 | 4550.3 | 4422.7 | 4095.1 | 4301.5 | 4408.7 | 4303.6 | 4598.8 | 4437.4 | 4449.8 | 3885.5 | 4126 | 4280.5 | 4751.6 | 4517.7 | 4355.2 | 4663.6 | 2981.4 | 3651.3 | 1958.2 | 3690.9 | [8 empty] | 2410.4 | 4508.3 | 4466.8 | 4304.8 | 3697.8 | 0 | 3744.5 | 4623.7 | 3830.8 | 2367.1 | 4580.7 | 4395.7 | 4212.8 | 4602.4 | 4475.2 | 4494 | [48 empty] | 4120.7 | 3764.1 | 3197.3 | 1154 | 1266.3 | 2951 | 3068.1 | 4030.3 | 1660.3 | 1878.2 | 2293.6 | 0 | 565.6 | 0 | 0 | 3861.7 | 4501.1 | 4502.9 | 4742.3 | 4547.2 | 4271.9 | 3180.3 | 4634.9 | 4568.1 | 4480.4 | 4514.7 | 4376.3 | 4584.3 | 4687.7 | 4644.8 | 4649.5 | 4165.1 | 3684.8 | 273.1 | 1683.2 | 0 | 0 | 257 | 3290.2 | 3721 | [120 empty] | 4542.3 | 4526.8 | 4321.5 | 4649.9 | 3610.9 | 3864.8 | 4425.3 | 4743.5 | 4322.1 | 4258.6 | 4250 | 2895.1 | 3745.9 | 3589.5 | 1871.4 | 1182.8 | [16 empty] | 34.3154 | [5 empty] | 41.1154 | [5 empty] | 4.3579 | [5 empty] | 11.13 | [5 empty] | 7.4604 | [11 empty] | 7.2688 | [27 empty] | 11749.2204 | 380.2574 | 7.4604 | 0 | 0 | 0 | 0 | 0 | 7.2688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764872.224 | 10058.944 | 0 | 754813.28 | 13 | 7.4604 |  | 7.2688 |  |  |  | 34.3154 | 41.1154 | 4.3579 | 11.13 | 768153.4 | [5 empty] | 764872.224 | 764872.224 | 10058.944 | 754813.28
2025-06-06 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 264915.58 | 6:12 | 19:14 | 1511.2 | 4176.1 | 3884.9 | 4710.8 | 4897.2 | 4734.8 | 3816.8 | 4495.4 | 4676.4 | 4532 | 4692.5 | 4827.6 | 4693.3 | 3896.3 | 2606.8 | 4732.4 | 4714.6 | 4699 | 4558.1 | 4771.5 | 4693.3 | 4657 | 4438.9 | 4600.8 | 4455.8 | 4814 | 4801.7 | 4703.8 | 4631.6 | 4306 | 4156.6 | 4213.6 | 3650.6 | 4523.8 | 3464.5 | 3846.3 | 4499.9 | 4617.6 | 3900.1 | 3857.1 | 2554.3 | 2564.2 | 4716.7 | 4651.2 | 4434.6 | 4825.8 | 4468.3 | 4197.9 | 4343.9 | 3569.7 | 4427.2 | 4806.7 | 4554.9 | 4682.5 | 4728.8 | 4590.3 | 4241.4 | 4570.7 | 4520 | 4145.2 | 3773.7 | 2469.7 | 4043.6 | 4367.3 | 4441.2 | 4562.8 | 4011.9 | 4255.9 | 4176.2 | 4011.4 | 4244.2 | 4172.9 | [12 empty] | 4782.3 | 3793.5 | 4546.2 | 4716.9 | 4271.6 | 4654.8 | 4486.3 | 4660.5 | 4718.1 | 4554.2 | 4681 | 4596.6 | 4823.1 | 4097 | 4168.1 | 4751.6 | 3737.1 | 4564.9 | 4445.3 | 4573.2 | 4455.3 | 4531.1 | 4584.5 | 4462.3 | 834.4 | 849.9 | 839.1 | 861.1 | 4694.9 | 4533.3 | 4585.1 | 4506.6 |  |  |  |  | 4522.6 | 4654 | 4602.5 | 4299.1 | 4622.9 | 4450.8 | 4123.2 | 4336 | 4424.6 | 4316.8 | 4464.2 | 4499 | 4518.8 | 3928.3 | 4138.8 | 4292.9 | 4805 | 4559.3 | 4338.9 | 4712.7 | 2657.5 | 3352 | 1742.7 | 3499.6 | [8 empty] | 2457.5 | 4566.9 | 4521.4 | 4354.1 | 3742.6 | 3151 | 3787.9 | 4683.3 | 3871.9 | 2417.9 | 4640.8 | 4441.3 | 4261.9 | 4663.7 | 4533.5 | 4552.3 | [48 empty] | 4161.6 | 3794.7 | 3180.4 | 1175.5 | 1292.9 | 3006.4 | 3117.6 | 4067.7 | 1695.6 | 1927.3 | 2342.2 | 0 | 578.1 | 0 | 0 | 3904.2 | 4554.5 | 4554.7 | 4803.7 | 4600.5 | 4310.6 | 3224.9 | 4693.3 | 4566.7 | 4516.9 | 4552.5 | 4407.9 | 4637.4 | 4741.1 | 4701.8 | 4678.2 | 4209.7 | 3713.6 | 283.8 | 1719.6 | 0 | 0 | 262.6 | 3335.8 | 3757.1 | [120 empty] | 4492.4 | 4484.1 | 4275 | 4592.4 | 3584.9 | 3826.1 | 4370 | 4688.1 | 4273.8 | 4212.7 | 4173 | 2832 | 3707.6 | 3559.1 | 1884.6 | 1198.3 | [16 empty] | 35.1499 | [5 empty] | 43.2075 | [5 empty] | 4.9429 | [5 empty] | 10.91 | [5 empty] | 7.6926 | [11 empty] | 7.5049 | [27 empty] | 12524.3077 | 390.7479 | 7.6926 | 0 | 0 | 0 | 0 | 0 | 7.5049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 775087.232 | 10490.496 | 0 | 764596.736 | 13.0333 | 7.6926 |  | 7.5049 |  |  |  | 35.1499 | 43.2075 | 4.9429 | 10.91 | 779681.1 | [5 empty] | 775087.232 | 775087.232 | 10490.496 | 764596.736
2025-06-07 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 264915.58 | 6:11 | 19:13 | 1511.7 | 3868.2 | 3577.9 | 4415.7 | 4619.8 | 4440.5 | 3505.9 | 4143.2 | 4383.7 | 4225.6 | 4398.6 | 4545.4 | 4399.8 | 3567.5 | 2543.6 | 4436.7 | 4418.8 | 4398.5 | 4255.2 | 4483.9 | 4399 | 3967.1 | 4134.2 | 4299.4 | 4151.1 | 4532.3 | 4516.7 | 4408.9 | 4270.9 | 3916.7 | 3832.8 | 3905.1 | 1390 | 1770.6 | 1300 | 1470 | 1760 | 1820 | 1500 | 1480 | 60 | 60 | 60 | 60 | 1720 | 1910 | 1740 | 1640 | 1680 | 1350 | 1720 | 1900 | 1780 | 1840 | 1870 | 1800 | 1660 | 1810 | 1800 | 1610 | 1430 | 950 | 1740 | 1710 | 1780 | 1780 | 1550 | 1700 | 1520 | 1540 | 1680 | 1600 | [12 empty] | 1880 | 1440 | 1770 | 1850 | 1660 | 1800 | 1750 | 1830 | 4396.6 | 4251 | 4388.1 | 4297.4 | 4535.4 | 3790 | 3862.3 | 4428.2 | 3423.1 | 4260.2 | 4140.4 | 4272.8 | 4148.9 | 4228.6 | 4284.4 | 4156.5 | 4349.1 | 4492.9 | 4426.6 | 4539.4 | 4400.5 | 4239.9 | 4294.6 | 4215.4 |  |  |  |  | 3700 | 4000 | 3900 | 3400 | 3900 | 3600 | 3000 | 3400 | 3500 | 3400 | 4000 | 3600 | 3700 | 2700 | 3000 | 3300 | 4540.5 | 4274.5 | 4134.7 | 4435.1 | 3850.5 | 4322.6 | 2533.2 | 4591.7 | [8 empty] | 2459.3 | 4264.9 | 4217.4 | 4027 | 3433.4 | 3426.7 | 3475.4 | 4392.9 | 3559.1 | 2419.6 | 4335.6 | 4125 | 3951 | 4362.7 | 4229.5 | 4251.4 | [48 empty] | 3852.4 | 3483 | 2956.9 | 1181.1 | 1300 | 2828.2 | 2909.5 | 3757.1 | 1703.4 | 1934.3 | 2353.5 | 0 | 584 | 0 | 0 | 3593.1 | 4256.6 | 4257.3 | 4520.8 | 4299.9 | 4006 | 2976.8 | 4399.5 | 4268.2 | 4180.2 | 4258.3 | 4108.2 | 4342.3 | 4455.6 | 4413.6 | 4357.8 | 3906.2 | 3401.9 | 288 | 1729.8 | 0 | 0 | 266.3 | 3066.9 | 3449.3 | [120 empty] | 4297 | 4284.7 | 4064.2 | 4407 | 3324.2 | 3577 | 4163.1 | 4514.7 | 4050.5 | 3993.5 | 3915.5 | 2755.5 | 3455.9 | 3301.9 | 1908.7 | 1233.7 | [16 empty] | 35.4874 | [5 empty] | 42.9734 | [5 empty] | 4.7163 | [5 empty] | 9.1 | [5 empty] | 7.8322 | [11 empty] | 7.6045 | [27 empty] | 13297.7861 | 401.4727 | 7.8322 | 0 | 0 | 0 | 0 | 0 | 7.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773478.432 | 10724.832 | 0 | 762753.6 | 13.0333 | 7.8322 |  | 7.6045 |  |  |  | 35.4874 | 42.9734 | 4.7163 | 9.1 | 624424.1 | [5 empty] | 773478.432 | 773478.432 | 10724.832 | 762753.6
2025-06-08 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 264915.58 | 6:18 | 19:32 | 1537.2 | 4082.2 | 3795.7 | 4625.7 | 4809.6 | 4652.5 | 3724.6 | 4426.8 | 4606.1 | 4459.8 | 4620.8 | 4754.1 | 4618.6 | 3777.5 | 2555 | 4655.4 | 4599 | 4582.3 | 4452.8 | 4653.4 | 4578.5 | 4174.1 | 4340.3 | 4490.9 | 4357.1 | 4698.4 | 4687.2 | 4593.7 | 4468.3 | 4065.7 | 4038.8 | 4113.9 | 3485.6 | 4162.2 | 3327.7 | 3544.3 | 4130.6 | 4206.5 | 3696.8 | 3662.8 | 2167.2 | 2501.9 | 4101.2 | 4068.2 | 4111.7 | 4376.9 | 4144.9 | 3964.6 | 4040.4 | 4314.1 | 4100.9 | 4335.7 | 4170.9 | 4243.5 | 4273.1 | 4189 | 3985.4 | 4214.2 | 4203.8 | 3906.5 | 3589.2 | 2494.2 | 4139.6 | 4045.7 | 4176.6 | 4184.2 | 3811 | 4061.2 | 3751.2 | 3921.3 | 4079.7 | 3941.9 | [12 empty] | 4355.9 | 3626.5 | 4257.1 | 4320 | 4015.9 | 4271.2 | 4274.3 | 4329.4 | 4588.2 | 4482.5 | 4611.3 | 4527.8 | 4745.5 | 4025.4 | 4098 | 4622.6 | 3644.5 | 4490.5 | 4346.4 | 4499.8 | 4386.6 | 4462.5 | 4518.3 | 4395.1 | 4456.6 | 4611.7 | 4521.6 | 3958.8 | 4589.9 | 4469.4 | 4520.8 | 4445.8 |  |  |  |  | 5450.4 | 5556.9 | 5455.1 | 4841.3 | 5482.7 | 5353.3 | 4703.7 | 5128.2 | 5274 | 5074.8 | 5583.7 | 5243.8 | 5302.6 | 4349.4 | 4782.2 | 5021.7 | 4740.3 | 4500.5 | 4367.1 | 4652.1 | 4085.2 | 4550.3 | 2595.4 | 4787 | [8 empty] | 2504.8 | 4498 | 4452.3 | 4254.2 | 3652.1 | 3644.1 | 3695.8 | 4609.2 | 3752.6 | 2472.7 | 4574.7 | 4345.4 | 4187.3 | 4593.4 | 4468.6 | 4485.1 | [48 empty] | 4067.2 | 3704.4 | 3147.1 | 1141.3 | 1317.3 | 2999.3 | 3095.1 | 3980.8 | 1731.4 | 1964.2 | 2388.5 | 0 | 595.1 | 0 | 0 | 3817.8 | 4456 | 4454.7 | 4697.2 | 4498 | 4211.7 | 3158.6 | 4567.9 | 4463.4 | 4226.5 | 4453.1 | 4313.5 | 4541.6 | 4634.3 | 4599.1 | 4550.8 | 4115.6 | 3618.7 | 292.5 | 1759 | 0 | 0 | 270.8 | 3268.8 | 3668.9 | [120 empty] | 4513.8 | 4477.1 | 4263.8 | 4580 | 3511.6 | 3766.9 | 4356 | 4676.2 | 4198 | 4137.2 | 4115.5 | 2961.6 | 3643.9 | 3424.7 | 1726.4 | 1222.2 | [16 empty] | 35.78 | [5 empty] | 42.04 | [5 empty] | 4.86 | [5 empty] | 10.4 | [5 empty] | 7.97 | [11 empty] | 7.75 | [27 empty] | 14080.6217 | 407.4733 | 7.97 | 0 | 0 | 0 | 0 | 0 | 7.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 782835.584 | 6000.64 | 0 | 776834.944 | 13.2333 | 7.97 |  | 7.75 |  |  |  | 35.78 | 42.04 | 4.86 | 10.4 | 789309.4 | [5 empty] | 782835.584 | 782835.584 | 6000.64 | 776834.944
2025-06-09 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 264915.58 | 6:11 | 19:15 | 1504.2 | 4030.6 | 3769.4 | 4596.6 | 4798.6 | 4626.6 | 3739.9 | 4383.9 | 4571.8 | 4418.8 | 4587.9 | 4736.1 | 4594.3 | 3753.8 | 2502 | 4629.2 | 4604.5 | 4586.6 | 4440.7 | 4656.6 | 4580.8 | 4155.4 | 4324.8 | 4487.2 | 4342.7 | 4718.1 | 4703.8 | 4602 | 4463 | 4060 | 4036.3 | 4100.9 | 900 | 1270 | 810 | 920 | 1240 | 1320 | 1000 | 4100.9 | 490 | 520 | 1370 | 1330 | 1220 | 1410 | 1250 | 1130 | 1180 | 850 | 1230 | 1400 | 1290 | 1330 | 1370 | 1310 | 1150 | 1280 | 1290 | 1100 | 930 | 500 | 1250 | 1210 | 1280 | 1260 | 1050 | 1210 | 1030 | 1130 | 1220 | 1130 | [12 empty] | 1390 | 940 | 1350 | 1380 | 1160 | 1320 | 1330 | 1370 | 4559.8 | 4448.1 | 4581.6 | 4490.8 | 4729.4 | 3990.6 | 4060.9 | 4592.3 | 3621.9 | 4453.8 | 4334.7 | 4461.8 | 4339.9 | 4425.3 | 4490.5 | 4327.6 | 4507.7 | 4678.2 | 4612.5 | 4725.7 | 4565.2 | 4433.6 | 4539.5 | 4403.1 |  |  |  |  | 4495.2 | 4559.1 | 4500.8 | 4130.9 | 4514.1 | 4422.7 | 4045.6 | 4301.8 | 4393.6 | 4270.5 | 4584.8 | 4387.1 | 4409.8 | 3854 | 4111.2 | 4253.6 | 4724.2 | 4464 | 4325.5 | 4626.7 | 4051.5 | 4523.2 | 2544.6 | 4774.4 | [8 empty] | 2546.4 | 4462.1 | 4414.7 | 4210.8 | 3635.7 | 3630.4 | 3679.1 | 4589.1 | 3706.8 | 2424.6 | 4541.5 | 4306.3 | 4155.1 | 4561.9 | 4431.8 | 4449.9 | [48 empty] | 4063.5 | 3686.3 | 3114.7 | 1086.6 | 1288.5 | 2959.4 | 3060.2 | 3931.7 | 1699.4 | 1927.7 | 2342 | 0 | 584.5 | 0 | 0 | 3797.8 | 4458.3 | 4455.7 | 4718.2 | 4499.5 | 4205.1 | 3151.4 | 4565.5 | 4463.3 | 4207.4 | 4455.4 | 4307.5 | 4560.9 | 4651.6 | 4609.6 | 4556.3 | 4108 | 3604.9 | 285.9 | 1724.5 | 0 | 0 | 262.7 | 3251.9 | 3652.7 | [120 empty] | 4483.5 | 4480.1 | 4259.3 | 4597.7 | 3521.5 | 3772.5 | 4350.6 | 4700.7 | 4149.8 | 4170 | 4130.1 | 2932.6 | 3648.3 | 3432.7 | 1681.9 | 1201.8 | [16 empty] | 35.4855 | [5 empty] | 42.6 | [5 empty] | 5.5725 | [5 empty] | 10.04 | [5 empty] | 7.8259 | [11 empty] | 7.6177 | [27 empty] | 14857.6526 | 423.0155 | 7.8259 | 0 | 0 | 0 | 0 | 0 | 7.6177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 777030.912 | 15542.176 | 0 | 761488.736 | 13.0667 | 7.8259 |  | 7.6177 |  |  |  | 35.4855 | 42.6 | 5.5725 | 10.04 | 643809.3 | [5 empty] | 777030.912 | 777030.912 | 15542.176 | 761488.736
2025-06-10 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 264915.58 | 6:10 | 19:16 | 1538.8 | 4022.7 | 3749.8 | 4552.5 | 4747.9 | 4581.2 | 3684.5 | 4343.2 | 5313.2 | 5134.6 | 5329 | 5498.9 | 4546.7 | 3726.2 | 2462.6 | 4574.7 | 4563 | 4545 | 4403.4 | 4623.7 | 4538.5 | 4122.2 | 4287.6 | 4465.3 | 4307.8 | 4672.8 | 4657.2 | 4560.5 | 4423.2 | 4031.3 | 3975.6 | 4069.8 | 3697.1 | 4218 | 3499.4 | 3751 | 4180.4 | 4248 | 3896.9 | 3864 | 4164.6 | 4325.5 | 4195.4 | 4074.6 | 2321.5 | 2518.6 | 4263.1 | 4247.6 | 4136.8 | 3607.7 | 4187.2 | 4328.4 | 4215.8 | 4078.5 | 4282 | 4135.3 | 4057.5 | 4101.8 | 4195.6 | 4003.1 | 3799.1 | 2417.1 | 4201.9 | 4148.8 | 3941.3 | 4217.1 | 3987.3 | 4158 | 3949.4 | 4072.5 | 4177.5 | 4082.9 | [12 empty] | 4318.5 | 3810.9 | 4300.2 | 4309.8 | 4306.3 | 4265.3 | 4271.7 | 4298.7 | 4512.2 | 4405.9 | 4234.1 | 4443.1 | 4678.2 | 3958.6 | 4025.7 | 4544.3 | 3575.7 | 4411.8 | 4296.1 | 4425 | 4306.3 | 4387 | 4453.7 | 4227.6 | 4457.1 | 4623.1 | 4560.7 | 4669.8 | 4517 | 4387 | 4530.7 | 4357.5 |  |  |  |  | 4445.2 | 4505 | 4449.2 | 4088.2 | 4461.3 | 4372.8 | 4015.6 | 4264.9 | 4346.6 | 4169.2 | 4531.7 | 4337.9 | 4359.8 | 3819.6 | 4069.5 | 4208.9 | 4673.6 | 4418.6 | 4285.9 | 4602.8 | 4026.7 | 4487.7 | 2504.7 | 4728.5 | [8 empty] | 2421.8 | 4423.1 | 4374.3 | 4172.1 | 3613 | 3607.9 | 3655.2 | 4537.3 | 3682.9 | 2387.4 | 4499.5 | 4272.8 | 4120.9 | 4519.5 | 4351.3 | 4406.4 | [48 empty] | 4035.2 | 3665.4 | 3091.1 | 1069.4 | 1268.4 | 2930.6 | 3036 | 3905.2 | 1676.7 | 1900.4 | 2310.5 | 0 | 572.9 | 0 | 0 | 3772.2 | 4412.5 | 4408.9 | 4666.9 | 4451.9 | 4166.2 | 3127.5 | 4517.4 | 4419.3 | 4165.8 | 4415.3 | 4265 | 4520.2 | 4596.4 | 4557.8 | 4505 | 4068.2 | 3385.7 | 279 | 1702.6 | 0 | 0 | 257.4 | 3230.4 | 3631.7 | [120 empty] | 4442.4 | 4441.7 | 4221.3 | 4553.7 | 3484.3 | 3447.7 | 4311.1 | 4652.2 | 4141.7 | 4152.8 | 4107.4 | 2883.2 | 3611.8 | 3415.1 | 458.6 | 1186.6 | [16 empty] | 35.0207 | [5 empty] | 41.4598 | [5 empty] | 5.1005 | [5 empty] | 10.02 | [5 empty] | 7.7094 | [11 empty] | 7.5036 | [27 empty] | 15623.2187 | 434.0859 | 7.7094 | 0 | 0 | 0 | 0 | 0 | 7.5036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765566.112 | 11070.4 | 0 | 754495.712 | 13.1 | 7.7094 |  | 7.5036 |  |  |  | 35.0207 | 41.4598 | 5.1005 | 10.02 | 772587.3 | [5 empty] | 765566.112 | 765566.112 | 11070.4 | 754495.712
2025-06-11 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 264915.58 | 6:10 | 19:18 | 2726.7 | 4187.9 | 3761.7 | 4567.3 | 4764.8 | 4602 | 3696.4 | 4365.5 | 4485.8 | 4430.6 | 4582.1 | 4733.4 | 4525.4 | 3750.5 | 2501.2 | 4690.9 | 4580.4 | 4566 | 4417.2 | 4637.7 | 4550.3 | 4130.3 | 4297.4 | 4492 | 4314.7 | 4682.5 | 4668.3 | 4570.3 | 4433.7 | 4033.6 | 3924 | 4074.3 | 3720.6 | 8241.7 | 3523.5 | 3769.6 | 4201.9 | 4270.2 | 3913.8 | 3881 | 4146.3 | 4344.7 | 4216.1 | 4093.8 | 2359.8 | 2548.5 | 4284.7 | 4258.1 | 4154.5 | 3631.4 | 4207.2 | 4345.6 | 4234.6 | 4096.9 | 4299.8 | 4152.6 | 4075.4 | 4116.1 | 4217.9 | 4019.1 | 3811.7 | 2449 | 4225.1 | 4167.9 | 3927.2 | 4231.4 | 3998.1 | 4178.1 | 3960.2 | 4083.5 | 4199.2 | 4098.4 | [12 empty] | 4339.7 | 3782.2 | 4321.7 | 4321.3 | 4329.7 | 4289 | 4294.3 | 4317.9 | 4528.1 | 4418.8 | 4548.7 | 4457.1 | 4692.4 | 3968.1 | 4038.4 | 4560.7 | 3583.8 | 4427.1 | 4309.4 | 4441.2 | 4319.8 | 4400.9 | 4470.3 | 4240.6 | 4488.8 | 4655.8 | 4593.5 | 4700.5 | 4539.7 | 4412.9 | 4560.3 | 4385.9 |  |  |  |  | 4472.2 | 4533.3 | 4479.2 | 4113.8 | 4489.9 | 4396.5 | 4033.2 | 4290.3 | 4375 | 4194.2 | 4562.2 | 4365.4 | 4388.6 | 3841.9 | 4097 | 4236 | 4696.1 | 4436.5 | 4279.8 | 4640.7 | 4024.9 | 4490.8 | 2542.6 | 4753 | [8 empty] | 2456.7 | 4444.5 | 4391.1 | 4096.9 | 3624.4 | 3616.4 | 3666.8 | 4557.1 | 3692.2 | 2415 | 4520.8 | 4294.3 | 4136.4 | 4545.9 | 4415.2 | 4422.4 | [48 empty] | 4033.1 | 3675 | 3103 | 1084.5 | 1284.1 | 2946.3 | 3054.9 | 3920.8 | 1700.1 | 1924.2 | 2340.9 | 0 | 581.4 | 0 | 0 | 3484.1 | 4433.4 | 4428.9 | 4691.9 | 4471.3 | 4179.5 | 3143.1 | 4537.2 | 4440.4 | 4173.3 | 4430.2 | 4300 | 4531.8 | 4600 | 4550 | 4510 | 4059 | 3596.3 | 284.1 | 1726.8 | 0 | 0 | 262.3 | 3246.2 | 3682.7 | [120 empty] | 4463.2 | 4465.3 | 4240.7 | 4572.2 | 3447.8 | 3760.3 | 4330.8 | 4675.9 | 4159.4 | 4170.2 | 4125.3 | 2923.3 | 3612.5 | 3429.2 | 267.9 | 1298.5 | [16 empty] | 34.8011 | [5 empty] | 40.956 | [5 empty] | 4.2831 | [5 empty] | 9.38 | [5 empty] | 7.8878 | [11 empty] | 7.6709 | [27 empty] | 16489.4944 | 444.9427 | 7.8878 | 0 | 0 | 0 | 0 | 0 | 7.6709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 866275.712 | 10856.8 | 0 | 855418.912 | 13.1333 | 7.8878 |  | 7.6709 |  |  |  | 34.8011 | 40.956 | 4.2831 | 9.38 | 778521.2 | [5 empty] | 866275.712 | 866275.712 | 10856.8 | 855418.912
2025-06-12 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 264915.58 | 6:10 | 19:14 | 2680.4 | 4242.2 | 3809.3 | 4625.2 | 4824.9 | 4659.6 | 3745.3 | 4419.7 | 4606.6 | 4522.2 | 4693.2 | 4820.8 | 4623.4 | 3818.2 | 2556.4 | 4819 | 4573.6 | 4605.4 | 4408.6 | 4629.4 | 4543 | 4171 | 4304.2 | 4518.2 | 4314.4 | 4674.4 | 4664.1 | 4565.8 | 4429.8 | 4041.1 | 3900.3 | 4080.3 | 3666.8 | 4178.1 | 3471.2 | 3713.8 | 4140 | 4205.6 | 3860 | 3827 | 4163.2 | 4320.2 | 4191.9 | 4074 | 2326.9 | 2504.5 | 4259.5 | 4234.8 | 4097.3 | 3578.6 | 4146.9 | 4285.6 | 4174.6 | 4024.1 | 4240.8 | 4094.3 | 4017.6 | 4047.9 | 4157.1 | 3965.2 | 3762.1 | 2384.9 | 4165.8 | 4107.4 | 3878.8 | 4171.7 | 3947.3 | 4120.6 | 3911.7 | 4030.9 | 4140.9 | 4037.8 | [12 empty] | 4313.1 | 3760.5 | 4294.7 | 4304.6 | 4303.2 | 4261.1 | 4266.9 | 4284.2 | 4589.5 | 4476.7 | 4609.3 | 4518.4 | 4752.4 | 4022 | 4096.9 | 4628.4 | 3633.9 | 4486.8 | 4371.6 | 4506.5 | 4385.6 | 4450 | 4534.3 | 4299.6 | 4530.4 | 4698 | 4637.6 | 4744.5 | 4589.4 | 4464.8 | 4614.5 | 4437.6 |  |  |  |  | 4516.8 | 4578.5 | 4521 | 4554.9 | 4531.8 | 4440.6 | 4076.6 | 4299.8 | 4361.7 | 4182.5 | 4538.8 | 4352.2 | 4369.5 | 3835.7 | 4096.6 | 4224.6 | 4741.6 | 4485 | 4351 | 4687.2 | 4065.3 | 4529.8 | 2498.7 | 4808.1 | [8 empty] | 2418.9 | 4507.2 | 4448.3 | 4153.5 | 3674.9 | 3667.1 | 3717 | 4615.9 | 3742.7 | 2374.1 | 4579.4 | 4348.6 | 4191.6 | 4608.3 | 4476.8 | 4481.7 | [48 empty] | 4068.3 | 3724.5 | 3081 | 1068.4 | 1263.9 | 2939.9 | 3031.8 | 3976.3 | 1671.7 | 1894.8 | 2303.6 | 0 | 573.5 | 0 | 0 | 3802 | 4432 | 4423.4 | 4686.2 | 4465.1 | 4177.5 | 3095.2 | 4536 | 4441.1 | 4183.7 | 4429.8 | 4283.6 | 4565.3 | 4610.5 | 4572.6 | 4486.7 | 4087.5 | 3642.6 | 280.8 | 1693.8 | 0 | 0 | 258.6 | 3245.4 | 3695.4 | [120 empty] | 2759.2 | 2764.7 | 2657.8 | 2802.8 | 2325.7 | 2452.9 | 2709.6 | 2865.8 | 2666.4 | 2648 | 2641.4 | 2093.9 | 2403.5 | 2295.5 | 195.1 | 918.8 | [16 empty] | 35.2856 | [5 empty] | 41.679 | [5 empty] | 3.2931 | [5 empty] | 7.73 | [5 empty] | 7.817 | [11 empty] | 7.5953 | [27 empty] | 17143.85 | 455.6829 | 7.817 | 0 | 0 | 0 | 0 | 0 | 7.5953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 654355.552 | 10740.192 | 0 | 643615.36 | 13.0667 | 7.817 |  | 7.5953 |  |  |  | 35.2856 | 41.679 | 3.2931 | 7.73 | 755932.3 | [5 empty] | 654355.552 | 654355.552 | 10740.192 | 643615.36
2025-06-13 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 264915.58 | 6:10 | 19:21 | 4282 | 4339.8 | 3939.8 | 4692.3 | 4859.5 | 4723.5 | 3906.1 | 4514.5 | 4660.3 | 4608.2 | 4782.9 | 4858.3 | 4692.4 | 3984.9 | 2381 | 4970.5 | 4747.4 | 4776.6 | 4570.6 | 4797.9 | 4730.1 | 4764.5 | 4542.4 | 4759.9 | 4524.7 | 4891.6 | 4878.7 | 4743.1 | 4665.2 | 4300.4 | 4151.1 | 4326.9 | 3564 | 4098.5 | 3426.3 | 3636.1 | 4093.2 | 4137.7 | 3745.5 | 3718.6 | 4014.7 | 4221.8 | 4071.3 | 3924 | 2175.4 | 2326.7 | 4156.6 | 4115.4 | 3986.4 | 3430.8 | 4067.1 | 4237.3 | 4113 | 3897.2 | 4164.4 | 3978.9 | 3926.6 | 3949.7 | 4072.2 | 3861.5 | 3668.7 | 2266.8 | 4102.4 | 4032.7 | 3800.2 | 4121.9 | 3870.4 | 4060.1 | 3831.8 | 3954.9 | 4085.4 | 3967.4 | [12 empty] | 4220 | 3641.5 | 4211.2 | 4226.8 | 4201 | 4139.6 | 4156.9 | 4143.6 | 4741.2 | 4646.2 | 4782.8 | 4695.7 | 4914.8 | 8243.7 | 4178.7 | 4780.8 | 3845.3 | 4667.6 | 4553.6 | 4691.8 | 4577.9 | 4625.6 | 4717.8 | 4518 | 4776.8 | 4949.2 | 4887.7 | 4987.4 | 4850.4 | 4715.9 | 4854.1 | 4682 |  |  |  |  | 4791.2 | 4840.7 | 4786.3 | 4430.8 | 4787.2 | 4704.8 | 4353.2 | 4543.9 | 4667.9 | 4491.8 | 4855.2 | 4663.3 | 4674.4 | 4138.8 | 4391.4 | 4526.9 | 0 | 0 | 0 | 0 | 4214.8 | 2627.4 | 2179.3 | 4910.3 | [8 empty] | 2269.1 | 4686.1 | 4650.4 | 4382 | 3898.4 | 3861.8 | 3933.8 | 4821.8 | 3971.1 | 2246.5 | 4777.2 | 4474.1 | 4421 | 4795.7 | 4662.3 | 4674.1 | [48 empty] | 4295.7 | 3959 | 2994.9 | 1006.6 | 1194.4 | 2796.2 | 2417.3 | 4216.3 | 1581.7 | 1801.8 | 2190.3 | 0 | 545 | 0 | 0 | 3843.7 | 4752.9 | 4736.5 | 4975.3 | 4761.7 | 4480.9 | 3132.5 | 4856.1 | 4759.3 | 4487.3 | 4731.9 | 4585.8 | 4862.4 | 4909.4 | 4865.7 | 4770.5 | 4401.4 | 3857.1 | 264.7 | 1600 | 0 | 0 | 240.6 | 3317.1 | 3934.3 | [120 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 37.9387 | [5 empty] | 42.867 | [5 empty] | 3.1106 | [5 empty] | 8.13 | [5 empty] | 7.2433 | [11 empty] | 7.1236 | [27 empty] | 17853.8602 | 466.5014 | 7.2433 | 0 | 0 | 0 | 0 | 0 | 7.1236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710010.24 | 10818.464 | 0 | 699191.776 | 13.1833 | 7.2433 |  | 7.1236 |  |  |  | 37.9387 | 42.867 | 3.1106 | 8.13 | 720297.6 | [5 empty] | 710010.24 | 710010.24 | 10818.464 | 699191.776
2025-06-14 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 264915.58 | 6:26 | 19:13 | 459 | 1286.2 | 980.9 | 1567.9 | 1696.9 | 1584.6 | 937.1 | 1413.3 | 1521.2 | 1480.7 | 1605.9 | 1677.8 | 1563.7 | 939.2 | 414.9 | 1736.3 | 1578 | 1593.8 | 1439.6 | 1604.4 | 1524.4 | 1539.3 | 1322.2 | 1534.6 | 1342.8 | 1654.9 | 1643.2 | 1563.9 | 1470.1 | 1210.8 | 1121.6 | 1222.3 | 833.8 | 1427.6 | 775.4 | 916.5 | 1501.2 | 1511.3 | 992.2 | 997.2 | 1336.2 | 1628.3 | 1378.3 | 1197.8 | 385.2 | 407.8 | 1533.1 | 1470.9 | 1296.4 | 732.7 | 1370.5 | 1624.8 | 1431.2 | 1093.2 | 1561.7 | 1250.3 | 1197 | 1224.5 | 1435.1 | 1129.8 | 915.9 | 405.3 | 1418.4 | 1323.1 | 1001.9 | 1442 | 1085 | 1330.8 | 1030.8 | 1195.8 | 1343.2 | 1188.3 | [12 empty] | 1615.6 | 881 | 1593 | 1620.3 | 1598.4 | 1524.5 | 1542.2 | 1582 | 1542.3 | 1472.3 | 1557.5 | 1492 | 1649.5 | 1114.4 | 1000.1 | 1549.9 | 855.9 | 1483.2 | 1378.5 | 1482.8 | 1375.9 | 1429.7 | 1495.7 | 1346.9 | 1459.1 | 1598.7 | 1584 | 1629.9 | 1565.1 | 1471.1 | 1578.8 | 1446.2 |  |  |  |  | 1507.4 | 1540.8 | 1492 | 1237.5 | 1520.2 | 1470 | 1207.1 | 1313.6 | 1437.6 | 1291.4 | 1576.6 | 1427.2 | 1444 | 794.5 | 1236.9 | 1310.8 | 0 | 0 | 0 | 0 | 1155.4 | 1477.3 | 409.6 | 1685.2 | [8 empty] | 399.9 | 1478.9 | 1429.1 | 1221.4 | 884.8 | 857.6 | 879 | 1574.9 | 924.5 | 392.3 | 1508.3 | 1267.2 | 999 | 1530.2 | 1437.2 | 1465.1 | [48 empty] | 1095.4 | 911.9 | 579.8 | 126.1 | 152.5 | 506.8 | 408.4 | 1053.7 | 222.6 | 288.4 | 366.6 | 0 | 20.1 | 0 | 0 | 798.1 | 1449.8 | 1439 | 1632.2 | 1480.7 | 1280.3 | 584.7 | 1529.7 | 1459.7 | 1105.3 | 1461.9 | 1324.8 | 1528.5 | 1604.5 | 1560.1 | 1473.6 | 1195.3 | 814.7 | 6 | 224.2 | 0 | 0 | 0.7 | 621.3 | 883.7 | [120 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 33.4049 | [5 empty] | 38.974 | [5 empty] | 3.0313 | [5 empty] | 10.39 | [5 empty] | 1.4674 | [11 empty] | 1.4336 | [27 empty] | 18076.6231 | 476.7979 | 1.4674 | 0 | 0 | 0 | 0 | 0 | 1.4336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222762.848 | 10296.544 | 0 | 212466.304 | 12.7833 | 1.4674 |  | 1.4336 |  |  |  | 33.4049 | 38.974 | 3.0313 | 10.39 | 214044.1 | [5 empty] | 222762.848 | 222762.848 | 10296.544 | 212466.304
2025-06-15 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 264916 | 7:20 | 19:14 | 680.2 | 1757.7 | 1393.7 | 2095.8 | 2249.1 | 2110.7 | 1322.2 | 1899.4 | 2037.8 | 1988.7 | 2148.9 | 2247.9 | 2100.7 | 1353.9 | 648.7 | 2290.1 | 2127.1 | 2124.4 | 1950.3 | 2142.2 | 2080.7 | 2099.3 | 1886 | 2104.1 | 1841.1 | 2203.8 | 2172.9 | 2082.2 | 1980.4 | 1683.7 | 1575.4 | 1697 | 1204.4 | 1901.2 | 1107.7 | 1298.2 | 1990 | 2008.1 | 1405.6 | 1403.5 | 1802.4 | 2133.9 | 1851.8 | 1638.7 | 598.5 | 626 | 2021.9 | 1953.8 | 1755.7 | 1075.3 | 1855.3 | 2135.4 | 1894.6 | 1661.6 | 2082.8 | 1943.2 | 1657 | 1701.7 | 1911.6 | 1563.7 | 1306.1 | 633.1 | 1898.8 | 1828.8 | 1421.2 | 1897.7 | 1498.9 | 1785.6 | 1423.3 | 1621.8 | 1780.8 | 1618.3 | [12 empty] | 2094.9 | 1236.6 | 2059.9 | 2092.6 | 2053.8 | 1969.3 | 2010.8 | 2052.5 | 2094.9 | 2011.6 | 2111.3 | 2039.9 | 2230.2 | 1591.9 | 1445.2 | 2105 | 1258 | 1982.1 | 1898.2 | 1038.3 | 1853.3 | 1616.5 | 2016.7 | 1845.2 | 2091.2 | 2159.8 | 2113.5 | 2222.5 | 20825 | 2020.8 | 2186.4 | 2071.9 |  |  |  |  | 2019.3 | 2070.9 | 2007.4 | 1697.7 | 2034 | 1965.8 | 1672.9 | 1785 | 1929 | 1757.8 | 2095.4 | 1918.7 | 1947 | 1464.8 | 1685.2 | 1789 | 0 | 0 | 0 | 0 | 1596.3 | 1955.6 | 619.3 | 2232.6 | [8 empty] | 632.7 | 2024.3 | 1985.8 | 1739.1 | 1306.6 | 1271 | 1294.6 | 2155 | 1347.6 | 623.5 | 2066.9 | 1744.3 | 1429.4 | 2052.5 | 1911.1 | 1739.7 | [48 empty] | 1579.6 | 1355.3 | 957.8 | 261.7 | 295 | 810.3 | 635.7 | 1506.1 | 342.5 | 482.7 | 600.1 | 0 | 95.3 | 0 | 0 | 1212.8 | 2024.7 | 2007.8 | 2211.8 | 2045.4 | 1804.4 | 912.5 | 2107.2 | 2030 | 1581.6 | 2020.9 | 1858 | 2110.5 | 2199.6 | 2154.3 | 2042 | 1701.1 | 611.1 | 0 | 411.4 | 0 | 0 | 22.7 | 982.5 | 1318.7 | [120 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 31.8905 | [5 empty] | 35.9754 | [5 empty] | 1.278 | [5 empty] | 4.15 | [5 empty] | 1.9756 | [11 empty] | 1.9129 | [27 empty] | 18375.7772 | 488.0308 | 1.9756 | 0 | 0 | 0 | 0 | 0 | 1.9129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299154.144 | 11232.864 | 0 | 287921.28 | 11.9 | 1.9756 |  | 1.9129 |  |  |  | 31.8905 | 35.9754 | 1.278 | 4.15 | 311234.8 | [5 empty] | 299154.144 | 299154.144 | 11232.864 | 287921.28
2025-06-16 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 241054.38 | 7:23 | 19:22 | 1900.1 | 4715.2 | 3694.2 | 5647.3 | 6082.3 | 5680.4 | 3318.5 | 5132.1 | 5466.5 | 5318 | 5766.5 | 6045.6 | 5612 | 3571 | 1800.2 | 6203.3 | 5706.2 | 5706.5 | 5245.3 | 5799.1 | 5617.5 | 5674.9 | 5042.7 | 5659.5 | 4890 | 5949.3 | 5877.6 | 5601.9 | 5243.7 | 4407.3 | 4068.3 | 4471 | [60 empty] | 5540.4 | 5289.5 | 5572.2 | 5364.7 | 5896.1 | 4122.6 | 3715.5 | 5553.5 | 3207.8 | 5142.3 | 4987.7 | 2667.2 | 4884.3 | 4189.6 | 5295.9 | 4800.7 | 5551 | 5609.4 | 5463.8 | 5810.4 | 5413.3 | 5237.7 | 5767.4 | 5435.1 |  |  |  |  | 5089.7 | 5182.4 | 5114.4 | 4291.5 | 5173.5 | 4959.4 | 4167.4 | 4488.1 | 4885.1 | 4439.7 | 5361.2 | 4910.8 | 4970.7 | 3659.6 | 4219.5 | 4517.7 | 0 | 0 | 0 | 0 | 4362.3 | 5367.9 | 1780 | 6133.7 | [8 empty] | 1684.6 | 5299.9 | 5178.7 | 4481.7 | 3306.2 | 3212.1 | 3298.7 | 5568.6 | 3433.4 | 1634.3 | 5416.5 | 3618.8 | 3433.3 | 5495.1 | 5152.1 | 5236.9 | [48 empty] | 4063.4 | 3405.6 | 2445.4 | 777.9 | 861.6 | 2074.7 | 1589.8 | 3455.4 | 1007.6 | 1316.5 | 1600.5 | 0 | 362 | 0 | 0 | 3113.1 | 5205.7 | 5183.8 | 5756.2 | 5318 | 4658.5 | 2339.6 | 5454.4 | 5246.7 | 3943.8 | 5107 | 4696.4 | 5452.2 | 5682.5 | 5597.9 | 5264 | 4339 | 1636.8 | 0 | 1153.8 | 0 | 0 | 140 | 2471.1 | 3319.2 | [120 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 35.8929 | [5 empty] | 40.987 | [5 empty] | 3.6599 | [5 empty] | 8.35 | [5 empty] | 3.6636 | [11 empty] | 3.4422 | [27 empty] | 19103.8697 | 498.9704 | 3.6636 | 0 | 0 | 0 | 0 | 0 | 3.4422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 728092.48 | 10939.584 | 0 | 717152.896 | 11.9833 | 3.6636 |  | 3.4422 |  |  |  | 35.8929 | 40.987 | 3.6599 | 8.35 | 553997.7 | [5 empty] | 728092.48 | 728092.48 | 10939.584 | 717152.896
2025-06-17 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 241054.38 | 6:33 | 19:26 | 2102.9 | 5185.5 | 4062.5 | 6195.4 | 6660 | 6230.1 | 3880.8 | 5644.1 | 5999.9 | 5861 | 6351.2 | 6637.7 | 6167.4 | 3961.3 | 1998.5 | 6787.1 | 6277 | 6282.5 | 5768.6 | 6386.6 | 6210.5 | 6272.9 | 5571.9 | 6241.2 | 5467.8 | 6594.8 | 6523.7 | 6229.1 | 5828.2 | 4934.1 | 4587.6 | 5034.4 | [60 empty] | 6163.8 | 5891.7 | 6217.1 | 5983.7 | 6563.8 | 4615.5 | 4157.4 | 6137.7 | 3596.1 | 5748.7 | 5558.1 | 2970.5 | 5445.6 | 4679.6 | 5902.5 | 5385.2 | 4005.7 | 4064 | 3959.9 | 4194.7 | 3863.2 | 3753.2 | 4110.5 | 3866.5 |  |  |  |  | 6035.5 | 6090.9 | 6055.8 | 5082.1 | 6087.2 | 5842.4 | 4888.2 | 5281.1 | 5724.2 | 5210.1 | 6290.1 | 5737.9 | 5809.5 | 4277 | 4930 | 5276 | 0 | 0 | 0 | 0 | 4883.8 | 5969.8 | 2001.8 | 6851.6 | [8 empty] | 1907.6 | 5929.2 | 5818.7 | 5049.7 | 3748.2 | 3664.1 | 3757 | 6334.9 | 3878.2 | 1801.1 | 6095.9 | 3636.3 | 3207.1 | 6132 | 5728.2 | 5766 | [48 empty] | 4398.7 | 3846.7 | 2778.4 | 901.8 | 992 | 2356.8 | 1860.4 | 3898 | 1156.5 | 1499.6 | 1816.2 | 0 | 439 | 0 | 0 | 3526.8 | 5928.7 | 5904.7 | 6541.1 | 6045.3 | 5297.5 | 2676 | 6212.3 | 5975.4 | 4539.8 | 5818.9 | 5396.7 | 6225.5 | 6471.5 | 6356.3 | 5978.3 | 4946.5 | 1865.5 | 0 | 1322.5 | 0 | 0 | 192.1 | 2803.5 | 3761.4 | [120 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 33.5702 | [5 empty] | 39.9877 | [5 empty] | 2.7947 | [5 empty] | 10.97 | [5 empty] | 5.8557 | [11 empty] | 5.7667 | [27 empty] | 19861.2902 | 509.7933 | 5.8557 | 0 | 0 | 0 | 0 | 0 | 5.7667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757420.48 | 10822.976 | 0 | 746597.504 | 12.8833 | 5.8557 |  | 5.7667 |  |  |  | 33.5702 | 39.9877 | 2.7947 | 10.97 | 605280.6 | [5 empty] | 757420.48 | 757420.48 | 10822.976 | 746597.504
2025-06-18 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 241054.38 | 6:13 | 19:19 | 2568.4 | 6311.6 | 4953.7 | 7389 | 7882.8 | 7481.8 | 4759.3 | 6879.9 | 7299 | 7091.3 | 7597.3 | 7892.9 | 7465.4 | 4890.5 | 2493.4 | 8048.4 | 7512.3 | 7504.6 | 7015.1 | 7575.7 | 7398.1 | 7445.1 | 6761.6 | 7453.3 | 6629.5 | 7761.6 | 7683.7 | 7441.4 | 7152.3 | 6006.5 | 5591.4 | 6121.3 | 3639 | 4135.8 | 3541.8 | 3712.9 | 4171.8 | 4174.9 | 3825.5 | 3831.5 | 2263 | 2400.9 | 4178.6 | 4149.7 | 4077.4 | 4233.8 | 4105.6 | 3987.7 | 4131.4 | 4023.1 | 4196.1 | 4156.8 | 4067.2 | 3476.6 | 4115.1 | 4248.6 | 3730.8 | 2324.2 | 4104.2 | 4093.9 | 3980 | 4014.3 | 4116.7 | 3919.6 | 3849.9 | 3949.6 | 4081.5 | 3984 | 3842.2 | 4075.5 | 3898.7 | 4079.1 | [12 empty] | 4215.8 | 3689.8 | 4208.2 | 4220.6 | 4212.6 | 4175.6 | 4185 | 4202.6 | 7414.4 | 7143.1 | 7458.2 | 7232.4 | 7767.3 | 5640.7 | 5102.2 | 7426.4 | 4384.8 | 6961.7 | 6775 | 3654.3 | 6651.7 | 5714.9 | 7156.8 | 6534.1 | 7863.1 | 7965.3 | 7757.5 | 8196.3 | 7569.2 | 7350.9 | 8042.4 | 7610.8 |  |  |  |  | 7290.2 | 7347 | 7312 | 6144.8 | 7349.9 | 7068.1 | 5929.4 | 6430.3 | 6937 | 6328.4 | 7584.9 | 6840.6 | 9695.2 | 5161 | 5972.8 | 6413.6 | 7449.5 | 6462.1 | 6354.2 | 7196.2 | 5845.4 | 7123.2 | 2427.7 | 7924.5 | [8 empty] | 2357 | 7157.8 | 7075 | 6173.5 | 4573.1 | 4455.5 | 4573.8 | 7508.1 | 4729.4 | 2212.2 | 7343.2 | 3059.1 | 3934.1 | 7417.6 | 6939.7 | 7122.1 | [48 empty] | 5693.2 | 4795.7 | 3518.1 | 1137.2 | 1250 | 2919.3 | 2344.7 | 4996.1 | 1437.3 | 1858.4 | 2249.9 | 0 | 559.6 | 0 | 2.6 | 4312.8 | 6986.4 | 7145.3 | 7734.1 | 7257.3 | 6426.3 | 3256.5 | 7417.9 | 7196.3 | 5579.1 | 7079.1 | 6645.9 | 7486.4 | 7673.4 | 7570.4 | 7223.1 | 6038.7 | 2323.4 | 0 | 1653.5 | 0 | 0 | 259.7 | 3461.4 | 4615.4 | [120 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 35.1678 | [5 empty] | 41.8979 | [5 empty] | 2.5244 | [5 empty] | 9.31 | [5 empty] | 7.4254 | [11 empty] | 7.2151 | [27 empty] | 20812.4718 | 520.2069 | 7.4254 | 0 | 0 | 0 | 0 | 0 | 7.2151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 951181.664 | 10413.536 | 0 | 940768.128 | 13.1 | 7.4254 |  | 7.2151 |  |  |  | 35.1678 | 41.8979 | 2.5244 | 9.31 | 972754.6 | [5 empty] | 951181.664 | 951181.664 | 10413.536 | 940768.128
2025-06-19 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 241054.38 | 6:07 | 19:43 | 2603 | 6384.6 | 5051 | 7581.7 | 8083 | 7647.9 | 4783.1 | 6935.3 | 7414.6 | 7168.7 | 7779.6 | 8089.7 | 7639.2 | 4911.7 | 2508.5 | 8287.9 | 7673.5 | 7639.7 | 7077.3 | 7758.4 | 7552.7 | 7539.4 | 6811.9 | 7623.5 | 6659.3 | 7966.5 | 7878.5 | 7606.3 | 7248.3 | 6040 | 5634.5 | 6153.2 | 3227.3 | 4330.8 | 3615.3 | 3788.7 | 4362.4 | 4353.2 | 3932.4 | 3947 | 4263.1 | 4442.4 | 4291.1 | 4146.3 | 2275.1 | 2415.6 | 4377.9 | 4345.6 | 4319 | 4191.5 | 4405.2 | 4354.1 | 4241.8 | 3553.9 | 4292.5 | 4447 | 4138.7 | 4177.2 | 4282.2 | 4019.3 | 3850.7 | 2366.8 | 4259.9 | 4274.3 | 3953.2 | 4240.1 | 4022.9 | 4249 | 3964.2 | 4091.6 | 4250.1 | 4124.7 | [12 empty] | 4228.2 | 4383.8 | 4357 | 4432.7 | 4431.1 | 3789 | 4415.9 | 4437.5 | 7568.6 | 7245.9 | 7606.2 | 7335.6 | 7975.3 | 5673.5 | 5133.9 | 7590.9 | 4426.4 | 7054.7 | 6806.7 | 3664.9 | 6667.4 | 5733.2 | 7265.4 | 6612.3 | 7856.7 | 7948.9 | 7721.6 | 8161 | 7569.6 | 7338 | 8055.7 | 7619 |  |  |  |  | 7254 | 7292.3 | 7273.7 | 6118.6 | 7353.1 | 7072.3 | 5926.7 | 6410.4 | 6934.5 | 6318.7 | 7593.7 | 6737 | 6999.4 | 5173.6 | 5988.7 | 6404.3 | 8007.7 | 6862.8 | 6820.5 | 7782.5 | 5876.5 | 7531 | 2441.7 | 8132.8 | [8 empty] | 2369.8 | 7196 | 7157.3 | 6197.7 | 4612.6 | 4492 | 4608.6 | 7671.7 | 4765.9 | 2237.6 | 7498.1 | 2825 | 3962 | 7574.9 | 6901.4 | 7216.2 | [48 empty] | 5558.6 | 4779.5 | 3554.1 | 1141.8 | 1058.8 | 2951.3 | 2369.9 | 4198.9 | 1442.4 | 1864.5 | 2271.5 | 0 | 554.3 | 0 | 2341 | 4331.5 | 7026.1 | 7217 | 7927 | 7381 | 6483.7 | 3278.6 | 7556.9 | 7286.4 | 5588.8 | 7070.8 | 6660.6 | 7605.5 | 7848.6 | 7727.7 | 7306 | 6059.7 | 2341.5 | 0 | 1666 | 0 | 0 | 248.9 | 3439.2 | 3648.8 | [120 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 34.807 | [5 empty] | 40.9876 | [5 empty] | 5.4483 | [5 empty] | 11.7 | [5 empty] | 7.4864 | [11 empty] | 7.3007 | [27 empty] | 21781.2512 | 529.9978 | 7.4864 | 0 | 0 | 0 | 0 | 0 | 7.3007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 968779.328 | 9790.912 | 0 | 958988.416 | 13.6 | 7.4864 |  | 7.3007 |  |  |  | 34.807 | 40.9876 | 5.4483 | 11.7 | 986403.4 | [5 empty] | 968779.328 | 968779.328 | 9790.912 | 958988.416
2025-06-20 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 241054 | 6:17 | 19:04 | 2322.3 | 5707.9 | 4489.6 | 6776.9 | 7271.2 | 6825.1 | 4261.1 | 6196.2 | 6612.9 | 6409.2 | 6972.2 | 7282.4 | 6852.9 | 4400.8 | 2241.4 | 7477.5 | 6884.6 | 6910.4 | 6333.3 | 6967.9 | 6758.4 | 6746.7 | 6113.6 | 6852.8 | 5988.5 | 7186.5 | 7093.9 | 6828.1 | 6496.5 | 5454.6 | 5106.3 | 5539.1 | 3383.7 | 3926.1 | 3252.9 | 3440.6 | 3954.5 | 3936.8 | 3567.4 | 3583.9 | 3864.2 | 4036.9 | 3864.2 | 3894 | 2037.9 | 2162.5 | 3973.5 | 3941.5 | 3845.9 | 3150.7 | 3895.5 | 4037.9 | 3909.8 | 3801.3 | 3999.1 | 3956.5 | 3764.2 | 3793.6 | 3879.6 | 3663.2 | 3488.5 | 2133.7 | 3883.1 | 3879.7 | 3592 | 3858.9 | 3676.1 | 3859.1 | 3629.6 | 3741 | 3858.8 | 3759.6 | [12 empty] | 4024 | 3702.6 | 4007.9 | 4028.2 | 4028.3 | 3980.8 | 4001.8 | 4044.3 | 6791.1 | 6513.1 | 6832 | 6569.7 | 7222.3 | 5124.4 | 4623.6 | 6819.1 | 4006.5 | 6374 | 6152.5 | 3309 | 6034.3 | 5198.5 | 6582.7 | 5997.5 | 6883 | 6962 | 6762.8 | 7135.2 | 6685.1 | 6469.1 | 7077.5 | 6709.9 |  |  |  |  | 6420.5 | 6437.7 | 6412.5 | 5405.6 | 6498.2 | 5917.9 | 5191.2 | 5665.4 | 6142.6 | 5594.9 | 6700.6 | 5973.8 | 6205.3 | 4586.7 | 5300.5 | 5662.9 | 7171.7 | 6110.3 | 6095.5 | 6977.6 | 5273 | 6490.4 | 2175.5 | 7303 | [8 empty] | 2121.9 | 6436.8 | 6404.4 | 5555.8 | 4132.3 | 4033 | 4125.8 | 6867.7 | 4297.7 | 2016.1 | 6730.7 | 2517.4 | 3549.1 | 6788.7 | 6179.8 | 6473.6 | [48 empty] | 4914.7 | 4328.3 | 3213.3 | 1023.5 | 951.6 | 2658.6 | 2133 | 3643.8 | 1294.2 | 1672.4 | 2037.8 | 0 | 64.8 | 0 | 2092.7 | 3881 | 6237.9 | 6414.2 | 7106.6 | 6589.5 | 5816.6 | 2936.4 | 6731 | 6479.2 | 4959.3 | 6219.3 | 5915.7 | 6755.3 | 7019.7 | 6896.7 | 6484.1 | 5379.9 | 2108.2 | 0 | 1503.8 | 0 | 0 | 222.9 | 2774.4 | 3289.3 | [120 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 34.118 | [5 empty] | 39.8877 | [5 empty] | 5.3578 | [5 empty] | 10.94 | [5 empty] | 6.5278 | [11 empty] | 6.336 | [27 empty] | 22649.7271 | 540.1863 | 6.5278 | 0 | 0 | 0 | 0 | 0 | 6.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 868475.936 | 10188.544 | 0 | 858287.392 | 12.7833 | 6.5278 |  | 6.336 |  |  |  | 34.118 | 39.8877 | 5.3578 | 10.94 | 883585.4 | [5 empty] | 868475.936 | 868475.936 | 10188.544 | 858287.392
2025-06-21 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 241054 | 6:11 | 18:41 | 1215.1 | 3122.4 | 2429.6 | 3747.3 | 4047.4 | 3780.4 | 2343.8 | 3409 | 3625.4 | 3541.2 | 3863.3 | 4039 | 3753 | 2360.1 | 1159.7 | 4160.7 | 3796.3 | 3814.5 | 3482.6 | 3858.5 | 3740.8 | 3740.4 | 3362.9 | 3777.7 | 3284.1 | 3991.2 | 3943.9 | 3780.3 | 0 | 2987.1 | 2788.6 | 3019 | 2029.6 | 3048.8 | 1881 | 2113.2 | 3105.6 | 3067.1 | 2338.4 | 2331.8 | 2910 | 3279.1 | 2960.7 | 2672.6 | 1063.4 | 1118.4 | 3156.2 | 3084.8 | 2875.3 | 1755.3 | 2961.1 | 3280.2 | 2966.8 | 2780.9 | 3180.6 | 3046.7 | 2710.5 | 2779.4 | 3025.2 | 2586.7 | 2246.3 | 1125.1 | 3005.7 | 2951.3 | 2301.1 | 2897.1 | 2504.8 | 2911.6 | 2414.8 | 2631.5 | 2901.2 | 2671.3 | [12 empty] | 3239.6 | 2561.4 | 3201.9 | 3253.4 | 3315.1 | 3171.4 | 3190.9 | 3285.4 | 3703.1 | 3542.3 | 3724.6 | 3614.6 | 3968.2 | 2756 | 2468.4 | 3713.4 | 2140.1 | 3459.5 | 3329 | 1755 | 3283.6 | 2796.5 | 3574.9 | 3240.6 | 3161.1 | 3196.7 | 3021.5 | 3294.5 | 3087.8 | 2974.3 | 3189 | 3078.5 |  |  |  |  | 2896.3 | 2914.1 | 2907.4 | 2447.5 | 2957.5 | 2668.8 | 2290.5 | 2547 | 1600.1 | 1452.3 | 1760.8 | 1554.6 | 1620.7 | 1192.5 | 1373.7 | 1476.9 | 3998.8 | 3360.5 | 3357.9 | 3887.5 | 2902.1 | 3592.7 | 1150.5 | 4089.4 | [8 empty] | 939.1 | 2958.2 | 2934 | 2526.7 | 1872.7 | 1825.5 | 1861.8 | 3153.5 | 1959.5 | 895.2 | 3104.4 | 878.5 | 1609.7 | 3135.8 | 2802.5 | 2987.9 | [64 empty] | 2616.3 | 2668.4 | 2988.3 | 2763 | 2420.8 | 1212.9 | 2819.6 | 2705 | 2429.9 | 3074.9 | 2899.3 | 3343.5 | 2429.9 | 3074.9 | 2899.3 | 3343.5 | [160 empty] | 31.4815 | [5 empty] | 37.9787 | [5 empty] | 5.4005 | [5 empty] | 11.49 | [5 empty] | 3.4647 | [11 empty] | 3.4181 | [27 empty] | 23094.1967 | 549.8358 | 3.4647 | 0 | 0 | 0 | 0 | 0 | 3.4181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 444469.632 | 9649.472 | 0 | 434820.16 | 12.5 | 3.4647 |  | 3.4181 |  |  |  | 31.4815 | 37.9787 | 5.4005 | 11.49 | 449063.4 | [5 empty] | 444469.632 | 444469.632 | 9649.472 | 434820.16
2025-06-22 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 241054 | 6:10 | 19:19 | 2370.6 | 5760.2 | 4506.6 | 6883 | 7433.2 | 7018.9 | 4555.5 | 6247.3 | 6393.4 | 6568 | 7205.7 | 7572.1 | 7039.8 | 4488.1 | 2296.7 | 7744 | 7086.2 | 7109.8 | 6544 | 7138 | 7006.1 | 6991.1 | 6211.4 | 6987.8 | 6041.8 | 7303 | 7226.1 | 6906.1 | 4603.7 | 4886.1 | 4605.8 | 5000.6 | 3366.9 | 3897 | 3262.5 | 3406.8 | 3925.2 | 3911.6 | 3546.7 | 3529.4 | 3835 | 4020.5 | 4057.9 | 3714.3 | 2074.5 | 2200 | 3945.8 | 3913.5 | 3797.4 | 3158.8 | 3851.8 | 4016.4 | 3843.9 | 3754.2 | 3965.5 | 3872.9 | 3701.4 | 3739.8 | 3850.4 | 3617.4 | 3441.3 | 2151.3 | 3849.8 | 3814.8 | 3487.3 | 3778.9 | 3379.4 | 3780.4 | 3537.4 | 3640 | 3780.2 | 3674.2 | [12 empty] | 3989 | 3649.8 | 3985.7 | 4006.2 | 4025.2 | 3938.4 | 3951.5 | 4002.3 | 7002 | 6685.6 | 7023.4 | 6845.6 | 7438.7 | 5226.9 | 4729.8 | 7020.8 | 4066.4 | 6496.1 | 6066.4 | 3335.9 | 6106.7 | 5238.6 | 6618.5 | 6041.2 | 7026.7 | 7088.6 | 6697.9 | 7267.4 | 6796.6 | 6582.4 | 7051.4 | 6825.6 |  |  |  |  | 6596.3 | 6592.6 | 6555 | 5499.8 | 6607.1 | 5998.7 | 5162.5 | 5789.2 | 6243.2 | 5671.5 | 6829 | 6061.5 | 6321.6 | 4655.6 | 5408.1 | 5786.3 | 7401.4 | 6525.8 | 6203.8 | 7160.2 | 5376.5 | 6626.7 | 2234.7 | 7566 | [8 empty] | 2294 | 6657.7 | 6616.8 | 5730.2 | 4256.1 | 4149.9 | 4264.1 | 7092 | 4378.1 | 2045.5 | 6856.6 | 1835.6 | 3640.3 | 7006 | 6280.5 | 6654.8 | [64 empty] | 6382.1 | 6610.1 | 7374.5 | 6816.8 | 5978.2 | 3015.3 | 6908.7 | 6643.3 | 5092.3 | 6471.1 | 6051.2 | 6954 | 7272 | 7142.3 | 6696.6 | 5554.5 | [160 empty] | 34.2469 | [5 empty] | 40.8976 | [5 empty] | 4.0327 | [5 empty] | 9.65 | [5 empty] | 6.9011 | [11 empty] | 6.8287 | [27 empty] | 23925.6252 | 560.4899 | 6.9011 | 0 | 0 | 0 | 0 | 0 | 6.8287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 831428.416 | 10654.048 | 0 | 820774.368 | 13.15 | 6.9011 |  | 6.8287 |  |  |  | 34.2469 | 40.8976 | 4.0327 | 9.65 | 848244.8 | [5 empty] | 831428.416 | 831428.416 | 10654.048 | 820774.368
2025-06-23 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 241054 | 6:14 | 19:16 | 2071 | 5328.8 | 4040.9 | 6152.2 | 6620.6 | 6193.9 | 3963.8 | 5531.5 | 5890.4 | 5821.6 | 6332.4 | 6615.4 | 6173.5 | 3923.7 | 1997.6 | 6804.6 | 6434.8 | 6279.4 | 5910.3 | 6338.2 | 6218.5 | 6201.9 | 5522.7 | 6218.5 | 5406.6 | 6544.3 | 6451 | 6191.1 | 5454 | 4909.2 | 4591.3 | 4981.3 | 3108.2 | 3856.6 | 2971.8 | 3154.5 | 3888.6 | 3870.2 | 3341 | 3338 | 3749.5 | 3988.1 | 3786 | 3578.7 | 1800.1 | 1906.7 | 3911.1 | 3869.6 | 3718.9 | 2860.3 | 3786.56 | 3992.4 | 3767.9 | 3650.4 | 3921.3 | 3815.2 | 3591.4 | 3645 | 3821.2 | 3508.6 | 3274.5 | 1914.9 | 3812.2 | 3751.8 | 3315.7 | 3730.5 | 3458.2 | 3730.8 | 3394.78 | 3549.6 | 3738.7 | 3578.4 | [12 empty] | 3954.1 | 3496.4 | 3939.6 | 3968.2 | 4004.8 | 3917.6 | 3927.4 | 3981.5 | 6117.1 | 5856.4 | 6154.6 | 5994.4 | 6541.8 | 4584.7 | 4126.9 | 6114.5 | 3588 | 5735.7 | 5364.7 | 2972.9 | 5442.5 | 4659 | 5915 | 5383.5 | 6278.2 | 6349.2 | 5843.7 | 6512.9 | 6074 | 5874.2 | 6289.8 | 6094.7 |  |  |  |  | 5798.3 | 5816.3 | 5813.1 | 4892.3 | 5893.6 | 5031.5 | 4613.8 | 5139.2 | 5555.2 | 5051.6 | 6097.4 | 5383.8 | 5606.2 | 4128.5 | 4790.7 | 5128.9 | 6451.5 | 5455 | 5440.3 | 6274 | 4713.8 | 5812.6 | 1931.9 | 6592.6 | [8 empty] | 1964.4 | 5782 | 5732.6 | 4952.2 | 3681.3 | 3596.7 | 3688.8 | 6177.6 | 3845.7 | 1997.7 | 6057.5 | 1618.6 | 3175.2 | 6108.7 | 5472.7 | 5663 | [64 empty] | 5618.8 | 5755.5 | 6396.9 | 5917.5 | 5171.7 | 2607.5 | 6073.6 | 5838.5 | 4487.7 | 5723.8 | 5336.5 | 6072.9 | 6361.4 | 6197.3 | 5824.2 | 4810.7 | [160 empty] | 34.3087 | [5 empty] | 40.9865 | [5 empty] | 3.8774 | [5 empty] | 7.9 | [5 empty] | 5.9409 | [11 empty] | 5.9192 | [27 empty] | 24681.7262 | 570.9917 | 5.9409 | 0 | 0 | 0 | 0 | 0 | 5.9192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756101.056 | 10501.824 | 0 | 745599.232 | 13.0333 | 5.9409 |  | 5.9192 |  |  |  | 34.3087 | 40.9865 | 3.8774 | 7.9 | 766742.24 | [5 empty] | 756101.056 | 756101.056 | 10501.824 | 745599.232
2025-06-24 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 241054 | 6:10 | 19:21 | 2302.3 | 6049.2 | 4550.6 | 6949.3 | 7511.6 | 7026.9 | 4682.4 | 6311.4 | 6710.2 | 6585 | 7215.2 | 7566.3 | 7064 | 4510.9 | 2260.3 | 7775.7 | 7281.5 | 7125.5 | 6665.9 | 7163.4 | 7021.6 | 6994.9 | 6218.9 | 7028.8 | 6083.5 | 7373.6 | 7263 | 6963.1 | 6412.9 | 5496 | 5136.9 | 5595.3 | 3542.4 | 4130.1 | 3406.1 | 3579.2 | 4144.6 | 4132.2 | 3750.7 | 3744.3 | 4048.6 | 4215 | 4083.7 | 3941.5 | 2121.2 | 2254.2 | 4153.3 | 4124.7 | 4015.8 | 3247.9 | 6061.6 | 4207.3 | 4058.7 | 3982.8 | 4153.8 | 4077.4 | 3908 | 3952.1 | 4064.4 | 3832.3 | 3625.2 | 2055.9 | 4058.5 | 3995.8 | 3669.9 | 3995 | 3780.1 | 3971.8 | 3731.5 | 3844.9 | 3990.7 | 3877.5 | [12 empty] | 4173.7 | 3848.1 | 4162.4 | 4177.6 | 4194.6 | 4126.6 | 4144.4 | 4187.9 | 6952.5 | 6629.8 | 7018 | 6822.2 | 7412.4 | 5202.6 | 4714.5 | 7012.9 | 4051.2 | 6468.4 | 6059 | 3304.7 | 6110.3 | 5244.7 | 6672.1 | 6064.3 | [28 empty] | 735.5 | 596 | 559.3 | 721 | 5315.5 | 6660.1 | 2227.2 | 7605.1 | [264 empty] | 35.2598 | [5 empty] | 41.9899 | [5 empty] | 4.5089 | [5 empty] | 10.54 | [5 empty] | 6.8896 | [11 empty] | 6.7475 | [27 empty] | 25190.3807 | 581.0455 | 6.8896 | 0 | 0 | 0 | 0 | 0 | 6.7475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508654.528 | 10053.792 | 0 | 498600.736 | 13.1833 | 6.8896 |  | 6.7475 |  |  |  | 35.2598 | 41.9899 | 4.5089 | 10.54 | 507601.4 | [5 empty] | 508654.528 | 508654.528 | 10053.792 | 498600.736
2025-06-25 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 241054 | 6:23 | 18:59 | 2088.4 | 5441.9 | 4126.4 | 6313.2 | 6313.6 | 5944.4 | 4167.2 | 5467.4 | 6072.6 | 5934.8 | 6506 | 6275.2 | 5910.5 | 4074.2 | 2042.1 | 7011.4 | 6563.4 | 6430.6 | 6035.7 | 6480.5 | 6334 | 6298.2 | 5588.9 | 6328.8 | 5625.4 | 6625 | 6588.8 | 5588.6 | 5733 | 4422.3 | 4619.3 | 5017.4 | 3134.8 | 3734.4 | 3045.6 | 3183.9 | 3770.8 | 3750.2 | 3325.9 | 3315.7 | 3658.7 | 3883.1 | 3698.1 | 3525.2 | 1919.1 | 2040.6 | 3795 | 3757.7 | 3636.7 | 2922 | 3698.4 | 3886.9 | 3683.1 | 3586.3 | 3813.4 | 3710 | 3536.8 | 3535.1 | 3722.1 | 3467.5 | 3261.7 | 1800.1 | 3724.1 | 3631.3 | 3295 | 3656.9 | 3431.9 | 3651 | 3374.4 | 3507.7 | 3657.4 | 3528 | [12 empty] | 3839 | 3455 | 3822.3 | 3850.9 | 3885.4 | 3802.9 | 3814.4 | 3869.1 | 6303.7 | 6015.9 | 6352.9 | 5080.3 | 6337 | 4708.2 | 4266.6 | 5223.3 | 3673.8 | 5871.7 | 5460.1 | 2393.1 | 5459 | 4726.2 | 6014.9 | 4427.1 | 6550.1 | 6627.9 | 6079.9 | 6794.5 | 6317.9 | 6108.8 | 6556 | 6364.6 |  |  |  |  | 5951.6 | 5499.3 | 4532 | 5002.2 | 6065.7 | 5157.7 | 3848.3 | 5115.4 | 5187 | 5137 | 6208.4 | 5489 | 5767.4 | 4198.8 | 4888.4 | 4935.4 | 6816.4 | 5094.8 | 3774.6 | 6601.7 | 3937.5 | 6103.7 | 1704.7 | 6935 | [8 empty] | 1501 | 5437.9 | 4553.1 | 5139.1 | 3699.9 | 3729.9 | 3829.1 | 5228.3 | 3964.9 | 1400.1 | 5690.5 | 1451.2 | 3265.4 | 5945.1 | 5663 | 4500.9 | [64 empty] | 5754.5 | 6191.9 | 6768.8 | 6255.9 | 5489.6 | 2778.7 | 6371.9 | 6268.8 | 4666.9 | 5977.3 | 5585.9 | 6375.7 | 6682.2 | 6549.7 | 6244.1 | 5093.2 | [160 empty] | 34.6453 | [5 empty] | 41.9221 | [5 empty] | 4.1952 | [5 empty] | 9.07 | [5 empty] | 6.1945 | [11 empty] | 6.0842 | [27 empty] | 25943.079 | 596.4353 | 6.1945 | 0 | 0 | 0 | 0 | 0 | 6.0842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752698.272 | 15389.824 | 0 | 737308.448 | 12.6 | 6.1945 |  | 6.0842 |  |  |  | 34.6453 | 41.9221 | 4.1952 | 9.07 | 761284.8 | [5 empty] | 752698.272 | 752698.272 | 15389.824 | 737308.448
2025-06-26 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 241054 | 6:16 | 17:56 | 2148.9 | 5555.1 | 4246.4 | 6495.3 | 6917.1 | 5836.7 | 4413.7 | 5847.7 | 5329.6 | 5246.9 | 5467.4 | 5967.4 | 5635.7 | 3617.5 | 1799.2 | 6137.1 | 4476.7 | 4358.2 | 4083.6 | 4377.4 | 4274.8 | 4313.2 | 3836.3 | 4330.8 | 5048.6 | 5914.3 | 5927.2 | 5630.8 | 5189.8 | 4432.1 | 4224.1 | 4589.6 | 2933.9 | 3611.2 | 2838.6 | 3003.3 | 3631.5 | 3640 | 3185.7 | 3174.9 | 3549.1 | 3746.2 | 3581.9 | 3406.8 | 1699.9 | 1797.9 | 3673 | 3838.5 | 3533.5 | 2599.4 | 3586.4 | 3749.8 | 3564.5 | 3467.2 | 3692.5 | 3607 | 3425.7 | 3769.4 | 3611.1 | 3548.1 | 3106.1 | 1598.1 | 3617.4 | 3537.2 | 3163.4 | 3550.6 | 3311.1 | 3549.1 | 3244.1 | 3394.7 | 3555.9 | 3423.7 | [12 empty] | 4305.9 | 3079.2 | 4297.2 | 4466.2 | 4504.2 | 4254.1 | 4159.2 | 4374.8 | 5638.8 | 5049 | 5705.4 | 5553.8 | 6027.3 | 4263.3 | 3827.5 | 5673.4 | 3318.2 | 5265.5 | 4883.8 | 2647.1 | 4901 | 4241.4 | 5079.3 | 4957.7 | 5762.1 | 5826 | 5363.8 | 5993.6 | 5560.1 | 5399.2 | 5789 | 5605.8 |  |  |  |  | 5339.8 | 5326.4 | 5301.4 | 4425.2 | 5356 | 4602.8 | 4202.2 | 4702.9 | 5070 | 4618.8 | 5539.4 | 4863.8 | 5068.2 | 3703.5 | 4329.6 | 4692.3 | 7134 | 5329.5 | 3911.4 | 6876.3 | 4104.5 | 6364.3 | 1788.6 | 7233.8 | [8 empty] | 1326.8 | 5337.3 | 5329.2 | 4592.5 | 3385.6 | 3305.2 | 3406.1 | 5731.2 | 3444 | 1629.3 | 5659.7 | 1297.9 | 2625.8 | 5671.8 | 5056.3 | 5074.6 | [64 empty] | 5151.9 | 5594.7 | 6043.2 | 5570.4 | 4665.3 | 2486.2 | 5743.9 | 5669.6 | 4160.7 | 5394.4 | 5006.8 | 5712 | 5978.9 | 5857.9 | 5630.1 | 4377.8 | [160 empty] | 33.3947 | [5 empty] | 39.7898 | [5 empty] | 3.086 | [5 empty] | 14.8 | [5 empty] | 5.6114 | [11 empty] | 5.5484 | [27 empty] | 26715.795 | 613.2391 | 5.6114 | 0 | 0 | 0 | 0 | 0 | 5.5484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772715.968 | 16803.776 | 0 | 755912.192 | 11.6667 | 5.6114 |  | 5.5484 |  |  |  | 33.3947 | 39.7898 | 3.086 | 14.8 | 709762.3 | [5 empty] | 772715.968 | 772715.968 | 16803.776 | 755912.192
2025-06-27 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 241054 | 6:12 | 18:41 | [8 empty] | 4140.8 | 4063.1 | 4429.1 | 4575.4 | 4296.3 | 2670.3 | 1315 | 4772.5 | 3830.8 | 3726.2 | 3509.5 | 3755.9 | 3680.8 | 3670.6 | 2770.8 | 3680.6 | 3821.1 | 4509 | 4497.1 | 4237.8 | 3894.8 | 3301.7 | 3137.2 | 3436.2 | 2229 | 3041.1 | 2179.6 | 3205.6 | 3032.4 | 3090.1 | 2480 | 2483.3 | 2860.1 | 3142 | 2944.8 | 2688.6 | 1459.5 | 1326.7 | 2101.7 | 4043 | 2869.4 | 1985.4 | 2940.9 | 3188.8 | 2931.7 | 158.7 | 3101 | 2968.7 | 114 | 2729.7 | 127.8 | 2603.3 | 2309.9 | 1144.4 | 2966.4 | 2805.7 | 2438.9 | 2468.2 | 2567.6 | 2812.6 | 2488.4 | 2638.6 | 2849.2 | 2695.4 | [20 empty] | 3122.1 | 2986.4 | 3154.3 | 3058 | 3357 | 2335 | 2082.9 | 3111.5 | 2462.2 | 3886.9 | 3499.6 | 1981.3 | 3736.4 | 3235.6 | 4122.3 | 3684.4 | 3122.3 | 3151.7 | 2882.7 | 3229.7 | 3003.7 | 2915 | 3132.5 | 3038.3 |  |  |  |  | 2908.8 | 2903.1 | 2900.3 | 2416.7 | 2935.1 | 2506.9 | 2291.6 | 2567.9 | 2743.1 | 2482.2 | 3020 | 2625.1 | 2773.5 | 2023.5 | 2352 | 2549.6 | [16 empty] | 468.8 | 2892.5 | 2872.5 | 2458.8 | 1762.2 | 1716.2 | 1817.9 | 3095.6 | 1844.3 | 838.7 | 1965 | 664 | 1396.9 | 3088.5 | 2756.3 | 2757.5 | [64 empty] | 2249.7 | 2440.1 | 2706.9 | 2500.8 | 2154.1 | 1099.9 | 2502.7 | 2464.5 | 2251.8 | 2938.1 | 2739.7 | 3149 | 3266.4 | 3211 | 3021.9 | 1919.1 | [160 empty] | 29.777 | [5 empty] | 35.7899 | [5 empty] | 2.339 | [5 empty] | 9.81 | [5 empty] | 4.1085 | [11 empty] | 4.0081 | [27 empty] | 27196.7057 | 628.4048 | 4.1085 | 0 | 0 | 0 | 0 | 0 | 4.0081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480910.72 | 15165.728 | 0 | 465744.992 | 12.4833 | 4.1085 |  | 4.0081 |  |  |  | 29.777 | 35.7899 | 2.339 | 9.81 | 377237.4 | [5 empty] | 480910.72 | 480910.72 | 15165.728 | 465744.992
2025-06-28 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 241054 | 6:26 | 19:20 | [8 empty] | 6546.6 | 6327.3 | 6862.6 | 7046.3 | 6793 | 4338.2 | 2216.8 | 6965.3 | 6867.9 | 6741.6 | 6148.7 | 6804.7 | 6668 | 6632.5 | 5918.1 | 6598.6 | 2995.8 | 3485.1 | 3104.1 | 3323.9 | 3091.5 | 2629 | 2504.5 | 2439.1 | 3223.4 | 3939.5 | 3215 | 3306.9 | 3927.9 | 3963.9 | 3428.3 | 3463.3 | 3827.6 | 4063.7 | 3848.8 | 3666.5 | 2029.6 | 2176.9 | 3976.4 | 3939.2 | 3781.3 | 2895.8 | 3859.6 | 4069.4 | 3820.4 | 3708 | 3980.5 | 3875.7 | 1921 | 2876.7 | 3746.9 | 3105 | 3243.5 | 1827.9 | 3900.6 | 3730.4 | 3566.2 | 3810.3 | 3520.8 | 3774.6 | 3448.4 | 3576.5 | 3791.4 | 3614.2 | [20 empty] | 1934.1 | 1845.4 | 1958.2 | 1883 | 2066.3 | 1435 | 1288.3 | 1933.6 | 3862 | 6046.3 | 5495.9 | 3173.3 | 5817.7 | 5034.9 | 6317.4 | 5683.1 | 2237.3 | 2255.9 | 2087.5 | 2343.6 | 2177.1 | 2111.6 | 2246.4 | 2160.2 |  |  |  |  | 2521.4 | 3048.9 | 3031 | 2543.6 | 3112.8 | 2621.1 | 2374.4 | 2675.7 | 6303 | 5720.4 | 6931.9 | 6182.4 | 6396.9 | 4636.5 | 5372.7 | 5780 | [16 empty] | 1578.6 | 6328.6 | 6252.2 | 1856.9 | 3918.9 | 3834.2 | 4035.7 | 5841.6 | 3968.6 | 1848.1 | 6451.9 | 891.7 | 3022.2 | 6581.6 | 5962.3 | 5284.8 | [72 empty] | 4877.9 | 6346 | 5967.8 | 6835.8 | 7079.6 | 6950.9 | 6512.3 | 5048.4 | [160 empty] | 30.8834 | [5 empty] | 35.88 | [5 empty] | 3.3712 | [5 empty] | 7.35 | [5 empty] | 4.6658 | [11 empty] | 4.3544 | [27 empty] | 28084.4612 | 643.2659 | 4.6658 | 0 | 0 | 0 | 0 | 0 | 4.3544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 887755.52 | 14861.088 | 0 | 872894.432 | 12.9 | 4.6658 |  | 4.3544 |  |  |  | 30.8834 | 35.88 | 3.3712 | 7.35 | 522414.6 | [5 empty] | 887755.52 | 887755.52 | 14861.088 | 872894.432
2025-06-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 241054 | 6:18 | 19:20 | [32 empty] | 2611.1 | 3641.9 | 2436.7 | 2689.9 | 3625 | 3686.6 | 2936.2 | 2947.6 | 3577.2 | 3925.3 | 3635.8 | 3357.9 | 1429.5 | 1521.2 | 3822.9 | 3758.3 | 3408.8 | 2154.6 | 3495.5 | 3784.6 | 3489.4 | 3442.2 | 3685.5 | 3529.6 | 2760.9 | 3247.1 | 3362.5 | 3038.4 | 2607.6 | 1214.2 | 3513 | 3306.8 | 2786.8 | 3371.9 | 2973.4 | 3286.9 | 2841.2 | 3049.3 | 3346.4 | 3144.9 | [36 empty] | 3759.9 | 3807.6 | 3501.4 | 3899 | 3598.1 | 3476.9 | 3763.9 | 3659.6 |  |  |  |  | 4781.8 | 4916.8 | 3996.4 | 4094.4 | 4933.8 | 4095.6 | 3871.6 | 3537.1 | 4376.8 | 3895.2 | 4916.4 | 4500.7 | 4426.8 | 3430.4 | 3990.3 | 3997.7 | [104 empty] | 3655.9 | 4750.1 | 4432.1 | 5023.8 | 5198.9 | 5093.2 | 4817.9 | 3228.9 | [160 empty] | 30.4445 | [5 empty] | 35.99 | [5 empty] | 3.8201 | [5 empty] | 8.7 | [5 empty] | 4.2911 | [11 empty] | 4.0604 | [27 empty] | 28857.3487 | 657.7788 | 4.2911 | 0 | 0 | 0 | 0 | 0 | 4.0604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772887.488 | 14512.864 | 0 | 758374.624 | 13.0333 | 4.2911 |  | 4.0604 |  |  |  | 30.4445 | 35.99 | 3.8201 | 8.7 | 257873.6 | [5 empty] | 772887.488 | 772887.488 | 14512.864 | 758374.624
2025-06-30 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 241054 | 6:44 | 18:45 | 2001.4 | 5075.8 | 3879.2 | 5039.8 | 6296.2 | 0 | 3997.6 | 5214 | 5690.9 | 5589.4 | 6082.9 | 6298 | 5973.3 | 3897.3 | 1934.8 | 6554.5 | 6047.9 | 5875.7 | 5526.9 | 5930.7 | 5829.9 | 5839 | 5171.4 | 5803.9 | 5306.5 | 6073.2 | 6041.6 | 5763.4 | 5366.5 | 4337.6 | 4281.1 | 4665.7 | 3113.2 | 4746.1 | 2906.3 | 3156 | 4602.8 | 4743.2 | 3601.3 | 3644.8 | 4600.9 | 5313.9 | 4678.3 | 4223.9 | 1758.7 | 1861 | 4956 | 4871.2 | 4436 | 2748 | 4580.9 | 5052.6 | 4598 | 4340 | 4865.9 | 4676.9 | 4141.9 | 4318.8 | 4516.1 | 4024.4 | 3366 | 1589.3 | 4738 | 4209 | 3550 | 4446.8 | 3832.3 | 4272.8 | 3616 | 4047.7 | 4369.2 | 4078.5 | [12 empty] | 6108.9 | 4387.8 | 5978.4 | 5961 | 1977.4 | 224.9 | 236.4 | 248.8 | 5938.4 | 5695.6 | 6017.7 | 4851.3 | 6360.8 | 4479.1 | 4045 | 5961.9 | 3466.2 | 5387 | 4899.4 | 2869.1 | 5239.8 | 4510.5 | 5694.9 | 5097.1 | 5469.1 | 5482.8 | 5072.8 | 5711.9 | 5331.1 | 5156.8 | 5560 | 5388.2 |  |  |  |  | 4881.2 | 4896.7 | 4888.5 | 4128.6 | 5004.3 | 4237 | 3874 | 4310.6 | 4643.3 | 4184.7 | 5164 | 4686.7 | 4803.4 | 3587.7 | 4141.5 | 4320.2 | 6271.9 | 4619.7 | 3469.2 | 6049.4 | 3602 | 5568.4 | 1567.4 | 6368.6 | [8 empty] | 1441.4 | 5624 | 5549.2 | 3943.2 | 3479.2 | 3381.8 | 3553.8 | 5907 | 3623.3 | 1744.2 | 5872.6 | 1260.5 | 2763.8 | 5921.4 | 5346.2 | 5372.3 | [48 empty] | 4331.2 | 1877.4 | 2798.3 | 897.5 | 816.9 | 2313.1 | 1765 | 3015.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1239.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4037.4 | 5249.5 | 4908.6 | 5699.7 | 5967.4 | 5901.6 | 5536.7 | 5259.8 | 872.8 | 0 | 0 | 0 | 0 | 0 | 655.1 | 738.2 | [120 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 31.6847 | [5 empty] | 37.0123 | [5 empty] | 4.2296 | [5 empty] | 8.67 | [5 empty] | 4.3656 | [11 empty] | 5.14 | [27 empty] | 29907.5886 | 671.3213 | 4.3656 | 0 | 0 | 0 | 0 | 0 | 5.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050239.936 | 13542.56 | 0 | 1036697.376 | 12.0167 | 4.3656 |  | 5.14 |  |  |  | 31.6847 | 37.0123 | 4.2296 | 8.67 | 709323.3 | [5 empty] | 1050239.936 | 1050239.936 | 13542.56 | 1036697.376
2025-07-01 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 241054 | 6:24 | 19:18 | 2279 | 5694.7 | 4425.2 | 6364.1 | 6775.7 | 0 | 4524.5 | 5798 | 6201.6 | 6124.8 | 6570.4 | 6748.9 | 6437 | 4399.9 | 2181.6 | 6979.1 | 6644.1 | 6513.6 | 6199.6 | 6693.4 | 6540.5 | 6437.3 | 5631.2 | 6294.2 | 5868 | 6722.7 | 6713.7 | 6407.8 | 6013.8 | 4992.9 | 4927.8 | 5303.3 | 3993.3 | 6121 | 3513.6 | 3969.3 | 6091.7 | 6281.4 | 4437.9 | 4467.9 | 1980.2 | 2099.4 | 6316.5 | 6138.2 | 5710.3 | 6647.1 | 5839.5 | 5182.5 | 5621.8 | 3194.7 | 5819.8 | 6663.5 | 5830.9 | 5464.9 | 6372.2 | 5958.2 | 5039.7 | 5289.8 | 5611.2 | 4907.9 | 3980.1 | 1802.9 | 5929.9 | 5925.9 | 4285.7 | 5635.9 | 4661.2 | 5406.9 | 4493.7 | 4913.8 | 5625.2 | 5143.9 | [12 empty] | 6550.7 | 4775.5 | 6427.7 | 6438.8 | 6714.1 | 6085 | 6381 | 6617.2 | 6388.8 | 6144.8 | 6431.9 | 5347.6 | 6747.1 | 4950.7 | 4482.7 | 6405.9 | 3855.4 | 5867.2 | 5367.9 | 3173.8 | 5727.5 | 4967.9 | 6108.9 | 5590.2 | 6492.8 | 6549.9 | 6096 | 6702.9 | 6190.7 | 6157.4 | 6552.4 | 6362.4 |  |  |  |  | 6110.5 | 6121.7 | 6100.6 | 5245.3 | 6150.8 | 5220.6 | 4970.3 | 5486.5 | 5868.1 | 5403.3 | 6341.3 | 5730.8 | 5932.8 | 4506.4 | 5165.2 | 5474.1 | 6731 | 5178.1 | 3921.3 | 6583.5 | 4130.6 | 6187.1 | 1791.8 | 6849.6 | [8 empty] | 1624.4 | 6115.1 | 6071.9 | 4430.9 | 3901.5 | 3797.8 | 3998.7 | 6440.3 | 4007.3 | 1923.9 | 6302.5 | 1400 | 3097.1 | 6390.5 | 5826.4 | 5820.6 | [48 empty] | 4293 | 1791 | 3062.7 | 988.7 | 901.2 | 2549.8 | 1949.2 | 3314.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1389.5 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4702.4 | 6097.5 | 5703.5 | 6555.1 | 6824.8 | 6709.5 | 6298.2 | 4871.4 | 953.5 | 0 | 0 | 0 | 0 | 0 | 0 | 464.3 | [152 empty] | 32.3273 | [5 empty] | 36.8766 | [5 empty] | 4.7993 | [5 empty] | 9.76 | [5 empty] | 6.2419 | [11 empty] | 6.0782 | [27 empty] | 30738.536 | 684.5293 | 6.2419 | 0 | 0 | 0 | 0 | 0 | 6.0782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 830947.328 | 13208.032 | 0 | 817739.296 | 12.9 | 6.2419 |  | 6.0782 |  |  |  | 32.3273 | 36.8766 | 4.7993 | 9.76 | 842223.7 | [5 empty] | 830947.328 | 830947.328 | 13208.032 | 817739.296
2025-07-02 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 334000 | 6:18 | 18:51 | 1344.8 | 3627.4 | 2664.6 | 4047.6 | 4377 | 0 | 2740.3 | 3607.1 | 3940 | 3886.5 | 4237.7 | 4370.3 | 4084.7 | 2664.1 | 1288.1 | 4546.1 | 0 | 0 | 0 | 0 | 4178.1 | 4171.6 | 3664.9 | 4119.8 | 3686.3 | 4343.5 | 4343.8 | 4096.8 | 3786 | 3075.1 | 3019.9 | 3272 | 2303.2 | 3877.9 | 2115.8 | 2398.6 | 3851.7 | 3999.3 | 2708.9 | 2715.5 | 1177.4 | 1242.9 | 4036.7 | 3896.9 | 3562.4 | 4295.1 | 3666 | 3190.8 | 3516.5 | 1942.7 | 3661.2 | 4298.4 | 3640.5 | 3364.3 | 4074.6 | 3759.1 | 3100.2 | 3307.9 | 3494.3 | 3001.2 | 2424 | 1067.3 | 3756 | 3394.3 | 2660.2 | 3547.4 | 2865 | 3364.6 | 2769.8 | 3024.6 | 3509.3 | 3106.2 | [8 empty] | 463.8 | 402.7 | 0 | 0 | 4194.2 | 2890.6 | 4103.9 | 4103.4 | 4324.6 | 3823.8 | 4071.3 | 4254.9 | 4078.7 | 3901.9 | 4118.1 | 3312.5 | 4376.2 | 3041.8 | 2732.5 | 4094.1 | 2359.1 | 3700.3 | 3337.5 | 1937 | 3600.8 | 3070.6 | 3797.3 | 3498 | 4144.5 | 4188.3 | 3844 | 4311.9 | 3924.1 | 3889.4 | 4205.7 | 4062.2 | 0 | 279.1 | 0 | 0 | 3844 | 3851.8 | 3842.3 | 3218.8 | 3891 | 3208.9 | 3049.9 | 3388.5 | 3686.4 | 3341 | 4045.5 | 3570.8 | 3731.3 | 2744.4 | 3181.4 | 3412.7 | 4325.2 | 3153.9 | 2358 | 4194 | 2477.9 | 3868.4 | 1034.8 | 4418.6 | 0 | 0 | 0 | 241.3 | 242.9 | 40.9 | 0 | 0 | 915.2 | 3878.2 | 3835.4 | 2711.3 | 2389.6 | 2322.1 | 2442.6 | 4160.6 | 2454.6 | 1151 | 4032.6 | 820.4 | 1885.9 | 4086.89 | 3662.8 | 3667.1 | [32 empty] | 1935.5 | 1699.5 | 609.5 | 916.5 | 1392.1 | 0 | 0 | 18 | 982.6 | 0 | 1495.1 | 1434.9 | 1802.8 | 797.7 | 0 | 0 | 2357.1 | 0 | 1872.8 | 568.4 | 514.9 | 1545.4 | 1168.5 | 2028 |  | 505.4 | 0 | 0 | 0 | 0 | 815.9 | 1414.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2916.6 | 0 | 0 | 4058.2 | 4222.4 | 4155.4 | 3911 | 2938.1 | 540.1 | 0 | 0 | 0 | 0 | 0 | 0 | 241.7 | 1934.5 | 0 | 0 | 0 | 0 | 1419 | 1935.1 | 1434.4 | 1212.2 | 1693.3 | 1660.1 | 1791 | 893.2 | 0 | 0 | 0 | 1979.4 | 2080.9 | 2068.4 | 0 | 1256.2 | 1083.3 | 1969.9 | 2107.1 | [8 empty] | 0 | 0 | 0 | 407.3 | 0 | 0 | 275.8 | 0 | 0 | 0 | 2239.8 | 0 | 0 | 0 | 0 | 381.2 | 1988.2 | 1719.2 | 2104.8 | 2107.4 | 2184.2 | 2402.2 | 2420.4 | 2178.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1510 | 1377 | 2040 | 1523 | 1740 | 756 | 1855 | 1573 | 0 | 0 | 0 | 0 | 487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1965 | 2431 | 2697 | 2723 | 2332 | 2454 | 2501 | 2180 | [48 empty] | 31.5946 | [5 empty] | 37.6566 | [5 empty] | 3.9681 | [5 empty] | 10.87 | [5 empty] | 3.6547 | [11 empty] | 3.5404 | [27 empty] | 31389.2732 | 698.6986 | 3.6547 | 0 | 0 | 0 | 0 | 0 | 3.5404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 650737.184 | 14169.248 | 0 | 636567.936 | 12.55 | 3.6547 |  | 3.5404 |  |  |  | 31.5946 | 37.6566 | 3.9681 | 10.87 | 598021.69 | [5 empty] | 650737.184 | 650737.184 | 14169.248 | 636567.936
2025-07-03 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 334000 | 6:38 | 19:06 | 1110.7 | 2602.9 | 2044.6 | 2821.3 | 2994.9 | 664 | 2030.4 | 2602.8 | 2770.8 | 2743.3 | 2924.1 | 3002.8 | 2812 | 2037.8 | 1060.6 | 3093.1 | 2486.1 | 2807 | 2680.8 | 2815 | 2890.2 | 2885.5 | 2613.8 | 2844 | 2616.9 | 2963 | 2981.4 | 2850.8 | 2686.4 | 2287.5 | 2244 | 2401.2 | 1785.3 | 2736.1 | 1666.1 | 1862.7 | 2722.6 | 2794.6 | 2058.5 | 2062.7 | 963 | 1019.7 | 2779.5 | 2752.8 | 2576.8 | 2973.7 | 2619.5 | 2359.9 | 2530.7 | 1526.6 | 2606.3 | 2950.8 | 2600.6 | 2440.9 | 2854.4 | 2678.1 | 2291.7 | 2517.6 | 2521.5 | 2232.7 | 1863.2 | 873.2 | 2712.7 | 2545.9 | 2067.8 | 2615.5 | 2146.9 | 2471.9 | 2096.7 | 2259.1 | 2515.4 | 2271.1 | [8 empty] | 894.9 | 785.1 | 0 | 0 | 2923.9 | 2196.5 | 2878.6 | 2878.1 | 2988.9 | 2721.4 | 2852.7 | 2949.9 | 2830.8 | 2737.9 | 2846.2 | 2419.8 | 2988 | 2555.8 | 2064.6 | 2831.9 | 1820.9 | 2631 | 2427.7 | 1519 | 2557.5 | 2276.2 | 2673.8 | 2520.8 | 2835.3 | 2853.6 | 2688.8 | 2928.5 | 2745.8 | 2732.8 | 2882.1 | 2795.9 | 0 | 520.2 | 0 | 0 | 2646.2 | 2666.5 | 2664.4 | 2343.1 | 2698.1 | 2320.1 | 2209.6 | 2408.9 | 2579.3 | 2396.1 | 2773.5 | 2533.8 | 2625.3 | 2660.9 | 2308.7 | 2424.8 | 2983.2 | 2348.8 | 1829.9 | 2899.3 | 1921.4 | 2731.9 | 863.2 | 3026.9 | 0 | 0 | 0 | 443 | 444.3 | 100.1 | 0 | 0 | 784.9 | 2725.3 | 2682.1 | 2038 | 1818.5 | 1768.5 | 1854.8 | 2822.2 | 1884.6 | 949.4 | 2804.2 | 676.5 | 1481.3 | 2823.3 | 2607.8 | 2616.4 | [32 empty] | 1753.5 | 1309.8 | 830.8 | 984 | 2204.1 | 0 | 0 | 161.4 | 2556.4 | 0 | 2266.8 | 2399.5 | 2588.5 | 1546 | 0 | 0 | 1523.7 | 686.7 | 1460.9 | 472.1 | 429.3 | 1222.2 | 935.6 | 1573.3 | 101.7 | 422.4 | 0 | 0 | 0 | 0 | 664.1 | 1126.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2312.2 | 2333.7 | 2176.2 | 3232.7 | 3370.9 | 3310.4 | 3096 | 2284.9 | 452 | 0 | 0 | 0 | 0 | 0 | 0 | 217.2 | 2619.8 | 0 | 0 | 0 | 0 | 2024.5 | 2639.7 | 2078.6 | 1778.9 | 2369.1 | 2320.5 | 2454.9 | 1344.9 | 0 | 0 | 0 | 2514.1 | 2634.8 | 2605.3 | 0 | 1744.3 | 1532.2 | 2532.7 | 2666.6 | [8 empty] | 0 | 0 | 0 | 580 | 0 | 0 | 400 | 0 | 0 | 0 | 2632 | 0 | 0 | 0 | 0 | 0 | 2240 | 1980 | 2340 | 2370 | 2439.5 | 2641.1 | 2636.9 | 2420 | [8 empty] | 1723.5 | 1607.5 | 2225.1 | 1744.3 | 1966.3 | 936.9 | 2075.6 | 1820.4 | [24 empty] | 2028.9 | 2412.5 | 2609.9 | 2628.1 | 2367.9 | 2466.1 | 2491.6 | 2242.6 | [48 empty] | 30.0325 | [5 empty] | 36.9544 | [5 empty] | 3.0713 | [5 empty] | 7.12 | [5 empty] | 3.1467 | [11 empty] | 3.1357 | [27 empty] | 31944.3955 | 712.6081 | 3.1467 | 0 | 0 | 0 | 0 | 0 | 3.1357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555122.304 | 13909.472 | 0 | 541212.832 | 12.4667 | 3.1467 |  | 3.1357 |  |  |  | 30.0325 | 36.9544 | 3.0713 | 7.12 | 495131.7 | [5 empty] | 555122.304 | 555122.304 | 13909.472 | 541212.832
2025-07-04 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 334000 | 6:16 | 19:17 | 1376.8 | 3866.5 | 3017.5 | 4346.5 | 4618.5 | 540.8 | 3014 | 2706.8 | 4210.4 | 3017.4 | 4410.9 | 4545.8 | 4143.2 | 3001.6 | 1310.6 | 4731.3 | 3764.6 | 4335.1 | 4294.8 | 4582.4 | 4510.7 | 4488.7 | 3996.7 | 4443.3 | 3981.3 | 4613 | 4628 | 4392.1 | 4046 | 3285.3 | 3158.3 | 3552.8 | 2547.6 | 4176.4 | 2425.6 | 2702.6 | 4076.8 | 4225.1 | 2973.3 | 3020.9 | 1082.3 | 1167.2 | 4143.4 | 4088.9 | 3765.9 | 4442.9 | 3879.7 | 3451.8 | 3706.7 | 2129 | 3936.5 | 4479.5 | 3874.2 | 3573.3 | 4200 | 3856.4 | 3413.5 | 3658.8 | 3702.4 | 3287.3 | 2696.2 | 891.8 | 4159.3 | 3822.3 | 3053.2 | 4872.4 | 3232.2 | 3753.1 | 3125.1 | 3319.4 | 3929.6 | 3363.2 | [8 empty] | 987 | 678 | 0 | 0 | 2666.8 | 2297 | 2901 | 2866 | 3007 | 2678 | 2977 | 2609 | 4330.6 | 4215.2 | 4426.5 | 3613.8 | 4595.3 | 3382.1 | 3068.5 | 4267.2 | 2709.8 | 4014.2 | 3650.2 | 2198.1 | 3861.6 | 3368.9 | 4054.6 | 3666.2 | 4380.5 | 4310 | 4119.8 | 4605.3 | 4170 | 4130.9 | 4428.7 | 4237.1 | 0 | 657 | 0 | 0 | 3857.9 | 3895.5 | 3882.2 | 3231.7 | 3987.9 | 3346.8 | 3248.7 | 3332.3 | 3903.4 | 3551.4 | 4202.3 | 3787.3 | 3913.9 | 2883.2 | 3328 | 3365 | 4562.6 | 3550.8 | 2720.6 | 4397.3 | 2857 | 4229.5 | 897.6 | 4652.5 | 0 | 0 | 0 | 515.4 | 501 | 104.7 | 0 | 0 | 628.5 | 4048.1 | 3991.2 | 2923 | 2562 | 2452.5 | 2103 | 3004 | 1704.3 | 845 | 2800.2 | 675.4 | 1407.4 | 2904.4 | 2766.9 | 2541.4 | [32 empty] | 1564.3 | 1206.1 | 800.4 | 879.4 | 2368.4 | 0 | 0 | 184.8 | 2503.1 | 0 | 2168.3 | 3144 | 2604 | 1408.1 | 0 | 0 | 1440.4 | 783.6 | 1440.4 | 560.3 | 668.4 | 1340.3 | 900.1 | 1607.1 | 108.3 | 500.1 | 0 | 0 | 0 | 0 | 564.4 | 1307.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2403.4 | 2375.3 | 2006.4 | 3166.4 | 3440 | 3207.4 | 3160.4 | 2366.8 | 501.3 | 0 | 0 | 0 | 0 | 0 | 0 | 109.4 | 2568.4 | 0 | 0 | 0 | 0 | 2140.4 | 2565 | 2001.2 | 1668.3 | 2004.1 | 2300.1 | 2368.3 | 1468.4 | 0 | 0 | 0 | 2788 | 2568 | 2700 | 0 | 1668.4 | 1306.4 | 2413.3 | 2563.6 | [8 empty] | 0 | 0 | 0 | 696.3 | 0 | 0 | 555 | 0 | 0 | 0 | 2788 | 0 | 0 | 0 | 0 | 0 | 2455 | 1864 | 2443 | 2178 | 2545 | 2756 | 2657 | 2434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1578 | 1788 | 2345 | 1856 | 1845 | 1008 | 1978 | 1489 | 0 | 0 | 0 | 0 | 578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2134 | 2455 | 2688 | 2697 | 2367 | 2745 | 2498 | 2466 | [48 empty] | 30.8381 | [5 empty] | 36.8877 | [5 empty] | 2.8563 | [5 empty] | 8.39 | [5 empty] | 5.8133 | [11 empty] | 5.6918 | [27 empty] | 32867.7689 | 721.154 | 5.8133 | 0 | 0 | 0 | 0 | 0 | 5.6918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 923373.408 | 8545.952 | 0 | 914827.456 | 13.0167 | 5.8133 |  | 5.6918 |  |  |  | 30.8381 | 36.8877 | 2.8563 | 8.39 | 643096.9 | [5 empty] | 923373.408 | 923373.408 | 8545.952 | 914827.456
2025-07-05 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 334000 | 6:27 | 19:26 | 1981.3 | 4015.4 | 3210.2 | 4475.7 | 4772.9 | 4510.6 | 3187.2 | 4068.7 | 4376.2 | 4323.7 | 4638 | 4745.2 | 4381.5 | 3206.2 | 1903.3 | 4873 | 4009.4 | 4586 | 4384.7 | 4641.3 | 4619.3 | 4612.3 | 4147 | 4545.6 | 4073.7 | 4716.4 | 4737.1 | 4515.4 | 4227.3 | 3564.4 | 3411.5 | 3755.1 | 2844.1 | 4236 | 2582.3 | 2914.7 | 4234 | 4567.1 | 3241.1 | 3234.3 | 1799.3 | 1860.3 | 4293.6 | 4279.8 | 3999.4 | 4644.9 | 4092.1 | 3683.9 | 3980.2 | 2515 | 4040.9 | 4600.6 | 4045.2 | 3831 | 4457.2 | 4174.5 | 3592.1 | 3834.8 | 3923.4 | 3543.2 | 3001.2 | 1727.3 | 4228.8 | 3944 | 3206.9 | 3948.4 | 3307.4 | 3818.2 | 3284.2 | 3535.7 | 3949 | 3550.8 | [8 empty] | 802.7 | 842.5 | 0 | 0 | 7098.3 | 4990.7 | 7054.3 | 7059.6 | 7341.2 | 6410.2 | 6910.5 | 7179.8 | 4386.4 | 4226.3 | 4406.8 | 3677 | 4621.6 | 3481.2 | 3241.9 | 4426.8 | 2875.4 | 4045.9 | 3770.2 | 2532 | 4005.6 | 3524.4 | 4137.1 | 3712.4 | 4242.8 | 4211.7 | 4017 | 4445 | 4111.4 | 4029.9 | 4524 | 4145.7 | 0 | 0 | 0 | 0 | 3989.6 | 4015.6 | 3991.1 | 3479.2 | 3924.6 | 3454.7 | 3522.3 | 3615.3 | 3859.2 | 3576.1 | 4120.4 | 3764.6 | 3870.1 | 3109.6 | 3469.3 | 3647.9 | 4709 | 3633.1 | 2867.6 | 4604.6 | 3083 | 4560.1 | 1678.4 | 4832.4 | 0 | 0 | 0 | 411.1 | 1116.6 | 230.7 | 0 | 0 | 1544.4 | 4199 | 4155.2 | 3193 | 2905.7 | 2853.5 | 2976.1 | 4406.5 | 2982.1 | 1783.3 | 4220 | 1421.5 | 2348.5 | 4566 | 4021.1 | 3951.8 | [32 empty] | 4345.4 | 3886.9 | 2570.3 | 2708.4 | 3469.1 | 0 | 0 | 1214.1 | 4342.9 | 3166.2 | 3491.1 | 4343.1 | 3947.6 | 2499.7 | 1638.2 | 3423.8 | 2874.8 | 1871.8 | 2454.6 | 1069.6 | 969.6 | 2149 | 1806.7 | 2581.1 | 308.4 | 954.4 | 0 | 0 | 0 | 0 | 1404.7 | 2036.2 | 1927.2 | 2298.9 | 2493.9 | 2489.9 | 0 | 0 | 0 | 0 | 4150.2 | 5245.2 | 4939.3 | 5600.7 | 5811.5 | 5700.8 | 5386.9 | 4144.6 | 976.3 | 0 | 0 | 0 | 0 | 0 | 0 | 491.9 | 4076.4 | 0 | 0 | 0 | 0 | 3247.8 | 4098 | 3297.6 | 2882.5 | 2684 | 3624.6 | 3694 | 2824.8 | 3330 | 3582.4 | 2987.3 | 3333.6 | 3537.2 | 3499.3 | 0 | 2756 | 2447.2 | 3864.8 | 4122.6 | [8 empty] | 0 | 0 | 0 | 762.5 | 0 | 0 | 927.5 | 0 | 3595 | 3286 | 6559.2 | 0 | 0 | 0 | 0 | 0 | 5576.5 | 4838.4 | 5893.4 | 5910.7 | 6094.4 | 6673.7 | 6758.4 | 6054.7 | 2041.5 | 4054 | 4858.5 | 2135.8 | 6947 | 6484.5 | 5385.7 | 5910.8 | 2835.1 | 2642.1 | 3497.7 | 2868.4 | 2142.7 | 1969.9 | 4166.8 | 3331.7 | 5251.4 | 3273.5 | 0 | 4387 | 1311.5 | 0 | 0 | 0 | 4418.6 | 2558.1 | 5266.9 | 5335.3 | 4766.9 | 4011.1 | 4903.8 | 3630.4 | 5131.7 | 5024.1 | 3386.3 | 6008.7 | 6116 | 0 | 6365.7 | 6136 | 4990.6 | 6160.6 | 6888.8 | 6888.3 | 0 | 0 | 0 | 0 | [48 empty] | 31.6394 | [5 empty] | 38.3487 | [5 empty] | 3.6162 | [5 empty] | 10.43 | [5 empty] | 6.6631 | [11 empty] | 6.4543 | [27 empty] | 34057.0245 | 727.5995 | 6.6631 | 0 | 0 | 0 | 0 | 0 | 6.4543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1189255.648 | 6445.472 | 0 | 1182810.176 | 12.9833 | 6.6631 |  | 6.4543 |  |  |  | 31.6394 | 38.3487 | 3.6162 | 10.43 | 986403.7 | [5 empty] | 1189255.648 | 1189255.648 | 6445.472 | 1182810.176
2025-07-06 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 334000 | 6:20 | 19:15 | 2023.5 | 3841.2 | 3144.4 | 4189.6 | 4437 | 4256.8 | 3124.4 | 3862.5 | 4108.4 | 4044.1 | 4314.9 | 4421.9 | 4153.2 | 3150.3 | 1947.9 | 4580 | 3783.6 | 4265.8 | 4080.4 | 4304.9 | 4299.5 | 4274.9 | 3892.3 | 4242 | 3862.9 | 4388.2 | 4378.9 | 4193.7 | 3942.2 | 3391.7 | 3205.4 | 3584.9 | 2814.2 | 4018.1 | 2676.7 | 2866.1 | 4014.6 | 4118.4 | 3155.3 | 3155.1 | 1794.9 | 1871.1 | 4079 | 4067.3 | 3819.4 | 4356 | 3895.9 | 3538.6 | 3781.8 | 2493.9 | 3874.3 | 4338.1 | 3872.3 | 3678.3 | 4183 | 3939.4 | 3481.6 | 3691.2 | 3729.7 | 3418.1 | 2908.9 | 1724 | 4040.1 | 3447.4 | 3184.8 | 3824.9 | 3236.1 | 3687.9 | 3178.7 | 3323 | 3749.6 | 3421.1 | [8 empty] | 1482.9 | 1498.9 | 0 | 0 | 4237.7 | 3287.1 | 4179 | 4181.7 | 4294.3 | 3942.8 | 4211.1 | 4300.4 | 4174.2 | 4051.3 | 4209.4 | 3568.5 | 4449.2 | 3414.2 | 3194.4 | 4218.9 | 2885.6 | 3912.2 | 3656.5 | 2541.1 | 3807.1 | 3441 | 3942.6 | 3635.6 | 4161.1 | 4184.5 | 3998.7 | 4348.7 | 4048.6 | 3931.9 | 4236.2 | 4130.9 | 0 | 972.8 | 0 | 0 | 3986 | 3998 | 3986.9 | 3449.4 | 3936.2 | 3500.9 | 3320.6 | 3639.2 | 3860 | 3524.6 | 4109.4 | 3786.1 | 3847.1 | 3147.8 | 3486.9 | 3648.8 | 4357.6 | 3482.9 | 2788.1 | 4245.6 | 2973.2 | 4056.7 | 1665.8 | 4440.5 | 0 | 0 | 0 | 2063.5 | 2495.5 | 208.6 | 0 | 0 | 1504.4 | 4024.1 | 3512.6 | 3154.5 | 2898.2 | 2852.5 | 2956.3 | 4224.2 | 2955.5 | 1772 | 3993.9 | 1332.8 | 2071.5 | 4092.5 | 3862.6 | 3794 | [32 empty] | 4169.2 | 3735.8 | 2583.7 | 2705.8 | 3383.3 | 0 | 0 | 1148.3 | 4171.3 | 3109.7 | 3415.5 | 4166.2 | 3892.5 | 2549.3 | 1639.2 | 3367.1 | 789.6 | 1865 | 651 | 951.4 | 865.6 | 2178.5 | 1785 | 2602.5 | 272.3 | 853.6 | 81.5 | 0 | 0 | 0 | 3112.8 | 2029.3 | 3085.6 | 3671.4 | 3952.5 | 4001.6 | 0 | 0 | 0 | 0 | 3283.1 | 3953.4 | 3779.8 | 4167.1 | 4291.1 | 4241.4 | 4064.6 | 3295.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3938.5 | 0 | 0 | 0 | 0 | 3239.6 | 3990.4 | 3240.3 | 3115 | 0 | 3596.4 | 3754.3 | 3277.2 | 3334.2 | 3569.2 | 3036 | 3766.6 | 3938 | 3924.9 | 0 | 2787.2 | 2526.9 | 3808.1 | 3997.2 | [8 empty] | 0 | 0 | 0 | 685 | 0 | 0 | 829.4 | 0 | 6531.9 | 5907.1 | 6102.5 | 0 | 0 | 0 | 0 | 0 | 5111.9 | 4444.5 | 5429.7 | 5408.7 | 5579.8 | 6117.2 | 6182.2 | 5494.5 | 1886.5 | 4033.2 | 5102 | 1969.2 | 6444.8 | 6015.2 | 4975.6 | 5476.1 | 2909.6 | 2713.6 | 3598.2 | 2981.9 | 3444.8 | 3691.4 | 4264.5 | 3315.6 | 4861.5 | 3005.3 | 0 | 5078 | 1273.5 | 0 | 0 | 0 | 4077.2 | 2367.2 | 4879.4 | 4877.2 | 4291.5 | 3594.5 | 4410.2 | 3269.3 | 4677.3 | 4655.8 | 3134.3 | 5522.7 | 5569.6 | 3068.8 | 5726.5 | 5535.8 | 3712.6 | 4405.6 | 4821.4 | 4820.6 | 4364.1 | 4532.8 | 4560.3 | 4120.7 | 1828.7 | 0 | 2090.3 | 4285.6 | 5706.1 | 4874.6 | 2375.7 | 4852.9 | 5676.8 | 3969.7 | 5838.2 | 3951.3 | 494.3 | 4424.7 | 5092.1 | 4986.2 | 5611 | 5976.6 | 5485.5 | 6180 | 3075.6 | 4228 | 5291.9 | 6473.5 | 4806.7 | 5271.1 | 5029.3 | 2222.8 | 3846.5 | 3129 | 198 | 1042.7 | 3218.8 | 1966.8 | 959.9 | 6771.8 | 3904.6 | 4218.2 | 5664.8 | 5813.8 | 4943.3 | 5140.3 | 5178.5 | 5178.8 | 1472.8 | 0 | 1494.4 | 4096.4 | 31.5823 | [5 empty] | 37.8755 | [5 empty] | 3.796 | [5 empty] | 9.25 | [5 empty] | 5.9959 | [11 empty] | 5.761 | [27 empty] | 35189.4188 | 742.7059 | 5.9959 | 0 | 0 | 0 | 0 | 0 | 5.761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1132394.304 | 15106.4 | 0 | 1117287.904 | 12.9167 | 5.9959 |  | 5.761 |  |  |  | 31.5823 | 37.8755 | 3.796 | 9.25 | 1136780.3 | [5 empty] | 1132394.304 | 1132394.304 | 15106.4 | 1117287.904
2025-07-07 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 334000 | 6:49 | 19:07 | 2070.4 | 3883.1 | 3218.4 | 4191.6 | 4411.3 | 4267 | 3189.1 | 3897.8 | 4128.1 | 4041.8 | 4285.1 | 4402.4 | 4165.2 | 3222.3 | 2014.2 | 4555.4 | 3773.9 | 4218.2 | 4072.3 | 4264.5 | 4229.1 | 4225.3 | 3894.4 | 4189.1 | 3912.5 | 4363.6 | 4367.6 | 4223 | 4019.4 | 3505.2 | 3394.1 | 3670 | 2912.1 | 4086.7 | 2764.7 | 2945.2 | 4055.9 | 4152.9 | 3235.6 | 3243.1 | 1852.8 | 1955.4 | 4107.5 | 4094.2 | 3858.7 | 4339 | 3907.2 | 3593.4 | 3775.7 | 2559.4 | 3834.3 | 4260.5 | 3869.3 | 3730.8 | 4181.8 | 3942.9 | 3490.9 | 3668.1 | 3710.1 | 3434 | 2980.7 | 1696.8 | 4009 | 3731.6 | 3266 | 3835.6 | 3285.8 | 3765.4 | 3309 | 3463.4 | 3835 | 3514.6 | [8 empty] | 1519.5 | 1532.1 | 0 | 0 | 4280.6 | 3423.4 | 4273.5 | 4278.3 | 4358.4 | 4001 | 4238.8 | 4340.8 | 4106.5 | 3997.8 | 4143.2 | 3581 | 3883.6 | 3516.8 | 3943.9 | 3668.4 | 2956.5 | 3893 | 3694.5 | 2660.1 | 3883.6 | 3516.8 | 3943.9 | 3668.4 | 4206.7 | 4235.5 | 4064.3 | 4402.7 | 4138.5 | 4044.2 | 4319.5 | 4226.3 | 0 | 1003 | 0 | 0 | 4043.4 | 4049.9 | 4050 | 3543.3 | 4093.7 | 3651.8 | 2969 | 3961.1 | 3963.9 | 3638.9 | 4204.8 | 3905.9 | 3966.8 | 3276.6 | 3579.8 | 3733.4 | 4449.2 | 3627 | 2937.1 | 4349.7 | 3109.9 | 4336.1 | 1660.4 | 4517.2 | 819.6 | 0 | 0 | 2375.4 | 2753.5 | 281.3 | 270.4 | 286.8 | 1512.4 | 3997.8 | 3554.6 | 3231.4 | 2935 | 2931.85 | 3030.1 | 4196.8 | 3036.9 | 1832.7 | 4003.7 | 1333.5 | 2167.7 | 4078.3 | 3859.2 | 3799.9 | [32 empty] | 4148.3 | 3755 | 2664.7 | 2781.4 | 3427.4 | 0 | 0 | 1356.3 | 4220.4 | 3199.4 | 3499.3 | 4193.7 | 3958.5 | 2671.9 | 1665.8 | 3487.5 | 2811.2 | 2020.4 | 2535.6 | 979.8 | 892.6 | 2332.6 | 1882.9 | 2763.1 | 270.7 | 854.7 | 1041.7 | 0 | 0 | 0 | 1327.41 | 2346.9 | 3157.6 | 3675.4 | 3902.2 | 4005.6 | 0 | 0 | 0 | 0 | 3363.2 | 3987.7 | 3834.7 | 4167.4 | 4255.8 | 4206.8 | 4069.9 | 3363.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4021.9 | 0 | 0 | 0 | 0 | 3373.1 | 4047.8 | 3383 | 3254 | 731.5 | 3704.3 | 3847.1 | 3319.2 | 3445 | 3600.9 | 3165 | 3824 | 3956.9 | 3955.2 | 0 | 2890.7 | 2628.3 | 3863.2 | 3984 | [8 empty] | 0 | 0 | 0 | 655 | 0 | 0 | 859.5 | 0 | 4334.8 | 4096.8 | 4192.8 | 0 | 0 | 0 | 0 | 0 | 3704.9 | 3393.5 | 3837.4 | 3831.9 | 3909.9 | 4170 | 4220.2 | 3910.5 | 1871.2 | 3150.3 | 3635.2 | 1958.7 | 4242.3 | 4056.6 | 3608.3 | 3810.1 | 3638 | 2819 | 3933.6 | 3734.6 | 3772.5 | 3810.8 | 4317 | 3421.3 | 4657.5 | 2890.7 | 0 | 4872.3 | 1215.1 | 0 | 0 | 0 | 3140.6 | 2194.2 | 3528.7 | 3540.7 | 3277.2 | 2916.1 | 3341.6 | 2726.6 | 3459.2 | 3432.2 | 2652.5 | 3853.6 | 3851.8 | 2874 | 3968.7 | 3872.4 | 3406.1 | 3890.5 | 4192 | 4174.9 | 3868.6 | 3982.2 | 3988.6 | 3686.7 | 1807.4 | 0 | 2085.7 | 3274.5 | 3953.7 | 3709 | 2251.8 | 3525.7 | 3944.8 | 3176.3 | 4013.4 | 3169.1 | 512.6 | 3384.3 | 3675 | 3639 | 3934.6 | 4086.4 | 3861.7 | 4149.6 | 2719 | 3704.5 | 3801.6 | 4313.6 | 3558.4 | 3771.7 | 3666 | 2208.4 | 3100.1 | 2734.5 | 208.1 | 1067.6 | 3128.6 | 2073.4 | 1066.8 | 4404.5 | 3109.3 | 3228.4 | 3904.4 | 3987 | 3597 | 3692.7 | 3669 | 3699.7 | 1492.8 | 0 | 1512.2 | 3215.4 | 31.0807 | [5 empty] | 37.9877 | [5 empty] | 4.1355 | [5 empty] | 8.83 | [5 empty] | 5.8486 | [11 empty] | 5.6344 | [27 empty] | 36247.4757 | 757.9527 | 5.8486 | 0 | 0 | 0 | 0 | 0 | 5.6344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1058056.864 | 15246.816 | 0 | 1042810.048 | 12.3 | 5.8486 |  | 5.6344 |  |  |  | 31.0807 | 37.9877 | 4.1355 | 8.83 | 1059589.16 | [5 empty] | 1058056.864 | 1058056.864 | 15246.816 | 1042810.048
2025-07-08 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 357326.545 | 6:24 | 19:20 | 1709.4 | 3743 | 3081.2 | 4068.7 | 4283 | 4123.9 | 3042.2 | 3764.4 | 3995.2 | 3959.1 | 4194.4 | 4287.7 | 4028.3 | 3080.8 | 1663.1 | 4403.3 | 3716.6 | 4146.6 | 3978.6 | 4170.5 | 4152.9 | 4150.5 | 3812.5 | 4123.8 | 3804.3 | 4264.2 | 4252.2 | 4080.6 | 3874.8 | 3354.4 | 3205.3 | 3548.4 | 2732.2 | 3899.7 | 2550 | 2771.2 | 3908 | 4012.4 | 3111.8 | 3097.3 | 1541.7 | 1606.4 | 3973.7 | 3952.8 | 4333.7 | 3434.8 | 3170.1 | 4025.7 | 3716.5 | 2359.8 | 3809.7 | 4227.6 | 3826.5 | 3641 | 4081.5 | 3866.3 | 3435.5 | 3632.2 | 3671.2 | 3370.1 | 2853.4 | 1413.4 | 3959.1 | 3697 | 3170.9 | 3765.8 | 3212.5 | 3685.5 | 3183.8 | 3349.3 | 3732.3 | 3427.5 | [8 empty] | 1378.6 | 1394.4 | 0 | 0 | 3997.7 | 3221 | 4051.6 | 4055.2 | 4146.2 | 3825 | 4059.2 | 4139.8 | 4083.9 | 3971.8 | 4112.7 | 3556.7 | 4333.7 | 3434.8 | 3170.1 | 4025.7 | 2854.8 | 3856.6 | 3467 | 2441.1 | 3797 | 3436.8 | 3871.3 | 3542.3 | 4013.4 | 3970.8 | 3807.5 | 4024.4 | 3882.8 | 3886.7 | 4047 | 3951.8 | 0 | 825.8 | 0 | 0 | 3870.8 | 3379.7 | 3962.2 | 3213.4 | 3869.2 | 3435.2 | 2421.4 | 3787.5 | 3699.8 | 3425.6 | 3945.1 | 3657.3 | 3717.3 | 3069.8 | 3358.9 | 3505.4 | 4199.3 | 3403.2 | 2661.6 | 4096.7 | 2872.2 | 3906.3 | 1319.6 | 4268.2 | 3305.7 | 2639.2 | 1929 | 2756.2 | 3124.5 | 2536.6 | 1453.5 | 1828.6 | 1266.5 | 3941.6 | 3483.3 | 3133.6 | 2808.8 | 2799.8 | 2909.5 | 4107.6 | 2933.5 | 1552.8 | 3903.6 | 1126.2 | 1891.9 | 4009.8 | 3798.4 | 3739.2 | [32 empty] | 4065 | 3679.1 | 2474.1 | 2629.6 | 3339.3 | 0 | 0 | 1271.9 | 4009.4 | 3046.9 | 3352.1 | 3988.7 | 3744.4 | 2390.5 | 1339 | 3281.2 | 1015.8 | 1674.8 | 2399.5 | 794.2 | 725.7 | 2036.8 | 1575.1 | 2544 | 215.2 | 706.5 | 862.4 | 0 | 0 | 0 | 1095.9 | 2223.7 | 3105.8 | 3637 | 3889 | 3911 | 0 | 0 | 0 | 0 | 3218.1 | 3816.8 | 3667.4 | 4015.8 | 4142.9 | 4104.7 | 3971.5 | 3245.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3888.1 | 0 | 0 | 0 | 0 | 3134.1 | 3778.8 | 3121.4 | 3062.9 | 3690.3 | 3582.3 | 3719.6 | 3179.8 | 3319.8 | 3450.4 | 3009.6 | 3692.4 | 3852.3 | 3830.4 | 0 | 2703.1 | 2381.2 | 3687.3 | 3798.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.4 | 0 | 0 | 705 | 0 | 4211.8 | 3946.1 | 4022.2 | 0 | 0 | 0 | 0 | 0 | 3558.3 | 3228.8 | 3691.8 | 3698.9 | 3766.5 | 4014.8 | 4043.6 | 3738.9 | 1513.4 | 3165.3 | 3498.7 | 1577.2 | 4106.3 | 3913.1 | 3471.4 | 3683.7 | 2830.1 | 2569 | 3743.2 | 3544.1 | 3573.3 | 3596.2 | 4092.1 | 3241.3 | 3891.6 | 2407.6 | 0 | 4084.1 | 998.5 | 0 | 0 | 0 | 2944.2 | 1742 | 3350 | 3399.2 | 3074.2 | 2703.1 | 3126.8 | 2498.1 | 3265.1 | 3255 | 2402.9 | 3647 | 3636.7 | 2653.6 | 3719.1 | 3645.8 | 3250.9 | 3730 | 4005.6 | 3998.7 | 3709.6 | 3838.5 | 3858.2 | 3557 | 1466.7 | 2004.7 | 3069.1 | 3121.6 | 3810.6 | 3588.5 | 1899 | 3359.6 | 3790.4 | 2981.2 | 3874 | 2988.1 | 381.3 | 3392.8 | 3530.5 | 3460.9 | 3809.3 | 3989.3 | 3755 | 4028.2 | 2462.5 | 3126.8 | 3634.2 | 4159.4 | 3429.1 | 3639.8 | 3538 | 1833.7 | 2921 | 2479.3 | 143.5 | 848.7 | 3789.3 | 2619.5 | 836.5 | 4253.2 | 2920.1 | 3073.4 | 3770.8 | 3842.7 | 3458.2 | 3554.6 | 3521.2 | 3558.9 | 1177.6 | 0 | 1195.2 | 3043.9 | 31.3505 | [5 empty] | 37.7659 | [5 empty] | 3.7157 | [5 empty] | 7.51 | [5 empty] | 4.7119 | [11 empty] | 4.6055 | [27 empty] | 37274.873 | 772.7904 | 4.7119 | 0 | 0 | 0 | 0 | 0 | 4.6055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1027397.28 | 14837.728 | 0 | 1012559.552 | 12.9333 | 4.7119 |  | 4.6055 |  |  |  | 31.3505 | 37.7659 | 3.7157 | 7.51 | 1024729.2 | [5 empty] | 1027397.28 | 1027397.28 | 14837.728 | 1012559.552
2025-07-09 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 357326.545 | 6:26 | 19:12 | 1493.5 | 3890.6 | 3883.4 | 5865.6 | 4718.7 | 4536.1 | 3834.9 | 5208.8 | 4310.4 | 4184 | 6146.3 | 6359.3 | 4438.4 | 2981.8 | 1925 | 6606.7 | 2832.7 | 3346 | 3193.4 | 3352.3 | 4048.1 | 4029 | 3531.8 | 3990.3 | 1517.7 | 3261.6 | 3240 | 3003.4 | 5341 | 4230.7 | 3986.2 | 4479 | 1945.2 | 3244.4 | 1772 | 1962.8 | 5607.8 | 5820.8 | 3980.9 | 3988.5 | 1001 | 1055.8 | 3285 | 3250.4 | 5204.6 | 6254.5 | 5362.1 | 4696.8 | 2841.9 | 1532.2 | 2961.2 | 3246.9 | 5323.7 | 5010.6 | 5930.1 | 5456 | 2496.6 | 2735.3 | 2795.5 | 2416.8 | 3471.1 | 1589.7 | 5575.8 | 5044.3 | 2150.4 | 2816.6 | 2184.4 | 2700.5 | 3963.9 | 4302 | 5035.7 | 4347.7 | [8 empty] | 1425.6 | 1439.6 | 0 | 0 | 3379.4 | 2468.1 | 3497 | 3483.9 | 6111 | 5368.6 | 5820 | 6102.9 | 3392.3 | 3228 | 3418.6 | 2752 | 6406.5 | 4500.2 | 4004.3 | 5831.7 | 1942.3 | 3039.1 | 2549.1 | 1549.6 | 5095.9 | 4455.1 | 5338.1 | 4699.1 | 3613.9 | 3535.3 | 3345.4 | 3778.1 | 5844.1 | 5865.2 | 6209.2 | 5995.3 | 0 | 899.5 | 0 | 0 | 3433.5 | 2781.2 | 3702.1 | 2908 | 5752.8 | 4585.4 | 2879.8 | 5377 | 3279.9 | 2924.9 | 3597.8 | 3247.6 | 5453.7 | 4254 | 4668.3 | 4989.8 | 3823.6 | 2811.6 | 1991.6 | 3652.9 | 3599.3 | 5565.6 | 1546.2 | 6399.3 | 2653.6 | 2134.8 | 1555.6 | 2139.4 | 3995.1 | 3545.7 | 2531 | 2528.9 | 1365.4 | 5356.6 | 4412.3 | 3769.3 | 3428.2 | 3514 | 3508.4 | 6042.6 | 2204.4 | 1045.1 | 3343.5 | 745.8 | 2126.4 | 5758.2 | 5326 | 5173.9 | [32 empty] | 5910.9 | 5090.6 | 2949 | 3170.1 | 4405.3 | 0 | 0 | 1615.5 | 3774.4 | 2485 | 2873.5 | 3621.6 | 5452.7 | 2953.1 | 1615.3 | 4471 | 2728.9 | 1834.6 | 2725.5 | 877 | 801.9 | 2272.2 | 1730 | 2949.7 | 247.4 | 787.4 | 959.2 | 0 | 0 | 0 | 1243.2 | 2576.2 | 3914.7 | 4921.7 | 5473.2 | 5567.2 | 0 | 0 | 0 | 0 | 4255.2 | 5541.7 | 5045.2 | 5913.3 | 6143.5 | 6056.3 | 5740.1 | 4222.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5458 | 0 | 0 | 0 | 0 | 3646.4 | 4253.1 | 3189.6 | 3724.9 | 4920.2 | 4784.9 | 5102.6 | 4040.7 | 4397.1 | 4595.8 | 3722.5 | 5167.4 | 5492.5 | 5476 | 0 | 3380.3 | 2908.9 | 5292.4 | 5519.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 478.1 | 0 | 0 | 774.3 | 0 | 6140.9 | 5556.8 | 5746.5 | 0 | 0 | 0 | 0 | 0 | 4618.7 | 4007.4 | 4888 | 4906.7 | 5217.7 | 5742.4 | 5779.4 | 5118.1 | 1740.4 | 3742 | 4732 | 1817.4 | 5978.8 | 5449.7 | 4593 | 5041.3 | 3427.3 | 3058.6 | 5473.6 | 5410.9 | 5726.1 | 5127.9 | 5390.8 | 4385.2 | 4636.2 | 2889.7 | 0 | 4889.8 | 1219.3 | 0 | 0 | 0 | 3904.7 | 2092.5 | 4676 | 4729 | 4212.6 | 3541.3 | 5327.6 | 3199.8 | 4550.7 | 4465.7 | 3016.1 | 5366.8 | 5447.8 | 3437.1 | 5651.9 | 5445.2 | 4340.1 | 5340.36 | 6005.5 | 5965.1 | 4286.6 | 4503.9 | 4272.9 | 3984.2 | 1378.8 | 3308 | 3258.5 | 3261.4 | 5350.2 | 4939.1 | 2209.5 | 4428.1 | 4333.6 | 3018.9 | 4438.9 | 3005.5 | 2898 | 4566.2 | 4718.2 | 4553.4 | 3707.9 | 3977.5 | 3617.6 | 4028.1 | 2275.3 | 3132 | 3951.3 | 4857.6 | 3120.8 | 3424.2 | 3270.4 | 1431.2 | 3559.5 | 2896.5 | 172.6 | 962.5 | 3402.9 | 2179.9 | 778 | 4176 | 2879 | 2984 | 3654 | 3903 | 3111 | 3237.4 | 3211.2 | 3240.5 | 1360.4 | 0 | 1379.9 | 3802.8 | 31.8112 | [5 empty] | 36.7899 | [5 empty] | 4.5783 | [5 empty] | 10.05 | [5 empty] | 5.5533 | [11 empty] | 5.3991 | [27 empty] | 38478.6026 | 789.8519 | 5.5533 | 0 | 0 | 0 | 0 | 0 | 5.3991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1203729.664 | 17061.504 | 0 | 1186668.16 | 12.7667 | 5.5533 |  | 5.3991 |  |  |  | 31.8112 | 36.7899 | 4.5783 | 10.05 | 1206750.26 | [5 empty] | 1203729.664 | 1203729.664 | 17061.504 | 1186668.16
2025-07-10 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 363511.955 | 6:19 | 19:13 | 2020.9 | 4185.4 | 3372 | 4608.8 | 4873.6 | 4671.8 | 3281.8 | 4181.1 | 4519.1 | 4458.7 | 4777.6 | 4890.8 | 4574.4 | 3381.7 | 1967.1 | 5025.3 | 4169.9 | 7416.3 | 4506.8 | 4763.5 | 4747.1 | 4754.2 | 4314.1 | 4708.9 | 4286.2 | 4912.4 | 4912.8 | 4699.6 | 4418.1 | 3715.2 | 3532.1 | 3883.7 | 2996.3 | 4372.1 | 2787.7 | 3023.6 | 4360.9 | 4485.8 | 3397.1 | 3577.2 | 1810.6 | 1895.5 | 4446.8 | 4455.4 | 4196.9 | 4818.4 | 4291.3 | 3877.6 | 4164.2 | 2708.7 | 4295.2 | 4832 | 4287.4 | 4088.4 | 4625.4 | 4359.8 | 3826.1 | 4006.3 | 4027.9 | 3729.9 | 3121 | 1659.6 | 4524.5 | 4175.7 | 3501.1 | 4298.3 | 3543 | 4216.9 | 3503.5 | 3726.1 | 4202.1 | 3766.1 | [8 empty] | 1412.4 | 1427.7 | 0 | 0 | 4484.4 | 3536.5 | 4577 | 4591.2 | 4692.5 | 4273.3 | 4505.5 | 4665.5 | 4658.2 | 4517.5 | 4717.3 | 4007.5 | 4995.5 | 3823.8 | 3299.2 | 4593.9 | 3442.8 | 4378.8 | 3817.5 | 2702.5 | 4245.1 | 3782.2 | 4391.2 | 3979.1 | 4634.5 | 4560 | 4362.6 | 4774.7 | 4418.1 | 4366.9 | 4669.9 | 4571.1 | 0 | 955 | 0 | 0 | 4456.4 | 3824.5 | 4755.3 | 3925.1 | 4589.1 | 3891 | 2769.2 | 4360.8 | 4276.9 | 3923.4 | 4557.3 | 4240 | 4267.7 | 3553.9 | 3799.2 | 3985.3 | 4799.5 | 3794.4 | 2951.5 | 4696.7 | 3158.4 | 4388.1 | 1597.1 | 4863.1 | 3674.2 | 3128.7 | 2354.3 | 3099.3 | 3500.7 | 3145.3 | 3772.6 | 2915.1 | 1483.5 | 4512.7 | 3909.7 | 3528.5 | 3140.2 | 3225.6 | 3236.8 | 4723.8 | 3218 | 1788.6 | 4420.7 | 1317.4 | 2197.1 | 4626.8 | 4434.2 | 4233.8 | [32 empty] | 4618 | 4152.5 | 1788.4 | 2902.6 | 3699.6 | 0 | 68.7 | 1806.4 | 4550.3 | 3342.2 | 3731.8 | 4435.2 | 4293.3 | 2676.3 | 1640.7 | 3684 | 3078.3 | 1944.9 | 2686.9 | 947.3 | 867.4 | 2353.4 | 1713.3 | 2853.9 | 207.9 | 850.5 | 1031.2 | 0 | 0 | 0 | 1331.6 | 2566.9 | 3907.7 | 4020.2 | 4298 | 4484.3 | 0 | 0 | 0 | 0 | 3577.2 | 4344.7 | 4046.8 | 4623.2 | 3719.2 | 4340.1 | 4184.6 | 3266.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4504.9 | 0 | 0 | 0 | 0 | 4048 | 4551.6 | 3670 | 3356.3 | 4096.7 | 4006.3 | 4023.2 | 3527.1 | 3729.6 | 3766.8 | 3323.7 | 4131.5 | 4397 | 4379 | 2440.6 | 3031.9 | 2710.9 | 4197.1 | 4335.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609 | 0 | 0 | 984.5 | 0 | 5016.1 | 4644.4 | 4752.3 | 0 | 0 | 0 | 0 | 0 | 4039.6 | 3612.9 | 4185.1 | 4192.9 | 4327 | 4693.3 | 4739.3 | 4319 | 2177.8 | 4229.8 | 5215 | 2279 | 6429 | 6079 | 5129 | 5589 | 3175.6 | 2853.6 | 4451.6 | 4369.4 | 4645.2 | 4235.8 | 4759.1 | 3623.6 | 4560 | 2830 | 0 | 4770 | 2920 | 0 | 0 | 0 | 3240 | 2550 | 3730 | 3740 | 3400 | 2950 | 3460 | 2760 | 3620 | 3600 | 2670 | 4120 | 4160 | 2910 | 4230 | 4130 | 3593 | 4231.2 | 4606.7 | 4596.3 | 4195 | 4361.6 | 4341.3 | 3969.7 | 1750 | 3530 | 3470 | 3440 | 4330 | 4060 | 2210 | 3750 | 4370 | 3340 | 4450 | 3300 | 3170 | 3830 | 3950 | 3900 | 4460 | 4700 | 4400 | 4760 | 2780 | 3530 | 4190 | 4920 | 3880 | 4220 | 4030 | 2110 | 3210 | 2740 | 180 | 1010 | 3870 | 2640 | 920 | 4390 | 2910 | 2980 | 3780 | 3940 | 3750 | 3950 | 3910 | 3790 | 1360 | 0 | 1380 | 3280 | 31.8931 | [5 empty] | 37.7899 | [5 empty] | 3.8842 | [5 empty] | 8.51 | [5 empty] | 5.7084 | [11 empty] | 5.5468 | [27 empty] | 39649.559 | 803.121 | 5.7084 | 0 | 0 | 0 | 0 | 0 | 5.5468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1170956.352 | 13269.056 | 0 | 1157687.296 | 12.9 | 5.7084 |  | 5.5468 |  |  |  | 31.8931 | 37.7899 | 3.8842 | 8.51 | 1183641.1 | [5 empty] | 1170956.352 | 1170956.352 | 13269.056 | 1157687.296
2025-07-11 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 363511.955 | 6:17 | 18:58 | 2023 | 3890.9 | 3188.2 | 4270.7 | 4496.9 | 4281.4 | 3545.6 | 3894.1 | 4143.8 | 4123.6 | 4170.7 | 4464.4 | 4158.3 | 3154.7 | 1875.4 | 4576.6 | 3854.7 | 4130 | 4191 | 4417 | 4410.4 | 4406.9 | 4022.3 | 4348.2 | 3951.5 | 4561.1 | 4588.7 | 4400.8 | 4161.9 | 3540.7 | 3548 | 3660.4 | 2821.8 | 4009.1 | 2676.1 | 2868.2 | 4007.2 | 4104 | 3151.9 | 3141.3 | 1818.5 | 1895 | 4072.6 | 4055.4 | 3828.3 | 4570.3 | 3891.3 | 3534.4 | 3821.3 | 2508.2 | 3917.3 | 4375.3 | 3880.2 | 3713.9 | 4223.6 | 3991.3 | 3528.5 | 3655.1 | 3705.5 | 3473.7 | 2960.3 | 1609.1 | 4043.3 | 3817.1 | 3243.9 | 3960.4 | 3341.9 | 3936.6 | 3321.3 | 3536.2 | 3919.8 | 3541 | [8 empty] | 1488.9 | 1505.6 | 0 | 0 | 4147.3 | 3321.2 | 4242.6 | 4253 | 4353.7 | 3971.6 | 4138.1 | 4318 | 4218.7 | 4099.6 | 4257.9 | 3628.7 | 4531.4 | 3492.8 | 3017.1 | 4132.6 | 2921.1 | 3992.8 | 3491.3 | 2576.9 | 3945.6 | 3430.7 | 4030.6 | 3644.2 | 4290.6 | 4236.1 | 4052.6 | 4442.2 | 4153 | 4074.5 | 4327.1 | 4215.8 | 0 | 991 | 0 | 0 | 4149.3 | 3552.5 | 4394.5 | 3648.7 | 4227.7 | 3613.9 | 2630.9 | 4067.4 | 3947.9 | 3621.2 | 4187.4 | 3888.8 | 3935 | 2288.7 | 3520.6 | 3680.4 | 4427.4 | 3536.1 | 2815.9 | 4342.3 | 3013.8 | 4094.7 | 1681.4 | 4505.8 | 3390 | 3054.7 | 2336.1 | 2893 | 3238.9 | 3212.6 | 3046 | 2735.9 | 1385.3 | 3999.2 | 3514.3 | 3207.3 | 2851.9 | 2930.8 | 2955.5 | 4232 | 2937.5 | 1694.5 | 3923.9 | 1245 | 1950.5 | 4095.9 | 3933.2 | 3712.5 | [32 empty] | 4098.6 | 3727.5 | 2618 | 2695.9 | 3361.3 | 0 | 1481.3 | 2419.9 | 4154.7 | 3097.8 | 3434.2 | 4033.6 | 3947.7 | 2536.3 | 1656.1 | 3405.4 | 2775 | 1812.9 | 2462.8 | 894.2 | 817.3 | 2117.5 | 1444.9 | 2568.2 | 251.1 | 798.8 | 964.8 | 0 | 0 | 0 | 1285.4 | 2345.6 | 3133.7 | 3701.7 | 3912.1 | 4030 | 0 | 0 | 0 | 0 | 3412.8 | 4104.8 | 3817.8 | 4267.8 | 3905.8 | 4295.4 | 4182.2 | 3380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.4 | 0 | 0 | 0 | 0 | 3684.3 | 4114.5 | 3339.5 | 3090.4 | 3744.9 | 3690 | 3872 | 3300.9 | 3510.2 | 3552.7 | 3130.6 | 3745 | 3961.1 | 3968 | 3199 | 2833.6 | 2556.2 | 3845.8 | 3938.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 526.2 | 0 | 0 | 843.2 | 0 | 4521.6 | 4215.8 | 4258.1 | 0 | 0 | 0 | 0 | 0 | 3758.3 | 3388.3 | 3885.7 | 3904.2 | 3995.3 | 4273.8 | 4345.1 | 3978.9 | 1837.3 | 3110 | 2688.8 | 1926.7 | 4415.5 | 4164.8 | 3629.6 | 3905.6 | 3824.4 | 3160.8 | 4192.7 | 3676.7 | 4486.1 | 4203.8 | 4496.4 | 3460.8 | 4827.8 | 3022.7 | 0 | 5145.6 | 4551.3 | 21.4 | 0 | 0 | 4668.4 | 2964.8 | 6246.3 | 5805.9 | 5331.6 | 4479.3 | 5202 | 3994.1 | 5538.7 | 5364.2 | 3663 | 6577.6 | 6722.9 | 4273.1 | 4998.9 | 6795.2 | 3396.4 | 3965.4 | 4301.2 | 4310 | 0 | 3988.9 | 4036.8 | 3714.6 | 4829.9 | 4442 | 4313.9 | 4319.8 | 5772.7 | 5312.5 | 2372.8 | 4819.3 | 5730.7 | 4016.5 | 3646.2 | 2444.5 | 3008 | 3321.6 | 5108.8 | 2378.9 | 5687 | 6090.5 | 5630.2 | 6354.1 | 3185.8 | 4317.4 | 5270.3 | 6564.2 | 5003.1 | 5467.8 | 5237.5 | 2313.4 | 3958.1 | 3213.7 | 105.4 | 1081.6 | 4967.9 | 3909.6 | 1064.7 | 6796 | 3897.2 | 4001.2 | 5481.5 | 5869 | 5740.6 | 6093.4 | 6002.3 | 5858.2 | 3829.7 | 6882.9 | 3043.3 | 4855.6 | 31.3342 | [5 empty] | 36.8899 | [5 empty] | 3.8624 | [5 empty] | 18.28 | [5 empty] | 6.0486 | [11 empty] | 6.0011 | [27 empty] | 40807.0682 | 818.2171 | 6.0486 | 0 | 0 | 0 | 0 | 0 | 6.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1157509.184 | 15096.064 | 0 | 1142413.12 | 12.6833 | 6.0486 |  | 6.0011 |  |  |  | 31.3342 | 36.8899 | 3.8624 | 18.28 | 1186180.5 | [5 empty] | 1157509.184 | 1157509.184 | 15096.064 | 1142413.12
2025-07-12 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 363511.955 | 6:19 | 19:16 | 1926.8 | 4233 | 3306.2 | 4725.6 | 4993 | 4766 | 3771.1 | 4270.4 | 4590.6 | 4466.1 | 4849.5 | 4932.4 | 4554.6 | 3327.1 | 1698.8 | 5124.5 | 4150.7 | 4757.1 | 4482.9 | 4808.4 | 4725.5 | 4784.1 | 4289.6 | 4722.9 | 4212 | 4941.1 | 4944.3 | 4697.8 | 4379.6 | 3007.7 | 3371 | 3790.9 | 2925.3 | 4454.4 | 2751.8 | 2975.9 | 4482.9 | 4617.9 | 3380.5 | 3390.3 | 1678.4 | 1750.8 | 4459.3 | 4436.8 | 4144.5 | 4874.7 | 4266 | 3819.2 | 4067.1 | 2518.4 | 4251.5 | 4864.9 | 4241.4 | 4034.6 | 4662.9 | 4554.9 | 3739.3 | 3899.1 | 3953.6 | 3660.4 | 1087.8 | 472 | 1038.8 | 2186.7 | 3240.5 | 4226.4 | 3445.5 | 4120.5 | 3400.6 | 3630.2 | 4079.9 | 3583.5 | [8 empty] | 0 | 0 | 0 | 0 | 4645 | 3558.7 | 4741.8 | 4754.7 | 4852.6 | 4388.9 | 4616.2 | 4871.2 | 4652.8 | 4472.7 | 4684 | 3906.5 | 4973.3 | 3659.8 | 3145.1 | 4568.3 | 2981.1 | 4113.4 | 3538.5 | 2512.6 | 4132.6 | 292.1 | 385.1 | 312.3 | 4857.1 | 4723.5 | 4544.3 | 5011.1 | 4582.7 | 4510.3 | 4858.6 | 4734.7 | 0 | 977.3 | 0 | 0 | 4616.7 | 3894.4 | 4982.1 | 4013 | 4772.7 | 3924.4 | 2683.6 | 4504.9 | 4345.1 | 52.5 | 4704.5 | 4303.6 | 4352.6 | 3521.4 | 3804.7 | 3988.4 | 3013.8 | 3857.2 | 2897.5 | 4889.4 | 3154.2 | 4524.2 | 1561.5 | 5084.8 | 4702.3 | 4256.4 | 2775.6 | 3634.1 | 4336.3 | 3752.6 | 4312.2 | 4017.7 | 1309.7 | 37.8 | 29.6 | 3275 | 2952.1 | 3046.6 | 3079 | 4707.2 | 3064.8 | 1648.5 | 4312 | 1240.2 | 1935.7 | 4525.1 | 4402 | 4039.4 | [32 empty] | 7077.6 | 6230.3 | 3706.1 | 3995.9 | 5556.3 | 0 | 1692.7 | 3531.6 | 6103.7 | 4085.3 | 4743.4 | 5987.6 | 5760.5 | 3011.8 | 1693.3 | 4662.8 | 2521.5 | 74.2 | 2287 | 750.1 | 835.1 | 2105.7 | 1402.8 | 2534.6 | 265.7 | 557.8 | 983.2 | 0 | 0 | 0 | 1248.3 | 2367.1 | 3392 | 4093.8 | 4427.8 | 4303.9 | 0 | 0 | 0 | 0 | 3530.3 | 4405.7 | 4052.8 | 4533.9 | 4123.3 | 4757.6 | 4458 | 3488.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5821.2 | 0 | 0 | 0 | 0 | 5056.2 | 5994.7 | 4275.4 | 3078.8 | 4079.4 | 4263.1 | 2324.4 | 4235.5 | 4690.6 | 4436.7 | 3630.4 | 6225 | 6953 | 6826 | 4988 | 4086 | 2973 | 6196 | 6515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 531.8 | 0 | 0 | 849.6 | 0 | 6564.2 | 5864 | 5853.7 | 0 | 0 | 0 | 0 | 0 | 4577.4 | 3869.7 | 5280.3 | 5336.3 | 5616.5 | 6063.6 | 6095 | 5417.8 | 1642.4 | 1969.9 | 3264.2 | 1707 | 3873.9 | 2662.5 | 3161.2 | 3993.2 | 4160.9 | 4274.3 | 3754.7 | 3800 | 4782.8 | 4467.4 | 4816.5 | 3818.7 | 5594.6 | 3772.1 | 1540.2 | 5842.9 | 5106.2 | 3738 | 4045.5 | 3019 | 4100.1 | 2705.8 | 5595.5 | 4962.2 | 4411.6 | 3454.6 | 4202.4 | 3371.6 | 4665.1 | 4649.3 | 3151.8 | 5596.8 | 1716.7 | 2473.8 | 5782.2 | 5661.1 | 3401.2 | 0 | 3270.6 | 4464.1 | 0 | 2996.8 | 0 | 2622.5 | 1638.6 | 4332.3 | 4231.7 | 4219.6 | 5468.8 | 5219.6 | 2363.8 | 0 | 0 | 3873.4 | 3340.8 | 2380.8 | 2939.8 | 3238.7 | 4950.4 | 2334.9 | 5651.4 | 6039.6 | 5527.8 | 6204.4 | 3006.1 | 4218.9 | 5118 | 6506.6 | 4808.2 | 5288.8 | 4935.3 | 2145.4 | 3819 | 3094.6 | 185.1 | 997.1 | 0 | 3071.2 | 549.4 | 6332.2 | 0 | 3589.9 | 4721.2 | 5006.3 | 4388 | 4455.3 | 4271.1 | 0 | 0 | 953.5 | 2687.2 | 3743.8 | 30.1634 | [5 empty] | 35.9787 | [5 empty] | 2.6214 | [5 empty] | 8.35 | [5 empty] | 6.1713 | [11 empty] | 6.0546 | [27 empty] | 41986.7827 | 832.8347 | 6.1713 | 0 | 0 | 0 | 0 | 0 | 6.0546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1179714.496 | 14617.632 | 0 | 1165096.864 | 12.95 | 6.1713 |  | 6.0546 |  |  |  | 30.1634 | 35.9787 | 2.6214 | 8.35 | 1199189.2 | [5 empty] | 1179714.496 | 1179714.496 | 14617.632 | 1165096.864
2025-07-13 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 363511.955 | 6:28 | 19:29 | 2161.1 | 4300.3 | 3383.8 | 4770.9 | 5028.1 | 4807.9 | 3863.7 | 4329.4 | 4643.8 | 4458.5 | 4894.33 | 4991.88 | 4636.7 | 3489 | 1911.6 | 5154.7 | 4237 | 4816.29 | 4538.7 | 4853.7 | 4829.5 | 4822.23 | 4354.5 | 4783.05 | 4289.42 | 4976.16 | 4971.19 | 4743.11 | 4444.22 | 3122.08 | 3517.38 | 3904.57 | 3112.39 | 4572.88 | 2948.9 | 3166.34 | 4585.8 | 4711.72 | 3534.9 | 3552.09 | 1945.29 | 2037.72 | 4609.06 | 4515.22 | 4186.5 | 4911.56 | 4374.84 | 3958.99 | 4179.36 | 2706.8 | 4357.66 | 4934.89 | 4393.75 | 4134.62 | 1073.99 | 4427.83 | 3870.16 | 4023.58 | 4056.69 | 3782.84 | 3169.2 | 1715.65 | 3461.81 | 4094.4 | 3405 | 4320.63 | 3580.2 | 4214.52 | 3535.82 | 3759.52 | 4185 | 3716.97 | [8 empty] | 0 | 0 | 0 | 0 | 4677.27 | 3689 | 4742 | 4809 | 3249.53 | 3880.51 | 4080.96 | 4284.75 | 4737.14 | 4573 | 4781.12 | 4014.52 | 5064.46 | 3862.43 | 3322.87 | 4667.53 | 3165.63 | 4227 | 3674.78 | 2705 | 4235.46 | 3617.7 | 4379.78 | 3813.31 | 5638.44 | 5681.61 | 5474.8 | 6019.83 | 5545.13 | 5456.11 | 5860.36 | 5634.79 | 0 | 355.13 | 0 | 0 | 5571.58 | 4703.45 | 6002.42 | 4854 | 5751.46 | 4758 | 3278.27 | 5434.74 | 5269.43 | 4784.94 | 5673.79 | 5203.49 | 5255.22 | 4243.2 | 4617.11 | 4819.76 | 5055.7 | 3973.6 | 3066.5 | 4918.38 | 3288.93 | 4567.52 | 1798 | 5097.6 | 4167.41 | 3767 | 2781.33 | 3436.43 | 3936.87 | 3510.74 | 3898.5 | 3652.5 | 1522.32 | 4545.83 | 3929.43 | 3432.71 | 3137.29 | 3230.64 | 3262 | 4788.85 | 4446.34 | 2134.86 | 6452 | 1590.81 | 2596.83 | 7010.59 | 6766.8 | 6143.17 | [32 empty] | 5072.82 | 4639 | 3297.19 | 3577.39 | 4128 | 0 | 1654.52 | 2897 | 5159 | 3762.11 | 4231.76 | 5111.5 | 4930 | 2976.81 | 1933.15 | 4185.39 | 4159.12 | 7.61 | 3490.16 | 1035.94 | 1044.93 | 2892.92 | 1837.72 | 3377 | 340.96 | 649.34 | 1242.82 | 0 | 0 | 0 | 1597.65 | 3260.12 | 4713 | 5891 | 6376.11 | 6531.32 | 0 | 0 | 0 | 0 | 5281.44 | 6779.53 | 6155.75 | 6954 | 6224 | 7354.7 | 6833.63 | 5159.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4932.12 | 0 | 0 | 0 | 6224 | 7354.7 | 6833.63 | 5159.69 | 2594.1 | 3525 | 3559.85 | 713 | 3814.47 | 4147 | 3966 | 3358 | 4614 | 5005 | 4976 | 3881.72 | 3391.79 | 2953.37 | 4742.58 | 4873.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5211 | 4745.7 | 3188.8 | 0 | 0 | 0 | 0 | 0 | 4108.36 | 3598.9 | 4597.23 | 4608.8 | 4382.2 | 4461.34 | 4723.98 | 4278.45 | 2524.6 | 3481.6 | 3896.7 | 1985.178 | 4783.32 | 4424.6 | 3916.25 | 4208.23 | 4326.5 | 4531.8 | 4624.8 | 3971.23 | 4944 | 4598.23 | 4876.171 | 4036.53 | 6792.5 | 6879.9 | 6241.85 | 5905 | 4898.89 | 3655.86 | 4890.17 | 3709.71 | 4621 | 3153.59 | 6151.9 | 5502.37 | 4930.67 | 3934.87 | 4742.5 | 4060.25 | 5204.85 | 5205 | 3640.96 | 6182.2 | 2036.7 | 2904.27 | 6347.68 | 6223.886 | 2364 | 2626 | 4431.85 | 4682.91 | 2652.99 | 3857 | 0 | 0 | 1944.49 | 4863.6 | 4754.9 | 4794.9 | 6104 | 5819.68 | 2776.34 | 3210.8 | 5954.34 | 4383.37 | 3859.83 | 3295.54 | 3401.99 | 3732.38 | 5502.96 | 2747.45 | 6203.6 | 6606.55 | 6065.72 | 6733.98 | 3446.44 | 4721.83 | 5659.86 | 7073.55 | 5325 | 5804.87 | 5406.89 | 2508.56 | 4332 | 3576.54 | 245.82 | 1145.36 | 3873.73 | 3569.7 | 627.51 | 7040.65 | 2896.17 | 4143.85 | 0 | 0 | 5044.5 | 5111.22 | 5146.77 | 3809.48 | 1958.14 | 1133.18 | 3193.36 | 4217.86 | 37.7099 | [5 empty] | 51.6433 | [5 empty] | 2.2238 | [5 empty] | 3.795 | [5 empty] | 7.401 | [11 empty] | 7.1413 | [27 empty] | 43298.4351 | 847.28 | 7.401 | 0 | 0 | 0 | 0 | 0 | 7.1413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1311652.416 | 14445.344 | 0 | 1297207.072 | 13.0167 | 7.401 |  | 7.1413 |  |  |  | 37.7099 | 51.6433 | 2.2238 | 3.795 | 1330504.385 | [5 empty] | 1311652.416 | 1311652.416 | 14445.344 | 1297207.072
2025-07-14 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 363511.955 | 6:20 | 19:20 | 2129.6 | 4301.6 | 3406.6 | 4714.9 | 4115.2 | 4753.9 | 3877.9 | 4307.6 | 4608.6 | 4426.2 | 4767.8 | 4869.5 | 4724.7 | 3540.5 | 1863.3 | 5093.4 | 4181.5 | 4686.3 | 4468.9 | 4706.6 | 4671.6 | 4662.2 | 4263.6 | 4617 | 4164.1 | 4755.1 | 4762.5 | 4553.5 | 4283.7 | 3056.7 | 3456.7 | 3798.9 | 3179.6 | 4517.8 | 2995.8 | 3225.1 | 4597.7 | 4652.7 | 3578.4 | 3596.1 | 1935.7 | 2044.9 | 4746.9 | 4468.7 | 4196 | 4791.2 | 4315.9 | 3956.2 | 4139.6 | 2740.6 | 4240.4 | 4743.1 | 4301.5 | 4108.4 | 3827.9 | 4376.5 | 3780.5 | 3936 | 4009.4 | 3745.8 | 3157.2 | 1645.5 | 3388.4 | 3973.5 | 3344.9 | 4179 | 3515 | 4072.3 | 3452.4 | 3639.8 | 4026.4 | 3604.7 | [8 empty] | 0 | 0 | 0 | 0 | 4537.4 | 3683 | 4556.7 | 4639 | 4654.4 | 4278.5 | 4576.1 | 4751.8 | 4469.5 | 4400 | 4571.5 | 3962.4 | 4783.9 | 3818.2 | 3305.6 | 4508.7 | 3128.9 | 4096.4 | 3578 | 2663.4 | 4045.4 | 3531 | 4172 | 3705.1 | 4606.2 | 4640.5 | 4471.3 | 4862 | 4523.7 | 4505.3 | 4791.2 | 4600.8 | 0 | 286.9 | 0 | 0 | 4562.3 | 3959.9 | 4837.9 | 4098 | 4721 | 4048.9 | 2940.3 | 4493.3 | 4399.3 | 4033.9 | 4668 | 4361.3 | 4379.7 | 3657.5 | 3940.6 | 4083 | 4915.9 | 3948 | 3061.3 | 4779.2 | 3286.4 | 4446.2 | 1686.2 | 4835.6 | 3820.3 | 3731.9 | 3152.7 | 3296.3 | 3647.1 | 3283.4 | 3380.3 | 3419.3 | 1470.8 | 4421.8 | 3885.3 | 3495.8 | 3162.3 | 3274.7 | 3306.6 | 4664.7 | 3224.1 | 1750.9 | 4192.9 | 1315.2 | 2171 | 4469.4 | 4370.9 | 4072.7 | [32 empty] | 4436.1 | 4144.7 | 3225.4 | 3452.4 | 3747.8 | 0 | 1480.2 | 2754.3 | 4614.4 | 3707.4 | 3896.6 | 4742.4 | 4406 | 2856.8 | 2277.1 | 3936.6 | 2983.6 | 1731.2 | 2627 | 831.7 | 839.9 | 2301.2 | 1505.5 | 2572.5 | 275.7 | 528.5 | 1021.5 | 0 | 0 | 0 | 1340.5 | 2589.3 | 3405.1 | 4008.8 | 4288.2 | 4285.7 | 0 | 0 | 0 | 0 | 3691.3 | 4420.5 | 4151.1 | 4510.9 | 4159.4 | 4659.8 | 4390.9 | 3608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4376.5 | 0 | 0 | 0 | 3255.3 | 3945.2 | 4536 | 3476.6 | 2851.5 | 3706.5 | 3540.6 | 2274.3 | 3292.7 | 3608.8 | 3490.3 | 3019.4 | 4174.7 | 4418.2 | 4395.1 | 3835.7 | 3836 | 3286.7 | 4253.4 | 4375.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4732.1 | 4385.4 | 0 | 0 | 0 | 0 | 0 | 0 | 3613.4 | 3148.6 | 4022.1 | 4083 | 4211.7 | 4427.4 | 4486.8 | 4066.2 | 2989.2 | 3790 | 3697 | 3055 | 4408.7 | 4087.1 | 3676 | 3902.2 | 4155.6 | 4289.8 | 4386.4 | 3835.2 | 4642 | 4431.4 | 4591.4 | 3918.2 | 5661.1 | 5753.8 | 5238.3 | 4956.8 | 3530 | 2861.7 | 3531.9 | 2833 | 3337.1 | 2474.8 | 4127.1 | 3812.4 | 3539.6 | 2995.7 | 3890.8 | 4431.1 | 3659.4 | 3655.5 | 2775.2 | 4128.8 | 1653.7 | 2359 | 4254.6 | 4186 | 3516.9 | 3834.4 | 4213.4 | 4399.5 | 3983.1 | 3672.5 | 0 | 768.9 | 1551.1 | 3355.2 | 3315.8 | 3516.4 | 3980.1 | 3866.1 | 2216 | 3349.6 | 2923 | 3001.7 | 2718 | 2480.2 | 2544.2 | 2738.7 | 3685.9 | 2162.6 | 3981.3 | 4170.2 | 4525.7 | 4220 | 2580.1 | 3249.1 | 3724.9 | 4354.3 | 3581.2 | 3821.7 | 3568.8 | 1971.6 | 3050.8 | 2631.3 | 175.3 | 885.5 | 3756.2 | 2692.1 | 485.6 | 4361.6 | 3001.6 | 3005.2 | 0 | 0 | 3383.7 | 3440.6 | 3479.7 | 562.7 | 2968.3 | 1041.8 | 2436.2 | 2967.5 | 38.1813 | [5 empty] | 48.4757 | [5 empty] | 1.6616 | [5 empty] | 3.03 | [5 empty] | 6.0364 | [11 empty] | 5.7248 | [27 empty] | 44452.7878 | 861.2513 | 6.0364 | 0 | 0 | 0 | 0 | 0 | 5.7248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1154352.704 | 13971.232 | 0 | 1140381.472 | 13 | 6.0364 |  | 5.7248 |  |  |  | 38.1813 | 48.4757 | 1.6616 | 3.03 | 1157069.1 | [5 empty] | 1154352.704 | 1154352.704 | 13971.232 | 1140381.472
2025-07-15 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 363511.955 | 6:18 | 19:05 | 1804.1 | 3673 | 2939.7 | 4079.3 | 4259.8 | 4110.4 | 3338.5 | 3710.3 | 3980.3 | 3848.1 | 4180 | 4245.4 | 4083.9 | 2989.7 | 1517 | 4391.4 | 3723.8 | 4142.5 | 3925.1 | 4096.6 | 4143.9 | 4155.5 | 3822.1 | 4142.6 | 3840.5 | 4292.1 | 4286.5 | 4125.6 | 3926 | 2981.4 | 3483.6 | 3544.6 | 2815.5 | 3950.7 | 2620.6 | 2559.4 | 3951 | 4099.9 | 3188.4 | 3162.6 | 1685.2 | 1757 | 4129.2 | 3887.6 | 3659.6 | 4211.8 | 3842.5 | 3503.6 | 3681.2 | 2470 | 3834.5 | 4280.3 | 3882.6 | 3675.4 | 1744 | 3877.5 | 3471.4 | 3609 | 3608.2 | 3385 | 2884.1 | 1459.8 | 3153.3 | 3687.4 | 3138.7 | 3848.4 | 3249.4 | 3775.2 | 3239.9 | 1437.2 | 3763.8 | 3379.5 | [8 empty] | 0 | 0 | 0 | 0 | 2591 | 1969.1 | 2646.6 | 2685.1 | 2685.4 | 2375.8 | 2628.3 | 2770.4 | 4030.9 | 4064.2 | 4225 | 3680 | 4445.4 | 3566.8 | 3080.8 | 4128.5 | 2945.9 | 3814.9 | 3352.9 | 2512.9 | 3839.9 | 3341.8 | 3945.9 | 3501.3 | 4018.7 | 4082 | 3849 | 4262.1 | 3975.6 | 3930.3 | 4040.1 | 3913.5 | 0 | 267.3 | 0 | 0 | 4069.4 | 3518.8 | 4292 | 3611.5 | 4151.6 | 3597.2 | 2651.5 | 4009.8 | 3907 | 3588 | 4123.7 | 3827.3 | 3864.8 | 3231.4 | 3514.9 | 3643 | 4248.4 | 3409.2 | 2625.5 | 4149.5 | 2814.7 | 2852.5 | 1399.2 | 4164.1 | 3538.6 | 3579 | 3426.3 | 3415.7 | 3661.1 | 3083.1 | 3290.8 | 3173.3 | 1085.3 | 3916.6 | 3407.4 | 3112.4 | 2861.2 | 3032 | 3050.9 | 4293.6 | 3030.3 | 1623.1 | 3942.8 | 1224.5 | 2033 | 4172.1 | 4046.3 | 3775.1 | [32 empty] | 4110.8 | 3753.2 | 2953.6 | 3162.3 | 3438.9 | 0 | 1313.2 | 2537.2 | 4123.7 | 3115.5 | 3692.4 | 4195.4 | 4078.2 | 2664.3 | 2346.6 | 3556.4 | 2868 | 1584.4 | 2539.6 | 776.9 | 786.5 | 2011.8 | 1408 | 2485.2 | 245.7 | 484.7 | 943.8 | 0 | 0 | 0 | 1190.5 | 2369.4 | 3285.1 | 3846.8 | 4099.6 | 3972.6 | 0 | 0 | 0 | 0 | 3435.6 | 4089.2 | 3833.4 | 4158.3 | 3883.5 | 4361.3 | 4155.1 | 3411.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4002.6 | 0 | 0 | 0 | 3142.7 | 3636.3 | 4070.8 | 3263.8 | 2779.9 | 2806.4 | 3541.4 | 3439.5 | 3228 | 3517.3 | 3584 | 2916.6 | 4172.6 | 4052.6 | 4034 | 3855 | 3740.2 | 3118.5 | 3695.5 | 3776.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4462.8 | 4151.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3338.2 | 3105.1 | 3503.2 | 3437.2 | 3830.2 | 1520.1 | 4240.5 | 3823.2 | 3094 | 4191.8 | 3835 | 3822.6 | 4339.9 | 4073.7 | 3652.1 | 3921.1 | 4049.2 | 4186.2 | 4269.2 | 3727 | 4498.5 | 4274.4 | 4453 | 3762.3 | 5437.8 | 5502.8 | 4980.9 | 4730.4 | 3387.6 | 2679.6 | 3370.8 | 2785.7 | 3234 | 2471.1 | 3995.7 | 3683.6 | 3389.3 | 3342.8 | 3763.9 | 4046.8 | 3544.7 | 3556.4 | 2749.6 | 4033.3 | 1540.9 | 2308.6 | 4077.8 | 4030.8 | 3451.3 | 3906 | 4131.2 | 4335.1 | 3934.9 | 3671.2 | 154.2 | 1611.2 | 1547.8 | 3384 | 3373.2 | 3381.9 | 4055.2 | 3900.5 | 2232.7 | 3604.3 | 2643.4 | 3124.3 | 2892.9 | 2664.6 | 2650.7 | 2827.1 | 3731.5 | 2197 | 4034.9 | 4216.5 | 3976.6 | 4305.9 | 2675.4 | 3326.1 | 3783.4 | 4448.5 | 3632 | 3885.8 | 3662.3 | 2056.1 | 3117.6 | 2759.8 | 186.1 | 914.7 | 3859.4 | 2409.6 | 509.6 | 4573.6 | 3142.1 | 2895.7 | 906.1 | 2005 | 3703.9 | 3525.7 | 3634.5 | 3635.5 | 3124.9 | 1100.3 | 2618.8 | 3109.4 | 30.4039 | [5 empty] | 36.9876 | [5 empty] | 3.607 | [5 empty] | 14.52 | [5 empty] | 5.2716 | [11 empty] | 5.2576 | [27 empty] | 45524.1972 | 875.5043 | 5.2716 | 0 | 0 | 0 | 0 | 0 | 5.2576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1071409.408 | 14253.024 | 0 | 1057156.384 | 12.7833 | 5.2716 |  | 5.2576 |  |  |  | 30.4039 | 36.9876 | 3.607 | 14.52 | 1068541.3 | [5 empty] | 1071409.408 | 1071409.408 | 14253.024 | 1057156.384
2025-07-16 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 363511.955 | 6:39 | 19:16 | 2326.8 | 5854.7 | 4294.2 | 6624.5 | 6997.6 | 6671.4 | 5195.3 | 6001.3 | 6415.5 | 6004.7 | 6770.7 | 6915.2 | 6653.4 | 4353.6 | 1902.1 | 7220.2 | 5057.9 | 5807.5 | 5443.3 | 5767.7 | 5853 | 5788.8 | 5210.9 | 5831.3 | 5254.3 | 6008.9 | 5972.1 | 5716.7 | 5374.2 | 3573 | 1911.9 | 4700.3 | 3425.2 | 5481.6 | 2941.5 | 2991.8 | 5433.9 | 5661.9 | 4010.3 | 4022.1 | 2056.8 | 2173.9 | 6671.6 | 6191.6 | 5726.2 | 6809.5 | 6026.2 | 5381.1 | 4976.7 | 2780.3 | 5164.4 | 5980 | 5084.1 | 4919.4 | 3715.3 | 5275 | 4483.8 | 4681.2 | 4888.5 | 4305.9 | 3411.2 | 1489.5 | 3997.7 | 4887 | 3825.7 | 5260.7 | 4153.7 | 5110.5 | 4065.3 | 4419.4 | 5006.6 | 4197.8 | [8 empty] | 0 | 0 | 0 | 0 | 6434.8 | 5036.5 | 6570.12 | 6566.7 | 6569 | 5779.8 | 6327 | 6667.8 | 6328.8 | 6351.6 | 6615.8 | 5551 | 7058.9 | 5296.1 | 4257.6 | 6560.7 | 4006 | 5850 | 5095 | 3213.8 | 5834.2 | 4827.4 | 6016.4 | 5155.4 | 6308.4 | 6413.6 | 5875.4 | 6785.3 | 6283.2 | 6194.2 | 6405.6 | 6139.4 | 0 | 0 | 0 | 0 | 6241.7 | 5243.9 | 6756.3 | 5449.6 | 6527.9 | 5375.8 | 3384.3 | 6125.9 | 5799.3 | 5182.2 | 6232.7 | 5741.5 | 5798.1 | 4564.1 | 5082.6 | 5208.7 | 4161.6 | 6259.1 | 1818.5 | 6849.3 | 6910.7 | 5275.6 | 3720.9 | 6728.1 | 4454.5 | 4526 | 4306.1 | 4343.7 | 4792.9 | 3829.5 | 4161.7 | 3809.2 | 567.7 | 6268 | 5323.9 | 4559.6 | 3692 | 4132 | 4147.1 | 6518.2 | 4141.6 | 1915 | 5955.8 | 1448.1 | 2368.7 | 6412.2 | 6160.9 | 5655.3 | [32 empty] | 5321.4 | 489.8 | 3560.8 | 4020.2 | 4512 | 0 | 1447 | 2794 | 5617.5 | 3933.2 | 4760.2 | 5660.7 | 5497.7 | 2823.2 | 2256.9 | 4692.5 | 3796.5 | 1885.6 | 3187.9 | 937.2 | 945.8 | 2278.3 | 1666.2 | 2369.4 | 304.2 | 583.9 | 1123.3 | 0 | 0 | 0 | 1483.8 | 2669.7 | 4819.4 | 5886.6 | 6494.8 | 5903 | 0 | 0 | 0 | 0 | 4645.4 | 5882.2 | 5423 | 6154.7 | 5559.7 | 6427.6 | 6031 | 4604.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6039.3 | 0 | 0 | 0 | 4138.6 | 5324.5 | 6155.1 | 4550.8 | 3610 | 977 | 5117.6 | 4884.1 | 4383.2 | 4943.2 | 4663.8 | 3809.9 | 6447.6 | 6221.8 | 6118.7 | 5732.8 | 6283.5 | 4534.8 | 5895.1 | 6105.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6718.1 | 6078 | 0 | 0 | 0 | 0 | 0 | 0 | 4504.1 | 4224.6 | 5119.4 | 5159.5 | 5407.8 | 5801.1 | 6069.4 | 2535 | 3766 | 5869 | 4981.7 | 5998.8 | 6193.9 | 5710.3 | 4993.1 | 5344.3 | 5869.2 | 6088.7 | 6210.8 | 5169.2 | 6683.4 | 6314.2 | 6705.6 | 5387.2 | 5796.1 | 5852.5 | 5298.1 | 5044.1 | 4410.1 | 3119.4 | 4417.9 | 3191.4 | 4009.1 | 3895.5 | 5542.5 | 5083 | 5309.8 | 5399.3 | 5715.4 | 4550.6 | 4290.7 | 4847.2 | 3283.9 | 5725.3 | 1831.3 | 2614.7 | 5927.5 | 5783.9 | 4580 | 5480 | 5960 | 6350 | 5570 | 5050 | 3750 | 1760 | 1640 | 4350 | 4260 | 4300 | 5470 | 5300 | 3850 | 4810 | 5370 | 3840 | 3400 | 2980 | 2950 | 3120 | 4550 | 2970 | 5139.9 | 5433.7 | 4977.4 | 5426.9 | 2730.2 | 3810.3 | 4671.7 | 5666.2 | 2832.8 | 4729.5 | 4273.7 | 1908 | 3445.8 | 2839.1 | 176.2 | 860.8 | 501.1 | 2136.2 | 193.1 | 5309.4 | 3754.4 | 3052.4 | 1767.3 | 4101.8 | 4760.5 | 4282.7 | 4661.4 | 759 | 3737.3 | 1142.1 | 2811.1 | 3537 | 31.4932 | [5 empty] | 37.9766 | [5 empty] | 3.6339 | [5 empty] | 7.68 | [5 empty] | 6.3938 | [11 empty] | 6.2096 | [27 empty] | 47006.7091 | 883.8547 | 6.3938 | 0 | 0 | 0 | 0 | 0 | 6.2096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1482511.904 | 8350.432 | 0 | 1474161.472 | 12.6167 | 6.3938 |  | 6.2096 |  |  |  | 31.4932 | 37.9766 | 3.6339 | 7.68 | 1492179.72 | [5 empty] | 1482511.904 | 1482511.904 | 8350.432 | 1474161.472
2025-07-17 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -47006709.088 | -883854.72 | 0 | -46122854.368 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-07-18 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-07-19 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-07-20 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-07-21 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-07-22 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-07-23 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-07-24 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-07-25 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-07-26 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-07-27 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-07-28 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-07-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-07-30 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-07-31 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-01 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-02 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-03 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-04 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-05 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-06 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-07 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-08 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-09 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-10 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-11 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-12 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-13 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-14 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-15 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-16 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-17 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-18 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-19 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-20 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-21 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-22 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-23 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-24 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-25 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-26 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-27 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-28 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-30 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-08-31 | 2026 | 2025 | Year_1 | Year_1 | 2025-08-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-01 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-02 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-03 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-04 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-05 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-06 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-07 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-08 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-09 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-10 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-11 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-12 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-13 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-14 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-15 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-16 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-17 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-18 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-19 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-20 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-21 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-22 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-23 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-24 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-25 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-26 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-27 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-28 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-09-30 | 2026 | 2025 | Year_1 | Year_1 | 2025-09-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-01 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-02 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-03 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-04 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-05 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-06 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-07 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-08 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-09 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-10 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-11 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-12 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-13 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-14 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-15 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-16 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-17 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-18 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-19 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-20 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-21 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-22 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-23 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-24 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-25 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-26 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-27 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-28 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-30 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-10-31 | 2026 | 2025 | Year_1 | Year_1 | 2025-10-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-01 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-02 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-03 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-04 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-05 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-06 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-07 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-08 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-09 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-10 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-11 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-12 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-13 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-14 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-15 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-16 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-17 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-18 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-19 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-20 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-21 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-22 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-23 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-24 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-25 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-26 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-27 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-28 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-11-30 | 2026 | 2025 | Year_1 | Year_1 | 2025-11-01 | 30 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-01 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-02 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-03 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-04 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-05 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-06 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-07 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-08 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-09 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-10 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-11 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-12 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-13 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-14 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-15 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-16 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-17 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-18 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-19 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-20 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-21 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-22 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-23 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-24 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-25 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-26 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-27 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-28 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-30 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2025-12-31 | 2026 | 2025 | Year_1 | Year_1 | 2025-12-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-01 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-02 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-03 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-04 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-05 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-06 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-07 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-08 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-09 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-10 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-11 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-12 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-13 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-14 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-15 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-16 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-17 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-18 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-19 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-20 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-21 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-22 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-23 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-24 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-25 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-26 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-27 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-28 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-29 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-30 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-01-31 | 2026 | 2026 | Year_1 | Year_1 | 2026-01-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-01 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-02 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-03 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-04 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-05 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-06 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-07 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-08 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-09 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-10 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-11 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-12 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-13 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-14 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-15 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-16 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-17 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-18 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-19 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-20 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-21 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-22 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-23 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-24 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-25 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-26 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-27 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-02-28 | 2026 | 2026 | Year_1 | Year_1 | 2026-02-01 | 28 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-01 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-02 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-03 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-04 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-05 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-06 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-07 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-08 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-09 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-10 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-11 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-12 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-13 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-14 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-15 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-16 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-17 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-18 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-19 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-20 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-21 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-22 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-23 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-24 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-25 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-26 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-27 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-28 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-29 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-30 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
2026-03-31 | 2026 | 2026 | Year_1 | Year_1 | 2026-03-01 | 31 | [477 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [6 empty] | 0 |  | 0
Formulas:
Month Year = Raw_Data[[#This Row],[Date]]-DAY(Raw_Data[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1
Note on QT77: Author: Data Taken Fron RB1
Note on QT78: Author: Data Taken Fron RB1
Note on QT80: Author: Data Taken Fron RB1
Note on QT81: Author: Data Taken Fron RB1
Note on QT82: Author: Data Taken Fron RB1
Note on QT84: Author: Data Taken Fron RB1
Note on QN91: Author: Data Taken Fron RB1
Note on QT91: Author: Data Taken Fron RB1
Note on QN93: Author: Data Taken Fron RB1
Note on QT93: Author: Data Taken Fron RB1
Note on QN95: Author: Data Taken Fron RB1
Note on QT95: Author: Data Taken Fron RB1
Note on QN96: Author: Data Taken Fron RB1
Note on QT96: Author: Data Taken Fron RB1
Note on QN97: Author: Data Taken Fron RB1
Note on QT97: Author: Data Taken Fron RB1
Note on QN98: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT98: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN99: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT99: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN100: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT100: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN102: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT102: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN103: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT103: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN104: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT104: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN105: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT105: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN106: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT106: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN108: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT108: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN109: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT109: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN110: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT110: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN111: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT111: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN112: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT112: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN113: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT113: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN114: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT114: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN115: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT115: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN118: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT118: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN119: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT119: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN120: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT120: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN121: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT121: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN122: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT122: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN123: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT123: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN124: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT124: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN125: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT125: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN126: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT126: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN127: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QT127: Author: Data Taken From RB-1 Due to RB2 data logger issue
Note on QN128: all POA value taken from RB-1 data Logger
Note on QT128: all POA value taken from RB-1 data Logger
Note on QN129: POA value taken from RB-1 data Logger
Note on QT129: POA value taken from RB-1 data Logger
Note on QN130: POA value taken from RB-1 data Logger
Note on QT130: POA value taken from RB-1 data Logger
Note on QN131: POA value taken from RB-1 data Logger
Note on QT131: POA value taken from RB-1 data Logger
Note on QN132: POA value taken from RB-1 data Logger
Note on QT132: POA value taken from RB-1 data Logger
Note on QN133: POA value taken from RB-1 data Logger
Note on QT133: POA value taken from RB-1 data Logger
Note on QN134: POA value taken from RB-1 data Logger
Note on QT134: POA value taken from RB-1 data Logger
Note on QN135: POA value taken from RB-1 data Logger
Note on QT135: POA value taken from RB-1 data Logger
Note on QN136: POA value taken from RB-1 data Logger
Note on QT136: POA value taken from RB-1 data Logger
Note on QN137: POA value taken from RB-1 data Logger
Note on QT137: POA value taken from RB-1 data Logger
Note on QN138: POA value taken from RB-1 data Logger
Note on QT138: POA value taken from RB-1 data Logger
Note on QN139: POA value taken from RB-1 data Logger
Note on QT139: POA value taken from RB-1 data Logger
Note on QN140: POA value taken from RB-1 data Logger
Note on QT140: POA value taken from RB-1 data Logger
Note on QN141: POA value taken from RB-1 data Logger
Note on QT141: POA value taken from RB-1 data Logger
Note on QN142: POA value taken from RB-1 data Logger
Note on QT142: POA value taken from RB-1 data Logger
Note on QN143: POA value taken from RB-1 data Logger
Note on QT143: POA value taken from RB-1 data Logger
Note on QN144: POA value taken from RB-1 data Logger
Note on QT144: POA value taken from RB-1 data Logger
Note on QN145: POA value taken from RB-1 data Logger
Note on QT145: POA value taken from RB-1 data Logger
Note on QN146: POA value taken from RB-1 data Logger
Note on QT146: POA value taken from RB-1 data Logger
Note on QN147: POA value taken from RB-1 data Logger
Note on QT147: POA value taken from RB-1 data Logger
Note on QN148: POA value taken from RB-1 data Logger
Note on QT148: POA value taken from RB-1 data Logger
Note on QN149: POA value taken from RB-1 data Logger
Note on QT149: POA value taken from RB-1 data Logger
Note on QN150: POA value taken from RB-1 data Logger
Note on QT150: POA value taken from RB-1 data Logger
Note on QN151: POA value taken from RB-1 data Logger
Note on QT151: POA value taken from RB-1 data Logger
Note on QN152: POA value taken from RB-1 data Logger
Note on QT152: POA value taken from RB-1 data Logger
Note on QN153: POA value taken from RB-1 data Logger
Note on QT153: POA value taken from RB-1 data Logger
Note on QN154: POA value taken from RB-1 data Logger
Note on QT154: POA value taken from RB-1 data Logger
Note on QN155: POA value taken from RB-1 data Logger
Note on QT155: POA value taken from RB-1 data Logger
Note on QN156: POA value taken from RB-1 data Logger
Note on QT156: POA value taken from RB-1 data Logger
Note on QN157: POA value taken from RB-1 data Logger
Note on QT157: POA value taken from RB-1 data Logger
Note on QN158: Data logger Hanged reading taken from scada
Note on QQ158: Data logger Hanged reading taken from scada
Note on QT158: Data logger Hanged reading taken from scada
Note on QW158: Data logger Hanged reading taken from scada
Note on QN159: POA data taken from Plot-2 Scada
Note on QQ159: Data logger Hanged reading taken from scada
Note on QT159: POA data taken from Plot-2 Scada
Note on QW159: Data logger Hanged reading taken from scada
Note on QN160: POA data taken from Plot-2 Scada
Note on QT160: POA data taken from Plot-2 Scada
Note on QN161: POA data taken from Plot-2 Scada
Note on QT161: POA data taken from Plot-2 Scada
Note on QN162: POA data taken from Plot-2 Scada
Note on QT162: POA data taken from Plot-2 Scada
Note on QN163: POA data taken from Plot-2 Scada
Note on QT163: POA data taken from Plot-2 Scada
Note on QN164: POA data taken from Plot-2 Scada
Note on QT164: POA data taken from Plot-2 Scada
Note on QN165: POA data taken from Plot-1
Note on QT165: POA data taken from Plot-1
Note on QN166: POA data taken from Plot-2 Scada
Note on QT166: POA data taken from Plot-2 Scada
Note on QN167: POA data taken from Plot-2 Scada
Note on QT167: POA data taken from Plot-2 Scada
Note on QN168: Author: datat ccollect from Rb-2 Scada
Note on QT168: Author: datat ccollect from Rb-2 Scada
Note on QN169: datat ccollect from Rb-2 Scada
Note on QT169: datat ccollect from Rb-2 Scada
Note on QN170: datat ccollect from Rb-2 Scada
Note on QT170: datat ccollect from Rb-2 Scada
Note on QN171: datat ccollect from Rb-2 Scada
Note on QT171: datat ccollect from Rb-2 Scada
Note on QN172: datat ccollect from Rb-2 Scada
Note on QT172: datat ccollect from Rb-2 Scada
Note on QN173: datat ccollect from Rb-2 Scada
Note on QT173: datat ccollect from Rb-2 Scada
Note on QN174: datat ccollect from Rb-2 Scada
Note on QT174: datat ccollect from Rb-2 Scada
Note on QN175: datat ccollect from Rb-2 Scada
Note on QT175: datat ccollect from Rb-2 Scada
Note on QN176: Author: data collect from sacda plot-2
Note on QT176: Author: data collect from sacda plot-2
Note on QN177: data collect from sacda plot-2
Note on QT177: data collect from sacda plot-2
Note on QN178: Author: Data From scada Plot-2
Note on QT178: Author: Data From scada Plot-2
Note on QN179: Data From scada Plot-2 data collect from Plot-2
Note on QT179: Data From scada Plot-2 data collect from Plot-2
Note on QN180: data collect from Plot-2
Note on QT180: data collect from Plot-2
Note on QN181: data collect from Plot-2
Note on QT181: data collect from Plot-2
Note on QN182: data collect from Plot-2
Note on QT182: data collect from Plot-2
Note on QN183: data collect from Plot-2
Note on QT183: data collect from Plot-2
Note on QN184: data collect from Plot-2
Note on QT184: data collect from Plot-2
Note on QN185: Author: data collect from Plot-2
Note on QT185: Author: data collect from Plot-2
Note on QN186: data collect from Plot-2
Note on QT186: data collect from Plot-2
Note on QN187: data collect from Plot-2
Note on QT187: data collect from Plot-2
Note on QN188: data collect from Plot-2
Note on QT188: data collect from Plot-2
Note on QN189: data collect from Plot-2
Note on QT189: data collect from Plot-2
Note on QN190: data collect from Plot-2
Note on QT190: data collect from Plot-2
Note on QN191: GTI value not show proper in SCADA. so we consider in DGR Plot-01 GTI value.
Note on QT191: GTI value not show proper in SCADA. so we consider in DGR Plot-01 GTI value.
Note on QN192: Author: Data Collect From Scada pLOT-2
Note on QT192: Author: Data Collect From Scada pLOT-2
Note on QN193: Data Collect From Scada pLOT-2
Note on QT193: Data Collect From Scada pLOT-2
Note on QN194: Data Collect From Scada pLOT-2
Note on QT194: Data Collect From Scada pLOT-2
Note on QN195: Data Collect From Scada pLOT-2
Note on QT195: Data Collect From Scada pLOT-2
Note on QN196: Data Collect From Scada pLOT-2
Note on QT196: Data Collect From Scada pLOT-2
Note on QN197: Data Collect From Scada pLOT-2
Note on QT197: Data Collect From Scada pLOT-2
Note on QN198: Data Collect From Scada pLOT-2
Note on QT198: Data Collect From Scada pLOT-2
Note on QN199: Data Collect From Scada pLOT-2
Note on QT199: Data Collect From Scada pLOT-2
Note on QN200: Data Collect From Scada pLOT-2
Note on QT200: Data Collect From Scada pLOT-2
Note on QN201: Data Collect From Scada pLOT-2
Note on QT201: Data Collect From Scada pLOT-2
Note on QN202: Data Collect From Scada pLOT-2
Note on QT202: Data Collect From Scada pLOT-2
Note on QN203: Data Collect From Scada pLOT-2
Note on QT203: Data Collect From Scada pLOT-2
Note on QN204: Data Collect From Scada pLOT-2
Note on QT204: Data Collect From Scada pLOT-2
Note on QN205: Data Collect From Scada pLOT-2
Note on QT205: Data Collect From Scada pLOT-2
Note on QN206: Data Collect From Scada pLOT-2
Note on QT206: Data Collect From Scada pLOT-2
Note on QN207: Data Collect From Scada pLOT-2
Note on QT207: Data Collect From Scada pLOT-2
Note on QN208: Data Collect From Scada pLOT-2
Note on QT208: Data Collect From Scada pLOT-2
Note on QN209: Data Collect From Scada pLOT-2
Note on QT209: Data Collect From Scada pLOT-2
Note on QN210: Data Collect From Scada pLOT-2
Note on QT210: Data Collect From Scada pLOT-2
Note on QN212: Author: Plot-2 Scada GTI value
Note on QT212: Author: Plot-2 Scada GTI value
Note on QN213: Author: collect datta from scada Plot-2
Note on QT213: Author: collect datta from scada Plot-2
Note on QN214: Author: data collect from scada Plot-2
Note on QT214: Author: data collect from scada Plot-2
Note on QN215: Author: data collect from scada plot-2
Note on QT215: Author: data collect from scada plot-2
Note on QN216: Author: scada Datat Colllect From Plot-2
Note on QT216: Author: scada Datat Colllect From Plot-2
Note on QN217: Author: data Collect From scada Plot-2
Note on QT217: Author: data Collect From scada Plot-2
Note on QN218: Author: data collect from Scada Plot-2
Note on QT218: Author: data collect from Scada Plot-2
Note on QN219: Author: Scada Data -Plot-2
Note on QT219: Author: Scada Data -Plot-2
Note on QN225: Author: gti value from plot1
Note on QT225: Author: gti value from plot1
Note on QN233: Author: gti value from plot1
Note on QT233: Author: gti value from plot1
Note on QN234: Author: GTI Value Consider From Plot-1
Note on QT234: Author: GTI Value Consider From Plot-1
Note on QQ251: Author: GTI-Plot-1
Note on QW251: Author: GTI-Plot-1
Note on QQ252: Author: GTI-Plot-1
Note on QW252: Author: GTI-Plot-1
Note on QQ253: Author: GTI-Plot-1
Note on QW253: Author: GTI-Plot-1
Note on QQ254: Author: GTI-Plot-1
Note on QW254: Author: GTI-Plot-1
Note on QQ255: Author: GTI-Plot-1
Note on QW255: Author: GTI-Plot-1
Note on QQ256: Author: GTI-Plot-1
Note on QW256: Author: GTI-Plot-1
Note on QQ257: Author: GTI-Plot-1
Note on QW257: Author: GTI-Plot-1
Note on QQ258: Author: GTI-Plot-1
Note on QW258: Author: GTI-Plot-1
Note on QQ259: Author: GTI-Plot-1
Note on QW259: Author: GTI-Plot-1
Note on QQ260: Author: GTI-Plot-1
Note on QW260: Author: GTI-Plot-1
Note on QQ261: Author: GTI-Plot-1
Note on QW261: Author: GTI-Plot-1
Note on QQ262: Author: GTI-Plot-1
Note on QW262: Author: GTI-Plot-1
Note on QQ263: Author: GTI-Plot-1
Note on QW263: Author: GTI-Plot-1
Note on QQ264: Author: GTI-Plot-1
Note on QW264: Author: GTI-Plot-1
Note on QQ265: Author: GTI-Plot-1
Note on QW265: Author: GTI-Plot-1
Note on QQ266: Author: GTI-Plot-1
Note on QW266: Author: GTI-Plot-1
Note on QQ267: Author: GTI-Plot-1
Note on QW267: Author: GTI-Plot-1
Note on QQ268: Author: GTI-Plot-1
Note on QW268: Author: GTI-Plot-1
Note on QQ269: Author: GTI-Plot-1
Note on QW269: Author: GTI-Plot-1
Note on QQ270: Author: GTI-Plot-1
Note on QW270: Author: GTI-Plot-1
Note on QQ271: Author: GTI-Plot-1
Note on QW271: Author: GTI-Plot-1
Note on QQ272: Author: GTI-Plot-1
Note on QW272: Author: GTI-Plot-1
Note on QQ273: Author: GTI-Plot-1
Note on QW273: Author: GTI-Plot-1
Note on QQ274: Author: GTI-Plot-1
Note on QW274: Author: GTI-Plot-1
Note on QQ275: Author: GTI-Plot-1
Note on QW275: Author: GTI-Plot-1
Note on QQ276: Author: GTI-Plot-1
Note on QW276: Author: GTI-Plot-1
Note on QQ277: Author: GTI-Plot-1
Note on QW277: Author: GTI-Plot-1
Note on QQ278: Author: GTI-Plot-1
Note on QW278: Author: GTI-Plot-1
Note on QN279: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ279: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT279: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW279: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN280: Author:
Note on QQ280: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT280: Author:
Note on QW280: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN281: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ281: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT281: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW281: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN282: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ282: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT282: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW282: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN283: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ283: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT283: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW283: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN284: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ284: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT284: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW284: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN285: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ285: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT285: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW285: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN286: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ286: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT286: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW286: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN287: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ287: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT287: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW287: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN288: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ288: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT288: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW288: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN289: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ289: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT289: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW289: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN290: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ290: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT290: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW290: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN291: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ291: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT291: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW291: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN292: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ292: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT292: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW292: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN293: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ293: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT293: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW293: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN294: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QT294: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QN295: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ295: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT295: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW295: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN296: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ296: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT296: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW296: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN297: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ297: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT297: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW297: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN298: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ298: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT298: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW298: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN299: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ299: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT299: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW299: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN300: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ300: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT300: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW300: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN301: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ301: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT301: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW301: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN302: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ302: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT302: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW302: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN303: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QQ303: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT303: Author: GTI-Plot 2 (Avg-Pyranometer-1&2)
Note on QW303: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QQ304: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QW304: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QQ305: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QW305: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QQ306: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QW306: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QQ307: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QW307: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QQ308: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QW308: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN310: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ310: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT310: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW310: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN311: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ311: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT311: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW311: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN312: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ312: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT312: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW312: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN313: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ313: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT313: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW313: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN314: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ314: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT314: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW314: Author: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN315: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ315: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot-1 Scada Pc
Note on QT315: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW315: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot-1 Scada Pc
Note on QN316: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ316: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT316: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW316: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN317: Author: Pyranometer Table Tilt In 5 degree
Note on QQ317: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT317: Author: Pyranometer Table Tilt In 5 degree
Note on QW317: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN318: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ318: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot 2 (Avg-Pyranometer-1&2)
Note on QT318: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW318: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot 2 (Avg-Pyranometer-1&2)
Note on QN319: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ319: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT319: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW319: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN320: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ320: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT320: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW320: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN321: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ321: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT321: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW321: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN322: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ322: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot-1 Scada Pc
Note on QT322: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW322: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot-1 Scada Pc
Note on QN323: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ323: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot-1 Scada Pc
Note on QT323: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW323: Plot-1 Data Logger Hanged.GTI Reading Taken From Plot-1 Scada Pc
Note on QN324: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ324: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT324: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW324: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN325: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ325: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT325: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW325: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN326: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ326: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT326: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW326: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN327: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ327: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT327: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW327: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN328: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ328: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT328: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW328: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN329: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ329: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT329: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW329: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN330: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ330: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT330: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW330: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN331: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ331: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT331: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW331: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN332: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ332: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT332: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW332: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN333: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ333: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT333: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW333: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN334: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ334: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT334: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW334: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN335: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QQ335: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT335: Author: GTI-Plot 2 ( Avg Pyranometer 1&2)
Note on QW335: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN336: Author: GTI:- PLOT2 Avr.(Pyranometer 1&2 )
Note on QQ336: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QT336: Author: GTI:- PLOT2 Avr.(Pyranometer 1&2 )
Note on QW336: GTI-Plot 1 (Avg-Pyranometer-1&2)
Note on QN337: Author: GTI:- PLOT2 Avg (Pranometer 1&2 )
Note on QQ337: Author: GTI:- Plot 1 Avg Pyranometer 1 &2
Note on QT337: Author: GTI:- PLOT2 Avg (Pranometer 1&2 )
Note on QW337: Author: GTI:- Plot 1 Avg Pyranometer 1 &2
Note on QN338: Author: GTI :-PLOT2 (Avg Pyranomeetr 1 &2 )
Note on QQ338: Author: GTI :PLOT 1 Avr Pyranometer 1&2
Note on QT338: Author: GTI :-PLOT2 (Avg Pyranomeetr 1 &2 )
Note on QW338: Author: GTI :PLOT 1 Avr Pyranometer 1&2
Note on QN339: Author: GTI:-PLOT2 avg. Pyranometer 1&2
Note on QQ339: Author: GTI :-Plot1 Avg. Pyranometer 1&2
Note on QT339: Author: GTI:-PLOT2 avg. Pyranometer 1&2
Note on QW339: Author: GTI :-Plot1 Avg. Pyranometer 1&2

## PA
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
Sr. No. | Date | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Inverter Station Number (if Bd in filed) | Inverter number (If Inv, SCb or Str BD) | Inverter Module Number | SCB Number (If SCB or Str BD) | String Type(If String BD) | Equipment (If any BD other than PV array and inv) | C1 | C2 | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Fault Category | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgement Time | Work Start time on Fault | Work Completion time on fault | Acknow. time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(Wh/m2) | Approximate Energy Loss (KWh) | Job Card No. | PTW No.
1 | 2025-05-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:04 | 12.8667 | IS3 | Inv2 | M4 | SCB2 |  |  | 1 | 1 | IS3Inv2M4SCB2 | 221.27 | 0.06087% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:04 | 0 | 0 |  | 12.85 | Informed to Project team | Open | 0.0078218 | 7.62 | 990.8034
2 | 2025-05-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:04 | 12.8667 | IS6 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS6Inv1M1SCB1 | 191.4 | 0.05265% | Module |  | Project Activities | 0.25833 | 0.25833 | 0.25833 | 0.79444 | 0 | 0 |  | 12.8667 | Informed to Project team | Open | 0.0067747 | 7.62 | 857.0514
3 | 2025-05-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:04 | 12.8667 | IS17 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS17Inv1M3SCB4 | 0 | 0% | Module |  | Project Activities | 0.25833 | 0.25833 | 0.25833 | 0.79444 | 0 | 0 |  | 12.8667 | Informed to Project team | Open | 0 | 7.62 | 0
4 | 2025-05-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:04 | 12.8667 | IS17 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS17Inv1M4SCB5 | 0 | 0% | Module |  | Project Activities | 0.25833 | 0.25833 | 0.25833 | 0.79444 | 0 | 0 |  | 12.8667 | Informed to Project team | Open | 0 | 7.62 | 0
5 | 2025-05-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:04 | 12.8667 | IS30 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS30Inv1M4SCB4 | 223.3 | 0.06143% | Module |  | Project Activities | 0.25833 | 0.25833 | 0.25833 | 0.79444 | 0 | 0 |  | 12.8667 | Informed to Project team | Open | 0.0079038 | 7.62 | 999.8933
6 | 2025-05-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:04 | 12.8667 | IS30 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS30Inv2M3SCB5 | 159.5 | 0.04388% | Module |  | Project Activities | 0.25833 | 0.25833 | 0.25833 | 0.79444 | 0 | 0 |  | 12.8667 | Informed to Project team | Open | 0.0056456 | 7.62 | 714.2095
7 | 2025-05-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:04 | 12.8667 | IS31 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS31Inv1M1SCB6 | 223.3 | 0.06143% | Module |  | Project Activities | 0.25833 | 0.25833 | 0.25833 | 0.79444 | 0 | 0 |  | 12.8667 | Informed to Project team | Open | 0.0079038 | 7.62 | 999.8933
8 | 2025-05-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:04 | 12.8667 | IS33 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS33Inv1M1SCB1 | 191.4 | 0.05265% | Module |  | Project Activities | 0.25833 | 0.25833 | 0.25833 | 0.79444 | 0 | 0 |  | 12.8667 | Informed to Project team | Open | 0.0067747 | 7.62 | 857.0514
9 | 2025-05-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:04 | 12.8667 | IS33 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS33Inv1M2SCB3 | 191.4 | 0.05265% | Module |  | Project Activities | 0.25833 | 0.25833 | 0.25833 | 0.79444 | 0 | 0 |  | 12.8667 | Informed to Project team | Open | 0.0067747 | 7.62 | 857.0514
10 | 2025-05-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:04 | 12.8667 | IS33 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS33Inv1M3SCB4 | 223.3 | 0.06143% | Module |  | Project Activities | 0.25833 | 0.25833 | 0.25833 | 0.79444 | 0 | 0 |  | 12.8667 | Informed to Project team | Open | 0.0079038 | 7.62 | 999.8933
11 | 2025-05-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:04 | 12.8667 | IS33 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS33Inv1M4SCB5 | 223.3 | 0.06143% | Module |  | Project Activities | 0.25833 | 0.25833 | 0.25833 | 0.79444 | 0 | 0 |  | 12.8667 | Informed to Project team | Open | 0.0079038 | 7.62 | 999.8933
12 | 2025-05-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:06 | 12.8333 | IS3 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS3Inv2M4SCB6 | 221.27 | 0.06087% | Module |  | Project Activities | 0.26111 | 0.26111 | 0.26111 | 19:06 | 0 | 0 |  | 12.8333 | Informed to Project team | Open | 0.0078117 | 7.5 | 975.2001
13 | 2025-05-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:06 | 12.8333 | IS5 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS5Inv2M3SCB2 | 223.3 | 0.06143% | Module |  | Project Activities | 0.26111 | 0.26111 | 0.26111 | 19:06 | 0 | 0 |  | 12.8333 | Informed to Project team | Open | 0.0078833 | 7.5 | 984.1469
14 | 2025-05-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:06 | 12.8333 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | Module |  | Project Activities | 0.26111 | 0.26111 | 0.26111 | 19:06 | 0 | 0 |  | 12.8333 | Informed to Project team | Open | 0.0067571 | 7.5 | 843.5545
15 | 2025-05-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:06 | 12.8333 | IS17 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS17Inv1M3SCB4 | 0 | 0% | Module |  | Project Activities | 0.26111 | 0.26111 | 0.26111 | 19:06 | 0 | 0 |  | 12.8333 | Informed to Project team | Open | 0 | 7.5 | 0
16 | 2025-05-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:06 | 12.8333 | IS17 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS17Inv1M4SCB5 | 0 | 0% | Module |  | Project Activities | 0.26111 | 0.26111 | 0.26111 | 19:06 | 0 | 0 |  | 12.8333 | Informed to Project team | Open | 0 | 7.5 | 0
17 | 2025-05-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:06 | 12.8333 | IS30 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS30Inv1M4SCB6 | 223.3 | 0.06143% | Module |  | Project Activities | 0.26111 | 0.26111 | 0.26111 | 19:06 | 0 | 0 |  | 12.8333 | Informed to Project team | Open | 0.0078833 | 7.5 | 984.1469
18 | 2025-05-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:06 | 12.8333 | IS30 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS30Inv2M3SCB4 | 191.4 | 0.05265% | Module |  | Project Activities | 0.26111 | 0.26111 | 0.26111 | 19:06 | 0 | 0 |  | 12.8333 | Informed to Project team | Open | 0.0067571 | 7.5 | 843.5545
19 | 2025-05-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:14 | 18:15 | 12.0167 | IS3 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS3Inv2M4SCB5 | 221.27 | 0.06087% | Module |  | Project Activities | 6:14 | 6:14 | 6:14 | 18:15 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073146 | 6.9 | 897.1841
20 | 2025-05-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:14 | 18:15 | 12.0167 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | Module |  | Project Activities | 6:14 | 6:14 | 6:14 | 18:15 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 6.9 | 0
21 | 2025-05-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:14 | 18:15 | 12.0167 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | Module |  | Project Activities | 6:14 | 6:14 | 6:14 | 18:15 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0063271 | 6.9 | 776.0702
22 | 2025-05-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:14 | 18:15 | 12.0167 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | Module |  | Project Activities | 6:14 | 6:14 | 6:14 | 18:15 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0063271 | 6.9 | 776.0702
23 | 2025-05-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:14 | 18:15 | 12.0167 | IS6 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS6Inv1M3SCB5 | 223.3 | 0.06143% | Module |  | Project Activities | 6:14 | 6:14 | 6:14 | 18:15 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 6.9 | 905.4152
24 | 2025-05-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:14 | 18:15 | 12.0167 | IS6 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS6Inv1M4SCB5 | 223.3 | 0.06143% | Module |  | Project Activities | 6:14 | 6:14 | 6:14 | 18:15 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 6.9 | 905.4152
25 | 2025-05-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:14 | 18:15 | 12.0167 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | Module |  | Project Activities | 6:14 | 6:14 | 6:14 | 18:15 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 6.9 | 0
26 | 2025-05-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:14 | 18:15 | 12.0167 | IS12 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS12Inv1M4SCB4 | 0 | 0% | Module |  | Project Activities | 6:14 | 6:14 | 6:14 | 18:15 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 6.9 | 0
27 | 2025-05-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:14 | 18:15 | 12.0167 | IS17 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS17Inv1M3SCB5 | 0 | 0% | Module |  | Project Activities | 6:14 | 6:14 | 6:14 | 18:15 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 6.9 | 0
28 | 2025-05-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:14 | 18:15 | 12.0167 | IS17 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS17Inv1M4SCB3 | 0 | 0% | Module |  | Project Activities | 6:14 | 6:14 | 6:14 | 18:15 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 6.9 | 0
29 | 2025-05-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:14 | 18:15 | 12.0167 | IS30 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS30Inv1M4SCB4 | 223.3 | 0.06143% | Module |  | Project Activities | 6:14 | 6:14 | 6:14 | 18:15 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 6.9 | 905.4152
30 | 2025-05-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:14 | 18:15 | 12.0167 | IS30 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS30Inv2M3SCB5 | 159.5 | 0.04388% | Module |  | Project Activities | 6:14 | 6:14 | 6:14 | 18:15 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0052726 | 6.9 | 646.7251
31 | 2025-05-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:14 | 13.0167 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:14 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 7.4 | 971.025
32 | 2025-05-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:14 | 13.0167 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:14 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 7.4 | 832.3071
33 | 2025-05-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:14 | 13.0167 | IS6 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS6Inv1M3SCB5 | 223.3 | 0.06143% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:14 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 7.4 | 971.025
34 | 2025-05-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:14 | 13.0167 | IS6 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv1M4SCB6 | 191.4 | 0.05265% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:14 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 7.4 | 832.3071
35 | 2025-05-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:14 | 13.0167 | IS12 | Inv1 | M2 |  |  |  | 1 | 1 | IS12Inv1M2 | 0 | 0% | Inverter |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:14 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 7.4 | 0
36 | 2025-05-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:14 | 13.0167 | IS12 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS12Inv1M4SCB2 | 0 | 0% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:14 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 7.4 | 0
37 | 2025-05-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:14 | 13.0167 | IS30 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS30Inv1M4SCB3 | 223.3 | 0.06143% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:14 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 7.4 | 971.025
38 | 2025-05-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:14 | 13.0167 | IS30 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS30Inv2M3SCB4 | 191.4 | 0.05265% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:14 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 7.4 | 832.3071
39 | 2025-05-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:07 | 12.9 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:07 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 7.1 | 931.6591
40 | 2025-05-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:07 | 12.9 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:07 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 7.1 | 931.6591
41 | 2025-05-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:07 | 12.9 | IS6 | Inv1 | M3 |  |  |  | 1 | 1 | IS6Inv1M3 | 1307.9 | 0.3598% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:07 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.046414 | 7.1 | 5456.8605
42 | 2025-05-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:07 | 12.9 | IS6 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS6Inv1M4SCB4 | 223.3 | 0.06143% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:07 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 7.1 | 931.6591
43 | 2025-05-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:07 | 12.9 | IS12 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS12Inv1M2SCB4 | 0 | 0% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:07 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 7.1 | 0
44 | 2025-05-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:07 | 12.9 | IS12 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS12Inv1M4SCB6 | 0 | 0% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:07 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 7.1 | 0
45 | 2025-05-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:07 | 12.9 | IS30 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS30Inv1M4SCB1 | 223.3 | 0.06143% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:07 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 7.1 | 931.6591
46 | 2025-05-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:13 | 19:07 | 12.9 | IS30 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS30Inv2M3SCB3 | 223.3 | 0.06143% | Module |  | Project Activities | 6:13 | 6:13 | 6:13 | 19:07 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 7.1 | 931.6591
47 | 2025-05-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:06 | 12.9 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | Module |  | Project Activities | 6:12 | 6:12 | 6:12 | 19:06 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 6.8 | 764.8228
48 | 2025-05-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:06 | 12.9 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | Module |  | Project Activities | 6:12 | 6:12 | 6:12 | 19:06 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.8 | 892.2932
49 | 2025-05-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:06 | 12.9 | IS6 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS6Inv1M3SCB6 | 223.3 | 0.06143% | Module |  | Project Activities | 6:12 | 6:12 | 6:12 | 19:06 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.8 | 892.2932
50 | 2025-05-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:06 | 12.9 | IS6 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS6Inv1M4SCB3 | 191.4 | 0.05265% | Module |  | Project Activities | 6:12 | 6:12 | 6:12 | 19:06 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 6.8 | 764.8228
51 | 2025-05-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:06 | 12.9 | IS12 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS12Inv1M2SCB4 | 0 | 0% | Module |  | Project Activities | 6:12 | 6:12 | 6:12 | 19:06 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.8 | 0
52 | 2025-05-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:06 | 12.9 | IS12 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS12Inv1M4SCB6 | 0 | 0% | Module |  | Project Activities | 6:12 | 6:12 | 6:12 | 19:06 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.8 | 0
53 | 2025-05-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:06 | 12.9 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | Project Activities | 6:12 | 6:12 | 6:12 | 19:06 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.045282 | 6.8 | 5098.8184
54 | 2025-05-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:06 | 12.9 | IS30 | Inv2 | M3 |  |  |  | 1 | 1 | IS30Inv2M3 | 1020.8 | 0.2808% | Module |  | Project Activities | 6:12 | 6:12 | 6:12 | 19:06 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.036225 | 6.8 | 4079.0547
55 | 2025-05-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:45 | 19:02 | 12.2833 | IS6 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS6Inv1M1SCB1 | 191.4 | 0.05265% | Module |  | Project Activities | 6:45 | 6:45 | 6:45 | 19:02 | 0 | 0 |  | 12.2833 | Informed to Project team | Open | 0.0064675 | 3.3 | 371.164
56 | 2025-05-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:45 | 19:02 | 12.2833 | IS6 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS6Inv1M2SCB2 | 223.3 | 0.06143% | Module |  | Project Activities | 6:45 | 6:45 | 6:45 | 19:02 | 0 | 0 |  | 12.2833 | Informed to Project team | Open | 0.0075455 | 3.3 | 433.0247
57 | 2025-05-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:45 | 19:02 | 12.2833 | IS6 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS6Inv1M3SCB4 | 223.3 | 0.06143% | Module |  | Project Activities | 6:45 | 6:45 | 6:45 | 19:02 | 0 | 0 |  | 12.2833 | Informed to Project team | Open | 0.0075455 | 3.3 | 433.0247
58 | 2025-05-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:45 | 19:02 | 12.2833 | IS6 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS6Inv1M4SCB5 | 223.3 | 0.06143% | Module |  | Project Activities | 6:45 | 6:45 | 6:45 | 19:02 | 0 | 0 |  | 12.2833 | Informed to Project team | Open | 0.0075455 | 3.3 | 433.0247
59 | 2025-05-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:45 | 19:02 | 12.2833 | IS12 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS12Inv1M2SCB6 | 0 | 0% | Module |  | Project Activities | 6:45 | 6:45 | 6:45 | 19:02 | 0 | 0 |  | 12.2833 | Informed to Project team | Open | 0 | 3.3 | 0
60 | 2025-05-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:45 | 19:02 | 12.2833 | IS12 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS12Inv1M4SCB3 | 0 | 0% | Module |  | Project Activities | 6:45 | 6:45 | 6:45 | 19:02 | 0 | 0 |  | 12.2833 | Informed to Project team | Open | 0 | 3.3 | 0
61 | 2025-05-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:45 | 19:02 | 12.2833 | IS30 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS30Inv1M4SCB4 | 223.3 | 0.06143% | Module |  | Project Activities | 6:45 | 6:45 | 6:45 | 19:02 | 0 | 0 |  | 12.2833 | Informed to Project team | Open | 0.0075455 | 3.3 | 433.0247
62 | 2025-05-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:45 | 19:02 | 12.2833 | IS30 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS30Inv2M3SCB5 | 159.5 | 0.04388% | Module |  | Project Activities | 6:45 | 6:45 | 6:45 | 19:02 | 0 | 0 |  | 12.2833 | Informed to Project team | Open | 0.0053896 | 3.3 | 309.3033
63 | 2025-05-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 19:05 | 12.8 | IS49 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS49Inv1M1SCB4 | 223.3 | 0.06143% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 19:05 | 0 | 0 |  | 12.8 | Informed to Project team | Open | 0.0078629 | 5.7 | 747.9517
64 | 2025-05-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 19:05 | 12.8 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 19:05 | 0 | 0 |  | 12.8 | Informed to Project team | Open | 0.0078629 | 5.7 | 747.9517
65 | 2025-05-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 19:05 | 12.8 | IS6 | Inv1 | M2 |  |  |  | 1 | 1 | IS6Inv1M2 | 1276 | 0.351% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 19:05 | 0 | 0 |  | 12.8 | Informed to Project team | Open | 0.044931 | 5.7 | 4274.0096
66 | 2025-05-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 19:05 | 12.8 | IS6 | Inv1 | M3 |  |  |  | 1 | 1 | IS6Inv1M3 | 1307.9 | 0.3598% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 19:05 | 0 | 0 |  | 12.8 | Informed to Project team | Open | 0.046054 | 5.7 | 4380.8598
67 | 2025-05-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 19:05 | 12.8 | IS6 | Inv1 | M4 |  |  |  | 1 | 1 | IS6Inv1M4 | 1244.1 | 0.3422% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 19:05 | 0 | 0 |  | 12.8 | Informed to Project team | Open | 0.043807 | 5.7 | 4167.1593
68 | 2025-05-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 19:05 | 12.8 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 19:05 | 0 | 0 |  | 12.8 | Informed to Project team | Open | 0 | 5.7 | 0
69 | 2025-05-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 19:05 | 12.8 | IS12 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS12Inv1M4SCB5 | 0 | 0% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 19:05 | 0 | 0 |  | 12.8 | Informed to Project team | Open | 0 | 5.7 | 0
70 | 2025-05-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 19:05 | 12.8 | IS30 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS30Inv1M4SCB6 | 223.3 | 0.06143% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 19:05 | 0 | 0 |  | 12.8 | Informed to Project team | Open | 0.0078629 | 5.7 | 747.9517
71 | 2025-05-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 19:05 | 12.8 | IS30 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS30Inv2M3SCB4 | 191.4 | 0.05265% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 19:05 | 0 | 0 |  | 12.8 | Informed to Project team | Open | 0.0067396 | 5.7 | 641.1014
72 | 2025-05-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 18:50 | 12.55 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 18:50 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 6.12 | 803.0639
73 | 2025-05-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 18:50 | 12.55 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 18:50 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 6.12 | 803.0639
74 | 2025-05-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 18:50 | 12.55 | IS6 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS6Inv1M3SCB4 | 223.3 | 0.06143% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 18:50 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 6.12 | 803.0639
75 | 2025-05-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 18:50 | 12.55 | IS6 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS6Inv1M4SCB5 | 223.3 | 0.06143% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 18:50 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 6.12 | 803.0639
76 | 2025-05-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 18:50 | 12.55 | IS12 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS12Inv1M2SCB6 | 0 | 0% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 18:50 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 6.12 | 0
77 | 2025-05-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 18:50 | 12.55 | IS12 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS12Inv1M4SCB6 | 0 | 0% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 18:50 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 6.12 | 0
78 | 2025-05-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 18:50 | 12.55 | IS33 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS33Inv1M4SCB4 | 223.3 | 0.06143% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 18:50 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 6.12 | 803.0639
79 | 2025-05-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 18:50 | 12.55 | IS33 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS33Inv2M3SCB2 | 207.35 | 0.05704% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 18:50 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0071586 | 6.12 | 745.7022
80 | 2025-05-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 18:50 | 12.55 | IS49 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS49INV1M1SCB3 | 223.3 | 0.06143% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 18:50 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 6.12 | 803.0639
81 | 2025-05-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:17 | 18:50 | 12.55 | IS21 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS21INV2M2SCB2 | 127.6 | 0.0351% | Module |  | Project Activities | 6:17 | 6:17 | 6:17 | 18:50 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0044053 | 6.12 | 458.8937
82 | 2025-05-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 18:58 | 12.7167 | IS6 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS6Inv1M1SCB1 | 191.4 | 0.05265% | Module |  | Project Activities | 6:15 | 6:15 | 6:15 | 18:58 | 0 | 0 |  | 12.7167 | Informed to Project team | Open | 0.0066957 | 6.12 | 688.3405
83 | 2025-05-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 18:58 | 12.7167 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | Module |  | Project Activities | 6:15 | 6:15 | 6:15 | 18:58 | 0 | 0 |  | 12.7167 | Informed to Project team | Open | 0.0066957 | 6.12 | 688.3405
84 | 2025-05-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 18:58 | 12.7167 | IS6 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS6Inv1M3SCB5 | 223.3 | 0.06143% | Module |  | Project Activities | 6:15 | 6:15 | 6:15 | 18:58 | 0 | 0 |  | 12.7167 | Informed to Project team | Open | 0.0078117 | 6.12 | 803.0639
85 | 2025-05-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 18:58 | 12.7167 | IS6 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS6Inv1M4SCB4 | 223.3 | 0.06143% | Module |  | Project Activities | 6:15 | 6:15 | 6:15 | 18:58 | 0 | 0 |  | 12.7167 | Informed to Project team | Open | 0.0078117 | 6.12 | 803.0639
86 | 2025-05-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 18:58 | 12.7167 | IS12 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS12INV1M2SCB5 | 0 | 0% | Module |  | Project Activities | 6:15 | 6:15 | 6:15 | 18:58 | 0 | 0 |  | 12.7167 | Informed to Project team | Open | 0 | 6.12 | 0
87 | 2025-05-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 18:58 | 12.7167 | IS12 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS12INV1M4SCB6 | 0 | 0% | Module |  | Project Activities | 6:15 | 6:15 | 6:15 | 18:58 | 0 | 0 |  | 12.7167 | Informed to Project team | Open | 0 | 6.12 | 0
88 | 2025-05-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 18:58 | 12.7167 | IS30 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS30INV1M4SCB1 | 223.3 | 0.06143% | Module |  | Project Activities | 6:15 | 6:15 | 6:15 | 18:58 | 0 | 0 |  | 12.7167 | Informed to Project team | Open | 0.0078117 | 6.12 | 803.0639
89 | 2025-05-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 18:58 | 12.7167 | IS30 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS30INV2M3SCB3 | 223.3 | 0.06143% | Module |  | Project Activities | 6:15 | 6:15 | 6:15 | 18:58 | 0 | 0 |  | 12.7167 | Informed to Project team | Open | 0.0078117 | 6.12 | 803.0639
90 | 2025-05-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 18:58 | 12.7167 | IS33 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS33INV1M4SCB4 | 223.3 | 0.06143% | Module |  | Project Activities | 6:15 | 6:15 | 6:15 | 18:58 | 0 | 0 |  | 12.7167 | Informed to Project team | Open | 0.0078117 | 6.12 | 803.0639
91 | 2025-05-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 18:58 | 12.7167 | IS33 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS33INV2M1SCB5 | 191.4 | 0.05265% | Module |  | Project Activities | 6:15 | 6:15 | 6:15 | 18:58 | 0 | 0 |  | 12.7167 | Informed to Project team | Open | 0.0066957 | 6.12 | 688.3405
92 | 2025-05-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:09 | 12.8833 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | Module |  | Project Activities | 6:16 | 6:16 | 6:16 | 19:09 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 6.12 | 803.0639
93 | 2025-05-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:09 | 12.8833 | IS6 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS6Inv1M2SCB2 | 223.3 | 0.06143% | Module |  | Project Activities | 6:16 | 6:16 | 6:16 | 19:09 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 6.12 | 803.0639
94 | 2025-05-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:09 | 12.8833 | IS6 | Inv1 | M3 | SCB3 |  |  | 1 | 1 | IS6Inv1M3SCB3 | 223.3 | 0.06143% | Module |  | Project Activities | 6:16 | 6:16 | 6:16 | 19:09 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 6.12 | 803.0639
95 | 2025-05-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:09 | 12.8833 | IS6 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS6Inv1M4SCB4 | 223.3 | 0.06143% | Module |  | Project Activities | 6:16 | 6:16 | 6:16 | 19:09 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 6.12 | 803.0639
96 | 2025-05-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:09 | 12.8833 | IS12 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS12INV1M4SCB5 | 0 | 0% | Module |  | Project Activities | 6:16 | 6:16 | 6:16 | 19:09 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0 | 6.12 | 0
97 | 2025-05-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:09 | 12.8833 | IS30 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS30INV1M4SCB6 | 223.3 | 0.06143% | Module |  | Project Activities | 6:16 | 6:16 | 6:16 | 19:09 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 6.12 | 803.0639
98 | 2025-05-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:09 | 12.8833 | IS30 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS30INV2M3SCB4 | 191.4 | 0.05265% | Module |  | Project Activities | 6:16 | 6:16 | 6:16 | 19:09 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 6.12 | 688.3405
99 | 2025-05-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:09 | 12.8833 | IS30 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS30INV2M4SCB5 | 223.3 | 0.06143% | Module |  | Project Activities | 6:16 | 6:16 | 6:16 | 19:09 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 6.12 | 803.0639
100 | 2025-05-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:09 | 12.8833 | IS33 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS33INV1M4SCB6 | 191.4 | 0.05265% | Module |  | Project Activities | 6:16 | 6:16 | 6:16 | 19:09 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 6.12 | 688.3405
101 | 2025-05-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:16 | 19:09 | 12.8833 | IS33 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS33INV2M1SCB3 | 223.3 | 0.06143% | Module |  | Project Activities | 6:16 | 6:16 | 6:16 | 19:09 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 6.12 | 803.0639
102 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS6 | INV1 |  | SCB4 |  |  | 1 | 1 | IS6INV1SCB4 |  |  | Inverter |  | Project Activities | 6:12 | 6:12 | 6:12 | 9:30 | 0 | 0 |  | 3.3 | Informed to Project team | Open |  | 1.106
103 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS9 | INV1 |  | SCB5 |  |  | 1 | 1 | IS9INV1SCB5 |  |  | Inverter |  | Project Activities | 6:12 | 6:12 | 6:12 | 9:30 | 0 | 0 |  | 3.3 | Informed to Project team | Open |  | 1.106
104 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS9 | INV2 |  | SCB5 |  |  | 1 | 1 | IS9INV2SCB5 |  |  | Inverter |  | Project Activities | 6:12 | 6:12 | 6:12 | 9:30 | 0 | 0 |  | 3.3 | Informed to Project team | Open |  | 1.106
105 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS12 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS12INV1M4SCB3 | 0 | 0% | Module |  | Project Activities | 6:12 | 6:12 | 6:12 | 9:30 | 0 | 0 |  | 3.3 | Informed to Project team | Open | 0 | 1.106 | 0
106 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS30 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS30INV1M4SCB4 | 223.3 | 0.06143% | Module |  | Project Activities | 6:12 | 6:12 | 6:12 | 9:30 | 0 | 0 |  | 3.3 | Informed to Project team | Open | 0.0020271 | 1.106 | 145.1321
107 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS30 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS30INV2M2SCB5 | 223.3 | 0.06143% | Module |  | Project Activities | 6:12 | 6:12 | 6:12 | 9:30 | 0 | 0 |  | 3.3 | Informed to Project team | Open | 0.0020271 | 1.106 | 145.1321
108 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS30 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS30INV2M3SCB3 | 223.3 | 0.06143% | Module |  | Project Activities | 6:12 | 6:12 | 6:12 | 9:30 | 0 | 0 |  | 3.3 | Informed to Project team | Open | 0.0020271 | 1.106 | 145.1321
109 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS33 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS33INV1M4SCB4 | 223.3 | 0.06143% | Module |  | Project Activities | 6:12 | 6:12 | 6:12 | 9:30 | 0 | 0 |  | 3.3 | Informed to Project team | Open | 0.0020271 | 1.106 | 145.1321
110 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS33 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS33INV2M1SCB5 | 191.4 | 0.05265% | Module |  | Project Activities | 6:12 | 6:12 | 6:12 | 9:30 | 0 | 0 |  | 3.3 | Informed to Project team | Open | 0.0017375 | 1.106 | 124.399
111 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS6 | INV1 |  | SCB6 |  |  | 1 | 1 | IS6INV1SCB6 |  |  | Inverter |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:10 | 0 | 0 |  | 3.6667 | Informed to Project team | Open |  | 1.1229
112 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS9 | INV1 |  | SCB4 |  |  | 1 | 1 | IS9INV1SCB4 |  |  | Inverter |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:10 | 0 | 0 |  | 3.6667 | Informed to Project team | Open |  | 1.1229
113 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS9 | INV2 |  | SCB5 |  |  | 1 | 1 | IS9INV2SCB5 |  |  | Inverter |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:10 | 0 | 0 |  | 3.6667 | Informed to Project team | Open |  | 1.1229
114 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS12 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS12INV1M4SCB6 | 0 | 0% | Module |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:10 | 0 | 0 |  | 3.6667 | Informed to Project team | Open | 0 | 1.1229 | 0
115 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS30 | INV1 | M4 | SCB2 |  |  | 1 | 1 | IS30INV1M4SCB2 | 223.3 | 0.06143% | Module |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:10 | 0 | 0 |  | 3.6667 | Informed to Project team | Open | 0.0022524 | 1.1229 | 147.3524
116 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS30 | INV2 | M2 | SCB3 |  |  | 1 | 1 | IS30INV2M2SCB3 | 95.7 | 0.02633% | Module |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:10 | 0 | 0 |  | 3.6667 | Informed to Project team | Open | 0.00096531 | 1.1229 | 63.151
117 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS30 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS30INV2M3SCB4 | 191.4 | 0.05265% | Module |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:10 | 0 | 0 |  | 3.6667 | Informed to Project team | Open | 0.0019306 | 1.1229 | 126.3021
118 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS33 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS33INV1M4SCB5 | 223.3 | 0.06143% | Module |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:10 | 0 | 0 |  | 3.6667 | Informed to Project team | Open | 0.0022524 | 1.1229 | 147.3524
119 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 | IS33 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS33INV2M1SCB6 | 223.3 | 0.06143% | Module |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:10 | 0 | 0 |  | 3.6667 | Informed to Project team | Open | 0.0022524 | 1.1229 | 147.3524
120 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:12 | 19:11 | 12.9833 |  |  |  | SCB4 |  | Line_Bay1 | 0 | 1 | Line_Bay1 | 363511.955 | 100% | Grid System |  | 220 KV Line Shutdown | 15:30 | 15:30 | 15:30 | 18:56 | 0 | 0 | 82:24 | 3.4333 | Plant Charge | Close | 3.4333 | 1.0948 | 233869.6685
121 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS6 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS6INV1M1SCB4 | 191.4 | 0.05265% | Module |  | Project Activities | 6:15 | 6:15 | 6:15 | 9:30 | 0 | 0 |  | 3.25 | Informed to Project team | Open | 0.0017112 | 0.91599 | 103.0247
122 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS6 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS6INV2M1SCB6 | 223.3 | 0.06143% | Module |  | Project Activities | 6:15 | 6:15 | 6:15 | 9:30 | 0 | 0 |  | 3.25 | Informed to Project team | Open | 0.0019964 | 0.91599 | 120.1955
123 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS6 | INV2 |  | SCB1 |  |  | 1 | 1 | IS6INV2SCB1 |  |  | Inverter |  | Communication Issue in inverter | 6:15 | 6:15 | 6:15 | 7:30 | 0 | 0 | 30:00 | 1.25 | after visually inspection INV restart | Close |  | 0.11375
124 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS9 | INV1 |  | SCB3 |  |  | 1 | 1 | IS9INV1SCB3 |  |  | Inverter |  | Communication Issue in inverter | 6:15 | 6:15 | 6:15 | 7:40 | 0 | 0 | 34:00 | 1.4167 | after visually inspection INV restart | Close |  | 0.14194
125 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS9 | INV2 |  | SCB4 |  |  | 1 | 1 | IS9INV2SCB4 |  |  | Inverter |  | Communication Issue in inverter | 6:15 | 6:15 | 6:15 | 7:40 | 0 | 0 | 34:00 | 1.4167 | after visually inspection INV restart | Close |  | 0.14194
126 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS12 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS12INV1M4SCB5 | 0 | 0% | Module |  | Project Activities | 6:15 | 6:15 | 6:15 | 9:30 | 0 | 0 |  | 3.25 | Informed to Project team | Open | 0 | 0.91599 | 0
127 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS15 | INV1 |  | SCB6 |  |  | 1 | 1 | IS15INV1SCB6 |  |  | Inverter |  | Inverter Shutdown mode | 15:30 | 15:30 | 15:30 | 16:08 | 0 | 0 | 15:12 | 0.63333 | after visually inspection INV restart | Close |  | 0.20701
128 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS15 | INV2 |  | SCB3 |  |  | 1 | 1 | IS15INV2SCB3 |  |  | Inverter |  | Inverter Shutdown mode | 15:30 | 15:30 | 15:30 | 16:08 | 0 | 0 | 15:12 | 0.63333 | after visually inspection INV restart | Close |  | 0.20701
129 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS17 | INV1 |  | SCB4 |  |  | 1 | 1 | IS17INV1SCB4 |  |  | Inverter |  | Inverter Shutdown mode | 15:30 | 15:30 | 15:30 | 16:18 | 0 | 0 | 19:12 | 0.8 | after visually inspection INV restart | Close |  | 0.25541
130 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS17 | INV2 |  | SCB6 |  |  | 1 | 1 | IS17INV2SCB6 |  |  | Inverter |  | Inverter Shutdown mode | 15:30 | 15:30 | 15:30 | 16:18 | 0 | 0 | 19:12 | 0.8 | after visually inspection INV restart | Close |  | 0.25541
131 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS29 | INV1 |  | SCB1 |  |  | 1 | 1 | IS29INV1SCB1 |  |  | Inverter |  | Inverter Shutdown mode | 15:30 | 15:30 | 15:30 | 17:15 | 0 | 0 | 42:00 | 1.75 | after visually inspection INV restart | Close |  | 0.62696
132 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS29 | INV2 |  | SCB2 |  |  | 1 | 1 | IS29INV2SCB2 |  |  | Inverter |  | Inverter Shutdown mode | 15:30 | 15:30 | 15:30 | 17:15 | 0 | 0 | 42:00 | 1.75 | after visually inspection INV restart | Close |  | 0.62696
133 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS30 | INV1 |  | SCB4 |  |  | 1 | 1 | IS30INV1SCB4 |  |  | Inverter |  | Inverter Shutdown mode | 15:30 | 15:30 | 15:30 | 17:04 | 0 | 0 | 37:36 | 1.5667 | after visually inspection INV restart | Close |  | 0.60452
134 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS30 | INV2 |  | SCB5 |  |  | 1 | 1 | IS30INV2SCB5 |  |  | Inverter |  | Inverter Shutdown mode | 15:30 | 15:30 | 15:30 | 17:04 | 0 | 0 | 37:36 | 1.5667 | after visually inspection INV restart | Close |  | 0.60452
135 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS33 | INV1 |  | SCB6 |  |  | 1 | 1 | IS33INV1SCB6 |  |  | Inverter |  | Inverter Shutdown mode | 15:30 | 15:30 | 15:30 | 17:24 | 0 | 0 | 45:36 | 1.9 | after visually inspection INV restart | Close |  | 0.64448
136 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS33 | INV2 |  | SCB3 |  |  | 1 | 1 | IS33INV2SCB3 |  |  | Inverter |  | Inverter in Ground Fault Project team work at SCB | 15:30 | 15:30 | 15:30 | 19:18 | 0 | 0 |  | 3.8 | Informed to Project team | Open |  | 0.92307
137 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS6 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS6INV1M1SCB4 | 191.4 | 0.05265% | Module |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:18 | 0 | 0 |  | 3.8 | Informed to Project team | Open | 0.0020008 | 0.92307 | 103.8209
138 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS6 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS6INV2M1SCB5 | 223.3 | 0.06143% | Module |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:18 | 0 | 0 |  | 3.8 | Informed to Project team | Open | 0.0023343 | 0.92307 | 121.1243
139 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS12 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS12INV1M4SCB4 | 0 | 0% | Module |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:18 | 0 | 0 |  | 3.8 | Informed to Project team | Open | 0 | 0.92307 | 0
140 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities | 6:15 | 6:15 | 6:15 | 9:30 | 0 | 0 |  | 3.25 | Informed to Project team | Open | 0.0017112 | 0.91599 | 103.0247
141 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS1 | INV1 | M1 |  |  |  | 1 | 1 | IS1INV1M1 | 957 | 0.2633% | SCB |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:18 | 0 | 0 |  | 3.8 | Informed to Project team | Open | 0.010004 | 0.92307 | 519.1043
142 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS1 | INV1 | M1 |  |  |  | 1 | 1 | IS1INV1M1 | 957 | 0.2633% | SCB |  | Project Activities | 6:15 | 6:15 | 6:15 | 9:30 | 0 | 0 |  | 3.25 | Informed to Project team | Open | 0.0085561 | 0.91599 | 515.1237
143 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS1 | INV1 | M1 |  |  |  | 1 | 1 | IS1INV1M1 | 957 | 0.2633% | SCB |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:18 | 0 | 0 |  | 3.8 | Informed to Project team | Open | 0.010004 | 0.92307 | 519.1043
144 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS1 | INV1 | M1 |  |  |  | 1 | 1 | IS1INV1M1 | 957 | 0.2633% | SCB |  | Project Activities | 6:15 | 6:15 | 6:15 | 9:30 | 0 | 0 |  | 3.25 | Informed to Project team | Open | 0.0085561 | 0.91599 | 515.1237
145 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS1 | INV1 | M1 |  |  |  | 1 | 1 | IS1INV1M1 | 957 | 0.2633% | SCB |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:18 | 0 | 0 |  | 3.8 | Informed to Project team | Open | 0.010004 | 0.92307 | 519.1043
146 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS1 | INV1 | M1 |  |  |  | 1 | 1 | IS1INV1M1 | 957 | 0.2633% | SCB |  | Project Activities | 6:15 | 6:15 | 6:15 | 9:30 | 0 | 0 |  | 3.25 | Informed to Project team | Open | 0.0085561 | 0.91599 | 515.1237
147 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS1 | INV1 | M1 |  |  |  | 1 | 1 | IS1INV1M1 | 957 | 0.2633% | SCB |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:18 | 0 | 0 |  | 3.8 | Informed to Project team | Open | 0.010004 | 0.92307 | 519.1043
148 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS3 | INV2 | M3 |  |  |  | 1 | 1 | IS3INV2M3 | 1296.01 | 0.3565% | SCB |  | Project Activities | 6:15 | 6:15 | 6:15 | 9:30 | 0 | 0 |  | 3.25 | Informed to Project team | Open | 0.011587 | 0.91599 | 697.6024
149 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 6:15 | 19:18 | 13.05 | IS3 | INV2 | M3 |  |  |  | 1 | 1 | IS3INV2M3 | 1296.01 | 0.3565% | SCB |  | Project Activities | 15:30 | 15:30 | 15:30 | 19:18 | 0 | 0 |  | 3.8 | Informed to Project team | Open | 0.013548 | 0.92307 | 702.9931
150 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS29 | INV2 | M4 |  |  |  | 1 | 1 | IS29INV2M4 | 1164.35 | 0.3203% | Inverter |  | Control Power Supply Abnormal | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.041747 | 6.6605 | 5141.3111
151 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS30 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS30INV2M3SCB3 | 223.3 | 0.06143% | Inverter |  | Control Power Supply Abnormal | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
152 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | Inverter |  | Emergency Stop | 6:15 | 6:15 | 6:15 | 11:30 | 0 | 0 | 126:00 | 5.25 | after visually inspection INV restart | Close | 0.003225 | 2.262 | 334.8587
153 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS33 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS33INV2M4SCB6 | 223.3 | 0.06143% | Inverter |  | Emergency Stop | 6:15 | 6:15 | 6:15 | 11:30 | 0 | 0 | 126:00 | 5.25 | after visually inspection INV restart | Close | 0.003225 | 2.262 | 334.8587
154 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS1 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS1INV1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0034312 | 6.6605 | 422.5735
155 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 6.6605 | 845.147
156 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 6.6605 | 845.147
157 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS1 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS1INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
158 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS1 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS1INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
159 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS3 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS3INV2M3SCB5 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0079334 | 6.6605 | 977.0412
160 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS6 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS6INV1M1SCB6 | 223.3 | 0.06143% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
161 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
162 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 6.6605 | 845.147
163 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS6 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS6INV1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
164 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
165 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS6 | INV2 | M4 | SCB2 |  |  | 1 | 1 | IS6INV2M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
166 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS9 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS9INV1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
167 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS12 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS12INV1M2SCB4 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 6.6605 | 0
168 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS12 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS12INV1M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 6.6605 | 0
169 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS12 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS12INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
170 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS17 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS17INV1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 6.6605 | 0
171 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS29 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS29INV1M2SCB6 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0011437 | 6.6605 | 140.8578
172 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS29 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS29INV1M2SCB1 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.004575 | 6.6605 | 563.4314
173 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS29 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS29INV1M3SCB3 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.004575 | 6.6605 | 563.4314
174 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 6.6605 | 845.147
175 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 6.6605 | 704.2892
176 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | Inverter |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
177 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | Inverter |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 6.6605 | 845.147
178 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS29 | INV2 | M4 | SCB3 |  |  | 1 | 1 | IS29INV2M4SCB3 | 207.35 | 0.05704% | Inverter |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0074343 | 6.6605 | 915.576
179 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
180 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 6.6605 | 704.2892
181 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS30 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS30INV1M1SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
182 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS30 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS30INV1M4SCB4 | 223.3 | 0.06143% | Inverter |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
183 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS33 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS33INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 6.6605 | 845.147
184 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 6.6605 | 845.147
185 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS33 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS33INV1M4SCB3 | 191.4 | 0.05265% | Inverter |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 6.6605 | 845.147
186 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS33 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS33INV2M1SCB4 | 223.3 | 0.06143% | Inverter |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
187 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
188 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
189 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:15 | 19:17 | 13.0333 | IS33 | INV2 | M2 | SCB3 |  |  | 1 | 1 | IS33INV2M2SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:15 | 6:15 | 6:15 | 19:17 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 6.6605 | 986.0049
190 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS29INV2M4SCB4 | 223.3 | 0.06143% | Inverter |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 9:06 | 0 | 0 | 68:48 | 2.8667 | Rectification work done INV restored | Close | 0.001761 | 0.66203 | 98.0056
191 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS30INV2M3SCB5 | 159.5 | 0.04388% | Inverter |  | Control Power Supply Abnormal | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0057406 | 7.0793 | 748.5767
192 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0068888 | 7.0793 | 898.2921
193 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS1 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS1INV1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0034444 | 7.0793 | 449.146
194 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0068888 | 7.0793 | 898.2921
195 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS1 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS1INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0057406 | 7.0793 | 748.5767
196 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS1 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS1INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
197 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS3 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS3INV2M3SCB5 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0079638 | 7.0793 | 1038.4801
198 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS6 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS6INV1M1SCB6 | 223.3 | 0.06143% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
199 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS6 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS6INV1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
200 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
201 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0068888 | 7.0793 | 898.2921
202 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
203 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
204 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0068888 | 7.0793 | 898.2921
205 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS12 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS12INV1M2SCB4 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0 | 7.0793 | 0
206 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS12 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS12INV1M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0 | 7.0793 | 0
207 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS12 | INV2 | M1 | SCB1 |  |  | 1 | 1 | IS12INV2M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
208 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS17 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS17INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0 | 7.0793 | 0
209 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0057406 | 7.0793 | 748.5767
210 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0057406 | 7.0793 | 748.5767
211 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0057406 | 7.0793 | 748.5767
212 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS29INV1M3SCB1 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0057406 | 7.0793 | 748.5767
213 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS29INV1M3SCB3 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0045925 | 7.0793 | 598.8614
214 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
215 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
216 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0068888 | 7.0793 | 898.2921
217 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV1 | M4 | SCB2 |  |  | 1 | 1 | IS29INV1M4SCB2 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0045925 | 7.0793 | 598.8614
218 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
219 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
220 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0068888 | 7.0793 | 898.2921
221 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
222 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0068888 | 7.0793 | 898.2921
223 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
224 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
225 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
226 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV2 | M2 |  |  |  | 1 | 1 | IS29INV2M2 | 1052.7 | 0.2896% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.037888 | 7.0793 | 4940.6065
227 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV2 | M3 |  |  |  | 1 | 1 | IS29INV2M3 | 893.2 | 0.2457% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.032148 | 7.0793 | 4192.0298
228 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV2 | M3 |  |  |  | 1 | 1 | IS29INV2M3 | 893.2 | 0.2457% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.032148 | 7.0793 | 4192.0298
229 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV2 | M3 |  |  |  | 1 | 1 | IS29INV2M3 | 893.2 | 0.2457% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.032148 | 7.0793 | 4192.0298
230 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS29 | INV2 | M4 |  |  |  | 1 | 1 | IS29INV2M4 | 1164.35 | 0.3203% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.041907 | 7.0793 | 5464.6103
231 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV1 | M1 |  |  |  | 1 | 1 | IS30INV1M1 | 1244.1 | 0.3422% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.044777 | 7.0793 | 5838.8986
232 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV1 | M1 |  |  |  | 1 | 1 | IS30INV1M1 | 1244.1 | 0.3422% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.044777 | 7.0793 | 5838.8986
233 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV1 | M1 |  |  |  | 1 | 1 | IS30INV1M1 | 1244.1 | 0.3422% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.044777 | 7.0793 | 5838.8986
234 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV1 | M2 |  |  |  | 1 | 1 | IS30INV1M2 | 1276 | 0.351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.045925 | 7.0793 | 5988.614
235 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV1 | M2 |  |  |  | 1 | 1 | IS30INV1M2 | 1276 | 0.351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.045925 | 7.0793 | 5988.614
236 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV1 | M2 |  |  |  | 1 | 1 | IS30INV1M2 | 1276 | 0.351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.045925 | 7.0793 | 5988.614
237 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
238 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0057406 | 7.0793 | 748.5767
239 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0045925 | 7.0793 | 598.8614
240 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
241 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS30INV1M4SCB5 | 159.5 | 0.04388% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0057406 | 7.0793 | 748.5767
242 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
243 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
244 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
245 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0045925 | 7.0793 | 598.8614
246 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0068888 | 7.0793 | 898.2921
247 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS30INV2M2SCB6 | 191.4 | 0.05265% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0068888 | 7.0793 | 898.2921
248 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS30INV2M3SCB4 | 191.4 | 0.05265% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0068888 | 7.0793 | 898.2921
249 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS30 | INV2 | M4 | SCB2 |  |  | 1 | 1 | IS30INV2M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
250 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS33 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS33INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0068888 | 7.0793 | 898.2921
251 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS33 | INV1 | M1 | SCB2 |  |  | 1 | 1 | IS33INV1M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0068888 | 7.0793 | 898.2921
252 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0011481 | 7.0793 | 149.7153
253 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
254 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
255 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS2 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS2INV2M2SCB4 | 223.3 | 0.06143% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0080369 | 7.0793 | 1048.0074
256 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0 | 7.0793 | 0
257 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:19 | 13.0833 | IS21 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS21INV2M2SCB6 | 111.65 | 0.03071% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:19 | 0 | 0 |  | 13.0833 | Informed to Project team | Open | 0.0040184 | 7.0793 | 524.0037
258 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV2 | M3 | SCB1 |  |  | 1 | 1 | IS30INV2M3SCB1 | 159.5 | 0.04388% | Inverter |  | Control Power Supply Abnormal | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 7.0261 | 742.9489
259 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
260 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS1 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS1INV1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0034181 | 7.0261 | 445.7693
261 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
262 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS1 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS1INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 7.0261 | 742.9489
263 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS1 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS1INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 7.0261 | 594.3591
264 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS1 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS1INV1M3SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 7.0261 | 742.9489
265 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS3 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS3INV2M3SCB4 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.007903 | 7.0261 | 1030.6727
266 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS6 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS6INV1M1SCB5 | 223.3 | 0.06143% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
267 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
268 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
269 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
270 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
271 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS6 | INV2 | M4 | SCB3 |  |  | 1 | 1 | IS6INV2M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
272 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
273 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS12 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS12INV1M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 7.0261 | 0
274 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS12 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS12INV1M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 7.0261 | 0
275 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS12 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS12INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
276 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS17 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS17INV1M4SCB4 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 7.0261 | 0
277 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 7.0261 | 742.9489
278 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS29INV1M2SCB3 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 7.0261 | 594.3591
279 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
280 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 7.0261 | 742.9489
281 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 7.0261 | 742.9489
282 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
283 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
284 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
285 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV1 | M4 | SCB2 |  |  | 1 | 1 | IS29INV1M4SCB2 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 7.0261 | 594.3591
286 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 7.0261 | 0
287 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
288 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
289 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
290 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
291 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
292 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 7.0261 | 594.3591
293 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS29INV2M2SCB1 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 7.0261 | 594.3591
294 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV2 | M2 | SCB3 |  |  | 1 | 1 | IS29INV2M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
295 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
296 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0034181 | 7.0261 | 445.7693
297 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS29INV2M3SCB6 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 7.0261 | 594.3591
298 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS29 | INV2 | M4 | SCB1 |  |  | 1 | 1 | IS29INV2M4SCB1 | 95.7 | 0.02633% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0034181 | 7.0261 | 445.7693
299 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
300 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
301 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS30INV1M1SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
302 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS30INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
303 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS30INV1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
304 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
305 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
306 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 7.0261 | 594.3591
307 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS30INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
308 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
309 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS30INV1M4SCB5 | 159.5 | 0.04388% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 7.0261 | 742.9489
310 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
311 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
312 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
313 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 7.0261 | 594.3591
314 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
315 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.038738 | 7.0261 | 5052.0522
316 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
317 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
318 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
319 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
320 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
321 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
322 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
323 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 7.0261 | 742.9489
324 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
325 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
326 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 7.0261 | 742.9489
327 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.045574 | 7.0261 | 5943.5909
328 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV2 | M1 |  |  |  | 1 | 1 | IS33INV2M1 | 1148.4 | 0.3159% | Inverter |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.041017 | 7.0261 | 5349.2318
329 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | Module |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0011394 | 7.0261 | 148.5898
330 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
331 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
332 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
333 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 7.0261 | 891.5386
334 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
335 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
336 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
337 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS33INV2M4SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 7.0261 | 742.9489
338 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS33 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS33INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 7.0261 | 1040.1284
339 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS2 | INV2 | M2 |  |  |  | 1 | 1 | IS2INV2M2 | 781.55 | 0.215% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.027914 | 7.0261 | 3640.4494
340 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS2 | INV2 | M3 |  |  |  | 1 | 1 | IS2INV2M3 | 430.65 | 0.1185% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.015381 | 7.0261 | 2005.9619
341 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:13 | 12.9833 | IS21 | INV2 | M2 |  |  |  | 1 | 1 | IS21INV2M2 | 829.4 | 0.2282% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:13 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.029623 | 7.0261 | 3863.3341
342 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
343 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
344 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 7.2183 | 610.624
345 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0034224 | 7.2183 | 457.968
346 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
347 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
348 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
349 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
350 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
351 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
352 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
353 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 7.2183 | 0
354 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 7.2183 | 0
355 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
356 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 7.2183 | 0
357 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2183 | 763.28
358 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2183 | 763.28
359 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
360 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2183 | 763.28
361 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2183 | 763.28
362 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
363 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 7.2183 | 0
364 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
365 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
366 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
367 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
368 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
369 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
370 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
371 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
372 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
373 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
374 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 7.2183 | 610.624
375 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0034224 | 7.2183 | 457.968
376 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
377 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0034224 | 7.2183 | 457.968
378 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
379 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
380 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
381 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2183 | 763.28
382 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
383 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
384 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
385 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
386 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
387 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2183 | 763.28
388 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 7.2183 | 610.624
389 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
390 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
391 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
392 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 7.2183 | 610.624
393 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
394 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
395 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
396 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
397 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
398 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
399 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
400 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
401 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2183 | 763.28
402 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
403 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
404 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2183 | 763.28
405 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0011408 | 7.2183 | 152.656
406 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
407 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
408 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
409 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2183 | 915.936
410 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
411 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
412 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
413 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS33INV2M4SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2183 | 763.28
414 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS33INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2183 | 1068.592
415 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS2 | INV2 | M2 |  |  |  | 1 | 1 | IS2INV2M2 | 781.55 | 0.215% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.02795 | 7.2183 | 3740.0719
416 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS2 | INV2 | M3 |  |  |  | 1 | 1 | IS2INV2M3 | 430.65 | 0.1185% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.015401 | 7.2183 | 2060.8559
417 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS6 | INV1 | M1 |  |  |  | 1 | 1 | IS6INV1M1 | 1244.1 | 0.3422% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.044492 | 7.2183 | 5953.5838
418 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS21 | INV2 | M2 |  |  |  | 1 | 1 | IS21INV2M2 | 829.4 | 0.2282% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.029661 | 7.2183 | 3969.0559
419 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.045633 | 7.2183 | 6106.2398
420 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.038788 | 7.2183 | 5190.3038
421 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M3 |  |  |  | 1 | 1 | IS30INV2M3 | 1020.8 | 0.2808% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.036506 | 7.2183 | 4884.9918
422 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.045633 | 7.2183 | 6106.2398
423 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M1 |  |  |  | 1 | 1 | IS33INV2M1 | 1148.4 | 0.3159% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.041069 | 7.2183 | 5495.6158
424 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS15 | INV1 | M4 |  |  |  | 1 | 1 | IS15INV1M4 | 1164.35 | 0.3203% | Inverter |  | Inverter shutdown mode | 12:45 | 12:45 | 12:45 | 15:00 | 0 | 0 |  | 2.25 | Rectification work done INV restored | Open | 0.0072069 | 1.8436 | 1423.1275
425 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
426 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
427 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 7.2627 | 614.3739
428 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0034224 | 7.2627 | 460.7804
429 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
430 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079131 | 7.2627 | 1065.3801
431 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
432 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
433 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
434 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
435 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
436 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
437 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 7.2627 | 0
438 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 7.2627 | 0
439 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
440 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 7.2627 | 0
441 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2627 | 767.9673
442 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2627 | 767.9673
443 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
444 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2627 | 767.9673
445 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2627 | 767.9673
446 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
447 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 7.2627 | 0
448 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
449 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
450 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
451 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
452 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
453 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
454 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
455 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
456 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
457 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
458 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 7.2627 | 614.3739
459 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0034224 | 7.2627 | 460.7804
460 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
461 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0034224 | 7.2627 | 460.7804
462 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
463 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
464 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
465 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2627 | 767.9673
466 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
467 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
468 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
469 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
470 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
471 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2627 | 767.9673
472 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 7.2627 | 614.3739
473 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
474 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
475 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
476 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 7.2627 | 614.3739
477 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
478 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
479 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
480 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
481 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
482 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
483 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
484 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
485 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2627 | 767.9673
486 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 7.2627 | 0
487 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
488 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
489 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2627 | 767.9673
490 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0011408 | 7.2627 | 153.5935
491 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
492 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
493 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
494 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 7.2627 | 921.5608
495 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
496 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
497 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
498 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS33INV2M4SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 7.2627 | 767.9673
499 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS33INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 7.2627 | 1075.1543
500 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS6 | INV1 | M1 |  |  |  | 1 | 1 | IS6INV1M1 | 1244.1 | 0.3422% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.044492 | 7.2627 | 5990.1452
501 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS21 | INV2 | M2 |  |  |  | 1 | 1 | IS21INV2M2 | 829.4 | 0.2282% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.029661 | 7.2627 | 3993.4301
502 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.045633 | 7.2627 | 6143.7386
503 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.038788 | 7.2627 | 5222.1778
504 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS30 | INV2 | M3 |  |  |  | 1 | 1 | IS30INV2M3 | 1020.8 | 0.2808% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.036506 | 7.2627 | 4914.9909
505 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.045633 | 7.2627 | 6143.7386
506 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS33 | INV2 | M1 |  |  |  | 1 | 1 | IS33INV2M1 | 1148.4 | 0.3159% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.041069 | 7.2627 | 5529.3648
507 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS15 | INV1 | M1 |  |  |  | 1 | 1 | IS15INV1M1 | 1020.8 | 0.2808% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.036506 | 7.2627 | 4914.9909
508 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS15 | INV1 | M2 |  |  |  | 1 | 1 | IS15INV1M2 | 1260.05 | 0.3466% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.045062 | 7.2627 | 6066.9419
509 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS15 | INV1 | M3 |  |  |  | 1 | 1 | IS15INV1M3 | 1276 | 0.351% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:13 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.045633 | 7.2627 | 6143.7386
510 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:13 | 13 | IS15 | INV1 | M4 |  |  |  | 1 | 1 | IS15INV1M4 | 1164.35 | 0.3203% | Inverter |  | Inverter shutdown mode | 12:15 | 12:15 | 12:15 | 19:13 | 0 | 0 |  | 6.9667 | Informed to Project team | Open | 0.022315 | 3.3508 | 2586.5617
511 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
512 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
513 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.004575 | 7.4995 | 634.4085
514 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0034312 | 7.4995 | 475.8064
515 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
516 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0079334 | 7.4995 | 1100.122
517 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
518 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
519 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
520 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
521 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
522 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
523 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 7.4995 | 0
524 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 7.4995 | 0
525 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
526 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 7.4995 | 0
527 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.4995 | 793.0106
528 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.4995 | 793.0106
529 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
530 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.4995 | 793.0106
531 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.4995 | 793.0106
532 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
533 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 7.4995 | 0
534 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
535 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
536 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
537 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
538 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
539 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
540 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
541 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
542 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
543 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
544 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.004575 | 7.4995 | 634.4085
545 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0034312 | 7.4995 | 475.8064
546 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
547 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0034312 | 7.4995 | 475.8064
548 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
549 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
550 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
551 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.4995 | 793.0106
552 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
553 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
554 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
555 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
556 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
557 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.4995 | 793.0106
558 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.004575 | 7.4995 | 634.4085
559 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
560 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
561 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
562 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.004575 | 7.4995 | 634.4085
563 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
564 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
565 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
566 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
567 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
568 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
569 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
570 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
571 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.4995 | 793.0106
572 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 7.4995 | 0
573 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
574 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
575 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.4995 | 793.0106
576 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0011437 | 7.4995 | 158.6021
577 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
578 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
579 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
580 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.4995 | 951.6127
581 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
582 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
583 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.4995 | 1110.2149
584 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.04575 | 7.4995 | 6344.085
585 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS30 | INV2 | M1 |  |  |  | 1 | 1 | IS30INV2M1 | 1212.2 | 0.3335% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.043462 | 7.4995 | 6026.8807
586 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.04575 | 7.4995 | 6344.085
587 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 19:14 | 13.0333 | IS33 | INV2 | M1 |  |  |  | 1 | 1 | IS33INV2M1 | 1148.4 | 0.3159% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 19:14 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.041175 | 7.4995 | 5709.6765
588 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
589 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
590 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.004575 | 7.5982 | 642.7607
591 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0034312 | 7.5982 | 482.0706
592 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
593 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0079334 | 7.5982 | 1114.6055
594 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
595 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
596 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
597 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
598 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
599 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
600 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 7.5982 | 0
601 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 7.5982 | 0
602 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
603 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 7.5982 | 0
604 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.5982 | 803.4509
605 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.5982 | 803.4509
606 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
607 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.5982 | 803.4509
608 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.5982 | 803.4509
609 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
610 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 7.5982 | 0
611 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
612 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
613 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
614 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
615 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
616 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
617 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
618 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
619 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
620 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
621 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.004575 | 7.5982 | 642.7607
622 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0034312 | 7.5982 | 482.0706
623 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
624 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0034312 | 7.5982 | 482.0706
625 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
626 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
627 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
628 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.5982 | 803.4509
629 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
630 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
631 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
632 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
633 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
634 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.5982 | 803.4509
635 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.004575 | 7.5982 | 642.7607
636 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
637 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
638 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
639 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.004575 | 7.5982 | 642.7607
640 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
641 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
642 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
643 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
644 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
645 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
646 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
647 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
648 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.5982 | 803.4509
649 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 7.5982 | 0
650 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
651 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
652 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 7.5982 | 803.4509
653 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0011437 | 7.5982 | 160.6902
654 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
655 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
656 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
657 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 7.5982 | 964.1411
658 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
659 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
660 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 7.5982 | 1124.8313
661 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS6 | INV1 | M1 |  |  |  | 1 | 1 | IS6INV1M1 | 1244.1 | 0.3422% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.044606 | 7.5982 | 6266.9172
662 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.04575 | 7.5982 | 6427.6074
663 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.038887 | 7.5982 | 5463.4663
664 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV2 | M3 |  |  |  | 1 | 1 | IS30INV2M3 | 1020.8 | 0.2808% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0366 | 7.5982 | 5142.0859
665 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.04575 | 7.5982 | 6427.6074
666 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:13 | 13.0333 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:13 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.038887 | 7.5982 | 5463.4663
667 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS6 | INV1 | M1 |  |  |  | 1 | 1 | IS6INV1M1 | 1244.1 | 0.3422% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.04529 | 7.75 | 6392.0888
668 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.046452 | 7.75 | 6555.9885
669 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.039484 | 7.75 | 5572.5902
670 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV2 | M3 |  |  |  | 1 | 1 | IS30INV2M3 | 1020.8 | 0.2808% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.037161 | 7.75 | 5244.7908
671 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.046452 | 7.75 | 6555.9885
672 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV1 | M1 |  |  |  | 1 | 1 | IS30INV1M1 | 1244.1 | 0.3422% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.04529 | 7.75 | 6392.0888
673 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
674 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
675 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0046452 | 7.75 | 655.5988
676 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0034839 | 7.75 | 491.6991
677 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
678 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0080551 | 7.75 | 1136.868
679 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
680 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
681 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
682 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
683 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
684 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
685 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0 | 7.75 | 0
686 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0 | 7.75 | 0
687 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
688 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0 | 7.75 | 0
689 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0058065 | 7.75 | 819.4986
690 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0058065 | 7.75 | 819.4986
691 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
692 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0058065 | 7.75 | 819.4986
693 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0058065 | 7.75 | 819.4986
694 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
695 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0 | 7.75 | 0
696 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
697 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
698 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
699 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
700 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
701 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
702 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
703 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
704 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
705 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
706 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0046452 | 7.75 | 655.5988
707 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0034839 | 7.75 | 491.6991
708 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
709 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0034839 | 7.75 | 491.6991
710 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
711 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
712 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
713 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0058065 | 7.75 | 819.4986
714 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
715 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
716 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
717 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
718 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
719 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0058065 | 7.75 | 819.4986
720 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0046452 | 7.75 | 655.5988
721 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
722 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
723 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
724 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0046452 | 7.75 | 655.5988
725 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
726 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
727 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
728 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
729 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
730 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
731 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
732 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
733 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0058065 | 7.75 | 819.4986
734 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0 | 7.75 | 0
735 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
736 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
737 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0058065 | 7.75 | 819.4986
738 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0011613 | 7.75 | 163.8997
739 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
740 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
741 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
742 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.0069677 | 7.75 | 983.3983
743 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
744 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
745 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:32 | 13.2333 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:32 | 0 | 0 |  | 13.2333 | Informed to Project team | Open | 0.008129 | 7.75 | 1147.298
746 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.045867 | 7.6177 | 6444.0386
747 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.038987 | 7.6177 | 5477.4328
748 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV2 | M3 |  |  |  | 1 | 1 | IS30INV2M3 | 1020.8 | 0.2808% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.036693 | 7.6177 | 5155.2309
749 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.045867 | 7.6177 | 6444.0386
750 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV2 | M1 |  |  |  | 1 | 1 | IS33INV2M1 | 1148.4 | 0.3159% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.04128 | 7.6177 | 5799.6347
751 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
752 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
753 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0045867 | 7.6177 | 644.4039
754 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00344 | 7.6177 | 483.3029
755 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
756 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0079537 | 7.6177 | 1117.4549
757 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
758 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
759 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
760 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
761 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
762 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
763 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0 | 7.6177 | 0
764 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0 | 7.6177 | 0
765 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
766 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0 | 7.6177 | 0
767 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.6177 | 805.5048
768 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.6177 | 805.5048
769 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
770 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.6177 | 805.5048
771 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.6177 | 805.5048
772 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
773 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0 | 7.6177 | 0
774 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
775 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
776 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
777 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
778 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
779 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
780 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
781 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
782 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
783 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
784 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0045867 | 7.6177 | 644.4039
785 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00344 | 7.6177 | 483.3029
786 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
787 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00344 | 7.6177 | 483.3029
788 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
789 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
790 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
791 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.6177 | 805.5048
792 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
793 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
794 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
795 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
796 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
797 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.6177 | 805.5048
798 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0045867 | 7.6177 | 644.4039
799 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
800 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
801 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
802 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0045867 | 7.6177 | 644.4039
803 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
804 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
805 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
806 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
807 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
808 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
809 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
810 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
811 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.6177 | 805.5048
812 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0 | 7.6177 | 0
813 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
814 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
815 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.6177 | 805.5048
816 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0011467 | 7.6177 | 161.101
817 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
818 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
819 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
820 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.6177 | 966.6058
821 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
822 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
823 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 19:15 | 13.0667 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 19:15 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.6177 | 1127.7068
824 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
825 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
826 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0045984 | 7.5 | 634.4505
827 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0034488 | 7.5 | 475.8379
828 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
829 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.007974 | 7.5 | 1100.1948
830 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
831 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
832 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
833 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
834 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
835 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
836 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0 | 7.5 | 0
837 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0 | 7.5 | 0
838 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
839 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0 | 7.5 | 0
840 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.5 | 793.0631
841 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.5 | 793.0631
842 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
843 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.5 | 793.0631
844 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.5 | 793.0631
845 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
846 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0 | 7.5 | 0
847 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
848 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
849 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
850 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
851 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
852 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
853 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
854 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
855 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
856 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
857 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0045984 | 7.5 | 634.4505
858 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0034488 | 7.5 | 475.8379
859 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
860 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0034488 | 7.5 | 475.8379
861 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
862 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
863 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
864 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.5 | 793.0631
865 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
866 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
867 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
868 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
869 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
870 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.5 | 793.0631
871 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0045984 | 7.5 | 634.4505
872 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
873 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
874 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
875 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0045984 | 7.5 | 634.4505
876 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
877 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
878 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
879 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
880 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
881 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
882 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
883 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
884 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.5 | 793.0631
885 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0 | 7.5 | 0
886 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
887 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
888 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.5 | 793.0631
889 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0011496 | 7.5 | 158.6126
890 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
891 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
892 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
893 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.5 | 951.6757
894 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
895 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
896 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.5 | 1110.2884
897 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.045984 | 7.5 | 6344.505
898 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.039086 | 7.5 | 5392.8292
899 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS30 | INV2 | M3 |  |  |  | 1 | 1 | IS30INV2M3 | 1020.8 | 0.2808% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.036787 | 7.5 | 5075.604
900 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:16 | 13.1 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:16 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.045984 | 7.5 | 6344.505
901 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
902 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
903 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0046101 | 7.6709 | 648.904
904 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0034575 | 7.6709 | 486.678
905 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
906 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0079943 | 7.6709 | 1125.2585
907 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
908 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
909 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
910 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
911 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
912 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
913 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0 | 7.6709 | 0
914 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0 | 7.6709 | 0
915 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
916 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0 | 7.6709 | 0
917 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0057626 | 7.6709 | 811.13
918 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0057626 | 7.6709 | 811.13
919 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
920 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0057626 | 7.6709 | 811.13
921 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0057626 | 7.6709 | 811.13
922 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
923 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0 | 7.6709 | 0
924 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
925 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
926 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
927 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
928 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
929 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
930 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
931 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
932 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
933 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
934 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0046101 | 7.6709 | 648.904
935 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0034575 | 7.6709 | 486.678
936 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
937 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0034575 | 7.6709 | 486.678
938 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
939 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
940 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
941 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0057626 | 7.6709 | 811.13
942 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
943 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
944 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
945 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
946 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
947 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0057626 | 7.6709 | 811.13
948 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0046101 | 7.6709 | 648.904
949 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
950 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
951 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
952 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0046101 | 7.6709 | 648.904
953 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
954 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
955 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
956 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
957 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
958 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
959 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
960 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
961 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0057626 | 7.6709 | 811.13
962 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0 | 7.6709 | 0
963 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
964 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
965 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0057626 | 7.6709 | 811.13
966 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0011525 | 7.6709 | 162.226
967 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
968 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
969 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
970 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0069151 | 7.6709 | 973.356
971 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
972 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
973 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.0080676 | 7.6709 | 1135.582
974 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.046101 | 7.6709 | 6489.0398
975 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.039186 | 7.6709 | 5515.6838
976 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS30 | INV2 | M3 |  |  |  | 1 | 1 | IS30INV2M3 | 1020.8 | 0.2808% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.036881 | 7.6709 | 5191.2318
977 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:18 | 0 | 0 |  | 13.1333 | Informed to Project team | Open | 0.046101 | 7.6709 | 6489.0398
978 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
979 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
980 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0045867 | 7.5898 | 642.0504
981 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00344 | 7.5898 | 481.5378
982 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
983 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0079537 | 7.5898 | 1113.3738
984 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
985 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
986 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
987 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
988 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
989 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
990 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0 | 7.5898 | 0
991 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0 | 7.5898 | 0
992 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
993 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0 | 7.5898 | 0
994 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.5898 | 802.563
995 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.5898 | 802.563
996 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
997 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.5898 | 802.563
998 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.5898 | 802.563
999 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
1000 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0 | 7.5898 | 0
1001 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1002 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1003 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1004 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
1005 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1006 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
1007 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1008 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
1009 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1010 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1011 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0045867 | 7.5898 | 642.0504
1012 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00344 | 7.5898 | 481.5378
1013 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1014 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00344 | 7.5898 | 481.5378
1015 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1016 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1017 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1018 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.5898 | 802.563
1019 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1020 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
1021 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1022 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
1023 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1024 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.5898 | 802.563
1025 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0045867 | 7.5898 | 642.0504
1026 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1027 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1028 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1029 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0045867 | 7.5898 | 642.0504
1030 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
1031 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1032 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1033 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
1034 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1035 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
1036 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1037 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1038 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.5898 | 802.563
1039 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0 | 7.5898 | 0
1040 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
1041 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1042 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0057333 | 7.5898 | 802.563
1043 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0011467 | 7.5898 | 160.5126
1044 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1045 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1046 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1047 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.00688 | 7.5898 | 963.0757
1048 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1049 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1050 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.0080267 | 7.5898 | 1123.5883
1051 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.045867 | 7.5898 | 6420.5044
1052 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.038987 | 7.5898 | 5457.4287
1053 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS30 | INV2 | M3 |  |  |  | 1 | 1 | IS30INV2M3 | 1020.8 | 0.2808% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.036693 | 7.5898 | 5136.4035
1054 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.045867 | 7.5898 | 6420.5044
1055 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:14 | 0 | 0 |  | 13.0667 | Informed to Project team | Open | 0.04128 | 7.5898 | 5778.4539
1056 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS49 | INV1 | M1 |  |  |  | 1 | 1 | IS49INV1M1 | 1180.3 | 0.3247% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.015802 | 7.5898 | 5938.9665
1057 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS49 | Inv1 | M2 |  |  |  | 1 | 1 | IS49Inv1M2 | 893.2 | 0.2457% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.011958 | 7.5898 | 4494.353
1058 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS49 | Inv1 | M3 |  |  |  | 1 | 1 | IS49Inv1M3 | 1164.35 | 0.3203% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.015588 | 7.5898 | 5858.7102
1059 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS49 | Inv1 | M4 |  |  |  | 1 | 1 | IS49Inv1M4 | 1260.05 | 0.3466% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.016869 | 7.5898 | 6340.2481
1060 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS49 | Inv2 | M1 |  |  |  | 1 | 1 | IS49Inv2M1 | 398.75 | 0.1097% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.0053384 | 7.5898 | 2006.4076
1061 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS49 | Inv2 | M2 |  |  |  | 1 | 1 | IS49Inv2M2 | 893.2 | 0.2457% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.011958 | 7.5898 | 4494.353
1062 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS49 | Inv2 | M3 |  |  |  | 1 | 1 | IS49Inv2M3 | 1084.6 | 0.2984% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.014521 | 7.5898 | 5457.4287
1063 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS49 | Inv2 | M4 |  |  |  | 1 | 1 | IS49Inv2M4 | 1020.8 | 0.2808% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.013666 | 7.5898 | 5136.4035
1064 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS50 | Inv1 | M1 |  |  |  | 1 | 1 | IS50Inv1M1 | 1196.25 | 0.3291% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.016015 | 7.5898 | 6019.2228
1065 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS50 | Inv1 | M2 |  |  |  | 1 | 1 | IS50Inv1M2 | 1212.2 | 0.3335% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.016229 | 7.5898 | 6099.4791
1066 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS50 | Inv1 | M3 |  |  |  | 1 | 1 | IS50Inv1M3 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.017937 | 7.5898 | 6741.5296
1067 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS50 | Inv1 | M4 |  |  |  | 1 | 1 | IS50Inv1M4 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.017937 | 7.5898 | 6741.5296
1068 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS50 | Inv2 | M1 |  |  |  | 1 | 1 | IS50Inv2M1 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.017937 | 7.5898 | 6741.5296
1069 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS50 | Inv2 | M2 |  |  |  | 1 | 1 | IS50Inv2M2 | 1307.9 | 0.3598% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.01751 | 7.5898 | 6581.017
1070 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS50 | Inv2 | M3 |  |  |  | 1 | 1 | IS50Inv2M3 | 1244.1 | 0.3422% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.016656 | 7.5898 | 6259.9917
1071 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | IS50 | Inv2 | M4 |  |  |  | 1 | 1 | IS50Inv2M4 | 1307.9 | 0.3598% | Inverter |  | INV off after discus with cleint | 14:22 | 14:22 | 14:22 | 19:14 | 0 | 0 |  | 4.8667 | Informed to Cleint | Open | 0.01751 | 7.5898 | 6581.017
1072 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1073 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1074 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0046276 | 7.1187 | 602.1969
1075 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0034707 | 7.1187 | 451.6477
1076 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1077 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080247 | 7.1187 | 1044.2641
1078 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1079 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1080 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1081 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1082 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1083 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1084 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 7.1187 | 0
1085 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 7.1187 | 0
1086 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1087 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 7.1187 | 0
1088 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0057845 | 7.1187 | 752.7461
1089 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0057845 | 7.1187 | 752.7461
1090 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1091 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0057845 | 7.1187 | 752.7461
1092 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0057845 | 7.1187 | 752.7461
1093 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1094 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 7.1187 | 0
1095 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1096 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1097 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1098 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1099 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1100 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1101 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1102 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1103 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1104 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1105 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0046276 | 7.1187 | 602.1969
1106 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0034707 | 7.1187 | 451.6477
1107 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1108 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0034707 | 7.1187 | 451.6477
1109 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1110 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1111 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1112 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0057845 | 7.1187 | 752.7461
1113 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1114 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1115 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1116 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1117 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1118 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0057845 | 7.1187 | 752.7461
1119 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0046276 | 7.1187 | 602.1969
1120 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1121 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1122 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1123 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0046276 | 7.1187 | 602.1969
1124 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1125 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1126 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1127 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1128 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1129 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1130 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1131 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1132 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0057845 | 7.1187 | 752.7461
1133 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 7.1187 | 0
1134 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1135 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1136 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0057845 | 7.1187 | 752.7461
1137 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0011569 | 7.1187 | 150.5492
1138 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1139 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1140 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1141 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 7.1187 | 903.2953
1142 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1143 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1144 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 7.1187 | 1053.8445
1145 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.046276 | 7.1187 | 6021.9687
1146 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.039335 | 7.1187 | 5118.6734
1147 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS30 | INV2 | M3 |  |  |  | 1 | 1 | IS30INV2M3 | 1020.8 | 0.2808% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.037021 | 7.1187 | 4817.575
1148 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.046276 | 7.1187 | 6021.9687
1149 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Inverter |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.041649 | 7.1187 | 5419.7719
1150 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS49 | INV1 | M1 |  |  |  | 1 | 1 | IS49INV1M1 | 1180.3 | 0.3247% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.042805 | 7.1187 | 5570.3211
1151 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS49 | Inv1 | M2 |  |  |  | 1 | 1 | IS49Inv1M2 | 893.2 | 0.2457% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.032393 | 7.1187 | 4215.3781
1152 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS49 | Inv1 | M3 |  |  |  | 1 | 1 | IS49Inv1M3 | 1164.35 | 0.3203% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.042227 | 7.1187 | 5495.0465
1153 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS49 | Inv1 | M4 |  |  |  | 1 | 1 | IS49Inv1M4 | 1260.05 | 0.3466% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.045698 | 7.1187 | 5946.6941
1154 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS49 | Inv2 | M1 |  |  |  | 1 | 1 | IS49Inv2M1 | 398.75 | 0.1097% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.014461 | 7.1187 | 1881.8652
1155 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS49 | Inv2 | M2 |  |  |  | 1 | 1 | IS49Inv2M2 | 893.2 | 0.2457% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.032393 | 7.1187 | 4215.3781
1156 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS49 | Inv2 | M3 |  |  |  | 1 | 1 | IS49Inv2M3 | 1084.6 | 0.2984% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.039335 | 7.1187 | 5118.6734
1157 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS49 | Inv2 | M4 |  |  |  | 1 | 1 | IS49Inv2M4 | 1020.8 | 0.2808% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.037021 | 7.1187 | 4817.575
1158 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS50 | Inv1 | M1 |  |  |  | 1 | 1 | IS50Inv1M1 | 1196.25 | 0.3291% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.043384 | 7.1187 | 5645.5957
1159 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS50 | Inv1 | M2 |  |  |  | 1 | 1 | IS50Inv1M2 | 1212.2 | 0.3335% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.043962 | 7.1187 | 5720.8703
1160 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS50 | Inv1 | M3 |  |  |  | 1 | 1 | IS50Inv1M3 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.04859 | 7.1187 | 6323.0672
1161 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS50 | Inv1 | M4 |  |  |  | 1 | 1 | IS50Inv1M4 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.04859 | 7.1187 | 6323.0672
1162 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS50 | Inv2 | M1 |  |  |  | 1 | 1 | IS50Inv2M1 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.04859 | 7.1187 | 6323.0672
1163 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS50 | Inv2 | M2 |  |  |  | 1 | 1 | IS50Inv2M2 | 1307.9 | 0.3598% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.047433 | 7.1187 | 6172.518
1164 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS50 | Inv2 | M3 |  |  |  | 1 | 1 | IS50Inv2M3 | 1244.1 | 0.3422% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.045119 | 7.1187 | 5871.4195
1165 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS50 | Inv2 | M4 |  |  |  | 1 | 1 | IS50Inv2M4 | 1307.9 | 0.3598% | Inverter |  | INV off after discus with cleint | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint | Open | 0.047433 | 7.1187 | 6172.518
1166 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS19 | Inv1 | M1 |  |  |  | 1 | 1 | IS19Inv1M1 | 1148.4 | 0.3159% | Inverter |  | Inverter Device Fault | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint and Team Sungrow | Open | 0.041649 | 7.1187 | 5419.7719
1167 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS19 | Inv1 | M2 |  |  |  | 1 | 1 | IS19Inv1M2 | 1116.5 | 0.3071% | Inverter |  | Inverter Device Fault | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint and Team Sungrow | Open | 0.040492 | 7.1187 | 5269.2227
1168 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS19 | Inv1 | M3 |  |  |  | 1 | 1 | IS19Inv1M3 | 1276 | 0.351% | Inverter |  | Inverter Device Fault | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint and Team Sungrow | Open | 0.046276 | 7.1187 | 6021.9687
1169 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS19 | Inv1 | M4 |  |  |  | 1 | 1 | IS19Inv1M4 | 1212.2 | 0.3335% | Inverter |  | Inverter Device Fault | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Cleint and Team Sungrow | Open | 0.043962 | 7.1187 | 5720.8703
1170 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1171 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1172 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 1.4258 | 120.6103
1173 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0033654 | 1.4258 | 90.4577
1174 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1175 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0077812 | 1.4258 | 209.1493
1176 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1177 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1178 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1179 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1180 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1181 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1182 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 1.4258 | 0
1183 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 1.4258 | 0
1184 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1185 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 1.4258 | 0
1186 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 1.4258 | 150.7629
1187 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 1.4258 | 150.7629
1188 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1189 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 1.4258 | 150.7629
1190 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 1.4258 | 150.7629
1191 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1192 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 1.4258 | 0
1193 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1194 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1195 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1196 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1197 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1198 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1199 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1200 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1201 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1202 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1203 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 1.4258 | 120.6103
1204 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0033654 | 1.4258 | 90.4577
1205 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1206 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0033654 | 1.4258 | 90.4577
1207 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1208 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1209 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1210 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 1.4258 | 150.7629
1211 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1212 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1213 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1214 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1215 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1216 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 1.4258 | 150.7629
1217 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 1.4258 | 120.6103
1218 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1219 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1220 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1221 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 1.4258 | 120.6103
1222 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1223 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1224 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1225 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1226 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1227 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1228 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1229 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1230 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 1.4258 | 150.7629
1231 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 1.4258 | 0
1232 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1233 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1234 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 1.4258 | 150.7629
1235 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0011218 | 1.4258 | 30.1526
1236 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1237 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1238 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1239 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 1.4258 | 180.9155
1240 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1241 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1242 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 1.4258 | 211.0681
1243 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.044872 | 1.4258 | 1206.1032
1244 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.038141 | 1.4258 | 1025.1878
1245 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS30 | INV2 | M3 |  |  |  | 1 | 1 | IS30INV2M3 | 1020.8 | 0.2808% | Inverter |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.035898 | 1.4258 | 964.8826
1246 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.044872 | 1.4258 | 1206.1032
1247 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Inverter |  | DC Cable theft | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.040385 | 1.4258 | 1085.4929
1248 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS49 | INV1 | M1 |  |  |  | 1 | 1 | IS49INV1M1 | 1180.3 | 0.3247% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.041507 | 1.4258 | 1115.6455
1249 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS49 | Inv1 | M2 |  |  |  | 1 | 1 | IS49Inv1M2 | 893.2 | 0.2457% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.03141 | 1.4258 | 844.2723
1250 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS49 | Inv1 | M3 |  |  |  | 1 | 1 | IS49Inv1M3 | 1164.35 | 0.3203% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.040946 | 1.4258 | 1100.5692
1251 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS49 | Inv1 | M4 |  |  |  | 1 | 1 | IS49Inv1M4 | 1260.05 | 0.3466% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.044311 | 1.4258 | 1191.027
1252 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS49 | Inv2 | M1 |  |  |  | 1 | 1 | IS49Inv2M1 | 398.75 | 0.1097% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.014023 | 1.4258 | 376.9073
1253 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS49 | Inv2 | M2 |  |  |  | 1 | 1 | IS49Inv2M2 | 893.2 | 0.2457% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.03141 | 1.4258 | 844.2723
1254 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS49 | Inv2 | M3 |  |  |  | 1 | 1 | IS49Inv2M3 | 1084.6 | 0.2984% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.038141 | 1.4258 | 1025.1878
1255 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS49 | Inv2 | M4 |  |  |  | 1 | 1 | IS49Inv2M4 | 1020.8 | 0.2808% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.035898 | 1.4258 | 964.8826
1256 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS50 | Inv1 | M1 |  |  |  | 1 | 1 | IS50Inv1M1 | 1196.25 | 0.3291% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.042068 | 1.4258 | 1130.7218
1257 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS50 | Inv1 | M2 |  |  |  | 1 | 1 | IS50Inv1M2 | 1212.2 | 0.3335% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.042628 | 1.4258 | 1145.7981
1258 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS50 | Inv1 | M3 |  |  |  | 1 | 1 | IS50Inv1M3 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.047116 | 1.4258 | 1266.4084
1259 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS50 | Inv1 | M4 |  |  |  | 1 | 1 | IS50Inv1M4 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.047116 | 1.4258 | 1266.4084
1260 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS50 | Inv2 | M1 |  |  |  | 1 | 1 | IS50Inv2M1 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.047116 | 1.4258 | 1266.4084
1261 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS50 | Inv2 | M2 |  |  |  | 1 | 1 | IS50Inv2M2 | 1307.9 | 0.3598% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.045994 | 1.4258 | 1236.2558
1262 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS50 | Inv2 | M3 |  |  |  | 1 | 1 | IS50Inv2M3 | 1244.1 | 0.3422% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.04375 | 1.4258 | 1175.9507
1263 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS50 | Inv2 | M4 |  |  |  | 1 | 1 | IS50Inv2M4 | 1307.9 | 0.3598% | Inverter |  | INV off after discus with cleint | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint | Open | 0.045994 | 1.4258 | 1236.2558
1264 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS19 | Inv1 | M1 |  |  |  | 1 | 1 | IS19Inv1M1 | 1148.4 | 0.3159% | Inverter |  | Inverter Device Fault | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint and Team Sungrow | Open | 0.040385 | 1.4258 | 1085.4929
1265 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS19 | Inv1 | M2 |  |  |  | 1 | 1 | IS19Inv1M2 | 1116.5 | 0.3071% | Inverter |  | Inverter Device Fault | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint and Team Sungrow | Open | 0.039263 | 1.4258 | 1055.3403
1266 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS19 | Inv1 | M3 |  |  |  | 1 | 1 | IS19Inv1M3 | 1276 | 0.351% | Inverter |  | Inverter Device Fault | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint and Team Sungrow | Open | 0.044872 | 1.4258 | 1206.1032
1267 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS19 | Inv1 | M4 |  |  |  | 1 | 1 | IS19Inv1M4 | 1212.2 | 0.3335% | Inverter |  | Inverter Device Fault | 6:26 | 6:26 | 6:26 | 19:13 | 0 | 0 |  | 12.7833 | Informed to Cleint and Team Sungrow | Open | 0.042628 | 1.4258 | 1145.7981
1268 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | IS18 | Inv2 | M2 |  |  |  | 1 | 1 | IS18Inv2M2 | 1148.4 | 0.3159% | Inverter |  | Dc switch anomaly | 6:26 | 6:26 | 6:26 | 9:07 | 0 | 0 |  | 2.6833 | Informed to Cleint and Team Sungrow | Open | 0.0084771 | 0.29146 | 221.8982
1269 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1270 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1271 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0041771 | 1.898 | 160.5603
1272 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0031329 | 1.898 | 120.4202
1273 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1274 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0072435 | 1.898 | 278.4262
1275 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1276 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1277 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1278 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1279 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1280 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1281 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0 | 1.898 | 0
1282 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0 | 1.898 | 0
1283 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1284 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0 | 1.898 | 0
1285 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0052214 | 1.898 | 200.7004
1286 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0052214 | 1.898 | 200.7004
1287 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1288 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0052214 | 1.898 | 200.7004
1289 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0052214 | 1.898 | 200.7004
1290 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1291 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0 | 1.898 | 0
1292 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1293 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1294 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1295 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1296 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1297 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1298 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1299 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1300 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1301 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1302 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0041771 | 1.898 | 160.5603
1303 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0031329 | 1.898 | 120.4202
1304 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1305 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0031329 | 1.898 | 120.4202
1306 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1307 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1308 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1309 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0052214 | 1.898 | 200.7004
1310 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1311 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1312 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1313 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1314 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1315 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0052214 | 1.898 | 200.7004
1316 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0041771 | 1.898 | 160.5603
1317 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1318 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1319 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1320 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0041771 | 1.898 | 160.5603
1321 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1322 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1323 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1324 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1325 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1326 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1327 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1328 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1329 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0052214 | 1.898 | 200.7004
1330 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0 | 1.898 | 0
1331 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1332 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1333 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0052214 | 1.898 | 200.7004
1334 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0010443 | 1.898 | 40.1401
1335 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1336 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1337 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1338 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.0062657 | 1.898 | 240.8405
1339 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1340 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1341 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.00731 | 1.898 | 280.9806
1342 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.041771 | 1.898 | 1605.6032
1343 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.035506 | 1.898 | 1364.7627
1344 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS30 | INV2 | M3 |  |  |  | 1 | 1 | IS30INV2M3 | 1020.8 | 0.2808% | Inverter |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.033417 | 1.898 | 1284.4825
1345 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.041771 | 1.898 | 1605.6032
1346 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Inverter |  | DC Cable theft | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Project team | Open | 0.037594 | 1.898 | 1445.0429
1347 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS49 | INV1 | M1 |  |  |  | 1 | 1 | IS49INV1M1 | 1180.3 | 0.3247% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.038639 | 1.898 | 1485.1829
1348 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS49 | Inv1 | M2 |  |  |  | 1 | 1 | IS49Inv1M2 | 893.2 | 0.2457% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.02924 | 1.898 | 1123.9222
1349 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS49 | Inv1 | M3 |  |  |  | 1 | 1 | IS49Inv1M3 | 1164.35 | 0.3203% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.038116 | 1.898 | 1465.1129
1350 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS49 | Inv1 | M4 |  |  |  | 1 | 1 | IS49Inv1M4 | 1260.05 | 0.3466% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.041249 | 1.898 | 1585.5331
1351 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS49 | Inv2 | M1 |  |  |  | 1 | 1 | IS49Inv2M1 | 398.75 | 0.1097% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.013054 | 1.898 | 501.751
1352 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS49 | Inv2 | M2 |  |  |  | 1 | 1 | IS49Inv2M2 | 893.2 | 0.2457% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.02924 | 1.898 | 1123.9222
1353 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS49 | Inv2 | M3 |  |  |  | 1 | 1 | IS49Inv2M3 | 1084.6 | 0.2984% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.035506 | 1.898 | 1364.7627
1354 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS49 | Inv2 | M4 |  |  |  | 1 | 1 | IS49Inv2M4 | 1020.8 | 0.2808% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.033417 | 1.898 | 1284.4825
1355 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS50 | Inv1 | M1 |  |  |  | 1 | 1 | IS50Inv1M1 | 1196.25 | 0.3291% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.039161 | 1.898 | 1505.253
1356 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS50 | Inv1 | M2 |  |  |  | 1 | 1 | IS50Inv1M2 | 1212.2 | 0.3335% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.039683 | 1.898 | 1525.323
1357 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS50 | Inv1 | M3 |  |  |  | 1 | 1 | IS50Inv1M3 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.04386 | 1.898 | 1685.8833
1358 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS50 | Inv1 | M4 |  |  |  | 1 | 1 | IS50Inv1M4 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.04386 | 1.898 | 1685.8833
1359 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS50 | Inv2 | M1 |  |  |  | 1 | 1 | IS50Inv2M1 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.04386 | 1.898 | 1685.8833
1360 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS50 | Inv2 | M2 |  |  |  | 1 | 1 | IS50Inv2M2 | 1307.9 | 0.3598% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.042816 | 1.898 | 1645.7433
1361 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS50 | Inv2 | M3 |  |  |  | 1 | 1 | IS50Inv2M3 | 1244.1 | 0.3422% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.040727 | 1.898 | 1565.4631
1362 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS50 | Inv2 | M4 |  |  |  | 1 | 1 | IS50Inv2M4 | 1307.9 | 0.3598% | Inverter |  | INV off after discus with cleint | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint | Open | 0.042816 | 1.898 | 1645.7433
1363 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS19 | Inv1 | M1 |  |  |  | 1 | 1 | IS19Inv1M1 | 1148.4 | 0.3159% | Inverter |  | Inverter Device Fault | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint and Team Sungrow | Open | 0.037594 | 1.898 | 1445.0429
1364 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS19 | Inv1 | M2 |  |  |  | 1 | 1 | IS19Inv1M2 | 1116.5 | 0.3071% | Inverter |  | Inverter Device Fault | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint and Team Sungrow | Open | 0.03655 | 1.898 | 1404.9028
1365 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS19 | Inv1 | M3 |  |  |  | 1 | 1 | IS19Inv1M3 | 1276 | 0.351% | Inverter |  | Inverter Device Fault | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint and Team Sungrow | Open | 0.041771 | 1.898 | 1605.6032
1366 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS19 | Inv1 | M4 |  |  |  | 1 | 1 | IS19Inv1M4 | 1212.2 | 0.3335% | Inverter |  | Inverter Device Fault | 7:20 | 7:20 | 7:20 | 19:14 | 0 | 0 |  | 11.9 | Informed to Cleint and Team Sungrow | Open | 0.039683 | 1.898 | 1525.323
1367 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | IS22 | Inv2 | M4 |  |  |  | 1 | 1 | IS22Inv2M4 | 1244.1 | 0.3422% | Inverter |  | Gfdi | 7:20 | 7:20 | 7:20 | 8:30 | 0 | 0 |  | 1.1667 | Informed to Cleint and Team Sungrow | Open | 0.0039929 | 0.065614 | 54.1176
1368 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1369 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1370 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0042064 | 3.4487 | 291.7338
1371 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0031548 | 3.4487 | 218.8004
1372 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1373 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0072943 | 3.4487 | 505.893
1374 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1375 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1376 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1377 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1378 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1379 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1380 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0 | 3.4487 | 0
1381 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0 | 3.4487 | 0
1382 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1383 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0 | 3.4487 | 0
1384 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.005258 | 3.4487 | 364.6673
1385 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.005258 | 3.4487 | 364.6673
1386 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1387 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.005258 | 3.4487 | 364.6673
1388 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.005258 | 3.4487 | 364.6673
1389 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1390 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0 | 3.4487 | 0
1391 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1392 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1393 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1394 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1395 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1396 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1397 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1398 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1399 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1400 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1401 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0042064 | 3.4487 | 291.7338
1402 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0031548 | 3.4487 | 218.8004
1403 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1404 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0031548 | 3.4487 | 218.8004
1405 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1406 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1407 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1408 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.005258 | 3.4487 | 364.6673
1409 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1410 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1411 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1412 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1413 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1414 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.005258 | 3.4487 | 364.6673
1415 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0042064 | 3.4487 | 291.7338
1416 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1417 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1418 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1419 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0042064 | 3.4487 | 291.7338
1420 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1421 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1422 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1423 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1424 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1425 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1426 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1427 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1428 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.005258 | 3.4487 | 364.6673
1429 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0 | 3.4487 | 0
1430 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1431 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1432 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.005258 | 3.4487 | 364.6673
1433 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0010516 | 3.4487 | 72.9335
1434 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1435 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1436 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1437 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0063096 | 3.4487 | 437.6007
1438 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1439 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1440 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.0073612 | 3.4487 | 510.5342
1441 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.042064 | 3.4487 | 2917.3383
1442 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.035754 | 3.4487 | 2479.7375
1443 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS30 | INV2 | M3 |  |  |  | 1 | 1 | IS30INV2M3 | 1020.8 | 0.2808% | Inverter |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.033651 | 3.4487 | 2333.8706
1444 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.042064 | 3.4487 | 2917.3383
1445 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Inverter |  | DC Cable theft | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Project team | Open | 0.037858 | 3.4487 | 2625.6045
1446 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS49 | INV1 | M1 |  |  |  | 1 | 1 | IS49INV1M1 | 1180.3 | 0.3247% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.038909 | 3.4487 | 2698.5379
1447 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS49 | Inv1 | M2 |  |  |  | 1 | 1 | IS49Inv1M2 | 893.2 | 0.2457% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.029445 | 3.4487 | 2042.1368
1448 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS49 | Inv1 | M3 |  |  |  | 1 | 1 | IS49Inv1M3 | 1164.35 | 0.3203% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.038383 | 3.4487 | 2662.0712
1449 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS49 | Inv1 | M4 |  |  |  | 1 | 1 | IS49Inv1M4 | 1260.05 | 0.3466% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.041538 | 3.4487 | 2880.8716
1450 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS49 | Inv2 | M1 |  |  |  | 1 | 1 | IS49Inv2M1 | 398.75 | 0.1097% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.013145 | 3.4487 | 911.6682
1451 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS49 | Inv2 | M2 |  |  |  | 1 | 1 | IS49Inv2M2 | 893.2 | 0.2457% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.029445 | 3.4487 | 2042.1368
1452 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS49 | Inv2 | M3 |  |  |  | 1 | 1 | IS49Inv2M3 | 1084.6 | 0.2984% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.035754 | 3.4487 | 2479.7375
1453 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS49 | Inv2 | M4 |  |  |  | 1 | 1 | IS49Inv2M4 | 1020.8 | 0.2808% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.033651 | 3.4487 | 2333.8706
1454 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS50 | Inv1 | M1 |  |  |  | 1 | 1 | IS50Inv1M1 | 1196.25 | 0.3291% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.039435 | 3.4487 | 2735.0046
1455 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS50 | Inv1 | M2 |  |  |  | 1 | 1 | IS50Inv1M2 | 1212.2 | 0.3335% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.039961 | 3.4487 | 2771.4714
1456 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS50 | Inv1 | M3 |  |  |  | 1 | 1 | IS50Inv1M3 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.044167 | 3.4487 | 3063.2052
1457 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS50 | Inv1 | M4 |  |  |  | 1 | 1 | IS50Inv1M4 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.044167 | 3.4487 | 3063.2052
1458 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS50 | Inv2 | M1 |  |  |  | 1 | 1 | IS50Inv2M1 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.044167 | 3.4487 | 3063.2052
1459 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS50 | Inv2 | M2 |  |  |  | 1 | 1 | IS50Inv2M2 | 1307.9 | 0.3598% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.043116 | 3.4487 | 2990.2717
1460 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS50 | Inv2 | M3 |  |  |  | 1 | 1 | IS50Inv2M3 | 1244.1 | 0.3422% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.041012 | 3.4487 | 2844.4048
1461 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS50 | Inv2 | M4 |  |  |  | 1 | 1 | IS50Inv2M4 | 1307.9 | 0.3598% | Inverter |  | INV off after discus with cleint | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint | Open | 0.043116 | 3.4487 | 2990.2717
1462 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS19 | Inv1 | M1 |  |  |  | 1 | 1 | IS19Inv1M1 | 1148.4 | 0.3159% | Inverter |  | Inverter Device Fault | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint and Team Sungrow | Open | 0.037858 | 3.4487 | 2625.6045
1463 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS19 | Inv1 | M2 |  |  |  | 1 | 1 | IS19Inv1M2 | 1116.5 | 0.3071% | Inverter |  | Inverter Device Fault | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint and Team Sungrow | Open | 0.036806 | 3.4487 | 2552.671
1464 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS19 | Inv1 | M3 |  |  |  | 1 | 1 | IS19Inv1M3 | 1276 | 0.351% | Inverter |  | Inverter Device Fault | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint and Team Sungrow | Open | 0.042064 | 3.4487 | 2917.3383
1465 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | IS19 | Inv1 | M4 |  |  |  | 1 | 1 | IS19Inv1M4 | 1212.2 | 0.3335% | Inverter |  | Inverter Device Fault | 7:23 | 7:23 | 7:23 | 19:22 | 0 | 0 |  | 11.9833 | Informed to Cleint and Team Sungrow | Open | 0.039961 | 5.7545 | 4624.5123
1466 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1467 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1468 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0045223 | 5.7545 | 486.7908
1469 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0033917 | 5.7545 | 365.0931
1470 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1471 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0078421 | 5.7545 | 844.1395
1472 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1473 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1474 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1475 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1476 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1477 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1478 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0 | 5.7545 | 0
1479 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0 | 5.7545 | 0
1480 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1481 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0 | 5.7545 | 0
1482 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0056529 | 5.7545 | 608.4885
1483 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0056529 | 5.7545 | 608.4885
1484 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1485 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0056529 | 5.7545 | 608.4885
1486 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0056529 | 5.7545 | 608.4885
1487 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1488 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0 | 5.7545 | 0
1489 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1490 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1491 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1492 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1493 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1494 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1495 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1496 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1497 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1498 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1499 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0045223 | 5.7545 | 486.7908
1500 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0033917 | 5.7545 | 365.0931
1501 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1502 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0033917 | 5.7545 | 365.0931
1503 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1504 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1505 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1506 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0056529 | 5.7545 | 608.4885
1507 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1508 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1509 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1510 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1511 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1512 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0056529 | 5.7545 | 608.4885
1513 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0045223 | 5.7545 | 486.7908
1514 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1515 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1516 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1517 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0045223 | 5.7545 | 486.7908
1518 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1519 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1520 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1521 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1522 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1523 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1524 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1525 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1526 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0056529 | 5.7545 | 608.4885
1527 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0 | 5.7545 | 0
1528 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1529 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1530 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0056529 | 5.7545 | 608.4885
1531 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0011306 | 5.7545 | 121.6977
1532 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1533 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1534 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1535 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.0067835 | 5.7545 | 730.1862
1536 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1537 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1538 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.007914 | 5.7545 | 851.8839
1539 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.045223 | 5.7545 | 4867.9077
1540 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.03844 | 5.7545 | 4137.7216
1541 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS30 | INV2 | M3 |  |  |  | 1 | 1 | IS30INV2M3 | 1020.8 | 0.2808% | Inverter |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.036178 | 5.7545 | 3894.3262
1542 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.045223 | 5.7545 | 4867.9077
1543 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Inverter |  | DC Cable theft | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Project team | Open | 0.040701 | 5.7545 | 4381.117
1544 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS49 | INV1 | M1 |  |  |  | 1 | 1 | IS49INV1M1 | 1180.3 | 0.3247% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.041831 | 5.7545 | 4502.8146
1545 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS49 | Inv1 | M2 |  |  |  | 1 | 1 | IS49Inv1M2 | 893.2 | 0.2457% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.031656 | 5.7545 | 3407.5354
1546 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS49 | Inv1 | M3 |  |  |  | 1 | 1 | IS49Inv1M3 | 1164.35 | 0.3203% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.041266 | 5.7545 | 4441.9658
1547 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS49 | Inv1 | M4 |  |  |  | 1 | 1 | IS49Inv1M4 | 1260.05 | 0.3466% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.044658 | 5.7545 | 4807.0589
1548 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS49 | Inv2 | M1 |  |  |  | 1 | 1 | IS49Inv2M1 | 398.75 | 0.1097% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.014132 | 5.7545 | 1521.2212
1549 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS49 | Inv2 | M2 |  |  |  | 1 | 1 | IS49Inv2M2 | 893.2 | 0.2457% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.031656 | 5.7545 | 3407.5354
1550 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS49 | Inv2 | M3 |  |  |  | 1 | 1 | IS49Inv2M3 | 1084.6 | 0.2984% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.03844 | 5.7545 | 4137.7216
1551 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS49 | Inv2 | M4 |  |  |  | 1 | 1 | IS49Inv2M4 | 1020.8 | 0.2808% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.036178 | 5.7545 | 3894.3262
1552 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS50 | Inv1 | M1 |  |  |  | 1 | 1 | IS50Inv1M1 | 1196.25 | 0.3291% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.042397 | 5.7545 | 4563.6635
1553 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS50 | Inv1 | M2 |  |  |  | 1 | 1 | IS50Inv1M2 | 1212.2 | 0.3335% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.042962 | 5.7545 | 4624.5123
1554 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS50 | Inv1 | M3 |  |  |  | 1 | 1 | IS50Inv1M3 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.047484 | 5.7545 | 5111.3031
1555 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS50 | Inv1 | M4 |  |  |  | 1 | 1 | IS50Inv1M4 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.047484 | 5.7545 | 5111.3031
1556 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS50 | Inv2 | M1 |  |  |  | 1 | 1 | IS50Inv2M1 | 1339.8 | 0.3686% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.047484 | 5.7545 | 5111.3031
1557 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS50 | Inv2 | M2 |  |  |  | 1 | 1 | IS50Inv2M2 | 1307.9 | 0.3598% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.046354 | 5.7545 | 4989.6054
1558 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS50 | Inv2 | M3 |  |  |  | 1 | 1 | IS50Inv2M3 | 1244.1 | 0.3422% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.044093 | 5.7545 | 4746.21
1559 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS50 | Inv2 | M4 |  |  |  | 1 | 1 | IS50Inv2M4 | 1307.9 | 0.3598% | Inverter |  | INV off after discus with cleint | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client | Open | 0.046354 | 5.7545 | 4989.6054
1560 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS19 | Inv1 | M1 |  |  |  | 1 | 1 | IS19Inv1M1 | 1148.4 | 0.3159% | Inverter |  | Inverter Device Fault | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client and Team Sungrow | Open | 0.040701 | 5.7545 | 4381.117
1561 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS19 | Inv1 | M2 |  |  |  | 1 | 1 | IS19Inv1M2 | 1116.5 | 0.3071% | Inverter |  | Inverter Device Fault | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client and Team Sungrow | Open | 0.03957 | 5.7545 | 4259.4193
1562 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS19 | Inv1 | M3 |  |  |  | 1 | 1 | IS19Inv1M3 | 1276 | 0.351% | Inverter |  | Inverter Device Fault | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client and Team Sungrow | Open | 0.045223 | 5.7545 | 4867.9077
1563 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS19 | Inv1 | M4 |  |  |  | 1 | 1 | IS19Inv1M4 | 1212.2 | 0.3335% | Inverter |  | Inverter Device Fault | 6:33 | 6:33 | 6:33 | 19:26 | 0 | 0 |  | 12.8833 | Informed to Client and Team Sungrow | Open | 0.042962 | 5.7545 | 4624.5123
1564 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS15 | Inv1 |  |  |  |  | 1 | 1 | IS15Inv1 | 4721.2 | 1.299% | Inverter |  | Over current | 12:34 | 12:34 | 12:34 | 15:10 | 0 | 0 | 2.6 | 2.6 | Informed to Client and Team Sungrow | Close | 0.033768 | 2.0837 | 6521.8799
1565 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS15 | Inv2 |  |  |  |  | 1 | 1 | IS15Inv2 | 5167.8 | 1.422% | Inverter |  | Over current | 12:34 | 12:34 | 12:34 | 15:10 | 0 | 0 | 2.6 | 2.6 | Informed to Client and Team Sungrow | Close | 0.036962 | 2.0837 | 7138.8145
1566 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | IS22 | Inv2 |  |  |  |  | 1 | 1 | IS22Inv2 | 3843.95 | 1.057% | Inverter |  | Gfdi | 16:52 | 16:52 | 16:52 | 17:15 | 0 | 0 | 0.38333 | 0.38333 | Informed to Client and Team Sungrow | Close | 0.0040536 | 0.048559 | 123.7455
1567 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1568 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1569 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0045984 | 7.2091 | 609.8388
1570 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0034488 | 7.2091 | 457.3791
1571 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1572 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.007974 | 7.2091 | 1057.516
1573 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1574 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1575 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1576 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1577 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1578 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1579 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0 | 7.2091 | 0
1580 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0 | 7.2091 | 0
1581 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1582 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0 | 7.2091 | 0
1583 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.2091 | 762.2985
1584 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.2091 | 762.2985
1585 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1586 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.2091 | 762.2985
1587 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.2091 | 762.2985
1588 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1589 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0 | 7.2091 | 0
1590 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1591 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1592 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1593 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1594 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1595 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1596 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1597 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1598 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1599 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1600 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0045984 | 7.2091 | 609.8388
1601 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0034488 | 7.2091 | 457.3791
1602 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1603 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0034488 | 7.2091 | 457.3791
1604 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1605 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1606 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1607 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.2091 | 762.2985
1608 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1609 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1610 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1611 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1612 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1613 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.2091 | 762.2985
1614 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0045984 | 7.2091 | 609.8388
1615 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1616 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1617 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1618 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0045984 | 7.2091 | 609.8388
1619 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1620 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1621 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1622 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1623 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1624 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1625 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1626 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1627 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.2091 | 762.2985
1628 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0 | 7.2091 | 0
1629 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1630 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1631 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.005748 | 7.2091 | 762.2985
1632 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0011496 | 7.2091 | 152.4597
1633 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1634 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1635 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1636 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0068975 | 7.2091 | 914.7582
1637 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1638 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1639 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.0080471 | 7.2091 | 1067.2179
1640 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.045984 | 7.2091 | 6098.3883
1641 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.039086 | 7.2091 | 5183.63
1642 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.045984 | 7.2091 | 6098.3883
1643 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Inverter |  | DC Cable theft | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Project team | Open | 0.041385 | 7.2091 | 5488.5494
1644 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS49 | INV1 |  |  |  |  | 1 | 1 | IS49INV1 | 4497.9 | 1.237% | Inverter |  | INV off after discus with cleint | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Client | Open | 0.16209 | 7.2091 | 21496.8186
1645 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS49 | Inv2 |  |  |  |  | 1 | 1 | IS49Inv2 | 3397.35 | 0.9346% | Inverter |  | INV off after discus with cleint | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Client | Open | 0.12243 | 7.2091 | 16236.9588
1646 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS50 | Inv1 |  |  |  |  | 1 | 1 | IS50Inv1 | 5088.05 | 1.4% | Inverter |  | INV off after discus with cleint | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Client | Open | 0.18336 | 7.2091 | 24317.3232
1647 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS50 | Inv2 |  |  |  |  | 1 | 1 | IS50Inv2 | 5199.7 | 1.43% | Inverter |  | INV off after discus with cleint | 6:13 | 6:13 | 6:13 | 19:19 | 0 | 0 |  | 13.1 | Informed to Client | Open | 0.18738 | 7.2091 | 24850.9322
1648 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | IS19 | Inv1 |  |  |  |  | 1 | 1 | IS19Inv1 | 4753.1 | 1.308% | Inverter |  | Gfdi | 6:13 | 6:13 | 6:13 | 8:42 | 0 | 0 | 2.4833 | 2.4833 | changed the grounding register | Close | 0.032471 | 0.51112 | 1610.5773
1649 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1650 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1651 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0047739 | 7.2962 | 617.2089
1652 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0035804 | 7.2962 | 462.9067
1653 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1654 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0082783 | 7.2962 | 1070.2964
1655 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1656 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1657 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1658 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1659 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1660 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1661 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0 | 7.2962 | 0
1662 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0 | 7.2962 | 0
1663 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1664 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0 | 7.2962 | 0
1665 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0059673 | 7.2962 | 771.5112
1666 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0059673 | 7.2962 | 771.5112
1667 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1668 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0059673 | 7.2962 | 771.5112
1669 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0059673 | 7.2962 | 771.5112
1670 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1671 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0 | 7.2962 | 0
1672 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1673 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1674 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1675 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1676 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1677 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1678 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1679 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1680 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1681 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1682 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0047739 | 7.2962 | 617.2089
1683 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0035804 | 7.2962 | 462.9067
1684 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1685 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0035804 | 7.2962 | 462.9067
1686 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1687 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1688 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1689 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0059673 | 7.2962 | 771.5112
1690 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1691 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1692 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1693 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1694 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1695 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0059673 | 7.2962 | 771.5112
1696 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0047739 | 7.2962 | 617.2089
1697 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1698 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1699 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1700 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0047739 | 7.2962 | 617.2089
1701 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1702 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1703 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1704 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1705 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1706 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1707 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1708 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1709 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0059673 | 7.2962 | 771.5112
1710 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0 | 7.2962 | 0
1711 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1712 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1713 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0059673 | 7.2962 | 771.5112
1714 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0011935 | 7.2962 | 154.3022
1715 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1716 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1717 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1718 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0071608 | 7.2962 | 925.8134
1719 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1720 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1721 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.0083543 | 7.2962 | 1080.1157
1722 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.047739 | 7.2962 | 6172.0894
1723 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.040578 | 7.2962 | 5246.276
1724 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.047739 | 7.2962 | 6172.0894
1725 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Inverter |  | DC Cable theft | 6:07 | 6:07 | 6:07 | 19:43 | 0 | 0 |  | 13.6 | Informed to Project team | Open | 0.042965 | 7.2962 | 5554.8805
1726 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1727 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1728 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 6.3249 | 535.0445
1729 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0033654 | 6.3249 | 401.2833
1730 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1731 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0077812 | 6.3249 | 927.8157
1732 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1733 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1734 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1735 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1736 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1737 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1738 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.3249 | 0
1739 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.3249 | 0
1740 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1741 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.3249 | 0
1742 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV1 | M2 | SCB4 | Str_Typ1(545*29) |  | 0 | 0 | Str_Typ1(545*29) | 15.805 | 0.004348% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0005558 | 6.3249 | 66.2726
1743 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 6.3249 | 668.8056
1744 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1745 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 6.3249 | 668.8056
1746 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 6.3249 | 668.8056
1747 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1748 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.3249 | 0
1749 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1750 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1751 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1752 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS29INV2M1SCB2 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1753 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS29INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1754 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS29INV2M1SCB4 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1755 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS29INV2M1SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1756 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS29INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1757 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS29INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1758 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS29INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1759 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS29INV2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 6.3249 | 535.0445
1760 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS29INV2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0033654 | 6.3249 | 401.2833
1761 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS29INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1762 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS29INV2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0033654 | 6.3249 | 401.2833
1763 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS29 | INV2 | M4 | SCB5 |  |  | 1 | 1 | IS29INV2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1764 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS30INV1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1765 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS30INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1766 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS30INV1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 6.3249 | 668.8056
1767 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS30INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1768 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS30INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1769 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS30INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1770 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS30INV1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1771 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS30INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1772 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS30INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 6.3249 | 668.8056
1773 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS30INV1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 6.3249 | 535.0445
1774 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS30INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1775 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS30INV2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1776 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV2 | M1 | SCB4 |  |  | 1 | 1 | IS30INV2M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1777 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV2 | M1 | SCB5 |  |  | 1 | 1 | IS30INV2M1SCB5 | 127.6 | 0.0351% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 6.3249 | 535.0445
1778 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV2 | M1 | SCB6 |  |  | 1 | 1 | IS30INV2M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1779 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV2 | M4 | SCB4 |  |  | 1 | 1 | IS30INV2M4SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1780 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS33INV1M1SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1781 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS33INV1M1SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1782 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV1 | M2 | SCB1 |  |  | 1 | 1 | IS33INV1M2SCB1 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1783 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS33INV1M2SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1784 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS33INV1M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1785 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS33INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1786 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS33INV1M2SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 6.3249 | 668.8056
1787 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV1 | M3 | SCB1 |  |  | 1 | 1 | IS33INV1M3SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.3249 | 0
1788 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV1 | M3 | SCB3 |  |  | 1 | 1 | IS33INV1M3SCB3 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1789 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS33INV1M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1790 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS33INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 6.3249 | 668.8056
1791 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV2 | M2 | SCB1 |  |  | 1 | 1 | IS33INV2M2SCB1 | 31.9 | 0.008776% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0011218 | 6.3249 | 133.7611
1792 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV2 | M2 | SCB2 |  |  | 1 | 1 | IS33INV2M2SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1793 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV2 | M2 | SCB4 |  |  | 1 | 1 | IS33INV2M2SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1794 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS33INV2M2SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1795 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS33INV2M2SCB6 | 191.4 | 0.05265% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.3249 | 802.5667
1796 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS33INV2M3SCB3 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1797 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS33INV2M3SCB4 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1798 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS33INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.3249 | 936.3278
1799 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV1 | M4 |  |  |  | 1 | 1 | IS30INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.044872 | 6.3249 | 5350.4446
1800 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS30 | INV2 | M2 |  |  |  | 1 | 1 | IS30INV2M2 | 1084.6 | 0.2984% | Inverter |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.038141 | 6.3249 | 4547.8779
1801 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | INV1 | M4 |  |  |  | 1 | 1 | IS33INV1M4 | 1276 | 0.351% | Inverter |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.044872 | 6.3249 | 5350.4446
1802 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Inverter |  | DC Cable theft | 6:17 | 6:17 | 6:17 | 19:04 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.040385 | 6.3249 | 4815.4001
1803 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS15 | INV1 |  |  |  |  | 1 | 1 | IS15INV1 | 4721.2 | 1.299% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 9:15 | 0 | 0 | 3.0667 | 3.0667 | Informed to Project team | Close | 0.039829 | 0.56762 | 1776.6275
1804 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS15 | Inv2 |  |  |  |  | 1 | 1 | IS15Inv2 | 5167.8 | 1.422% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 9:15 | 0 | 0 | 3.0667 | 3.0667 | Informed to Project team | Close | 0.043597 | 0.56762 | 1944.6869
1805 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS17 | INV1 |  |  |  |  | 1 | 1 | IS17INV1 | 350.9 | 0.09653% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 9:17 | 0 | 0 | 3.1 | 3.1 | Informed to Project team | Close | 0.0029924 | 0.60046 | 139.685
1806 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS17 | Inv2 |  |  |  |  | 1 | 1 | IS17Inv2 | 0 | 0% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 9:17 | 0 | 0 | 3.1 | 3.1 | Informed to Project team | Close | 0 | 0.60046 | 0
1807 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS18 | INV1 |  |  |  |  | 1 | 1 | IS18INV1 | 5088.05 | 1.4% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 9:18 | 0 | 0 | 3.1167 | 3.1167 | Informed to Project team | Close | 0.043624 | 0.60893 | 2054.0186
1808 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS18 | Inv2 |  |  |  |  | 1 | 1 | IS18Inv2 | 4657.4 | 1.281% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 9:18 | 0 | 0 | 3.1167 | 3.1167 | Informed to Project team | Close | 0.039931 | 0.60893 | 1880.1675
1809 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS21 | INV1 |  |  |  |  | 1 | 1 | IS21INV1 | 3126.2 | 0.86% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 9:16 | 0 | 0 | 3.0833 | 3.0833 | Informed to Project team | Close | 0.026517 | 0.59142 | 1225.7483
1810 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS21 | Inv2 |  |  |  |  | 1 | 1 | IS21Inv2 | 2823.15 | 0.7766% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 9:16 | 0 | 0 | 3.0833 | 3.0833 | Informed to Project team | Close | 0.023946 | 0.59142 | 1106.9258
1811 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS22 | INV1 |  |  |  |  | 1 | 1 | IS22INV1 | 5040.2 | 1.387% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 9:16 | 0 | 0 | 3.0833 | 3.0833 | Informed to Project team | Close | 0.042751 | 0.59142 | 1976.2064
1812 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS22 | Inv2 |  |  |  |  | 1 | 1 | IS22Inv2 | 3843.95 | 1.057% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 9:16 | 0 | 0 | 3.0833 | 3.0833 | Informed to Project team | Close | 0.032605 | 0.59142 | 1507.1701
1813 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS29 | INV1 |  |  |  |  | 1 | 1 | IS29INV1 | 3572.8 | 0.9829% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.12286 | 3.4069 | 8069.591
1814 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS29 | Inv2 |  |  |  |  | 1 | 1 | IS29Inv2 | 4290.55 | 1.18% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.14754 | 3.4069 | 9690.7142
1815 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS30 | INV1 |  |  |  |  | 1 | 1 | IS30INV1 | 4912.6 | 1.351% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.16893 | 3.4069 | 11095.6876
1816 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS30 | Inv2 |  |  |  |  | 1 | 1 | IS30Inv2 | 4657.4 | 1.281% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.16015 | 3.4069 | 10519.2882
1817 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS33 | INV1 |  |  |  |  | 1 | 1 | IS33INV1 | 4625.5 | 1.272% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.15906 | 3.4069 | 10447.2383
1818 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS33 | Inv2 |  |  |  |  | 1 | 1 | IS33Inv2 | 4481.95 | 1.233% | Inverter |  | HT cable puncher by project team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.15412 | 3.4069 | 10123.0137
1819 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS18 | INV1 |  |  |  |  | 1 | 1 | IS18INV1 | 5088.05 | 1.4% | Inverter |  | Shutdown on request by project | 12:28 | 12:28 | 12:28 | 18:41 | 0 | 0 | 6.2167 | 6.2167 | Informed to Project team | Close | 0.087014 | 1.1029 | 3720.3349
1820 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS18 | Inv2 |  |  |  |  | 1 | 1 | IS18Inv2 | 4657.4 | 1.281% | Inverter |  | Shutdown on request by project | 12:28 | 12:28 | 12:28 | 18:41 | 0 | 0 | 6.2167 | 6.2167 | Informed to Project team | Close | 0.079649 | 1.1029 | 3405.4476
1821 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS31 | INV1 |  |  |  |  | 1 | 1 | IS31INV1 | 5072.1 | 1.395% | Inverter |  | Shutdown on request by project | 16:15 | 16:15 | 16:15 | 18:41 | 0 | 0 | 2.4333 | 2.4333 | Informed to Project team | Close | 0.033952 | 0.14803 | 497.7777
1822 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS31 | Inv2 |  |  |  |  | 1 | 1 | IS31Inv2 | 5311.35 | 1.461% | Inverter |  | Shutdown on request by project | 16:15 | 16:15 | 16:15 | 18:41 | 0 | 0 | 2.4333 | 2.4333 | Informed to Project team | Close | 0.035554 | 0.14803 | 521.2578
1823 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS32 | INV1 |  |  |  |  | 1 | 1 | IS32INV1 | 4976.4 | 1.369% | Inverter |  | Shutdown on request by project | 16:15 | 16:15 | 16:15 | 18:41 | 0 | 0 | 2.4333 | 2.4333 | Informed to Project team | Close | 0.033312 | 0.14803 | 488.3857
1824 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS32 | Inv2 |  |  |  |  | 1 | 1 | IS32Inv2 | 5135.9 | 1.413% | Inverter |  | Shutdown on request by project | 16:15 | 16:15 | 16:15 | 18:41 | 0 | 0 | 2.4333 | 2.4333 | Informed to Project team | Close | 0.034379 | 0.14803 | 504.0391
1825 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.0065816 | 3.4069 | 432.2995
1826 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.0065816 | 3.4069 | 432.2995
1827 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.0043878 | 3.4069 | 288.1997
1828 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.0032908 | 3.4069 | 216.1498
1829 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.0076786 | 3.4069 | 504.3494
1830 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.0076088 | 3.4069 | 499.7644
1831 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.0076786 | 3.4069 | 504.3494
1832 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.0065816 | 3.4069 | 432.2995
1833 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.0076786 | 3.4069 | 504.3494
1834 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.0076786 | 3.4069 | 504.3494
1835 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.0076786 | 3.4069 | 504.3494
1836 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.0065816 | 3.4069 | 432.2995
1837 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0 | 3.4069 | 0
1838 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0 | 3.4069 | 0
1839 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0.0076786 | 3.4069 | 504.3494
1840 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:11 | 6:11 | 6:11 | 18:41 | 0 | 0 |  | 12.5 | Informed to Project team | Open | 0 | 3.4069 | 0
1841 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 182174.52 | 50.12% |  |  | PTR-1 Trip in earht fault | 6:11 | 6:11 | 6:11 | 9:04 | 0 | 0 | 2.8833 | 2.8833 | Found the Incomer -30 cable fault then isolted the same and reset the realy and charge the PTR | Close | 1.445 | 0.52462 | 63360.4809
1842 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS29 | INV1 |  |  |  |  | 1 | 1 | IS29INV1 | 3572.8 | 0.9829% | Inverter |  | HT cable puncher by project team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.12925 | 6.823 | 16161.0893
1843 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS29 | Inv2 |  |  |  |  | 1 | 1 | IS29Inv2 | 4290.55 | 1.18% | Inverter |  | HT cable puncher by project team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.15521 | 6.823 | 19407.7367
1844 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS30 | INV1 |  |  |  |  | 1 | 1 | IS30INV1 | 4912.6 | 1.351% | Inverter |  | HT cable puncher by project team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.17771 | 6.823 | 22221.4978
1845 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS30 | Inv2 |  |  |  |  | 1 | 1 | IS30Inv2 | 4657.4 | 1.281% | Inverter |  | HT cable puncher by project team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.16848 | 6.823 | 21067.1343
1846 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS33 | INV1 |  |  |  |  | 1 | 1 | IS33INV1 | 4625.5 | 1.272% | Inverter |  | HT cable puncher by project team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.16733 | 6.823 | 20922.8389
1847 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS33 | Inv2 |  |  |  |  | 1 | 1 | IS33Inv2 | 4481.95 | 1.233% | Inverter |  | HT cable puncher by project team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.16213 | 6.823 | 20273.5094
1848 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS4 | Inv2 | M2 |  |  |  | 1 | 1 | IS4Inv2M2 | 1100.55 | 0.3028% | Inverter |  | Gfdi | 0.36458 | 0.36458 | 0.36458 | 0.41319 | 0 | 0 | 1.1667 | 1.1667 | Informed to Client and Team Sungrow | Close | 0.0035321 | 0.72945 | 532.2234
1849 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS4 | Inv2 | M3 |  |  |  | 1 | 1 | IS4Inv2M3 | 1036.75 | 0.2852% | Inverter |  | Gfdi | 0.36458 | 0.36458 | 0.36458 | 0.41319 | 0 | 0 | 1.1667 | 1.1667 | Informed to Client and Team Sungrow | Close | 0.0033274 | 0.72945 | 501.3699
1850 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS4 | Inv2 | M4 |  |  |  | 1 | 1 | IS4Inv2M4 | 1036.75 | 0.2852% | Inverter |  | Gfdi | 0.36458 | 0.36458 | 0.36458 | 0.41319 | 0 | 0 | 1.1667 | 1.1667 | Informed to Client and Team Sungrow | Close | 0.0033274 | 0.72945 | 501.3699
1851 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.0069239 | 6.823 | 865.7726
1852 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.0069239 | 6.823 | 865.7726
1853 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.0046159 | 6.823 | 577.1818
1854 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.0034619 | 6.823 | 432.8863
1855 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.0080778 | 6.823 | 1010.0681
1856 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.0080044 | 6.823 | 1000.8856
1857 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.0080778 | 6.823 | 1010.0681
1858 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.0069239 | 6.823 | 865.7726
1859 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.0080778 | 6.823 | 1010.0681
1860 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.0080778 | 6.823 | 1010.0681
1861 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.0080778 | 6.823 | 1010.0681
1862 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.0069239 | 6.823 | 865.7726
1863 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0 | 6.823 | 0
1864 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0 | 6.823 | 0
1865 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0.0080778 | 6.823 | 1010.0681
1866 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | DC Cable theft | 6:10 | 6:10 | 6:10 | 19:19 | 0 | 0 |  | 13.15 | Informed to Project team | Open | 0 | 6.823 | 0
1867 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS29 | INV1 |  |  |  |  | 1 | 1 | IS29INV1 | 3572.8 | 0.9829% | Inverter |  | HT cable puncher by project team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.1281 | 3.2724 | 7750.9982
1868 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS29 | Inv2 |  |  |  |  | 1 | 1 | IS29Inv2 | 4290.55 | 1.18% | Inverter |  | HT cable puncher by project team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.15383 | 3.2724 | 9308.1183
1869 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS30 | INV1 |  |  |  |  | 1 | 1 | IS30INV1 | 4912.6 | 1.351% | Inverter |  | HT cable puncher by project team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.17614 | 3.2724 | 10657.6225
1870 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS30 | Inv2 |  |  |  |  | 1 | 1 | IS30Inv2 | 4657.4 | 1.281% | Inverter |  | HT cable puncher by project team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.16699 | 3.2724 | 10103.9797
1871 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS33 | INV1 |  |  |  |  | 1 | 1 | IS33INV1 | 4625.5 | 1.272% | Inverter |  | HT cable puncher by project team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.16584 | 3.2724 | 10034.7744
1872 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS33 | Inv2 |  |  |  |  | 1 | 1 | IS33Inv2 | 4481.95 | 1.233% | Inverter |  | HT cable puncher by project team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.1607 | 3.2724 | 9723.3504
1873 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS1 | INV1 | M1 | SCB3 |  |  | 1 | 1 | IS1INV1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 3.2724 | 415.232
1874 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 3.2724 | 415.232
1875 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.004575 | 3.2724 | 276.8214
1876 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS1 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS1INV1M2SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0034312 | 3.2724 | 207.616
1877 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 3.2724 | 484.4374
1878 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS3 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS3INV1M2SCB3 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0079334 | 3.2724 | 480.0334
1879 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS6 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS6INV1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 3.2724 | 484.4374
1880 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS6 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS6INV1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 3.2724 | 415.232
1881 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS6 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS6INV1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 3.2724 | 484.4374
1882 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS6 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS6INV1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 3.2724 | 484.4374
1883 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS6 | INV2 | M4 | SCB6 |  |  | 1 | 1 | IS6INV2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 3.2724 | 484.4374
1884 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS9 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS9INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 3.2724 | 415.232
1885 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS12 | INV1 | M2 | SCB2 |  |  | 1 | 1 | IS12INV1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 3.2724 | 0
1886 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS12 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS12INV1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 3.2724 | 0
1887 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS12 | INV2 | M1 | SCB2 |  |  | 1 | 1 | IS12INV2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 3.2724 | 484.4374
1888 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | IS17 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS17INV1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:14 | 6:14 | 6:14 | 19:16 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 3.2724 | 0
1889 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS1 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS1INV1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0034707 | 6.7411 | 427.689
1890 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 6.7411 | 855.378
1891 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0046276 | 6.7411 | 570.252
1892 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1893 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1894 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1895 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0046276 | 6.7411 | 570.252
1896 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1897 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1898 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1899 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS3 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS3INV2M3SCB4 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080247 | 6.7411 | 988.8688
1900 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1901 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1902 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1903 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1904 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1905 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1906 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1907 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1908 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1909 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1910 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 6.7411 | 855.378
1911 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 6.7411 | 855.378
1912 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1913 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1914 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1915 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 6.7411 | 855.378
1916 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1917 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1918 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1919 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 6.7411 | 855.378
1920 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1921 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.006363 | 6.7411 | 784.0965
1922 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1923 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1924 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1925 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1926 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0057845 | 6.7411 | 712.815
1927 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1928 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0057845 | 6.7411 | 712.815
1929 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1930 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1931 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 6.7411 | 855.378
1932 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1933 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 6.7411 | 855.378
1934 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1935 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS12 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS12Inv1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1936 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0 | 6.7411 | 0
1937 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0069414 | 6.7411 | 855.378
1938 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1939 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1940 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1941 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1942 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1943 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 |  | 13.1833 | Informed to Project team | Open | 0.0080983 | 6.7411 | 997.9409
1944 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | IS19 | Inv1 |  |  |  |  | 1 | 1 | IS19Inv1 | 4753.1 | 1.308% | Inverter |  | Gfdi | 9:44 | 9:44 | 9:44 | 18:05 | 0 | 0 | 8.35 | 8.35 | Restoration done | Close | 0.10918 | 5.6532 | 17813.832
1945 | 2025-06-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 182174.52 | 50.12% | PTR |  | PTR-1 Trip in earht fault | 6:10 | 6:10 | 6:10 | 19:21 | 0 | 0 | 13.1833 | 13.1833 | Restoration done | Close | 6.6068 | 6.7411 | 814148.7382
1946 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS1 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS1INV1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0033171 | 6.0738 | 385.3509
1947 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0066343 | 6.0738 | 770.7019
1948 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0044229 | 6.0738 | 513.8012
1949 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1950 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1951 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1952 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0044229 | 6.0738 | 513.8012
1953 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1954 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1955 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1956 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS3 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS3INV2M3SCB4 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0076696 | 6.0738 | 890.9781
1957 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1958 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1959 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1960 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1961 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1962 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1963 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1964 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1965 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1966 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1967 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0066343 | 6.0738 | 770.7019
1968 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0066343 | 6.0738 | 770.7019
1969 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1970 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1971 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1972 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0066343 | 6.0738 | 770.7019
1973 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1974 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1975 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1976 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0066343 | 6.0738 | 770.7019
1977 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1978 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0060814 | 6.0738 | 706.4767
1979 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1980 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1981 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1982 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1983 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0055286 | 6.0738 | 642.2516
1984 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1985 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0055286 | 6.0738 | 642.2516
1986 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1987 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1988 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0066343 | 6.0738 | 770.7019
1989 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1990 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0066343 | 6.0738 | 770.7019
1991 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1992 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS12 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS12Inv1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1993 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
1994 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0066343 | 6.0738 | 770.7019
1995 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1996 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1997 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1998 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
1999 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2000 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2001 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS17 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS17Inv1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
2002 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS19 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS19Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0066343 | 6.0738 | 770.7019
2003 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS19 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2004 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS19 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv1M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2005 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS19 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS19Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2006 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS19 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS19Inv2M1SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0033171 | 6.0738 | 385.3509
2007 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS19 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS19Inv2M3SCB2 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0022114 | 6.0738 | 256.9006
2008 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS19 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS19Inv2M3SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0055286 | 6.0738 | 642.2516
2009 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS19 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0044229 | 6.0738 | 513.8012
2010 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS19 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv2M3SCB5 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0011057 | 6.0738 | 128.4503
2011 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0055286 | 6.0738 | 642.2516
2012 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0044229 | 6.0738 | 513.8012
2013 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2014 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0055286 | 6.0738 | 642.2516
2015 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00387 | 6.0738 | 449.5761
2016 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0022114 | 6.0738 | 256.9006
2017 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0071871 | 6.0738 | 834.927
2018 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2019 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2020 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.0066343 | 6.0738 | 770.7019
2021 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS22 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS22Inv1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2022 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2023 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0 | 6.0738 | 0
2024 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2025 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS31 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS31Inv2M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2026 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS31 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS31Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2027 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS31 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS31Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2028 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS31 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS31Inv2M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2029 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS32 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS32Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.00774 | 6.0738 | 899.1522
2030 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS1 | Inv2 | M1 |  |  |  | 1 | 1 | IS1Inv2M1 | 1339.8 | 0.3686% | Inverter |  | Neutral point shift ,shut down | 6:23 | 6:23 | 6:23 | 9:05 | 0 | 0 | 2.7 | 2.7 | Restoration done | Close | 0.0099514 | 0.4265 | 378.8312
2031 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS1 | Inv2 | M2 |  |  |  | 1 | 1 | IS1Inv2M2 | 1244.1 | 0.3422% | Inverter |  | Neutral point shift ,shut down | 6:23 | 6:23 | 6:23 | 9:05 | 0 | 0 | 2.7 | 2.7 | Restoration done | Close | 0.0092406 | 0.4265 | 351.7718
2032 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS2 | Inv1 | M4 |  |  |  | 1 | 1 | IS2Inv1M4 | 1339.8 | 0.3686% | Inverter |  | Neutral point shift ,shut down | 6:23 | 6:23 | 6:23 | 9:25 | 0 | 0 | 3.0333 | 3.0333 | Restoration done | Close | 0.01118 | 0.51213 | 454.8933
2033 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS2 | Inv2 | M1 |  |  |  | 1 | 1 | IS2Inv2M1 | 1244.1 | 0.3422% | Inverter |  | Neutral point shift ,shut down | 6:23 | 6:23 | 6:23 | 9:20 | 0 | 0 | 2.95 | 2.95 | Restoration done | Close | 0.010096 | 0.49062 | 404.6553
2034 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS13 | Inv1 | M4 |  |  |  | 1 | 1 | IS13Inv1M4 | 1307.9 | 0.3598% | Inverter |  | Neutral point shift ,shut down | 6:23 | 6:23 | 6:23 | 10:30 | 0 | 0 | 4.1167 | 4.1167 | Restoration done | Close | 0.014812 | 1.1145 | 966.3675
2035 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS13 | Inv2 | M4 |  |  |  | 1 | 1 | IS13Inv2M4 | 1307.9 | 0.3598% | Inverter |  | Neutral point shift ,shut down | 6:23 | 6:23 | 6:23 | 10:25 | 0 | 0 | 4.0333 | 4.0333 | Restoration done | Close | 0.014512 | 1.0397 | 901.5311
2036 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS14 | Inv1 | M4 |  |  |  | 1 | 1 | IS14Inv1M4 | 1307.9 | 0.3598% | Inverter |  | Neutral point shift ,shut down | 6:23 | 6:23 | 6:23 | 10:35 | 0 | 0 | 4.2 | 4.2 | Restoration done | Close | 0.015111 | 1.1876 | 1029.7664
2037 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS14 | Inv2 | M4 |  |  |  | 1 | 1 | IS14Inv2M4 | 1307.9 | 0.3598% | Inverter |  | Neutral point shift ,shut down | 6:23 | 6:23 | 6:23 | 10:35 | 0 | 0 | 4.2 | 4.2 | Restoration done | Close | 0.015111 | 1.1876 | 1029.7664
2038 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS17 | Inv1 | M3 |  |  |  | 1 | 1 | IS17Inv1M3 | 0 | 0% | Inverter |  | Neutral point shift ,shut down | 6:23 | 6:23 | 6:23 | 10:55 | 0 | 0 | 4.5333 | 4.5333 | Restoration done | Close | 0 | 1.4721 | 0
2039 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS21 | Inv1 | M3 |  |  |  | 1 | 1 | IS21Inv1M3 | 510.4 | 0.1404% | Inverter |  | AC under voltage | 6:23 | 6:23 | 6:23 | 10:55 | 0 | 0 | 4.5333 | 4.5333 | Restoration done | Close | 0.0063652 | 1.4721 | 498.1166
2040 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS22 | Inv1 | M2 |  |  |  | 1 | 1 | IS22Inv1M2 | 1276 | 0.351% | Inverter |  | AC under voltage | 6:23 | 6:23 | 6:23 | 10:55 | 0 | 0 | 4.5333 | 4.5333 | Restoration done | Close | 0.015913 | 1.4721 | 1245.2916
2041 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS18 | Inv1 | M1 |  |  |  | 1 | 1 | IS18Inv1M1 | 1291.95 | 0.3554% | Inverter |  | AC under voltage | 10:15 | 10:15 | 10:15 | 10:50 | 0 | 0 | 0.58333 | 0.58333 | Restoration done | Close | 0.0020732 | 0.52806 | 452.2907
2042 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS21 | Inv2 | M4 |  |  |  | 1 | 1 | IS21Inv2M4 | 558.25 | 0.1536% | Inverter |  | AC under voltage | 8:35 | 8:35 | 8:35 | 10:50 | 0 | 0 | 2.25 | 2.25 | Restoration done | Close | 0.0034554 | 1.1631 | 430.4489
2043 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS22 | Inv1 | M3 |  |  |  | 1 | 1 | IS22Inv1M3 | 1307.9 | 0.3598% | Inverter |  | AC under voltage | 10:15 | 10:15 | 10:15 | 10:55 | 0 | 0 | 0.66667 | 0.66667 | Restoration done | Close | 0.0023986 | 0.59372 | 514.8053
2044 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS29 | INV1 |  |  |  |  | 1 | 1 | IS29INV1 | 3572.8 | 0.9829% | Inverter |  | HT cable puncher by project team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.12384 | 6.0738 | 14386.4349
2045 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS29 | Inv2 |  |  |  |  | 1 | 1 | IS29Inv2 | 4290.55 | 1.18% | Inverter |  | HT cable puncher by project team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.14872 | 6.0738 | 17276.567
2046 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS30 | INV1 |  |  |  |  | 1 | 1 | IS30INV1 | 4912.6 | 1.351% | Inverter |  | HT cable puncher by project team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.17028 | 6.0738 | 19781.348
2047 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS30 | Inv2 |  |  |  |  | 1 | 1 | IS30Inv2 | 4657.4 | 1.281% | Inverter |  | HT cable puncher by project team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.16143 | 6.0738 | 18753.7455
2048 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS33 | INV1 |  |  |  |  | 1 | 1 | IS33INV1 | 4625.5 | 1.272% | Inverter |  | HT cable puncher by project team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.16033 | 6.0738 | 18625.2952
2049 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | IS33 | Inv2 |  |  |  |  | 1 | 1 | IS33Inv2 | 4481.95 | 1.233% | Inverter |  | HT cable puncher by project team | 6:23 | 6:23 | 6:23 | 18:59 | 0 | 0 |  | 12.6 | Informed to Project team | Open | 0.15535 | 6.0738 | 18047.2688
2050 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS1 | INV1 | M1 | SCB4 |  |  | 1 | 1 | IS1INV1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0030714 | 6.0738 | 385.3509
2051 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS1 | INV1 | M1 | SCB5 |  |  | 1 | 1 | IS1INV1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0061429 | 5.5393 | 702.8821
2052 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS1 | INV1 | M1 | SCB6 |  |  | 1 | 1 | IS1INV1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0040952 | 5.5393 | 468.5881
2053 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS1 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS1INV2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2054 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2055 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2056 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0040952 | 5.5393 | 468.5881
2057 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2058 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2059 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2060 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS3 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS3INV2M3SCB4 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071015 | 5.5393 | 812.5743
2061 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2062 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2063 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2064 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2065 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2066 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2067 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2068 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2069 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2070 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2071 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0061429 | 5.5393 | 702.8821
2072 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0061429 | 5.5393 | 702.8821
2073 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2074 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2075 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2076 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0061429 | 5.5393 | 702.8821
2077 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2078 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2079 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2080 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0061429 | 5.5393 | 702.8821
2081 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2082 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0056309 | 5.5393 | 644.3086
2083 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2084 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2085 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2086 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2087 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.005119 | 5.5393 | 585.7351
2088 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2089 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.005119 | 5.5393 | 585.7351
2090 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2091 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2092 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0061429 | 5.5393 | 702.8821
2093 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2094 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0061429 | 5.5393 | 702.8821
2095 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2096 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS12 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS12Inv1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2097 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2098 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0061429 | 5.5393 | 702.8821
2099 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2100 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2101 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2102 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2103 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2104 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2105 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS17 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS17Inv1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2106 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS19 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS19Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0061429 | 5.5393 | 702.8821
2107 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS19 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2108 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS19 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv1M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2109 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS19 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS19Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2110 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS19 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS19Inv2M1SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0030714 | 5.5393 | 351.441
2111 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS19 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS19Inv2M3SCB2 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0020476 | 5.5393 | 234.294
2112 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS19 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS19Inv2M3SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.005119 | 5.5393 | 585.7351
2113 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS19 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0040952 | 5.5393 | 468.5881
2114 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS19 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv2M3SCB5 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0010238 | 5.5393 | 117.147
2115 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.005119 | 5.5393 | 585.7351
2116 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0040952 | 5.5393 | 468.5881
2117 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2118 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.005119 | 5.5393 | 585.7351
2119 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0035833 | 5.5393 | 410.0145
2120 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0020476 | 5.5393 | 234.294
2121 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0066548 | 5.5393 | 761.4556
2122 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2123 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2124 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0061429 | 5.5393 | 702.8821
2125 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS22 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS22Inv1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2126 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2127 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0 | 5.5393 | 0
2128 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2129 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS31 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS31Inv2M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2130 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS31 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS31Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2131 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS31 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS31Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2132 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS31 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS31Inv2M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2133 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS32 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS32Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.0071667 | 5.5393 | 820.0291
2134 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS29 | INV1 |  |  |  |  | 1 | 1 | IS29INV1 | 3572.8 | 0.9829% | Inverter |  | HT cable puncher by project team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.11467 | 5.5393 | 13120.4655
2135 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS29 | Inv2 |  |  |  |  | 1 | 1 | IS29Inv2 | 4290.55 | 1.18% | Inverter |  | HT cable puncher by project team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.1377 | 5.5393 | 15756.2733
2136 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS30 | INV1 |  |  |  |  | 1 | 1 | IS30INV1 | 4912.6 | 1.351% | Inverter |  | HT cable puncher by project team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.15767 | 5.5393 | 18040.64
2137 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS30 | Inv2 |  |  |  |  | 1 | 1 | IS30Inv2 | 4657.4 | 1.281% | Inverter |  | HT cable puncher by project team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.14948 | 5.5393 | 17103.4639
2138 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS33 | INV1 |  |  |  |  | 1 | 1 | IS33INV1 | 4625.5 | 1.272% | Inverter |  | HT cable puncher by project team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.14845 | 5.5393 | 16986.3169
2139 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS33 | Inv2 |  |  |  |  | 1 | 1 | IS33Inv2 | 4481.95 | 1.233% | Inverter |  | HT cable puncher by project team | 6:16 | 6:16 | 6:16 | 17:56 | 0 | 0 |  | 11.6667 | Informed to Project team | Open | 0.14385 | 5.5393 | 16459.1553
2140 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS1 | Inv2 | M2 |  |  |  | 1 | 1 | IS1Inv2M2 | 1244.1 | 0.3422% | Inverter |  | Neutral point shift ,shut down | 6:16 | 6:16 | 6:16 | 9:00 | 0 | 0 | 2.7333 | 2.7333 | Restoration done | Close | 0.0093547 | 0.67285 | 554.9558
2141 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS2 | Inv1 | M3 |  |  |  | 1 | 1 | IS2Inv1M3 | 1244.1 | 0.3422% | Inverter |  | Neutral point shift ,shut down | 6:16 | 6:16 | 6:16 | 8:07 | 0 | 0 | 1.85 | 1.85 | Restoration done | Close | 0.0063315 | 0.30499 | 251.5495
2142 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS13 | Inv1 | M2 |  |  |  | 1 | 1 | IS13Inv1M2 | 1276 | 0.351% | Inverter |  | Neutral point shift ,shut down | 6:16 | 6:16 | 6:16 | 8:33 | 0 | 0 | 2.2833 | 2.2833 | Restoration done | Close | 0.008015 | 0.47146 | 398.8278
2143 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS14 | Inv2 | M3 |  |  |  | 1 | 1 | IS14Inv2M3 | 1228.15 | 0.3379% | Inverter |  | Neutral point shift ,shut down | 6:16 | 6:16 | 6:16 | 8:26 | 0 | 0 | 2.1667 | 2.1667 | Restoration done | Close | 0.0073202 | 0.42273 | 344.193
2144 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS12 | INV1 |  |  |  |  | 1 | 1 | IS12INV1 | 0 | 0% | Inverter |  | IDT Trip In O/C Fault | 9:05 | 9:05 | 9:05 | 12:03 | 0 | 0 | 2.9667 | 2.9667 | Restoration done | Close | 0 | 2.0219 | 0
2145 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS12 | Inv2 |  |  |  |  | 1 | 1 | IS12Inv2 | 5295.4 | 1.457% | Inverter |  | IDT Trip In O/C Fault | 9:05 | 9:05 | 9:05 | 12:03 | 0 | 0 | 2.9667 | 2.9667 | Restoration done | Close | 0.043216 | 2.0219 | 7097.9952
2146 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS3 | INV1 |  |  |  |  | 1 | 1 | IS3INV1 | 5105.015 | 1.404% | Inverter |  | IDT Trip In O/C Fault | 12:18 | 12:18 | 12:18 | 13:50 | 0 | 0 | 1.5333 | 1.5333 | Restoration done | Close | 0.021534 | 1.0486 | 3548.8724
2147 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | IS3 | Inv2 |  |  |  |  | 1 | 1 | IS3Inv2 | 5120.82 | 1.409% | Inverter |  | IDT Trip In O/C Fault | 12:18 | 12:18 | 12:18 | 13:50 | 0 | 0 | 1.5333 | 1.5333 | Restoration done | Close | 0.0216 | 1.0486 | 3559.8596
2148 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | IDT Trip In O/C Fault | 12:18 | 12:18 | 12:18 | 13:50 | 0 | 0 | 1.5333 | 1.5333 | Restoration done | Close | 0 | 1.0486 | 0
2149 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2150 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0043819 | 4.0081 | 339.0603
2151 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2152 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2153 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2154 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS3 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS3INV2M3SCB4 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0075986 | 4.0081 | 587.9615
2155 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2156 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2157 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2158 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2159 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2160 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2161 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2162 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2163 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2164 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2165 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0065729 | 4.0081 | 508.5905
2166 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0065729 | 4.0081 | 508.5905
2167 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2168 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2169 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2170 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0065729 | 4.0081 | 508.5905
2171 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2172 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2173 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2174 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0065729 | 4.0081 | 508.5905
2175 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2176 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0060251 | 4.0081 | 466.208
2177 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2178 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2179 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2180 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2181 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0054774 | 4.0081 | 423.8254
2182 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2183 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0054774 | 4.0081 | 423.8254
2184 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2185 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2186 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0065729 | 4.0081 | 508.5905
2187 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2188 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0065729 | 4.0081 | 508.5905
2189 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2190 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0065729 | 4.0081 | 508.5905
2191 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2192 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2193 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2194 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2195 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2196 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2197 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS17 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS17Inv1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2198 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0054774 | 4.0081 | 423.8254
2199 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0038342 | 4.0081 | 296.6778
2200 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.002191 | 4.0081 | 169.5302
2201 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0071206 | 4.0081 | 550.9731
2202 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2203 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2204 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0065729 | 4.0081 | 508.5905
2205 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS22 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS22Inv1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2206 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2207 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0 | 4.0081 | 0
2208 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2209 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS31 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS31Inv2M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.0076683 | 4.0081 | 593.3556
2210 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS31 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS31Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 12:35 | 0 | 0 | 6.3833 | 6.3833 | Informed to Project team | Close | 0.0039212 | 2.5133 | 372.0683
2211 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS31 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS31Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 12:35 | 0 | 0 | 6.3833 | 6.3833 | Informed to Project team | Close | 0.0039212 | 2.5133 | 372.0683
2212 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS31 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS31Inv2M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 12:35 | 0 | 0 | 6.3833 | 6.3833 | Informed to Project team | Close | 0.0039212 | 2.5133 | 372.0683
2213 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS32 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS32Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:12 | 6:12 | 6:12 | 12:35 | 0 | 0 | 6.3833 | 6.3833 | Informed to Project team | Close | 0.0039212 | 2.5133 | 372.0683
2214 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS29 | [5 empty] | 1 | 1 | IS29 | 7863.35 | 2.163% | IDT |  | HT cable puncher by project team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.27003 | 4.0081 | 20894.5936
2215 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS30 | [5 empty] | 1 | 1 | IS30 | 9570 | 2.633% | IDT |  | HT cable puncher by project team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.32864 | 4.0081 | 25429.5257
2216 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS33 | [5 empty] | 1 | 1 | IS33 | 9107.45 | 2.505% | IDT |  | HT cable puncher by project team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.31276 | 4.0081 | 24200.432
2217 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS1 | [5 empty] | 1 | 1 | IS1 | 9091.5 | 2.501% | IDT |  | HT cable puncher by project team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.31221 | 4.0081 | 24158.0494
2218 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS12 | [5 empty] | 1 | 1 | IS12 | 5295.4 | 1.457% | IDT |  | HT cable puncher by project team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.18185 | 4.0081 | 14071.0042
2219 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS19 | [5 empty] | 1 | 1 | IS19 | 8453.5 | 2.326% | IDT |  | HT cable puncher by project team | 6:12 | 6:12 | 6:12 | 18:41 | 0 | 0 |  | 12.4833 | Informed to Project team | Open | 0.2903 | 4.0081 | 22462.7477
2220 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS3 | [5 empty] | 1 | 1 | IS3 | 10225.835 | 2.813% | IDT |  | Isolation Protection | 14:23 | 14:23 | 14:23 | 15:53 | 0 | 0 | 1.5 | 1.5 | Informed to Project team | Close | 0.042196 | 0.59281 | 4018.8412
2221 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS3 | Inv2 | M3 |  |  |  | 1 | 1 | IS3Inv2M3 | 1296.01 | 0.3565% | Inverter |  | Low Insolation Rassistance | 6:12 | 6:12 | 6:12 | 9:07 | 0 | 0 | 2.9167 | 2.9167 | Restoration done | Close | 0.010399 | 0.59213 | 508.7551
2222 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS21 | Inv1 | M1 |  |  |  | 1 | 1 | IS21Inv1M1 | 988.9 | 0.272% | Inverter |  | Low Insolation Rassistance | 6:12 | 6:12 | 6:12 | 9:50 | 0 | 0 | 3.6333 | 3.6333 | Restoration done | Close | 0.0098841 | 1.0585 | 693.9779
2223 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS22 | Inv1 | M3 |  |  |  | 1 | 1 | IS22Inv1M3 | 1307.9 | 0.3598% | Inverter |  | Low Insolation Rassistance | 6:12 | 6:12 | 6:12 | 9:58 | 0 | 0 | 3.7667 | 3.7667 | Restoration done | Close | 0.013552 | 1.1269 | 977.0866
2224 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 182174.52 | 50.12% | PTR |  | O/C and E/F | 12:35 | 12:35 | 12:35 | 14:56 | 0 | 0 | 2.35 | 2.35 | Restoration done | Close | 1.1777 | 0.85506 | 103268.8487
2225 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | IS31 | [5 empty] | 1 | 1 | IS31 | 10383.45 | 2.856% | IDT |  | ICR Cable Faulty By Project Team | 14:56 | 14:56 | 14:56 | 18:41 | 0 | 0 | 3.75 | 3.75 | Restoration done | Close | 0.10712 | 0.64711 | 4454.5832
2226 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2227 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2228 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0045282 | 4.3469 | 367.7214
2229 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2230 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2231 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2232 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS3 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS3INV2M3SCB4 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0078522 | 4.3469 | 637.6624
2233 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2234 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2235 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2236 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2237 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2238 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2239 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2240 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2241 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2242 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2243 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 4.3469 | 551.5822
2244 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 4.3469 | 551.5822
2245 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2246 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2247 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2248 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 4.3469 | 551.5822
2249 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2250 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2251 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2252 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 4.3469 | 551.5822
2253 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2254 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0062262 | 4.3469 | 505.617
2255 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2256 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2257 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2258 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2259 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0056602 | 4.3469 | 459.6518
2260 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2261 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0056602 | 4.3469 | 459.6518
2262 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2263 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2264 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 4.3469 | 551.5822
2265 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2266 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 4.3469 | 551.5822
2267 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2268 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 4.3469 | 551.5822
2269 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2270 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2271 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2272 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2273 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2274 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2275 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS17 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS17Inv1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2276 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0056602 | 4.3469 | 459.6518
2277 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0045282 | 4.3469 | 367.7214
2278 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2279 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0056602 | 4.3469 | 459.6518
2280 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0039621 | 4.3469 | 321.7563
2281 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0022641 | 4.3469 | 183.8607
2282 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0073583 | 4.3469 | 597.5473
2283 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2284 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2285 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 4.3469 | 551.5822
2286 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS22 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS22Inv1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2287 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2288 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 4.3469 | 0
2289 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2290 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS31 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS31Inv2M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2291 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS31 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS31Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2292 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS31 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS31Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2293 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS31 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS31Inv2M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2294 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS32 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS32Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 4.3469 | 643.5125
2295 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS29 | [5 empty] | 1 | 1 | IS29 | 7863.35 | 2.163% | IDT |  | HT cable puncher by project team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.27905 | 4.3469 | 22660.8335
2296 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS30 | [5 empty] | 1 | 1 | IS30 | 9570 | 2.633% | IDT |  | HT cable puncher by project team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.33961 | 4.3469 | 27579.1077
2297 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS33 | [5 empty] | 1 | 1 | IS33 | 9107.45 | 2.505% | IDT |  | HT cable puncher by project team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.3232 | 4.3469 | 26246.1175
2298 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS1 | [5 empty] | 1 | 1 | IS1 | 9091.5 | 2.501% | IDT |  | HT cable puncher by project team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.32263 | 4.3469 | 26200.1523
2299 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS12 | [5 empty] | 1 | 1 | IS12 | 5295.4 | 1.457% | IDT |  | HT cable puncher by project team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.18792 | 4.3469 | 15260.4396
2300 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS19 | [5 empty] | 1 | 1 | IS19 | 8453.5 | 2.326% | IDT |  | HT cable puncher by project team | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.29999 | 4.3469 | 24361.5451
2301 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS3 | Inv1 | M3 |  |  |  | 1 | 1 | IS3Inv1M3 | 1232.79 | 0.3391% | Inverter |  | Neutral point shift ,shut down | 6:26 | 6:26 | 6:26 | 8:20 | 0 | 0 | 1.9 | 1.9 | Restoration done | Close | 0.0064435 | 0.27641 | 225.9059
2302 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS4 | Inv1 | M3 |  |  |  | 1 | 1 | IS4Inv1M3 | 1307.9 | 0.3598% | Inverter |  | Neutral point shift ,shut down | 6:26 | 6:26 | 6:26 | 8:30 | 0 | 0 | 2.0667 | 2.0667 | Restoration done | Close | 0.0074358 | 0.32308 | 280.1382
2303 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS4 | Inv2 | M4 |  |  |  | 1 | 1 | IS4Inv2M4 | 1036.75 | 0.2852% | Inverter |  | Neutral point shift ,shut down | 6:26 | 6:26 | 6:26 | 8:33 | 0 | 0 | 2.1167 | 2.1167 | Restoration done | Close | 0.0060368 | 0.33966 | 233.4564
2304 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS21 | Inv1 | M4 |  |  |  | 1 | 1 | IS21Inv1M4 | 861.3 | 0.2369% | Inverter |  | Neutral point shift ,shut down | 6:26 | 6:26 | 6:26 | 13:46 | 0 | 0 | 7.3333 | 7.3333 | Restoration done | Close | 0.017375 | 2.9843 | 1704.0353
2305 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS21 | Inv2 | M4 |  |  |  | 1 | 1 | IS21Inv2M4 | 558.25 | 0.1536% | Inverter |  | Neutral point shift ,shut down | 6:26 | 6:26 | 6:26 | 10:08 | 0 | 0 | 3.7 | 3.7 | Restoration done | Close | 0.0056821 | 8.622 | 3190.9732
2306 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS22 | Inv1 | M4 |  |  |  | 1 | 1 | IS22Inv1M4 | 1339.8 | 0.3686% | Inverter |  | Neutral point shift ,shut down | 6:26 | 6:26 | 6:26 | 12:30 | 0 | 0 | 6.0667 | 6.0667 | Restoration done | Close | 0.02236 | 2.2405 | 1990.1107
2307 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS17 | Inv1 | M1 |  |  |  | 1 | 1 | IS17Inv1M1 | 287.1 | 0.07898% | Inverter |  | Neutral point shift ,shut down | 6:26 | 6:26 | 6:26 | 9:38 | 0 | 0 | 3.2 | 3.2 | Restoration done | Close | 0.0025273 | 0.5896 | 112.2221
2308 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS31 | [5 empty] | 1 | 1 | IS31 | 10383.45 | 2.856% | IDT |  | IDT Trip (Inverter flash over) | 6:26 | 6:26 | 6:26 | 19:20 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.36848 | 4.3469 | 29923.3318
2309 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS4 | [5 empty] | 1 | 1 | IS4 | 9522.15 | 2.619% | IDT |  | IDT Trip In O/C Fault | 12:28 | 12:28 | 12:28 | 17:23 | 0 | 0 | 4.9167 | 4.9167 | Restoration done | Close | 0.12879 | 2.0092 | 12683.328
2310 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS13 | [5 empty] | 1 | 1 | IS13 | 10271.8 | 2.826% | IDT |  | IDT Trip In O/C Fault | 11:17 | 11:17 | 11:17 | 18:01 | 0 | 0 | 6.7333 | 6.7333 | Restoration done | Close | 0.19026 | 2.836 | 19312.4904
2311 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS17 | [5 empty] | 1 | 1 | IS17 | 350.9 | 0.09653% | IDT |  | IDT Trip In O/C Fault | 12:33 | 12:33 | 12:33 | 18:42 | 0 | 0 | 6.15 | 6.15 | Restoration done | Close | 0.0059366 | 2.0825 | 484.4481
2312 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | IS15 | [5 empty] | 1 | 1 | IS15 | 9889 | 2.72% | IDT |  | IDT Trip In O/C Fault | 11:22 | 11:22 | 11:22 | 18:26 | 0 | 0 | 7.0667 | 7.0667 | Restoration done | Close | 0.19224 | 2.8012 | 18364.9591
2313 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2314 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2315 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.004575 | 4.0604 | 343.4804
2316 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2317 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2318 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2319 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS3 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS3INV2M3SCB4 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0079334 | 4.0604 | 595.6262
2320 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2321 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2322 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2323 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2324 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2325 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2326 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2327 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2328 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2329 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2330 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 4.0604 | 515.2206
2331 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 4.0604 | 515.2206
2332 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2333 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2334 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2335 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 4.0604 | 515.2206
2336 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2337 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2338 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2339 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 4.0604 | 515.2206
2340 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2341 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0062906 | 4.0604 | 472.2855
2342 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2343 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2344 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2345 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 4.0604 | 429.3505
2346 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2347 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 4.0604 | 429.3505
2348 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2349 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2350 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 4.0604 | 515.2206
2351 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2352 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 4.0604 | 515.2206
2353 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2354 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 4.0604 | 515.2206
2355 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2356 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2357 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2358 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2359 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS17 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS17Inv1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2360 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 4.0604 | 429.3505
2361 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.004575 | 4.0604 | 343.4804
2362 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2363 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0057187 | 4.0604 | 429.3505
2364 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0040031 | 4.0604 | 300.5453
2365 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0022875 | 4.0604 | 171.7402
2366 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0074343 | 4.0604 | 558.1556
2367 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2368 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2369 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0068624 | 4.0604 | 515.2206
2370 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2371 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0 | 4.0604 | 0
2372 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.0080062 | 4.0604 | 601.0907
2373 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS2 | Inv1 | M3 |  |  |  | 1 | 1 | IS2Inv1M3 | 1244.1 | 0.3422% | Inverter |  | Neutral point shift ,shut down | 6:18 | 6:18 | 6:18 | 8:34 | 0 | 0 | 2.2667 | 2.2667 | Inverter Reboot and restart | Close | 0.0077575 | 0.28232 | 232.8556
2374 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS3 | Inv1 | M2 |  |  |  | 1 | 1 | IS3Inv1M2 | 1327.62 | 0.3652% | Inverter |  | Neutral point shift ,shut down | 6:18 | 6:18 | 6:18 | 8:41 | 0 | 0 | 2.3833 | 2.3833 | Inverter Reboot and restart | Close | 0.0087044 | 0.32362 | 284.8374
2375 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS4 | Inv1 | M4 |  |  |  | 1 | 1 | IS4Inv1M4 | 1228.15 | 0.3379% | Inverter |  | Neutral point shift ,shut down | 6:18 | 6:18 | 6:18 | 8:50 | 0 | 0 | 2.5333 | 2.5333 | Inverter Reboot and restart | Close | 0.008559 | 0.36783 | 299.4954
2376 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS8 | Inv1 | M1 |  |  |  | 1 | 1 | IS8Inv1M1 | 1244.1 | 0.3422% | Inverter |  | Neutral point shift ,shut down | 6:18 | 6:18 | 6:18 | 9:16 | 0 | 0 | 2.9667 | 2.9667 | Inverter Reboot and restart | Close | 0.010153 | 0.48521 | 400.195
2377 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS14 | Inv2 | M2 |  |  |  | 1 | 1 | IS14Inv2M2 | 1276 | 0.351% | Inverter |  | Neutral point shift ,shut down | 6:18 | 6:18 | 6:18 | 9:38 | 0 | 0 | 3.3333 | 3.3333 | Inverter Reboot and restart | Close | 0.011701 | 0.52971 | 448.0977
2378 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS13 | Inv2 | M4 |  |  |  | 1 | 1 | IS13Inv2M4 | 1307.9 | 0.3598% | Inverter |  | Neutral point shift ,shut down | 6:18 | 6:18 | 6:18 | 9:47 | 0 | 0 | 3.4833 | 3.4833 | Inverter Reboot and restart | Close | 0.012533 | 0.55097 | 477.7359
2379 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS13 | Inv2 | M3 |  |  |  | 1 | 1 | IS13Inv2M3 | 1307.9 | 0.3598% | Inverter |  | Neutral point shift ,shut down | 6:18 | 6:18 | 6:18 | 9:47 | 0 | 0 | 3.4833 | 3.4833 | Inverter Reboot and restart | Close | 0.012533 | 0.55097 | 477.7359
2380 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS18 | Inv1 | M1 |  |  |  | 1 | 1 | IS18Inv1M1 | 1291.95 | 0.3554% | Inverter |  | AC Over Voltage | 10:10 | 10:10 | 10:10 | 10:16 | 0 | 0 | 0.1 | 0.1 | after Visual Inspection INV Reboot | Close | 0.00035541 | 0.041775 | 35.7808
2381 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS18 | Inv1 | M2 |  |  |  | 1 | 1 | IS18Inv1M2 | 1212.2 | 0.3335% | Inverter |  | AC Over Voltage | 10:10 | 10:10 | 10:10 | 10:16 | 0 | 0 | 0.1 | 0.1 | after Visual Inspection INV Reboot | Close | 0.00033347 | 0.041775 | 33.5721
2382 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS17 | Inv1 | M3 |  |  |  | 1 | 1 | IS17Inv1M3 | 0 | 0% | Inverter |  | Neutral point shift ,shut down | 6:18 | 6:18 | 6:18 | 10:41 | 0 | 0 | 4.3833 | 4.3833 | Inverter Reboot and restart | Close | 0 | 0.79333 | 0
2383 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS17 | Inv2 | M4 |  |  |  | 1 | 1 | IS17Inv2M4 | 0 | 0% | Inverter |  | Neutral point shift ,shut down | 6:18 | 6:18 | 6:18 | 10:39 | 0 | 0 | 4.35 | 4.35 | Inverter Reboot and restart | Close | 0 | 0.78124 | 0
2384 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS21 | Inv2 | M4 |  |  |  | 1 | 1 | IS21Inv2M4 | 558.25 | 0.1536% | Inverter |  | Neutral point shift ,shut down | 6:18 | 6:18 | 6:18 | 11:30 | 0 | 0 | 5.2 | 5.2 | Inverter Reboot and restart | Close | 0.0079857 | 1.1903 | 440.5235
2385 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS22 | Inv1 | M4 |  |  |  | 1 | 1 | IS22Inv1M4 | 1339.8 | 0.3686% | Inverter |  | Neutral point shift ,shut down | 6:18 | 6:18 | 6:18 | 11:37 | 0 | 0 | 5.3167 | 5.3167 | Inverter Reboot and restart | Close | 0.019596 | 1.2525 | 1112.4799
2386 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS15 | [5 empty] | 1 | 1 | IS15 | 9889 | 2.72% | IDT |  | IDT Trip In O/C Fault | 13:06 | 13:06 | 13:06 | 14:52 | 0 | 0 | 1.7667 | 1.7667 | Relay Setting Update & IDT Charged | Close | 0.048061 | 0.60667 | 3977.3482
2387 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS31 | [5 empty] | 1 | 1 | IS31 | 10383.45 | 2.856% | IDT |  | HT cable puncher by project team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.37229 | 4.0604 | 27950.7171
2388 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS29 | [5 empty] | 1 | 1 | IS29 | 7863.35 | 2.163% | IDT |  | HT cable puncher by project team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.28193 | 4.0604 | 21166.9793
2389 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS30 | [5 empty] | 1 | 1 | IS30 | 9570 | 2.633% | IDT |  | HT cable puncher by project team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.34312 | 4.0604 | 25761.0296
2390 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS33 | [5 empty] | 1 | 1 | IS33 | 9107.45 | 2.505% | IDT |  | HT cable puncher by project team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.32654 | 4.0604 | 24515.9132
2391 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS1 | [5 empty] | 1 | 1 | IS1 | 9091.5 | 2.501% | IDT |  | HT cable puncher by project team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.32597 | 4.0604 | 24472.9781
2392 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS12 | [5 empty] | 1 | 1 | IS12 | 5295.4 | 1.457% | IDT |  | HT cable puncher by project team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.18986 | 4.0604 | 14254.4364
2393 | 2025-06-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:18 | 19:20 | 13.0333 | IS19 | [5 empty] | 1 | 1 | IS19 | 8453.5 | 2.326% | IDT |  | HT cable puncher by project team | 6:18 | 6:18 | 6:18 | 19:20 | 0 | 0 |  | 13.0333 | Informed to Project team | Open | 0.30309 | 4.0604 | 22755.5762
2394 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2395 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2396 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0042181 | 4.0602 | 343.4633
2397 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2398 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2399 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2400 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS3 | INV2 | M3 | SCB4 |  |  | 1 | 1 | IS3INV2M3SCB4 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073146 | 4.0602 | 595.5966
2401 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2402 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2403 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2404 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2405 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2406 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2407 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2408 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2409 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2410 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2411 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0063271 | 4.0602 | 515.1949
2412 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0063271 | 4.0602 | 515.1949
2413 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2414 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2415 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2416 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0063271 | 4.0602 | 515.1949
2417 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2418 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2419 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2420 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0063271 | 4.0602 | 515.1949
2421 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2422 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0057999 | 4.0602 | 472.262
2423 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2424 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2425 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2426 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0052726 | 4.0602 | 429.3291
2427 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2428 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0052726 | 4.0602 | 429.3291
2429 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2430 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2431 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0063271 | 4.0602 | 515.1949
2432 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2433 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0063271 | 4.0602 | 515.1949
2434 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2435 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0063271 | 4.0602 | 515.1949
2436 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2437 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2438 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2439 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2440 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS17 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS17Inv1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2441 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0052726 | 4.0602 | 429.3291
2442 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0042181 | 4.0602 | 343.4633
2443 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2444 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0052726 | 4.0602 | 429.3291
2445 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0036908 | 4.0602 | 300.5304
2446 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.002109 | 4.0602 | 171.7316
2447 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0068544 | 4.0602 | 558.1279
2448 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2449 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2450 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0063271 | 4.0602 | 515.1949
2451 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2452 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0 | 4.0602 | 0
2453 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.0073817 | 4.0602 | 601.0608
2454 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS1 | Inv2 | M2 |  |  |  | 1 | 1 | IS1Inv2M2 | 1244.1 | 0.3422% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.041126 | 4.0602 | 3348.7671
2455 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS30 | Inv1 |  |  |  |  | 1 | 1 | IS30Inv1 | 4912.6 | 1.351% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.1624 | 4.0602 | 13223.3369
2456 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.040072 | 4.0602 | 3262.9013
2457 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.035854 | 4.0602 | 2919.438
2458 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS30 | Inv2 | M4 |  |  |  | 1 | 1 | IS30Inv2M4 | 1339.8 | 0.3686% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.04429 | 4.0602 | 3606.3646
2459 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS31 | [5 empty] | 1 | 1 | IS31 | 10383.45 | 2.856% | IDT |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.34325 | 4.0602 | 27949.3257
2460 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS33 | Inv1 | M2 |  |  |  | 1 | 1 | IS33Inv1M2 | 1244.1 | 0.3422% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.041126 | 4.0602 | 3348.7671
2461 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS33 | Inv1 | M3 |  |  |  | 1 | 1 | IS33Inv1M3 | 925.1 | 0.2545% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.030581 | 4.0602 | 2490.1089
2462 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS33 | Inv1 | M4 |  |  |  | 1 | 1 | IS33Inv1M4 | 1276 | 0.351% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.042181 | 4.0602 | 3434.633
2463 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.037963 | 4.0602 | 3091.1697
2464 | 2025-06-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:44 | 18:45 | 12.0167 | IS33 | Inv2 | M2 |  |  |  | 1 | 1 | IS33Inv2M2 | 1116.5 | 0.3071% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:44 | 6:44 | 6:44 | 18:45 | 0 | 0 |  | 12.0167 | Informed to Project team | Open | 0.036908 | 4.0602 | 3005.3038
2465 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2466 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2467 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0045282 | 6.07 | 605.2259
2468 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2469 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2470 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2471 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2472 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2473 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2474 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2475 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2476 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2477 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2478 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2479 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2480 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2481 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 6.07 | 907.8388
2482 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 6.07 | 907.8388
2483 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2484 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2485 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2486 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 6.07 | 907.8388
2487 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2488 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2489 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2490 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 6.07 | 907.8388
2491 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2492 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0062262 | 6.07 | 832.1856
2493 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2494 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2495 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2496 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0056602 | 6.07 | 756.5324
2497 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2498 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0056602 | 6.07 | 756.5324
2499 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2500 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2501 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 6.07 | 907.8388
2502 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2503 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 6.07 | 907.8388
2504 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2505 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 6.07 | 907.8388
2506 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2507 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2508 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2509 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2510 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS17 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS17Inv1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2511 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0056602 | 6.07 | 756.5324
2512 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0045282 | 6.07 | 605.2259
2513 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2514 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0056602 | 6.07 | 756.5324
2515 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0039621 | 6.07 | 529.5727
2516 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0022641 | 6.07 | 302.6129
2517 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0073583 | 6.07 | 983.4921
2518 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2519 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2520 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 6.07 | 907.8388
2521 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2522 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 6.07 | 0
2523 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 6.07 | 1059.1453
2524 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS3 | [5 empty] | 1 | 1 | IS3 | 10225.835 | 2.813% | IDT |  | Shutdown taken by Project team | 17:50 | 17:50 | 17:50 | 19:18 | 0 | 0 | 1.4667 | 1.4667 | Informed to Project team | Close | 0.041258 | 0.15971 | 1276.1943
2526 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS30 | Inv1 |  |  |  |  | 1 | 1 | IS30Inv1 | 4912.6 | 1.351% | Module |  | SPD FAULT | 6:24 | 6:24 | 6:24 | 18:56 | 0 | 0 | 12.5333 | 12.5333 | SPD Replaced | Close | 0.16938 | 6.0571 | 23251.8979
2527 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | SPD FAULT | 6:24 | 6:24 | 6:24 | 18:56 | 0 | 0 | 12.5333 | 12.5333 | SPD Replaced | Close | 0.041795 | 6.0571 | 5737.4813
2528 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | SPD FAULT | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.038489 | 6.07 | 5144.4201
2533 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS31 | [5 empty] | 1 | 1 | IS31 | 10383.45 | 2.856% | IDT |  | IDT TRIP (INVERTER FLASH OVER) | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.36848 | 6.07 | 49250.2567
2534 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS33 | Inv1 | M2 |  |  |  | 1 | 1 | IS33Inv1M2 | 1244.1 | 0.3422% | Module |  | SCB Dc string cable theft | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.04415 | 6.07 | 5900.9524
2535 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS33 | Inv1 | M3 |  |  |  | 1 | 1 | IS33Inv1M3 | 925.1 | 0.2545% | Module |  | SCB Dc string cable theft | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.032829 | 6.07 | 4387.8877
2536 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS33 | Inv1 | M4 |  |  |  | 1 | 1 | IS33Inv1M4 | 1276 | 0.351% | Module |  | SCB Dc string cable theft | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.045282 | 6.07 | 6052.2589
2537 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Module |  | SCB Dc string cable theft | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.040753 | 6.07 | 5447.033
2538 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS33 | Inv2 | M2 |  |  |  | 1 | 1 | IS33Inv2M2 | 1116.5 | 0.3071% | Module |  | SCB Dc string cable theft | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.039621 | 6.07 | 5295.7265
2539 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS33 | Inv2 | M3 |  |  |  | 1 | 1 | IS33Inv2M3 | 1260.05 | 0.3466% | Module |  | SCB Dc string cable theft | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.044716 | 6.07 | 5976.6057
2540 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | IS1 | Inv2 | M2 |  |  |  | 1 | 1 | IS1Inv2M2 | 1244.1 | 0.3422% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:18 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.04415 | 6.07 | 5900.9524
2541 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2542 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2543 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0044053 | 3.5324 | 352.213
2544 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2545 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2546 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2547 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2548 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2549 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2550 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2551 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2552 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2553 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2554 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2555 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2556 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2557 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.006608 | 3.5324 | 528.3195
2558 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.006608 | 3.5324 | 528.3195
2559 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2560 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2561 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2562 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.006608 | 3.5324 | 528.3195
2563 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2564 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2565 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2566 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.006608 | 3.5324 | 528.3195
2567 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2568 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0060573 | 3.5324 | 484.2929
2569 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2570 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2571 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2572 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0055066 | 3.5324 | 440.2662
2573 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2574 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0055066 | 3.5324 | 440.2662
2575 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2576 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2577 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.006608 | 3.5324 | 528.3195
2578 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2579 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.006608 | 3.5324 | 528.3195
2580 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2581 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.006608 | 3.5324 | 528.3195
2582 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2583 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2584 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2585 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2586 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS17 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS17Inv1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2587 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0055066 | 3.5324 | 440.2662
2588 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0044053 | 3.5324 | 352.213
2589 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2590 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0055066 | 3.5324 | 440.2662
2591 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0038546 | 3.5324 | 308.1864
2592 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0022027 | 3.5324 | 176.1065
2593 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0071586 | 3.5324 | 572.3461
2594 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2595 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2596 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.006608 | 3.5324 | 528.3195
2597 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2598 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0 | 3.5324 | 0
2599 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.0077093 | 3.5324 | 616.3727
2600 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS1 | Inv2 | M2 |  |  |  | 1 | 1 | IS1Inv2M2 | 1244.1 | 0.3422% | Module |  | DC Switch anomaly | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.042952 | 3.5324 | 3434.0767
2601 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS3 | Inv1 |  |  |  |  | 1 | 1 | IS3Inv1 | 5105.015 | 1.404% | Inverter |  | Rasistor burn Out | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 | 12.55 | 12.55 | Inverter Rasister Repaced | Close | 0.17625 | 3.5324 | 14091.3214
2602 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS29 | Inv1 | M2 |  |  |  | 1 | 1 | IS29Inv1M2 | 733.7 | 0.2018% | Module |  | LOW INSULATION RESISTENCE | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Inverter Check and Reboot | Open | 0.02533 | 3.5324 | 2025.2247
2603 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS30 | Inv1 | M1 |  |  |  | 1 | 1 | IS30Inv1M1 | 1244.1 | 0.3422% | Module |  | SPD FAULTY | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.042952 | 3.5324 | 3434.0767
2604 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS30 | Inv1 | M3 |  |  |  | 1 | 1 | IS30Inv1M3 | 1116.5 | 0.3071% | Module |  | SPD FAULTY | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.038546 | 3.5324 | 3081.8637
2605 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | SPD FAULTY | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.044053 | 3.5324 | 3522.1299
2606 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | SPD FAULTY | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.04185 | 3.5324 | 3346.0234
2607 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | SPD FAULTY | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.037445 | 3.5324 | 2993.8104
2608 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS30 | Inv2 | M3 |  |  |  | 1 | 1 | IS30Inv2M3 | 1020.8 | 0.2808% | Module |  | LOW INSULATION RESISTENCE | 6:18 | 6:18 | 6:18 | 17:15 | 0 | 0 | 10.95 | 10.95 | Inverter Check and Reboot | Close | 0.030749 | 3.3972 | 2709.7861
2609 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS31 | [5 empty] | 1 | 1 | IS31 | 10383.45 | 2.856% | IDT |  | IDT TRIP (INVERTER FLASH OVER) | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.35848 | 3.5324 | 28661.3322
2610 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS32 | Inv1 | M2 |  |  |  | 1 | 1 | IS32Inv1M2 | 1244.1 | 0.3422% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.042952 | 3.5324 | 3434.0767
2611 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS32 | Inv1 | M3 |  |  |  | 1 | 1 | IS32Inv1M3 | 1307.9 | 0.3598% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.045154 | 3.5324 | 3610.1832
2612 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS33 | Inv1 | M2 |  |  |  | 1 | 1 | IS33Inv1M2 | 1244.1 | 0.3422% | Module |  | SCB Dc string cable theft | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.042952 | 3.5324 | 3434.0767
2613 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS33 | Inv1 | M3 |  |  |  | 1 | 1 | IS33Inv1M3 | 925.1 | 0.2545% | Module |  | SCB Dc string cable theft | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.031938 | 3.5324 | 2553.5442
2614 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS33 | Inv1 | M4 |  |  |  | 1 | 1 | IS33Inv1M4 | 1276 | 0.351% | Module |  | SCB Dc string cable theft | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.044053 | 3.5324 | 3522.1299
2615 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Module |  | SCB Dc string cable theft | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.039648 | 3.5324 | 3169.9169
2616 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS33 | Inv2 | M2 |  |  |  | 1 | 1 | IS33Inv2M2 | 1116.5 | 0.3071% | Module |  | SCB Dc string cable theft | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.038546 | 3.5324 | 3081.8637
2617 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | IS33 | Inv2 | M3 |  |  |  | 1 | 1 | IS33Inv2M3 | 1260.05 | 0.3466% | Module |  | SCB Dc string cable theft | 6:18 | 6:18 | 6:18 | 18:51 | 0 | 0 |  | 12.55 | Informed to Project team | Open | 0.043502 | 3.5324 | 3478.1033
2618 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2619 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2620 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0043761 | 3.1267 | 311.7566
2621 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2622 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2623 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2624 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2625 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2626 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2627 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2628 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2629 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2630 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2631 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2632 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2633 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2634 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0065641 | 3.1267 | 467.6349
2635 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0065641 | 3.1267 | 467.6349
2636 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2637 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2638 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2639 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0065641 | 3.1267 | 467.6349
2640 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2641 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2642 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2643 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0065641 | 3.1267 | 467.6349
2644 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2645 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0060171 | 3.1267 | 428.6653
2646 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2647 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2648 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2649 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0054701 | 3.1267 | 389.6958
2650 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2651 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0054701 | 3.1267 | 389.6958
2652 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2653 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2654 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0065641 | 3.1267 | 467.6349
2655 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2656 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0065641 | 3.1267 | 467.6349
2657 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2658 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0065641 | 3.1267 | 467.6349
2659 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2660 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2661 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2662 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2663 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS17 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS17Inv1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2664 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0054701 | 3.1267 | 389.6958
2665 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0043761 | 3.1267 | 311.7566
2666 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2667 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0054701 | 3.1267 | 389.6958
2668 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.003829 | 3.1267 | 272.787
2669 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.002188 | 3.1267 | 155.8783
2670 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0071111 | 3.1267 | 506.6045
2671 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2672 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2673 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0065641 | 3.1267 | 467.6349
2674 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2675 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0 | 3.1267 | 0
2676 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.0076581 | 3.1267 | 545.5741
2677 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS29 | Inv1 | M2 |  |  |  | 1 | 1 | IS29Inv1M2 | 733.7 | 0.2018% | Module |  | ISLANDING PROTECTION | 6:38 | 6:38 | 6:38 | 10:05 | 0 | 0 | 3.45 | 3.45 | Inverter Check and Reboot | Close | 0.0069634 | 1.0102 | 579.1888
2678 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS30 | Inv1 | M1 |  |  |  | 1 | 1 | IS30Inv1M1 | 1244.1 | 0.3422% | Module |  | INITAL STANDBY,ISLANDING PROTECTION | 6:38 | 6:38 | 6:38 | 9:55 | 0 | 0 | 3.2833 | 3.2833 | Inverter Check and Reboot | Close | 0.011237 | 0.88205 | 857.4875
2679 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS30 | Inv1 | M3 |  |  |  | 1 | 1 | IS30Inv1M3 | 1116.5 | 0.3071% | Module |  | 10-DSP COMMINUCATION ANOMALY | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.03829 | 3.1267 | 2727.8703
2680 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | ALL SCB string cable theft | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.043761 | 3.1267 | 3117.566
2681 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | ALL SCB string cable theft | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.041572 | 3.1267 | 2961.6877
2682 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | ALL SCB string cable theft | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.037196 | 3.1267 | 2649.9311
2683 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS31 | [5 empty] | 1 | 1 | IS31 | 10383.45 | 2.856% | IDT |  | IDT TRIP (INVERTER FLASH OVER) | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.3561 | 3.1267 | 25369.1936
2684 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS32 | Inv1 | M2 |  |  |  | 1 | 1 | IS32Inv1M2 | 1244.1 | 0.3422% | Module |  | MODULE FAULT | 6:38 | 6:38 | 6:38 | 9:45 | 0 | 0 | 3.1167 | 3.1167 | Inverter Check and Reboot | Close | 0.010667 | 0.76885 | 747.4372
2685 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS32 | Inv1 | M3 |  |  |  | 1 | 1 | IS32Inv1M3 | 1307.9 | 0.3598% | Module |  | MODULE FAULT | 6:38 | 6:38 | 6:38 | 9:45 | 0 | 0 | 3.1167 | 3.1167 | Inverter Check and Reboot | Close | 0.011214 | 0.76885 | 785.7673
2686 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS33 | Inv1 | M2 |  |  |  | 1 | 1 | IS33Inv1M2 | 1244.1 | 0.3422% | Module |  | ALL SCB string cable theft | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.042666 | 3.1267 | 3039.6269
2687 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS33 | Inv1 | M3 |  |  |  | 1 | 1 | IS33Inv1M3 | 925.1 | 0.2545% | Module |  | ALL SCB string cable theft | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.031726 | 3.1267 | 2260.2354
2688 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS33 | Inv1 | M4 |  |  |  | 1 | 1 | IS33Inv1M4 | 1276 | 0.351% | Module |  | ALL SCB string cable theft | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.043761 | 3.1267 | 3117.566
2689 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Module |  | ALL SCB string cable theft | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.039384 | 3.1267 | 2805.8094
2690 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS33 | Inv2 | M2 |  |  |  | 1 | 1 | IS33Inv2M2 | 1116.5 | 0.3071% | Module |  | ALL SCB string cable theft | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.03829 | 3.1267 | 2727.8703
2691 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS33 | Inv2 | M3 |  |  |  | 1 | 1 | IS33Inv2M3 | 1260.05 | 0.3466% | Module |  | ALL SCB string cable theft | 6:38 | 6:38 | 6:38 | 19:06 | 0 | 0 |  | 12.4667 | Informed to Project team | Open | 0.043213 | 3.1267 | 3078.5965
2692 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | IS1 | Inv2 | M2 |  |  |  | 1 | 1 | IS1Inv2M2 | 1244.1 | 0.3422% | Module |  | SHUT DOWN GFDI PROTECTION | 10:37 | 10:37 | 10:37 | 12:10 | 0 | 0 | 1.55 | 1.55 | Inverter Check and Reboot | Close | 0.0053048 | 0.99518 | 967.463
2693 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2694 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2695 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0045691 | 5.683 | 566.6421
2696 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2697 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2698 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2699 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2700 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2701 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2702 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2703 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2704 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2705 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2706 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2707 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2708 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2709 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 5.683 | 849.9632
2710 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 5.683 | 849.9632
2711 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2712 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2713 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2714 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 5.683 | 849.9632
2715 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2716 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2717 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2718 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 5.683 | 849.9632
2719 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2720 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0062825 | 5.683 | 779.1329
2721 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2722 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2723 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2724 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0057114 | 5.683 | 708.3026
2725 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2726 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0057114 | 5.683 | 708.3026
2727 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2728 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2729 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 5.683 | 849.9632
2730 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2731 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 5.683 | 849.9632
2732 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2733 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 5.683 | 849.9632
2734 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2735 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2736 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2737 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2738 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS17 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS17Inv1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2739 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0057114 | 5.683 | 708.3026
2740 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0045691 | 5.683 | 566.6421
2741 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2742 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0057114 | 5.683 | 708.3026
2743 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.003998 | 5.683 | 495.8119
2744 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0022846 | 5.683 | 283.3211
2745 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0074248 | 5.683 | 920.7934
2746 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2747 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2748 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 5.683 | 849.9632
2749 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2750 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 5.683 | 0
2751 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 5.683 | 991.6237
2752 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS30 | Inv1 | M3 |  |  |  | 1 | 1 | IS30Inv1M3 | 1116.5 | 0.3071% | Module |  | DSP Communication Anomay | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.03998 | 5.683 | 4958.1185
2753 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | DSP Communication Anomay | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.045691 | 5.683 | 5666.4212
2754 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | DSP Communication Anomay | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.043407 | 5.683 | 5383.1001
2755 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | DSP Communication Anomay | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.038837 | 5.683 | 4816.458
2756 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS33 | Inv1 | M2 |  |  |  | 1 | 1 | IS33Inv1M2 | 1244.1 | 0.3422% | Module |  | DSP Communication Anomay | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.044549 | 5.683 | 5524.7607
2757 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS33 | Inv1 | M3 |  |  |  | 1 | 1 | IS33Inv1M3 | 925.1 | 0.2545% | Module |  | DSP Communication Anomay | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.033126 | 5.683 | 4108.1554
2758 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS33 | Inv1 | M4 |  |  |  | 1 | 1 | IS33Inv1M4 | 1276 | 0.351% | Module |  | DSP Communication Anomay | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.045691 | 5.683 | 5666.4212
2759 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Module |  | DSP Communication Anomay | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.041122 | 5.683 | 5099.7791
2760 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS33 | Inv2 | M4 |  |  |  | 1 | 1 | IS33Inv2M4 | 957 | 0.2633% | Module |  | DSP Communication Anomay | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.034268 | 5.683 | 4249.8159
2761 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | IS31 | [5 empty] | 1 | 1 | IS31 | 10383.45 | 2.856% | IDT |  | Shutdown by Project team | 6:16 | 6:16 | 6:16 | 19:17 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.37181 | 5.683 | 46110.5025
2762 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS1 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS1Inv1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0034181 | 6.4465 | 482.0728
2763 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS1 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS1Inv1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2764 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS1 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS1Inv1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 6.4465 | 642.7637
2765 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS1 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS1Inv2M2SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2766 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2767 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2768 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 6.4465 | 642.7637
2769 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2770 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2771 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2772 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS3 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS3Inv1M1SCB5 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.007903 | 6.4465 | 1114.6107
2773 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2774 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2775 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2776 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2777 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2778 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2779 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2780 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2781 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2782 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2783 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2784 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2785 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2786 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2787 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2788 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2789 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2790 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2791 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2792 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2793 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2794 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0062664 | 6.4465 | 883.8001
2795 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2796 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2797 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2798 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2799 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 6.4465 | 803.4546
2800 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2801 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 6.4465 | 803.4546
2802 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2803 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2804 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2805 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2806 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS9 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS9Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2807 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS9 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS9Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2808 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2809 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2810 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS9 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS9Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2811 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS12 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS12Inv1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2812 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2813 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS13 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS13Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2814 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2815 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2816 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS14 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS14Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2817 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2818 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS14 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS14Inv1M2SCB6 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0074058 | 6.4465 | 1044.491
2819 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS14 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS14Inv1M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 6.4465 | 642.7637
2820 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2821 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2822 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2823 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2824 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS14 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS14Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2825 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS17 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS17Inv1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2826 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS18 | Inv1 | M3 | SCB2 |  |  | 1 | 1 | IS18Inv1M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2827 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS18 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS18Inv2M3SCB5 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0022787 | 6.4465 | 321.3819
2828 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS19 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS19Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2829 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS19 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2830 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS19 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv1M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2831 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS19 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS19Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2832 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS19 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS19Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2833 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS19 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS19Inv2M1SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0034181 | 6.4465 | 482.0728
2834 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS19 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS19Inv2M3SCB2 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0022787 | 6.4465 | 321.3819
2835 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS19 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS19Inv2M3SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 6.4465 | 803.4546
2836 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS19 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 6.4465 | 642.7637
2837 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS19 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv2M3SCB5 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0011394 | 6.4465 | 160.6909
2838 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 6.4465 | 803.4546
2839 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 6.4465 | 642.7637
2840 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2841 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS21 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS21Inv1M4SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 6.4465 | 642.7637
2842 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 6.4465 | 803.4546
2843 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0039877 | 6.4465 | 562.4182
2844 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0022787 | 6.4465 | 321.3819
2845 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0074058 | 6.4465 | 1044.491
2846 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2847 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2848 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2849 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2850 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2851 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2852 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS29Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2853 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS29Inv1M1SCB6 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0034181 | 6.4465 | 482.0728
2854 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS29INV1M2SCB3 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 6.4465 | 642.7637
2855 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 6.4465 | 803.4546
2856 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 6.4465 | 803.4546
2857 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS29INV1M2SCB6 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0011394 | 6.4465 | 160.6909
2858 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2859 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 6.4465 | 803.4546
2860 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0056968 | 6.4465 | 803.4546
2861 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2862 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0 | 6.4465 | 0
2863 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2864 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2865 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2866 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS29Inv2M1SCB2 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2867 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS29Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2868 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS29Inv2M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2869 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS29Inv2M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2870 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS29Inv2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2871 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS29Inv2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2872 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS29Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2873 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS29Inv2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 6.4465 | 642.7637
2874 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS29Inv2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0034181 | 6.4465 | 482.0728
2875 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS29Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2876 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS29Inv2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0034181 | 6.4465 | 482.0728
2877 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS29Inv2M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0045574 | 6.4465 | 642.7637
2878 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS29Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0079755 | 6.4465 | 1124.8365
2879 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS29 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS29Inv2M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.0068361 | 6.4465 | 964.1456
2880 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS30 | Inv1 | M3 |  |  |  | 1 | 1 | IS30Inv1M3 | 1116.5 | 0.3071% | Module |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.039877 | 6.4465 | 5624.1824
2881 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.045574 | 6.4465 | 6427.6371
2882 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.043295 | 6.4465 | 6106.2552
2883 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.038738 | 6.4465 | 5463.4915
2884 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS33 | Inv1 | M2 |  |  |  | 1 | 1 | IS33Inv1M2 | 1244.1 | 0.3422% | Module |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.044435 | 6.4465 | 6266.9462
2885 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS33 | Inv1 | M3 |  |  |  | 1 | 1 | IS33Inv1M3 | 925.1 | 0.2545% | Module |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.033041 | 6.4465 | 4660.0369
2886 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS33 | Inv1 | M4 |  |  |  | 1 | 1 | IS33Inv1M4 | 1276 | 0.351% | Module |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.045574 | 6.4465 | 6427.6371
2887 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Module |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.041017 | 6.4465 | 5784.8734
2888 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS33 | Inv2 | M2 |  |  |  | 1 | 1 | IS33Inv2M2 | 1116.5 | 0.3071% | Module |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.039877 | 6.4465 | 5624.1824
2889 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS33 | Inv2 | M3 |  |  |  | 1 | 1 | IS33Inv2M3 | 1260.05 | 0.3466% | Module |  | SCB string cable theft | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.045004 | 6.4465 | 6347.2916
2890 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS31 | Inv1 |  |  |  |  | 1 | 1 | IS31Inv1 | 5072.1 | 1.395% | Inverter |  | Inverter Flash Over IDT Trip | 6:27 | 6:27 | 6:27 | 12:10 | 0 | 0 | 5.7167 | 5.7167 | Informed to Project team | Close | 0.079765 | 2.7588 | 10934.3004
2891 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS31 | Inv2 |  |  |  |  | 1 | 1 | IS31Inv2 | 5311.35 | 1.461% | Inverter |  | Inverter Flash Over IDT Trip | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 |  | 12.9833 | Informed to Project team | Open | 0.1897 | 6.4465 | 26755.0393
2892 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS1 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS1Inv1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0034005 | 5.7541 | 430.2963
2893 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS1 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS1Inv1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2894 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS1 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS1Inv1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.004534 | 5.7541 | 573.7285
2895 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS1 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS1Inv2M2SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2896 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2897 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2898 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.004534 | 5.7541 | 573.7285
2899 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2900 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2901 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2902 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS3 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS3Inv1M1SCB5 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0078624 | 5.7541 | 994.8973
2903 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2904 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2905 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2906 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2907 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2908 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2909 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2910 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2911 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2912 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2913 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2914 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2915 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2916 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2917 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2918 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2919 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2920 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2921 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2922 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2923 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2924 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0062343 | 5.7541 | 788.8766
2925 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2926 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2927 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2928 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2929 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0056675 | 5.7541 | 717.1606
2930 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2931 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0056675 | 5.7541 | 717.1606
2932 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2933 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2934 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2935 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2936 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS9 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS9Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2937 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS9 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS9Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2938 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2939 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2940 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS9 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS9Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2941 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS12 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS12Inv1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2942 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2943 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS13 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS13Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2944 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2945 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2946 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS14 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS14Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2947 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2948 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS14 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS14Inv1M2SCB6 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0073678 | 5.7541 | 932.3087
2949 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS14 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS14Inv1M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.004534 | 5.7541 | 573.7285
2950 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2951 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2952 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2953 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2954 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS14 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS14Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2955 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS17 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS17Inv1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2956 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS18 | Inv1 | M3 | SCB2 |  |  | 1 | 1 | IS18Inv1M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2957 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS18 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS18Inv2M3SCB5 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.002267 | 5.7541 | 286.8642
2958 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS19 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS19Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2959 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS19 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2960 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS19 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv1M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2961 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS19 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS19Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2962 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS19 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS19Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2963 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS19 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS19Inv2M1SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0034005 | 5.7541 | 430.2963
2964 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS19 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS19Inv2M3SCB2 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.002267 | 5.7541 | 286.8642
2965 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS19 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS19Inv2M3SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0056675 | 5.7541 | 717.1606
2966 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS19 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.004534 | 5.7541 | 573.7285
2967 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS19 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv2M3SCB5 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0011335 | 5.7541 | 143.4321
2968 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0056675 | 5.7541 | 717.1606
2969 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.004534 | 5.7541 | 573.7285
2970 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2971 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS21 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS21Inv1M4SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.004534 | 5.7541 | 573.7285
2972 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0056675 | 5.7541 | 717.1606
2973 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0039673 | 5.7541 | 502.0124
2974 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.002267 | 5.7541 | 286.8642
2975 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0073678 | 5.7541 | 932.3087
2976 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2977 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2978 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2979 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2980 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2981 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2982 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS29Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2983 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS29Inv1M1SCB6 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0034005 | 5.7541 | 430.2963
2984 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS29INV1M2SCB3 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.004534 | 5.7541 | 573.7285
2985 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0056675 | 5.7541 | 717.1606
2986 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0056675 | 5.7541 | 717.1606
2987 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS29INV1M2SCB6 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0011335 | 5.7541 | 143.4321
2988 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | INV1 | M3 | SCB4 |  |  | 1 | 1 | IS29INV1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2989 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | INV1 | M3 | SCB5 |  |  | 1 | 1 | IS29INV1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0056675 | 5.7541 | 717.1606
2990 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | INV1 | M3 | SCB6 |  |  | 1 | 1 | IS29INV1M3SCB6 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0056675 | 5.7541 | 717.1606
2991 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2992 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0 | 5.7541 | 0
2993 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2994 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2995 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2996 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS29Inv2M1SCB2 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2997 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS29Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
2998 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS29Inv2M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
2999 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS29Inv2M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
3000 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS29Inv2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
3001 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS29Inv2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
3002 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS29Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
3003 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS29Inv2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.004534 | 5.7541 | 573.7285
3004 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS29Inv2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0034005 | 5.7541 | 430.2963
3005 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS29Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
3006 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS29Inv2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0034005 | 5.7541 | 430.2963
3007 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS29Inv2M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.004534 | 5.7541 | 573.7285
3008 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS29Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.0079345 | 5.7541 | 1004.0248
3009 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS29 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS29Inv2M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.006801 | 5.7541 | 860.5927
3010 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS31 | Inv2 |  |  |  |  | 1 | 1 | IS31Inv2 | 5311.35 | 1.461% | Inverter |  | Inverter Flash Over | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.18873 | 5.7541 | 23881.4468
3011 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS30 | Inv1 | M3 |  |  |  | 1 | 1 | IS30Inv1M3 | 1116.5 | 0.3071% | Module |  | DSP Communication Anomaly (SPD FAULTY) | 6:20 | 6:20 | 6:20 | 16:35 | 0 | 0 | 10.25 | 10.25 | Inverter Check and Reboot | Close | 0.031482 | 5.2577 | 4587.0588
3012 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | SCB string cable theft | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.04534 | 5.7541 | 5737.2845
3013 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | SCB string cable theft | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.043073 | 5.7541 | 5450.4203
3014 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | SCB string cable theft | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.038539 | 5.7541 | 4876.6918
3015 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS33 | Inv1 | M2 |  |  |  | 1 | 1 | IS33Inv1M2 | 1244.1 | 0.3422% | Module |  | SCB string cable theft | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.044207 | 5.7541 | 5593.8524
3016 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS33 | Inv1 | M3 |  |  |  | 1 | 1 | IS33Inv1M3 | 925.1 | 0.2545% | Module |  | SCB string cable theft | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.032872 | 5.7541 | 4159.5313
3017 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS33 | Inv1 | M4 |  |  |  | 1 | 1 | IS33Inv1M4 | 1276 | 0.351% | Module |  | SCB string cable theft | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.04534 | 5.7541 | 5737.2845
3018 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS33 | Inv2 | M1 |  |  |  | 1 | 1 | IS33Inv2M1 | 1148.4 | 0.3159% | Module |  | SCB string cable theft | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.040806 | 5.7541 | 5163.5561
3019 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS33 | Inv2 | M2 |  |  |  | 1 | 1 | IS33Inv2M2 | 1116.5 | 0.3071% | Module |  | SCB string cable theft | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.039673 | 5.7541 | 5020.1239
3020 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | IS33 | Inv2 | M3 |  |  |  | 1 | 1 | IS33Inv2M3 | 1260.05 | 0.3466% | Module |  | SCB string cable theft | 6:20 | 6:20 | 6:20 | 19:15 | 0 | 0 |  | 12.9167 | Informed to Project team | Open | 0.044773 | 5.7541 | 5665.5684
3021 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS1 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS1Inv1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0032382 | 5.6236 | 420.5377
3022 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS1 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS1Inv1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3023 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS1 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS1Inv1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0043175 | 5.6236 | 560.7169
3024 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS1 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS1Inv2M2SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3025 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3026 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3027 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0043175 | 5.6236 | 560.7169
3028 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3029 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3030 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3031 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS3 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS3Inv1M1SCB5 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.007487 | 5.6236 | 972.334
3032 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3033 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3034 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3035 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3036 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3037 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3038 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3039 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3040 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3041 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3042 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3043 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3044 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3045 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3046 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3047 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3048 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3049 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3050 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3051 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3052 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3053 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0059366 | 5.6236 | 770.9857
3054 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3055 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3056 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3057 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3058 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0053969 | 5.6236 | 700.8961
3059 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3060 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0053969 | 5.6236 | 700.8961
3061 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3062 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3063 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3064 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3065 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS9 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS9Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3066 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS9 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS9Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3067 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3068 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3069 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS9 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS9Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3070 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS12 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS12Inv1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3071 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3072 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS13 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS13Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3073 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3074 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3075 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS14 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS14Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3076 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3077 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS14 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS14Inv1M2SCB6 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.007016 | 5.6236 | 911.1649
3078 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS14 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS14Inv1M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0043175 | 5.6236 | 560.7169
3079 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3080 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3081 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3082 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3083 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS14 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS14Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3084 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS17 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS17Inv1M4SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3085 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS18 | Inv1 | M3 | SCB2 |  |  | 1 | 1 | IS18Inv1M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3086 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS18 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS18Inv2M3SCB5 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0021588 | 5.6236 | 280.3584
3087 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS19 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS19Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3088 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS19 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3089 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS19 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv1M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3090 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS19 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS19Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3091 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS19 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS19Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3092 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS19 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS19Inv2M1SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0032382 | 5.6236 | 420.5377
3093 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS19 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS19Inv2M3SCB2 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0021588 | 5.6236 | 280.3584
3094 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS19 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS19Inv2M3SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0053969 | 5.6236 | 700.8961
3095 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS19 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0043175 | 5.6236 | 560.7169
3096 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS19 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv2M3SCB5 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0010794 | 5.6236 | 140.1792
3097 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0053969 | 5.6236 | 700.8961
3098 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0043175 | 5.6236 | 560.7169
3099 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3100 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS21 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS21Inv1M4SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0043175 | 5.6236 | 560.7169
3101 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0053969 | 5.6236 | 700.8961
3102 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0037779 | 5.6236 | 490.6273
3103 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0021588 | 5.6236 | 280.3584
3104 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.007016 | 5.6236 | 911.1649
3105 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3106 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3107 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3108 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3109 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3110 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3111 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS29INV1M2SCB3 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0043175 | 5.6236 | 560.7169
3112 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0053969 | 5.6236 | 700.8961
3113 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0053969 | 5.6236 | 700.8961
3114 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS29INV1M2SCB6 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0010794 | 5.6236 | 140.1792
3115 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3116 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3117 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3118 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3119 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3120 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS29Inv2M1SCB2 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3121 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS29Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3122 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS29Inv2M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3123 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS29Inv2M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3124 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS29Inv2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3125 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS29Inv2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3126 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS29Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3127 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS29Inv2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0043175 | 5.6236 | 560.7169
3128 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS29Inv2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0032382 | 5.6236 | 420.5377
3129 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS29Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3130 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS29Inv2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0032382 | 5.6236 | 420.5377
3131 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS29Inv2M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0043175 | 5.6236 | 560.7169
3132 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS29Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3133 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS29Inv2M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3134 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv1 | M1 |  |  |  | 1 | 1 | IS29Inv1M1 | 988.9 | 0.272% | Module |  | Isolation Protection | 6:49 | 6:49 | 6:49 | 8:54 | 0 | 0 | 2.0833 | 2.0833 | Inverter Check and Reboot | Close | 0.0056675 | 0.24171 | 186.7755
3135 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS29 | Inv1 | M3 |  |  |  | 1 | 1 | IS29Inv1M3 | 861.3 | 0.2369% | Module |  | Isolation Protection | 6:49 | 6:49 | 6:49 | 8:54 | 0 | 0 | 2.0833 | 2.0833 | Inverter Check and Reboot | Close | 0.0049362 | 0.24171 | 162.6755
3136 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS16 | Inv1 | M1 |  |  |  | 1 | 1 | IS16Inv1M1 | 1276 | 0.351% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.043175 | 5.6236 | 5607.1688
3137 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS16 | Inv1 | M3 |  |  |  | 1 | 1 | IS16Inv1M3 | 1307.9 | 0.3598% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.044255 | 5.6236 | 5747.348
3138 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS16 | Inv1 | M4 |  |  |  | 1 | 1 | IS16Inv1M4 | 1180.3 | 0.3247% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.039937 | 5.6236 | 5186.6311
3139 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS20 | Inv1 | M1 |  |  |  | 1 | 1 | IS20Inv1M1 | 1291.95 | 0.3554% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 15:26 | 0 | 0 | 8.6167 | 8.6167 | Inverter Check and Reboot | Close | 0.030624 | 4.6768 | 4721.4725
3140 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS20 | Inv1 | M2 |  |  |  | 1 | 1 | IS20Inv1M2 | 1164.35 | 0.3203% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.039398 | 5.6236 | 5116.5415
3141 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS20 | Inv1 | M3 |  |  |  | 1 | 1 | IS20Inv1M3 | 1276 | 0.351% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.043175 | 5.6236 | 5607.1688
3142 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS20 | Inv2 | M2 |  |  |  | 1 | 1 | IS20Inv2M2 | 350.9 | 0.09653% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 15:35 | 0 | 0 | 8.7667 | 8.7667 | Inverter Check and Reboot | Close | 0.0084625 | 4.7594 | 1305.0028
3143 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS20 | Inv2 | M3 |  |  |  | 1 | 1 | IS20Inv2M3 | 1212.2 | 0.3335% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 15:35 | 0 | 0 | 8.7667 | 8.7667 | Inverter Check and Reboot | Close | 0.029234 | 4.7594 | 4508.1914
3144 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS27 | Inv2 | M2 |  |  |  | 1 | 1 | IS27Inv2M2 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3145 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS27 | Inv2 | M3 |  |  |  | 1 | 1 | IS27Inv2M3 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3146 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | SCB string cable theft | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.043175 | 5.6236 | 5607.1688
3147 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | SCB string cable theft | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.041017 | 5.6236 | 5326.8104
3148 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | SCB string cable theft | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.036699 | 5.6236 | 4766.0935
3149 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS31 | Inv2 |  |  |  |  | 1 | 1 | IS31Inv2 | 5311.35 | 1.461% | Inverter |  | Inverter Flash over | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.17972 | 5.6236 | 23339.8401
3150 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS33 | [5 empty] | 1 | 1 | IS33 | 9107.45 | 2.505% | IDT |  | SCB string cable theft | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.30816 | 5.6236 | 40021.1673
3151 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS34 | Inv1 | M2 |  |  |  | 1 | 1 | IS34Inv1M2 | 893.2 | 0.2457% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.030223 | 5.6236 | 3925.0182
3152 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS34 | Inv1 | M3 |  |  |  | 1 | 1 | IS34Inv1M3 | 1180.3 | 0.3247% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.039937 | 5.6236 | 5186.6311
3153 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS34 | Inv1 | M4 |  |  |  | 1 | 1 | IS34Inv1M4 | 1180.3 | 0.3247% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.039937 | 5.6236 | 5186.6311
3154 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS34 | Inv2 | M1 |  |  |  | 1 | 1 | IS34Inv2M1 | 1307.9 | 0.3598% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 15:50 | 0 | 0 | 9.0167 | 9.0167 | Inverter Check and Reboot | Close | 0.032442 | 4.877 | 4984.3105
3155 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS36 | Inv1 | M4 |  |  |  | 1 | 1 | IS36Inv1M4 | 893.2 | 0.2457% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.030223 | 5.6236 | 3925.0182
3156 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS38 | Inv1 | M1 |  |  |  | 1 | 1 | IS38Inv1M1 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3157 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS38 | Inv1 | M2 |  |  |  | 1 | 1 | IS38Inv1M2 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3158 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS38 | Inv1 | M3 |  |  |  | 1 | 1 | IS38Inv1M3 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3159 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS38 | Inv2 | M1 |  |  |  | 1 | 1 | IS38Inv2M1 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3160 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS38 | Inv2 | M2 |  |  |  | 1 | 1 | IS38Inv2M2 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3161 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS38 | Inv2 | M4 |  |  |  | 1 | 1 | IS38Inv2M4 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3162 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS39 | Inv1 | M4 |  |  |  | 1 | 1 | IS39Inv1M4 | 191.4 | 0.05265% | Module |  | Initial Shutdown | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0064763 | 5.6236 | 841.0753
3163 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS39 | Inv2 |  |  |  |  | 1 | 1 | IS39Inv2 | 223.3 | 0.06143% | Inverter |  | IO-DSP COMMINUCATION ANOMALY | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.0075557 | 5.6236 | 981.2545
3164 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS43 | Inv1 | M3 |  |  |  | 1 | 1 | IS43Inv1M3 | 1276 | 0.351% | Module |  | Emergency Stop | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.043175 | 5.6236 | 5607.1688
3165 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS43 | Inv2 | M2 |  |  |  | 1 | 1 | IS43Inv2M2 | 1276 | 0.351% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.043175 | 5.6236 | 5607.1688
3166 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS43 | Inv2 | M3 |  |  |  | 1 | 1 | IS43Inv2M3 | 1244.1 | 0.3422% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.042096 | 5.6236 | 5466.9896
3167 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS43 | Inv2 | M4 |  |  |  | 1 | 1 | IS43Inv2M4 | 957 | 0.2633% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.032382 | 5.6236 | 4205.3766
3168 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS47 | Inv1 | M2 |  |  |  | 1 | 1 | IS47Inv1M2 | 1068.65 | 0.294% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.036159 | 5.6236 | 4696.0039
3169 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS52 | Inv2 | M2 |  |  |  | 1 | 1 | IS52Inv2M2 | 893.2 | 0.2457% | Module |  | Emergency Stop | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0.030223 | 5.6236 | 3925.0182
3170 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS11 | Inv1 | M3 |  |  |  | 1 | 1 | IS11Inv1M3 | 0 | 0% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3171 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | IS11 | Inv1 | M4 |  |  |  | 1 | 1 | IS11Inv1M4 | 0 | 0% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:49 | 6:49 | 6:49 | 19:07 | 0 | 0 |  | 12.3 | Informed to Project team | Open | 0 | 5.6236 | 0
3172 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS1 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS1Inv1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0034049 | 4.5982 | 343.8553
3173 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS1 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS1Inv1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3174 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS1 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS1Inv1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0045399 | 4.5982 | 458.4737
3175 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS1 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS1Inv2M2SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3176 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3177 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3178 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0045399 | 4.5982 | 458.4737
3179 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3180 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3181 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3182 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS3 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS3Inv1M1SCB5 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0078725 | 4.5982 | 795.0351
3183 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3184 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3185 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3186 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3187 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3188 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3189 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3190 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3191 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3192 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3193 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3194 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3195 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3196 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3197 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3198 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3199 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3200 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3201 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3202 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3203 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3204 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0062423 | 4.5982 | 630.4014
3205 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3206 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3207 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3208 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3209 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0056748 | 4.5982 | 573.0922
3210 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3211 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0056748 | 4.5982 | 573.0922
3212 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3213 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3214 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3215 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3216 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS9 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS9Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3217 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS9 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS9Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3218 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3219 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3220 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS9 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS9Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3221 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS12 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS12Inv1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3222 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3223 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS13 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS13Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3224 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3225 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3226 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS14 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS14Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3227 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3228 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS14 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS14Inv1M2SCB6 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0073773 | 4.5982 | 745.0198
3229 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS14 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS14Inv1M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0045399 | 4.5982 | 458.4737
3230 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3231 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3232 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3233 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3234 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS14 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS14Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3235 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS18 | Inv1 | M3 | SCB2 |  |  | 1 | 1 | IS18Inv1M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3236 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS18 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS18Inv2M3SCB5 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0022699 | 4.5982 | 229.2369
3237 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS19 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS19Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3238 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS19 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3239 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS19 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv1M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3240 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS19 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS19Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3241 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS19 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS19Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3242 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS19 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS19Inv2M1SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0034049 | 4.5982 | 343.8553
3243 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS19 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS19Inv2M3SCB2 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0022699 | 4.5982 | 229.2369
3244 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS19 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS19Inv2M3SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0056748 | 4.5982 | 573.0922
3245 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS19 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0045399 | 4.5982 | 458.4737
3246 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS19 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv2M3SCB5 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.001135 | 4.5982 | 114.6184
3247 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0056748 | 4.5982 | 573.0922
3248 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0045399 | 4.5982 | 458.4737
3249 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3250 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS21 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS21Inv1M4SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0045399 | 4.5982 | 458.4737
3251 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0056748 | 4.5982 | 573.0922
3252 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0039724 | 4.5982 | 401.1645
3253 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0022699 | 4.5982 | 229.2369
3254 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0073773 | 4.5982 | 745.0198
3255 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3256 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3257 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3258 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3259 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3260 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3261 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS29INV1M2SCB3 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0045399 | 4.5982 | 458.4737
3262 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0056748 | 4.5982 | 573.0922
3263 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0056748 | 4.5982 | 573.0922
3264 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS29INV1M2SCB6 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.001135 | 4.5982 | 114.6184
3265 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3266 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3267 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3268 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3269 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3270 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS29Inv2M1SCB2 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3271 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS29Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3272 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS29Inv2M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3273 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS29Inv2M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3274 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS29Inv2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3275 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS29Inv2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3276 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS29Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3277 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS29Inv2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0045399 | 4.5982 | 458.4737
3278 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS29Inv2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0034049 | 4.5982 | 343.8553
3279 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS29Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3280 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS29Inv2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0034049 | 4.5982 | 343.8553
3281 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS29Inv2M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0045399 | 4.5982 | 458.4737
3282 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS29Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3283 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS29 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS29Inv2M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3284 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS16 | Inv1 | M1 |  |  |  | 1 | 1 | IS16Inv1M1 | 1276 | 0.351% | Module |  | PROJECT WORK PENDING | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.045399 | 4.5982 | 4584.7372
3285 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS16 | Inv1 | M3 |  |  |  | 1 | 1 | IS16Inv1M3 | 1307.9 | 0.3598% | Module |  | PROJECT WORK PENDING | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.046534 | 4.5982 | 4699.3556
3286 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS16 | Inv1 | M4 |  |  |  | 1 | 1 | IS16Inv1M4 | 1180.3 | 0.3247% | Module |  | PROJECT WORK PENDING | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.041994 | 4.5982 | 4240.8819
3287 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS20 | Inv1 | M2 |  |  |  | 1 | 1 | IS20Inv1M2 | 1164.35 | 0.3203% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 9:00 | 0 | 0 | 2.6 | 2.6 | Inverter Check and Reboot | Close | 0.008328 | 0.28497 | 259.2756
3288 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS20 | Inv1 | M3 |  |  |  | 1 | 1 | IS20Inv1M3 | 1276 | 0.351% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 9:00 | 0 | 0 | 2.6 | 2.6 | Inverter Check and Reboot | Close | 0.0091265 | 0.28497 | 284.1377
3289 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS27 | Inv2 | M2 |  |  |  | 1 | 1 | IS27Inv2M2 | 0 | 0% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3290 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS27 | Inv2 | M3 |  |  |  | 1 | 1 | IS27Inv2M3 | 0 | 0% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3291 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | SCB string cable theft | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.045399 | 4.5982 | 4584.7372
3292 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | SCB string cable theft | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.043129 | 4.5982 | 4355.5003
3293 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | SCB string cable theft | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.038589 | 4.5982 | 3897.0266
3294 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS31 | Inv2 |  |  |  |  | 1 | 1 | IS31Inv2 | 5311.35 | 1.461% | Inverter |  | Inverter Flash over | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.18897 | 4.5982 | 19083.9686
3295 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS33 | [5 empty] | 1 | 1 | IS33 | 9107.45 | 2.505% | IDT |  | SCB string cable theft | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.32403 | 4.5982 | 32723.5618
3296 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS34 | Inv1 | M2 |  |  |  | 1 | 1 | IS34Inv1M2 | 893.2 | 0.2457% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.031779 | 4.5982 | 3209.316
3297 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS34 | Inv1 | M3 |  |  |  | 1 | 1 | IS34Inv1M3 | 1180.3 | 0.3247% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.041994 | 4.5982 | 4240.8819
3298 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS34 | Inv1 | M4 |  |  |  | 1 | 1 | IS34Inv1M4 | 1180.3 | 0.3247% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.041994 | 4.5982 | 4240.8819
3299 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS34 | Inv2 | M1 |  |  |  | 1 | 1 | IS34Inv2M1 | 1307.9 | 0.3598% | Module |  | SHUT DOWN EMERGENCY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.046534 | 4.5982 | 4699.3556
3300 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS36 | Inv1 | M4 |  |  |  | 1 | 1 | IS36Inv1M4 | 893.2 | 0.2457% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.031779 | 4.5982 | 3209.316
3301 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS38 | Inv1 | M1 |  |  |  | 1 | 1 | IS38Inv1M1 | 0 | 0% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3302 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS38 | Inv1 | M2 |  |  |  | 1 | 1 | IS38Inv1M2 | 0 | 0% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3303 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS38 | Inv1 | M3 |  |  |  | 1 | 1 | IS38Inv1M3 | 0 | 0% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3304 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS38 | Inv2 | M1 |  |  |  | 1 | 1 | IS38Inv2M1 | 0 | 0% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3305 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS38 | Inv2 | M2 |  |  |  | 1 | 1 | IS38Inv2M2 | 0 | 0% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3306 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS38 | Inv2 | M4 |  |  |  | 1 | 1 | IS38Inv2M4 | 0 | 0% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0 | 4.5982 | 0
3307 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS39 | Inv1 | M4 |  |  |  | 1 | 1 | IS39Inv1M4 | 191.4 | 0.05265% | Module |  | INITIAL STAND BY (DC WORK PRNDING) | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0068098 | 4.5982 | 687.7106
3308 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS39 | Inv2 |  |  |  |  | 1 | 1 | IS39Inv2 | 223.3 | 0.06143% | Inverter |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.0079448 | 4.5982 | 802.329
3309 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS43 | Inv1 | M3 |  |  |  | 1 | 1 | IS43Inv1M3 | 1276 | 0.351% | Module |  | Emergency Stop(PROJECT WORK) | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.045399 | 4.5982 | 4584.7372
3310 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS43 | Inv2 | M2 |  |  |  | 1 | 1 | IS43Inv2M2 | 1276 | 0.351% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.045399 | 4.5982 | 4584.7372
3311 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS43 | Inv2 | M3 |  |  |  | 1 | 1 | IS43Inv2M3 | 1244.1 | 0.3422% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.044264 | 4.5982 | 4470.1188
3312 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS43 | Inv2 | M4 |  |  |  | 1 | 1 | IS43Inv2M4 | 957 | 0.2633% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.034049 | 4.5982 | 3438.5529
3313 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS47 | Inv1 | M2 |  |  |  | 1 | 1 | IS47Inv1M2 | 1068.65 | 0.294% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 11:40 | 0 | 0 | 5.2667 | 5.2667 | Inverter Check and Reboot | Close | 0.015483 | 1.7638 | 1472.8816
3314 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS52 | Inv2 | M2 |  |  |  | 1 | 1 | IS52Inv2M2 | 893.2 | 0.2457% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:24 | 6:24 | 6:24 | 19:20 | 0 | 0 |  | 12.9333 | Informed to Project team | Open | 0.031779 | 4.5982 | 3209.316
3315 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | IS17 | Inv1 | M4 |  |  |  | 1 | 1 | IS17Inv1M4 | 0 | 0% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:24 | 6:24 | 6:24 | 8:44 | 0 | 0 | 2.3333 | 2.3333 | Inverter Check and Reboot | Close | 0 | 0.19983 | 0
3316 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS1 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS1Inv1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.003361 | 5.391 | 403.1446
3317 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS1 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS1Inv1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.006722 | 5.391 | 806.2891
3318 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS1 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS1Inv1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.0044814 | 5.391 | 537.5261
3319 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS1 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS1Inv2M2SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.006722 | 5.391 | 806.2891
3320 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0 | 5.391 | 0
3321 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0 | 5.391 | 0
3322 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.0044814 | 5.391 | 537.5261
3323 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0 | 5.391 | 0
3324 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0 | 5.391 | 0
3325 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0 | 5.391 | 0
3326 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS11 | Inv1 | M3 |  |  |  | 1 | 1 | IS11Inv1M3 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0 | 5.391 | 0
3327 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS11 | Inv1 | M4 |  |  |  | 1 | 1 | IS11Inv1M4 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0 | 5.391 | 0
3328 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS16 | Inv1 | M1 |  |  |  | 1 | 1 | IS16Inv1M1 | 1276 | 0.351% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.044814 | 5.391 | 5375.2609
3329 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS16 | Inv1 | M3 |  |  |  | 1 | 1 | IS16Inv1M3 | 1307.9 | 0.3598% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.045934 | 5.391 | 5509.6424
3330 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS16 | Inv1 | M4 |  |  |  | 1 | 1 | IS16Inv1M4 | 1180.3 | 0.3247% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.041453 | 5.391 | 4972.1164
3331 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS27 | Inv2 | M2 |  |  |  | 1 | 1 | IS27Inv2M2 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0 | 5.391 | 0
3332 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS27 | Inv2 | M3 |  |  |  | 1 | 1 | IS27Inv2M3 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0 | 5.391 | 0
3333 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.044814 | 5.391 | 5375.2609
3334 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.042573 | 5.391 | 5106.4979
3335 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.038092 | 5.391 | 4568.9718
3336 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS31 | Inv2 |  |  |  |  | 1 | 1 | IS31Inv2 | 5311.35 | 1.461% | Inverter |  | Inverter flash over | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.18654 | 5.391 | 22374.5236
3337 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS33 | [5 empty] | 1 | 1 | IS33 | 9107.45 | 2.505% | Inverter |  | SCB string cable theft | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.31986 | 5.391 | 38365.9248
3338 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS34 | Inv1 | M2 |  |  |  | 1 | 1 | IS34Inv1M2 | 893.2 | 0.2457% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.031369 | 5.391 | 3762.6826
3339 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS34 | Inv1 | M3 |  |  |  | 1 | 1 | IS34Inv1M3 | 1180.3 | 0.3247% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.041453 | 5.391 | 4972.1164
3340 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS34 | Inv1 | M4 |  |  |  | 1 | 1 | IS34Inv1M4 | 1180.3 | 0.3247% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.041453 | 5.391 | 4972.1164
3341 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS36 | Inv1 | M4 |  |  |  | 1 | 1 | IS36Inv1M4 | 893.2 | 0.2457% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.031369 | 5.391 | 3762.6826
3342 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS38 | Inv1 | M1 |  |  |  | 1 | 1 | IS38Inv1M1 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0 | 5.391 | 0
3343 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS38 | Inv1 | M2 |  |  |  | 1 | 1 | IS38Inv1M2 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0 | 5.391 | 0
3344 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS38 | Inv1 | M3 |  |  |  | 1 | 1 | IS38Inv1M3 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0 | 5.391 | 0
3345 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS38 | Inv2 | M1 |  |  |  | 1 | 1 | IS38Inv2M1 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0 | 5.391 | 0
3346 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS38 | Inv2 | M2 |  |  |  | 1 | 1 | IS38Inv2M2 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0 | 5.391 | 0
3347 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS38 | Inv2 | M4 |  |  |  | 1 | 1 | IS38Inv2M4 | 0 | 0% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0 | 5.391 | 0
3348 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS39 | Inv1 | M4 |  |  |  | 1 | 1 | IS39Inv1M4 | 191.4 | 0.05265% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.006722 | 5.391 | 806.2891
3349 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS39 | Inv2 |  |  |  |  | 1 | 1 | IS39Inv2 | 223.3 | 0.06143% | Inverter |  | Project Activities SCB Shutdowen taken by Project Team | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.0078424 | 5.391 | 940.6707
3350 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS43 | Inv1 | M3 |  |  |  | 1 | 1 | IS43Inv1M3 | 1276 | 0.351% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.044814 | 5.391 | 5375.2609
3351 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS43 | Inv2 | M2 |  |  |  | 1 | 1 | IS43Inv2M2 | 1276 | 0.351% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.044814 | 5.391 | 5375.2609
3352 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS43 | Inv2 | M3 |  |  |  | 1 | 1 | IS43Inv2M3 | 1244.1 | 0.3422% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.043693 | 5.391 | 5240.8794
3353 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS43 | Inv2 | M4 |  |  |  | 1 | 1 | IS43Inv2M4 | 957 | 0.2633% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.03361 | 5.391 | 4031.4457
3354 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS52 | Inv2 | M2 |  |  |  | 1 | 1 | IS52Inv2M2 | 893.2 | 0.2457% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 |  | 12.7667 | Informed to Project team | Open | 0.031369 | 5.391 | 3762.6826
3355 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5024.25 | 1.382% | Inverter |  | Inverter triped in GFDI Fault | 10:53 | 10:53 | 10:53 | 16:50 | 0 | 0 | 5.95 | 5.95 | Reboot and restart inverter | Close | 0.082237 | 3.5106 | 13782.7255
3356 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS4 | [5 empty] | 1 | 1 | IS4 | 9522.15 | 2.619% | Inverter |  | Inverter triped in GFDI Fault | 16:54 | 16:54 | 16:54 | 17:09 | 0 | 0 | 0.25 | 0.25 | Reboot and restart inverter | Close | 0.0065487 | 0.10016 | 745.2562
3357 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | IS34 | Inv2 |  |  |  |  | 1 | 1 | IS34Inv2 | 5104 | 1.404% | Inverter |  | Standby Field Side SCB off | 6:26 | 6:26 | 6:26 | 19:12 | 0 | 0 | 12.7667 | 12.7667 | Reboot and restart inverter | Close | 0.17925 | 5.391 | 21501.0437
3358 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS1 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS1Inv1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0033961 | 5.5394 | 414.2448
3359 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS1 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS1Inv1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3360 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS1 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS1Inv1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0045282 | 5.5394 | 552.3264
3361 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS1 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS1Inv2M2SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3362 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3363 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3364 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0045282 | 5.5394 | 552.3264
3365 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3366 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3367 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3368 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS3 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS3Inv1M1SCB5 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0078522 | 5.5394 | 957.7842
3369 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3370 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3371 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3372 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3373 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3374 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3375 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3376 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3377 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3378 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3379 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3380 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3381 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3382 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3383 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3384 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3385 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3386 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3387 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3388 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3389 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3390 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0062262 | 5.5394 | 759.4488
3391 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3392 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3393 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3394 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3395 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0056602 | 5.5394 | 690.408
3396 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3397 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0056602 | 5.5394 | 690.408
3398 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3399 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3400 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3401 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3402 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS9 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS9Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3403 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS9 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS9Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3404 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3405 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3406 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS9 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS9Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3407 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS12 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS12Inv1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3408 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3409 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS13 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS13Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3410 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3411 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3412 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS14 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS14Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3413 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3414 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS14 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS14Inv1M2SCB6 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0073583 | 5.5394 | 897.5304
3415 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS14 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS14Inv1M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0045282 | 5.5394 | 552.3264
3416 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3417 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3418 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3419 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3420 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS14 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS14Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3421 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS18 | Inv1 | M3 | SCB2 |  |  | 1 | 1 | IS18Inv1M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3422 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS18 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS18Inv2M3SCB5 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0022641 | 5.5394 | 276.1632
3423 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS19 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS19Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3424 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS19 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3425 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS19 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv1M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3426 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS19 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS19Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3427 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS19 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS19Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3428 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS19 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS19Inv2M1SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0033961 | 5.5394 | 414.2448
3429 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS19 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS19Inv2M3SCB2 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0022641 | 5.5394 | 276.1632
3430 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS19 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS19Inv2M3SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0056602 | 5.5394 | 690.408
3431 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS19 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0045282 | 5.5394 | 552.3264
3432 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS19 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv2M3SCB5 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.001132 | 5.5394 | 138.0816
3433 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0056602 | 5.5394 | 690.408
3434 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0045282 | 5.5394 | 552.3264
3435 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3436 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS21 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS21Inv1M4SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0045282 | 5.5394 | 552.3264
3437 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0056602 | 5.5394 | 690.408
3438 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0039621 | 5.5394 | 483.2856
3439 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0022641 | 5.5394 | 276.1632
3440 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0073583 | 5.5394 | 897.5304
3441 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3442 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3443 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3444 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3445 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3446 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3447 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS29INV1M2SCB3 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0045282 | 5.5394 | 552.3264
3448 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0056602 | 5.5394 | 690.408
3449 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0056602 | 5.5394 | 690.408
3450 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS29INV1M2SCB6 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.001132 | 5.5394 | 138.0816
3451 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3452 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0 | 5.5394 | 0
3453 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3454 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3455 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3456 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS29Inv2M1SCB2 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3457 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS29Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3458 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS29Inv2M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3459 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS29Inv2M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3460 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS29Inv2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3461 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS29Inv2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3462 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS29Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3463 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS29Inv2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0045282 | 5.5394 | 552.3264
3464 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS29Inv2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0033961 | 5.5394 | 414.2448
3465 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS29Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3466 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS29Inv2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0033961 | 5.5394 | 414.2448
3467 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS29Inv2M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0045282 | 5.5394 | 552.3264
3468 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS29Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3469 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS29 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS29Inv2M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3470 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | SCB string cable theft | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.045282 | 5.5394 | 5523.2639
3471 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | SCB string cable theft | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.043018 | 5.5394 | 5247.1007
3472 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | SCB string cable theft | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.038489 | 5.5394 | 4694.7743
3473 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS31 | Inv2 |  |  |  |  | 1 | 1 | IS31Inv2 | 5311.35 | 1.461% | Inverter |  | Inverter Flash over | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.18848 | 5.5394 | 22990.586
3474 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS33 | [5 empty] | 1 | 1 | IS33 | 9107.45 | 2.505% | IDT |  | SCB string cable theft | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.3232 | 5.5394 | 39422.2961
3475 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS36 | Inv1 | M4 |  |  |  | 1 | 1 | IS36Inv1M4 | 893.2 | 0.2457% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:19 | 6:19 | 6:19 | 11:05 | 0 | 0 | 4.7667 | 4.7667 | Inverter Check and Reboot | Close | 0.011712 | 1.4409 | 1005.6938
3476 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS39 | Inv1 | M4 |  |  |  | 1 | 1 | IS39Inv1M4 | 191.4 | 0.05265% | Module |  | INITIAL STAND BY (DC WORK PRNDING) | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0067922 | 5.5394 | 828.4896
3477 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS39 | Inv2 |  |  |  |  | 1 | 1 | IS39Inv2 | 223.3 | 0.06143% | Inverter |  | IO-DSP COMMINUCATION ANOMALY | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.0079243 | 5.5394 | 966.5712
3478 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS16 | Inv1 | M1 |  |  |  | 1 | 1 | IS16Inv1M1 | 1276 | 0.351% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:19 | 6:19 | 6:19 | 19:13 | 0 | 0 |  | 12.9 | Informed to Project team | Open | 0.045282 | 5.5394 | 5523.2639
3479 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS51 | [5 empty] | 1 | 1 | IS51 | 8944.76 | 2.461% | IDT | Shutdown taken by project team | Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 9:05 | 0 | 0 | 2.7667 | 2.7667 | Shutdown clear after discussion with project team | Close | 0.068078 | 0.46825 | 3272.8707
3480 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | IS32 | Inv2 | M1 |  |  |  | 1 | 1 | IS32Inv2M1 | 1563.1 | 0.43% | Module |  | GFDI | 10:48 | 10:48 | 10:48 | 12:51 | 0 | 0 | 2.05 | 2.05 | Inverter Check and Reboot | Close | 0.008815 | 1.4464 | 1766.6349
3481 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS1 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS1Inv1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0033391 | 5.9947 | 448.2928
3482 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS1 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS1Inv1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3483 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS1 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS1Inv1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0044521 | 5.9947 | 597.7238
3484 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS1 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS1Inv2M2SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3485 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3486 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3487 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0044521 | 5.9947 | 597.7238
3488 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3489 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3490 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3491 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS3 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS3Inv1M1SCB5 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077204 | 5.9947 | 1036.5074
3492 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3493 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3494 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3495 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3496 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3497 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3498 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3499 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3500 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3501 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3502 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS6 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS6Inv1M1SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3503 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS6 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS6Inv1M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3504 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS6 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS6Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3505 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS6 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS6Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3506 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS6 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS6Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3507 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS6 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS6Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3508 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS6 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS6Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3509 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS6 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS6Inv1M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3510 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3511 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3512 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3513 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0061216 | 5.9947 | 821.8702
3514 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3515 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3516 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3517 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3518 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0055651 | 5.9947 | 747.1547
3519 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3520 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0055651 | 5.9947 | 747.1547
3521 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3522 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3523 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3524 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3525 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS9 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS9Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3526 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS9 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS9Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3527 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3528 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3529 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS9 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS9Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3530 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS12 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS12Inv1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3531 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3532 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS13 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS13Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3533 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3534 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3535 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS14 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS14Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3536 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3537 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS14 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS14Inv1M2SCB6 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0072347 | 5.9947 | 971.3012
3538 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS14 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS14Inv1M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0044521 | 5.9947 | 597.7238
3539 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3540 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3541 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3542 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3543 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS14 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS14Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3544 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS18 | Inv1 | M3 | SCB2 |  |  | 1 | 1 | IS18Inv1M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3545 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS18 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS18Inv2M3SCB5 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0022261 | 5.9947 | 298.8619
3546 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS19 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS19Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3547 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS19 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3548 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS19 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv1M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3549 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS19 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS19Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3550 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS19 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS19Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3551 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS19 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS19Inv2M1SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0033391 | 5.9947 | 448.2928
3552 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS19 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS19Inv2M3SCB2 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0022261 | 5.9947 | 298.8619
3553 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS19 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS19Inv2M3SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0055651 | 5.9947 | 747.1547
3554 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS19 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0044521 | 5.9947 | 597.7238
3555 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS19 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv2M3SCB5 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.001113 | 5.9947 | 149.4309
3556 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0055651 | 5.9947 | 747.1547
3557 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0044521 | 5.9947 | 597.7238
3558 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3559 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS21 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS21Inv1M4SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0044521 | 5.9947 | 597.7238
3560 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0055651 | 5.9947 | 747.1547
3561 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0038956 | 5.9947 | 523.0083
3562 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0022261 | 5.9947 | 298.8619
3563 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0072347 | 5.9947 | 971.3012
3564 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3565 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3566 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3567 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3568 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3569 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3570 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS29INV1M2SCB3 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0044521 | 5.9947 | 597.7238
3571 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0055651 | 5.9947 | 747.1547
3572 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0055651 | 5.9947 | 747.1547
3573 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS29INV1M2SCB6 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.001113 | 5.9947 | 149.4309
3574 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3575 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0 | 5.9947 | 0
3576 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3577 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3578 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3579 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS29Inv2M1SCB2 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3580 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS29Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3581 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS29Inv2M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3582 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS29Inv2M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3583 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS29Inv2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3584 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS29Inv2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3585 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS29Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3586 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS29Inv2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0044521 | 5.9947 | 597.7238
3587 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS29Inv2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0033391 | 5.9947 | 448.2928
3588 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS29Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3589 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS29Inv2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0033391 | 5.9947 | 448.2928
3590 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS29Inv2M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0044521 | 5.9947 | 597.7238
3591 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS29Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3592 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS29 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS29Inv2M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3593 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | SCB string cable theft | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.044521 | 5.9947 | 5977.2379
3594 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | SCB string cable theft | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.042295 | 5.9947 | 5678.376
3595 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | SCB string cable theft | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.037843 | 5.9947 | 5080.6522
3596 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS31 | Inv2 |  |  |  |  | 1 | 1 | IS31Inv2 | 5311.35 | 1.461% | Inverter |  | Inverter Flash over | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.18532 | 5.9947 | 24880.2526
3597 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS33 | [5 empty] | 1 | 1 | IS33 | 9107.45 | 2.505% | IDT |  | SCB string cable theft | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.31777 | 5.9947 | 42662.5352
3598 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS39 | Inv1 | M4 |  |  |  | 1 | 1 | IS39Inv1M4 | 191.4 | 0.05265% | Module |  | INITIAL STAND BY (DC WORK PRNDING) | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0066782 | 5.9947 | 896.5857
3599 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS39 | Inv2 |  |  |  |  | 1 | 1 | IS39Inv2 | 223.3 | 0.06143% | Inverter |  | IO-DSP COMMINUCATION ANOMALY | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.0077912 | 5.9947 | 1046.0166
3600 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS46 | Inv2 | M1 |  |  |  | 1 | 1 | IS46Inv2M1 | 1148.4 | 0.3159% | Module |  | Emergency Stop(PROJECT WORK) | 6:17 | 6:17 | 6:17 | 18:58 | 0 | 0 |  | 12.6833 | Informed to Project team | Open | 0.040069 | 5.9947 | 5379.5141
3601 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | IS52 | Inv2 | M2 |  |  |  | 1 | 1 | IS52Inv2M2 | 893.2 | 0.2457% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:17 | 6:17 | 6:17 | 12:20 | 0 | 0 | 6.05 | 6.05 | Inverter Check and Reboot | Close | 0.014866 | 3.2733 | 2284.6457
3602 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS1 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS1Inv1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0034093 | 6.0491 | 452.358
3603 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS1 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS1Inv1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3604 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS1 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS1Inv1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0045457 | 6.0491 | 603.144
3605 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS1 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS1Inv2M2SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3606 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3607 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3608 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0045457 | 6.0491 | 603.144
3609 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3610 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3611 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3612 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS3 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS3Inv1M1SCB5 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0078827 | 6.0491 | 1045.9065
3613 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3614 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3615 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3616 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3617 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3618 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3619 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3620 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3621 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3622 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3631 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3632 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3633 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3634 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0062504 | 6.0491 | 829.3229
3635 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3636 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3637 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3638 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3639 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0056821 | 6.0491 | 753.9299
3640 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3641 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0056821 | 6.0491 | 753.9299
3642 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3643 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3644 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3645 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3646 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS9 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS9Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3647 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS9 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS9Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3648 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3649 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3650 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS9 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS9Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3651 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS12 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS12Inv1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3652 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3653 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS13 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS13Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3654 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3655 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3656 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS14 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS14Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3657 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3658 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS14 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS14Inv1M2SCB6 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0073868 | 6.0491 | 980.1089
3659 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS14 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS14Inv1M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0045457 | 6.0491 | 603.144
3660 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3661 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3662 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3663 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3664 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS14 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS14Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3665 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS18 | Inv1 | M3 | SCB2 |  |  | 1 | 1 | IS18Inv1M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3666 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS18 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS18Inv2M3SCB5 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0022729 | 6.0491 | 301.572
3667 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS19 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS19Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3668 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS19 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3669 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS19 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv1M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3670 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS19 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS19Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3671 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS19 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS19Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3672 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS19 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS19Inv2M1SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0034093 | 6.0491 | 452.358
3673 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS19 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS19Inv2M3SCB2 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0022729 | 6.0491 | 301.572
3674 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS19 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS19Inv2M3SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0056821 | 6.0491 | 753.9299
3675 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS19 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0045457 | 6.0491 | 603.144
3676 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS19 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv2M3SCB5 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0011364 | 6.0491 | 150.786
3677 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0056821 | 6.0491 | 753.9299
3678 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0045457 | 6.0491 | 603.144
3679 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3680 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS21 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS21Inv1M4SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0045457 | 6.0491 | 603.144
3681 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0056821 | 6.0491 | 753.9299
3682 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0039775 | 6.0491 | 527.751
3683 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0022729 | 6.0491 | 301.572
3684 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0073868 | 6.0491 | 980.1089
3685 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3686 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3687 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3688 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3689 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3690 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3691 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | INV1 | M2 | SCB3 |  |  | 1 | 1 | IS29INV1M2SCB3 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0045457 | 6.0491 | 603.144
3692 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | INV1 | M2 | SCB4 |  |  | 1 | 1 | IS29INV1M2SCB4 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0056821 | 6.0491 | 753.9299
3693 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | INV1 | M2 | SCB5 |  |  | 1 | 1 | IS29INV1M2SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0056821 | 6.0491 | 753.9299
3694 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | INV1 | M2 | SCB6 |  |  | 1 | 1 | IS29INV1M2SCB6 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0011364 | 6.0491 | 150.786
3695 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3696 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0 | 6.0491 | 0
3697 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3698 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3699 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3700 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS29Inv2M1SCB2 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3701 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS29Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3702 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS29Inv2M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3703 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS29Inv2M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3704 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS29Inv2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3705 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS29Inv2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3706 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS29Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3707 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS29Inv2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0045457 | 6.0491 | 603.144
3708 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS29Inv2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0034093 | 6.0491 | 452.358
3709 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS29Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3710 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS29Inv2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0034093 | 6.0491 | 452.358
3711 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS29Inv2M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0045457 | 6.0491 | 603.144
3712 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS29Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3713 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS29 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS29Inv2M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3714 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS30Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3715 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS30Inv1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3716 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS30Inv1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3717 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS30Inv1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0056821 | 6.0491 | 753.9299
3718 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS30Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3719 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS30Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3720 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS30Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3721 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS30Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3722 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS30Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3723 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv1 | M3 | SCB3 |  |  | 1 | 1 | IS30Inv1M3SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3724 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS30Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3725 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS30Inv1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0056821 | 6.0491 | 753.9299
3726 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS30Inv1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0045457 | 6.0491 | 603.144
3727 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | SCB string cable theft | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.045457 | 6.0491 | 6031.4396
3728 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | SCB string cable theft | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.043184 | 6.0491 | 5729.8676
3729 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | SCB string cable theft | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.038639 | 6.0491 | 5126.7236
3730 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS30Inv2M3SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3731 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS30Inv2M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3732 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS30Inv2M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0056821 | 6.0491 | 753.9299
3733 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS30Inv2M3SCB6 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0022729 | 6.0491 | 301.572
3734 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv2 | M4 | SCB2 |  |  | 1 | 1 | IS30Inv2M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3735 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv2 | M4 | SCB4 |  |  | 1 | 1 | IS30Inv2M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3736 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS30 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS30Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3737 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS31 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS31Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0045457 | 6.0491 | 603.144
3738 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS31 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS31Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3739 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS31 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS31Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3740 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS31 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS31Inv2M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3741 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS32 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS32Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3742 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS49 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS49Inv2M1SCB2 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0034093 | 6.0491 | 452.358
3743 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS49 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS49Inv2M1SCB3 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0011364 | 6.0491 | 150.786
3744 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS49 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS49Inv2M2SCB4 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0062504 | 6.0491 | 829.3229
3745 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS50Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3746 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS50Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3747 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS50Inv1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3748 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS50Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3749 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS50Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3750 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS50Inv2M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3751 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv2 | M3 | SCB1 |  |  | 1 | 1 | IS50Inv2M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3752 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS50Inv2M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3753 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS50Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0045457 | 6.0491 | 603.144
3754 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS50Inv2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3755 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS50Inv2M3SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3756 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS50Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3757 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv2 | M4 | SCB2 |  |  | 1 | 1 | IS50Inv2M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3758 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv2 | M4 | SCB3 |  |  | 1 | 1 | IS50Inv2M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3759 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv2 | M4 | SCB4 |  |  | 1 | 1 | IS50Inv2M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.007955 | 6.0491 | 1055.5019
3760 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS50 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS50Inv2M4SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.0068186 | 6.0491 | 904.7159
3761 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS8 | Inv2 | M4 |  |  |  | 1 | 1 | IS8Inv2M4 | 1339.8 | 0.3686% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 11:35 |  | 0 | 5.2667 | 5.2667 | Reboot and restart inverter | Close | 0.019411 | 2.7754 | 2905.6446
3762 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS33 | [5 empty] | 1 | 1 | IS33 | 9107.45 | 2.505% | IDT |  | SCB string cable theft | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.32445 | 6.0491 | 43049.3999
3763 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS31 | Inv2 |  |  |  |  | 1 | 1 | IS31Inv2 | 5311.35 | 1.461% | Inverter |  | Inverter Flash over | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.18922 | 6.0491 | 25105.8672
3764 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS35 | Inv1 | M4 |  |  |  | 1 | 1 | IS35Inv1M4 | 893.2 | 0.2457% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 |  | Open | 0.03182 | 6.0491 | 4222.0077
3765 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS46 | Inv1 |  |  |  |  | 1 | 1 | IS46Inv1 | 4131.05 | 1.136% | Inverter |  | gfdi | 6:19 | 6:19 | 6:19 | 7:32 | 0 | 0 | 1.2167 | 1.2167 | Reboot and restart inverter | Close | 0.013827 | 0.17868 | 576.7718
3766 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS14 | Inv2 | M2 |  |  |  | 1 | 1 | IS14Inv2M2 | 1276 | 0.351% | Module |  | LOW INSULATION RESISTENCE | 6:19 | 6:19 | 6:19 | 17:14 | 0 | 0 | 10.9167 | 10.9167 | Reboot and restart inverter | Close | 0.03832 | 5.7749 | 5758.0779
3767 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS14 | Inv2 | M3 |  |  |  | 1 | 1 | IS14Inv2M3 | 1228.15 | 0.3379% | Module |  | LOW INSULATION RESISTENCE | 6:19 | 6:19 | 6:19 | 17:14 | 0 | 0 | 10.9167 | 10.9167 | Reboot and restart inverter | Close | 0.036883 | 5.7749 | 5542.15
3768 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS14 | Inv2 | M4 |  |  |  | 1 | 1 | IS14Inv2M4 | 1307.9 | 0.3598% | Module |  | LOW INSULATION RESISTENCE | 6:19 | 6:19 | 6:19 | 17:14 | 0 | 0 | 10.9167 | 10.9167 | Reboot and restart inverter | Close | 0.039278 | 5.7749 | 5902.0298
3769 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS18 | Inv1 | M2 |  |  |  | 1 | 1 | IS18Inv1M2 | 1212.2 | 0.3335% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 |  | Open | 0.043184 | 6.0491 | 5729.8676
3770 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS21 | Inv1 | M3 |  |  |  | 1 | 1 | IS21Inv1M3 | 510.4 | 0.1404% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 |  | Open | 0.018183 | 6.0491 | 2412.5758
3771 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS46 | Inv1 | M2 |  |  |  | 1 | 1 | IS46Inv1M2 | 988.9 | 0.272% | Module |  | Emergency Stop(PROJECT WORK) | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.035229 | 6.0491 | 4674.3657
3772 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS42 | Inv1 | M3 |  |  |  | 1 | 1 | IS42Inv1M3 | 1100.55 | 0.3028% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 9:00 | 0 | 0 | 2.6833 | 2.6833 | Reboot and restart inverter | Close | 0.0081239 | 0.82127 | 706.2797
3773 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS8 | Inv2 | M1 |  |  |  | 1 | 1 | IS8Inv2M1 | 1212.2 | 0.3335% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 15:26 | 0 | 0 | 9.1167 | 9.1167 | Reboot and restart inverter | Close | 0.030401 | 4.9205 | 4660.8264
3774 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS8 | Inv2 | M2 |  |  |  | 1 | 1 | IS8Inv2M2 | 1244.1 | 0.3422% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 15:26 | 0 | 0 | 9.1167 | 9.1167 | Reboot and restart inverter | Close | 0.031201 | 4.9205 | 4783.4798
3775 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS8 | Inv2 | M3 |  |  |  | 1 | 1 | IS8Inv2M3 | 1164.35 | 0.3203% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 15:26 | 0 | 0 | 9.1167 | 9.1167 | Reboot and restart inverter | Close | 0.029201 | 4.9205 | 4476.8465
3776 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS47 | Inv2 | M4 |  |  |  | 1 | 1 | IS47Inv2M4 | 988.9 | 0.272% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 |  | Open | 0.035229 | 6.0491 | 4674.3657
3777 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS48 | Inv1 | M1 |  |  |  | 1 | 1 | IS48Inv1M1 | 319 | 0.08776% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 |  | Open | 0.011364 | 6.0491 | 1507.8599
3778 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS51 | Inv2 | M1 |  |  |  | 1 | 1 | IS51Inv2M1 | 1036.75 | 0.2852% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 |  | Open | 0.036934 | 6.0491 | 4900.5446
3779 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS51 | Inv1 | M1 |  |  |  | 1 | 1 | IS51Inv1M1 | 1084.6 | 0.2984% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 |  | Open | 0.038639 | 6.0491 | 5126.7236
3780 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS52 | Inv2 | M4 |  |  |  | 1 | 1 | IS52Inv2M4 | 1036.75 | 0.2852% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 |  | Open | 0.036934 | 6.0491 | 4900.5446
3781 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS6 | Inv1 |  |  |  |  | 1 | 1 | IS6Inv1 | 5072.1 | 1.395% | Inverter |  | gfdi | 6:19 | 6:19 | 6:19 | 17:58 | 0 | 0 | 11.65 | 11.65 | Reboot and restart inverter | Close | 0.16255 | 5.9456 | 23564.7376
3782 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS41 | Inv1 | M3 |  |  |  | 1 | 1 | IS41Inv1M3 | 1052.7 | 0.2896% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 10:35 | 0 | 0 | 4.2667 | 4.2667 | Reboot and restart inverter | Close | 0.012356 | 1.9946 | 1640.7039
3783 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS41 | Inv1 | M4 |  |  |  | 1 | 1 | IS41Inv1M4 | 1084.6 | 0.2984% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 10:35 | 0 | 0 | 4.2667 | 4.2667 | Reboot and restart inverter | Close | 0.01273 | 1.9946 | 1690.4222
3784 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS41 | Inv2 | M1 |  |  |  | 1 | 1 | IS41Inv2M1 | 1148.4 | 0.3159% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 10:35 | 0 | 0 | 4.2667 | 4.2667 | Reboot and restart inverter | Close | 0.013479 | 1.9946 | 1789.8588
3785 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS41 | Inv2 | M2 |  |  |  | 1 | 1 | IS41Inv2M2 | 1244.1 | 0.3422% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 10:35 | 0 | 0 | 4.2667 | 4.2667 | Reboot and restart inverter | Close | 0.014602 | 1.9946 | 1939.0138
3786 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS41 | Inv2 | M3 |  |  |  | 1 | 1 | IS41Inv2M3 | 1180.3 | 0.3247% | Module |  | gfdi | 6:19 | 6:19 | 6:19 | 10:35 | 0 | 0 | 4.2667 | 4.2667 | Reboot and restart inverter | Close | 0.013854 | 1.9946 | 1839.5771
3787 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS46 | Inv2 | M1 |  |  |  | 1 | 1 | IS46Inv2M1 | 1148.4 | 0.3159% | Module |  | Emergency Stop(PROJECT WORK) | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.040911 | 6.0491 | 5428.2956
3788 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS46 | Inv2 | M3 |  |  |  | 1 | 1 | IS46Inv2M3 | 1212.2 | 0.3335% | Module |  | Emergency Stop(PROJECT WORK) | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.043184 | 6.0491 | 5729.8676
3789 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | IS11 | Inv1 |  |  |  |  | 1 | 1 | IS11Inv1 | 685.85 | 0.1887% | Inverter |  | Shutdown by project team for DC cable terminations | 6:19 | 6:19 | 6:19 | 19:16 | 0 | 0 |  | 12.95 | Informed to Project team | Open | 0.024433 | 6.0491 | 3241.8988
3790 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS1 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS1Inv1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0034268 | 6.0491 | 452.358
3791 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS1 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS1Inv1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3792 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS1 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS1Inv1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0045691 | 6.0491 | 603.144
3793 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS1 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS1Inv2M2SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3794 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3795 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3796 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0045691 | 6.0491 | 603.144
3797 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3798 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3799 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3800 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS3 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS3Inv1M1SCB5 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079233 | 6.0491 | 1045.9065
3801 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3802 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3803 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3804 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3805 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3806 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3807 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3808 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3809 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3810 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3811 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3812 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3813 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3814 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0062825 | 6.0491 | 829.3229
3815 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3816 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3817 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3818 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3819 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0057114 | 6.0491 | 753.9299
3820 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3821 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0057114 | 6.0491 | 753.9299
3822 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3823 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3824 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3825 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3826 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS9 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS9Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3827 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS9 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS9Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3828 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3829 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3830 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS9 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS9Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3831 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS12 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS12Inv1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3832 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3833 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS13 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS13Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3834 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3835 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3836 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS14 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS14Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3837 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3838 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS14 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS14Inv1M2SCB6 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0074248 | 6.0491 | 980.1089
3839 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS14 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS14Inv1M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0045691 | 6.0491 | 603.144
3840 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3841 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3842 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3843 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3844 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS14 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS14Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3845 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS18 | Inv1 | M3 | SCB2 |  |  | 1 | 1 | IS18Inv1M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3846 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS18 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS18Inv2M3SCB5 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0022846 | 6.0491 | 301.572
3847 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS19 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS19Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3848 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS19 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3849 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS19 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv1M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3850 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS19 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS19Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3851 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS19 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS19Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3852 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS19 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS19Inv2M1SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0034268 | 6.0491 | 452.358
3853 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS19 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS19Inv2M3SCB2 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0022846 | 6.0491 | 301.572
3854 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS19 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS19Inv2M3SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0057114 | 6.0491 | 753.9299
3855 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS19 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0045691 | 6.0491 | 603.144
3856 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS19 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv2M3SCB5 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0011423 | 6.0491 | 150.786
3857 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0057114 | 6.0491 | 753.9299
3858 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0045691 | 6.0491 | 603.144
3859 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3860 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS21 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS21Inv1M4SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0045691 | 6.0491 | 603.144
3861 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0057114 | 6.0491 | 753.9299
3862 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.003998 | 6.0491 | 527.751
3863 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0022846 | 6.0491 | 301.572
3864 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0074248 | 6.0491 | 980.1089
3865 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3866 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3867 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3868 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3869 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3870 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3871 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3872 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0 | 6.0491 | 0
3873 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3874 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3875 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3876 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS29Inv2M1SCB2 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3877 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS29Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3878 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS29Inv2M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3879 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS29Inv2M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3880 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS29Inv2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3881 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS29Inv2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3882 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS29Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3883 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS29Inv2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0045691 | 6.0491 | 603.144
3884 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS29Inv2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0034268 | 6.0491 | 452.358
3885 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS29Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3886 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS29Inv2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0034268 | 6.0491 | 452.358
3887 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS29Inv2M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0045691 | 6.0491 | 603.144
3888 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS29Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3889 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS29Inv2M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3890 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS30Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3891 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS30Inv1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3892 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS30Inv1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3893 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS30Inv1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0057114 | 6.0491 | 753.9299
3894 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS30Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3895 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS30Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3896 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS30Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3897 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS30Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3898 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS30Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3899 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv1 | M3 | SCB3 |  |  | 1 | 1 | IS30Inv1M3SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3900 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS30Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3901 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS30Inv1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0057114 | 6.0491 | 753.9299
3902 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS30Inv1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0045691 | 6.0491 | 603.144
3903 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.045691 | 6.0491 | 6031.4396
3904 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.043407 | 6.0491 | 5729.8676
3905 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.038837 | 6.0491 | 5126.7236
3906 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS30Inv2M3SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3907 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS30Inv2M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3908 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS30Inv2M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0057114 | 6.0491 | 753.9299
3909 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS30Inv2M3SCB6 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0022846 | 6.0491 | 301.572
3910 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv2 | M4 | SCB2 |  |  | 1 | 1 | IS30Inv2M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3911 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv2 | M4 | SCB4 |  |  | 1 | 1 | IS30Inv2M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3912 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS30 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS30Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3913 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS31 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS31Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0045691 | 6.0491 | 603.144
3914 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS31 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS31Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3915 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS31 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS31Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3916 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS31 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS31Inv2M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3917 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS32 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS32Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3918 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS49 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS49Inv2M1SCB2 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0034268 | 6.0491 | 452.358
3919 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS49 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS49Inv2M1SCB3 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0011423 | 6.0491 | 150.786
3920 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS49 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS49Inv2M2SCB4 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0062825 | 6.0491 | 829.3229
3921 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS50Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3922 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS50Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3923 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS50Inv1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3924 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS50Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3925 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS50Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3926 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS50Inv2M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3927 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv2 | M3 | SCB1 |  |  | 1 | 1 | IS50Inv2M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3928 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS50Inv2M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3929 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS50Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0045691 | 6.0491 | 603.144
3930 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS50Inv2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3931 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS50Inv2M3SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3932 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS50Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3933 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv2 | M4 | SCB2 |  |  | 1 | 1 | IS50Inv2M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3934 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv2 | M4 | SCB3 |  |  | 1 | 1 | IS50Inv2M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3935 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv2 | M4 | SCB4 |  |  | 1 | 1 | IS50Inv2M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3936 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS50 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS50Inv2M4SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3937 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS7 | Inv2 | M3 |  |  |  | 1 | 1 | IS7Inv2M3 | 1244.1 | 0.3422% | Module |  | gfdi | 6:28 | 6:28 | 6:28 | 16:07 | 0 | 0 | 9.65 | 9.65 | Reboot and restart inverter | Close | 0.033027 | 6.0491 | 5880.6536
3938 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS46 | Inv1 | M1 |  |  |  | 1 | 1 | IS46Inv1M1 | 1004.85 | 0.2764% | Module |  | Shutdown by project team for DC cable terminations | 6:28 | 6:28 | 6:28 | 12:00 | 0 | 0 | 5.5333 | 5.5333 | Reboot and restart inverter | Close | 0.015296 | 6.0491 | 4749.7587
3939 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS46 | Inv2 | M3 |  |  |  | 1 | 1 | IS46Inv2M3 | 1212.2 | 0.3335% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 |  | Open | 0.043407 | 6.0491 | 5729.8676
3940 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS46 | Inv2 | M4 |  |  |  | 1 | 1 | IS46Inv2M4 | 1132.45 | 0.3115% | Module |  | Shutdown by project team for DC cable terminations | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.040551 | 6.0491 | 5352.9026
3941 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS31 | Inv2 |  |  |  |  | 1 | 1 | IS31Inv2 | 5311.35 | 1.461% | Inverter |  | Inverter Flash over | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.19019 | 6.0491 | 25105.8672
3942 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS33 | [5 empty] | 1 | 1 | IS33 | 9107.45 | 2.505% | IDT |  | SCB string cable theft | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.32612 | 6.0491 | 43049.3999
3943 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS34 | Inv1 | M2 |  |  |  | 1 | 1 | IS34Inv1M2 | 893.2 | 0.2457% | Module |  | Project Team work | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.031984 | 6.0491 | 4222.0077
3944 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS34 | Inv1 | M3 |  |  |  | 1 | 1 | IS34Inv1M3 | 1180.3 | 0.3247% | Module |  | Project Team work | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.042264 | 6.0491 | 5579.0816
3945 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS34 | Inv1 | M4 |  |  |  | 1 | 1 | IS34Inv1M4 | 1180.3 | 0.3247% | Module |  | Project Team work | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.042264 | 6.0491 | 5579.0816
3946 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS52 | Inv1 | M4 |  |  |  | 1 | 1 | IS52Inv1M4 | 1339.8 | 0.3686% | Module |  | gfdi | 6:28 | 6:28 | 6:28 | 10:56 | 0 | 0 | 4.4667 | 4.4667 | Reboot and restart inverter | Close | 0.016463 | 6.0491 | 6333.0115
3947 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS52 | Inv2 | M1 |  |  |  | 1 | 1 | IS52Inv2M1 | 861.3 | 0.2369% | Module |  | gfdi | 6:28 | 6:28 | 6:28 | 16:00 | 0 | 0 | 9.5333 | 9.5333 | Reboot and restart inverter | Close | 0.022588 | 6.0491 | 4071.2217
3948 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS51 | Inv1 | M1 |  |  |  | 1 | 1 | IS51Inv1M1 | 1084.6 | 0.2984% | Module |  | LOW INSULATION RESISTENCE | 6:28 | 6:28 | 6:28 | 11:20 | 0 | 0 | 4.8667 | 4.8667 | Reboot and restart inverter | Close | 0.014521 | 6.0491 | 5126.7236
3949 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS51 | Inv2 | M1 |  |  |  | 1 | 1 | IS51Inv2M1 | 1036.75 | 0.2852% | Module |  | LOW INSULATION RESISTENCE | 6:28 | 6:28 | 6:28 | 11:20 | 0 | 0 | 4.8667 | 4.8667 | Reboot and restart inverter | Close | 0.01388 | 6.0491 | 4900.5446
3950 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS51 | Inv2 | M3 |  |  |  | 1 | 1 | IS51Inv2M3 | 1307.9 | 0.3598% | Module |  | LOW INSULATION RESISTENCE | 6:28 | 6:28 | 6:28 | 11:20 | 0 | 0 | 4.8667 | 4.8667 | Reboot and restart inverter | Close | 0.01751 | 6.0491 | 6182.2256
3951 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS51 | Inv2 | M4 |  |  |  | 1 | 1 | IS51Inv2M4 | 1244.1 | 0.3422% | Module |  | gfdi | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 |  | Open | 0.044549 | 6.0491 | 5880.6536
3952 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS39 | Inv2 |  |  |  |  | 1 | 1 | IS39Inv2 | 223.3 | 0.06143% | Inverter |  | Project Team work | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0079959 | 6.0491 | 1055.5019
3953 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS39 | Inv1 | M4 |  |  |  | 1 | 1 | IS39Inv1M4 | 191.4 | 0.05265% | Module |  | Project Team work | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 | Informed to Project team | Open | 0.0068537 | 6.0491 | 904.7159
3954 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS40 | Inv2 |  |  |  |  | 1 | 1 | IS40Inv2 | 287.1 | 0.07898% | Inverter |  | gfdi | 6:28 | 6:28 | 6:28 | 12:55 | 0 | 0 | 6.45 | 6.45 | Reboot and restart inverter | Close | 0.0050942 | 6.0491 | 1357.0739
3955 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS12 | Inv2 | M1 |  |  |  | 1 | 1 | IS12Inv2M1 | 1339.8 | 0.3686% | Module |  | gfdi | 11:52 | 11:52 | 11:52 | 15:35 | 0 | 0 | 3.7167 | 3.7167 | Reboot and restart inverter | Close | 0.013699 | 6.0491 | 6333.0115
3956 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS29 | Inv1 | M2 |  |  |  | 1 | 1 | IS29Inv1M2 | 733.7 | 0.2018% | Module |  | gfdi | 6:28 | 6:28 | 6:28 | 18:43 | 0 | 0 | 12.25 | 12.25 | Reboot and restart inverter | Close | 0.024725 | 6.0491 | 3468.0778
3957 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS35 | Inv1 | M4 |  |  |  | 1 | 1 | IS35Inv1M4 | 893.2 | 0.2457% | Module |  | gfdi | 14:15 | 14:15 | 14:15 | 16:28 | 0 | 0 | 2.2167 | 2.2167 | Reboot and restart inverter | Close | 0.0054467 | 6.0491 | 4222.0077
3958 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS12 | Inv2 | M2 |  |  |  | 1 | 1 | IS12Inv2M2 | 1339.8 | 0.3686% | Module |  | gfdi | 14:52 | 14:52 | 14:52 | 15:35 | 0 | 0 | 0.71667 | 0.71667 | Reboot and restart inverter | Close | 0.0026414 | 6.0491 | 6333.0115
3959 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS12 | Inv2 | M3 |  |  |  | 1 | 1 | IS12Inv2M3 | 1307.9 | 0.3598% | Module |  | gfdi | 14:52 | 14:52 | 14:52 | 15:35 | 0 | 0 | 0.71667 | 0.71667 | Reboot and restart inverter | Close | 0.0025785 | 6.0491 | 6182.2256
3960 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS12 | Inv2 | M4 |  |  |  | 1 | 1 | IS12Inv2M4 | 1307.9 | 0.3598% | Module |  | gfdi | 14:52 | 14:52 | 14:52 | 15:35 | 0 | 0 | 0.71667 | 0.71667 | Reboot and restart inverter | Close | 0.0025785 | 6.0491 | 6182.2256
3961 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | IS51 | Inv2 | M3 |  |  |  | 1 | 1 | IS51Inv2M3 | 1307.9 | 0.3598% | Module |  | gfdi | 6:28 | 6:28 | 6:28 | 19:29 | 0 | 0 |  | 13.0167 |  | Open | 0.046833 | 6.0491 | 6182.2256
3962 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS1 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS1Inv1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0034224 | 6.0491 | 452.358
3963 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS1 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS1Inv1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
3964 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS1 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS1Inv1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 6.0491 | 603.144
3965 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS1 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS1Inv2M2SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
3966 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
3967 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
3968 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 6.0491 | 603.144
3969 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
3970 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
3971 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
3972 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS3 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS3Inv1M1SCB5 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079131 | 6.0491 | 1045.9065
3973 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
3974 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
3975 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
3976 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
3977 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
3978 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
3979 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
3980 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
3981 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
3982 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
3983 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
3984 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
3985 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
3986 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0062745 | 6.0491 | 829.3229
3987 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
3988 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
3989 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
3990 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
3991 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 6.0491 | 753.9299
3992 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
3993 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 6.0491 | 753.9299
3994 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
3995 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
3996 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
3997 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
3998 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS9 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS9Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
3999 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS9 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS9Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4000 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4001 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4002 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS9 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS9Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4003 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS12 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS12Inv1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
4004 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
4005 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS13 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS13Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4006 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4007 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4008 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS14 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS14Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4009 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4010 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS14 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS14Inv1M2SCB6 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0074153 | 6.0491 | 980.1089
4011 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS14 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS14Inv1M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 6.0491 | 603.144
4012 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4013 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4014 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4015 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4016 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS14 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS14Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4017 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS18 | Inv1 | M3 | SCB2 |  |  | 1 | 1 | IS18Inv1M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4018 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS18 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS18Inv2M3SCB5 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0022816 | 6.0491 | 301.572
4019 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS19 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS19Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4020 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS19 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4021 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS19 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv1M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4022 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS19 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS19Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4023 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS19 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS19Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4024 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS19 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS19Inv2M1SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0034224 | 6.0491 | 452.358
4025 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS19 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS19Inv2M3SCB2 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0022816 | 6.0491 | 301.572
4026 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS19 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS19Inv2M3SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 6.0491 | 753.9299
4027 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS19 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 6.0491 | 603.144
4028 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS19 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv2M3SCB5 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0011408 | 6.0491 | 150.786
4029 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 6.0491 | 753.9299
4030 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 6.0491 | 603.144
4031 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4032 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS21 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS21Inv1M4SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 6.0491 | 603.144
4033 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 6.0491 | 753.9299
4034 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0039929 | 6.0491 | 527.751
4035 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0022816 | 6.0491 | 301.572
4036 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0074153 | 6.0491 | 980.1089
4037 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4038 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4039 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4040 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4041 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
4042 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4043 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4044 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0 | 6.0491 | 0
4045 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4046 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4047 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4048 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS29Inv2M1SCB2 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4049 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS29Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4050 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS29Inv2M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4051 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS29Inv2M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4052 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS29Inv2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4053 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS29Inv2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4054 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS29Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4055 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS29Inv2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 6.0491 | 603.144
4056 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS29Inv2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0034224 | 6.0491 | 452.358
4057 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS29Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4058 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS29Inv2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0034224 | 6.0491 | 452.358
4059 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS29Inv2M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 6.0491 | 603.144
4060 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS29Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4061 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS29 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS29Inv2M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4062 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS30Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4063 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS30Inv1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4064 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS30Inv1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4065 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS30Inv1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 6.0491 | 753.9299
4066 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS30Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4067 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS30Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4068 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS30Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4069 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS30Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4070 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS30Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4071 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv1 | M3 | SCB3 |  |  | 1 | 1 | IS30Inv1M3SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4072 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS30Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4073 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS30Inv1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 6.0491 | 753.9299
4074 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS30Inv1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 6.0491 | 603.144
4075 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.045633 | 6.0491 | 6031.4396
4076 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.043351 | 6.0491 | 5729.8676
4077 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.038788 | 6.0491 | 5126.7236
4078 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS30Inv2M3SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4079 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS30Inv2M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4080 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS30Inv2M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0057041 | 6.0491 | 753.9299
4081 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS30Inv2M3SCB6 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0022816 | 6.0491 | 301.572
4082 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv2 | M4 | SCB2 |  |  | 1 | 1 | IS30Inv2M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4083 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv2 | M4 | SCB4 |  |  | 1 | 1 | IS30Inv2M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4084 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS30Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4085 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS31 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS31Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 6.0491 | 603.144
4086 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS31 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS31Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4087 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS31 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS31Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4088 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS31 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS31Inv2M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4089 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS32 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS32Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4090 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS49 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS49Inv2M1SCB2 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0034224 | 6.0491 | 452.358
4091 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS49 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS49Inv2M1SCB3 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0011408 | 6.0491 | 150.786
4092 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS49 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS49Inv2M2SCB4 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0062745 | 6.0491 | 829.3229
4093 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS50Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4094 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS50Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4095 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS50Inv1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4096 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS50Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4097 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS50Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4098 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS50Inv2M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4099 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv2 | M3 | SCB1 |  |  | 1 | 1 | IS50Inv2M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4100 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS50Inv2M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4101 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS50Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0045633 | 6.0491 | 603.144
4102 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS50Inv2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4103 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS50Inv2M3SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4104 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS50Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4105 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv2 | M4 | SCB2 |  |  | 1 | 1 | IS50Inv2M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4106 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv2 | M4 | SCB3 |  |  | 1 | 1 | IS50Inv2M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4107 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv2 | M4 | SCB4 |  |  | 1 | 1 | IS50Inv2M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4108 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS50 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS50Inv2M4SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4109 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS31 | Inv2 |  |  |  |  | 1 | 1 | IS31Inv2 | 5311.35 | 1.461% | Inverter |  | Inverter Flash over | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.18995 | 6.0491 | 25105.8672
4110 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS33 | [5 empty] | 1 | 1 | IS33 | 9107.45 | 2.505% | IDT |  | SCB string cable theft | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.3257 | 6.0491 | 43049.3999
4111 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | SCB string cable theft | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.045633 | 6.0491 | 6031.4396
4112 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | SCB string cable theft | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.043351 | 6.0491 | 5729.8676
4113 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | SCB string cable theft | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.038788 | 6.0491 | 5126.7236
4114 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS39 | Inv1 | M4 |  |  |  | 1 | 1 | IS39Inv1M4 | 191.4 | 0.05265% | Module |  | Project Team work | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0068449 | 6.0491 | 904.7159
4115 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS39 | Inv2 |  |  |  |  | 1 | 1 | IS39Inv2 | 223.3 | 0.06143% | Inverter |  | Shutdown by project team for DC cable terminations | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.0079857 | 6.0491 | 1055.5019
4116 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS46 | Inv2 | M3 |  |  |  | 1 | 1 | IS46Inv2M3 | 1212.2 | 0.3335% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.043351 | 6.0491 | 5729.8676
4117 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS51 | Inv2 | M3 |  |  |  | 1 | 1 | IS51Inv2M3 | 1307.9 | 0.3598% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.046773 | 6.0491 | 6182.2256
4118 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS51 | Inv2 | M4 |  |  |  | 1 | 1 | IS51Inv2M4 | 1244.1 | 0.3422% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Informed to Project team | Open | 0.044492 | 6.0491 | 5880.6536
4119 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS52 | Inv1 | M4 |  |  |  | 1 | 1 | IS52Inv1M4 | 1339.8 | 0.3686% | Module |  | gfdi | 6:20 | 6:20 | 6:20 | 15:25 | 0 | 0 | 9.0833 | 9.0833 | Reboot and restart inverter | Close | 0.033479 | 6.0491 | 6333.0115
4120 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS35 | Inv1 | M4 |  |  |  | 1 | 1 | IS35Inv1M4 | 893.2 | 0.2457% | Module |  | LOW INSULATION RESISTENCE | 6:20 | 6:20 | 6:20 | 10:58 | 0 | 0 | 4.6333 | 4.6333 | Reboot and restart inverter | Close | 0.011385 | 6.0491 | 4222.0077
4121 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS7 | Inv2 | M3 |  |  |  | 1 | 1 | IS7Inv2M3 | 1244.1 | 0.3422% | Module |  | gfdi | 6:20 | 6:20 | 6:20 | 9:36 | 0 | 0 | 3.2667 | 3.2667 | Reboot and restart inverter | Close | 0.01118 | 6.0491 | 5880.6536
4122 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | IS39 | Inv1 | M3 |  |  |  | 1 | 1 | IS39Inv1M3 | 0 | 0% | Module |  | Shutdown by project team for DC cable terminations | 6:20 | 6:20 | 6:20 | 19:20 | 0 | 0 |  | 13 | Reboot and restart inverter | Open | 0 | 6.0491 | 0
4123 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS1 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS1Inv1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0033654 | 6.0491 | 452.358
4124 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS1 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS1Inv1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4125 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS1 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS1Inv1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 6.0491 | 603.144
4126 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS1 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS1Inv2M2SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4127 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4128 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4129 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 6.0491 | 603.144
4130 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4131 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4132 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4133 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS3 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS3Inv1M1SCB5 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0077812 | 6.0491 | 1045.9065
4134 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4135 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4136 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4137 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4138 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4139 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4140 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4141 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4142 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4143 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4144 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4145 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4146 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4147 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0061699 | 6.0491 | 829.3229
4148 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4149 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4150 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4151 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4152 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 6.0491 | 753.9299
4153 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4154 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 6.0491 | 753.9299
4155 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4156 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4157 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4158 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4159 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS9 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS9Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4160 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS9 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS9Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4161 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4162 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4163 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS9 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS9Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4164 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS12 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS12Inv1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4165 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4166 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS13 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS13Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4167 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4168 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4169 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS14 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS14Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4170 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4171 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS14 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS14Inv1M2SCB6 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0072917 | 6.0491 | 980.1089
4172 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS14 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS14Inv1M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 6.0491 | 603.144
4173 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4174 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4175 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4176 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4177 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS14 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS14Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4178 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS18 | Inv1 | M3 | SCB2 |  |  | 1 | 1 | IS18Inv1M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4179 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS18 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS18Inv2M3SCB5 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0022436 | 6.0491 | 301.572
4180 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS19 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS19Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4181 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS19 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4182 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS19 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv1M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4183 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS19 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS19Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4184 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS19 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS19Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4185 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS19 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS19Inv2M1SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0033654 | 6.0491 | 452.358
4186 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS19 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS19Inv2M3SCB2 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0022436 | 6.0491 | 301.572
4187 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS19 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS19Inv2M3SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 6.0491 | 753.9299
4188 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS19 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 6.0491 | 603.144
4189 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS19 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv2M3SCB5 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0011218 | 6.0491 | 150.786
4190 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 6.0491 | 753.9299
4191 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 6.0491 | 603.144
4192 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4193 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS21 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS21Inv1M4SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 6.0491 | 603.144
4194 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 6.0491 | 753.9299
4195 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0039263 | 6.0491 | 527.751
4196 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0022436 | 6.0491 | 301.572
4197 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0072917 | 6.0491 | 980.1089
4198 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4199 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4200 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4201 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4202 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4203 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4204 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4205 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4206 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4207 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4208 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4209 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS29Inv2M1SCB2 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4210 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS29Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4211 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS29Inv2M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4212 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS29Inv2M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4213 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS29Inv2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4214 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS29Inv2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4215 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS29Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4216 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS29Inv2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 6.0491 | 603.144
4217 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS29Inv2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0033654 | 6.0491 | 452.358
4218 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS29Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4219 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS29Inv2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0033654 | 6.0491 | 452.358
4220 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS29Inv2M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 6.0491 | 603.144
4221 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS29Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4222 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS29 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS29Inv2M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4223 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS30Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4224 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS30Inv1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4225 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS30Inv1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4226 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS30Inv1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 6.0491 | 753.9299
4227 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS30Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4228 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS30Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4229 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS30Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4230 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS30Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4231 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS30Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4232 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv1 | M3 | SCB3 |  |  | 1 | 1 | IS30Inv1M3SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4233 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS30Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4234 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS30Inv1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 6.0491 | 753.9299
4235 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS30Inv1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 6.0491 | 603.144
4236 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS30Inv2M3SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4237 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS30Inv2M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4238 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS30Inv2M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.005609 | 6.0491 | 753.9299
4239 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS30Inv2M3SCB6 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0022436 | 6.0491 | 301.572
4240 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv2 | M4 | SCB2 |  |  | 1 | 1 | IS30Inv2M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4241 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv2 | M4 | SCB4 |  |  | 1 | 1 | IS30Inv2M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4242 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS30Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4243 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS31 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS31Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 6.0491 | 603.144
4244 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS31 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS31Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4245 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS31 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS31Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4246 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS31 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS31Inv2M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4247 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS32 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS32Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4248 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS49 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS49Inv2M1SCB2 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0033654 | 6.0491 | 452.358
4249 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS49 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS49Inv2M1SCB3 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0011218 | 6.0491 | 150.786
4250 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS49 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS49Inv2M2SCB4 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0061699 | 6.0491 | 829.3229
4251 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS50Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4252 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS50Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4253 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS50Inv1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4254 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS50Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4255 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS50Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4256 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS50Inv2M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4257 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv2 | M3 | SCB1 |  |  | 1 | 1 | IS50Inv2M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4258 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS50Inv2M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4259 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS50Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0044872 | 6.0491 | 603.144
4260 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS50Inv2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4261 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS50Inv2M3SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4262 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS50Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4263 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv2 | M4 | SCB2 |  |  | 1 | 1 | IS50Inv2M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4264 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv2 | M4 | SCB3 |  |  | 1 | 1 | IS50Inv2M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4265 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv2 | M4 | SCB4 |  |  | 1 | 1 | IS50Inv2M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4266 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS50 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS50Inv2M4SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4267 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS31 | Inv2 |  |  |  |  | 1 | 1 | IS31Inv2 | 5311.35 | 1.461% | Inverter |  | Inverter Flash over | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.18678 | 6.0491 | 25105.8672
4268 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS33 | [5 empty] | 1 | 1 | IS33 | 9107.45 | 2.505% | IDT |  | SCB string cable theft | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.32027 | 6.0491 | 43049.3999
4269 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | SCB string cable theft | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.044872 | 6.0491 | 6031.4396
4270 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | SCB string cable theft | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.042628 | 6.0491 | 5729.8676
4271 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | SCB string cable theft | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.038141 | 6.0491 | 5126.7236
4272 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS46 | Inv2 | M3 |  |  |  | 1 | 1 | IS46Inv2M3 | 1212.2 | 0.3335% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:18 | 6:18 | 6:18 | 16:33 | 0 | 0 | 10.25 | 10.25 | Reboot and restart inverter | Close | 0.034181 | 6.0491 | 5729.8676
4273 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS51 | Inv2 | M3 |  |  |  | 1 | 1 | IS51Inv2M3 | 1307.9 | 0.3598% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:18 | 6:18 | 6:18 | 12:26 | 0 | 0 | 6.1333 | 6.1333 | Reboot and restart inverter | Close | 0.022067 | 6.0491 | 6182.2256
4274 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS51 | Inv2 | M4 |  |  |  | 1 | 1 | IS51Inv2M4 | 1244.1 | 0.3422% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:18 | 6:18 | 6:18 | 12:26 | 0 | 0 | 6.1333 | 6.1333 | Reboot and restart inverter | Close | 0.020991 | 6.0491 | 5880.6536
4275 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS39 | Inv1 | M3 |  |  |  | 1 | 1 | IS39Inv1M3 | 0 | 0% | Module |  | Shutdown by project team for DC cable terminations | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0 | 6.0491 | 0
4276 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS39 | Inv1 | M4 |  |  |  | 1 | 1 | IS39Inv1M4 | 191.4 | 0.05265% | Module |  | Shutdown by project team for DC cable terminations | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0067308 | 6.0491 | 904.7159
4277 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS39 | Inv2 |  |  |  |  | 1 | 1 | IS39Inv2 | 223.3 | 0.06143% | Inverter |  | Shutdown by project team for DC cable terminations | 6:18 | 6:18 | 6:18 | 19:05 | 0 | 0 |  | 12.7833 | Informed to Project team | Open | 0.0078526 | 6.0491 | 1055.5019
4278 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS40 | Inv2 | M2 |  |  |  | 1 | 1 | IS40Inv2M2 | 0 | 0% | Module |  | GFDI | 6:18 | 6:18 | 6:18 | 13:00 | 0 | 0 | 6.7 | 6.7 | Reboot and restart inverter | Close | 0 | 6.0491 | 0
4279 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS48 | Inv1 | M1 |  |  |  | 1 | 1 | IS48Inv1M1 | 319 | 0.08776% | Module |  | GFDI | 6:18 | 6:18 | 6:18 | 10:00 | 0 | 0 | 3.7 | 3.7 | Reboot and restart inverter | Close | 0.0032469 | 6.0491 | 1507.8599
4280 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS12 | [5 empty] | 1 | 1 | IS12 | 5295.4 | 1.457% | IDT |  | GFDI | 11:00 | 11:00 | 11:00 | 14:22 | 0 | 0 | 3.3667 | 3.3667 | Reboot and restart inverter | Close | 0.049043 | 6.0491 | 25030.4742
4281 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | IS7 | Inv2 | M3 |  |  |  | 1 | 1 | IS7Inv2M3 | 1244.1 | 0.3422% | Module |  | GFDI | 6:18 | 6:18 | 6:18 | 12:53 | 0 | 0 | 6.5833 | 6.5833 | Reboot and restart inverter | Close | 0.022531 | 6.0491 | 5880.6536
4282 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS1 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS1Inv1M1SCB4 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0033215 | 6.1992 | 463.5844
4283 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS1 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS1Inv1M1SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4284 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS1 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS1Inv1M1SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0044287 | 6.1992 | 618.1125
4285 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS1 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS1Inv2M2SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4286 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS2 | INV2 | M2 | SCB5 |  |  | 1 | 1 | IS2INV2M2SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4287 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS2 | INV2 | M2 | SCB6 |  |  | 1 | 1 | IS2INV2M2SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4288 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS2 | INV2 | M3 | SCB2 |  |  | 1 | 1 | IS2INV2M3SCB2 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0044287 | 6.1992 | 618.1125
4289 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS2 | INV2 | M3 | SCB3 |  |  | 1 | 1 | IS2INV2M3SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4290 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS2 | INV2 | M3 | SCB5 |  |  | 1 | 1 | IS2INV2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4291 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS2 | INV2 | M3 | SCB6 |  |  | 1 | 1 | IS2INV2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4292 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS3 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS3Inv1M1SCB5 | 221.27 | 0.06087% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0076798 | 6.1992 | 1071.8633
4293 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS5 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS5Inv1M1SCB1 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4294 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS5 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS5Inv1M1SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4295 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS5 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv1M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4296 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS5 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv1M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4297 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS5 | Inv1 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv1M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4298 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS5 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv1M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4299 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS5 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS5Inv2M3SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4300 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS5 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS5Inv2M3SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4301 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS5 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS5Inv2M4SCB5 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4302 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS5 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS5Inv2M4SCB6 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4303 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS6 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS6Inv2M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4304 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS7 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS7Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4305 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS7 | Inv1 | M2 | SCB1 |  |  | 1 | 1 | IS7Inv1M2SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4306 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS7 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS7Inv1M2SCB2 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0060895 | 6.1992 | 849.9047
4307 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS7 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS7Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4308 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS7 | Inv1 | M3 | SCB1 |  |  | 1 | 1 | IS7Inv1M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4309 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS8 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv1M1SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4310 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS8 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4311 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS8 | Inv2 | M1 | SCB1 |  |  | 1 | 1 | IS8Inv2M1SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0055359 | 6.1992 | 772.6406
4312 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS8 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS8Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4313 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS8 | Inv2 | M2 | SCB1 |  |  | 1 | 1 | IS8Inv2M2SCB1 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0055359 | 6.1992 | 772.6406
4314 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS8 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS8Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4315 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS8 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS8Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4316 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS8 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS8Inv2M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4317 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS8 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS8Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4318 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS9 | Inv1 | M1 | SCB1 |  |  | 1 | 1 | IS9Inv1M1SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4319 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS9 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS9Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4320 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS9 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS9Inv1M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4321 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS9 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS9Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4322 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS9 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS9Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4323 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS12 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS12Inv1M2SCB2 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4324 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS12 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS12Inv1M2SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4325 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS13 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS13Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4326 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS13 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS13Inv2M2SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4327 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS13 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS13Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4328 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS14 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS14Inv1M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4329 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS14 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS14Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4330 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS14 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS14Inv1M2SCB6 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0071966 | 6.1992 | 1004.4328
4331 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS14 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS14Inv1M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0044287 | 6.1992 | 618.1125
4332 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS14 | Inv1 | M4 | SCB1 |  |  | 1 | 1 | IS14Inv1M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4333 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS14 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS14Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4334 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS14 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS14Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4335 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS14 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS14Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4336 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS14 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS14Inv2M3SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4337 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS18 | Inv1 | M3 | SCB2 |  |  | 1 | 1 | IS18Inv1M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4338 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS18 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS18Inv2M3SCB5 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0022144 | 6.1992 | 309.0563
4339 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS19 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS19Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4340 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS19 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4341 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS19 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv1M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4342 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS19 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS19Inv1M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4343 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS19 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS19Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4344 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS19 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS19Inv2M1SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0033215 | 6.1992 | 463.5844
4345 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS19 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS19Inv2M3SCB2 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0022144 | 6.1992 | 309.0563
4346 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS19 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS19Inv2M3SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0055359 | 6.1992 | 772.6406
4347 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS19 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS19Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0044287 | 6.1992 | 618.1125
4348 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS19 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS19Inv2M3SCB5 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0011072 | 6.1992 | 154.5281
4349 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS21 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS21Inv1M1SCB2 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0055359 | 6.1992 | 772.6406
4350 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS21 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS21Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0044287 | 6.1992 | 618.1125
4351 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS21 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS21Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4352 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS21 | Inv1 | M4 | SCB6 |  |  | 1 | 1 | IS21Inv1M4SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0044287 | 6.1992 | 618.1125
4353 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS21 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS21Inv2M1SCB3 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0055359 | 6.1992 | 772.6406
4354 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS21 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS21Inv2M2SCB4 | 111.65 | 0.03071% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0038751 | 6.1992 | 540.8484
4355 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS21 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS21Inv2M3SCB3 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0022144 | 6.1992 | 309.0563
4356 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS22 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv1M1SCB3 | 207.35 | 0.05704% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0071966 | 6.1992 | 1004.4328
4357 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS22 | Inv1 | M2 | SCB2 |  |  | 1 | 1 | IS22Inv1M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4358 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS22 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS22Inv1M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4359 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS22 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS22Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4360 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS22 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS22Inv2M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4361 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS22 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS22Inv2M1SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4362 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS22 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS22Inv2M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4363 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | INV1 | M4 | SCB1 |  |  | 1 | 1 | IS29INV1M4SCB1 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4364 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | INV1 | M4 | SCB3 |  |  | 1 | 1 | IS29INV1M4SCB3 | 0 | 0% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4365 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | INV1 | M4 | SCB4 |  |  | 1 | 1 | IS29INV1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4366 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | INV1 | M4 | SCB5 |  |  | 1 | 1 | IS29INV1M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4367 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | INV1 | M4 | SCB6 |  |  | 1 | 1 | IS29INV1M4SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4368 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS29Inv2M1SCB2 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4369 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS29Inv2M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4370 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS29Inv2M1SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4371 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | Inv2 | M1 | SCB5 |  |  | 1 | 1 | IS29Inv2M1SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4372 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | Inv2 | M1 | SCB6 |  |  | 1 | 1 | IS29Inv2M1SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4373 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS29Inv2M2SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4374 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | Inv2 | M2 | SCB5 |  |  | 1 | 1 | IS29Inv2M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4375 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS29Inv2M2SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0044287 | 6.1992 | 618.1125
4376 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS29Inv2M3SCB3 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0033215 | 6.1992 | 463.5844
4377 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS29Inv2M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4378 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS29Inv2M3SCB5 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0033215 | 6.1992 | 463.5844
4379 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS29Inv2M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0044287 | 6.1992 | 618.1125
4380 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS29Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4381 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS29 | Inv2 | M4 | SCB6 |  |  | 1 | 1 | IS29Inv2M4SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4382 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv1 | M1 | SCB2 |  |  | 1 | 1 | IS30Inv1M1SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4383 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv1 | M1 | SCB3 |  |  | 1 | 1 | IS30Inv1M1SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4384 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv1 | M1 | SCB4 |  |  | 1 | 1 | IS30Inv1M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4385 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS30Inv1M1SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0055359 | 6.1992 | 772.6406
4386 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv1 | M1 | SCB6 |  |  | 1 | 1 | IS30Inv1M1SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4387 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv1 | M2 | SCB3 |  |  | 1 | 1 | IS30Inv1M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4388 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv1 | M2 | SCB4 |  |  | 1 | 1 | IS30Inv1M2SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4389 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv1 | M2 | SCB5 |  |  | 1 | 1 | IS30Inv1M2SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4390 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv1 | M2 | SCB6 |  |  | 1 | 1 | IS30Inv1M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4391 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv1 | M3 | SCB3 |  |  | 1 | 1 | IS30Inv1M3SCB3 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4392 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv1 | M3 | SCB4 |  |  | 1 | 1 | IS30Inv1M3SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4393 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv1 | M3 | SCB5 |  |  | 1 | 1 | IS30Inv1M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0055359 | 6.1992 | 772.6406
4394 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv1 | M3 | SCB6 |  |  | 1 | 1 | IS30Inv1M3SCB6 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0044287 | 6.1992 | 618.1125
4395 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv2 | M3 | SCB3 |  |  | 1 | 1 | IS30Inv2M3SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4396 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS30Inv2M3SCB4 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4397 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS30Inv2M3SCB5 | 159.5 | 0.04388% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0055359 | 6.1992 | 772.6406
4398 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS30Inv2M3SCB6 | 63.8 | 0.01755% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0022144 | 6.1992 | 309.0563
4399 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv2 | M4 | SCB2 |  |  | 1 | 1 | IS30Inv2M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4400 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv2 | M4 | SCB4 |  |  | 1 | 1 | IS30Inv2M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4401 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS30Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4402 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS31 | Inv1 | M1 | SCB5 |  |  | 1 | 1 | IS31Inv1M1SCB5 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0044287 | 6.1992 | 618.1125
4403 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS31 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS31Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4404 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS31 | Inv2 | M2 | SCB3 |  |  | 1 | 1 | IS31Inv2M2SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4405 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS31 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS31Inv2M2SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4406 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS32 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS32Inv2M4SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4407 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS49 | Inv2 | M1 | SCB2 |  |  | 1 | 1 | IS49Inv2M1SCB2 | 95.7 | 0.02633% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0033215 | 6.1992 | 463.5844
4408 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS49 | Inv2 | M1 | SCB3 |  |  | 1 | 1 | IS49Inv2M1SCB3 | 31.9 | 0.008776% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0011072 | 6.1992 | 154.5281
4409 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS49 | Inv2 | M2 | SCB4 |  |  | 1 | 1 | IS49Inv2M2SCB4 | 175.45 | 0.04827% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0060895 | 6.1992 | 849.9047
4410 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv1 | M4 | SCB2 |  |  | 1 | 1 | IS50Inv1M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4411 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv1 | M4 | SCB3 |  |  | 1 | 1 | IS50Inv1M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4412 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv1 | M4 | SCB4 |  |  | 1 | 1 | IS50Inv1M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4413 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv2 | M1 | SCB4 |  |  | 1 | 1 | IS50Inv2M1SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4414 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv2 | M2 | SCB2 |  |  | 1 | 1 | IS50Inv2M2SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4415 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv2 | M2 | SCB6 |  |  | 1 | 1 | IS50Inv2M2SCB6 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4416 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv2 | M3 | SCB1 |  |  | 1 | 1 | IS50Inv2M3SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4417 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv2 | M3 | SCB2 |  |  | 1 | 1 | IS50Inv2M3SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4418 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv2 | M3 | SCB4 |  |  | 1 | 1 | IS50Inv2M3SCB4 | 127.6 | 0.0351% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0044287 | 6.1992 | 618.1125
4419 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv2 | M3 | SCB5 |  |  | 1 | 1 | IS50Inv2M3SCB5 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4420 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv2 | M3 | SCB6 |  |  | 1 | 1 | IS50Inv2M3SCB6 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4421 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv2 | M4 | SCB1 |  |  | 1 | 1 | IS50Inv2M4SCB1 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4422 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv2 | M4 | SCB2 |  |  | 1 | 1 | IS50Inv2M4SCB2 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4423 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv2 | M4 | SCB3 |  |  | 1 | 1 | IS50Inv2M4SCB3 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4424 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv2 | M4 | SCB4 |  |  | 1 | 1 | IS50Inv2M4SCB4 | 223.3 | 0.06143% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4425 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS50 | Inv2 | M4 | SCB5 |  |  | 1 | 1 | IS50Inv2M4SCB5 | 191.4 | 0.05265% | SCB |  | Project Activities SCB Shutdowen taken by Project Team | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4426 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS4 | Inv2 | M3 |  |  |  | 1 | 1 | IS4Inv2M3 | 1036.75 | 0.2852% | Module |  | GFDI | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.035983 | 6.1992 | 5022.1641
4427 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS7 | Inv2 | M3 |  |  |  | 1 | 1 | IS7Inv2M3 | 1244.1 | 0.3422% | Module |  | GFDI | 6:39 | 6:39 | 6:39 | 15:18 | 0 | 0 | 8.65 | 8.65 | Reboot and restart inverter | Close | 0.029604 | 4.9304 | 4793.1207
4428 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS11 | Inv1 |  |  |  |  | 1 | 1 | IS11Inv1 | 685.85 | 0.1887% | Inverter |  | IO-DSP COMMINUCATION ANOMALY | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.023804 | 6.1992 | 3322.3547
4429 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS16 | Inv1 |  |  |  |  | 1 | 1 | IS16Inv1 | 5008.3 | 1.378% | Inverter |  | IO-DSP COMMINUCATION ANOMALY | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.17383 | 6.1992 | 24260.916
4430 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS20 | Inv1 |  |  |  |  | 1 | 1 | IS20Inv1 | 5072.1 | 1.395% | Inverter |  | GFDI | 6:39 | 6:39 | 6:39 | 16:25 | 0 | 0 | 9.7667 | 9.7667 | Reboot and restart inverter | Close | 0.13627 | 5.6025 | 22204.8628
4431 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS21 | Inv1 | M1 |  |  |  | 1 | 1 | IS21Inv1M1 | 988.9 | 0.272% | Module |  | GFDI | 6:39 | 6:39 | 6:39 | 14:00 | 0 | 0 | 7.35 | 7.35 | Reboot and restart inverter | Close | 0.019995 | 3.9691 | 3067.0339
4432 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS27 | Inv2 | M2 |  |  |  | 1 | 1 | IS27Inv2M2 | 0 | 0% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4433 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS28 | Inv2 | M3 |  |  |  | 1 | 1 | IS28Inv2M3 | 350.9 | 0.09653% | Module |  | NEUTRAL POINT SHIFT | 6:39 | 6:39 | 6:39 | 9:54 | 0 | 0 | 3.25 | 3.25 | Reboot and restart inverter | Close | 0.0031372 | 0.68743 | 188.4925
4434 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv1 | M4 |  |  |  | 1 | 1 | IS30Inv1M4 | 1276 | 0.351% | Module |  | SCB string cable theft | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.044287 | 6.1992 | 6181.1251
4435 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv2 | M1 |  |  |  | 1 | 1 | IS30Inv2M1 | 1212.2 | 0.3335% | Module |  | SCB string cable theft | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.042073 | 6.1992 | 5872.0689
4436 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS30 | Inv2 | M2 |  |  |  | 1 | 1 | IS30Inv2M2 | 1084.6 | 0.2984% | Module |  | SCB string cable theft | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.037644 | 6.1992 | 5253.9563
4437 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS31 | Inv2 |  |  |  |  | 1 | 1 | IS31Inv2 | 5311.35 | 1.461% | Inverter |  | INVERTER Flash over | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.18434 | 6.1992 | 25728.9333
4438 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS33 | [5 empty] | 1 | 1 | IS33 | 9107.45 | 2.505% | IDT |  | SCB string cable theft | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.3161 | 6.1992 | 44117.7804
4439 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS34 | Inv1 | M2 |  |  |  | 1 | 1 | IS34Inv1M2 | 893.2 | 0.2457% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.031001 | 6.1992 | 4326.7876
4440 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS34 | Inv1 | M3 |  |  |  | 1 | 1 | IS34Inv1M3 | 1180.3 | 0.3247% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.040966 | 6.1992 | 5717.5407
4441 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS34 | Inv1 | M4 |  |  |  | 1 | 1 | IS34Inv1M4 | 1180.3 | 0.3247% | Module |  | IO-DSP COMMINUCATION ANOMALY | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.040966 | 6.1992 | 5717.5407
4442 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS35 | Inv1 | M2 |  |  |  | 1 | 1 | IS35Inv1M2 | 1180.3 | 0.3247% | Module |  | OVER CURRENT FAULT | 6:39 | 6:39 | 6:39 | 15:41 | 0 | 0 | 9.0333 | 9.0333 | Reboot and restart inverter | Close | 0.029331 | 5.187 | 4784.0048
4443 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS38 | [5 empty] | 1 | 1 | IS38 | 0 | 0% | IDT |  | IO-DSP COMMINUCATION ANOMALY | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4444 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS39 | Inv1 | M3 |  |  |  | 1 | 1 | IS39Inv1M3 | 0 | 0% | Module |  | LOW INSULATION RESISTENCE | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0 | 6.1992 | 0
4445 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS39 | Inv1 | M4 |  |  |  | 1 | 1 | IS39Inv1M4 | 191.4 | 0.05265% | Module |  | LOW INSULATION RESISTENCE | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0066431 | 6.1992 | 927.1688
4446 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS39 | Inv2 |  |  |  |  | 1 | 1 | IS39Inv2 | 223.3 | 0.06143% | Inverter |  | IO-DSP COMMINUCATION ANOMALY | 6:39 | 6:39 | 6:39 | 19:16 | 0 | 0 |  | 12.6167 | Informed to Project team | Open | 0.0077502 | 6.1992 | 1081.6969
4447 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS40 | Inv1 | M1 |  |  |  | 1 | 1 | IS40Inv1M1 | 1291.95 | 0.3554% | Module |  | GFDI | 6:39 | 6:39 | 6:39 | 9:10 | 0 | 0 | 2.5167 | 2.5167 | Reboot and restart inverter | Close | 0.0089444 | 0.41474 | 418.6977
4448 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS40 | Inv2 | M4 |  |  |  | 1 | 1 | IS40Inv2M4 | 287.1 | 0.07898% | Module |  | GFDI | 6:39 | 6:39 | 6:39 | 13:17 | 0 | 0 | 6.6333 | 6.6333 | Reboot and restart inverter | Close | 0.005239 | 3.4196 | 767.1625
4449 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS44 | Inv2 | M4 |  |  |  | 1 | 1 | IS44Inv2M4 | 925.1 | 0.2545% | Module |  | GFDI | 6:39 | 6:39 | 6:39 | 10:55 | 0 | 0 | 4.2667 | 4.2667 | Reboot and restart inverter | Close | 0.010858 | 1.3984 | 1010.8985
4450 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS45 | Inv1 | M1 |  |  |  | 1 | 1 | IS45Inv1M1 | 797.5 | 0.2194% | Module |  | LOW INSULATION FAULT | 6:39 | 6:39 | 6:39 | 9:30 | 0 | 0 | 2.85 | 2.85 | Reboot and restart inverter | Close | 0.0062525 | 0.55611 | 346.5545
4451 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS51 | Inv1 | M1 |  |  |  | 1 | 1 | IS51Inv1M1 | 1084.6 | 0.2984% | Module |  | INTIAL STAND BY | 6:39 | 6:39 | 6:39 | 16:10 | 0 | 0 | 9.5167 | 9.5167 | Reboot and restart inverter | Close | 0.028395 | 5.4751 | 4640.2446
4452 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS51 | Inv1 | M3 |  |  |  | 1 | 1 | IS51Inv1M3 | 953.81 | 0.2624% | Module |  | LOW INSULATION RESISTENCE | 6:39 | 6:39 | 6:39 | 13:54 | 0 | 0 | 7.25 | 7.25 | Reboot and restart inverter | Close | 0.019023 | 3.8781 | 2890.4015
4453 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS51 | Inv1 | M2 |  |  |  | 1 | 1 | IS51Inv1M2 | 1116.5 | 0.3071% | Module |  | CONTROL POWER SUPPLY ABNORMAL | 6:39 | 6:39 | 6:39 | 13:54 | 0 | 0 | 7.25 | 7.25 | Reboot and restart inverter | Close | 0.022268 | 3.8781 | 3383.4132
4454 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS51 | Inv1 | M4 |  |  |  | 1 | 1 | IS51Inv1M4 | 1116.5 | 0.3071% | Module |  | CONTROL POWER SUPPLY ABNORMAL | 6:39 | 6:39 | 6:39 | 13:54 | 0 | 0 | 7.25 | 7.25 | Reboot and restart inverter | Close | 0.022268 | 3.8781 | 3383.4132
4455 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | IS52 | Inv1 | M4 |  |  |  | 1 | 1 | IS52Inv1M4 | 1339.8 | 0.3686% | Module |  | LOW INSULATION FAULT | 6:39 | 6:39 | 6:39 | 15:50 | 0 | 0 | 9.1833 | 9.1833 | Reboot and restart inverter | Close | 0.033847 | 5.0621 | 5299.6332

## GA
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
Sr. No. | Date | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Breakdown Description | Fault Time | Work Completion time on fault | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(Wh/m2) | Approximate Energy Loss (KWh)
1 | 2025-05-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.27917 | 0.77917 | 12 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
2 | 2025-05-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.28194 | 0.78194 | 12 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
3 | 2025-05-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.27014 | 0.77014 | 12 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
4 | 2025-05-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.28056 | 0.78056 | 12 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
5 | 2025-05-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.29097 | 0.79097 | 12 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
6 | 2025-05-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.28194 | 0.78194 | 12 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
7 | 2025-05-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.28125 | 0.78056 | 11.9833 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
8 | 2025-05-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.27708 | 0.78542 | 12.2 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
9 | 2025-05-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.28542 | 0.78542 | 12 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
10 | 2025-05-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.27431 | 0.77431 | 12 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
11 | 2025-05-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.29028 | 0.79028 | 12 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
12 | 2025-05-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.29028 | 0.79028 | 12 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
13 | 2025-05-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.27917 | 0.77917 | 12 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
14 | 2025-05-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.28542 | 0.78542 | 12 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
15 | 2025-05-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.27847 | 0.77847 | 12 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
16 | 2025-05-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.27083 | 0.77083 | 12 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
17 | 2025-05-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.28542 | 0.78472 | 11.9833 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
18 | 2025-05-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.28958 | 0.79028 | 12.0167 | Grid |  | 0% |  |  |  | 0 |  |  | 0 |  | 0
19 | 2025-05-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25833 | 0.79444 | 12.8667 | Grid |  | 0% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 0 | 5.3359 | 0
20 | 2025-05-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.26111 | 0.79583 | 12.8333 | Grid |  | 0% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 0 | 5.299 | 0
21 | 2025-05-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25972 | 0.76042 | 12.0167 | Grid |  | 0% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 0 | 5.1947 | 0
22 | 2025-05-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25903 | 0.80139 | 13.0167 | Grid |  | 0% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 0 | 5.1611 | 0
23 | 2025-05-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25903 | 0.79653 | 12.9 | Grid |  | 0% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 0 | 4.9127 | 0
24 | 2025-05-24 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25833 | 0.79583 | 12.9 | Grid |  | 0% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 0 | 4.8015 | 0
25 | 2025-05-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.28125 | 0.79306 | 12.2833 | Grid |  | 0% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 0 | 2.3513 | 0
26 | 2025-05-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.26181 | 0.79514 | 12.8 | Grid |  | 0% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 0 | 4.066 | 0
27 | 2025-05-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.26181 | 0.78472 | 12.55 | Grid |  | 0% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 0 | 4.3745 | 0
28 | 2025-05-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.26042 | 0.79028 | 12.7167 | Grid |  | 0% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 0 | 4.0382 | 0
29 | 2025-05-29 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.26111 | 0.79792 | 12.8833 | Grid |  | 0% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 0 | 4.642 | 0
30 | 2025-05-30 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25833 | 0.79931 | 12.9833 | Grid |  | 0% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 0 | 5.1641 | 0
31 | 2025-05-31 | FY25 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.26042 | 0.80417 | 13.05 | Grid |  | 0% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 0 | 4.8972 | 0
32 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26042 | 0.80347 | 13.0333 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 6:14 | 9:00 | 2.7667 |  | Close | 0.11067 | 0.72206 | 5072.581
33 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26042 | 0.80347 | 13.0333 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 9:00 | 9:30 | 0.5 |  | Close | 0.24 | 0.30741 | 25915.4423
34 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26042 | 0.80347 | 13.0333 | Grid | 170870.5491 | 64.5% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 3.87 | 5.0452 | 571518.2572
35 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26042 | 0.80347 | 13.0333 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 15:30 | 16:00 | 0.5 |  | Close | 0.24 | 0.25522 | 21515.5472
36 | 2025-06-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26042 | 0.80347 | 13.0333 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 16:00 | 19:19 | 3.3167 |  | Close | 0.13267 | 3.631 | 25508.3556
37 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25972 | 0.80486 | 13.0833 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 6:14 | 9:00 | 2.7667 |  | Close | 0.11067 | 0.71653 | 5033.7183
38 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25972 | 0.80486 | 13.0833 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 9:00 | 9:30 | 0.5 |  | Close | 0.24 | 0.30641 | 25831.1618
39 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25972 | 0.80486 | 13.0833 | Grid | 170870.5491 | 64.5% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 3.87 | 5.0452 | 571518.2572
40 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25972 | 0.80486 | 13.0833 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 15:30 | 16:00 | 0.5 |  | Close | 0.24 | 0.25022 | 21094.145
41 | 2025-06-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25972 | 0.80486 | 13.0833 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 16:00 | 19:19 | 3.3167 |  | Close | 0.13267 | 0.78619 | 5523.0596
42 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25972 | 0.80069 | 12.9833 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 6:14 | 9:00 | 2.7667 |  | Close | 0.11067 | 0.66366 | 4662.27
43 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25972 | 0.80069 | 12.9833 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 9:00 | 9:30 | 0.5 |  | Close | 0.24 | 0.28855 | 24325.1205
44 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25972 | 0.80069 | 12.9833 | Grid | 170870.5491 | 64.5% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 3.87 | 4.8746 | 552199.0326
45 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25972 | 0.80069 | 12.9833 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 15:30 | 16:00 | 0.5 |  | Close | 0.24 | 0.285 | 24025.5774
46 | 2025-06-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25972 | 0.80069 | 12.9833 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 16:00 | 19:13 | 3.2167 |  | Close | 0.12867 | 0.74573 | 5238.8538
47 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25903 | 0.80069 | 13 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 6:13 | 9:00 | 2.7833 |  | Close | 0.11133 | 0.76295 | 5359.7839
48 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25903 | 0.80069 | 13 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 9:00 | 9:30 | 0.5 |  | Close | 0.24 | 0.30784 | 25951.1686
49 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25903 | 0.80069 | 13 | Grid | 170870.5491 | 64.5% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 3.87 | 5.0626 | 573492.6386
50 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25903 | 0.80069 | 13 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 15:30 | 16:00 | 0.5 |  | Close | 0.24 | 0.30067 | 25346.9168
51 | 2025-06-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25903 | 0.80069 | 13 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 16:00 | 19:13 | 3.2167 |  | Close | 0.12867 | 0.78919 | 5544.1139
52 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25903 | 0.80069 | 13 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 6:13 | 9:00 | 2.7833 |  | Close | 0.11133 | 0.70316 | 4939.7831
53 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25903 | 0.80069 | 13 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 9:00 | 9:30 | 0.5 |  | Close | 0.24 | 0.3083 | 25990.3691
54 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25903 | 0.80069 | 13 | Grid | 170870.5491 | 64.5% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 3.87 | 5.1501 | 583407.5893
55 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25903 | 0.80069 | 13 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 15:30 | 16:00 | 0.5 |  | Close | 0.24 | 0.30521 | 25729.3633
56 | 2025-06-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25903 | 0.80069 | 13 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 16:00 | 19:13 | 3.2167 |  | Close | 0.12867 | 0.79172 | 5561.9433
57 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25833 | 0.80139 | 13.0333 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 6:12 | 9:00 | 2.8 |  | Close | 0.112 | 0.82143 | 5770.644
58 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25833 | 0.80139 | 13.0333 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 9:00 | 9:30 | 0.5 |  | Close | 0.24 | 0.32867 | 27707.1203
59 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25833 | 0.80139 | 13.0333 | Grid | 170870.5491 | 64.5% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 3.87 | 5.2329 | 592781.3153
60 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25833 | 0.80139 | 13.0333 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 15:30 | 16:00 | 0.5 |  | Close | 0.24 | 0.25672 | 21641.7614
61 | 2025-06-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25833 | 0.80139 | 13.0333 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 16:00 | 19:14 | 3.2333 |  | Close | 0.12933 | 0.95468 | 6706.7243
62 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25764 | 0.80069 | 13.0333 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 6:11 | 9:00 | 2.8167 |  | Close | 0.11267 | 0.83737 | 5882.5874
63 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25764 | 0.80069 | 13.0333 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 9:00 | 9:30 | 0.5 |  | Close | 0.24 | 0.32402 | 27315.1024
64 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25764 | 0.80069 | 13.0333 | Grid | 170870.5491 | 64.5% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 3.87 | 5.2894 | 599181.0487
65 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25764 | 0.80069 | 13.0333 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 15:30 | 16:00 | 0.5 |  | Close | 0.24 | 0.31644 | 26675.9389
66 | 2025-06-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25764 | 0.80069 | 13.0333 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 16:00 | 19:13 | 3.2167 |  | Close | 0.12867 | 0.82632 | 5804.9592
67 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.2625 | 0.81389 | 13.2333 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 6:18 | 9:00 | 3.18 |  | Close | 0.1272 | 0.89151 | 6262.9435
68 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.2625 | 0.81389 | 13.2333 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 9:00 | 9:30 | 0.5 |  | Close | 0.24 | 0.33807 | 28499.856
69 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.2625 | 0.81389 | 13.2333 | Grid | 170870.5491 | 64.5% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 3.87 | 5.3602 | 607204.3575
70 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.2625 | 0.81389 | 13.2333 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 15:30 | 16:00 | 0.5 |  | Close | 0.24 | 0.32177 | 27125.2418
71 | 2025-06-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.2625 | 0.81389 | 13.2333 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 16:00 | 19:32 | 3.32 |  | Close | 0.1328 | 0.84239 | 5917.8502
72 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25764 | 0.80208 | 13.0667 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 6:11 | 9:00 | 3.18 |  | Close | 0.1272 | 0.85408 | 6000.0024
73 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25764 | 0.80208 | 13.0667 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 9:00 | 9:30 | 0.5 |  | Close | 0.24 | 0.32681 | 27550.6123
74 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25764 | 0.80208 | 13.0667 | Grid | 170870.5491 | 64.5% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 3.87 | 5.2836 | 598531.4644
75 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25764 | 0.80208 | 13.0667 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 15:30 | 16:00 | 0.5 |  | Close | 0.24 | 0.31776 | 26787.9865
76 | 2025-06-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25764 | 0.80208 | 13.0667 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 16:00 | 19:15 | 3.32 |  | Close | 0.1328 | 0.82351 | 5785.2322
77 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25694 | 0.80278 | 13.1 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 6:10 | 9:00 | 2.5 |  | Close | 0.1 | 0.84102 | 5908.2483
78 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25694 | 0.80278 | 13.1 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 9:00 | 9:30 | 0.3 |  | Close | 0.144 | 0.31979 | 26958.5697
79 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25694 | 0.80278 | 13.1 | Grid | 170870.5491 | 64.5% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 3.87 | 5.199 | 588945.6598
80 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25694 | 0.80278 | 13.1 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 15:30 | 16:00 | 0.3 |  | Close | 0.144 | 0.31533 | 26583.1134
81 | 2025-06-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25694 | 0.80278 | 13.1 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 16:00 | 19:16 | 3.16 |  | Close | 0.1264 | 0.8185 | 5750.0301
82 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 6:10 | 9:00 | 2.5 |  | Close | 0.1 | 0.84102 | 5908.2483
83 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 9:00 | 9:30 | 0.3 |  | Close | 0.144 | 0.31979 | 26958.5697
84 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | Grid | 170870.5491 | 64.5% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 3.87 | 5.199 | 588945.6598
85 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 15:30 | 16:00 | 0.3 |  | Close | 0.144 | 0.31533 | 26583.1134
86 | 2025-06-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:18 | 13.1333 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 16:00 | 19:16 | 3.16 |  | Close | 0.1264 | 0.8185 | 5750.0301
87 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 6:10 | 9:00 | 2.5 |  | Close | 0.1 | 0.86878 | 6103.2462
88 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 9:00 | 9:30 | 0.3 |  | Close | 0.144 | 0.33901 | 28578.8861
89 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | Grid | 170870.5491 | 64.5% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 3.87 | 5.2689 | 596862.5141
90 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 15:30 | 16:00 | 0.3 |  | Close | 0.144 | 0.33017 | 27833.4767
91 | 2025-06-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:14 | 13.0667 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 16:00 | 19:14 | 3.14 |  | Close | 0.1256 | 0.82598 | 5802.6225
92 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 6:10 | 9:00 | 2.5 |  | Close | 0.1 | 0.83153 | 5841.5771
93 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 9:00 | 9:30 | 0.3 |  | Close | 0.144 | 0.32688 | 27556.505
94 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | Grid | 170870.5491 | 64.5% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 3.87 | 5.0488 | 571922.1958
95 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 15:30 | 16:00 | 0.3 |  | Close | 0.144 | 0.2263 | 19076.9873
96 | 2025-06-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:21 | 13.1833 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 16:00 | 19:21 | 3.21 |  | Close | 0.1284 | 0.72193 | 5071.6408
97 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 6:26 | 9:00 | 2.34 |  | Close | 0.0936 | 0.2515 | 1766.8333
98 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 9:00 | 9:30 | 0.3 |  | Close | 0.144 | 0.13814 | 11645.2219
99 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | Grid | 170870.5491 | 64.5% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 3.87 | 0.62119 | 70368.3229
100 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 15:30 | 16:00 | 0.3 |  | Close | 0.144 | 0.042758 | 3604.5638
101 | 2025-06-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:13 | 12.7833 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 16:00 | 19:13 | 3.13 |  | Close | 0.1252 | 0.38224 | 2685.3085
102 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 7:20 | 9:00 | 1.4 |  | Close | 0.056 | 0.068748 | 482.9622
103 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 9:00 | 9:30 | 0.3 |  | Close | 0.144 | 0.026161 | 2205.4019
104 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | Grid | 170870.5491 | 64.5% | Load Shedding as per Standing Committee Approval | 9:30 | 15:30 | 6 |  | Close | 3.87 | 1.224 | 138650.8406
105 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | Grid | 127159.4784 | 48% | Load Shedding as per Standing Committee Approval | 15:30 | 16:00 | 0.3 |  | Close | 0.144 | 0.11289 | 9517.166
106 | 2025-06-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:20 | 19:14 | 11.9 | Grid | 10596.6232 | 4% | Load Shedding as per Standing Committee Approval | 16:00 | 19:14 | 3.14 |  | Close | 0.1256 | 0.46534 | 3269.0765
107 | 2025-06-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 7:23 | 19:22 | 11.9833 | Grid | 111264.72 | 46.16% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 1.8463 | 1.9734 | 145567.6052
108 | 2025-06-17 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:33 | 19:26 | 12.8833 | Grid | 111264.72 | 46.16% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 1.8463 | 3.0678 | 226294.9861
109 | 2025-06-18 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:13 | 19:19 | 13.1 | Grid | 111264.72 | 46.16% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 1.8463 | 3.6452 | 268887.1643
110 | 2025-06-19 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:07 | 19:43 | 13.6 | Grid | 111264.72 | 46.16% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 1.8463 | 3.6056 | 265964.4995
111 | 2025-06-20 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:17 | 19:04 | 12.7833 | Grid | 100832.8882 | 41.83% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 1.6732 | 3.3606 | 224649.1544
112 | 2025-06-21 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:11 | 18:41 | 12.5 | Grid | 100832.8882 | 41.83% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 1.6732 | 1.6508 | 110350.2424
113 | 2025-06-22 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:10 | 19:19 | 13.15 | Grid | 100832.8882 | 41.83% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 1.6732 | 3.5131 | 234840.6047
114 | 2025-06-23 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:14 | 19:16 | 13.0333 | Grid | 100832.8882 | 41.83% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 1.6732 | 3.258 | 217789.8534
115 | 2025-06-25 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:23 | 18:59 | 12.6 | Grid | 100832.8882 | 41.83% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 1.6732 | 3.3864 | 226373.4059
116 | 2025-06-26 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:16 | 17:56 | 11.6667 | Grid | 111264.72 | 46.16% | Load Shedding as per Standing Committee Approval | 10:30 | 12:15 | 4 |  | Close | 1.8463 | 2.62 | 193261.617
117 | 2025-06-27 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:12 | 18:41 | 12.4833 | Grid | 111264.72 | 46.16% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 1.8463 | 1.5424 | 113773.5748
118 | 2025-06-28 | FY25 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 6:26 | 19:20 | 12.9 | Grid | 111264.72 | 46.16% | Load Shedding as per Standing Committee Approval | 10:30 | 10:50 | 0.2 |  | Close | 0.092315 | 0.20796 | 15339.803
119 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | Grid | 20959.6453 | 8.695% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.013043 | 0.16637 | 2724.8103
120 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | Grid | 109113.0931 | 45.27% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 1.8106 | 3.2187 | 274434.3551
121 | 2025-07-01 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:18 | 12.9 | Grid | 20959.6453 | 8.695% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.013043 | 0.17406 | 2850.7906
122 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | Grid | 293476.5 | 87.87% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.1318 | 0.090304 | 20708.9298
123 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | Grid | 392215.5 | 117.4% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 4.6972 | 1.2407 | 380248.046
124 | 2025-07-02 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 18:51 | 12.55 | Grid | 23476.5 | 7.029% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.010543 | 0.097215 | 1783.3799
125 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | Grid | 293476.5 | 87.87% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.1318 | 0.20874 | 47868.5799
126 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | Grid | 392215.5 | 117.4% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 4.6972 | 1.7198 | 527076.6753
127 | 2025-07-03 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:38 | 19:06 | 12.4667 | Grid | 23476.5 | 7.029% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.010543 | 0.0042042 | 77.1246
128 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | Grid | 181520.65 | 54.35% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.081521 | 0.15335 | 21751.2903
129 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | Grid | 242592.55 | 72.63% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 2.9053 | 3.2233 | 611020.6599
130 | 2025-07-04 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:16 | 19:17 | 13.0167 | Grid | 16190.65 | 4.848% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.0072712 | 0.10781 | 1364.0052
131 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | Grid | 181520.65 | 54.35% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.081521 | 0.2097 | 29744.7831
132 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | Grid | 242592.55 | 72.63% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 2.9053 | 3.3574 | 636441.2213
133 | 2025-07-05 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | Grid | 16190.65 | 4.848% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.0072712 | 0.21164 | 2677.6003
134 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | Grid | 181520.65 | 54.35% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.081521 | 0.13463 | 19095.7384
135 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | Grid | 242592.55 | 72.63% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 2.9053 | 3.1519 | 597483.4071
136 | 2025-07-06 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:15 | 12.9167 | Grid | 16190.65 | 4.848% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.0072712 | 0.18112 | 2291.4771
137 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | Grid | 181520.65 | 54.35% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.081521 | 0.1065 | 15106.2455
138 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | Grid | 242592.55 | 72.63% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 2.9053 | 3.31 | 627464.1333
139 | 2025-07-07 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:49 | 19:07 | 12.3 | Grid | 16190.65 | 4.848% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.0072712 | 0.18609 | 2354.3007
140 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | Grid | 181520.65 | 50.8% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.076199 | 0.15934 | 22600.7656
141 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | Grid | 242592.55 | 67.89% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 2.7156 | 2.3843 | 451983.4756
142 | 2025-07-08 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:24 | 19:20 | 12.9333 | Grid | 16190.65 | 4.531% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.0067966 | 0.10994 | 1390.9423
143 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | Grid | 181520.65 | 50.8% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.076199 | 0.10117 | 14350.6493
144 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | Grid | 242592.55 | 67.89% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 2.7156 | 2.3754 | 450284.3093
145 | 2025-07-09 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:26 | 19:12 | 12.7667 | Grid | 16190.65 | 4.531% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.0067966 | 0.20001 | 2530.3716
146 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | Grid | 181520.65 | 49.94% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.074903 | 0.14927 | 21172.4567
147 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | Grid | 242592.55 | 66.74% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 2.6694 | 2.6991 | 511644.8819
148 | 2025-07-10 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:13 | 12.9 | Grid | 16190.65 | 4.454% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.0066809 | 0.21446 | 2713.3024
149 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | Grid | 181520.65 | 49.94% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.074903 | 0.19277 | 27342.834
150 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | Grid | 242592.55 | 66.74% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 2.6694 | 3.1546 | 597996.8611
151 | 2025-07-11 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:17 | 18:58 | 12.6833 | Grid | 16190.65 | 4.454% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.0066809 | 0.090872 | 1149.6652
152 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | Grid | 181520.65 | 49.94% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.074903 | 0.21147 | 29995.0253
153 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | Grid | 242592.55 | 66.74% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 2.6694 | 2.5706 | 487296.6417
154 | 2025-07-12 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:19 | 19:16 | 12.95 | Grid | 16190.65 | 4.454% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.0066809 | 0.09357 | 1183.8056
155 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | Grid | 181520.65 | 49.94% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.074903 | 0.187 | 26524.5341
156 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | Grid | 242592.55 | 66.74% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 2.6694 | 3.577 | 678066.271
157 | 2025-07-13 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:28 | 19:29 | 13.0167 | Grid | 16190.65 | 4.454% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.0066809 | 0.1383 | 1749.6491
158 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | Grid | 181520.65 | 49.94% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.074903 | 0.18347 | 26024.2217
159 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | Grid | 242592.55 | 66.74% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 2.6694 | 3.0415 | 576551.3994
160 | 2025-07-14 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:20 | 19:20 | 13 | Grid | 16190.65 | 4.454% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.0066809 | 0.085722 | 1084.5212
161 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | Grid | 181520.65 | 49.94% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.074903 | 0.19048 | 27017.6289
162 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | Grid | 242592.55 | 66.74% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 2.6694 | 2.8308 | 536626.5846
163 | 2025-07-15 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:18 | 19:05 | 12.7833 | Grid | 16190.65 | 4.454% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.0066809 | 0.09775 | 1236.6891
164 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | Grid | 181756 | 50% | Load Shedding as per Standing Committee Approval | 6:39 | 10:15 | 3.36 |  | Close | 1.68 | 0.89968 | 127777.9152
165 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | Grid | 50519.0802 | 13.9% | Load Shedding as per Standing Committee Approval | 10:15 | 10:30 | 0.15 |  | Close | 0.020846 | 0.19387 | 7653.0865
166 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | Grid | 186830.5673 | 51.4% | Load Shedding as per Standing Committee Approval | 10:30 | 14:30 | 4 |  | Close | 2.0558 | 3.253 | 474907.4846
167 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | Grid | 50519.0802 | 13.9% | Load Shedding as per Standing Committee Approval | 14:30 | 14:45 | 0.15 |  | Close | 0.020846 | 0.20748 | 8190.4533
168 | 2025-07-16 | FY25 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 6:39 | 19:16 | 12.6167 | Grid | 181756 | 50% | Load Shedding as per Standing Committee Approval | 14:45 | 19:16 | 4.31 |  | Close | 2.155 | 1.6497 | 234301.9832
Formulas:
Sunrise Time (POA>20 W/m2) = IFERROR(XLOOKUP(GA[[#This Row],[Date]],'Raw_Data'!$B:$B,'Raw_Data'!$J:$J),"")
Sunset Time (POA<20 W/m2) = IFERROR(XLOOKUP(GA[[#This Row],[Date]],'Raw_Data'!$B:$B,'Raw_Data'!$K:$K),"")

## Curtailment records
Sr. No | Month | Date | Plant Name | Categoty | Equipment Name | Inverter No. | From | To | Duration in MIN | Total Breakdown Hrs. | Avg POA During BD time | Lost POA | Total POA | Net POA | Loss of Capacity in KWp | Estimated PR % (Pvsyst) | Loss of Generation kWh | Remark | Current Load befor Load Sheeding (AC MW) | Load to be maintain (AC Mw)
1 | May | 2025-05-18 | XLXPPL | Load Shedding | All Block | All inverter | 9:55 | 19:30 | 9:35 | 9.581 | 667.8731 | 6.3989 | 0 | -6.3989 | 132763 | 58.76 | 499185.2114 | Load Shedding as per Standing Committee Approval
2 | May | 2025-05-19 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 889.5441 | 5.3359 | 7.6259 | 2.2899 | 137763 | 58.76 | 431941.9697 | Load Shedding as per Standing Committee Approval | 111.8 | 0
3 | May | 2025-05-20 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 883.3897 | 5.299 | 7.482 | 2.183 | 137763 | 58.76 | 428953.5624 | Load Shedding as per Standing Committee Approval | 111.8 | 0
4 | May | 2025-05-21 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 865.993 | 5.1947 | 6.9463 | 1.7516 | 137763 | 58.76 | 420506.1206 | Load Shedding as per Standing Committee Approval | 111.8 | 0
5 | May | 2025-05-22 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 860.3961 | 5.1611 | 7.3569 | 2.1958 | 137763 | 58.76 | 417788.3928 | Load Shedding as per Standing Committee Approval | 111.8 | 0
6 | May | 2025-05-23 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 818.9847 | 4.9127 | 7.0824 | 2.1697 | 137763 | 58.76 | 397679.9676 | Load Shedding as per Standing Committee Approval | 111.8 | 0
7 | May | 2025-05-24 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 800.4428 | 4.8015 | 6.8333 | 2.0319 | 137763 | 58.76 | 388676.4753 | Load Shedding as per Standing Committee Approval | 111.8 | 0
8 | May | 2025-05-25 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 391.9759 | 2.3513 | 3.3064 | 0.95508 | 137763 | 58.76 | 190334.4243 | Load Shedding as per Standing Committee Approval | 111.8 | 0
9 | May | 2025-05-26 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 677.841 | 4.066 | 5.7493 | 1.6833 | 137763 | 58.76 | 329143.8607 | Load Shedding as per Standing Committee Approval | 111.8 | 0
10 | May | 2025-05-27 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 729.2699 | 4.3745 | 6.1228 | 1.7483 | 137763 | 58.76 | 354116.5623 | Load Shedding as per Standing Committee Approval | 111.8 | 0
11 | May | 2025-05-28 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 673.2039 | 4.0382 | 5.5703 | 1.532 | 137763 | 58.76 | 326892.1894 | Load Shedding as per Standing Committee Approval | 111.8 | 0
12 | May | 2025-05-29 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 773.852 | 4.642 | 6.526 | 1.884 | 137763 | 58.76 | 375764.5878 | Load Shedding as per Standing Committee Approval | 111.8 | 0
13 | May | 2025-05-30 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 860.9029 | 5.1641 | 6.7895 | 1.6254 | 137763 | 58.76 | 418034.5077 | Load Shedding as per Standing Committee Approval | 111.8 | 0
14 | May | 2025-05-31 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 816.3943 | 4.8972 | 6.8592 | 1.9621 | 137763 | 58.76 | 396422.1344 | Load Shedding as per Standing Committee Approval | 111.8 | 0
15 | Jun | 2025-06-01 | XLXPPL | Load Shedding | All Block | All inverter | 6:14 | 9:00 | 2:46 | 2.766 | 261.0517 | 0.72206 | 6.681 | 5.959 | 10596.6232 | 66.3 | 5072.9048 | Load Shedding as per Standing Committee Approval | 200 | 192
16 | Jun | 2025-06-01 | XLXPPL | Load Shedding | All Block | All inverter | 9:00 | 9:30 | 0:30 | 0.49988 | 614.9811 | 0.30741 | 6.681 | 6.3736 | 127159.4784 | 66.3 | 25917.0966 | Load Shedding as per Standing Committee Approval | 200 | 104
17 | Jun | 2025-06-01 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 841.0727 | 5.0452 | 6.681 | 1.6359 | 170870.5491 | 66.3 | 571554.7406 | Load Shedding as per Standing Committee Approval | 200 | 71
18 | Jun | 2025-06-01 | XLXPPL | Load Shedding | All Block | All inverter | 15:30 | 16:00 | 0:30 | 0.49988 | 510.5703 | 0.25522 | 6.681 | 6.4258 | 127159.4784 | 66.3 | 21516.9207 | Load Shedding as per Standing Committee Approval | 200 | 104
19 | Jun | 2025-06-01 | XLXPPL | Load Shedding | All Block | All inverter | 4:00 | 19:19 | 15:19 | 15.3129 | 237.1224 | 3.631 | 6.681 | 3.05 | 10596.6232 | 66.3 | 25509.984 | Load Shedding as per Standing Committee Approval | 200 | 192
15 | Jun | 2025-06-02 | XLXPPL | Load Shedding | All Block | All inverter | 6:14 | 9:00 | 2:46 | 2.766 | 259.0517 | 0.71653 | 7.1118 | 6.3953 | 10596.6232 | 66.3 | 5034.0396 | Load Shedding as per Standing Committee Approval | 200 | 192
16 | Jun | 2025-06-02 | XLXPPL | Load Shedding | All Block | All inverter | 9:00 | 9:30 | 0:30 | 0.49988 | 612.9811 | 0.30641 | 7.1118 | 6.8054 | 127159.4784 | 66.3 | 25832.8108 | Load Shedding as per Standing Committee Approval | 200 | 104
17 | Jun | 2025-06-02 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 841.0727 | 5.0452 | 7.1118 | 2.0666 | 170870.5491 | 66.3 | 571554.7406 | Load Shedding as per Standing Committee Approval | 200 | 71
18 | Jun | 2025-06-02 | XLXPPL | Load Shedding | All Block | All inverter | 15:30 | 16:00 | 0:30 | 0.49988 | 500.5703 | 0.25022 | 7.1118 | 6.8616 | 127159.4784 | 66.3 | 21095.4915 | Load Shedding as per Standing Committee Approval | 200 | 104
19 | Jun | 2025-06-02 | XLXPPL | Load Shedding | All Block | All inverter | 16:00 | 19:19 | 3:19 | 3.3158 | 237.1004 | 0.78619 | 7.1118 | 6.3256 | 10596.6232 | 66.3 | 5523.4122 | Load Shedding as per Standing Committee Approval | 200 | 192
20 | Jun | 2025-06-03 | XLXPPL | Load Shedding | All Block | All inverter | 6:14 | 9:00 | 2:46 | 2.766 | 239.9358 | 0.66366 | 6.8708 | 6.2071 | 10596.6232 | 66.3 | 4662.5676 | Load Shedding as per Standing Committee Approval | 200 | 192
21 | Jun | 2025-06-03 | XLXPPL | Load Shedding | All Block | All inverter | 9:00 | 9:30 | 0:30 | 0.49988 | 577.2423 | 0.28855 | 6.8708 | 6.5822 | 127159.4784 | 66.3 | 24326.6733 | Load Shedding as per Standing Committee Approval | 200 | 104
22 | Jun | 2025-06-03 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 812.6416 | 4.8746 | 6.8708 | 1.9961 | 170870.5491 | 66.3 | 552234.2827 | Load Shedding as per Standing Committee Approval | 200 | 71
23 | Jun | 2025-06-03 | XLXPPL | Load Shedding | All Block | All inverter | 15:30 | 16:00 | 0:30 | 0.49988 | 570.134 | 0.285 | 6.8708 | 6.5858 | 127159.4784 | 66.3 | 24027.1111 | Load Shedding as per Standing Committee Approval | 200 | 104
24 | Jun | 2025-06-03 | XLXPPL | Load Shedding | All Block | All inverter | 16:00 | 19:13 | 3:13 | 3.2159 | 231.8914 | 0.74573 | 6.8708 | 6.125 | 10596.6232 | 66.3 | 5239.1882 | Load Shedding as per Standing Committee Approval | 200 | 192
25 | Jun | 2025-06-04 | XLXPPL | Load Shedding | All Block | All inverter | 6:13 | 9:00 | 2:47 | 2.7826 | 274.1804 | 0.76295 | 7.2337 | 6.4707 | 10596.6232 | 66.3 | 5360.126 | Load Shedding as per Standing Committee Approval | 200 | 192
26 | Jun | 2025-06-04 | XLXPPL | Load Shedding | All Block | All inverter | 9:00 | 9:30 | 0:30 | 0.49988 | 615.8289 | 0.30784 | 7.2337 | 6.9258 | 127159.4784 | 66.3 | 25952.8253 | Load Shedding as per Standing Committee Approval | 200 | 104
27 | Jun | 2025-06-04 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 843.9783 | 5.0626 | 7.2337 | 2.1711 | 170870.5491 | 66.3 | 573529.248 | Load Shedding as per Standing Committee Approval | 200 | 71
28 | Jun | 2025-06-04 | XLXPPL | Load Shedding | All Block | All inverter | 15:30 | 16:00 | 0:30 | 0.49988 | 601.4898 | 0.30067 | 7.2337 | 6.933 | 127159.4784 | 66.3 | 25348.5349 | Load Shedding as per Standing Committee Approval | 200 | 104
29 | Jun | 2025-06-04 | XLXPPL | Load Shedding | All Block | All inverter | 16:00 | 19:13 | 3:13 | 3.2159 | 245.4033 | 0.78919 | 7.2337 | 6.4445 | 10596.6232 | 66.3 | 5544.4678 | Load Shedding as per Standing Committee Approval | 200 | 192
30 | Jun | 2025-06-05 | XLXPPL | Load Shedding | All Block | All inverter | 6:13 | 9:00 | 2:47 | 2.7826 | 252.6952 | 0.70316 | 7.2688 | 6.5656 | 10596.6232 | 66.3 | 4940.0984 | Load Shedding as per Standing Committee Approval | 200 | 192
31 | Jun | 2025-06-05 | XLXPPL | Load Shedding | All Block | All inverter | 9:00 | 9:30 | 0:30 | 0.49988 | 616.7591 | 0.3083 | 7.2688 | 6.9605 | 127159.4784 | 66.3 | 25992.0282 | Load Shedding as per Standing Committee Approval | 200 | 104
32 | Jun | 2025-06-05 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 858.5696 | 5.1501 | 7.2688 | 2.1186 | 170870.5491 | 66.3 | 583444.8316 | Load Shedding as per Standing Committee Approval | 200 | 71
33 | Jun | 2025-06-05 | XLXPPL | Load Shedding | All Block | All inverter | 15:30 | 16:00 | 0:30 | 0.49988 | 610.5654 | 0.30521 | 7.2688 | 6.9636 | 127159.4784 | 66.3 | 25731.0057 | Load Shedding as per Standing Committee Approval | 200 | 104
34 | Jun | 2025-06-05 | XLXPPL | Load Shedding | All Block | All inverter | 16:00 | 19:13 | 3:13 | 3.2159 | 246.1925 | 0.79172 | 7.2688 | 6.4771 | 10596.6232 | 66.3 | 5562.2983 | Load Shedding as per Standing Committee Approval | 200 | 192
35 | Jun | 2025-06-06 | XLXPPL | Load Shedding | All Block | All inverter | 6:12 | 9:00 | 2:48 | 2.7993 | 293.4409 | 0.82143 | 7.5049 | 6.6834 | 10596.6232 | 66.3 | 5771.0124 | Load Shedding as per Standing Committee Approval | 200 | 192
36 | Jun | 2025-06-06 | XLXPPL | Load Shedding | All Block | All inverter | 9:00 | 9:30 | 0:30 | 0.49988 | 657.4981 | 0.32867 | 7.5049 | 7.1762 | 127159.4784 | 66.3 | 27708.889 | Load Shedding as per Standing Committee Approval | 200 | 104
37 | Jun | 2025-06-06 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 872.3644 | 5.2329 | 7.5049 | 2.272 | 170870.5491 | 66.3 | 592819.156 | Load Shedding as per Standing Committee Approval | 200 | 71
38 | Jun | 2025-06-06 | XLXPPL | Load Shedding | All Block | All inverter | 15:30 | 16:00 | 0:30 | 0.49988 | 513.5654 | 0.25672 | 7.5049 | 7.2482 | 127159.4784 | 66.3 | 21643.1429 | Load Shedding as per Standing Committee Approval | 200 | 104
39 | Jun | 2025-06-06 | XLXPPL | Load Shedding | All Block | All inverter | 16:00 | 19:14 | 3:14 | 3.2325 | 295.3346 | 0.95468 | 7.5049 | 6.5502 | 10596.6232 | 66.3 | 6707.1524 | Load Shedding as per Standing Committee Approval | 200 | 192
40 | Jun | 2025-06-07 | XLXPPL | Load Shedding | All Block | All inverter | 6:11 | 9:00 | 2:49 | 2.816 | 297.3633 | 0.83737 | 7.6045 | 6.7672 | 10596.6232 | 66.3 | 5882.963 | Load Shedding as per Standing Committee Approval | 200 | 192
41 | Jun | 2025-06-07 | XLXPPL | Load Shedding | All Block | All inverter | 9:00 | 9:30 | 0:30 | 0.49988 | 648.1954 | 0.32402 | 7.6045 | 7.2805 | 127159.4784 | 66.3 | 27316.8461 | Load Shedding as per Standing Committee Approval | 200 | 104
42 | Jun | 2025-06-07 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 881.7825 | 5.2894 | 7.6045 | 2.3151 | 170870.5491 | 66.3 | 599219.298 | Load Shedding as per Standing Committee Approval | 200 | 71
43 | Jun | 2025-06-07 | XLXPPL | Load Shedding | All Block | All inverter | 15:30 | 16:00 | 0:30 | 0.49988 | 633.0279 | 0.31644 | 7.6045 | 7.2881 | 127159.4784 | 66.3 | 26677.6418 | Load Shedding as per Standing Committee Approval | 200 | 104
44 | Jun | 2025-06-07 | XLXPPL | Load Shedding | All Block | All inverter | 16:00 | 19:13 | 3:13 | 3.2159 | 256.9493 | 0.82632 | 7.6045 | 6.7782 | 10596.6232 | 66.3 | 5805.3298 | Load Shedding as per Standing Committee Approval | 200 | 192
45 | Jun | 2025-06-08 | XLXPPL | Load Shedding | All Block | All inverter | 6:18 | 9:00 | 2:42 | 2.6993 | 330.27 | 0.89151 | 7.75 | 6.8585 | 10596.6232 | 66.3 | 6263.3433 | Load Shedding as per Standing Committee Approval | 200 | 192
46 | Jun | 2025-06-08 | XLXPPL | Load Shedding | All Block | All inverter | 9:00 | 9:30 | 0:30 | 0.49988 | 676.31 | 0.33807 | 7.75 | 7.4119 | 127159.4784 | 66.3 | 28501.6753 | Load Shedding as per Standing Committee Approval | 200 | 104
47 | Jun | 2025-06-08 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 893.59 | 5.3602 | 7.75 | 2.3898 | 170870.5491 | 66.3 | 607243.1189 | Load Shedding as per Standing Committee Approval | 200 | 71
48 | Jun | 2025-06-08 | XLXPPL | Load Shedding | All Block | All inverter | 15:30 | 16:00 | 0:30 | 0.49988 | 643.69 | 0.32177 | 7.75 | 7.4282 | 127159.4784 | 66.3 | 27126.9734 | Load Shedding as per Standing Committee Approval | 200 | 104
49 | Jun | 2025-06-08 | XLXPPL | Load Shedding | All Block | All inverter | 16:00 | 19:32 | 3:32 | 3.5325 | 238.47 | 0.84239 | 7.75 | 6.9076 | 10596.6232 | 66.3 | 5918.228 | Load Shedding as per Standing Committee Approval | 200 | 192
50 | Jun | 2025-06-09 | XLXPPL | Load Shedding | All Block | All inverter | 6:11 | 9:00 | 2:49 | 2.816 | 303.2986 | 0.85408 | 7.6177 | 6.7636 | 10596.6232 | 66.3 | 6000.3854 | Load Shedding as per Standing Committee Approval | 200 | 192
51 | Jun | 2025-06-09 | XLXPPL | Load Shedding | All Block | All inverter | 9:00 | 9:30 | 0:30 | 0.49988 | 653.7842 | 0.32681 | 7.6177 | 7.2909 | 127159.4784 | 66.3 | 27552.371 | Load Shedding as per Standing Committee Approval | 200 | 104
52 | Jun | 2025-06-09 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 880.8266 | 5.2836 | 7.6177 | 2.334 | 170870.5491 | 66.3 | 598569.6722 | Load Shedding as per Standing Committee Approval | 200 | 71
53 | Jun | 2025-06-09 | XLXPPL | Load Shedding | All Block | All inverter | 15:30 | 16:00 | 0:30 | 0.49988 | 635.6868 | 0.31776 | 7.6177 | 7.2999 | 127159.4784 | 66.3 | 26789.6966 | Load Shedding as per Standing Committee Approval | 200 | 104
54 | Jun | 2025-06-09 | XLXPPL | Load Shedding | All Block | All inverter | 16:00 | 19:15 | 3:15 | 3.2492 | 253.4497 | 0.82351 | 7.6177 | 6.7942 | 10596.6232 | 66.3 | 5785.6015 | Load Shedding as per Standing Committee Approval | 200 | 192
55 | Jun | 2025-06-10 | XLXPPL | Load Shedding | All Block | All inverter | 6:10 | 9:00 | 2:50 | 2.8326 | 296.9036 | 0.84102 | 7.5036 | 6.6625 | 10596.6232 | 66.3 | 5908.6255 | Load Shedding as per Standing Committee Approval | 200 | 192
56 | Jun | 2025-06-10 | XLXPPL | Load Shedding | All Block | All inverter | 9:00 | 9:30 | 0:30 | 0.49988 | 639.7348 | 0.31979 | 7.5036 | 7.1838 | 127159.4784 | 66.3 | 26960.2907 | Load Shedding as per Standing Committee Approval | 200 | 104
57 | Jun | 2025-06-10 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 866.7197 | 5.199 | 7.5036 | 2.3045 | 170870.5491 | 66.3 | 588983.2556 | Load Shedding as per Standing Committee Approval | 200 | 71
58 | Jun | 2025-06-10 | XLXPPL | Load Shedding | All Block | All inverter | 15:30 | 16:00 | 0:30 | 0.49988 | 630.8251 | 0.31533 | 7.5036 | 7.1882 | 127159.4784 | 66.3 | 26584.8103 | Load Shedding as per Standing Committee Approval | 200 | 104
59 | Jun | 2025-06-10 | XLXPPL | Load Shedding | All Block | All inverter | 16:00 | 19:16 | 3:16 | 3.2659 | 250.6223 | 0.8185 | 7.5036 | 6.6851 | 10596.6232 | 66.3 | 5750.3972 | Load Shedding as per Standing Committee Approval | 200 | 192
60 | Jun | 2025-06-11 | XLXPPL | Load Shedding | All Block | All inverter | 6:10 | 9:00 | 2:50 | 2.8326 | 313.7594 | 0.88876 | 7.6709 | 6.7821 | 10596.6232 | 66.3 | 6244.07 | Load Shedding as per Standing Committee Approval | 200 | 192
61 | Jun | 2025-06-11 | XLXPPL | Load Shedding | All Block | All inverter | 9:00 | 9:30 | 0:30 | 0.49988 | 638.1226 | 0.31898 | 7.6709 | 7.3519 | 127159.4784 | 66.3 | 26892.3469 | Load Shedding as per Standing Committee Approval | 200 | 104
62 | Jun | 2025-06-11 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 882.1257 | 5.2914 | 7.6709 | 2.3794 | 170870.5491 | 66.3 | 599452.472 | Load Shedding as per Standing Committee Approval | 200 | 71
63 | Jun | 2025-06-11 | XLXPPL | Load Shedding | All Block | All inverter | 15:30 | 16:00 | 0:30 | 0.49988 | 652.6522 | 0.32625 | 7.6709 | 7.3446 | 127159.4784 | 66.3 | 27504.6651 | Load Shedding as per Standing Committee Approval | 200 | 104
64 | Jun | 2025-06-11 | XLXPPL | Load Shedding | All Block | All inverter | 16:00 | 19:18 | 3:18 | 3.2992 | 254.8905 | 0.84093 | 7.6709 | 6.8299 | 10596.6232 | 66.3 | 5908.0054 | Load Shedding as per Standing Committee Approval | 200 | 192
65 | Jun | 2025-06-12 | XLXPPL | Load Shedding | All Block | All inverter | 6:10 | 9:00 | 2:50 | 2.8326 | 304.8335 | 0.86348 | 7.5953 | 6.7318 | 10596.6232 | 66.3 | 6066.4376 | Load Shedding as per Standing Committee Approval | 200 | 192
66 | Jun | 2025-06-12 | XLXPPL | Load Shedding | All Block | All inverter | 9:00 | 9:30 | 0:30 | 0.49988 | 656.1457 | 0.32799 | 7.5953 | 7.2673 | 127159.4784 | 66.3 | 27651.8944 | Load Shedding as per Standing Committee Approval | 200 | 104
67 | Jun | 2025-06-12 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 875.7201 | 5.253 | 7.5953 | 2.3422 | 170870.5491 | 66.3 | 595099.5663 | Load Shedding as per Standing Committee Approval | 200 | 71
68 | Jun | 2025-06-12 | XLXPPL | Load Shedding | All Block | All inverter | 15:30 | 16:00 | 0:30 | 0.49988 | 639.0318 | 0.31944 | 7.5953 | 7.2758 | 127159.4784 | 66.3 | 26930.6632 | Load Shedding as per Standing Committee Approval | 200 | 104
69 | Jun | 2025-06-12 | XLXPPL | Load Shedding | All Block | All inverter | 16:00 | 19:14 | 3:14 | 3.2325 | 254.1486 | 0.82154 | 7.5953 | 6.7737 | 10596.6232 | 66.3 | 5771.8025 | Load Shedding as per Standing Committee Approval | 200 | 192
70 | Jun | 2025-06-13 | XLXPPL | Load Shedding | All Block | All inverter | 6:10 | 9:00 | 2:50 | 2.8326 | 291.7642 | 0.82646 | 7.1236 | 6.2972 | 10596.6232 | 66.3 | 5806.3466 | Load Shedding as per Standing Committee Approval | 200 | 192
71 | Jun | 2025-06-13 | XLXPPL | Load Shedding | All Block | All inverter | 9:00 | 9:30 | 0:30 | 0.49988 | 632.6728 | 0.31626 | 7.1236 | 6.8074 | 127159.4784 | 66.3 | 26662.6755 | Load Shedding as per Standing Committee Approval | 200 | 104
72 | Jun | 2025-06-13 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 841.4585 | 5.0475 | 7.1236 | 2.0761 | 170870.5491 | 66.3 | 571816.8944 | Load Shedding as per Standing Committee Approval | 200 | 71
73 | Jun | 2025-06-13 | XLXPPL | Load Shedding | All Block | All inverter | 15:30 | 16:00 | 0:30 | 0.49988 | 437.9906 | 0.21894 | 7.1236 | 6.9047 | 127159.4784 | 66.3 | 18458.2015 | Load Shedding as per Standing Committee Approval | 200 | 104
74 | Jun | 2025-06-13 | XLXPPL | Load Shedding | All Block | All inverter | 16:00 | 19:21 | 3:21 | 3.3492 | 214.4347 | 0.71818 | 7.1236 | 6.4055 | 10596.6232 | 66.3 | 5045.6045 | Load Shedding as per Standing Committee Approval | 200 | 192
75 | Jun | 2025-06-14 | XLXPPL | Load Shedding | All Block | All inverter | 6:26 | 9:00 | 2:34 | 2.566 | 97.3558 | 0.24982 | 1.4336 | 1.1838 | 10596.6232 | 66.3 | 1755.1111 | Load Shedding as per Standing Committee Approval | 200 | 192
76 | Jun | 2025-06-14 | XLXPPL | Load Shedding | All Block | All inverter | 9:00 | 9:30 | 0:30 | 0.49988 | 267.3639 | 0.13365 | 1.4336 | 1.3 | 127159.4784 | 66.3 | 11267.4947 | Load Shedding as per Standing Committee Approval | 200 | 104
77 | Jun | 2025-06-14 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 103.2448 | 0.61932 | 1.4336 | 0.81429 | 170870.5491 | 66.3 | 70160.4766 | Load Shedding as per Standing Committee Approval | 200 | 71
78 | Jun | 2025-06-14 | XLXPPL | Load Shedding | All Block | All inverter | 15:30 | 16:00 | 0:30 | 0.49988 | 83.7576 | 0.041868 | 1.4336 | 1.3917 | 127159.4784 | 66.3 | 3529.7882 | Load Shedding as per Standing Committee Approval | 200 | 104
79 | Jun | 2025-06-14 | XLXPPL | Load Shedding | All Block | All inverter | 16:00 | 19:13 | 3:13 | 3.2159 | 118.2199 | 0.38018 | 1.4336 | 1.0534 | 10596.6232 | 66.3 | 2670.9748 | Load Shedding as per Standing Committee Approval | 200 | 192
80 | Jun | 2025-06-15 | XLXPPL | Load Shedding | All Block | All inverter | 7:20 | 9:00 | 1:40 | 1.6663 | 41.259 | 0.068748 | 1.9129 | 1.8442 | 10596.6232 | 66.3 | 482.993 | Load Shedding as per Standing Committee Approval | 200 | 192
81 | Jun | 2025-06-15 | XLXPPL | Load Shedding | All Block | All inverter | 9:00 | 9:30 | 0:30 | 0.49988 | 52.3348 | 0.026161 | 1.9129 | 1.8868 | 127159.4784 | 66.3 | 2205.5427 | Load Shedding as per Standing Committee Approval | 200 | 104
82 | Jun | 2025-06-15 | XLXPPL | Load Shedding | All Block | All inverter | 9:30 | 15:30 | 6:00 | 5.9985 | 204.045 | 1.224 | 1.9129 | 0.68897 | 170870.5491 | 66.3 | 138659.6915 | Load Shedding as per Standing Committee Approval | 200 | 71
83 | Jun | 2025-06-15 | XLXPPL | Load Shedding | All Block | All inverter | 15:30 | 16:00 | 0:30 | 0.49988 | 225.8452 | 0.11289 | 1.9129 | 1.8 | 127159.4784 | 66.3 | 9517.7736 | Load Shedding as per Standing Committee Approval | 200 | 104
84 | Jun | 2025-06-15 | XLXPPL | Load Shedding | All Block | All inverter | 16:00 | 19:14 | 3:14 | 3.2325 | 143.9557 | 0.46534 | 1.9129 | 1.4476 | 10596.6232 | 66.3 | 3269.2852 | Load Shedding as per Standing Committee Approval | 200 | 192
85 | Jun | 2025-06-16 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 493.4795 | 1.9734 | 3.4422 | 1.4688 | 111264.72 | 66.3 | 145576.8976 | Load Shedding as per Standing Committee Approval | 200 | 116
86 | Jun | 2025-06-17 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 767.1483 | 3.0678 | 5.7667 | 2.6988 | 111264.72 | 66.3 | 226309.4319 | Load Shedding as per Standing Committee Approval | 200 | 116
87 | Jun | 2025-06-18 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 911.5374 | 3.6452 | 7.2151 | 3.5699 | 111264.72 | 66.3 | 268904.329 | Load Shedding as per Standing Committee Approval | 200 | 116
88 | Jun | 2025-06-19 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 901.6294 | 3.6056 | 7.3007 | 3.6951 | 111264.72 | 66.3 | 265981.4776 | Load Shedding as per Standing Committee Approval | 200 | 116
89 | Jun | 2025-06-20 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 840.3583 | 3.3606 | 6.336 | 2.9754 | 100832.8882 | 66.3 | 224663.4951 | Load Shedding as per Standing Committee Approval | 200 | 116
90 | Jun | 2025-06-21 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 412.7936 | 1.6508 | 3.4181 | 1.7673 | 100832.8882 | 66.3 | 110357.2867 | Load Shedding as per Standing Committee Approval | 200 | 116
91 | Jun | 2025-06-22 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 878.482 | 3.5131 | 6.8287 | 3.3156 | 100832.8882 | 66.3 | 234855.5959 | Load Shedding as per Standing Committee Approval | 200 | 116
92 | Jun | 2025-06-23 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 814.6993 | 3.258 | 5.9192 | 2.6613 | 100832.8882 | 66.3 | 217803.7562 | Load Shedding as per Standing Committee Approval | 200 | 116
93 | Jun | 2025-06-25 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 846.8083 | 3.3864 | 6.0842 | 2.6978 | 100832.8882 | 66.3 | 226387.8567 | Load Shedding as per Standing Committee Approval | 200 | 116
94 | Jun | 2025-06-26 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 12:15 | 1:45 | 1.7496 | 680.9152 | 1.1913 | 5.5484 | 4.3571 | 111264.72 | 66.3 | 87880.8793 | Load Shedding as per Standing Committee Approval | 200 | 116
95 | Jun | 2025-06-27 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 12:35 | 2:05 | 2.0828 | 488.7283 | 1.0179 | 4.0081 | 2.9902 | 111264.72 | 66.3 | 75091.2953 | Load Shedding as per Standing Committee Approval | 200 | 116
96 | Jun | 2025-06-28 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 10:50 | 0:20 | 0.33325 | 624.03 | 0.20796 | 4.3544 | 4.1464 | 111264.72 | 66.3 | 15340.7822 | Load Shedding as per Standing Committee Approval | 200 | 116
97 | Jul | 2025-07-01 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 665.6425 | 0.16637 | 6.0782 | 5.9119 | 20959.6453 | 78.14 | 2724.7755 | Load Shedding as per Standing Committee Approval | 200 | 182.61
98 | Jul | 2025-07-01 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 804.8785 | 3.2187 | 6.0782 | 2.8595 | 109113.0931 | 78.14 | 274430.8456 | Load Shedding as per Standing Committee Approval | 200 | 109.47
99 | Jul | 2025-07-01 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 696.4182 | 0.17406 | 6.0782 | 5.9042 | 20959.6453 | 78.14 | 2850.7542 | Load Shedding as per Standing Committee Approval | 200 | 182.61
100 | Jul | 2025-07-02 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 361.3042 | 0.090304 | 3.5404 | 3.4501 | 293476.5 | 78.14 | 20708.665 | Load Shedding as per Standing Committee Approval | 400 | 182.61
101 | Jul | 2025-07-02 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 310.2494 | 1.2407 | 3.5404 | 2.2997 | 392215.5 | 78.14 | 380243.1834 | Load Shedding as per Standing Committee Approval | 400 | 109.47
102 | Jul | 2025-07-02 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 388.9549 | 0.097215 | 3.5404 | 3.4431 | 23476.5 | 78.14 | 1783.3571 | Load Shedding as per Standing Committee Approval | 400 | 382.61
103 | Jul | 2025-07-03 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 835.1528 | 0.20874 | 3.1357 | 2.9269 | 293476.5 | 78.14 | 47867.9678 | Load Shedding as per Standing Committee Approval | 400 | 182.61
104 | Jul | 2025-07-03 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 430.0488 | 1.7198 | 3.1357 | 1.4159 | 392215.5 | 78.14 | 527069.9352 | Load Shedding as per Standing Committee Approval | 400 | 109.47
105 | Jul | 2025-07-03 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 16.8209 | 0.0042042 | 3.1357 | 3.1314 | 23476.5 | 78.14 | 77.1236 | Load Shedding as per Standing Committee Approval | 400 | 382.61
106 | Jul | 2025-07-04 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 613.5468 | 0.15335 | 5.6918 | 5.5384 | 181520.65 | 78.14 | 21751.0121 | Load Shedding as per Standing Committee Approval | 400 | 182.61
107 | Jul | 2025-07-04 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 806.0225 | 3.2233 | 5.6918 | 2.4685 | 242592.55 | 78.14 | 611012.8463 | Load Shedding as per Standing Committee Approval | 400 | 109.47
108 | Jul | 2025-07-04 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 431.3606 | 0.10781 | 5.6918 | 5.584 | 16190.65 | 78.14 | 1363.9877 | Load Shedding as per Standing Committee Approval | 400 | 382.61
109 | Jul | 2025-07-05 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 839.0223 | 0.2097 | 6.4543 | 6.2446 | 181520.65 | 78.14 | 29744.4027 | Load Shedding as per Standing Committee Approval | 400 | 182.61
110 | Jul | 2025-07-05 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 839.5558 | 3.3574 | 6.4543 | 3.0969 | 242592.55 | 78.14 | 636433.0826 | Load Shedding as per Standing Committee Approval | 400 | 109.47
111 | Jul | 2025-07-05 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 846.7792 | 0.21164 | 6.4543 | 6.2427 | 16190.65 | 78.14 | 2677.5661 | Load Shedding as per Standing Committee Approval | 400 | 382.61
112 | Jul | 2025-07-06 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 538.6407 | 0.13463 | 5.761 | 5.6264 | 181520.65 | 78.14 | 19095.4942 | Load Shedding as per Standing Committee Approval | 400 | 182.61
113 | Jul | 2025-07-06 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 788.165 | 3.1519 | 5.761 | 2.6091 | 242592.55 | 78.14 | 597475.7666 | Load Shedding as per Standing Committee Approval | 400 | 109.47
114 | Jul | 2025-07-06 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 724.6695 | 0.18112 | 5.761 | 5.5799 | 16190.65 | 78.14 | 2291.4478 | Load Shedding as per Standing Committee Approval | 400 | 382.61
115 | Jul | 2025-07-07 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 426.1075 | 0.1065 | 5.6344 | 5.5279 | 181520.65 | 78.14 | 15106.0523 | Load Shedding as per Standing Committee Approval | 400 | 182.61
116 | Jul | 2025-07-07 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 827.7138 | 3.31 | 5.6344 | 2.3244 | 242592.55 | 78.14 | 627456.1094 | Load Shedding as per Standing Committee Approval | 400 | 109.47
117 | Jul | 2025-07-07 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 744.5371 | 0.18609 | 5.6344 | 5.4483 | 16190.65 | 78.14 | 2354.2706 | Load Shedding as per Standing Committee Approval | 400 | 382.61
118 | Jul | 2025-07-08 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 637.5083 | 0.15934 | 4.6055 | 4.4462 | 181520.65 | 78.14 | 22600.4766 | Load Shedding as per Standing Committee Approval | 400 | 182.61
119 | Jul | 2025-07-08 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 596.23 | 2.3843 | 4.6055 | 2.2212 | 242592.55 | 78.14 | 451977.6958 | Load Shedding as per Standing Committee Approval | 400 | 109.47
120 | Jul | 2025-07-08 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 439.8793 | 0.10994 | 4.6055 | 4.4956 | 16190.65 | 78.14 | 1390.9245 | Load Shedding as per Standing Committee Approval | 400 | 382.61
121 | Jul | 2025-07-09 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 404.7942 | 0.10117 | 5.3991 | 5.298 | 181520.65 | 78.14 | 14350.4657 | Load Shedding as per Standing Committee Approval | 400 | 182.61
122 | Jul | 2025-07-09 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 593.9886 | 2.3754 | 5.3991 | 3.0238 | 242592.55 | 78.14 | 450278.5511 | Load Shedding as per Standing Committee Approval | 400 | 109.47
123 | Jul | 2025-07-09 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 800.2188 | 0.20001 | 5.3991 | 5.1991 | 16190.65 | 78.14 | 2530.3392 | Load Shedding as per Standing Committee Approval | 400 | 382.61
124 | Jul | 2025-07-10 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 597.2194 | 0.14927 | 5.5468 | 5.3975 | 181520.65 | 78.14 | 21172.186 | Load Shedding as per Standing Committee Approval | 400 | 182.61
125 | Jul | 2025-07-10 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 674.9318 | 2.6991 | 5.5468 | 2.8477 | 242592.55 | 78.14 | 511638.339 | Load Shedding as per Standing Committee Approval | 400 | 109.47
126 | Jul | 2025-07-10 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 858.0698 | 0.21446 | 5.5468 | 5.3323 | 16190.65 | 78.14 | 2713.2677 | Load Shedding as per Standing Committee Approval | 400 | 382.61
127 | Jul | 2025-07-11 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 771.2696 | 0.19277 | 6.0011 | 5.8083 | 181520.65 | 78.14 | 27342.4843 | Load Shedding as per Standing Committee Approval | 400 | 182.61
128 | Jul | 2025-07-11 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 788.8423 | 3.1546 | 6.0011 | 2.8465 | 242592.55 | 78.14 | 597989.214 | Load Shedding as per Standing Committee Approval | 400 | 109.47
129 | Jul | 2025-07-11 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 363.5765 | 0.090872 | 6.0011 | 5.9102 | 16190.65 | 78.14 | 1149.6505 | Load Shedding as per Standing Committee Approval | 400 | 382.61
130 | Jul | 2025-07-12 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 846.081 | 0.21147 | 6.0546 | 5.8431 | 181520.65 | 78.14 | 29994.6417 | Load Shedding as per Standing Committee Approval | 400 | 182.61
131 | Jul | 2025-07-12 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 642.8131 | 2.5706 | 6.0546 | 3.4839 | 242592.55 | 78.14 | 487290.4103 | Load Shedding as per Standing Committee Approval | 400 | 109.47
132 | Jul | 2025-07-12 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 374.3733 | 0.09357 | 6.0546 | 5.961 | 16190.65 | 78.14 | 1183.7905 | Load Shedding as per Standing Committee Approval | 400 | 382.61
133 | Jul | 2025-07-13 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 748.1875 | 0.187 | 7.1413 | 6.9543 | 181520.65 | 78.14 | 26524.1949 | Load Shedding as per Standing Committee Approval | 400 | 182.61
134 | Jul | 2025-07-13 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 894.4651 | 3.577 | 7.1413 | 3.5643 | 242592.55 | 78.14 | 678057.6 | Load Shedding as per Standing Committee Approval | 400 | 109.47
135 | Jul | 2025-07-13 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 553.3188 | 0.1383 | 7.1413 | 7.003 | 16190.65 | 78.14 | 1749.6267 | Load Shedding as per Standing Committee Approval | 400 | 382.61
136 | Jul | 2025-07-14 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 734.075 | 0.18347 | 5.7248 | 5.5413 | 181520.65 | 78.14 | 26023.8889 | Load Shedding as per Standing Committee Approval | 400 | 182.61
137 | Jul | 2025-07-14 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 760.5527 | 3.0415 | 5.7248 | 2.6833 | 242592.55 | 78.14 | 576544.0266 | Load Shedding as per Standing Committee Approval | 400 | 109.47
138 | Jul | 2025-07-14 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 342.975 | 0.085722 | 5.7248 | 5.6391 | 16190.65 | 78.14 | 1084.5073 | Load Shedding as per Standing Committee Approval | 400 | 382.61
139 | Jul | 2025-07-15 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 762.0964 | 0.19048 | 5.2576 | 5.0671 | 181520.65 | 78.14 | 27017.2834 | Load Shedding as per Standing Committee Approval | 400 | 182.61
140 | Jul | 2025-07-15 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 707.8862 | 2.8308 | 5.2576 | 2.4268 | 242592.55 | 78.14 | 536619.7223 | Load Shedding as per Standing Committee Approval | 400 | 109.47
141 | Jul | 2025-07-15 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 391.0974 | 0.09775 | 5.2576 | 5.1599 | 16190.65 | 78.14 | 1236.6733 | Load Shedding as per Standing Committee Approval | 400 | 382.61
142 | Jul | 2025-07-16 | XLXPPL | Load Shedding | All Block | All inverter | 6:39 | 10:15 | 3:36 | 3.5991 | 249.9731 | 0.89968 | 6.2096 | 5.3099 | 181756 | 78.14 | 127776.2812 | Load Shedding as per Standing Committee Approval | 400 | 200
143 | Jul | 2025-07-16 | XLXPPL | Load Shedding | All Block | All inverter | 10:15 | 10:30 | 0:15 | 0.24994 | 775.6573 | 0.19387 | 6.2096 | 6.0158 | 50519.0802 | 78.14 | 7652.9886 | Load Shedding as per Standing Committee Approval | 400 | 344.41
144 | Jul | 2025-07-16 | XLXPPL | Load Shedding | All Block | All inverter | 10:30 | 14:30 | 4:00 | 3.999 | 813.448 | 3.253 | 6.2096 | 2.9566 | 186830.5673 | 78.14 | 474901.4115 | Load Shedding as per Standing Committee Approval | 400 | 194.21
145 | Jul | 2025-07-16 | XLXPPL | Load Shedding | All Block | All inverter | 14:30 | 14:45 | 0:15 | 0.24994 | 830.1207 | 0.20748 | 6.2096 | 6.0021 | 50519.0802 | 78.14 | 8190.3485 | Load Shedding as per Standing Committee Approval | 400 | 344.41
146 | Jul | 2025-07-16 | XLXPPL | Load Shedding | All Block | All inverter | 14:45 | 19:16 | 4:31 | 4.5155 | 365.3406 | 1.6497 | 6.2096 | 4.5599 | 181756 | 78.14 | 234298.987 | Load Shedding as per Standing Committee Approval | 400 | 200
147 | [17 empty] | Load Shedding as per Standing Committee Approval
148 | [17 empty] | Load Shedding as per Standing Committee Approval
149 | [17 empty] | Load Shedding as per Standing Committee Approval
150 | [17 empty] | Load Shedding as per Standing Committee Approval
151 | [17 empty] | Load Shedding as per Standing Committee Approval
152 | [17 empty] | Load Shedding as per Standing Committee Approval
153 | [17 empty] | Load Shedding as per Standing Committee Approval
154 | [17 empty] | Load Shedding as per Standing Committee Approval
155 | [17 empty] | Load Shedding as per Standing Committee Approval
156 | [17 empty] | Load Shedding as per Standing Committee Approval
157 | [17 empty] | Load Shedding as per Standing Committee Approval
158 | [17 empty] | Load Shedding as per Standing Committee Approval
159 | [17 empty] | Load Shedding as per Standing Committee Approval
160 | [17 empty] | Load Shedding as per Standing Committee Approval
161 | [17 empty] | Load Shedding as per Standing Committee Approval
162 | [17 empty] | Load Shedding as per Standing Committee Approval
163 | [17 empty] | Load Shedding as per Standing Committee Approval
164 | [17 empty] | Load Shedding as per Standing Committee Approval
165 | [17 empty] | Load Shedding as per Standing Committee Approval
166 | [17 empty] | Load Shedding as per Standing Committee Approval
167 | [17 empty] | Load Shedding as per Standing Committee Approval
168 | [17 empty] | Load Shedding as per Standing Committee Approval
169 | [17 empty] | Load Shedding as per Standing Committee Approval
170 | [17 empty] | Load Shedding as per Standing Committee Approval
171 | [17 empty] | Load Shedding as per Standing Committee Approval
172 | [17 empty] | Load Shedding as per Standing Committee Approval
173 | [17 empty] | Load Shedding as per Standing Committee Approval
174 | [17 empty] | Load Shedding as per Standing Committee Approval
175 | [17 empty] | Load Shedding as per Standing Committee Approval
176 | [17 empty] | Load Shedding as per Standing Committee Approval
177 | [17 empty] | Load Shedding as per Standing Committee Approval
178 | [17 empty] | Load Shedding as per Standing Committee Approval
179 | [17 empty] | Load Shedding as per Standing Committee Approval
180 | [17 empty] | Load Shedding as per Standing Committee Approval
181 | [17 empty] | Load Shedding as per Standing Committee Approval
182 | [17 empty] | Load Shedding as per Standing Committee Approval
183 | [17 empty] | Load Shedding as per Standing Committee Approval
184 | [17 empty] | Load Shedding as per Standing Committee Approval
185 | [17 empty] | Load Shedding as per Standing Committee Approval
186 | [17 empty] | Load Shedding as per Standing Committee Approval
187 | [17 empty] | Load Shedding as per Standing Committee Approval
188 | [17 empty] | Load Shedding as per Standing Committee Approval
189 | [17 empty] | Load Shedding as per Standing Committee Approval
190 | [17 empty] | Load Shedding as per Standing Committee Approval
191 | [17 empty] | Load Shedding as per Standing Committee Approval
192 | [17 empty] | Load Shedding as per Standing Committee Approval
193 | [17 empty] | Load Shedding as per Standing Committee Approval
194 | [17 empty] | Load Shedding as per Standing Committee Approval
195 | [17 empty] | Load Shedding as per Standing Committee Approval
196 | [17 empty] | Load Shedding as per Standing Committee Approval
197 | [17 empty] | Load Shedding as per Standing Committee Approval
198 | [17 empty] | Load Shedding as per Standing Committee Approval
199 | [17 empty] | Load Shedding as per Standing Committee Approval
200 | [17 empty] | Load Shedding as per Standing Committee Approval
201 | [17 empty] | Load Shedding as per Standing Committee Approval
202 | [17 empty] | Load Shedding as per Standing Committee Approval
203 | [17 empty] | Load Shedding as per Standing Committee Approval
204 | [17 empty] | Load Shedding as per Standing Committee Approval
205 | [17 empty] | Load Shedding as per Standing Committee Approval
206 | [17 empty] | Load Shedding as per Standing Committee Approval
207 | [17 empty] | Load Shedding as per Standing Committee Approval
208 | [17 empty] | Load Shedding as per Standing Committee Approval
209 | [17 empty] | Load Shedding as per Standing Committee Approval
210 | [17 empty] | Load Shedding as per Standing Committee Approval
211 | [17 empty] | Load Shedding as per Standing Committee Approval
212 | [17 empty] | Load Shedding as per Standing Committee Approval
213 | [17 empty] | Load Shedding as per Standing Committee Approval
214 | [17 empty] | Load Shedding as per Standing Committee Approval
215 | [17 empty] | Load Shedding as per Standing Committee Approval
216 | [17 empty] | Load Shedding as per Standing Committee Approval
217 | [17 empty] | Load Shedding as per Standing Committee Approval
218 | [17 empty] | Load Shedding as per Standing Committee Approval
219 | [17 empty] | Load Shedding as per Standing Committee Approval
220 | [17 empty] | Load Shedding as per Standing Committee Approval
221 | [17 empty] | Load Shedding as per Standing Committee Approval
222 | [17 empty] | Load Shedding as per Standing Committee Approval
223 | [17 empty] | Load Shedding as per Standing Committee Approval
224 | [17 empty] | Load Shedding as per Standing Committee Approval
225 | [17 empty] | Load Shedding as per Standing Committee Approval
226 | [17 empty] | Load Shedding as per Standing Committee Approval
227 | [17 empty] | Load Shedding as per Standing Committee Approval
228 | [17 empty] | Load Shedding as per Standing Committee Approval
229 | [17 empty] | Load Shedding as per Standing Committee Approval
230 | [17 empty] | Load Shedding as per Standing Committee Approval
231 | [17 empty] | Load Shedding as per Standing Committee Approval
232 | [17 empty] | Load Shedding as per Standing Committee Approval
233 | [17 empty] | Load Shedding as per Standing Committee Approval
234 | [17 empty] | Load Shedding as per Standing Committee Approval
235 | [17 empty] | Load Shedding as per Standing Committee Approval
236 | [17 empty] | Load Shedding as per Standing Committee Approval
237 | [17 empty] | Load Shedding as per Standing Committee Approval
238 | [17 empty] | Load Shedding as per Standing Committee Approval
239 | [17 empty] | Load Shedding as per Standing Committee Approval
240 | [17 empty] | Load Shedding as per Standing Committee Approval
241 | [17 empty] | Load Shedding as per Standing Committee Approval
242 | [17 empty] | Load Shedding as per Standing Committee Approval
243 | [17 empty] | Load Shedding as per Standing Committee Approval
244 | [17 empty] | Load Shedding as per Standing Committee Approval
245 | [17 empty] | Load Shedding as per Standing Committee Approval
246 | [17 empty] | Load Shedding as per Standing Committee Approval
247 | [17 empty] | Load Shedding as per Standing Committee Approval
248 | [17 empty] | Load Shedding as per Standing Committee Approval
249 | [17 empty] | Load Shedding as per Standing Committee Approval
250 | [17 empty] | Load Shedding as per Standing Committee Approval
251 | [17 empty] | Load Shedding as per Standing Committee Approval
252 | [17 empty] | Load Shedding as per Standing Committee Approval
253 | [17 empty] | Load Shedding as per Standing Committee Approval
254 | [17 empty] | Load Shedding as per Standing Committee Approval
255 | [17 empty] | Load Shedding as per Standing Committee Approval
256 | [17 empty] | Load Shedding as per Standing Committee Approval
257 | [17 empty] | Load Shedding as per Standing Committee Approval
258 | [17 empty] | Load Shedding as per Standing Committee Approval
259 | [17 empty] | Load Shedding as per Standing Committee Approval
260 | [17 empty] | Load Shedding as per Standing Committee Approval
261 | [17 empty] | Load Shedding as per Standing Committee Approval
262 | [17 empty] | Load Shedding as per Standing Committee Approval
263 | [17 empty] | Load Shedding as per Standing Committee Approval
264 | [17 empty] | Load Shedding as per Standing Committee Approval
265 | [17 empty] | Load Shedding as per Standing Committee Approval
266 | [17 empty] | Load Shedding as per Standing Committee Approval
267 | [17 empty] | Load Shedding as per Standing Committee Approval
268 | [17 empty] | Load Shedding as per Standing Committee Approval
269 | [17 empty] | Load Shedding as per Standing Committee Approval
270 | [17 empty] | Load Shedding as per Standing Committee Approval
271 | [17 empty] | Load Shedding as per Standing Committee Approval
272 | [17 empty] | Load Shedding as per Standing Committee Approval
273 | [17 empty] | Load Shedding as per Standing Committee Approval
274 | [17 empty] | Load Shedding as per Standing Committee Approval
275 | [17 empty] | Load Shedding as per Standing Committee Approval
276 | [17 empty] | Load Shedding as per Standing Committee Approval
277 | [17 empty] | Load Shedding as per Standing Committee Approval
278 | [17 empty] | Load Shedding as per Standing Committee Approval
279 | [17 empty] | Load Shedding as per Standing Committee Approval
280 | [17 empty] | Load Shedding as per Standing Committee Approval
281 | [17 empty] | Load Shedding as per Standing Committee Approval
282 | [17 empty] | Load Shedding as per Standing Committee Approval
283 | [17 empty] | Load Shedding as per Standing Committee Approval
284 | [17 empty] | Load Shedding as per Standing Committee Approval
285 | [17 empty] | Load Shedding as per Standing Committee Approval
286 | [17 empty] | Load Shedding as per Standing Committee Approval
[13 empty] | 59673.8 | 0.99456

## Modelling New
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | CC*Bugt (MTD) | CC*Bugt (YTD)
1 | April | 4 | 2025-04-01 | 2025 | FY26 | 30 | 209.7 | 216.8 |  | 31.6 |  | 0 | 0 |  | 7.2267 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 99.75% | 99.75%
2 | May | 5 | 2025-05-01 | 2025 | FY26 | 31 | 221.5 | 218.1 |  | 34 |  | 34604.2459 | 270 | 58.76% | 7.0355 | 13 | 91.4613 | 91.4613 | 1116.266 | 14511.4579 | 14511.4579 | 17.23% | 17.23% | 17.23% | 137.763 | 137.763 |  |  |  | 99.75% | 99.75%
3 | June | 6 | 2025-06-01 | 2025 | FY26 | 30 | 200.7 | 193.7 |  | 33.4 |  | 34672.0237 | 270 | 66.3% | 6.4567 | 30 | 193.7 | 285.1613 | 1155.7341 | 34672.0237 | 49183.4816 | 17.84% | 17.84% | 17.65% | 252.9849 | 195.3739 |  |  |  | 99.75% | 99.75%
4 | July | 7 | 2025-07-01 | 2025 | FY26 | 31 | 170.2 | 166 |  | 31.1 |  | 70045.5917 | 540 | 78.14% | 5.3548 | 16 | 85.6774 | 370.8387 | 2259.5352 | 36152.5635 | 85336.0451 | 17.43% | 17.43% | 11.16% | 177.5578 | 189.4352 |  |  |  | 99.75% | 99.75%
5 | August | 8 | 2025-08-01 | 2025 | FY26 | 31 | 168.6 | 170.2 |  | 29.7 |  | 64192.239 | 540 | 69.84% | 5.4903 | 0 | 0 | 370.8387 | 2070.7174 | 0 | 85336.0451 | 15.98% |  | 11.16% | 0 | 142.0764 |  |  |  | 99.75% | 99.75%
6 | September | 9 | 2025-09-01 | 2025 | FY26 | 30 | 176.9 | 188.9 |  | 30 |  | 75901.7459 | 540 | 74.41% | 6.2967 | 0 | 0 | 370.8387 | 2530.0582 | 0 | 85336.0451 | 19.52% |  | 11.16% | 0 | 113.6611 |  |  |  | 99.75% | 99.75%
7 | October | 10 | 2025-10-01 | 2025 | FY26 | 31 | 173.4 | 200 |  | 28.7 |  | 91487.6017 | 540 | 84.71% | 6.4516 | 0 | 0 | 370.8387 | 2951.213 | 0 | 85336.0451 | 22.77% |  | 11.16% | 0 | 94.7176 |  |  |  | 99.75% | 99.75%
8 | November | 11 | 2025-11-01 | 2025 | FY26 | 30 | 134.7 | 163.9 |  | 23.1 |  | 75428.9864 | 540 | 85.22% | 5.4633 | 0 | 0 | 370.8387 | 2514.2995 | 0 | 85336.0451 | 19.4% |  | 11.16% | 0 | 81.1865 |  |  |  | 99.75% | 99.75%
9 | December | 12 | 2025-12-01 | 2025 | FY26 | 31 | 125.9 | 160 |  | 17.79 |  | 77842.5397 | 540 | 90.1% | 5.1613 | 0 | 0 | 370.8387 | 2511.0497 | 0 | 85336.0451 | 19.38% |  | 11.16% | 0 | 71.0382 |  |  |  | 99.75% | 99.75%
10 | January | 1 | 2026-01-01 | 2026 | FY26 | 31 | 134 | 168.3 |  | 16.2 |  | 82032.5731 | 540 | 90.26% | 5.429 | 0 | 0 | 370.8387 | 2646.212 | 0 | 85336.0451 | 20.42% |  | 11.16% | 0 | 63.1451 |  |  |  | 99.75% | 99.75%
11 | February | 2 | 2026-02-01 | 2026 | FY26 | 28 | 147 | 173.6 |  | 20.2 |  | 73703.5619 | 540 | 78.62% | 6.2 | 0 | 0 | 370.8387 | 2632.2701 | 0 | 85336.0451 | 20.31% |  | 11.16% | 0 | 56.8306 |  |  |  | 99.75% | 99.75%
12 | March | 3 | 2026-03-01 | 2026 | FY26 | 31 | 194.5 | 214.2 |  | 26.3 |  | 96606.5148 | 540 | 83.52% | 6.9097 | 0 | 0 | 370.8387 | 3116.3392 | 0 | 85336.0451 | 24.05% |  | 11.16% | 0 | 51.6641 |  |  |  | 99.75% | 99.75%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))