1460 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS13 | INV3 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.75 | 198.4226 | PTW295805
1461 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS6 | INV3 | M2 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.75 | 198.4226 | PTW295805
1462 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS6 | INV3 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.75 | 198.4226 | PTW295805
1463 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS9 | INV3 | M1 | SCB6 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012358 | 7.75 | 200.2599 | PTW295805
1464 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.75 | 163.5149 | PTW295805
1465 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.75 | 163.5149 | PTW295805
1466 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS8 | INV4 | M1 | SCB1 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0010203 | 7.75 | 165.3522 | PTW295805
1467 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.75 | 163.5149 | PTW295967
1468 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.75 | 163.5149 | PTW295967
1469 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0010203 | 7.75 | 165.3522 | PTW295967
1470 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.75 | 198.4226 | PTW295967
1471 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.75 | 198.4226 | PTW295967
1472 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.75 | 198.4226 | PTW295967
1473 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.75 | 198.4226 | PTW295967
1474 | 2025-05-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.75 | 198.4226 | PTW295967
1475 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS13 | INV3 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.64 | 195.6063 | PTW295805
1476 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS6 | INV3 | M2 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.64 | 195.6063 | PTW295805
1477 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS6 | INV3 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.64 | 195.6063 | PTW295805
1478 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS9 | INV3 | M1 | SCB6 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012358 | 7.64 | 197.4175 | PTW295805
1479 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.64 | 161.1941 | PTW295805
1480 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.64 | 161.1941 | PTW295805
1481 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS8 | INV4 | M1 | SCB1 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0010203 | 7.64 | 163.0052 | PTW295805
1482 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.64 | 161.1941 | PTW295967
1483 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.64 | 161.1941 | PTW295967
1484 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0010203 | 7.64 | 163.0052 | PTW295967
1485 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.64 | 195.6063 | PTW295967
1486 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.64 | 195.6063 | PTW295967
1487 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.64 | 195.6063 | PTW295967
1488 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.64 | 195.6063 | PTW295967
1489 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:25 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.64 | 195.6063 | PTW295967
1490 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS7 |  |  |  |  | Tx | 0 | 1 | IS7Tx | 16443 | 4.907% | IDT | IDT_Manual stop for LV Side Thermography | IDT manual stop for thermography work | 12:47 | 12:47 | 12:47 | 13:33 | 0 | 0 | 0.76667 | 0.76667 | After thermography work done IDT Charged. | Close | 0.037621 | 0.78542 | 10557.2033 | PTW296741
1491 | 2025-05-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:25 | 13.1 | IS7 |  |  |  |  | Tx | 0 | 1 | IS7Tx | 16443 | 4.907% | IDT | IDT_Manual stop for LV Side Thermography | IDT manual stop for thermography work | 14:10 | 14:10 | 14:10 | 14:41 | 0 | 0 | 0.51667 | 0.51667 | After thermography work done IDT Charged. | Close | 0.025353 | 0.48248 | 6485.3152 | PTW296741
1492 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS13 | INV3 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295805
1493 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS6 | INV3 | M2 | SCB7 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295805
1494 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS6 | INV3 | M1 | SCB1 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295805
1495 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS9 | INV3 | M1 | SCB6 | Str_Typ10(545*58) |  | 0 | 0 | Str_Typ10(545*58) | 31.61 | 0.009433% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012389 | 7.6 | 196.3839 | PTW295805
1496 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0010116 | 7.6 | 160.3501 | PTW295805
1497 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0010116 | 7.6 | 160.3501 | PTW295805
1498 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS8 | INV4 | M1 | SCB1 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0010229 | 7.6 | 162.1518 | PTW295805
1499 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0010116 | 7.6 | 160.3501 | PTW295967
1500 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0010116 | 7.6 | 160.3501 | PTW295967
1501 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0010229 | 7.6 | 162.1518 | PTW295967
1502 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295967
1503 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295967
1504 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295967
1505 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295967
1506 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | Module Restored and Run | Close | 0.0012275 | 7.6 | 194.5822 | PTW295967
1507 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.31 | 154.2315 | PTW295805
1508 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.31 | 154.2315 | PTW295805
1509 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.31 | 154.2315 | PTW295967
1510 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.001009 | 7.31 | 154.2315 | PTW295967
1511 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0010203 | 7.31 | 155.9644 | PTW295967
1512 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.31 | 187.1573 | PTW295967
1513 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.31 | 187.1573 | PTW295967
1514 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.31 | 187.1573 | PTW295967
1515 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.31 | 187.1573 | PTW295967
1516 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:18 | 6:18 | 6:18 | 19:24 | 0 | 0 | 13.1 | 13.1 | Module Restored and Run | Close | 0.0012244 | 7.31 | 187.1573 | PTW295967
1517 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS15 | INV2 | M1 |  |  |  | 1 | 1 | IS15INV2M1 | 2004.48 | 0.5982% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:18 | 6:18 | 6:42 | 7:20 | 0 | 0.4 | 1.0333 | 1.0333 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.0061813 | 0.097872 | 160.3723 | PTW297021
1518 | 2025-05-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:18 | 19:24 | 13.1 | IS15 | INV2 | M2 |  |  |  | 1 | 1 | IS15INV2M2 | 1941.84 | 0.5795% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:02 | 7:02 | 7:02 | 7:20 | 0 | 0 | 0.3 | 0.3 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0017385 | 0.047683 | 75.6916 | PTW297021
1519 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS5 | INV4 | M1 | SCB5 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.00095766 | 5.03 | 106.1265 | PTW295805
1520 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS5 | INV4 | M1 | SCB8 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.00095766 | 5.03 | 106.1265 | PTW295805
1521 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS2 | INV3 | M2 | SCB7 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.00095766 | 5.03 | 106.1265 | PTW295967
1522 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS3 | INV2 | M2 | SCB6 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.00095766 | 5.03 | 106.1265 | PTW295967
1523 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS4 | INV1 | M2 | SCB2 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.00096842 | 5.03 | 107.3189 | PTW295967
1524 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.0011621 | 5.03 | 128.7827 | PTW295967
1525 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS20 | INV2 | M1 | SCB2 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.0011621 | 5.03 | 128.7827 | PTW295967
1526 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS20 | INV2 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.0011621 | 5.03 | 128.7827 | PTW295967
1527 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS20 | INV2 | M2 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.0011621 | 5.03 | 128.7827 | PTW295967
1528 | 2025-05-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:55 | 19:21 | 12.4333 | IS19 | INV4 | M1 | SCB9 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:55 | 6:55 | 6:55 | 19:21 | 0 | 0 | 12.4333 | 12.4333 | Module Restored and Run | Close | 0.0011621 | 5.03 | 128.7827 | PTW295967
1529 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS6 | INV3 | M2 | SCB10 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | String Affected Due to Wind Strom. | Close | 0.00061533 | 6.6 | 84.4896 | PTW297811
1530 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS14 | INV4 | M1 | SCB5 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | String Affected Due to Wind Strom. | Close | 0.00061533 | 6.6 | 84.4896 | PTW297811
1531 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS13 | INV1 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | String Affected Due to Wind Strom. | Close | 0.00061533 | 6.6 | 84.4896 | PTW297811
1532 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS12 | INV4 | M2 | SCB7 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | String Affected Due to Wind Strom. | Close | 0.00061533 | 6.6 | 84.4896 | PTW297811
1533 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS20 | INV4 | M2 | SCB7 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Affected Due to Wind Strom. | String Affected Due to Wind Strom. | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | String Affected Due to Wind Strom. | Close | 0.00061533 | 6.6 | 84.4896 | PTW297811
1534 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | Module Restored and Run | Close | 0.0012307 | 6.6 | 168.9793 | PTW297883
1535 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS6 | INV4 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | Module Restored and Run | Close | 0.0012307 | 6.6 | 168.9793 | PTW297883
1536 | 2025-05-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:20 | 19:30 | 13.1667 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:20 | 6:20 | 6:20 | 19:30 | 0 | 0 | 13.1667 | 13.1667 | Module Restored and Run | Close | 0.0012307 | 6.6 | 168.9793 | PTW297883
1537 | 2025-05-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:26 | 19:28 | 13.0333 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:26 | 6:26 | 6:26 | 19:28 | 0 | 0 | 13.0333 | 13.0333 | Module Restored and Run | Close | 0.0012182 | 6.23 | 159.5062 | PTW297883
1538 | 2025-05-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:26 | 19:28 | 13.0333 | IS6 | INV4 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:26 | 6:26 | 6:26 | 19:28 | 0 | 0 | 13.0333 | 13.0333 | Module Restored and Run | Close | 0.0012182 | 6.23 | 159.5062 | PTW297883
1539 | 2025-05-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:26 | 19:28 | 13.0333 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:26 | 6:26 | 6:26 | 19:28 | 0 | 0 | 13.0333 | 13.0333 | Module Restored and Run | Close | 0.0012182 | 6.23 | 159.5062 | PTW297883
1540 | 2025-05-30 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:26 | 13.1167 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:26 | 0 | 0 | 13.1167 | 13.1167 | Module Restored and Run | Close | 0.001226 | 7.08 | 181.2687 | PTW297883
1541 | 2025-05-30 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:26 | 13.1167 | IS6 | INV4 | M1 | SCB3 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:26 | 0 | 0 | 13.1167 | 13.1167 | Module Restored and Run | Close | 0.001226 | 7.08 | 181.2687 | PTW297883
1542 | 2025-05-30 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:26 | 13.1167 | IS6 | INV4 | M2 | SCB4 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Module | PV Module_EL Testing | PV modules removed for EL Testing | 6:19 | 6:19 | 6:19 | 19:26 | 0 | 0 | 13.1167 | 13.1167 | Module Restored and Run | Close | 0.001226 | 7.08 | 181.2687 | PTW297883
1543 | 2025-05-31 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS9 | INV1 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Manully stop due to IV Testing work | Manully stop due to IV Testing work | 10:35 | 10:35 | 10:35 | 13:26 | 0 | 0 | 2.85 | 2.85 | Manully stop due to IV Testing work | Close | 0.00026638 | 2.53 | 64.7754 | PTW298338
1544 | 2025-05-31 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS9 | INV1 | M2 | SCB6 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Manully stop due to IV Testing work | Manully stop due to IV Testing work | 10:35 | 10:35 | 10:35 | 13:26 | 0 | 0 | 2.85 | 2.85 | Manully stop due to IV Testing work | Close | 0.00026638 | 2.53 | 64.7754 | PTW298338
1545 | 2025-05-31 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 13.1333 | IS7 | INV1 | M1 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | MC4 connector damage | MC4 connector Replaced. | 6:19 | 6:19 | 6:19 | 19:27 | 0 | 0 | 13.1333 | 13.1333 | MC4 connector Replaced. | Close | 0.00061377 | 6.91 | 88.4581 | PTW298409
1546 | 2025-06-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:31 | 19:25 | 12.9 | [5 empty] | Power_Tx2 | 0 | 1 | Power_Tx2 | 167768.915 | 50.07% | PTR | Tripped due to the 87T Differential Protection operation. | R-Phase Cable End Termination Failure | 19:25 | 19:25 | 19:25 | 5:15 | 0 | 0 |  |  | R phase End termination replaced and Check IR Value then PTR Charged. | Close | 0 | 0 | 0 | PTW298610
1547 | 2025-06-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:26 | 13.1667 | IS4 | INV3 | M1 | SCB6 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:56 | 10:56 | 10:56 | 12:35 | 0 | 0 | 1.65 | 1.65 | String Manully shutdown for IV Testing work | Close | 0.00012852 | 1.49 | 32.2737 | PTW298884
1548 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS1 | INV3 | M2 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:46 | 10:46 | 10:46 | 11:06 | 0 | 0 | 0.33333 | 0.33333 | String Manully shutdown for IV Testing work | Close | 1.2837e-05 | 0.30154 | 3.2294 | PTW299319
1549 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS5 | INV3 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:15 | 11:15 | 11:15 | 11:30 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.24352 | 2.608 | PTW299319
1550 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:45 | 11:45 | 11:45 | 12:00 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1792e-05 | 0.25457 | 3.3391 | PTW299319
1551 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:20 | 12:20 | 12:20 | 12:35 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26092 | 3.3909 | PTW299319
1552 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS16 | INV3 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:45 | 12:45 | 12:45 | 13:00 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26183 | 3.4028 | PTW299319
1553 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS18 | INV4 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:10 | 13:10 | 13:10 | 13:30 | 0 | 0 | 0.33333 | 0.33333 | String Manully shutdown for IV Testing work | Close | 1.5578e-05 | 0.33905 | 4.4063 | PTW299319
1554 | 2025-06-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:27 | 13.1833 | IS6 | INV2 | M1 | SCB2 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 14:45 | 14:45 | 14:45 | 15:03 | 0 | 0 | 0.3 | 0.3 | String Manully shutdown for IV Testing work | Close | 1.389e-05 | 0.25993 | 3.3467 | PTW299319
1555 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS1 | INV3 | M2 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:30 | 10:30 | 10:30 | 10:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.22043 | 2.3608 | PTW299485
1556 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS5 | INV3 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:00 | 11:00 | 11:00 | 11:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.2379 | 2.5479 | PTW299485
1557 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:30 | 11:30 | 11:30 | 11:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1792e-05 | 0.25215 | 3.3073 | PTW299485
1558 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:00 | 12:00 | 12:00 | 12:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26067 | 3.3877 | PTW299485
1559 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS16 | INV3 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:30 | 12:30 | 12:30 | 12:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26505 | 3.4446 | PTW299485
1560 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS18 | INV4 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:00 | 13:00 | 13:00 | 13:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26388 | 3.4295 | PTW299485
1561 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS6 | INV2 | M1 | SCB2 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:30 | 13:30 | 13:30 | 13:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1575e-05 | 0.25915 | 3.3368 | PTW299485
1562 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS9 | INV4 | M2 |  |  |  | 1 | 1 | IS9INV4M2 | 1959.82 | 0.5849% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:17 | 6:17 | 6:45 | 19:29 | 0 | 0.46667 | 13.2 | 13.2 | After Genration AC Breaker Replace with Sungrow Team. | Close | 0.077202 | 7.3191 | 11904.0443 | PTW299590
1563 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS9 | INV4 | M1 |  |  |  | 1 | 1 | IS9INV4M1 | 2244.31 | 0.6698% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:55 | 7:55 | 7:55 | 9:11 | 0 | 0 | 1.2667 | 1.2667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0084836 | 0.56024 | 1043.4672 | PTW299590
1564 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS9 | INV4 | M1 |  |  |  | 1 | 1 | IS9INV4M1 | 2244.31 | 0.6698% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 9:35 | 9:35 | 9:35 | 9:47 | 0 | 0 | 0.2 | 0.2 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0013395 | 0.14326 | 266.8238 | PTW299590
1565 | 2025-06-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:29 | 13.2 | IS16 | INV3 | M1 |  |  |  | 1 | 1 | IS16INV3M1 | 2129.76 | 0.6356% | Inverter | Inverter trip in GFDI falut | Inverter trip in GFDI falut | 14:28 | 14:45 | 14:45 | 15:22 | 0.28333 | 0.28333 | 0.9 | 0.9 | Inverter Auto Reset and Run | Close | 0.0057202 | 0.72991 | 1290.0983
1566 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS4 | INV2 | M1 |  |  |  | 1 | 1 | IS4INV2M1 | 2114.1 | 0.6309% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:20 | 6:20 | 7:05 | 7:40 | 0 | 0.75 | 1.3333 | 1.3333 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.008412 | 0.15156 | 265.9083 | PTW299810
1567 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS4 | INV2 | M2 |  |  |  | 1 | 1 | IS4INV2M2 | 2088 | 0.6231% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:25 | 7:25 | 7:25 | 7:40 | 0 | 0 | 0.25 | 0.25 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0015578 | 0.054265 | 94.0312 | PTW299810
1568 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS1 | INV3 | M2 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:30 | 10:30 | 10:30 | 10:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.2207 | 2.3636 | PTW299638
1569 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS5 | INV3 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:00 | 11:00 | 11:00 | 11:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.23875 | 2.557 | PTW299638
1570 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:30 | 11:30 | 11:30 | 11:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1792e-05 | 0.2523 | 3.3093 | PTW299638
1571 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:00 | 12:00 | 12:00 | 12:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26177 | 3.402 | PTW299638
1572 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS16 | INV3 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:30 | 12:30 | 12:30 | 12:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26597 | 3.4565 | PTW299638
1573 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS18 | INV4 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:00 | 13:00 | 13:00 | 13:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26517 | 3.4461 | PTW299638
1574 | 2025-06-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:13 | 19:30 | 13.2833 | IS6 | INV2 | M1 | SCB2 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:30 | 13:30 | 13:30 | 13:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1575e-05 | 0.26072 | 3.3569 | PTW299638
1575 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS1 | INV3 | M2 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:31 | 10:31 | 10:31 | 10:45 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 8.9861e-06 | 0.21297 | 2.2808 | PTW299846
1576 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS5 | INV3 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:02 | 11:02 | 11:02 | 11:15 | 0 | 0 | 0.21667 | 0.21667 | String Manully shutdown for IV Testing work | Close | 8.3443e-06 | 0.21248 | 2.2756 | PTW299846
1577 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:31 | 11:31 | 11:31 | 11:45 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.1005e-05 | 0.2381 | 3.123 | PTW299846
1578 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:00 | 12:00 | 12:00 | 12:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.24873 | 3.2326 | PTW299846
1579 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS16 | INV3 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:30 | 12:30 | 12:30 | 12:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.25043 | 3.2547 | PTW299846
1580 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS18 | INV4 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:01 | 13:01 | 13:01 | 13:15 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.0905e-05 | 0.24678 | 3.2072 | PTW299846
1581 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 13.25 | IS6 | INV2 | M1 | SCB2 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:30 | 13:30 | 13:30 | 13:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1575e-05 | 0.25177 | 3.2417 | PTW299846
1582 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS1 | INV3 | M2 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 10:30 | 10:30 | 10:30 | 10:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 9.628e-06 | 0.20813 | 2.2291 | PTW300061
1583 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS5 | INV3 | M1 | SCB1 | Str_Typ1(445*29) |  | 0 | 0 | Str_Typ1(445*29) | 12.905 | 0.003851% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:02 | 11:02 | 11:02 | 11:15 | 0 | 0 | 0.21667 | 0.21667 | String Manully shutdown for IV Testing work | Close | 8.3443e-06 | 0.21002 | 2.2492 | PTW300061
1584 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 11:31 | 11:31 | 11:31 | 11:45 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.1005e-05 | 0.23737 | 3.1134 | PTW300061
1585 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:00 | 12:00 | 12:00 | 12:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26255 | 3.4121 | PTW300061
1586 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS16 | INV3 | M1 | SCB4 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:30 | 12:30 | 12:30 | 12:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.25037 | 3.2538 | PTW300061
1587 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS18 | INV4 | M1 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:01 | 13:01 | 13:01 | 13:15 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.0905e-05 | 0.25013 | 3.2508 | PTW300061
1588 | 2025-06-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS6 | INV2 | M1 | SCB2 | Str_Typ3(535*29) |  | 0 | 0 | Str_Typ3(535*29) | 15.515 | 0.00463% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:31 | 13:31 | 13:31 | 13:45 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.0804e-05 | 0.24548 | 3.1608 | PTW300061
1589 | 2025-06-10 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:00 | 12:00 | 12:00 | 12:15 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1792e-05 | 0.25882 | 3.3948 | PTW300295
1590 | 2025-06-10 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:31 | 13.2667 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:30 | 12:30 | 12:30 | 12:45 | 0 | 0 | 0.25 | 0.25 | String Manully shutdown for IV Testing work | Close | 1.1683e-05 | 0.26412 | 3.4325 | PTW300295
1591 | 2025-06-11 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:33 | 13.3167 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:15 | 12:15 | 12:15 | 12:37 | 0 | 0 | 0.36667 | 0.36667 | String Manully shutdown for IV Testing work | Close | 1.7294e-05 | 0.37892 | 4.97 | PTW300457
1592 | 2025-06-11 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:33 | 13.3167 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:54 | 12:54 | 12:54 | 13:08 | 0 | 0 | 0.23333 | 0.23333 | String Manully shutdown for IV Testing work | Close | 1.0905e-05 | 0.24947 | 3.2421 | PTW300457
1593 | 2025-06-11 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:33 | 13.3167 | IS5 |  |  |  |  | Tx | 0 | 1 | IS5Tx | 16724.88 | 4.991% | IDT | IDT_Manual stop for LV Side Thermography | IDT manual stop for thermography work | 12:17 | 12:17 | 12:17 | 12:59 | 0 | 0 | 0.7 | 0.7 | After thermography work IDT Charged Sucessfully. | Close | 0.034938 | 0.71287 | 9894.4839 | PTW300540
1594 | 2025-06-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 13.2833 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:37 | 12:37 | 12:37 | 13:02 | 0 | 0 | 0.41667 | 0.41667 | String Manully shutdown for IV Testing work | Close | 1.9653e-05 | 0.43092 | 5.6521 | PTW300678
1595 | 2025-06-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 13.2833 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:15 | 13:15 | 13:15 | 13:32 | 0 | 0 | 0.28333 | 0.28333 | String Manully shutdown for IV Testing work | Close | 1.3241e-05 | 0.29373 | 3.8174 | PTW300678
1596 | 2025-06-13 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:29 | 13.1833 | IS9 | INV1 | M2 | SCB3 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 12:02 | 12:02 | 12:02 | 12:45 | 0 | 0 | 0.71667 | 0.71667 | String Manully shutdown for IV Testing work | Close | 3.3803e-05 | 0.69153 | 9.0705 | PTW300966
1597 | 2025-06-13 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:29 | 13.1833 | IS12 | INV1 | M2 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | String Manully shutdown for IV Testing work | String Manully shutdown for IV Testing work | 13:06 | 13:06 | 13:06 | 13:32 | 0 | 0 | 0.43333 | 0.43333 | String Manully shutdown for IV Testing work | Close | 2.0251e-05 | 0.42897 | 5.5749 | PTW300966
1598 | 2025-06-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:48 | 19:26 | 12.6333 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:48 | 6:48 | 6:48 | 19:26 | 0 | 0 | 12.6333 | 12.6333 | Module Remove for damage module replacement work | Close | 0.00097307 | 1.79 | 38.3409 | PTW301070
1599 | 2025-06-15 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:39 | 19:31 | 12.8667 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:39 | 6:39 | 6:39 | 19:31 | 0 | 0 | 12.8667 | 12.8667 | Module Remove for damage module replacement work | Close | 0.00099104 | 2.95 | 63.1876 | PTW301312
1600 | 2025-06-16 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:40 | 13.4333 | IS4 | INV2 | M1 |  |  |  | 1 | 1 | IS4INV2M1 | 2114.1 | 0.6309% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:22 | 6:22 | 7:42 | 8:10 | 0 | 1.3333 | 1.8 | 1.8 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.011356 | 0.21953 | 385.1586 | PTW301465
1601 | 2025-06-16 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:40 | 13.4333 | IS4 | INV2 | M2 |  |  |  | 1 | 1 | IS4INV2M2 | 2088 | 0.6231% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:45 | 7:45 | 7:45 | 8:10 | 0 | 0 | 0.41667 | 0.41667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0025963 | 0.067603 | 117.1441 | PTW301465
1602 | 2025-06-16 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:40 | 13.4333 | IS9 | INV4 | M1 |  |  |  | 1 | 1 | IS9INV4M1 | 2244.31 | 0.6698% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:20 | 6:20 | 6:45 | 7:52 | 0 | 0.41667 | 1.5333 | 1.5333 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.01027 | 0.17218 | 320.6908 | PTW301465
1603 | 2025-06-16 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:14 | 19:40 | 13.4333 | IS9 | INV4 | M2 |  |  |  | 1 | 1 | IS9INV4M2 | 1959.82 | 0.5849% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:30 | 7:30 | 7:30 | 7:52 | 0 | 0 | 0.36667 | 0.36667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0021445 | 0.063402 | 103.119 | PTW301465
1604 | 2025-06-17 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:31 | 19:39 | 13.1333 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:31 | 6:31 | 6:31 | 19:39 | 0 | 0 | 13.1333 | 13.1333 | Module Remove for damage module replacement work | Close | 0.0010116 | 5.75 | 123.1623 | PTW301312
1605 | 2025-06-18 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:36 | 13.2333 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:22 | 6:22 | 6:22 | 19:36 | 0 | 0 | 13.2333 | 13.2333 | Module Remove for damage module replacement work | Close | 0.0010193 | 7.2 | 154.2206 | PTW301944
1606 | 2025-06-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:12 | 19:28 | 13.2667 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:12 | 6:12 | 6:12 | 19:28 | 0 | 0 | 13.2667 | 13.2667 | Module Remove for damage module replacement work | Close | 0.0010218 | 6.75 | 144.5818 | PTW302162
1607 | 2025-06-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:12 | 19:28 | 13.2667 | IS7 | INV2 | M1 |  |  |  | 1 | 1 | IS7INV2M1 | 2098.44 | 0.6262% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 17:46 | 17:46 | 17:46 | 19:28 | 0 | 0 | 1.7 | 1.7 | Auto Reset and Run. | Close | 0.010646 | 0.13604 | 236.905
1608 | 2025-06-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:12 | 19:28 | 13.2667 | IS7 | INV2 | M2 |  |  |  | 1 | 1 | IS7INV2M2 | 2004.48 | 0.5982% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 17:46 | 17:46 | 17:46 | 19:28 | 0 | 0 | 1.7 | 1.7 | Auto Reset and Run. | Close | 0.010169 | 0.13604 | 226.2973
1609 | 2025-06-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:12 | 19:28 | 13.2667 | [5 empty] | Power_Tx1 | 0 | 1 | Power_Tx1 | 167322.75 | 49.93% | PTR | PTR-1 Trip in 87 Activated. | PTR-1 Trip in 87 Activated. | 19:32 | 19:32 | 20:02 | 22:49 | 0 | 0.5 | 3.2833 | 3.2833 | Cheack Related parameter and IR value after that disscuss with HT team then PTR charged. | Close | 1.6395 | 0 | 0 | PTW302345
1610 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS7 | INV2 | M1 |  |  |  | 1 | 1 | IS7INV2M1 | 2098.44 | 0.6262% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:18 | 6:18 | 6:40 | 19:35 | 0 | 0.36667 | 13.2833 | 13.2833 | After Genration OEM team replaced AC Breaker and inverter kept in observation | Close | 0.083184 | 6.58 | 11458.9356 | PTW302566
1611 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS7 | INV2 | M2 |  |  |  | 1 | 1 | IS7INV2M2 | 2004.48 | 0.5982% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:18 | 6:18 | 6:40 | 19:35 | 0 | 0.36667 | 13.2833 | 13.2833 | After Genration OEM team replaced AC Breaker and inverter kept in observation | Close | 0.07946 | 6.58 | 10945.849 | PTW302566
1612 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS18 | INV3 | M1 |  |  |  | 1 | 1 | IS18INV3M1 | 2223.72 | 0.6636% | Inverter | Inverter tripped in GFDI Fault | Inverter tripped in GFDI Fault | 6:18 | 6:18 | 7:00 | 8:15 | 0 | 0.7 | 1.95 | 1.95 | checked related connection and parameter then the inverter and start | Close | 0.012941 | 0.2264 | 417.8025 | PTW302616
1613 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS18 | INV3 | M2 |  |  |  | 1 | 1 | IS18INV3M2 | 1973.16 | 0.5888% | Inverter | Manually stop for Inv Unit_GFDI Fault rectification | Manually stop for Inv Unit_GFDI Fault rectification | 7:20 | 7:20 | 7:20 | 8:15 | 0 | 0 | 0.91667 | 0.91667 | Manually stop for Inv Unit_GFDI Fault rectification | Close | 0.0053977 | 0.16585 | 271.5839 | PTW302616
1614 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS18 | INV3 | M1 | SCB6 |  |  | 1 | 1 | IS18INV3M1SCB6 | 250.56 | 0.07477% | SCB | Manually stop SCB_GFDI Fault rectification | Manually stop SCB_GFDI Fault rectification | 8:15 | 8:15 | 8:15 | 8:55 | 0 | 0 | 0.66667 | 0.66667 | Manually stop SCB_GFDI Fault rectification | Close | 0.00049849 | 0.1619 | 33.6648 | PTW302616
1615 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS18 | INV3 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 8:55 | 8:55 | 8:55 | 19:35 | 0 | 0 | 10.6667 | 10.6667 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00049849 | 6.1941 | 80.499 | PTW302616
1616 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS18 | INV2 | M2 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:18 | 6:18 | 6:18 | 19:35 | 0 | 0 | 13.2833 | 13.2833 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00062078 | 6.58 | 85.5144 | PTW302616
1617 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 13.2833 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:18 | 6:18 | 6:18 | 19:35 | 0 | 0 | 13.2833 | 13.2833 | Module Remove for damage module replacement work | Close | 0.0010231 | 6.58 | 140.9405 | PTW302441
1618 | 2025-06-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 19:28 | 13.0833 | IS7 | INV2 | M1 |  |  |  | 1 | 1 | IS7INV2M1 | 2098.44 | 0.6262% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:23 | 6:23 | 6:23 | 19:28 | 0 | 0 | 13.0833 | 13.0833 | After Genration OEM team attend inverter and found 20Amp. Fuse was blown, fuse arrenge other site and replaced in early morning then inverter reboot and run. | Close | 0.081932 | 2.13 | 3709.3515 | PTW302772
1619 | 2025-06-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 19:28 | 13.0833 | IS7 | INV2 | M2 |  |  |  | 1 | 1 | IS7INV2M2 | 2004.48 | 0.5982% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:23 | 6:23 | 6:23 | 19:28 | 0 | 0 | 13.0833 | 13.0833 | After Genration OEM team attend inverter and found 20Amp. Fuse was blown, fuse arrenge other site and replaced in early morning then inverter reboot and run. | Close | 0.078263 | 2.13 | 3543.2611 | PTW302772
1620 | 2025-06-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 19:28 | 13.0833 | IS18 | INV3 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:23 | 6:23 | 6:23 | 19:28 | 0 | 0 | 13.0833 | 13.0833 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00061143 | 2.13 | 27.6817 | PTW302616
1621 | 2025-06-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 19:28 | 13.0833 | IS18 | INV2 | M2 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:23 | 6:23 | 6:23 | 19:28 | 0 | 0 | 13.0833 | 13.0833 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00061143 | 2.13 | 27.6817 | PTW302616
1622 | 2025-06-21 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 19:28 | 13.0833 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:23 | 6:23 | 6:23 | 19:28 | 0 | 0 | 13.0833 | 13.0833 | Module Remove for damage module replacement work | Close | 0.0010077 | 2.13 | 45.6236 | PTW302441
1623 | 2025-06-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 13.2833 | IS18 | INV3 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:15 | 6:15 | 6:15 | 19:32 | 0 | 0 | 13.2833 | 13.2833 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00062078 | 7 | 90.9728 | PTW302616
1624 | 2025-06-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 13.2833 | IS18 | INV2 | M2 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:15 | 6:15 | 6:15 | 19:32 | 0 | 0 | 13.2833 | 13.2833 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00062078 | 7 | 90.9728 | PTW302616
1625 | 2025-06-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 13.2833 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:15 | 6:15 | 6:15 | 19:32 | 0 | 0 | 13.2833 | 13.2833 | Module Remove for damage module replacement work | Close | 0.0010231 | 7.04 | 150.7935 | PTW302441
1626 | 2025-06-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:26 | 19:28 | 13.0333 | IS18 | INV3 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:26 | 6:26 | 6:26 | 19:28 | 0 | 0 | 13.0333 | 13.0333 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00060909 | 5.7 | 74.0779 | PTW302616
1627 | 2025-06-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:26 | 19:28 | 13.0333 | IS18 | INV2 | M2 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:26 | 6:26 | 6:26 | 19:28 | 0 | 0 | 13.0333 | 13.0333 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00060909 | 5.7 | 74.0779 | PTW302616
1628 | 2025-06-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:26 | 19:28 | 13.0333 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:26 | 6:26 | 6:26 | 19:28 | 0 | 0 | 13.0333 | 13.0333 | Module Remove for damage module replacement work | Close | 0.0010039 | 5.74 | 122.9481 | PTW302441
1629 | 2025-06-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:29 | 19:31 | 13.0333 | IS18 | INV3 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:29 | 6:29 | 6:29 | 19:31 | 0 | 0 | 13.0333 | 13.0333 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00060909 | 6.51 | 84.6047 | PTW302616
1630 | 2025-06-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:29 | 19:31 | 13.0333 | IS18 | INV2 | M2 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:29 | 6:29 | 6:29 | 19:31 | 0 | 0 | 13.0333 | 13.0333 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00060909 | 6.51 | 84.6047 | PTW302616
1631 | 2025-06-24 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:29 | 19:31 | 13.0333 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:29 | 6:29 | 6:29 | 19:31 | 0 | 0 | 13.0333 | 13.0333 | Module Remove for damage module replacement work | Close | 0.0010039 | 6.44 | 137.9417 | PTW302441
1632 | 2025-06-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:23 | 13.0167 | IS18 | INV3 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:22 | 6:22 | 6:22 | 19:23 | 0 | 0 | 13.0167 | 13.0167 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00060832 | 6.16 | 80.0561 | PTW302616
1633 | 2025-06-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:23 | 13.0167 | IS18 | INV2 | M2 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:22 | 6:22 | 6:22 | 19:23 | 0 | 0 | 13.0167 | 13.0167 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00060832 | 6.16 | 80.0561 | PTW302616
1634 | 2025-06-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:23 | 13.0167 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:22 | 6:22 | 6:22 | 19:23 | 0 | 0 | 13.0167 | 13.0167 | Module Remove for damage module replacement work | Close | 0.0010026 | 6.13 | 131.3017 | PTW302441
1635 | 2025-06-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 18:15 | 11.8667 | IS18 | INV3 | M1 | SCB6 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:23 | 6:23 | 6:23 | 18:15 | 0 | 0 | 11.8667 | 11.8667 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00055457 | 5.23 | 67.9697 | PTW303787
1636 | 2025-06-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 18:15 | 11.8667 | IS18 | INV2 | M2 | SCB1 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Due to heavy wind strom module found damage so string remove from SCB side in B/D | 6:23 | 6:23 | 6:23 | 18:15 | 0 | 0 | 11.8667 | 11.8667 | Due to heavy wind strom module found damage so string remove from SCB side in B/D | Close | 0.00055457 | 5.23 | 67.9697 | PTW303787
1637 | 2025-06-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 18:15 | 11.8667 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:23 | 6:23 | 6:23 | 18:15 | 0 | 0 | 11.8667 | 11.8667 | Module Remove for damage module replacement work | Close | 0.00091402 | 5.54 | 118.6642 | PTW302441
1638 | 2025-06-26 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:23 | 18:15 | 11.8667 | IS6 | INV2 | M1 |  |  |  | 1 | 1 | IS6INV2M1 | 2203.13 | 0.6575% | Inverter | Inverter tripped in GFDI Fault | Inverter tripped in GFDI Fault | 17:32 | 17:32 | 17:32 | 18:15 | 0 | 0 | 0.71667 | 0.71667 | Auto Reset and Run. | Close | 0.0047119 | 0.015161 | 27.7204
1639 | 2025-06-27 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:15 | 12.8833 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:22 | 6:22 | 6:22 | 19:15 | 0 | 0 | 12.8833 | 12.8833 | Module Remove for damage module replacement work | Close | 0.00099232 | 4.25 | 91.033 | PTW302441
1640 | 2025-06-27 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:15 | 12.8833 | IS9 | INV4 | M1 |  |  |  | 1 | 1 | IS9INV4M1 | 2244.31 | 0.6698% | Inverter | Inverter tripped in GFDI Fault | Inverter tripped in GFDI Fault | 10:06 | 10:06 | 10:20 | 11:02 | 0 | 0.23333 | 0.93333 | 0.93333 | MC4 connector found burn, replace and Run. | Close | 0.0062511 | 0.66535 | 1239.2321 | PTW304064
1641 | 2025-06-27 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:15 | 12.8833 | IS9 | INV4 | M2 |  |  |  | 1 | 1 | IS9INV4M2 | 1959.82 | 0.5849% | Inverter | Manually stop for Inv Unit_GFDI Fault rectification | Manually stop for Inv Unit_GFDI Fault rectification | 10:20 | 10:20 | 10:20 | 11:02 | 0 | 0 | 0.7 | 0.7 | Manually stop for Inv Unit_GFDI Fault rectification | Close | 0.004094 | 0.50024 | 813.6157 | PTW304064
1642 | 2025-06-27 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:15 | 12.8833 | IS9 | INV4 | M1 | SCB8 | Str_Typ5(545*29) |  | 0 | 0 | Str_Typ5(545*29) | 15.805 | 0.004717% | Connectors | MC4 connector damage | MC4 connector damage | 11:02 | 11:02 | 11:02 | 19:15 | 0 | 0 | 8.2167 | 8.2167 | MC4 Connector Replaced & Run. | Close | 0.00038755 | 2.4104 | 31.6162 | PTW304064
1643 | 2025-06-28 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:33 | 19:30 | 12.95 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:33 | 6:33 | 6:33 | 19:30 | 0 | 0 | 12.95 | 12.95 | Module Remove for damage module replacement work | Close | 0.00099746 | 5.92 | 126.8036 | PTW302441
1644 | 2025-06-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:32 | 13.1667 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:22 | 6:22 | 6:22 | 19:33 | 0 | 0 | 13.1833 | 13.1833 | Module Remove for damage module replacement work | Close | 0.0010154 | 5.18 | 110.9531 | PTW302441
1645 | 2025-06-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:32 | 13.1667 | IS16 | INV3 | M1 |  |  |  | 1 | 1 | IS16INV3M1 | 2129.76 | 0.6356% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:22 | 6:22 | 7:02 | 8:43 | 0 | 0.66667 | 2.35 | 2.35 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.014936 | 0.45257 | 799.9109 | PTW304339
1646 | 2025-06-29 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:32 | 13.1667 | IS16 | INV3 | M2 |  |  |  | 1 | 1 | IS16INV3M2 | 1879.2 | 0.5608% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 8:28 | 8:28 | 8:28 | 8:43 | 0 | 0 | 0.25 | 0.25 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.001402 | 0.10361 | 161.5807 | PTW304339
1647 | 2025-06-30 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:31 | 13.2333 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:17 | 6:17 | 6:17 | 19:31 | 0 | 0 | 13.2333 | 13.2333 | Module Remove for damage module replacement work | Close | 0.0010193 | 5.34 | 114.3803 | PTW302441
1648 | 2025-07-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:30 | 13.0333 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:28 | 6:28 | 6:28 | 19:30 | 0 | 0 | 13.0333 | 13.0333 | Module Remove for damage module replacement work | Close | 0.0010039 | 6.24 | 135.2882 | PTW302441
1649 | 2025-07-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:30 | 13.0333 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:28 | 6:28 | 6:28 | 19:30 | 0 | 0 | 13.0333 | 13.0333 | Module Remove for damage module replacement work | Close | 0.0012182 | 6.24 | 164.1699 | PTW304763
1650 | 2025-07-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:30 | 13.0333 | IS15 | INV1 | M1 | SCB8 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Y-connector fuse found damage | Y-connector fuse found damage | 6:28 | 6:28 | 6:28 | 19:30 | 0 | 0 | 13.0333 | 13.0333 | Fuse Replaced & Run. | Close | 0.0012182 | 6.24 | 164.1699 | PTW304900
1651 | 2025-07-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:30 | 13.0333 | IS16 | INV3 | M1 | SCB3 | Str_Typ4(540*29) |  | 0 | 0 | Str_Typ4(540*29) | 15.66 | 0.004673% | Connectors | MC4 connector damage | MC4 connector damage | 6:28 | 6:28 | 6:28 | 19:30 | 0 | 0 | 13.0333 | 13.0333 | MC4 Connector Replaced & Run. | Close | 0.00060909 | 6.24 | 82.085 | PTW304900
1652 | 2025-07-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 18:46 | 12.3 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:28 | 6:28 | 6:28 | 18:46 | 0 | 0 | 12.3 | 12.3 | Module Remove for damage module replacement work | Close | 0.00094739 | 3.44 | 74.582 | PTW302441
1653 | 2025-07-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 18:46 | 12.3 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:28 | 6:28 | 6:28 | 18:46 | 0 | 0 | 12.3 | 12.3 | Module Remove for damage module replacement work | Close | 0.0011496 | 3.44 | 90.5039 | PTW304763
1654 | 2025-07-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 | 12.9833 | 12.9833 | Module Remove for damage module replacement work | Close | 0.001 | 2.617 | 56.7387 | PTW302441
1655 | 2025-07-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:27 | 6:27 | 6:27 | 19:26 | 0 | 0 | 12.9833 | 12.9833 | Module Remove for damage module replacement work | Close | 0.0012135 | 2.4948 | 65.6365 | PTW304763
1656 | 2025-07-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS7 | INV3 | M1 |  |  |  | 1 | 1 | IS7INV3M1 | 2223.72 | 0.6636% | Inverter | Inverter trip in GFDI falut | Inverter trip in GFDI falut | 6:27 | 6:27 | 7:00 | 7:37 | 0 | 0.55 | 1.1667 | 1.1667 | Inverter Reboot and Run | Close | 0.0077422 | 0.070914 | 132.4654 | PTW305128
1657 | 2025-07-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS4 | INV2 | M1 |  |  |  | 1 | 1 | IS4INV2M1 | 2114.1 | 0.6309% | Inverter | Inverter tripped in GFDI Fault | Inverter tripped in GFDI Fault | 6:27 | 6:27 | 7:00 | 8:02 | 0 | 0.55 | 1.5833 | 1.5833 | Module found damage, module bypass and run | Close | 0.0099893 | 0.14305 | 254.0324 | PTW305128
1658 | 2025-07-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS4 | INV2 | M1 | SCB3 |  |  | 1 | 1 | IS4INV2M1SCB3 | 234.9 | 0.0701% | SCB | Manually stop for Inv Unit_GFDI Fault rectification | Manually stop for Inv Unit_GFDI Fault rectification | 8:02 | 8:02 | 8:02 | 8:25 | 0 | 0 | 0.38333 | 0.38333 | Manually stop for Inv Unit_GFDI Fault rectification | Close | 0.00026872 | 0.054827 | 10.8184 | PTW305128
1659 | 2025-07-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS4 | INV2 | M1 | SCB3 | Str_Typ7(450*58) |  | 0 | 0 | Str_Typ7(450*58) | 26.1 | 0.007789% | Connectors | Module found damage | Module found damage | 8:25 | 8:25 | 8:25 | 8:49 | 0 | 0 | 0.4 | 0.4 | Module found damage, module bypass and run | Close | 3.1156e-05 | 0.093073 | 2.0406 | PTW305128
1660 | 2025-07-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:27 | 19:26 | 12.9833 | IS4 |  |  |  |  | Tx | 0 | 1 | IS4Tx | 16547.4 | 4.938% | IDT | Manually stop due to IDT LV side thermography work | Manually stop due to IDT LV side thermography work | 12:45 | 12:45 | 12:45 | 13:42 | 0 | 0 | 0.95 | 0.95 | Manually stop due to IDT LV side thermography work | Close | 0.046913 | 0.14328 | 1991.6233 | PTW305276
1661 | 2025-07-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:31 | 19:31 | 13 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:31 | 6:31 | 6:31 | 19:31 | 0 | 0 | 13 | 13 | Module Remove for damage module replacement work | Close | 0.0010013 | 5.0858 | 110.265 | PTW302441
1662 | 2025-07-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:31 | 19:31 | 13 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:31 | 6:31 | 6:31 | 19:31 | 0 | 0 | 13 | 13 | Module Remove for damage module replacement work | Close | 0.0012151 | 5.0858 | 133.8048 | PTW304763
1663 | 2025-07-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:31 | 19:31 | 13 | IS20 | INV2 | M1 |  |  |  | 1 | 1 | IS20INV2M1 | 2255.04 | 0.673% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 8:15 | 8:20 | 8:55 | 11:00 | 0.083333 | 0.66667 | 2.75 | 2.75 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.018506 | 1.268 | 2401.8395 | PTW305457
1664 | 2025-07-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:31 | 19:31 | 13 | IS20 | INV2 | M2 |  |  |  | 1 | 1 | IS20INV2M2 | 2255.04 | 0.673% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 10:32 | 10:32 | 10:32 | 11:00 | 0 | 0 | 0.46667 | 0.46667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0031405 | 0.33314 | 631.0503 | PTW305457
1665 | 2025-07-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:31 | 19:31 | 13 | IS3 |  |  |  |  | Tx | 0 | 1 | IS3Tx | 16766.64 | 5.004% | IDT | Manually stop due to IDT LV side thermography work | Manually stop due to IDT LV side thermography work | 12:42 | 12:42 | 12:42 | 13:38 | 0 | 0 | 0.93333 | 0.93333 | Manually stop due to IDT LV side thermography work | Close | 0.0467 | 0.51797 | 7295.2127 | PTW305479
1665 | 2025-07-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:33 | 13.0833 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:28 | 6:28 | 6:28 | 19:33 | 0 | 0 | 13.0833 | 13.0833 | Module Remove for damage module replacement work | Close | 0.0010077 | 6.3045 | 136.687 | PTW302441
1665 | 2025-07-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:33 | 13.0833 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:28 | 6:28 | 6:28 | 19:33 | 0 | 0 | 13.0833 | 13.0833 | Module Remove for damage module replacement work | Close | 0.0012229 | 6.3045 | 165.8674 | PTW304763
1665 | 2025-07-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:33 | 13.0833 | IS11 |  |  |  |  | Tx | 0 | 1 | IS11Tx | 16595.25 | 4.952% | IDT | Manually stop due to IDT LV side thermography work | Manually stop due to IDT LV side thermography work | 12:22 | 12:22 | 12:22 | 13:05 | 0 | 0 | 0.71667 | 0.71667 | Manually stop due to IDT LV side thermography work | Close | 0.035493 | 0.7314 | 10195.935 | PTW305658
1666 | 2025-07-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:33 | 13.0833 | IS10 | INV4 | M2 | SCB10 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Junction Box Burn. | During String current checking found 8 nos. Module JB found. | 6:28 | 6:28 | 6:28 | 19:33 | 0 | 0 | 13.0833 | 13.0833 | During String current checking found 8 nos. Module JB found. | Close | 0.0012229 | 6.3045 | 165.8674 | PTW305652
1667 | 2025-07-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:27 | 12.75 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:42 | 6:42 | 6:42 | 19:27 | 0 | 0 | 12.75 | 12.75 | Module Remove for damage module replacement work | Close | 0.00098205 | 6.6503 | 144.1845 | PTW302441
1668 | 2025-07-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:27 | 12.75 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:42 | 6:42 | 6:42 | 19:27 | 0 | 0 | 12.75 | 12.75 | Module Remove for damage module replacement work | Close | 0.0011917 | 6.6503 | 174.9655 | PTW304763
1669 | 2025-07-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:27 | 12.75 | IS12 |  |  |  |  | Tx | 0 | 1 | IS12Tx | 16912.8 | 5.047% | IDT | Manually stop due to IDT LV side thermography work | Manually stop due to IDT LV side thermography work | 13:12 | 13:12 | 13:12 | 13:56 | 0 | 0 | 0.73333 | 0.73333 | Manually stop due to IDT LV side thermography work | Close | 0.037013 | 0.63879 | 9075.2752 | PTW305848
1670 | 2025-07-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:27 | 12.75 | IS10 | INV4 | M2 | SCB10 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Junction Box Burn. | During String current checking found 8 nos. Module JB found. | 6:42 | 6:42 | 6:42 | 19:27 | 0 | 0 | 12.75 | 12.75 | During String current checking found 8 nos. Module JB found. | Close | 0.0011917 | 6.6503 | 174.9655 | PTW305652
1671 | 2025-07-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:21 | 12.65 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:42 | 6:42 | 6:42 | 19:21 | 0 | 0 | 12.65 | 12.65 | Module Remove for damage module replacement work | Close | 0.00097435 | 5.5071 | 119.3986 | PTW302441
1672 | 2025-07-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:21 | 12.65 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:42 | 6:42 | 6:42 | 19:21 | 0 | 0 | 12.65 | 12.65 | Module Remove for damage module replacement work | Close | 0.0011824 | 5.5071 | 144.8881 | PTW304763
1673 | 2025-07-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:21 | 12.65 | IS13 |  |  |  |  | Tx | 0 | 1 | IS13Tx | 16599.6 | 4.954% | IDT | Manually stop due to IDT LV side thermography work | Manually stop due to IDT LV side thermography work | 12:34 | 12:34 | 12:34 | 13:15 | 0 | 0 | 0.68333 | 0.68333 | Manually stop due to IDT LV side thermography work | Close | 0.033851 | 0.51514 | 7183.0718 | PTW306053
1674 | 2025-07-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:21 | 12.65 | IS16 | INV3 | M1 |  |  |  | 1 | 1 | IS16INV3M1 | 2129.76 | 0.6356% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:42 | 6:42 | 7:08 | 7:46 | 0 | 0.43333 | 1.0667 | 1.0667 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.0067795 | 0.081427 | 145.6752 | PTW305917
1675 | 2025-07-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:21 | 12.65 | IS16 | INV3 | M2 |  |  |  | 1 | 1 | IS16INV3M2 | 1879.2 | 0.5608% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:32 | 7:32 | 7:32 | 7:46 | 0 | 0 | 0.23333 | 0.23333 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0013085 | 0.028347 | 44.7468 | PTW305917
1676 | 2025-07-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:21 | 12.65 | IS20 | INV2 | M1 |  |  |  | 1 | 1 | IS20INV2M1 | 2255.04 | 0.673% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:42 | 6:42 | 7:32 | 8:08 | 0 | 0.83333 | 1.4333 | 1.4333 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.0096458 | 0.14999 | 284.1122 | PTW305917
1677 | 2025-07-07 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:21 | 12.65 | IS20 | INV2 | M2 |  |  |  | 1 | 1 | IS20INV2M2 | 2255.04 | 0.673% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 7:55 | 7:55 | 7:55 | 8:08 | 0 | 0 | 0.21667 | 0.21667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0014581 | 0.045742 | 86.647 | PTW305917
1678 | 2025-07-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:25 | 19:32 | 13.1167 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:25 | 6:25 | 6:25 | 19:32 | 0 | 0 | 13.1167 | 13.1167 | Module Remove for damage module replacement work | Close | 0.0010103 | 5.0696 | 109.9125 | PTW302441
1679 | 2025-07-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:25 | 19:32 | 13.1167 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:25 | 6:25 | 6:25 | 19:32 | 0 | 0 | 13.1167 | 13.1167 | Module Remove for damage module replacement work | Close | 0.001226 | 5.0696 | 133.377 | PTW304763
1680 | 2025-07-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:25 | 19:32 | 13.1167 | IS15 | INV4 | M2 |  |  |  | 1 | 1 | IS15INV4M2 | 2004.48 | 0.5982% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:25 | 6:25 | 6:50 | 6:58 | 0 | 0.41667 | 0.55 | 0.55 | AC Breaker manually discharge & PU reset then inverter start. | Close | 0.00329 | 0.033194 | 55.8913 | PTW306126
1681 | 2025-07-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:25 | 19:32 | 13.1167 | IS15 | INV4 | M1 |  |  |  | 1 | 1 | IS15INV4M1 | 2192.4 | 0.6543% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 6:54 | 6:54 | 6:54 | 6:58 | 0 | 0 | 0.066667 | 0.066667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.00043618 | 0.0080383 | 14.8038 | PTW306126
1682 | 2025-07-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:25 | 19:32 | 13.1167 | IS20 | INV4 | M1 |  |  |  | 1 | 1 | IS20INV4M1 | 2255.04 | 0.673% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:25 | 6:25 | 6:25 | 6:37 | 0 | 0 | 0.2 | 0.2 | Auto Reboot and Run. | Close | 0.0013459 | 0.00657 | 12.4453 | PTW306126
1683 | 2025-07-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:37 | 19:31 | 12.9 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:37 | 6:37 | 6:37 | 19:31 | 0 | 0 | 12.9 | 12.9 | Module Remove for damage module replacement work | Close | 0.00099361 | 5.46 | 118.3772 | PTW302441
1684 | 2025-07-09 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:37 | 19:31 | 12.9 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:37 | 6:37 | 6:37 | 19:31 | 0 | 0 | 12.9 | 12.9 | Module Remove for damage module replacement work | Close | 0.0012057 | 5.46 | 143.6487 | PTW304763
1685 | 2025-07-10 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:26 | 19:24 | 12.9667 | IS1 | INV4 | M2 | SCB4 | Str_Typ6(445*58) |  | 0 | 0 | Str_Typ6(445*58) | 25.81 | 0.007702% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:26 | 6:26 | 6:26 | 19:24 | 0 | 0 | 12.9667 | 12.9667 | Module Remove for damage module replacement work | Close | 0.00099874 | 5.56 | 120.5453 | PTW302441
1686 | 2025-07-10 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:26 | 19:24 | 12.9667 | IS13 | INV3 | M1 | SCB5 | Str_Typ9(540*58) |  | 0 | 0 | Str_Typ9(540*58) | 31.32 | 0.009347% | Connectors | Module Remove for damage module replacement work | Module Remove for damage module replacement work | 6:26 | 6:26 | 6:26 | 19:24 | 0 | 0 | 12.9667 | 12.9667 | Module Remove for damage module replacement work | Close | 0.001212 | 5.56 | 146.2796 | PTW304763
1687 | 2025-07-10 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:26 | 19:24 | 12.9667 | IS1 | INV1 | M1 |  |  |  | 1 | 1 | IS1INV1M1 | 2064.8 | 0.6162% | Inverter | Fan abnormal alarm | Running on half load due to fan failuer. | 14:00 | 14:00 | 14:00 | 19:24 | 0 | 0 | 5.4 | 5.4 | After Genration Fan Replace and issue resolve. | Close | 0.033274 | 2.0457 | 3548.198 | PTW306687
1688 | 2025-07-10 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:26 | 19:24 | 12.9667 | IS1 | INV1 | M2 |  |  |  | 1 | 1 | IS1INV1M2 | 2090.61 | 0.6239% | Inverter | Fan abnormal alarm | Running on half load due to fan failuer. | 14:00 | 14:00 | 14:00 | 19:24 | 0 | 0 | 5.4 | 5.4 | After Genration Fan Replace and issue resolve. | Close | 0.03369 | 2.0457 | 3592.5505 | PTW306687
1689 | 2025-07-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:31 | 19:32 | 13.0167 | IS17 | INV4 | M2 |  |  |  | 1 | 1 | IS17INV4M2 | 2004.48 | 0.5982% | Inverter | Inverter trip in Abnormar Deration of fan(DSP-Com-flt) | Inverter trip in Abnormar Deration of fan(DSP-Com-flt) | 6:31 | 6:31 | 6:55 | 19:32 | 0 | 0.4 | 13.0167 | 13.0167 | OEM engineer inspection and found LVRT, Fuses,PE card and control cables are faulty. So, due to unavailability of control cable Unit is under B/D. | Close | 0.077864 | 4.1823 | 7042.0498 | PTW307089
1690 | 2025-07-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:31 | 19:32 | 13.0167 | IS17 | INV4 | M1 |  |  |  | 1 | 1 | IS17INV4M1 | 2004.48 | 0.5982% | Inverter | Manually stop for Inv Unit_2 rectification work | Manually stop for Inv Unit_2 rectification work | 7:33 | 7:33 | 7:33 | 9:00 | 0 | 0 | 1.45 | 1.45 | Manually stop for Inv Unit_2 rectification work | Close | 0.0086738 | 0.50494 | 850.2179 | PTW307089
1691 | 2025-07-13 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:22 | 19:34 | 13.2 | IS7 |  |  |  |  | Tx | 0 | 1 | IS7Tx | 16443 | 4.907% | IDT | IDT trip in under diffencial oprate | IDT trip in under diffencial oprate | 6:22 | 6:22 | 7:10 | 12:33 | 0 | 0.8 | 6.1833 | 6.1833 | During Visual inspection LV side found CTs damage and after that check all related parameters & connection IDT charge | Close | 0.30342 | 3.1931 | 44104.2242 | PTW307131
1692 | 2025-07-13 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:22 | 19:34 | 13.2 | IS7 | INV2 | M1 |  |  |  | 1 | 1 | IS7INV2M1 | 2098.44 | 0.6262% | Inverter | Inverter trip in GFDI Pro falut | Inverter trip in GFDI Pro falut | 12:33 | 12:33 | 12:33 | 19:34 | 0 | 0 | 7.0167 | 7.0167 | checked related connection and parameter then the inverter and inverter Kept in observation. | Close | 0.04394 | 3.5925 | 6332.5301 | PTW307276
1693 | 2025-07-13 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:22 | 19:34 | 13.2 | IS7 | INV2 | M2 |  |  |  | 1 | 1 | IS7INV2M2 | 2004.48 | 0.5982% | Inverter | Inverter trip in GFDI Pro falut | Inverter trip in GFDI Pro falut | 12:33 | 12:33 | 12:33 | 19:34 | 0 | 0 | 7.0167 | 7.0167 | checked related connection and parameter then the inverter and inverter Kept in observation. | Close | 0.041973 | 3.5925 | 6048.984 | PTW307276
1694 | 2025-07-13 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:22 | 19:34 | 13.2 | IS17 | INV4 | M2 |  |  |  | 1 | 1 | IS17INV4M2 | 2004.48 | 0.5982% | Inverter | Inverter trip in Abnormar Deration of fan(DSP-Com-flt) | Inverter trip in Abnormar Deration of fan(DSP-Com-flt) | 6:22 | 6:22 | 6:22 | 19:34 | 0 | 0 | 13.2 | 13.2 | OEM engineer inspection and found LVRT, Fuses,PE card and control cables are faulty and replaced. | Close | 0.078961 | 6.6725 | 11235.1474 | PTW307294
1695 | 2025-07-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:13 | 12.75 | IS2 | INV4 | M2 |  |  |  | 1 | 1 | IS2INV4M2 | 2090.61 | 0.6239% | Inverter | Inverter tripped in AC switch disconnection fault | Inverter tripped in AC switch disconnection fault | 6:28 | 6:28 | 6:28 | 19:13 | 0 | 0 | 12.75 | 12.75 | As per instruction OEM Team remove the AC coil from the breaker, clean the breaker with the blower and use CRC Spray to clean coil contact points, manually charged and discharged the breaker for 2-3 times and then again installed the coil in the breaker, take the test of the inverter and now ok. | Close | 0.079546 | 5.6904 | 9993.0912 | PTW307503
1696 | 2025-07-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:13 | 12.75 | IS2 | INV4 | M1 |  |  |  | 1 | 1 | IS2INV4M1 | 2090.61 | 0.6239% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 8:25 | 8:25 | 8:25 | 8:42 | 0 | 0 | 0.28333 | 0.28333 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0017677 | 0.099305 | 174.394 | PTW307297
1697 | 2025-07-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:13 | 12.75 | IS2 | INV4 | M1 |  |  |  | 1 | 1 | IS2INV4M1 | 2090.61 | 0.6239% | Inverter | Manualy stop for Inv Unit_AC Coil failure rectification | Manualy stop for Inv Unit_AC Coil failure rectification | 10:15 | 10:15 | 10:15 | 10:52 | 0 | 0 | 0.61667 | 0.61667 | Manualy stop for Inv Unit_AC Coil failure rectification | Close | 0.0038473 | 0.39624 | 695.849 | PTW307297
1698 | 2025-07-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:13 | 12.75 | IS7 | INV2 | M1 |  |  |  | 1 | 1 | IS7INV2M1 | 2098.44 | 0.6262% | Inverter | Inverter trip in GFDI Pro falut | Inverter trip in GFDI Pro falut | 6:28 | 6:28 | 6:28 | 14:39 | 0 | 0 | 8.1833 | 8.1833 | checked all SCB Voc, found ok & inverter phase to phase and phase to ground voltage, found ok finally taken shutdown IDT-7 and found CT connection wire touch to LV-2 busbar, close the point and charge IDT sucessfully and then the inverter Run. | Close | 0.051246 | 4.6085 | 8123.5487 | PTW307462
1699 | 2025-07-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:13 | 12.75 | IS7 | INV2 | M2 |  |  |  | 1 | 1 | IS7INV2M2 | 2004.48 | 0.5982% | Inverter | Inverter trip in GFDI Pro falut | Inverter trip in GFDI Pro falut | 6:28 | 6:28 | 6:28 | 14:39 | 0 | 0 | 8.1833 | 8.1833 | checked all SCB Voc, found ok & inverter phase to phase and phase to ground voltage, found ok finally taken shutdown IDT-7 and found CT connection wire touch to LV-2 busbar, close the point and charge IDT sucessfully and then the inverter Run. | Close | 0.048952 | 4.6085 | 7759.8077 | PTW307462
1700 | 2025-07-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:13 | 12.75 | IS9 | INV1 | M1 |  |  |  | 1 | 1 | IS9INV1M1 | 2102.065 | 0.6273% | Inverter | Inverter trip in INS fault | Inverter trip in INS fault | 6:28 | 6:28 | 7:28 | 7:50 | 0 | 1 | 1.3667 | 1.3667 | Reboot the inverter and Run | Close | 0.0085733 | 0.16263 | 287.1603 | PTW307297
1701 | 2025-07-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:13 | 12.75 | IS9 | INV4 | M1 |  |  |  | 1 | 1 | IS9INV4M1 | 2244.31 | 0.6698% | Inverter | Inverter trip in INS fault | Inverter trip in INS fault | 6:28 | 6:28 | 7:28 | 7:50 | 0 | 1 | 1.3667 | 1.3667 | Reboot the inverter and Run | Close | 0.0091534 | 0.16263 | 306.5921 | PTW307297
1702 | 2025-07-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:13 | 12.75 | IS14 | INV3 | M2 |  |  |  | 1 | 1 | IS14INV3M2 | 2004.48 | 0.5982% | Inverter | Inverter trip in INS fault | Inverter trip in INS fault | 6:28 | 6:28 | 7:28 | 7:50 | 0 | 1 | 1.3667 | 1.3667 | Reboot the inverter and Run | Close | 0.0081753 | 0.16263 | 273.8293 | PTW307297
1703 | 2025-07-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:13 | 12.75 | IS7 |  |  |  |  | Tx | 0 | 1 | IS7Tx | 16443 | 4.907% | IDT | IDT trip manually due to LV side CT connection checking work | IDT trip manually due to LV side CT connection checking work | 13:58 | 13:58 | 13:58 | 14:39 | 0 | 0 | 0.68333 | 0.68333 | IDT trip manully LV side CT connection checking work due to inverter B/D | Close | 0.033531 | 0.45545 | 6290.8694 | PTW307462
[25 empty] | 445.7199 | 341421.42 | 5.6904
[25 empty] | 331.0167 | 5958.3 | 0.099305
[25 empty] | 625.6368 | 23774.2 | 0.39624
[25 empty] | 562.0152 | 276511.48 | 4.6085
[25 empty] | 562.0152 | 276511.48 | 4.6085
[25 empty] | 117.5612 | 9757.58 | 0.16263
[25 empty] | 117.5612 | 9757.58 | 0.16263
[25 empty] | 117.5612 | 9757.58 | 0.16263
[25 empty] | 650.6452 | 27327.1 | 0.45545
Formulas:
Days = DAY(EOMONTH(PA[[#This Row],[Month Year]],0))

## GA
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
Sr. No. | Date | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Breakdown Description | Fault Time | Work Completion time on fault | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(Wh/m2) | Approximate Energy Loss (KWh)
1 | 2022-07-06 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 18:13 | 19:30 | 1.2833 | Restored plant post Grid resumed | Close | 1.2833
2 | 2022-07-07 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 17:50 | 18:37 | 0.78333 | Restored plant post Grid resumed | Close | 0.78333
3 | 2022-07-07 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 18:51 | 19:30 | 0.65 | Restored plant post Grid resumed | Close | 0.65
4 | 2022-07-08 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 16:59 | 17:34 | 0.58333 | Restored plant post Grid resumed | Close | 0.58333
5 | 2022-07-10 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 14:13 | 14:26 | 0.21667 | Restored plant post Grid resumed | Close | 0.21667
6 | 2022-07-17 | FY22 | 2022 | Year_2 | Year_2 | 2022-07-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Outgoing line tripped in Over volatage | 16:00 | 16:15 | 0.25 | Restored plant post Grid resumed | Close | 0.25
7 | 2022-09-07 | FY22 | 2022 | Year_2 | Year_2 | 2022-09-01 | 30 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Line Shurt Down | 20:04 | 23:59 | 3.9167 | Restored plant post Grid resumed | Close | 3.9167
8 | 2022-09-12 | FY22 | 2022 | Year_2 | Year_2 | 2022-09-01 | 30 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Line tripped | 17:58 | 19:00 | 1.0333 | Restored plant post Grid resumed | Close | 1.0333
9 | 2023-01-22 | FY23 | 2023 | Year_2 | Year_2 | 2023-01-01 | 31 | 6:30 | 18:55 | 12.3833 | Grid | 335091.665 | 100% | Line tripped | 7:26 | 8:46 | 1.3333 | Restored plant post Grid resumed | Close | 1.3333
10 | 2023-05-18 | FY23 | 2023 | Year_2 | Year_2 | 2023-05-18 | 31 | 6:15 | 19:24 | 12.3833 | Grid | 335091.665 | 100% | Line Shurt Down | 19:46 | 23:25 | 3.65 | Restored plant post Grid resumed | Close | 3.65
11 | 2024-06-30 | FY24 | 2024 | Year_3 | Year_3 | 2024-06-30 | 30 | 6:21 | 19:41 | 12.3833 | Grid | 335091.665 | 100% | Line Shurt Down | 19:47 | 5:29 | 9.42 | Restored plant post Grid resumed | Close | 9.42
12 | 2024-07-01 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:21 | 19:43 | 12.3833 | Grid | 335091.665 | 100% | Emergency Line Shutdown | 9:04 | 10:29 | 1.25 | Restored plant post Grid resumed | Close | 1.25
13 | 2024-07-01 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:21 | 19:43 | 12.3833 | Grid | 335091.665 | 100% | Line Shut Down | 20:42 | 2:26 | 5.44 | Restored plant post Grid resumed | Close
14 | 2024-07-02 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:13 | 19:40 | 12.3833 | Grid | 335091.665 | 100% | Line Shut Down | 21:06 | 3:05 | 5.59 | Restored plant post Grid resumed | Close
15 | 2024-07-05 | FY24 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 6:19 | 19:39 | 12.3833 | Grid | 335091.665 | 100% | Line Shurt Down From GSS End due to Maintenance Work Purpose | 20:39 | 2:53 | 6.14 | Restored plant post Grid resumed | Close
16 | 2024-08-19 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:47 | 19:10 | 12.3833 | Grid | 335091.665 | 100% | Line Shurt Down From GSS End due to Maintenance Work Purpose | 21:00 | 6:00 |  | Restored plant post Grid resumed | Close | 0
17 | 2024-08-28 | FY24 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 6:42 | 19:05 | 12.3833 | Grid | 335091.665 | 100% | Line Trip From GSS End due to Bus-1 fail | 10:20 | 13:35 | 3.25 | Restored plant post Grid resumed | Close | 3.25 | 2.18
18 | 2024-09-19 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 7:00 | 18:42 | 12.3833 | Grid | 335091.665 | 100% | 220KV Line trip due to GSS End ICT trip during load shifting. | 8:09 | 9:26 | 1.2833 | Restored plant post Grid resumed | Close | 1.2833
19 | 2024-09-20 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 6:53 | 18:37 | 12.3833 | Grid | 335091.665 | 100% | 220KV Line trip GSS End due to other line Y-phase Jumper Open. | 12:01 | 14:04 | 2.05 | Restored plant post Grid resumed | Close | 2.05
20 | 2024-09-21 | FY24 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 7:34 | 18:38 | 12.3833 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Bus Jumper Replace Work. | 6:50 | 7:30 | 0.66667 | Restored plant post Grid resumed | Close | 0.66667
21 | 2024-12-11 | FY24 | 2024 | Year_3 | Year_3 | 2024-12-11 | 31 | 7:28 | 17:56 | 12.3833 | Grid | 335091.665 | 100% | 220KV Jaisalmer blackout occurred when the main line (Aakl-1 & 2) tripped. | 12:13 | 16:10 | 3.95 | Restored plant post Grid resumed | Close | 3.95 | 3.097 | 922015
22 | 2024-12-30 | FY24 | 2024 | Year_3 | Year_3 | 2024-12-11 | 31 | 7:36 | 18:07 | 12.3833 | Grid | 335091.665 | 100% | Line tripped from GSS End. | 18:11 | 21:00 |  | Restored plant post Grid resumed | Close | 0
23 | 2025-02-05 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:32 | 18:31 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to New T/F Jumper Work. | 18:52 | 22:13 |  | Restored plant post Grid resumed | Close | 0
24 | 2025-02-06 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:31 | 18:31 | 12.45 | Grid | 335091.665 | 100% | 220KV Line trip due to GSS End ICT trip during load shifting. | 11:30 | 12:28 | 0.96667 | Restored plant post Grid resumed | Close | 0.96667 | 0.92 | 262004
25 | 2025-02-25 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:18 | 18:23 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Aux. Bus Charge. | 18:25 | 18:46 |  | Restored plant post Grid resumed | Close | 0
26 | 2025-02-25 | FY25 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 7:18 | 18:23 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Relay Inspection work. | 19:31 | 3:27 |  | Restored plant post Grid resumed | Close | 0
27 | 2025-03-03 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:18 | 18:50 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End For erection and stringing work in new 220 KV LV side bay-206 for ICT-2 of New 400/220 KV 500 MVA ICT2 | 19:15 | 4:34 |  | Restored plant post Grid resumed | Close | 0
28 | 2025-03-04 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:14 | 18:48 | 12.45 | Grid | 335091.665 | 100% | 220kV line manually tripped(S/D) from 400kV GSS Bhainsara for erection and stringing work in new 220 KV LV side bay-206 for ICT-2 of New 400/220 KV 500 MVA ICT3 at 400 kV GSS Bhainsara. | 19:15 | 5:37 |  | Restored plant post Grid resumed | Close | 0
29 | 2025-03-05 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:08 | 18:50 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End For erection and stringing work in new 220 KV LV side bay-206 for ICT-2 of New 400/220 KV 500 MVA ICT2 | 19:00 | 1:00 |  | Restored plant post Grid resumed | Close | 0
30 | 2025-03-07 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:11 | 18:50 | 12.45 | Grid | 335091.665 | 100% | 220kV Line manually tripped(S/D) by 400kV GSS, Bhainsara for erection and stringing work in new 220 KV LV side (for New 400/220 KV 500 MVA ICT2) | 19:15 | 0:15 |  | Restored plant post Grid resumed | Close | 0
31 | 2025-03-21 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 7:01 | 18:56 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Bay maintinance. | 20:01 | 5:20 |  | Restored plant post Grid resumed | Close | 0
32 | 2025-03-29 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 6:49 | 19:01 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Bay maintinance. | 21:50 | 4:29 |  | Restored plant post Grid resumed | Close | 0
33 | 2025-03-30 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 6:46 | 19:03 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Bay maintinance. | 19:30 | 6:52 |  | Restored plant post Grid resumed | Close | 0
34 | 2025-03-31 | FY25 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 6:45 | 19:02 | 12.45 | Grid | 335091.665 | 100% | 220KV Line Shutdown to GSS End due to Bay maintinance. | 6:45 | 7:18 | 0.55 | Restored plant post Grid resumed | Close | 0.55 | 0.025244 | 6940.6095
35 | 2025-04-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:38 | 19:06 | 12.45 | Grid | 335091.665 | 100% | Due to 220KV GSS End Line protection panel sparking issue, Load Down Zero. | 10:45 | 16:10 | 5.4167 | Restored plant post Grid resumed | Close | 5.4167 | 4.876 | 1317626.8056
36 | 2025-04-25 | FY25 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 6:28 | 19:11 | 12.45 | Grid | 335091.665 | 100% | Line Shut-Down for Switchyard Maintinance work | 18:25 | 3:09 | 8.44 | Restored plant post Grid resumed | Close | 8.44
37 | 2025-05-05 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 7:28 | 19:13 | 12.45 | Grid | 335091.665 | 100% | SF6 Line CB tripped Due to Fault at GSS End. (NTPC Feeder R-Phase Jumper broken) | 11:52 | 14:12 | 2.3333 | Restored plant post Grid resumed | Close | 2.3333 | 1.9244 | 525936
38 | 2025-05-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:21 | 19:17 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Active Power. | 12:48 | 15:07 |  |  | Close | 0 | 2.125 | 82821.875
39 | 2025-05-13 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:16 | 19:18 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 12:03 | 13:53 |  |  | Close | 0 | 1.79 | 36077.45
40 | 2025-05-18 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:22 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 12:05 | 14:15 |  |  | Close | 0 | 2.08 | 41615.6
41 | 2025-05-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:17 | 19:23 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 10:15 | 15:04 |  |  | Close | 0 | 4.445 | 87255.35
42 | 2025-05-23 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 11:21 | 13:34 |  |  | Close | 0 | 2.207 | 43891.7125
43 | 2025-05-31 | FY25 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 6:19 | 19:27 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 11:45 | 13:50 |  |  | Close | 0 | 1.912 | 38345.16
44 | 2025-06-01 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:31 | 19:25 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Current Load. | 10:06 | 13:45 |  |  | Close | 0 | 3.1 | 196137
45 | 2025-06-02 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:27 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 11:50 | 14:10 |  |  | Close | 0 | 2.16 | 43178.4
46 | 2025-06-03 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:16 | 19:26 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 12:25 | 14:01 |  |  | Close | 0 | 1.46 | 29889.85
47 | 2025-06-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:25 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Active Power. | 10:31 | 12:59 |  |  | Close | 0 | 2.2 | 84524
48 | 2025-06-04 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:17 | 19:25 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Active Power. | 12:59 | 14:44 |  |  | Close | 0 | 1.55 | 29775.5
49 | 2025-06-08 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:30 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Current Load. | 15:27 | 16:55 |  |  | Close | 0 | 0.881 | 29456.6755
50 | 2025-06-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Active Power due to 400KV Akal Line trip. | 13:49 | 14:43 |  |  | Close | 0 | 0.842 | 33309.52
51 | 2025-06-12 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 12.45 | Grid |  | 0% | Load Curtailment 30% of Active Power due to 400KV Akal Line trip. | 14:44 | 16:27 |  |  | Close | 0 | 1.24 | 68676.16
52 | 2025-06-13 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:29 | 12.45 | Grid |  | 0% | Load Curtailment 10% of Current Load due to 400KV Akal Line trip.(PPC Set Point 155MW) | 9:33 | 16:07 |  |  | Close | 0 | 5.487 | 432597.8235
53 | 2025-06-17 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:31 | 19:39 | 12.45 | Grid |  | 0% | Load Curtailment 20% of Current Load.(PPC Set Point 135MW) | 9:38 | 15:03 |  |  | Close | 0 | 2.56 | 244322.56
54 | 2025-06-18 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:22 | 19:36 | 12.45 | Grid |  | 0% | Load Curtailment @ 20% of Active Power due to heavy under drawl, high frequency. | 11:56 | 15:33 |  |  | Close | 0 | 3.22 | 133613.9
55 | 2025-06-19 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:12 | 19:28 | 12.45 | Grid |  | 0% | Load Curtailment @ 20% of Active Power due to heavy under drawl, high frequency. | 11:18 | 14:00 |  |  | Close | 0 | 2.46 | 102077.7
56 | 2025-06-20 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:18 | 19:35 | 12.45 | Grid |  | 0% | Load Curtailment @ 20% of Active Power due to heavy under drawl, high frequency. | 12:32 | 13:30 |  |  | Close | 0 | 0.925 | 38382.875
57 | 2025-06-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 12.45 | Grid |  | 0% | Load Curtailment @ 20% of Active Power due to heavy under drawl, high frequency. | 10:14 | 11:33 |  |  | Close | 0 | 1.072 | 44482.64
58 | 2025-06-22 | FY25 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 6:15 | 19:32 | 12.45 | Grid |  | 0% | Load Curtailment @ 40% of Active Power due to heavy under drawl, high frequency. | 11:34 | 14:05 |  |  | Close | 0 | 2.31 | 172536.21
59 | 2025-07-06 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:42 | 19:27 | 12.45 | Grid |  | 0% | Load Curtailment @ 20% of Active Power due to heavy under drawl, high frequency. | 11:21 | 14:58 |  |  | Close | 0 | 3.09 | 129780
60 | 2025-07-14 | FY25 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 6:28 | 19:13 | 12.45 | Grid |  | 0% | Load Curtailment @ 20% of Current Load. | 13:31 | 13:55 |  |  | Close | 0 | 0.30105 | 10115.28
Formulas:
Days = DAY(EOMONTH(GA[[#This Row],[Month Year]],0))

## Inv_SY
| 2013.18 | 2090.61 | 2090.61 | 2077.705 | 2090.61 | 2090.61 | 2090.61 | 2193.85 | 2090.61 | 2116.42 | 2064.8 | 2090.61 | 2064.8 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2111.49 | 2114.1 | 2061.9 | 2088 | 2088 | 1853.1 | 2111.49 | 2114.1 | 2114.1 | 2088 | 2061.9 | 2114.1 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2234.16 | 1985.92 | 2203.13 | 1954.89 | 2161.08 | 2442.96 | 1954.89 | 2234.16 | 1973.16 | 2020.14 | 2145.42 | 2004.48 | 2223.72 | 1973.16 | 2223.72 | 1973.16 | 1973.16 | 2270.7 | 1973.16 | 2239.38 | 2223.72 | 1973.16 | 2192.4 | 2088 | 2102.065 | 1991.43 | 2102.065 | 2212.7 | 2275.92 | 2023.04 | 2244.31 | 1959.82 | 2161.08 | 2129.76 | 1973.16 | 2239.38 | 1941.84 | 2255.04 | 1973.16 | 2223.72 | 2023.04 | 2196.895 | 2054.65 | 2275.92 | 2023.04 | 2181.09 | 2023.04 | 1785.965 | 2192.4 | 2129.76 | 1941.84 | 2255.04 | 2192.4 | 2004.48 | 2004.48 | 2208.06 | 1957.5 | 2035.8 | 2239.38 | 1941.84 | 2255.04 | 1941.84 | 2192.4 | 2004.48 | 2223.72 | 1910.52 | 2223.72 | 2004.48 | 2192.4 | 2004.48 | 2192.4 | 2004.48 | 1973.16 | 2192.4 | 2004.48 | 1941.84 | 2208.06 | 2223.72 | 2192.4 | 2004.48 | 2223.72 | 1973.16 | 2129.76 | 1973.16 | 2098.44 | 1847.88 | 2161.08 | 1973.16 | 2004.48 | 2004.48 | 1988.82 | 1722.6 | 1973.16 | 1753.92 | 2004.48 | 2004.48 | 2255.04 | 1941.84 | 2255.04 | 1973.16 | 2223.72 | 1973.16 | 2004.48 | 2004.48 | 2161.08 | 2255.04 | 2223.72 | 2223.72 | 2223.72 | 2255.04 | 2004.48 | 2223.72 | 2239.38 | 2255.04 | 2255.04 | 2255.04 | 2255.04 | 2004.48 | 2255.04 | 2004.48
Date | IS1_INV1_M1 | IS1_INV1_M2 | IS1_INV2_M1 | IS1_INV2_M2 | IS1_INV3_M1 | IS1_INV3_M2 | IS1_INV4_M1 | IS1_INV4_M2 | IS2_INV1_M1 | IS2_INV1_M2 | IS2_INV2_M1 | IS2_INV2_M2 | IS2_INV3_M1 | IS2_INV3_M2 | IS2_INV4_M1 | IS2_INV4_M2 | IS3_INV1_M1 | IS3_INV1_M2 | IS3_INV2_M1 | IS3_INV2_M2 | IS3_INV3_M1 | IS3_INV3_M2 | IS3_INV4_M1 | IS3_INV4_M2 | IS4_INV1_M1 | IS4_INV1_M2 | IS4_INV2_M1 | IS4_INV2_M2 | IS4_INV3_M1 | IS4_INV3_M2 | IS4_INV4_M1 | IS4_INV4_M2 | IS5_INV1_M1 | IS5_INV1_M2 | IS5_INV2_M1 | IS5_INV2_M2 | IS5_INV3_M1 | IS5_INV3_M2 | IS5_INV4_M1 | IS5_INV4_M2 | IS6_INV1_M1 | IS6_INV1_M2 | IS6_INV2_M1 | IS6_INV2_M2 | IS6_INV3_M1 | IS6_INV3_M2 | IS6_INV4_M1 | IS6_INV4_M2 | IS7_INV1_M1 | IS7_INV1_M2 | IS7_INV2_M1 | IS7_INV2_M2 | IS7_INV3_M1 | IS7_INV3_M2 | IS7_INV4_M1 | IS7_INV4_M2 | IS8_INV1_M1 | IS8_INV1_M2 | IS8_INV2_M1 | IS8_INV2_M2 | IS8_INV3_M1 | IS8_INV3_M2 | IS8_INV4_M1 | IS8_INV4_M2 | IS9_INV1_M1 | IS9_INV1_M2 | IS9_INV2_M1 | IS9_INV2_M2 | IS9_INV3_M1 | IS9_INV3_M2 | IS9_INV4_M1 | IS9_INV4_M2 | IS10_INV1_M1 | IS10_INV1_M2 | IS10_INV2_M1 | IS10_INV2_M2 | IS10_INV3_M1 | IS10_INV3_M2 | IS10_INV4_M1 | IS10_INV4_M2 | IS11_INV1_M1 | IS11_INV1_M2 | IS11_INV2_M1 | IS11_INV2_M2 | IS11_INV3_M1 | IS11_INV3_M2 | IS11_INV4_M1 | IS11_INV4_M2 | IS12_INV1_M1 | IS12_INV1_M2 | IS12_INV2_M1 | IS12_INV2_M2 | IS12_INV3_M1 | IS12_INV3_M2 | IS12_INV4_M1 | IS12_INV4_M2 | IS13_INV1_M1 | IS13_INV1_M2 | IS13_INV2_M1 | IS13_INV2_M2 | IS13_INV3_M1 | IS13_INV3_M2 | IS13_INV4_M1 | IS13_INV4_M2 | IS14_INV1_M1 | IS14_INV1_M2 | IS14_INV2_M1 | IS14_INV2_M2 | IS14_INV3_M1 | IS14_INV3_M2 | IS14_INV4_M1 | IS14_INV4_M2 | IS15_INV1_M1 | IS15_INV1_M2 | IS15_INV2_M1 | IS15_INV2_M2 | IS15_INV3_M1 | IS15_INV3_M2 | IS15_INV4_M1 | IS15_INV4_M2 | IS16_INV1_M1 | IS16_INV1_M2 | IS16_INV2_M1 | IS16_INV2_M2 | IS16_INV3_M1 | IS16_INV3_M2 | IS16_INV4_M1 | IS16_INV4_M2 | IS17_INV1_M1 | IS17_INV1_M2 | IS17_INV2_M1 | IS17_INV2_M2 | IS17_INV3_M1 | IS17_INV3_M2 | IS17_INV4_M1 | IS17_INV4_M2 | IS18_INV1_M1 | IS18_INV1_M2 | IS18_INV2_M1 | IS18_INV2_M2 | IS18_INV3_M1 | IS18_INV3_M2 | IS18_INV4_M1 | IS18_INV4_M2 | IS19_INV1_M1 | IS19_INV1_M2 | IS19_INV2_M1 | IS19_INV2_M2 | IS19_INV3_M1 | IS19_INV3_M2 | IS19_INV4_M1 | IS19_INV4_M2 | IS20_INV1_M1 | IS20_INV1_M2 | IS20_INV2_M1 | IS20_INV2_M2 | IS20_INV3_M1 | IS20_INV3_M2 | IS20_INV4_M1 | IS20_INV4_M2
2025-06-13 | 1.096% | -0.6661% | -0.3024% | 0.2345% | 0.451% | 0.3733% | 0.279% | -2.98% | -0.09824% | -1.675% | -9.327% | -0.577% | -8.184% | -0.8692% | 0.7453% | 0.8634% | -0.08373% | 0.108% | 0.1349% | 1.315% | -0.6644% | -0.5688% | 1.323% | 0.1958% | -0.6685% | 6.156% | -1.891% | -2.191% | -0.6754% | 0.0173% | 1.428% | -0.7266% | 30.29% | 30.83% | 32.28% | 30.88% | 0.8759% | 0.1712% | 0.1287% | -0.1957% | -3.117% | -7.078% | -2.338% | -7.703% | -9.734% | -9.266% | -7.485% | -3.261% | -4.931% | -4.048% | -1.547% | 2.944% | -3.783% | -2.694% | -4.213% | -4.731% | 2.63% | -5.643% | 3.394% | -4.432% | -4.378% | 2.669% | -4.797% | -2.178% | -1.348% | 1.768% | -1.624% | -4.73% | -6.81% | 0.6866% | -6.062% | 2.584% | -3.489% | -2.724% | 2.621% | -6.134% | 3.413% | -5.664% | 2.697% | -5.233% | 1.177% | -4.108% | 0.06542% | -6.023% | 1.336% | -3.531% | 0.799% | 9.373% | -3.393% | -2.169% | 4.458% | -4.57% | -3.248% | 2.834% | 1.969% | -3.862% | 4.381% | 2.206% | -4.051% | 5.069% | -4.358% | 5.463% | -2.144% | 3.439% | -3.818% | 5.723% | -3.311% | 2.693% | -2.44% | 2.612% | -2.153% | 4.095% | 3.487% | -2.966% | 2.844% | 5.361% | -2.999% | -3.533% | -2.785% | 3.054% | -3.88% | 3.842% | -0.363% | 4.464% | 0.422% | 8.593% | -1.653% | 4.513% | 3.025% | 2.946% | 3.274% | 12.3% | 2.955% | 10.79% | 2.166% | 2.295% | -3.403% | 5.987% | -3.32% | 5.426% | -2.459% | 4.655% | 3.722% | 3.03% | -0.9058% | -3.97% | -2.561% | -2.764% | -2.493% | -3.643% | 4.287% | -2.505% | -3.829% | -4.424% | -4.57% | -4.703% | -4.207% | 3.425% | -3.542% | 3.699%
2025-06-14 | -3.685% | -3.137% | -2.854% | -3.127% | -2.131% | -1.442% | -0.9393% | -3.8% | -1.265% | -1.699% | -11.78% | -2.573% | -10.48% | -3.296% | -1.159% | -0.9302% | -1.384% | -2.445% | -1.256% | -0.1285% | -1.101% | -2.854% | -1.152% | -1.487% | -2.992% | -4.437% | -4.686% | -4.982% | -1.317% | -0.788% | -0.05139% | -0.5509% | 1.118% | 1.682% | 2.246% | 1.103% | 1.432% | -0.5522% | 0.4659% | -0.3479% | 1.51% | -9.195% | 3.315% | -10.52% | -8.611% | -0.7807% | -10.18% | 2.676% | -5.972% | -4.434% | -3.212% | -1.661% | -3.616% | -2.307% | -2.76% | -4.008% | -4.07% | -2.768% | -4.231% | -2.569% | -3.106% | -4.037% | -4.818% | -5.198% | -2.813% | -3.171% | -3.431% | -2.581% | -3.486% | -2.23% | -3.601% | -4.617% | -2.633% | -4.116% | -2.287% | -2.848% | -2.985% | -1.759% | -3.395% | -2.126% | -1.934% | -1.64% | -1.448% | -2.741% | -1.795% | -2.077% | -1.033% | -2.129% | 0.8097% | -0.7166% | -0.2318% | 0.7873% | -0.05654% | 0.6848% | -0.6282% | 1.22% | 2.203% | 1.797% | 2.07% | 2.564% | 1.514% | 2.433% | 1.295% | 1.623% | 2.046% | 1.384% | 2.456% | 1.759% | 1.993% | 1.356% | 3.769% | 2.945% | 1.935% | 2.376% | 1.96% | 2.568% | 3.217% | 2.892% | 3.033% | 2.538% | 2.946% | 3.2% | 4.436% | 3.42% | 4.759% | 3.055% | 3.105% | 3.859% | 3.184% | 4.528% | 3.467% | 2.219% | 2.118% | 2.413% | 1.556% | 2.754% | 5.716% | 5.672% | 7.089% | 6.84% | 6.95% | 6.407% | 5.527% | 3.05% | 5.503% | 5.888% | 4.474% | 4.648% | 5.044% | 4.424% | 5.826% | 6.494% | 4.822% | 4.908% | 5.871% | 4.766% | 4.913% | 4.932% | 5.108% | 4.983%
2025-06-15 | 0.1586% | 1.554% | 1.587% | 1.129% | 2.742% | 2.819% | 3.285% | 1.473% | 2.058% | 1.571% | -8.905% | 0.5696% | -7.395% | -0.3851% | 2.665% | 2.626% | 2.212% | 1.431% | 2.043% | 3.047% | 1.883% | 0.3472% | 1.912% | 1.334% | -0.2017% | -1.807% | -1.962% | -2.045% | 1.182% | 1.43% | 1.862% | 1.662% | 1.819% | 2.643% | 4.262% | 2.909% | 3.125% | 1.234% | 1.894% | 0.6726% | 3.794% | -7.975% | 4.425% | -9.407% | -7.202% | 1.109% | -8.452% | 4.463% | -3.21% | -1.573% | -0.2054% | 0.8638% | -0.02% | 0.9035% | -0.2673% | -1.831% | -1.79% | -0.7685% | -1.215% | -0.2377% | -0.7377% | -1.01% | -2.781% | -3.071% | -1.065% | -1.596% | -1.53% | -1.622% | -1.487% | -0.7307% | -3.792% | -3.05% | -0.6722% | -1.882% | -0.07864% | -0.8875% | -0.8178% | 0.394% | -0.5795% | 0.03361% | -1.464% | -0.8636% | -1.734% | -2.705% | -1.839% | -2.555% | -0.7288% | -2.525% | 0.9487% | -1.14% | -0.5683% | 0.66% | -0.4616% | 0.3593% | -0.8897% | 0.7082% | 0.1431% | -0.5765% | -0.1731% | 0.218% | -0.179% | 0.4041% | -0.4318% | -0.2278% | -0.3036% | -0.7539% | -0.1099% | -1.145% | -0.5002% | -1.331% | 0.7838% | -0.3794% | -1.302% | -0.4143% | -0.8859% | -0.07911% | -0.1173% | -0.7446% | -0.6125% | -3.908% | -1.262% | -1.162% | 0.6494% | -0.2619% | 0.8963% | -1.704% | -1.379% | -1.186% | -1.542% | -0.5866% | -1.523% | -2.407% | -2.725% | -2.382% | -2.156% | -1.379% | 2.563% | 2.292% | 3.435% | 2.749% | 2.586% | 1.471% | 1.061% | 0.8159% | 2.882% | 2.957% | 2.233% | 1.95% | 2.346% | 1.385% | 2.635% | 3.256% | 2.903% | 3.268% | 4.183% | 2.944% | 3.266% | 2.665% | 2.983% | 2.999%
2025-06-16 | 1.884% | 3.381% | 3.449% | 3.055% | 4.41% | 4.941% | 4.81% | 2.282% | 4.007% | 1.624% | -6.209% | 2.552% | -5.495% | 1.807% | 3.719% | 4.307% | 3.342% | 4.025% | 3.746% | 4.494% | 3.27% | 2.868% | 3.607% | 3.105% | 1.455% | -0.1023% | -4.698% | -1.997% | 3.217% | 2.721% | 3.538% | 3.041% | 3.168% | 4.594% | 5.234% | 4.337% | 4.668% | 2.916% | 3.044% | 2.538% | 3.517% | -6.331% | 4.043% | -8.012% | -6.784% | -0.4914% | -6.543% | 4.475% | -1.369% | 0.235% | 1.803% | 2.656% | 1.217% | 1.364% | 0.4856% | -0.8263% | 0.6612% | 0.3328% | 1.368% | 1.13% | 0.7731% | 1.287% | -1.003% | -0.958% | -0.325% | -1.907% | -0.6639% | -2.531% | -1.242% | -1.488% | -4.283% | -2.936% | 0.2024% | -1.326% | 1.81% | -1.211% | 0.9418% | 0.7343% | 1.557% | 0.1169% | -1.516% | -1.854% | -2.282% | -2.392% | -1.593% | -2.864% | -1.428% | -1.437% | -0.07748% | -1.452% | 0.7463% | -0.01814% | -0.2876% | 1.706% | 0.5909% | -0.0104% | 0.7895% | 0.8119% | 0.2116% | 2.041% | 0.05386% | 2.245% | 0.2854% | 1.487% | 0.1543% | 0.9755% | 0.8634% | 0.2021% | 0.9139% | 0.679% | 1.533% | 1.94% | 0.2627% | -0.8171% | -1.172% | 0.5613% | -0.458% | -1.386% | -1.073% | -0.9825% | -2.076% | -1.041% | 0.5677% | 1.203% | 0.7466% | -0.8185% | -1.763% | -1.104% | -1.445% | -0.9602% | -1.863% | -1.817% | -3.121% | -1.836% | -4.088% | -3.298% | -1.089% | 0.4202% | -1.481% | 0.1685% | -0.6297% | -1.404% | -1.135% | -1.857% | -2.17% | -2.829% | -2.083% | -2.417% | -1.562% | -1.994% | -0.8509% | -1.881% | -2.821% | -3.282% | -4.145% | -4.272% | -3.8% | -3.283% | -2.705% | -1.975%
2025-06-17 | 0.531% | -0.4098% | -0.6019% | -0.02236% | -0.1022% | 0.3884% | 0.3209% | -2.91% | -0.2787% | -2.01% | -6.814% | -1.203% | -6.345% | -1.025% | 1.592% | 1.749% | 0.5662% | 0.6259% | 0.7349% | 2.172% | -0.2535% | -0.2483% | 0.9361% | 0.2215% | -1.052% | 5.629% | -1.46% | -1.894% | -0.9888% | -1.225% | 0.4755% | -1.139% | 31.09% | 31.97% | 34% | 32.9% | 0.4144% | -0.3436% | -0.3098% | -0.6875% | -2.32% | -7.332% | -1.718% | -8.015% | -10.18% | -8.761% | -8.055% | -2.534% | -4.292% | -3.598% | -0.7699% | 2.433% | -2.761% | -1.826% | -3.897% | -4.226% | 1.624% | -5.155% | 2.331% | -4.319% | -4.265% | 1.717% | -4.555% | -2.075% | -1.828% | 0.6221% | -2.152% | -5.017% | -6.382% | -0.3734% | -6.088% | 1.172% | -3.338% | -2.86% | 2.166% | -5.182% | 3.33% | -4.798% | 2.537% | -4.035% | 0.1081% | -4.235% | -0.4733% | -5.957% | 0.4581% | -3.701% | 0.07319% | 7.589% | -2.32% | -1.809% | 4.059% | -4.044% | -2.954% | 2.393% | 1.39% | -3.248% | 3.583% | 1.56% | -4.107% | 3.656% | -4.573% | 3.506% | -3.395% | 1.66% | -4.701% | 3.489% | -4.211% | 0.7453% | -3.603% | 0.6384% | -3.298% | 2.142% | 2.096% | -3.891% | 0.6154% | 3.08% | -4.29% | -4.82% | -4.362% | 0.5842% | -5.288% | 1.367% | -2.071% | 2.276% | -1.19% | 5.534% | -3.433% | 2.091% | 1.361% | 1.725% | 0.2684% | 8.837% | 1.642% | 9.39% | 2.593% | 3.141% | -2.143% | 5.912% | -1.31% | 6.132% | -0.4728% | 5.305% | 4.535% | 3.948% | 1.775% | -0.8757% | 0.1299% | -0.13% | -0.352% | -1.914% | 5.463% | 0.08599% | -0.3922% | -1.274% | -1.56% | -1.529% | -1.121% | 4.975% | -0.1466% | 5.603%
2025-06-18 | 1.022% | 0.4799% | 0.9639% | 1.16% | 1.803% | 2.149% | 1.856% | -1.048% | 1.393% | 0.0713% | -4.636% | -0.07273% | -1.888% | -0.309% | 1.705% | 2.256% | 1.092% | 1.152% | 1.368% | 2.067% | 0.4778% | 0.4313% | 1.345% | 0.7238% | -0.3211% | 2.703% | -1.31% | -1.676% | 0.05734% | -0.292% | 1.485% | 0.4051% | 10.53% | 10.54% | 11.73% | 10.62% | 2.142% | 0.9647% | 1.138% | 0.7629% | -0.8226% | -7.835% | -0.253% | -9.058% | -9.665% | -6.362% | -8.406% | -0.4309% | -3.478% | -2.21% | -0.09518% | 2.471% | -1.616% | -1.109% | -2.02% | -3.166% | 1.661% | -2.814% | 2.122% | -1.554% | -1.657% | 1.662% | -2.839% | -1.648% | -0.5848% | 0.6723% | -0.8943% | -2.786% | -3.958% | 0.2899% | -3.628% | 0.691% | -1.812% | -1.748% | 2.044% | -3.465% | 2.22% | -2.342% | 1.987% | -2.439% | 0.7134% | -2.336% | -0.09966% | -3.188% | 0.8109% | -2.352% | 0.5058% | 4.346% | -1.136% | -1.389% | 2.953% | -1.684% | -1.251% | 2.398% | 1.313% | -1.403% | 2.813% | 1.481% | -2.133% | 2.856% | -2.932% | 2.644% | -1.995% | 1.202% | -3.111% | 2.072% | -2.492% | 0.4711% | -2.207% | 0.2164% | -1.725% | 1.906% | 1.345% | -2.212% | 0.7211% | 2.483% | -2.256% | -2.666% | -2.474% | 0.5225% | -3.143% | 1.126% | -0.4811% | 2.155% | -0.008265% | 3.286% | -1.888% | 1.421% | 0.5529% | 0.6255% | 4.016% | 5.456% | -0.5762% | 4.304% | -0.07226% | 0.3755% | -0.8224% | 4.724% | -0.5838% | 4.743% | 0.141% | 3.722% | 3.078% | 1.584% | 0.9528% | -0.8363% | 0.01672% | -0.2858% | -0.1126% | -1.233% | 3.828% | 0.06147% | -0.412% | -1.235% | -1.295% | -1.616% | -1.367% | 2.895% | -0.7595% | 3.386%
2025-06-19 | 0.7824% | 0.2877% | 1.021% | 0.9858% | 2.298% | 2.324% | 1.351% | -1.704% | 1.113% | -0.397% | -5.573% | -0.909% | -1.382% | -0.483% | 1.579% | 2.208% | 0.9331% | 0.8631% | 0.6787% | 1.368% | -0.3562% | -0.4892% | 1.017% | 0.1759% | -1.131% | 1.415% | -2.309% | -2.62% | -0.5521% | -0.7519% | 1.049% | -0.1865% | 8.544% | 8.34% | 9.126% | 8.002% | 1.312% | -0.2802% | 1.045% | 0.8225% | 1.755% | -6.55% | 2.167% | -7.327% | -8.108% | -3.949% | -7.228% | 1.781% | -5.454% | -3.566% | -2.973% | -0.8428% | -2.207% | -1.668% | -3.008% | -3.956% | 0.3003% | -3.468% | 1.414% | -2.347% | -2.118% | 1.089% | -3.118% | -1.868% | -1.65% | -0.5289% | -2.081% | -3.737% | -4.477% | -0.8864% | -4.18% | -0.2356% | -2.499% | -2.405% | 1.086% | -3.825% | 1.493% | -2.57% | 1.712% | -2.509% | -0.4034% | -3.074% | -1.252% | -3.959% | -0.5063% | -3.302% | -1.118% | 1.416% | -2.173% | -2.285% | 1.602% | -2.114% | -1.528% | 1.998% | 1.235% | -1.437% | 2.461% | 1.417% | -1.626% | 2.92% | -2.661% | 2.492% | -1.926% | 1.151% | -3.005% | 1.803% | -2.539% | 0.2534% | -2.367% | -0.2889% | -1.519% | 1.878% | 1.679% | -1.603% | 0.7986% | 2.657% | -1.917% | -2.214% | -2.091% | 0.638% | -2.689% | 1.26% | -0.4236% | 2.179% | 0.292% | 4.058% | -1.389% | 2.012% | 5.642% | 6.402% | 0.7259% | 4.528% | 0.3872% | 5.081% | 1.017% | 1.31% | 0.8851% | 5.682% | 1.593% | 6.012% | 0.4259% | 4.399% | 4.33% | 2.513% | 2.269% | 0.8885% | 1.629% | 1.255% | 1.41% | 0.6056% | 5.211% | 2.068% | 1.134% | 0.509% | 0.5722% | 0.5321% | 0.744% | 4.255% | 1.123% | 4.955%
2025-06-20 | 2.152% | 3.747% | 3.406% | 3.166% | 4.346% | 4.909% | 5.565% | 3.274% | 3.932% | 3.321% | -0.4254% | 4.159% | 2.209% | 3.294% | 4.228% | 4.106% | 3.386% | 3.114% | 3.512% | 3.981% | 2.678% | 2.273% | 2.774% | 2.341% | 1.011% | 1.129% | -0.3267% | -0.5478% | 2.705% | 3.592% | 3.16% | 2.545% | 7.381% | 6.953% | 7.782% | 7.101% | 4.945% | 3.24% | 3.764% | 3.305% | 3.006% | -8.281% | 3.3% | -8.425% | -7.393% | -1.322% | -7.217% | 3.676% | -0.4812% | 0.5723% | -100% | -100% | 1.192% | 2.291% | 0.6443% | 0.4318% | 1.339% | 0.2929% | 1.528% | 1.073% | 0.4156% | 1.04% | 0.1692% | -0.04185% | 0.3056% | -0.5409% | -0.3126% | -2.134% | -1.399% | -0.4214% | -1.612% | -0.8436% | -0.1883% | -1.255% | 1.443% | -1.601% | 1.053% | -0.001093% | 1.357% | -0.596% | -0.4346% | -1.416% | -0.5213% | -1.907% | -0.3047% | -1.808% | -0.4242% | 0.6206% | 0.4406% | -0.9465% | 1.588% | 0.6577% | 0.7952% | 2.829% | 1.997% | 0.7479% | 2.53% | 1.112% | 0.3022% | 1.873% | 0.09934% | 1.923% | -0.03217% | 1.016% | -0.6901% | 1.021% | -0.426% | -0.08727% | -0.4892% | -0.2328% | -0.01204% | 0.9249% | -0.4464% | -1.046% | 0.3714% | 1.552% | -0.6942% | -1.193% | -1.588% | -1.32% | -1.618% | -0.06262% | 0.6208% | 0.9558% | 0.7066% | 1.032% | -1.324% | 0.1358% | 0.7717% | 1.476% | 0.3781% | 1.712% | 1.029% | 1.881% | -0.1735% | 0.2421% | 1.951% | 4.233% | 2.848% | 4.079% | -5.002% | 1.535% | 3.691% | 1.82% | 3.84% | 3.214% | 3.188% | 2.818% | 2.567% | 1.543% | 4.455% | 3.645% | 3.654% | 3.158% | 3.331% | 2.973% | 3.297% | 4.784% | 3.084% | 5.105%
2025-06-21 | 2.328% | 4.802% | 4.812% | 4.595% | 6.18% | 5.948% | 6.875% | 5.354% | 5.133% | 4.442% | 1.58% | 5.048% | 5.413% | 4.126% | 6.621% | 6.282% | 6.267% | 2.329% | 5.39% | 5.392% | 5.549% | 4.445% | 4.808% | 4.501% | 1.666% | 0.08405% | 0.9915% | 0.3838% | 4.64% | 6.23% | 4.939% | 4.157% | 5.888% | 5.811% | 7.015% | 5.955% | 6.145% | 3.874% | 5.599% | 3.929% | 9.097% | -4.843% | 9.576% | -4.87% | -3.018% | 5.053% | -4.461% | 9.691% | -4.333% | -3.213% | -100% | -100% | 1.007% | 3.482% | 0.3863% | -0.1454% | 0.06516% | 1.181% | 1.705% | 1.986% | -0.02842% | 1.214% | -0.6013% | -1.286% | 0.06371% | -1.46% | -0.3874% | -0.9952% | -0.7274% | -0.5837% | -0.9851% | -3.117% | 1.001% | -2.473% | 0.2183% | -1.402% | -0.7278% | 1.377% | -3.249% | -2.775% | -1.23% | -0.6607% | -0.7184% | -1.58% | -0.9623% | -1.694% | 0.413% | -1.784% | 2.134% | 0.2108% | 1.242% | 1.848% | 1.911% | 2.653% | 1.483% | 2.269% | 3.038% | 1.47% | 1.718% | 1.658% | 1.853% | 1.701% | 1.205% | 0.5448% | 2.162% | 0.6624% | 2.12% | 0.1913% | 1.785% | 0.8073% | 3.46% | -0.0141% | 0.3482% | 0.2946% | 0.06128% | 0.2758% | 0.8953% | -0.5814% | 0.442% | -1.478% | -0.6142% | -0.463% | 2.307% | -0.8168% | 2.665% | -1.156% | -1.032% | -0.4286% | -0.4638% | 1.491% | 0.3697% | -1.169% | 0.1365% | -1.374% | -2.912% | -2.686% | 0.1381% | -0.3628% | 0.8428% | -0.4471% | 0.02313% | 0.147% | -0.6016% | -0.8745% | -0.8557% | -0.6706% | -1.195% | -1.064% | -0.5158% | -1.558% | -0.8537% | -0.0331% | -0.6438% | -0.6128% | -0.3055% | -1.884% | -1.38% | -1.818% | -0.05598% | -1.077%
2025-06-22 | 1.36% | 1.401% | 0.7888% | 0.929% | 1.673% | 1.53% | 2.214% | -0.8486% | 1.794% | 1.119% | -1.815% | 1.731% | -1.863% | 0.64% | 0.1831% | 1.415% | 0.4317% | -2.772% | 0.6592% | 1.188% | 0.5325% | -1.785% | 2.062% | 0.8552% | -0.2751% | 1.675% | -2.727% | -2.387% | 1.376% | 2.487% | 2.489% | 1.342% | 17.18% | 16.6% | 18.17% | 17.79% | 3.374% | 1.938% | 2.338% | -0.2057% | 0.4524% | -9.115% | 1.27% | -10.63% | -8.497% | -5.891% | -7.283% | 0.5153% | -3.834% | -3.098% | -1.048% | 2.067% | -6.276% | -1.083% | -2.518% | -4.251% | -0.1198% | -3.467% | 1.544% | -2.097% | -4.23% | 1.05% | -2.093% | -0.6807% | -0.5023% | 0.7586% | -2.463% | -4.263% | -3.955% | 0.2259% | -4.285% | -2.831% | -1.72% | -3.595% | 1.518% | -3.294% | -0.458% | -2.559% | 1.708% | -2.072% | 0.5582% | -2.495% | 0.5983% | -7.225% | 1.084% | -5.456% | 0.587% | 3.659% | -1.059% | -0.6795% | 3.475% | -1.26% | -0.9588% | 2.598% | 1.434% | -1.099% | 2.755% | 1.627% | -1.741% | 2.508% | -2.787% | 2.869% | -1.708% | 1.299% | -2.802% | 0.4512% | -2.183% | 0.5782% | -1.755% | -0.3729% | -1.121% | -1.827% | 1.375% | -1.752% | -0.5571% | 1.215% | -1.513% | -2.02% | -1.531% | 1.198% | -2.115% | 2.072% | 0.6171% | -1.057% | 1.335% | 0.6743% | -0.9767% | 2.089% | -1.651% | 2.547% | 2.029% | 5.533% | 2.278% | 5.029% | 0.08063% | 0.386% | -0.9858% | 4.103% | -0.7714% | 3.193% | -0.7257% | 3.469% | 2.901% | 1.576% | 1.137% | -0.6913% | -1.131% | -0.3475% | -0.4423% | -1.505% | 3.152% | 0.009831% | 0.1573% | -0.7064% | -0.0612% | -1.991% | -0.782% | 3.167% | -0.8079% | 3.111%
2025-06-23 | -0.2232% | 1.422% | 0.7757% | 0.5963% | 1.844% | 2.066% | 2.639% | 1.153% | 2.044% | 1.65% | 1.551% | 1.951% | 1.711% | 0.5531% | 1.138% | 1.799% | 1.162% | -0.1236% | 1.286% | 1.73% | 0.6255% | -0.7246% | 0.3864% | 0.1013% | -1.073% | -2.789% | -2.723% | -2.876% | 0.3995% | 1.508% | 0.8759% | 0.7126% | 2.252% | 2.204% | 2.943% | 2.174% | 3.079% | 1.016% | 1.677% | 0.2276% | 2.538% | -9.16% | 3.016% | -11.31% | -9.276% | -1.453% | -9.541% | 3.143% | -3.49% | -2.08% | -0.9949% | 0.05099% | -1.547% | 0.06537% | -1.389% | -2.901% | -2.142% | -0.8561% | -2.301% | -0.853% | -1.744% | -1.976% | -1.082% | -1.467% | -0.8076% | -1.722% | -1.802% | -2.359% | -1.747% | -1.363% | -1.835% | -3.244% | -1.15% | -2.797% | -0.3986% | -1.514% | -1.157% | -0.08074% | -1.046% | -0.8192% | -1.264% | -1.382% | -1.58% | -1.529% | -1.471% | -2.26% | -1.091% | -2.005% | 0.5807% | -1.173% | -0.1012% | 0.7631% | -0.01172% | 0.6309% | -0.4742% | 0.7572% | 1.322% | 0.6127% | 0.8193% | 0.7626% | -0.01104% | 0.5869% | -0.4881% | -0.2049% | -0.6908% | -0.7704% | -0.3095% | -1.022% | -0.8391% | -1.864% | 0.3185% | -0.2039% | -0.7597% | -0.6919% | -0.8354% | 0.04583% | 0.0744% | -0.6034% | -0.7513% | -1.319% | -1.209% | -1.116% | 0.7363% | 0.03535% | 0.7988% | -0.9167% | -1.343% | -0.9479% | -0.4649% | 0.6237% | -0.8386% | -1.27% | 0.1161% | -0.3504% | -0.9272% | -0.6135% | 2.72% | 3.313% | 3.237% | 2.969% | 3.688% | 3.37% | 3.417% | 1.249% | 2.807% | 2.779% | 2.518% | 2.514% | 2.638% | 1.692% | 2.976% | 3.408% | 3.51% | 3.174% | 3.604% | 2.825% | 2.924% | 2.549% | 3.161% | 3.172%
2025-06-24 | 0.04474% | 1.843% | 1.874% | 1.749% | 2.757% | 2.652% | 3.074% | 1.247% | 2.049% | 1.697% | 1.518% | 1.782% | 1.66% | 0.9027% | 1.751% | 2.021% | 1.028% | 0.932% | 1.152% | 1.977% | 0.2507% | -0.1508% | 0.2704% | -0.1181% | -1.579% | -3.235% | -2.884% | -3.147% | 0.4942% | 1.222% | 0.8444% | 0.4354% | 1.242% | 1.32% | 2.067% | 1.324% | 2.631% | 0.7587% | 1.263% | 0.7152% | 2.891% | -8.514% | 3.124% | -9.997% | -8.961% | -1.487% | -8.998% | 3.578% | -3.027% | -1.847% | -1.027% | -0.3061% | -1.069% | -0.2284% | -2.108% | -2.471% | -2.711% | -2.062% | -1.916% | -0.6648% | -1.155% | -2.093% | -1.636% | -1.948% | -2.347% | -3.025% | -2.873% | -2.905% | -3.206% | -2.203% | -3.237% | -3.047% | -2.557% | -2.561% | -1.224% | -2.171% | -1.004% | -0.4842% | -0.5183% | -1.156% | -1.653% | -1.832% | -1.983% | -1.943% | -2.009% | -2.994% | -2.533% | -3.049% | -0.717% | -2.566% | -1.221% | -0.5419% | -1.239% | -0.6064% | -1.733% | -0.6563% | 0.5054% | 0.5046% | 0.8223% | 1.121% | 0.4303% | 1.09% | 0.105% | 0.428% | -0.5263% | -0.273% | -0.08183% | -0.7185% | -0.6611% | -1.766% | 0.2033% | 0.6087% | -0.3972% | -0.2764% | -1.013% | 0.451% | 0.2726% | -0.08684% | -1.197% | -1.561% | -0.7235% | -0.5117% | 0.9452% | 0.6653% | 1.079% | -0.1309% | -0.6081% | -0.2367% | 0.07579% | 0.745% | -0.5533% | -0.8303% | 0.2049% | -0.4181% | -0.8316% | -0.434% | 3.254% | 3.719% | 3.58% | 3.564% | 4.14% | 3.818% | 3.974% | 1.668% | 3.61% | 3.53% | 3.295% | 3.059% | 3.388% | 2.404% | 3.276% | 4.009% | 4.1% | 3.568% | 4.213% | 3.597% | 3.722% | 3.61% | 1.813% | 3.892%
2025-06-25 | -0.5206% | 0.7208% | 0.6335% | 0.3989% | 1.745% | 2.122% | 2.607% | 1.013% | 1.598% | 1.018% | 1.051% | 1.472% | 2.005% | 1.198% | 2.46% | 2.537% | 2.149% | 0.6268% | 2.365% | 2.798% | 1.83% | -1.022% | 1.851% | 1.548% | 0.4437% | -1.163% | -1.385% | -1.336% | 2.145% | 2.156% | 1.745% | 1.881% | 2.192% | 2.288% | 3.905% | 2.848% | 3.835% | 1.403% | 2.018% | 0.119% | 2.266% | -9.627% | 2.736% | -11.04% | -8.993% | -1.903% | -9.037% | 2.899% | -3.251% | -1.334% | -0.09017% | 0.927% | -2.311% | 0.7963% | -0.9709% | -1.638% | -1.636% | -1.306% | -1.44% | -0.3979% | -2.005% | -1.776% | -1.84% | -2.023% | -1.725% | -2.715% | -2.614% | -3.199% | -2.954% | -2.526% | -3.372% | -4.103% | -2.137% | -3.761% | -1.223% | -2.913% | -1.578% | -1.021% | -2.992% | -1.497% | -2.134% | -2.401% | -2.151% | -4.453% | -2.04% | -3.186% | -2.055% | -4.256% | 0.05003% | -1.789% | -0.07705% | 0.2499% | -0.3329% | 0.08839% | -2.498% | 0.1655% | 0.7224% | -0.2192% | -0.1755% | -0.307% | -0.3186% | -0.01266% | -0.8878% | -1.138% | -1.173% | -1.895% | -0.7335% | -1.41% | -0.6904% | -1.191% | 0.4429% | -2.243% | -2.407% | -1.849% | -2.122% | -1.006% | -0.5562% | -1.319% | -1.428% | -1.664% | -1.359% | -0.8977% | 0.8047% | -1.854% | 1.369% | -2.13% | -0.939% | -0.7629% | -3.393% | -0.0225% | -1.124% | -1.838% | -0.7851% | -0.986% | -1.619% | -0.8373% | 4.105% | 5.425% | 4.487% | 4.663% | 4.32% | 4.076% | 3.714% | 1.492% | 5.354% | 4.833% | 2.582% | 4.122% | 4.269% | 3.114% | 4.537% | 4.683% | 3.611% | 4.817% | 5.4% | 2.997% | 4.774% | 5.415% | 3.427% | 5.496%
2025-06-26 | 2.02% | 2.387% | 0.4375% | 0.6823% | 0.9391% | 1.259% | 2.769% | 0.9135% | 3.737% | 3.56% | 1.606% | 3.261% | 0.9226% | 2.072% | 0.8257% | 1.438% | -0.04641% | -0.2931% | 1.266% | 2.237% | -0.1003% | 0.01412% | -0.1329% | -0.1778% | 0.1984% | -0.5845% | -1.235% | -1.924% | 1.185% | 1.063% | 1.379% | 1.303% | 4.137% | 4.145% | 4.508% | 3.393% | 4.084% | 1.932% | 2.299% | 2.583% | -0.7144% | -10.62% | -8.505% | -9.42% | -10.9% | -4.325% | -11.25% | -0.2343% | -2.513% | -0.4078% | 0.9838% | 2.878% | 0.09511% | 0.3836% | 0.7966% | -0.3927% | 1.165% | 0.7563% | 0.7606% | 1.824% | 1.443% | 0.8356% | 0.1844% | -0.01108% | 1.153% | 0.6698% | 0.4988% | 0.1482% | -0.567% | 1.009% | -0.4316% | 0.07877% | 0.4574% | 0.287% | 1.761% | 0.06842% | 1.798% | 0.9587% | 1.865% | 0.9052% | 1.152% | 0.7131% | -0.003974% | 0.3202% | 0.7454% | -0.547% | 1.46% | 0.4031% | 2.21% | 0.9449% | 2.519% | 2.052% | 1.821% | 3.268% | 1.879% | 1.816% | 2.76% | 1.921% | 1.047% | 1.731% | 1.096% | 1.938% | 0.8234% | 1.025% | 0.4092% | 0.6206% | 0.6831% | 0.1229% | 0.7808% | 0.2857% | 1.35% | 1.762% | -2.137% | -0.679% | -0.4762% | 0.5998% | 0.1409% | -0.4362% | -0.682% | -0.9744% | -1.118% | -0.4843% | 1.124% | 1.17% | 1.306% | -0.3142% | -0.9047% | -0.6033% | -0.5902% | 0.239% | -1.566% | -1.616% | -0.6794% | -0.6018% | -4.366% | -3.869% | -1.083% | 0.6357% | -1.478% | -0.02557% | -0.716% | -0.1711% | -0.1517% | -2% | -1.498% | -2.06% | -1.339% | -1.708% | -1.119% | -2.068% | -0.5088% | -1.366% | -2.031% | -2.825% | -3.209% | -3.744% | -3.462% | -2.598% | -2.847% | -1.279%
2025-06-27 | 4.901% | 6.173% | 5.42% | 5.757% | 5.976% | 6.221% | 7.176% | 5.055% | 6.18% | 6.34% | 4.478% | 5.763% | 4.803% | 4.485% | 5.831% | 5.904% | 5.207% | 3.576% | 4.824% | 5.633% | 4.197% | 1.819% | 3.801% | 3.545% | 1.759% | 1.018% | 0.7226% | 0.3164% | 3.957% | 4.702% | 3.773% | 3.112% | 3.767% | 3.548% | 5.785% | 4.593% | 5.15% | 2.993% | 2.168% | 1.782% | 3.877% | -7.057% | 3.8% | 1.772% | -7.407% | -1.428% | -7.739% | 4.228% | -0.01152% | 1.823% | 2.678% | 3.744% | 0.8779% | 4.001% | 1.642% | 0.7394% | 1.876% | 1.19% | 2.606% | 2.34% | 0.5487% | 2.556% | 0.9356% | 0.8896% | 0.7882% | 0.05763% | 0.278% | -1.121% | -1.787% | 0.114% | -17.05% | -4.442% | 0.7915% | -1.154% | 2.047% | -0.6637% | 1.324% | 1.33% | 1.666% | 1.108% | -0.5507% | -1.156% | -1.099% | -5.211% | -1.067% | -2.884% | 0.3735% | -2.034% | 1.38% | -0.3479% | 1.551% | 0.5727% | 0.4335% | 2.107% | 0.8556% | 0.6001% | 1.725% | -0.2264% | -0.9108% | -0.2026% | -1.035% | 0.338% | -1.204% | -0.9236% | -1.264% | -1.125% | -1.091% | -1.95% | -3.218% | -2.926% | -0.2083% | -13.23% | -3.2% | -2.926% | -4.23% | -1.652% | -5.041% | -4.434% | -5.324% | -4.631% | -5.14% | -4.359% | -1.689% | -6.729% | -2.137% | -6.614% | -5.355% | -5.18% | -11.7% | -3.242% | -4.875% | -5.357% | -4.023% | -4.101% | -4.122% | -3.569% | -0.7207% | 0.411% | -0.6163% | -2.151% | -0.4069% | -0.2324% | -1.416% | -2.188% | -0.4386% | -0.9245% | -2.058% | -1.481% | -1.194% | -3.338% | -0.5216% | -0.5141% | -2.638% | -1.498% | -1.193% | -3.474% | -1.859% | -0.9604% | -1.116% | -0.8542%
2025-06-28 | -2.974% | -2.647% | -2.959% | -2.209% | -2.262% | -2.73% | -1.953% | -2.918% | -1.443% | -0.9288% | -2.232% | -1.021% | -2.282% | -2.52% | -3.663% | -2.595% | -2.484% | -5.77% | -2.383% | -1.612% | -3.043% | -5.607% | -3.139% | -3.674% | -3.948% | -4.835% | -5.987% | -6.005% | -3.703% | -1.011% | -0.9853% | -2.286% | 1.553% | -0.3021% | -0.5406% | -1.435% | 0.01318% | -1.567% | 0.9627% | -0.9278% | 2.819% | -8.237% | 1.899% | 0.3991% | -8.295% | -1.552% | -7.349% | 3.363% | -5.654% | -4.421% | -3.356% | -1.589% | -6.052% | -2.999% | -4.203% | -6.554% | -4.466% | -3.801% | -3.831% | -3.256% | -4.08% | -3.847% | -3.301% | -2.916% | -3.245% | -3.298% | -4.577% | -5.071% | -4.724% | -2.584% | -4.39% | -3.947% | -3.156% | -4.176% | -1.293% | -3.589% | -1.876% | -1.607% | -1.792% | -1.833% | -2.12% | -2.964% | -2.811% | -4.633% | -2.95% | -5.241% | -2.91% | -4.392% | -0.05345% | -2.988% | -0.06542% | -0.2881% | 0.02689% | 1.942% | 1.196% | 1.253% | 4.744% | 3.771% | 2.567% | 4.49% | 2.212% | 4.337% | 2.413% | 3.413% | 1.623% | 2.795% | 2.101% | 2.458% | 1.945% | 2.599% | 3.515% | 3.65% | 1.23% | 2.608% | 2.9% | 4.549% | 3.049% | 2.088% | 2.501% | 3.029% | 1.781% | 3.837% | 4.35% | 3.727% | 4.194% | 3.563% | 2.75% | 4.019% | 3.916% | 5.765% | 4.996% | 4.294% | 5.701% | 5.532% | 2.557% | 2.719% | 4.419% | 6.364% | 4.977% | 6.483% | 5.139% | 5.544% | 5.349% | 4.044% | 6.821% | 5.292% | 4.586% | 5.533% | 5.362% | 3.961% | 5.86% | 5.728% | 4.202% | 4.5% | 5.148% | 4.356% | 4.964% | 6.702% | 4.386% | 7.745%
2025-06-29 | 0.05098% | 2.222% | 3.357% | 2.688% | 5.313% | 5.057% | 4.63% | 2.706% | 1.795% | 1.988% | 1.23% | 1.205% | 2.846% | 1.274% | 4.561% | 4.729% | 4.291% | 2.041% | 3.291% | 3.421% | 3.377% | 0.5658% | 4.349% | 3.307% | 0.2076% | -1.787% | -1.944% | -1.144% | 3.352% | 5.547% | 5.221% | 3.001% | 3.029% | 2.343% | 3.236% | 2.619% | 4.536% | 3.709% | 4.698% | 3.133% | 6.268% | 5.594% | 6.157% | 4.588% | -3.852% | 2.338% | -3.92% | 6.701% | -3.034% | -2.046% | -0.7033% | -0.06683% | -1.268% | 1.895% | -2.436% | -2.179% | -3.243% | -2.876% | -2.099% | -2.262% | -3.136% | -2.375% | -3.027% | -2.561% | -3.636% | -4.293% | -3.973% | -4.869% | -4.177% | -3.226% | -3.822% | -5.894% | -2.564% | -2.415% | -1.133% | -2.288% | -1.129% | -1.053% | -0.01531% | -0.8308% | -3.235% | -3.09% | -3.348% | -6.647% | -3.529% | -5.166% | -3.352% | -5.937% | -1.123% | -2.943% | -0.6148% | -0.5385% | 0.02041% | 2.169% | 1.198% | 0.1553% | 1.668% | -0.2273% | -0.3166% | 0.5912% | -0.174% | 1.148% | 0.2948% | 0.8346% | 0.01063% | 0.5158% | 0.3988% | -0.1207% | -0.06441% | 0.07519% | 2.436% | -0.328% | -2.582% | -1.063% | -1.235% | 0.1644% | -1.289% | -0.7596% | -2.078% | -1.751% | -1.466% | 0.2709% | 0.955% | -0.7344% | -7.657% | -0.07378% | -0.5783% | 0.7899% | -0.7953% | 2.112% | 1.626% | 1.179% | 1.658% | 1.406% | -2.109% | -1.358% | 0.0276% | 2.282% | 0.1345% | 1.189% | 1.323% | 1.55% | -0.675% | -0.4757% | 0.5255% | -0.2493% | -1.324% | -0.6057% | -0.3074% | -2.149% | -1.598% | -0.04718% | -1.748% | -0.9651% | -1.1% | -2.895% | -1.944% | -0.01644% | -2.105% | -0.1252%
2025-06-30 | -2.777% | -1.228% | -1.581% | -1.957% | -0.1328% | 0.5109% | 1.012% | -0.664% | -0.6406% | -1.003% | -0.3195% | -0.964% | 0.7242% | -0.4542% | 1.263% | 1.079% | 1.27% | 1.205% | 1.542% | 1.747% | 0.5592% | 0.433% | 1.145% | 0.4365% | -0.9073% | -2.5% | -2.693% | -2.571% | 1.202% | 2.263% | 1.887% | 1.222% | 2.197% | 1.839% | 2.713% | 1.543% | 3.271% | 1.646% | 1.985% | 1.344% | 6.146% | 6.467% | 4.83% | 5.208% | -4.822% | 2.075% | 6.604% | 5.93% | -3.896% | -2.562% | -1.483% | -1.05% | -1.075% | -0.2203% | -2.879% | -2.197% | -3.687% | -3.154% | -3.476% | -2.45% | -3.154% | -4.005% | -3.39% | -3.199% | -3.537% | -3.806% | -3.364% | -3.665% | -3.671% | -2.501% | -3.072% | -2.771% | -3.241% | -2.814% | -1.91% | -2.515% | -1.095% | -1.819% | -1.152% | -1.934% | -2.515% | -2.215% | -2.821% | -3.298% | -3.041% | -3.435% | -2.861% | -2.969% | 0.04012% | -2.363% | -0.3726% | -0.0441% | -0.2604% | 1.162% | 0.02035% | -0.134% | 1.121% | 0.2067% | -0.06051% | 0.4668% | -0.03837% | 0.9215% | -0.2172% | 0.6284% | -0.09845% | 0.05127% | 0.592% | 0.003163% | 1.076% | 0.6928% | 2.311% | 2.359% | -2.488% | -0.7692% | -0.4083% | 0.8982% | 0.8402% | 0.05261% | 0.5106% | 0.247% | 0.1485% | 0.7491% | 2.081% | 1.88% | 1.527% | 0.4061% | 0.2425% | 0.4032% | 0.9818% | 1.494% | 0.7419% | 0.537% | 0.6476% | -0.2872% | -2.668% | -1.229% | 0.9089% | 1.915% | 1.815% | 2.485% | 2.427% | 1.72% | 1.739% | 0.05687% | 2.178% | 1.783% | 2.265% | 1.893% | 1.813% | 0.5909% | 2.971% | 2.728% | 1.735% | 1.258% | 1.848% | 1.433% | 1.483% | 1.806% | 1.944% | 2.63%
2025-07-01 | 1.098% | 2.775% | 2.427% | 2.382% | 3.253% | 3.406% | 4.056% | 1.725% | 3.168% | 2.527% | 2.627% | 2.678% | 2.305% | 2.088% | 1.415% | 2.124% | 0.7783% | 0.5039% | 1.146% | 1.854% | 0.05432% | -0.07642% | -0.03107% | -0.378% | -1.013% | -2.377% | -2.503% | -2.633% | 0.5744% | 0.9518% | 0.5309% | 0.5086% | 1.98% | 1.83% | 2.741% | 1.539% | 2.703% | 0.5368% | 1.123% | 0.8312% | 0.5861% | 0.6273% | 1.186% | 1.264% | -9.977% | -3.108% | 1.197% | 0.9563% | -2.772% | -0.4695% | 0.3346% | 1.147% | -0.09341% | 0.6454% | -0.4919% | -1.042% | -0.8693% | -0.175% | -0.4211% | 0.622% | 0.08398% | -0.537% | -0.4585% | -0.9476% | -0.866% | -1.859% | -1.315% | -2.211% | -1.544% | -1.537% | -1.601% | -2.682% | -0.8739% | -2.118% | -0.05221% | -2% | -1.05% | 0.04099% | -0.4289% | -1.448% | -1.928% | -2.092% | -2.372% | -1.983% | -1.953% | -2.707% | -1.768% | -2.458% | 0.04215% | -1.754% | -0.2204% | 0.5269% | 0.1021% | 0.7629% | -0.3618% | 0.4296% | 0.9158% | 0.3922% | 0.2393% | 0.1653% | -1.594% | -0.01037% | -0.8288% | -0.5814% | -1.201% | -1.214% | -1.012% | -1.703% | -1.516% | -2.24% | -0.8219% | -0.3979% | -2.608% | -1.203% | -1.614% | -0.454% | -0.6087% | -1.246% | -1.45% | -1.821% | -1.891% | -1.838% | -0.1052% | -0.5844% | -0.8519% | -1.516% | -2.07% | -1.63% | -0.6213% | 0.1744% | -1.464% | -1.564% | -0.3825% | -1.149% | -3.849% | -2.513% | 1.825% | 2.435% | 2.583% | 3.248% | 2.683% | 1.785% | 1.747% | -0.7145% | 1.934% | 1.918% | 1.925% | 1.711% | 2.002% | 1.05% | 2.71% | 2.687% | 1.868% | 1.37% | 1.892% | 1.367% | 1.47% | 1.447% | 0.8066% | 1.954%
2025-07-02 | 0.03599% | 1.548% | 1.343% | 1.153% | 2.409% | 2.665% | 2.9% | 0.89% | 2.103% | 1.363% | 1.784% | 1.419% | 2.182% | 1.095% | 2.369% | 2.698% | 1.937% | 1.432% | 1.742% | 2.254% | 1.336% | 0.4676% | 1.28% | 0.9752% | -0.8014% | -2.351% | -2.297% | -2.364% | 1.334% | 2.024% | 1.566% | 1.168% | 1.974% | 2.013% | 3.132% | 1.792% | 2.72% | 0.7326% | 1.547% | 0.8165% | 3.123% | 2.729% | 3.716% | 3.161% | -3.749% | -0.1623% | 3.701% | 3.686% | -3.104% | -1.073% | -0.1285% | 0.3859% | -0.3074% | 0.7869% | -0.8932% | -1.4% | -1.983% | -1.235% | -1.318% | -0.4872% | -1.238% | -1.473% | -2.678% | -3.082% | -1.919% | -2.502% | -2.374% | -2.811% | -2.57% | -2.206% | -2.928% | -3.343% | -1.659% | -2.92% | -1.25% | -2.365% | -1.765% | -0.7659% | -1.354% | -1.494% | -2.247% | -2.063% | -2.222% | -3.038% | -2.258% | -2.8% | -1.988% | -2.596% | -0.3811% | -1.679% | -0.939% | -0.2372% | -0.6137% | 0.1412% | -0.9429% | -0.1197% | 0.5617% | 0.08922% | 0.1776% | 0.2302% | -1.861% | -0.07257% | -0.8004% | -0.7306% | -0.9019% | -1.192% | -0.6244% | -1.453% | -0.9782% | -1.75% | 0.004086% | -1.017% | -1.992% | -0.9234% | -1.257% | -0.2884% | -0.0579% | -0.8786% | -0.8078% | -1.591% | -1.279% | -1.198% | 0.4121% | -0.592% | 0.5131% | -1.116% | -1.453% | -1.078% | -1.051% | -0.007859% | -1.043% | -1.514% | -0.8455% | -1.413% | -2.095% | -1.729% | 1.642% | 1.988% | 2.289% | 2.419% | 2.554% | 1.125% | 1.708% | -0.09698% | 1.805% | 1.68% | 1.593% | 1.463% | 1.58% | 0.6227% | 2.04% | 2.319% | 2.04% | 1.596% | 1.931% | 1.17% | 1.377% | 1.447% | 1.219% | 1.95%
2025-07-03 | 2.761% | 5.224% | 4.816% | 4.186% | 6.021% | 5.771% | 5.623% | 0.8041% | 4.821% | 4.258% | 4.815% | 4.581% | 5.147% | 4.515% | -1.008% | 3.139% | 3.923% | -3.411% | 4.101% | 4.743% | 3.12% | -4.248% | 2.341% | 2.594% | -4.226% | -6.246% | -13.06% | -8.132% | -2.638% | -2.492% | -2.868% | -2.59% | 4.477% | 4.686% | 5.51% | 3.97% | 4.712% | 0.255% | 3.17% | 1.261% | 4.518% | -1.655% | 5.523% | -1.266% | 0.5369% | -2.415% | 4.765% | 4.841% | -5.002% | -1.342% | 2.393% | 3.126% | -5.625% | 2.706% | 1.031% | -5.546% | -2.708% | 0.417% | 0.0286% | 1.817% | -4.896% | 1.162% | -0.8002% | -0.6266% | 0.341% | -0.8147% | -4.762% | -4.209% | -1.552% | -0.8169% | -0.08392% | -6.793% | 1.52% | -3.478% | 2.061% | 0.3387% | 0.01066% | 2.195% | -2.065% | -0.3063% | -0.5995% | -0.05772% | -0.6456% | -7.043% | -1.119% | -7.138% | -0.8833% | -8.002% | -1.945% | -1.655% | -0.5975% | -3.946% | 0.1525% | 1.162% | -1.453% | 0.558% | 0.8927% | -0.3193% | -2.395% | 0.564% | -3.383% | 0.4662% | -0.1284% | -0.8089% | 0.6913% | -0.529% | 0.9766% | -0.1019% | -1.508% | -2.17% | 2.375% | -4.113% | -1.154% | -1.508% | -3.041% | -2.455% | -0.09425% | -1.51% | -1.605% | -4.482% | -1.708% | -0.7952% | 2.031% | -5.191% | 2.909% | -5.726% | -0.7211% | -0.5981% | -7.618% | -0.4323% | -1.295% | -2.569% | -1.34% | -2.413% | -2.47% | -1.324% | 0.5127% | 1.516% | 2.394% | -0.8469% | -0.1626% | 0.998% | -2.604% | 0.2447% | 3.447% | 3.429% | -2.528% | 1.674% | 1.416% | -2.582% | 1.788% | 3.011% | 1.416% | 0.4655% | 5.717% | 0.9255% | 4.764% | 4.429% | 2.599% | 3.539%
2025-07-04 | -1.859% | -0.04146% | -0.345% | -0.1444% | 0.7076% | 1.083% | 0.3606% | -0.5279% | 0.309% | -2.969% | 1.032% | 0.6309% | 1.403% | 2.399% | 2.657% | 2.783% | -8.774% | -8.372% | -7.326% | -6.982% | -8.331% | -9.026% | -7.53% | -8.366% | -0.1963% | -1.868% | -1.636% | -2.039% | 1.444% | 5.102% | 5.293% | 2.617% | 4.132% | 3.793% | 3.989% | 3.569% | 5.57% | 3.583% | 5.476% | 4.571% | 16.03% | 16.45% | 16.89% | 15.18% | 12.12% | 8.165% | 15.6% | 15.32% | -1.392% | 0.08642% | 1.247% | 1.604% | 0.3499% | 2.719% | -0.9681% | -1.332% | -1.278% | -2.546% | -0.2067% | -0.1827% | -3.07% | -1.879% | -3.632% | -3.274% | -4.279% | -7.506% | -6.249% | -9.838% | -7.712% | -9.868% | -10.4% | -12.18% | -5.555% | -11.04% | -5.463% | -10.04% | -8.05% | -5.461% | -6.357% | -9.228% | -10.2% | -10.92% | -9.101% | -11.09% | -8.22% | -8.929% | -6.545% | -7.6% | -1.858% | -5.241% | -2.611% | -2.087% | -1.088% | 1.502% | 1.078% | -0.03589% | 2.386% | 0.7184% | -0.1423% | 1.092% | 1.192% | 1.871% | 3.783% | 2.182% | 3.906% | 2.106% | 3.422% | 1.707% | 4.043% | 3.697% | 5.65% | 1.207% | -0.9076% | -2.536% | -2.252% | -0.8389% | -0.5055% | -2.482% | -1.638% | -2.904% | -1.905% | -0.6266% | 2.392% | 0.4875% | 3.428% | -0.6471% | -0.8589% | -0.6035% | -2.372% | -1.201% | 0.03337% | -1.363% | -2.102% | -2.388% | -3.256% | -2.508% | 2.686% | 2.204% | 6.422% | 4.362% | 1.96% | 2.313% | 1.584% | -1.196% | 10.1% | 9.206% | 6.334% | 7.009% | 7.326% | 3.163% | 9.052% | 9.222% | 4.463% | 5.003% | -17.53% | -2.92% | 8.698% | 10.51% | 3.706% | 7.998%
2025-07-05 | -1.698% | -0.6234% | -1.793% | -2.148% | -0.813% | -0.9029% | 0.09473% | -2.62% | 0.3024% | -0.5533% | -2.377% | -0.3915% | -2.435% | -1.228% | 1.261% | 0.3437% | 1.36% | 1.106% | 1.409% | 1.77% | 0.4576% | 0.3531% | 1.381% | 0.4439% | 0.4232% | -0.9708% | -2.072% | -1.967% | 1.648% | 3.208% | 3.238% | 2.52% | 4.918% | 4.09% | 4.341% | 3.624% | 5.003% | 3.548% | 3.733% | 3.28% | 3.862% | 3.451% | 4.133% | 3.253% | 0.1979% | -1.366% | 4.681% | 3.928% | -5.515% | -3.347% | -1.669% | 0.8701% | -2.001% | -1.374% | -1.26% | -1.399% | -1.452% | -1.875% | -3.175% | -2.393% | -3.191% | -3.192% | -2.249% | -2.695% | -2.691% | -3.228% | -1.855% | -2.884% | -2.958% | -1.51% | -2.874% | -2.099% | -1.772% | -1.946% | -0.6523% | -2.761% | -0.8032% | -2.316% | -1.178% | -3.874% | -11.89% | -12.57% | -10.8% | -12.64% | -11.13% | -12.09% | -11.9% | -11.56% | 1.252% | -1.359% | 1.403% | 0.622% | 1.187% | 3.713% | 3.116% | 1.997% | 5.311% | 3.824% | 1.367% | 3.092% | -0.2337% | 2.803% | 0.7441% | 1.452% | -0.2769% | 0.7767% | -0.3563% | -0.147% | -1.021% | -0.9456% | -0.4172% | 0.7773% | 1.155% | -0.6426% | -0.07386% | 1.405% | -0.6733% | -1.682% | -1.017% | -0.8697% | -1.598% | -0.2133% | 0.9589% | 1.046% | 1.076% | 0.8647% | -0.7051% | 0.1029% | -0.1507% | 1.015% | 0.1215% | -0.9241% | -0.5142% | -0.7553% | -0.04386% | 0.782% | 3.719% | 6.046% | 3.405% | 6.227% | 4.005% | 4.398% | 5.033% | 1.901% | 4.966% | 3.558% | 3.404% | 3.075% | 3.701% | 2.748% | 6.025% | 3.803% | 2.373% | 1.519% | 1.458% | 1.126% | 1.763% | 4.217% | 2.126% | 5.252%
2025-07-06 | 2.786% | 2.596% | 1.724% | 2.074% | 2.301% | 2.276% | 3.12% | -0.2863% | 2.752% | 2.262% | -0.9099% | 2.363% | -1.207% | 1.404% | 1.694% | 1.878% | 1.183% | 0.8019% | 1.068% | 1.865% | 0.2439% | -0.1926% | 0.9059% | 0.3286% | -0.6923% | 2.301% | -1.552% | -2.025% | 0.02738% | 0.8211% | 0.7344% | -0.3745% | 6.984% | 7.001% | 8.601% | 7.098% | 1.236% | -0.1819% | 0.1886% | -0.4292% | -0.702% | -1.064% | -0.07466% | -1.562% | -4.068% | -5.776% | -0.235% | -0.437% | -3.977% | -1.945% | -0.3058% | 2.823% | -1.932% | -0.4253% | -1.582% | -2.207% | 1.443% | -2.387% | 1.894% | -1.732% | -1.758% | 1.867% | -1.125% | 0.5569% | -0.1242% | 1.419% | -0.3829% | -2.156% | -3.235% | 1.144% | -3.049% | 0.4682% | -0.8049% | -1.374% | 2.949% | -2.752% | 2.583% | -1.339% | 2.41% | -2.029% | 1.27% | -1.85% | 0.4939% | -3.221% | 1.468% | -1.546% | 1.525% | 3.335% | -9.723% | -9.553% | -7.014% | -11.02% | -10.9% | -7.931% | -9.335% | -10.94% | 3.15% | 1.427% | -1.894% | 2.956% | -3.913% | 2.803% | -1.863% | 1.321% | -2.676% | 2.057% | -2.408% | 0.5571% | -2.065% | 0.3538% | -1.131% | -0.06714% | 1.762% | -1.623% | 0.5993% | 2.556% | -2.119% | -3.399% | -2.332% | 0.1122% | -2.559% | 1.726% | 0.07439% | 0.8255% | 1.18% | 3.198% | -1.062% | 2.339% | 0.1352% | 2.565% | 2.258% | 4.636% | 2.748% | 5.407% | 1.475% | 1.812% | 0.2837% | 5.581% | 0.7423% | 5.616% | 1.741% | 4.703% | 4.422% | 2.902% | 1.734% | 0.06892% | -0.4882% | 0.703% | 1.157% | -0.1842% | 4.539% | 1.336% | -0.6356% | -0.682% | -0.607% | -1.759% | -0.399% | 3.698% | -0.1979% | 3.762%
2025-07-07 | 2.312% | 4.412% | 4.471% | 3.714% | 5.73% | 5.397% | 5.309% | 2.629% | 3.953% | 2.728% | 2.522% | 3.593% | 1.98% | 3.41% | 4.088% | 4.077% | 3.812% | 2.204% | 3.581% | 4.453% | 3.703% | 2.384% | 4.442% | 4.018% | 2.248% | 1.82% | -0.4939% | 0.007819% | 3.625% | 3.683% | 2.985% | 2.604% | 2.413% | 2.305% | 4.888% | 3.186% | 3.643% | 1.981% | 2.739% | 1.952% | 3.449% | 3.61% | 4.571% | 3.428% | 0.9473% | -1.225% | 4.357% | 4.322% | -2.544% | 0.09622% | 0.567% | 2.706% | -0.5403% | 1.287% | -0.567% | -1.247% | 0.6217% | -0.9352% | 1.957% | 0.1048% | -0.5866% | 1.598% | -0.5431% | 0.6453% | -0.7042% | -1.105% | -0.9252% | -3.101% | -2.295% | -0.5934% | -2.595% | -1.06% | -0.6086% | -1.437% | 1.276% | -1.937% | 1.14% | 0.08765% | 1.61% | -0.3561% | -0.8649% | -2.032% | -1.932% | -3.67% | -1.693% | -3.613% | -0.9701% | -1.878% | -0.5442% | -1.879% | -0.2749% | -1.203% | -0.5692% | 2.099% | 0.7928% | -0.3883% | -7.923% | -8.981% | -10.56% | -9.197% | -12.63% | -9.355% | -11.71% | -10.52% | -2.11% | -0.2008% | -1.73% | -1.358% | -1.611% | -1.025% | -0.3667% | -0.1582% | -0.541% | -2.677% | -1.493% | -0.4175% | -2.424% | -3.488% | -3.025% | -1.306% | -2.685% | 0.2378% | -0.5363% | 1.164% | -0.536% | 0.6596% | -1.064% | 0.9743% | -1.196% | 0.5245% | 1.033% | 0.1822% | 0.624% | 0.02937% | -1.659% | -1.438% | -1.792% | 0.2684% | -1.73% | 0.1717% | -0.4116% | 0.2228% | 0.8408% | 0.04845% | 1.096% | -0.2584% | -0.4127% | -1.142% | -0.9498% | -2.317% | -0.3557% | -0.4446% | -1.004% | -0.301% | -3.074% | -1.845% | -0.4563% | 0.9367% | -1.014% | 1.684%
2025-07-08 | 5.692% | 6.335% | 6.097% | 6.246% | 7.547% | 7.923% | 8.051% | 5.261% | 6.613% | 7.216% | 5.433% | 5.683% | 5.625% | 5.221% | 5.755% | 6.567% | 3.705% | 2.677% | 3.134% | 4.366% | 1.858% | 1.769% | 0.4253% | 0.6729% | -1.026% | -1.409% | -0.9768% | -1.65% | 0.5967% | 0.4785% | -0.1394% | -0.03977% | -0.4731% | 0.0307% | 2.369% | 0.4617% | 1.056% | -0.7689% | -0.4072% | -1.168% | -3.788% | -4.204% | -3.464% | -4.211% | -6.338% | -6.3% | -2.044% | -2.492% | -0.09645% | 2.319% | 3.022% | 3.565% | 2.381% | 3.759% | 1.432% | 0.4772% | 2.116% | 2.229% | 2.439% | 3.271% | 2.33% | 2.087% | 1.037% | 1.368% | 1.47% | 0.3532% | 1.009% | -0.05391% | 0.8069% | 1.353% | 0.01842% | 0.1586% | 1.506% | 0.7168% | 2.354% | 0.8168% | 2.193% | 2.5% | 2.965% | 2.372% | 0.6993% | 0.89% | 0.2718% | 0.0898% | 0.3447% | -0.815% | 0.04018% | -0.6676% | 1.227% | -0.5729% | 0.04348% | -0.4757% | -1.931% | -1.627% | -2.912% | -2.178% | -2.572% | -2.754% | -3.545% | -3.121% | -5.581% | -3.809% | -5.344% | -5.194% | -6.478% | -6.299% | -6.242% | -6.861% | -6.861% | -7.742% | -6.067% | -6.231% | -3.971% | -4.83% | -6.798% | -5.119% | -5.43% | -5.668% | -6.587% | -7.979% | -6.372% | -5.902% | -5.294% | -5.665% | -5.332% | -6.447% | -6.357% | -5.774% | -4.888% | -3.174% | -5.223% | -5.383% | -3.539% | -3.197% | -2.797% | -2.435% | 2.333% | 2.584% | 3.272% | 3.171% | 2.458% | 0.5919% | 0.8291% | -1.064% | 4.071% | 3.63% | 4.091% | 3.42% | 3.373% | 1.914% | 3.576% | 3.85% | 4.548% | 4.111% | 3.546% | 2.742% | 3.182% | 3.659% | 4.232% | 4.805%
2025-07-09 | -0.1229% | 2.906% | 3.288% | 2.52% | 4.561% | 5.201% | 5.209% | 3.194% | 2.887% | -0.1887% | 3.352% | 3.064% | 3.531% | 3.555% | 4.415% | 4.779% | 2.599% | 1.538% | 1.861% | 3.375% | 0.6174% | 0.3184% | 1.217% | 0.6623% | -0.9248% | -1.699% | -1.651% | -2.671% | 1.195% | 1.727% | 0.9215% | 1.19% | 1.723% | 1.64% | 2.86% | 1.782% | 2.798% | 0.6985% | 0.6255% | 0.252% | 1.816% | 2.263% | 2.652% | 2.866% | -0.7178% | -2.08% | 2.688% | 2.138% | -0.9548% | 0.5558% | 1.606% | 2.388% | 1.157% | 2.196% | 0.2051% | -0.05967% | 0.5316% | 0.2331% | 1.06% | 1.166% | 0.4976% | 0.4318% | -0.9254% | -1.691% | 0.03928% | -0.9228% | -0.568% | -1.833% | -1.305% | -1.015% | -1.76% | -2.215% | -0.4753% | -1.848% | 0.1605% | -2.602% | -1.009% | -0.9247% | -0.4023% | -2.215% | -1.384% | -2.267% | -2.932% | -2.206% | -1.814% | -2.707% | -0.7825% | -1.186% | 0.5903% | -0.6155% | 0.2562% | -0.2065% | -0.8598% | 0.2102% | -0.5569% | -0.6311% | 0.8985% | 0.3452% | -0.627% | 0.4385% | -1.893% | 0.5126% | -0.9607% | -0.04258% | -2.838% | -1.333% | -2.757% | -2.975% | -3.442% | -4.327% | -2.741% | -2.51% | -0.7673% | -1.306% | -1.668% | -0.2075% | -1.261% | -1.458% | -2.451% | -2.205% | -2.916% | -2.672% | -1.959% | -2.462% | -1.906% | -2.524% | -3.391% | -2.566% | -0.622% | 0.1417% | -2.444% | -2.028% | -0.7723% | -1.088% | 0.1009% | 0.7521% | 1.301% | 3.582% | 1.674% | 5.951% | 3.325% | 2.891% | 3.899% | 1.901% | -1.244% | -2.123% | -1.892% | -1.935% | -0.159% | -0.237% | 1.519% | -0.4942% | -1.259% | -2.021% | -1.743% | -2.176% | -2.163% | -1.515% | -2.343% | -1.01%
2025-07-10 | -13.18% | -12.44% | 1.889% | 1.064% | 4.309% | 4.976% | 3.631% | 2.039% | 0.8331% | -2.856% | 1.282% | 0.6065% | 3.062% | 1.677% | 4.832% | 4.849% | 4.431% | 3.687% | 4.524% | 4.77% | 2.883% | 2.833% | 2.369% | 2.349% | 1.498% | 0.1902% | -0.5082% | 0.01296% | 2.589% | 2.697% | 2.376% | 1.952% | 2.432% | 2.79% | 5.038% | 3.007% | 3.423% | 1.448% | 2.177% | 1.423% | 5.588% | 5.873% | 6.496% | 6.048% | 2.839% | 1.946% | 7.136% | 6.629% | -2.659% | -1.885% | 0.2598% | 0.3248% | 0.4887% | 1.629% | -1.517% | -0.9917% | -3.453% | -3.478% | -2.057% | -2.571% | -3.365% | -2.554% | -5.687% | -5.918% | -4.518% | -4.984% | -5.383% | -5.223% | -6.202% | -4.896% | -6.098% | -6.167% | -5.405% | -6.055% | -4.493% | -6.294% | -5.269% | -5.069% | -5.107% | -6.142% | -4.186% | -4.913% | -5.717% | -4.39% | -4.177% | -4.939% | -4.181% | -4.889% | -1.782% | -4.129% | -1.045% | -0.7045% | -0.09809% | 1.408% | 0.62% | 0.312% | 1.863% | 0.8203% | 1.441% | 1.686% | -0.1388% | 2.05% | 1.157% | 1.413% | 0.32% | 1.024% | 0.4395% | 0.1965% | -0.6975% | -1.645% | -0.3514% | 0.5355% | -0.1858% | -0.08537% | -0.2271% | 0.9521% | -0.1114% | -0.677% | -0.3171% | -2.214% | -0.4224% | 0.2853% | 1.698% | 1.521% | 1.294% | 0.4964% | 0.2108% | 0.383% | -0.6998% | 0.01893% | -0.06564% | -0.9083% | -0.6166% | -1.233% | -2.098% | -1.499% | 1.522% | 2.89% | 1.616% | 14.15% | 2.969% | 1.636% | 2.008% | 1.186% | 1.443% | 1.203% | 0.7538% | 0.4067% | 0.4472% | -0.3337% | 1.778% | 1.393% | 1.855% | 1.208% | 1.432% | 1.115% | 1.112% | 1.614% | 1.014% | 1.845%
2025-07-11 | 2.061% | 3.905% | 2.929% | 2.968% | 3.674% | 4.812% | 5.988% | 4.624% | 5.121% | 1.69% | 4.768% | 5.605% | 4.807% | 5.907% | 4.966% | 5.77% | 4.198% | 3.163% | 4.908% | 5.818% | 2.941% | 3.099% | 2.252% | 2.272% | 1.457% | 0.6288% | 0.9276% | 0.2803% | 2.341% | 2.515% | 2.422% | 1.837% | 2.583% | 2.423% | 4.904% | 3.22% | 3.909% | 2.124% | 2.698% | 2.572% | 0.9066% | 0.5948% | 2.054% | 0.5164% | -1.288% | -1.791% | 3.503% | 2.878% | 1.175% | 2.085% | 3.407% | 3.918% | 2.71% | 3.715% | 1.46% | 1.361% | 1.078% | 1.103% | 2.295% | 2.421% | 2.219% | 2.224% | 0.8363% | 0.3955% | -1.27% | -4.041% | -2.316% | -4.822% | -2.15% | -3.951% | -3.604% | -4.911% | -0.8099% | -4.158% | -0.1486% | -4.282% | -2.391% | -0.1461% | -0.125% | -1.821% | -5.297% | -5.051% | -8.014% | -5.244% | -5.411% | -6.248% | -3.633% | -4.99% | -1.493% | -3.332% | -0.4656% | 0.4667% | 0.6642% | 1.609% | 0.4579% | 1.003% | 2.102% | 1.103% | 0.5236% | 1.041% | -2.293% | 0.6796% | -1.305% | -0.2277% | -2.26% | -1.773% | -2.212% | -3.01% | -3.702% | -4.747% | -2.193% | -2.329% | -0.9847% | -1.63% | -0.9943% | -0.03206% | -1.544% | -2.686% | -2.343% | -3.418% | -3.267% | -2.944% | -1.163% | -1.586% | -1.565% | -2.249% | -3.15% | -2.455% | -2.643% | -1.955% | -1.998% | -3.339% | -2.383% | -2.972% | -4.801% | -4.394% | -1.935% | -0.3639% | -1.427% | 11.23% | 0.1593% | 0.7724% | 0.1277% | 7.94% | -1.559% | -2.251% | -2.372% | -2.704% | -2.455% | -3.255% | -1.101% | -2.211% | -1.438% | -1.671% | -1.524% | -1.621% | -1.233% | -0.9827% | -1.772% | -0.5173%
2025-07-12 | -0.7089% | 1.51% | 0.6871% | -0.2446% | 1.961% | 1.875% | 2.864% | 0.9992% | 2.006% | 1.556% | 1.799% | 1.244% | 1.885% | 0.9635% | 2.466% | 2.537% | 2.556% | 0.2917% | 1.74% | 2.553% | 2.334% | -1.237% | 1.853% | 1.57% | -0.2954% | -2.15% | -2.135% | -2.166% | 1.983% | 3.424% | 2.895% | 2.133% | 3.549% | 2.995% | 4.146% | 3.146% | 4.27% | 2.406% | 3.447% | 1.899% | 3.916% | 2.492% | 5.873% | -5.693% | 3.416% | 2.383% | 5.465% | 5.833% | -3.548% | -1.659% | -1.008% | 0.1703% | -1.652% | 1.319% | -0.6671% | -1.245% | -2.201% | -0.4927% | -1.694% | -0.4222% | -1.988% | -1.757% | -1.806% | -1.626% | -1.489% | -2.578% | -2.711% | -3.291% | -2.709% | -2.45% | -3.022% | -11.21% | -0.5963% | -3.79% | -0.05439% | -2.625% | -1.978% | 0.5895% | -3.092% | -0.5341% | -3.06% | -2.897% | -4.522% | -6.583% | -3.015% | -4.756% | -2.094% | -4.328% | 0.5855% | -2.091% | -0.339% | 0.8813% | 0.4442% | 1.329% | -0.2311% | 0.5733% | 2.087% | 1.02% | 1.177% | 1.176% | -2.213% | 1.22% | 0.226% | 0.2683% | -0.1449% | -0.4145% | -2.914% | -0.5497% | 0.6107% | -0.5732% | 2.167% | -11.8% | 0.2082% | 0.3496% | -0.9815% | 0.4968% | -0.2281% | -0.09264% | 0.1869% | -2.157% | -0.5167% | -0.3837% | 1.798% | -4.121% | 2.013% | -1.668% | -0.8433% | -0.8447% | -3.513% | 2.637% | 0.8089% | -0.3389% | 1.999% | 1.343% | -10.73% | -100% | 3.747% | 3.876% | 4.484% | 16.76% | 4.805% | 12.79% | 3.489% | 14.07% | 3.353% | 3.623% | 2.684% | 3.388% | 3.593% | 2.301% | 3.553% | 4.279% | 2.689% | 4.129% | 4.384% | 2.992% | 3.24% | 2.863% | 3.654% | 3.707%
2025-07-13 | 3.501% | 5.622% | 4.89% | 4.67% | 6.133% | 6.81% | 7.516% | 5.253% | 6.289% | 4.455% | 4.934% | 6.16% | 5.528% | 5.95% | 6.665% | 6.711% | 5.899% | 5.129% | 5.49% | 6.115% | 4.651% | 4.202% | 3.584% | 3.755% | 2.191% | 0.9938% | 1.274% | 0.9261% | 4.058% | 4.422% | 3.989% | 3.57% | 4.625% | 4.458% | 5.757% | 4.573% | 5.69% | 3.874% | 4.381% | 3.781% | 3.205% | 2.309% | -3.176% | -4.244% | 1.302% | -2.497% | 4.857% | 4.964% | -48.64% | -51.88% | -100% | -100% | -49.26% | -48.12% | -50.26% | -50.39% | 2.235% | 1.964% | 2.647% | 3.917% | 3.53% | 2.566% | 2.891% | 2.639% | 0.6367% | 1.218% | 1.65% | 0.8526% | 0.006686% | 1.502% | 0.1368% | 0.3426% | 1.723% | 0.9317% | 2.887% | 1.202% | 2.347% | 3.643% | 3.611% | 2.956% | -0.034% | 1.29% | -0.2657% | 0.7246% | 1.328% | 0.3779% | 1.455% | -0.1124% | 2.905% | 0.9145% | 1.876% | 2.325% | 1.731% | 2.667% | 1.878% | 2.954% | 5.036% | 4.352% | 4.379% | 5.092% | 1.334% | 4.934% | 3.51% | 4.034% | 2.433% | 2.298% | 1.464% | 2.654% | 2.314% | 0.5687% | 4.158% | 2.265% | 3.796% | 3.927% | 1.848% | 4.581% | 4.263% | 3.919% | 3.576% | 3.192% | 2.74% | 3.002% | 4.756% | 0.5398% | 4.626% | 2.786% | 2.858% | 3.499% | 3.289% | 5.521% | 3.268% | 2.604% | 5.249% | 4.46% | -15.91% | -100% | 7.142% | 8.818% | 7.396% | 21.11% | 8.323% | 17.6% | 8.75% | 17.2% | 9.477% | 9.604% | 8.343% | 8.217% | 7.962% | 6.327% | 9.133% | 8.727% | 6.797% | 7.273% | 8.139% | 7.09% | 8.143% | 9.467% | 7.428% | 9.599%
2025-07-14 | -1.446% | -0.4055% | -0.4759% | -0.3374% | 0.4365% | 0.3418% | 0.4551% | -1.599% | -0.1672% | -1.131% | -0.9942% | -0.4026% | -1.128% | -0.4719% | -8.964% | -100% | 0.1835% | 0.292% | 1.281% | 1.47% | 1.815% | 0.7338% | 2.793% | 1.956% | 0.6237% | -0.3031% | -2.079% | -1.224% | 2.498% | 3.209% | 3.237% | 2.251% | 4.479% | 4.39% | 4.573% | 3.96% | 4.214% | 2.824% | 3.396% | 2.502% | 1.757% | 0.7566% | 3.239% | 1.306% | -0.4638% | -1.333% | 2.787% | 3.095% | -10.47% | -9.545% | -79.29% | -78.68% | -8.496% | -7.916% | -8.336% | -8.783% | -1.237% | -1.473% | -2.445% | -1.63% | -2.253% | -2.451% | -2.574% | -2.727% | -4.165% | -0.859% | -0.3964% | -1.683% | -2.191% | 0.0914% | -4.106% | -0.6906% | -1.189% | -0.6982% | -0.03726% | -1.454% | -0.1308% | -1.464% | -0.7897% | -1.93% | 0.09039% | -0.858% | -2.55% | -2.223% | -1.226% | -2.855% | -1.01% | -2.328% | -0.6851% | -1.907% | -0.1613% | -0.6418% | -0.4214% | 1.618% | 0.7146% | -0.2342% | 1.093% | 0.02381% | -0.8964% | 1.145% | -3.315% | 1.125% | -0.8332% | 0.2235% | -2.275% | -0.4145% | -1.861% | -0.9451% | -1.457% | -3.829% | 0.2716% | 0.2092% | 0.07192% | -0.7083% | -2% | 0.4256% | -2.158% | -0.6494% | -2.488% | -1.252% | -0.4914% | 1.082% | 0.976% | 0.8342% | 2.057% | 1.017% | 0.3262% | 1.687% | 0.7757% | 2.687% | 1.982% | 1.682% | 2.422% | 2.44% | -0.7047% | -1.317% | 1.836% | 5.207% | 123.4% | 152.5% | 4.871% | 13.35% | 5.174% | 14.02% | 1.312% | 1.459% | -1.168% | -0.04599% | 0.472% | 0.3308% | 4.079% | 2.384% | -0.1513% | -0.2162% | 0.7356% | -0.05045% | 0.3109% | 1.684% | -2.618% | 0.4996%
2025-07-15 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Formulas:
Date = [Date, row above]+1

## ModellingYTD (hidden)
Year Number | Month | POA(kWh/m2) | GHI (kWh/m2) | Budgeted Energy (MWh) | Tmod | Irradiationce Losses (IAM+NearShadding+Solining) | Bifacial Gain | Temperature Loss | Mismatch Loss | DC Ohmic Loss | Inverter Conversion Loss | MPPT Mismatch Losse | AC Ohmic Loss | Clipping Loss | Plant Uptime | Grid Uptime | Tracker Uptime
Year-Apr | Apr | 215.9 | 208.9997 | 59637.6 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | May | 217.9 | 221.9002 | 61013.7 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | Jun | 192.8 | 200.2009 | 54806.4 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | Jul | 168.9 | 173.5997 | 48598.11 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | Aug | 174.2 | 172.6002 | 49476.24 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | Sep | 192.1 | 178.8993 | 53840.16 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | Oct | 202.3 | 174.6008 | 56487.42 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | Nov | 162.9 | 133.6994 | 47868.48 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | Dec | 158.6 | 124.4 | 47682.36 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | Jan | 169.0285 | 133.8993 | 50622.66 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | Feb | 172.5591 | 145.4008 | 49925.7 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | Mar | 215.7458 | 195.5989 | 59767.29 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2022-04-01 | 215.9 | 208.9997 | 59637.6 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2022-05-01 | 217.9 | 221.9002 | 61013.7 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2022-06-01 | 192.8 | 200.2009 | 54806.4 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2022-07-01 | 168.9 | 173.5997 | 48598.11 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2022-08-01 | 174.2 | 172.6002 | 49476.24 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2022-09-01 | 192.1 | 178.8993 | 53840.16 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2022-10-01 | 202.3 | 174.6008 | 56487.42 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2022-11-01 | 162.9 | 133.6994 | 47868.48 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2022-12-01 | 158.6 | 124.4 | 47682.36 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2023-01-01 | 169.0285 | 133.8993 | 50622.66 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2023-02-01 | 172.5591 | 145.4008 | 49925.7 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2023-03-01 | 215.7458 | 195.5989 | 59767.29 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2023-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2023-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2023-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2023-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2023-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2023-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2023-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2023-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2023-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2024-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2024-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2024-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2024-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2024-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2024-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2024-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2024-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2024-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2024-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2024-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2024-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2025-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2025-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2025-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2025-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2025-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2025-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2025-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2025-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2025-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2025-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2025-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2025-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2026-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2026-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2026-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2026-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2026-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2026-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2026-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2026-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2026-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2026-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2026-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2026-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2027-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2027-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2027-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2027-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2027-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2027-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2027-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2027-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2027-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2027-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2027-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2027-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2028-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2028-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2028-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2028-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2028-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2028-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2028-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2028-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2028-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2028-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2028-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2028-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2029-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2029-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2029-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2029-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2029-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2029-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2029-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2029-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2029-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2029-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2029-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2029-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2030-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2030-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2030-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2030-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2030-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2030-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2030-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2030-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2030-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2030-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2030-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2030-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2031-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2031-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2031-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2031-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2031-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2031-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2031-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2031-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2031-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2031-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2031-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2031-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2032-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2032-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2032-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2032-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2032-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2032-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2032-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2032-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2032-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2032-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2032-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2032-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2033-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2033-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2033-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2033-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2033-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2033-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2033-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2033-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2033-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2033-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2033-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2033-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2034-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2034-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2034-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2034-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2034-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2034-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2034-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2034-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2034-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2034-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2034-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2034-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2035-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2035-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2035-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2035-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2035-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2035-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2035-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2035-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2035-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2035-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2035-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2035-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2036-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2036-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2036-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2036-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2036-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2036-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2036-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2036-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2036-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2036-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2036-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2036-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2037-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2037-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2037-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2037-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2037-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2037-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2037-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2037-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2037-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2037-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2037-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2037-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2038-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2038-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2038-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2038-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2038-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2038-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2038-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2038-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2038-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2038-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2038-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2038-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2039-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2039-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2039-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2039-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2039-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2039-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2039-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2039-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2039-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2039-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2039-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2039-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2040-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2040-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2040-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2040-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2040-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2040-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2040-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2040-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2040-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2040-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2040-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2040-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2041-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2041-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2041-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2041-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2041-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2041-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2041-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2041-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2041-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2041-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2041-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2041-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2042-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2042-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2042-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2042-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2042-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2042-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2042-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2042-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2042-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2042-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2042-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2042-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2043-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2043-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2043-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2043-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2043-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2043-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2043-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2043-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2043-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2043-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2043-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2043-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2044-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2044-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2044-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2044-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2044-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2044-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2044-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2044-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2044-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2044-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2044-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2044-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2045-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2045-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2045-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2045-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2045-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2045-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2045-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2045-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2045-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2045-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2045-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2045-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2046-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2046-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2046-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
#REF! | 2046-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 9.506% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
#REF! | 2046-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 9.834% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
#REF! | 2046-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 9.834% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
#REF! | 2046-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 9.178% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
#REF! | 2046-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 8.851% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
#REF! | 2046-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 8.523% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
#REF! | 2046-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 8.851% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
#REF! | 2046-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 8.851% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
#REF! | 2046-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 8.851% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
#REF! | 2047-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 8.851% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
#REF! | 2047-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 8.851% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
#REF! | 2047-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 9.178% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Note on H26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear
Note on H37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 67.22% correct to convert to view factor rear

## Basic Data (hidden)
Equipment | Affected DC Capacity | Plant Equivalent Weightage | Fault Category Plant BD sheet |  | IS Number |  | SCB Number |  | String Type | Equipment | Inverter Module Number |  | Status |  | Plant capacity | Month No. | Month Name
IS1INV1M1 | 2064.8 | 0.6162% | Module |  | IS1 |  | SCB1 |  | Str_Typ1(445*29) | Tx | M1 |  | Open |  | 335091
IS1INV1M2 | 2090.61 | 0.6239% | Cables |  | IS2 |  | SCB2 |  | Str_Typ2 (450*29) | MVP | M2 |  | Close
IS1INV2M1 | 2090.61 | 0.6239% | String Fuses |  | IS3 |  | SCB3 |  | Str_Typ3(535*29) | Aux_Tx
IS1INV2M2 | 2077.705 | 0.62% | SCB |  | IS4 |  | SCB4 |  | Str_Typ4(540*29) | MCR_MVP_Inc1
IS1INV3M1 | 2090.61 | 0.6239% | Inverter |  | IS5 |  | SCB5 |  | Str_Typ5(545*29) | MCR_MVP_Inc2
IS1INV3M2 | 2090.61 | 0.6239% | IDT |  | IS6 |  | SCB6 |  | Str_Typ6(445*58) | MCR_MVP_Inc3
IS1INV4M1 | 2090.61 | 0.6239% | PTR |  | IS7 |  | SCB7 |  | Str_Typ7(450*58) | MCR_MVP_Inc4
IS1INV4M2 | 2193.85 | 0.6547% | MV Panel |  | IS8 |  | SCB8 |  | Str_Typ8(535*58) | MCR_MVP_Inc5
IS2INV1M1 | 2090.61 | 0.6239% | Metering System Plant |  | IS9 |  | SCB9 |  | Str_Typ9(540*58) | MCR_MVP_Inc8
IS2INV1M2 | 2090.61 | 0.6239% | Grid System |  | IS10 |  | SCB10 |  | Str_Typ10(545*58) | MCR_MVP_Inc9
IS2INV2M1 | 2090.61 | 0.6239% | Metering System Grid |  | IS11 |  |  |  |  | MCR_MVP_Inc10
IS2INV2M2 | 2090.61 | 0.6239% | WMS |  | IS12 |  |  |  |  | MCR_MVP_Inc11
IS2INV3M1 | 2064.8 | 0.6162% | MMS |  | IS13 |  |  |  |  | MCR_MVP_Inc12
IS2INV3M2 | 2090.61 | 0.6239% | Battery Charger_MCR |  | IS14 |  |  |  |  | MCR_MVP_OG1
IS2INV4M1 | 2090.61 | 0.6239% | IC_UPS |  | IS15 |  |  |  |  | MCR_MVP_OG2
IS2INV4M2 | 2090.61 | 0.6239% | IC_Auxiliary Tranformer |  | IS16 |  |  |  |  | Power_Tx1
IS3INV1M1 | 2090.61 | 0.6239% | IC_Auxiliary DB |  | IS17 |  |  |  |  | Power_Tx2
IS3INV1M2 | 2090.61 | 0.6239% | IC_SCADA Panel |  | IS18 |  |  |  |  | Line_Bay1
IS3INV2M1 | 2090.61 | 0.6239% | Connectors |  | IS19
IS3INV2M2 | 2090.61 | 0.6239% |  |  | IS20
IS3INV3M1 | 2114.1 | 0.6309%
IS3INV3M2 | 2088 | 0.6231%
IS3INV4M1 | 2114.1 | 0.6309%
IS3INV4M2 | 2088 | 0.6231%
IS4INV1M1 | 2088 | 0.6231%
IS4INV1M2 | 1879.2 | 0.5608%
IS4INV2M1 | 2114.1 | 0.6309%
IS4INV2M2 | 2088 | 0.6231%
IS4INV3M1 | 2114.1 | 0.6309%
IS4INV3M2 | 2088 | 0.6231%
IS4INV4M1 | 2114.1 | 0.6309%
IS4INV4M2 | 2061.9 | 0.6153%
IS5INV1M1 | 2090.61 | 0.6239%
IS5INV1M2 | 2090.61 | 0.6239%
IS5INV2M1 | 2090.61 | 0.6239%
IS5INV2M2 | 2090.61 | 0.6239%
IS5INV3M1 | 2090.61 | 0.6239%
IS5INV3M2 | 2090.61 | 0.6239%
IS5INV4M1 | 2090.61 | 0.6239%
IS5INV4M2 | 2090.61 | 0.6239%
IS6INV1M1 | 2234.16 | 0.6667%
IS6INV1M2 | 1985.92 | 0.5927%
IS6INV2M1 | 2203.13 | 0.6575%
IS6INV2M2 | 1985.92 | 0.5927%
IS6INV3M1 | 2192.4 | 0.6543%
IS6INV3M2 | 2380.32 | 0.7104%
IS6INV4M1 | 2203.13 | 0.6575%
IS6INV4M2 | 1985.92 | 0.5927%
IS7INV1M1 | 1973.16 | 0.5888%
IS7INV1M2 | 1973.16 | 0.5888%
IS7INV2M1 | 2098.44 | 0.6262%
IS7INV2M2 | 2004.48 | 0.5982%
IS7INV3M1 | 2223.72 | 0.6636%
IS7INV3M2 | 1973.16 | 0.5888%
IS7INV4M1 | 2223.72 | 0.6636%
IS7INV4M2 | 1973.16 | 0.5888%
IS8INV1M1 | 2004.48 | 0.5982%
IS8INV1M2 | 2255.04 | 0.673%
IS8INV2M1 | 2255.04 | 0.673%
IS8INV2M2 | 2004.48 | 0.5982%
IS8INV3M1 | 2255.04 | 0.673%
IS8INV3M2 | 2004.48 | 0.5982%
IS8INV4M1 | 2088 | 0.6231%
IS8INV4M2 | 2061.9 | 0.6153%
IS9INV1M1 | 2102.065 | 0.6273%
IS9INV1M2 | 2023.04 | 0.6037%
IS9INV2M1 | 2102.065 | 0.6273%
IS9INV2M2 | 2212.7 | 0.6603%
IS9INV3M1 | 2275.33 | 0.679%
IS9INV3M2 | 2023.04 | 0.6037%
IS9INV4M1 | 2244.31 | 0.6698%
IS9INV4M2 | 1959.82 | 0.5849%
IS10INV1M1 | 2067.12 | 0.6169%
IS10INV1M2 | 2098.44 | 0.6262%
IS10INV2M1 | 1973.16 | 0.5888%
IS10INV2M2 | 2223.72 | 0.6636%
IS10INV3M1 | 1941.84 | 0.5795%
IS10INV3M2 | 2255.04 | 0.673%
IS10INV4M1 | 1973.16 | 0.5888%
IS10INV4M2 | 2223.72 | 0.6636%
IS11INV1M1 | 2023.04 | 0.6037%
IS11INV1M2 | 2212.7 | 0.6603%
IS11INV2M1 | 2275.92 | 0.6792%
IS11INV2M2 | 2038.845 | 0.6084%
IS11INV3M1 | 2023.04 | 0.6037%
IS11INV3M2 | 2212.7 | 0.6603%
IS11INV4M1 | 2023.04 | 0.6037%
IS11INV4M2 | 1785.965 | 0.533%
IS12INV1M1 | 2192.4 | 0.6543%
IS12INV1M2 | 2114.1 | 0.6309%
IS12INV2M1 | 1941.84 | 0.5795%
IS12INV2M2 | 2255.04 | 0.673%
IS12INV3M1 | 2192.4 | 0.6543%
IS12INV3M2 | 2004.48 | 0.5982%
IS12INV4M1 | 2004.48 | 0.5982%
IS12INV4M2 | 2208.06 | 0.6589%
IS13INV1M1 | 2004.48 | 0.5982%
IS13INV1M2 | 2004.48 | 0.5982%
IS13INV2M1 | 2192.4 | 0.6543%
IS13INV2M2 | 2004.48 | 0.5982%
IS13INV3M1 | 2192.4 | 0.6543%
IS13INV3M2 | 2004.48 | 0.5982%
IS13INV4M1 | 2192.4 | 0.6543%
IS13INV4M2 | 2004.48 | 0.5982%
IS14INV1M1 | 2223.72 | 0.6636%
IS14INV1M2 | 1910.52 | 0.5701%
IS14INV2M1 | 2223.72 | 0.6636%
IS14INV2M2 | 2004.48 | 0.5982%
IS14INV3M1 | 2192.4 | 0.6543%
IS14INV3M2 | 2004.48 | 0.5982%
IS14INV4M1 | 2192.4 | 0.6543%
IS14INV4M2 | 2004.48 | 0.5982%
IS15INV1M1 | 2004.48 | 0.5982%
IS15INV1M2 | 2192.4 | 0.6543%
IS15INV2M1 | 2004.48 | 0.5982%
IS15INV2M2 | 1941.84 | 0.5795%
IS15INV3M1 | 2223.72 | 0.6636%
IS15INV3M2 | 2192.4 | 0.6543%
IS15INV4M1 | 2192.4 | 0.6543%
IS15INV4M2 | 2004.48 | 0.5982%
IS16INV1M1 | 2192.4 | 0.6543%
IS16INV1M2 | 2004.48 | 0.5982%
IS16INV2M1 | 2161.08 | 0.6449%
IS16INV2M2 | 2004.48 | 0.5982%
IS16INV3M1 | 2129.76 | 0.6356%
IS16INV3M2 | 1879.2 | 0.5608%
IS16INV4M1 | 2129.76 | 0.6356%
IS16INV4M2 | 1973.16 | 0.5888%
IS17INV1M1 | 1973.16 | 0.5888%
IS17INV1M2 | 2004.48 | 0.5982%
IS17INV2M1 | 2004.48 | 0.5982%
IS17INV2M2 | 1753.92 | 0.5234%
IS17INV3M1 | 1957.5 | 0.5842%
IS17INV3M2 | 1753.92 | 0.5234%
IS17INV4M1 | 2004.48 | 0.5982%
IS17INV4M2 | 2004.48 | 0.5982%
IS18INV1M1 | 2255.04 | 0.673%
IS18INV1M2 | 1973.16 | 0.5888%
IS18INV2M1 | 2255.04 | 0.673%
IS18INV2M2 | 1973.16 | 0.5888%
IS18INV3M1 | 2223.72 | 0.6636%
IS18INV3M2 | 1973.16 | 0.5888%
IS18INV4M1 | 2004.48 | 0.5982%
IS18INV4M2 | 2004.48 | 0.5982%
IS19INV1M1 | 2161.08 | 0.6449%
IS19INV1M2 | 2255.04 | 0.673%
IS19INV2M1 | 2223.72 | 0.6636%
IS19INV2M2 | 2223.72 | 0.6636%
IS19INV3M1 | 2223.72 | 0.6636%
IS19INV3M2 | 2255.04 | 0.673%
IS19INV4M1 | 2004.48 | 0.5982%
IS19INV4M2 | 2223.72 | 0.6636%
IS20INV1M1 | 2255.04 | 0.673%
IS20INV1M2 | 2255.04 | 0.673%
IS20INV2M1 | 2255.04 | 0.673%
IS20INV2M2 | 2255.04 | 0.673%
IS20INV3M1 | 2255.04 | 0.673%
IS20INV3M2 | 2004.48 | 0.5982%
IS20INV4M1 | 2255.04 | 0.673%
IS20INV4M2 | 2004.48 | 0.5982%
IS1INV1M1SCB1 | 232.29 | 0.06932%
IS1INV1M1SCB2 | 232.29 | 0.06932%
IS1INV1M1SCB3 | 232.29 | 0.06932%
IS1INV1M1SCB4 | 232.29 | 0.06932%
IS1INV1M1SCB5 | 206.48 | 0.06162%
IS1INV1M1SCB6 | 232.29 | 0.06932%
IS1INV1M1SCB7 | 232.29 | 0.06932%
IS1INV1M1SCB8 | 232.29 | 0.06932%
IS1INV1M1SCB9 | 232.29 | 0.06932%
IS1INV1M1SCB10 | 0 | 0%
IS1INV1M2SCB1 | 232.29 | 0.06932%
IS1INV1M2SCB2 | 232.29 | 0.06932%
IS1INV1M2SCB3 | 232.29 | 0.06932%
IS1INV1M2SCB4 | 232.29 | 0.06932%
IS1INV1M2SCB5 | 232.29 | 0.06932%
IS1INV1M2SCB6 | 232.29 | 0.06932%
IS1INV1M2SCB7 | 232.29 | 0.06932%
IS1INV1M2SCB8 | 232.29 | 0.06932%
IS1INV1M2SCB9 | 232.29 | 0.06932%
IS1INV1M2SCB10 | 0 | 0%
IS1INV2M1SCB1 | 232.29 | 0.06932%
IS1INV2M1SCB2 | 232.29 | 0.06932%
IS1INV2M1SCB3 | 232.29 | 0.06932%
IS1INV2M1SCB4 | 232.29 | 0.06932%
IS1INV2M1SCB5 | 232.29 | 0.06932%
IS1INV2M1SCB6 | 232.29 | 0.06932%
IS1INV2M1SCB7 | 232.29 | 0.06932%
IS1INV2M1SCB8 | 232.29 | 0.06932%
IS1INV2M1SCB9 | 232.29 | 0.06932%
IS1INV2M1SCB10 | 0 | 0%
IS1INV2M2SCB1 | 232.29 | 0.06932%
IS1INV2M2SCB2 | 232.29 | 0.06932%
IS1INV2M2SCB3 | 232.29 | 0.06932%
IS1INV2M2SCB4 | 232.29 | 0.06932%
IS1INV2M2SCB5 | 232.29 | 0.06932%
IS1INV2M2SCB6 | 219.385 | 0.06547%
IS1INV2M2SCB7 | 232.29 | 0.06932%
IS1INV2M2SCB8 | 232.29 | 0.06932%
IS1INV2M2SCB9 | 232.29 | 0.06932%
IS1INV2M2SCB10 | 0 | 0%
IS1INV3M1SCB1 | 232.29 | 0.06932%
IS1INV3M1SCB2 | 232.29 | 0.06932%
IS1INV3M1SCB3 | 232.29 | 0.06932%
IS1INV3M1SCB4 | 232.29 | 0.06932%
IS1INV3M1SCB5 | 232.29 | 0.06932%
IS1INV3M1SCB6 | 232.29 | 0.06932%
IS1INV3M1SCB7 | 232.29 | 0.06932%
IS1INV3M1SCB8 | 232.29 | 0.06932%
IS1INV3M1SCB9 | 232.29 | 0.06932%
IS1INV3M1SCB10 | 0 | 0%
IS1INV3M2SCB1 | 232.29 | 0.06932%
IS1INV3M2SCB2 | 232.29 | 0.06932%
IS1INV3M2SCB3 | 232.29 | 0.06932%
IS1INV3M2SCB4 | 232.29 | 0.06932%
IS1INV3M2SCB5 | 232.29 | 0.06932%
IS1INV3M2SCB6 | 232.29 | 0.06932%
IS1INV3M2SCB7 | 232.29 | 0.06932%
IS1INV3M2SCB8 | 232.29 | 0.06932%
IS1INV3M2SCB9 | 232.29 | 0.06932%
IS1INV3M2SCB10 | 0 | 0%
IS1INV4M1SCB1 | 232.29 | 0.06932%
IS1INV4M1SCB2 | 232.29 | 0.06932%
IS1INV4M1SCB3 | 232.29 | 0.06932%
IS1INV4M1SCB4 | 232.29 | 0.06932%
IS1INV4M1SCB5 | 232.29 | 0.06932%
IS1INV4M1SCB6 | 232.29 | 0.06932%
IS1INV4M1SCB7 | 232.29 | 0.06932%
IS1INV4M1SCB8 | 232.29 | 0.06932%
IS1INV4M1SCB9 | 232.29 | 0.06932%
IS1INV4M1SCB10 | 0 | 0%
IS1INV4M2SCB1 | 232.29 | 0.06932%
IS1INV4M2SCB2 | 232.29 | 0.06932%
IS1INV4M2SCB3 | 232.29 | 0.06932%
IS1INV4M2SCB4 | 232.29 | 0.06932%
IS1INV4M2SCB5 | 206.48 | 0.06162%
IS1INV4M2SCB6 | 206.48 | 0.06162%
IS1INV4M2SCB7 | 206.48 | 0.06162%
IS1INV4M2SCB8 | 232.29 | 0.06932%
IS1INV4M2SCB9 | 206.48 | 0.06162%
IS1INV4M2SCB10 | 206.48 | 0.06162%
IS2INV1M1SCB1 | 232.29 | 0.06932%
IS2INV1M1SCB2 | 232.29 | 0.06932%
IS2INV1M1SCB3 | 232.29 | 0.06932%
IS2INV1M1SCB4 | 232.29 | 0.06932%
IS2INV1M1SCB5 | 232.29 | 0.06932%
IS2INV1M1SCB6 | 232.29 | 0.06932%
IS2INV1M1SCB7 | 232.29 | 0.06932%
IS2INV1M1SCB8 | 232.29 | 0.06932%
IS2INV1M1SCB9 | 232.29 | 0.06932%
IS2INV1M1SCB10 | 0 | 0%
IS2INV1M2SCB1 | 232.29 | 0.06932%
IS2INV1M2SCB2 | 232.29 | 0.06932%
IS2INV1M2SCB3 | 232.29 | 0.06932%
IS2INV1M2SCB4 | 232.29 | 0.06932%
IS2INV1M2SCB5 | 232.29 | 0.06932%
IS2INV1M2SCB6 | 232.29 | 0.06932%
IS2INV1M2SCB7 | 232.29 | 0.06932%
IS2INV1M2SCB8 | 232.29 | 0.06932%
IS2INV1M2SCB9 | 232.29 | 0.06932%
IS2INV1M2SCB10 | 0 | 0%
IS2INV2M1SCB1 | 232.29 | 0.06932%
IS2INV2M1SCB2 | 232.29 | 0.06932%
IS2INV2M1SCB3 | 232.29 | 0.06932%
IS2INV2M1SCB4 | 232.29 | 0.06932%
IS2INV2M1SCB5 | 232.29 | 0.06932%
IS2INV2M1SCB6 | 232.29 | 0.06932%
IS2INV2M1SCB7 | 232.29 | 0.06932%
IS2INV2M1SCB8 | 232.29 | 0.06932%
IS2INV2M1SCB9 | 232.29 | 0.06932%
IS2INV2M1SCB10 | 0 | 0%
IS2INV2M2SCB1 | 232.29 | 0.06932%
IS2INV2M2SCB2 | 232.29 | 0.06932%
IS2INV2M2SCB3 | 232.29 | 0.06932%
IS2INV2M2SCB4 | 232.29 | 0.06932%
IS2INV2M2SCB5 | 232.29 | 0.06932%
IS2INV2M2SCB6 | 232.29 | 0.06932%
IS2INV2M2SCB7 | 232.29 | 0.06932%
IS2INV2M2SCB8 | 232.29 | 0.06932%
IS2INV2M2SCB9 | 232.29 | 0.06932%
IS2INV2M2SCB10 | 0 | 0%
IS2INV3M1SCB1 | 232.29 | 0.06932%
IS2INV3M1SCB2 | 232.29 | 0.06932%
IS2INV3M1SCB3 | 232.29 | 0.06932%
IS2INV3M1SCB4 | 232.29 | 0.06932%
IS2INV3M1SCB5 | 206.48 | 0.06162%
IS2INV3M1SCB6 | 232.29 | 0.06932%
IS2INV3M1SCB7 | 232.29 | 0.06932%
IS2INV3M1SCB8 | 232.29 | 0.06932%
IS2INV3M1SCB9 | 232.29 | 0.06932%
IS2INV3M1SCB10 | 0 | 0%
IS2INV3M2SCB1 | 232.29 | 0.06932%
IS2INV3M2SCB2 | 232.29 | 0.06932%
IS2INV3M2SCB3 | 232.29 | 0.06932%
IS2INV3M2SCB4 | 232.29 | 0.06932%
IS2INV3M2SCB5 | 232.29 | 0.06932%
IS2INV3M2SCB6 | 232.29 | 0.06932%
IS2INV3M2SCB7 | 232.29 | 0.06932%
IS2INV3M2SCB8 | 232.29 | 0.06932%
IS2INV3M2SCB9 | 232.29 | 0.06932%
IS2INV3M2SCB10 | 0 | 0%
IS2INV4M1SCB1 | 232.29 | 0.06932%
IS2INV4M1SCB2 | 232.29 | 0.06932%
IS2INV4M1SCB3 | 232.29 | 0.06932%
IS2INV4M1SCB4 | 232.29 | 0.06932%
IS2INV4M1SCB5 | 232.29 | 0.06932%
IS2INV4M1SCB6 | 232.29 | 0.06932%
IS2INV4M1SCB7 | 232.29 | 0.06932%
IS2INV4M1SCB8 | 232.29 | 0.06932%
IS2INV4M1SCB9 | 232.29 | 0.06932%
IS2INV4M1SCB10 | 0 | 0%
IS2INV4M2SCB1 | 232.29 | 0.06932%
IS2INV4M2SCB2 | 232.29 | 0.06932%
IS2INV4M2SCB3 | 232.29 | 0.06932%
IS2INV4M2SCB4 | 232.29 | 0.06932%
IS2INV4M2SCB5 | 232.29 | 0.06932%
IS2INV4M2SCB6 | 232.29 | 0.06932%
IS2INV4M2SCB7 | 232.29 | 0.06932%
IS2INV4M2SCB8 | 232.29 | 0.06932%
IS2INV4M2SCB9 | 232.29 | 0.06932%
IS2INV4M2SCB10 | 0 | 0%
IS3INV1M1SCB1 | 232.29 | 0.06932%
IS3INV1M1SCB2 | 232.29 | 0.06932%
IS3INV1M1SCB3 | 232.29 | 0.06932%
IS3INV1M1SCB4 | 232.29 | 0.06932%
IS3INV1M1SCB5 | 232.29 | 0.06932%
IS3INV1M1SCB6 | 232.29 | 0.06932%
IS3INV1M1SCB7 | 232.29 | 0.06932%
IS3INV1M1SCB8 | 232.29 | 0.06932%
IS3INV1M1SCB9 | 232.29 | 0.06932%
IS3INV1M1SCB10 | 0 | 0%
IS3INV1M2SCB1 | 232.29 | 0.06932%
IS3INV1M2SCB2 | 232.29 | 0.06932%
IS3INV1M2SCB3 | 232.29 | 0.06932%
IS3INV1M2SCB4 | 232.29 | 0.06932%
IS3INV1M2SCB5 | 232.29 | 0.06932%
IS3INV1M2SCB6 | 232.29 | 0.06932%
IS3INV1M2SCB7 | 232.29 | 0.06932%
IS3INV1M2SCB8 | 232.29 | 0.06932%
IS3INV1M2SCB9 | 232.29 | 0.06932%
IS3INV1M2SCB10 | 0 | 0%
IS3INV2M1SCB1 | 232.29 | 0.06932%
IS3INV2M1SCB2 | 232.29 | 0.06932%
IS3INV2M1SCB3 | 232.29 | 0.06932%
IS3INV2M1SCB4 | 232.29 | 0.06932%
IS3INV2M1SCB5 | 232.29 | 0.06932%
IS3INV2M1SCB6 | 232.29 | 0.06932%
IS3INV2M1SCB7 | 232.29 | 0.06932%
IS3INV2M1SCB8 | 232.29 | 0.06932%
IS3INV2M1SCB9 | 232.29 | 0.06932%
IS3INV2M1SCB10 | 0 | 0%
IS3INV2M2SCB1 | 232.29 | 0.06932%
IS3INV2M2SCB2 | 232.29 | 0.06932%
IS3INV2M2SCB3 | 232.29 | 0.06932%
IS3INV2M2SCB4 | 232.29 | 0.06932%
IS3INV2M2SCB5 | 232.29 | 0.06932%
IS3INV2M2SCB6 | 232.29 | 0.06932%
IS3INV2M2SCB7 | 232.29 | 0.06932%
IS3INV2M2SCB8 | 232.29 | 0.06932%
IS3INV2M2SCB9 | 232.29 | 0.06932%
IS3INV2M2SCB10 | 0 | 0%
IS3INV3M1SCB1 | 234.9 | 0.0701%
IS3INV3M1SCB2 | 234.9 | 0.0701%
IS3INV3M1SCB3 | 234.9 | 0.0701%
IS3INV3M1SCB4 | 234.9 | 0.0701%
IS3INV3M1SCB5 | 234.9 | 0.0701%
IS3INV3M1SCB6 | 234.9 | 0.0701%
IS3INV3M1SCB7 | 234.9 | 0.0701%
IS3INV3M1SCB8 | 234.9 | 0.0701%
IS3INV3M1SCB9 | 234.9 | 0.0701%
IS3INV3M1SCB10 | 0 | 0%
IS3INV3M2SCB1 | 234.9 | 0.0701%
IS3INV3M2SCB2 | 234.9 | 0.0701%
IS3INV3M2SCB3 | 234.9 | 0.0701%
IS3INV3M2SCB4 | 234.9 | 0.0701%
IS3INV3M2SCB5 | 234.9 | 0.0701%
IS3INV3M2SCB6 | 234.9 | 0.0701%
IS3INV3M2SCB7 | 234.9 | 0.0701%
IS3INV3M2SCB8 | 234.9 | 0.0701%
IS3INV3M2SCB9 | 208.8 | 0.06231%
IS3INV3M2SCB10 | 0 | 0%
IS3INV4M1SCB1 | 234.9 | 0.0701%
IS3INV4M1SCB2 | 234.9 | 0.0701%
IS3INV4M1SCB3 | 234.9 | 0.0701%
IS3INV4M1SCB4 | 234.9 | 0.0701%
IS3INV4M1SCB5 | 234.9 | 0.0701%
IS3INV4M1SCB6 | 234.9 | 0.0701%
IS3INV4M1SCB7 | 234.9 | 0.0701%
IS3INV4M1SCB8 | 234.9 | 0.0701%
IS3INV4M1SCB9 | 234.9 | 0.0701%
IS3INV4M1SCB10 | 0 | 0%
IS3INV4M2SCB1 | 234.9 | 0.0701%
IS3INV4M2SCB2 | 234.9 | 0.0701%
IS3INV4M2SCB3 | 234.9 | 0.0701%
IS3INV4M2SCB4 | 234.9 | 0.0701%
IS3INV4M2SCB5 | 234.9 | 0.0701%
IS3INV4M2SCB6 | 234.9 | 0.0701%
IS3INV4M2SCB7 | 234.9 | 0.0701%
IS3INV4M2SCB8 | 234.9 | 0.0701%
IS3INV4M2SCB9 | 208.8 | 0.06231%
IS3INV4M2SCB10 | 0 | 0%
IS4INV1M1SCB1 | 234.9 | 0.0701%
IS4INV1M1SCB2 | 234.9 | 0.0701%
IS4INV1M1SCB3 | 234.9 | 0.0701%
IS4INV1M1SCB4 | 208.8 | 0.06231%
IS4INV1M1SCB5 | 234.9 | 0.0701%
IS4INV1M1SCB6 | 234.9 | 0.0701%
IS4INV1M1SCB7 | 234.9 | 0.0701%
IS4INV1M1SCB8 | 234.9 | 0.0701%
IS4INV1M1SCB9 | 234.9 | 0.0701%
IS4INV1M1SCB10 | 0 | 0%
IS4INV1M2SCB1 | 234.9 | 0.0701%
IS4INV1M2SCB2 | 234.9 | 0.0701%
IS4INV1M2SCB3 | 234.9 | 0.0701%
IS4INV1M2SCB4 | 0 | 0%
IS4INV1M2SCB5 | 234.9 | 0.0701%
IS4INV1M2SCB6 | 234.9 | 0.0701%
IS4INV1M2SCB7 | 234.9 | 0.0701%
IS4INV1M2SCB8 | 234.9 | 0.0701%
IS4INV1M2SCB9 | 234.9 | 0.0701%
IS4INV1M2SCB10 | 0 | 0%
IS4INV2M1SCB1 | 234.9 | 0.0701%
IS4INV2M1SCB2 | 234.9 | 0.0701%
IS4INV2M1SCB3 | 234.9 | 0.0701%
IS4INV2M1SCB4 | 234.9 | 0.0701%
IS4INV2M1SCB5 | 234.9 | 0.0701%
IS4INV2M1SCB6 | 234.9 | 0.0701%
IS4INV2M1SCB7 | 234.9 | 0.0701%
IS4INV2M1SCB8 | 234.9 | 0.0701%
IS4INV2M1SCB9 | 234.9 | 0.0701%
IS4INV2M1SCB10 | 0 | 0%
IS4INV2M2SCB1 | 234.9 | 0.0701%
IS4INV2M2SCB2 | 234.9 | 0.0701%
IS4INV2M2SCB3 | 234.9 | 0.0701%
IS4INV2M2SCB4 | 234.9 | 0.0701%
IS4INV2M2SCB5 | 234.9 | 0.0701%
IS4INV2M2SCB6 | 234.9 | 0.0701%
IS4INV2M2SCB7 | 234.9 | 0.0701%
IS4INV2M2SCB8 | 234.9 | 0.0701%
IS4INV2M2SCB9 | 208.8 | 0.06231%
IS4INV2M2SCB10 | 0 | 0%
IS4INV3M1SCB1 | 234.9 | 0.0701%
IS4INV3M1SCB2 | 234.9 | 0.0701%
IS4INV3M1SCB3 | 234.9 | 0.0701%
IS4INV3M1SCB4 | 234.9 | 0.0701%
IS4INV3M1SCB5 | 234.9 | 0.0701%
IS4INV3M1SCB6 | 234.9 | 0.0701%
IS4INV3M1SCB7 | 234.9 | 0.0701%
IS4INV3M1SCB8 | 234.9 | 0.0701%
IS4INV3M1SCB9 | 234.9 | 0.0701%
IS4INV3M1SCB10 | 0 | 0%
IS4INV3M2SCB1 | 234.9 | 0.0701%
IS4INV3M2SCB2 | 234.9 | 0.0701%
IS4INV3M2SCB3 | 234.9 | 0.0701%
IS4INV3M2SCB4 | 208.8 | 0.06231%
IS4INV3M2SCB5 | 234.9 | 0.0701%
IS4INV3M2SCB6 | 234.9 | 0.0701%
IS4INV3M2SCB7 | 234.9 | 0.0701%
IS4INV3M2SCB8 | 234.9 | 0.0701%
IS4INV3M2SCB9 | 234.9 | 0.0701%
IS4INV3M2SCB10 | 0 | 0%
IS4INV4M1SCB1 | 234.9 | 0.0701%
IS4INV4M1SCB2 | 234.9 | 0.0701%
IS4INV4M1SCB3 | 234.9 | 0.0701%
IS4INV4M1SCB4 | 234.9 | 0.0701%
IS4INV4M1SCB5 | 234.9 | 0.0701%
IS4INV4M1SCB6 | 234.9 | 0.0701%
IS4INV4M1SCB7 | 234.9 | 0.0701%
IS4INV4M1SCB8 | 234.9 | 0.0701%
IS4INV4M1SCB9 | 234.9 | 0.0701%
IS4INV4M1SCB10 | 0 | 0%
IS4INV4M2SCB1 | 234.9 | 0.0701%
IS4INV4M2SCB2 | 234.9 | 0.0701%
IS4INV4M2SCB3 | 234.9 | 0.0701%
IS4INV4M2SCB4 | 234.9 | 0.0701%
IS4INV4M2SCB5 | 208.8 | 0.06231%
IS4INV4M2SCB6 | 234.9 | 0.0701%
IS4INV4M2SCB7 | 234.9 | 0.0701%
IS4INV4M2SCB8 | 208.8 | 0.06231%
IS4INV4M2SCB9 | 234.9 | 0.0701%
IS4INV4M2SCB10 | 0 | 0%
IS5INV1M1SCB1 | 232.29 | 0.06932%
IS5INV1M1SCB2 | 232.29 | 0.06932%
IS5INV1M1SCB3 | 232.29 | 0.06932%
IS5INV1M1SCB4 | 232.29 | 0.06932%
IS5INV1M1SCB5 | 232.29 | 0.06932%
IS5INV1M1SCB6 | 232.29 | 0.06932%
IS5INV1M1SCB7 | 232.29 | 0.06932%
IS5INV1M1SCB8 | 232.29 | 0.06932%
IS5INV1M1SCB9 | 232.29 | 0.06932%
IS5INV1M1SCB10 | 0 | 0%
IS5INV1M2SCB1 | 232.29 | 0.06932%
IS5INV1M2SCB2 | 232.29 | 0.06932%
IS5INV1M2SCB3 | 232.29 | 0.06932%
IS5INV1M2SCB4 | 232.29 | 0.06932%
IS5INV1M2SCB5 | 232.29 | 0.06932%
IS5INV1M2SCB6 | 232.29 | 0.06932%
IS5INV1M2SCB7 | 232.29 | 0.06932%
IS5INV1M2SCB8 | 232.29 | 0.06932%
IS5INV1M2SCB9 | 232.29 | 0.06932%
IS5INV1M2SCB10 | 0 | 0%
IS5INV2M1SCB1 | 232.29 | 0.06932%
IS5INV2M1SCB2 | 232.29 | 0.06932%
IS5INV2M1SCB3 | 232.29 | 0.06932%
IS5INV2M1SCB4 | 232.29 | 0.06932%
IS5INV2M1SCB5 | 232.29 | 0.06932%
IS5INV2M1SCB6 | 232.29 | 0.06932%
IS5INV2M1SCB7 | 232.29 | 0.06932%
IS5INV2M1SCB8 | 232.29 | 0.06932%
IS5INV2M1SCB9 | 232.29 | 0.06932%
IS5INV2M1SCB10 | 0 | 0%
IS5INV2M2SCB1 | 232.29 | 0.06932%
IS5INV2M2SCB2 | 232.29 | 0.06932%
IS5INV2M2SCB3 | 232.29 | 0.06932%
IS5INV2M2SCB4 | 232.29 | 0.06932%
IS5INV2M2SCB5 | 232.29 | 0.06932%
IS5INV2M2SCB6 | 232.29 | 0.06932%
IS5INV2M2SCB7 | 232.29 | 0.06932%
IS5INV2M2SCB8 | 232.29 | 0.06932%
IS5INV2M2SCB9 | 232.29 | 0.06932%
IS5INV2M2SCB10 | 0 | 0%
IS5INV3M1SCB1 | 232.29 | 0.06932%
IS5INV3M1SCB2 | 232.29 | 0.06932%
IS5INV3M1SCB3 | 232.29 | 0.06932%
IS5INV3M1SCB4 | 232.29 | 0.06932%
IS5INV3M1SCB5 | 232.29 | 0.06932%
IS5INV3M1SCB6 | 232.29 | 0.06932%
IS5INV3M1SCB7 | 232.29 | 0.06932%
IS5INV3M1SCB8 | 232.29 | 0.06932%
IS5INV3M1SCB9 | 232.29 | 0.06932%
IS5INV3M1SCB10 | 0 | 0%
IS5INV3M2SCB1 | 232.29 | 0.06932%
IS5INV3M2SCB2 | 232.29 | 0.06932%
IS5INV3M2SCB3 | 232.29 | 0.06932%
IS5INV3M2SCB4 | 232.29 | 0.06932%
IS5INV3M2SCB5 | 232.29 | 0.06932%
IS5INV3M2SCB6 | 232.29 | 0.06932%
IS5INV3M2SCB7 | 232.29 | 0.06932%
IS5INV3M2SCB8 | 232.29 | 0.06932%
IS5INV3M2SCB9 | 232.29 | 0.06932%
IS5INV3M2SCB10 | 0 | 0%
IS5INV4M1SCB1 | 232.29 | 0.06932%
IS5INV4M1SCB2 | 232.29 | 0.06932%
IS5INV4M1SCB3 | 232.29 | 0.06932%
IS5INV4M1SCB4 | 232.29 | 0.06932%
IS5INV4M1SCB5 | 232.29 | 0.06932%
IS5INV4M1SCB6 | 232.29 | 0.06932%
IS5INV4M1SCB7 | 232.29 | 0.06932%
IS5INV4M1SCB8 | 232.29 | 0.06932%
IS5INV4M1SCB9 | 232.29 | 0.06932%
IS5INV4M1SCB10 | 0 | 0%
IS5INV4M2SCB1 | 232.29 | 0.06932%
IS5INV4M2SCB2 | 232.29 | 0.06932%
IS5INV4M2SCB3 | 232.29 | 0.06932%
IS5INV4M2SCB4 | 232.29 | 0.06932%
IS5INV4M2SCB5 | 232.29 | 0.06932%
IS5INV4M2SCB6 | 232.29 | 0.06932%
IS5INV4M2SCB7 | 232.29 | 0.06932%
IS5INV4M2SCB8 | 232.29 | 0.06932%
IS5INV4M2SCB9 | 232.29 | 0.06932%
IS5INV4M2SCB10 | 0 | 0%
IS6INV1M1SCB1 | 248.24 | 0.07408%
IS6INV1M1SCB2 | 248.24 | 0.07408%
IS6INV1M1SCB3 | 248.24 | 0.07408%
IS6INV1M1SCB4 | 248.24 | 0.07408%
IS6INV1M1SCB5 | 248.24 | 0.07408%
IS6INV1M1SCB6 | 248.24 | 0.07408%
IS6INV1M1SCB7 | 248.24 | 0.07408%
IS6INV1M1SCB8 | 248.24 | 0.07408%
IS6INV1M1SCB9 | 248.24 | 0.07408%
IS6INV1M1SCB10 | 0 | 0%
IS6INV1M2SCB1 | 248.24 | 0.07408%
IS6INV1M2SCB2 | 248.24 | 0.07408%
IS6INV1M2SCB3 | 248.24 | 0.07408%
IS6INV1M2SCB4 | 248.24 | 0.07408%
IS6INV1M2SCB5 | 248.24 | 0.07408%
IS6INV1M2SCB6 | 248.24 | 0.07408%
IS6INV1M2SCB7 | 248.24 | 0.07408%
IS6INV1M2SCB8 | 248.24 | 0.07408%
IS6INV1M2SCB9 | 0 | 0%
IS6INV1M2SCB10 | 0 | 0%
IS6INV2M1SCB1 | 217.21 | 0.06482%
IS6INV2M1SCB2 | 248.24 | 0.07408%
IS6INV2M1SCB3 | 248.24 | 0.07408%
IS6INV2M1SCB4 | 248.24 | 0.07408%
IS6INV2M1SCB5 | 248.24 | 0.07408%
IS6INV2M1SCB6 | 248.24 | 0.07408%
IS6INV2M1SCB7 | 248.24 | 0.07408%
IS6INV2M1SCB8 | 248.24 | 0.07408%
IS6INV2M1SCB9 | 248.24 | 0.07408%
IS6INV2M1SCB10 | 0 | 0%
IS6INV2M2SCB1 | 248.24 | 0.07408%
IS6INV2M2SCB2 | 248.24 | 0.07408%
IS6INV2M2SCB3 | 248.24 | 0.07408%
IS6INV2M2SCB4 | 248.24 | 0.07408%
IS6INV2M2SCB5 | 248.24 | 0.07408%
IS6INV2M2SCB6 | 248.24 | 0.07408%
IS6INV2M2SCB7 | 248.24 | 0.07408%
IS6INV2M2SCB8 | 248.24 | 0.07408%
IS6INV2M2SCB9 | 0 | 0%
IS6INV2M2SCB10 | 0 | 0%
IS6INV3M1SCB1 | 250.56 | 0.07477%
IS6INV3M1SCB2 | 250.56 | 0.07477%
IS6INV3M1SCB3 | 250.56 | 0.07477%
IS6INV3M1SCB4 | 219.24 | 0.06543%
IS6INV3M1SCB5 | 219.24 | 0.06543%
IS6INV3M1SCB6 | 250.56 | 0.07477%
IS6INV3M1SCB7 | 250.56 | 0.07477%
IS6INV3M1SCB8 | 250.56 | 0.07477%
IS6INV3M1SCB9 | 250.56 | 0.07477%
IS6INV3M1SCB10 | 0 | 0%
IS6INV3M2SCB1 | 250.56 | 0.07477%
IS6INV3M2SCB2 | 250.56 | 0.07477%
IS6INV3M2SCB3 | 219.24 | 0.06543%
IS6INV3M2SCB4 | 219.24 | 0.06543%
IS6INV3M2SCB5 | 219.24 | 0.06543%
IS6INV3M2SCB6 | 219.24 | 0.06543%
IS6INV3M2SCB7 | 250.56 | 0.07477%
IS6INV3M2SCB8 | 250.56 | 0.07477%
IS6INV3M2SCB9 | 250.56 | 0.07477%
IS6INV3M2SCB10 | 250.56 | 0.07477%
IS6INV4M1SCB1 | 248.24 | 0.07408%
IS6INV4M1SCB2 | 248.24 | 0.07408%
IS6INV4M1SCB3 | 248.24 | 0.07408%
IS6INV4M1SCB4 | 248.24 | 0.07408%
IS6INV4M1SCB5 | 248.24 | 0.07408%
IS6INV4M1SCB6 | 248.24 | 0.07408%
IS6INV4M1SCB7 | 248.24 | 0.07408%
IS6INV4M1SCB8 | 248.24 | 0.07408%
IS6INV4M1SCB9 | 217.21 | 0.06482%
IS6INV4M1SCB10 | 0 | 0%
IS6INV4M2SCB1 | 248.24 | 0.07408%
IS6INV4M2SCB2 | 248.24 | 0.07408%
IS6INV4M2SCB3 | 248.24 | 0.07408%
IS6INV4M2SCB4 | 248.24 | 0.07408%
IS6INV4M2SCB5 | 248.24 | 0.07408%
IS6INV4M2SCB6 | 248.24 | 0.07408%
IS6INV4M2SCB7 | 248.24 | 0.07408%
IS6INV4M2SCB8 | 248.24 | 0.07408%
IS6INV4M2SCB9 | 0 | 0%
IS6INV4M2SCB10 | 0 | 0%
IS7INV1M1SCB1 | 250.56 | 0.07477%
IS7INV1M1SCB2 | 250.56 | 0.07477%
IS7INV1M1SCB3 | 250.56 | 0.07477%
IS7INV1M1SCB4 | 250.56 | 0.07477%
IS7INV1M1SCB5 | 250.56 | 0.07477%
IS7INV1M1SCB6 | 250.56 | 0.07477%
IS7INV1M1SCB7 | 250.56 | 0.07477%
IS7INV1M1SCB8 | 219.24 | 0.06543%
IS7INV1M1SCB9 | 0 | 0%
IS7INV1M1SCB10 | 0 | 0%
IS7INV1M2SCB1 | 250.56 | 0.07477%
IS7INV1M2SCB2 | 250.56 | 0.07477%
IS7INV1M2SCB3 | 250.56 | 0.07477%
IS7INV1M2SCB4 | 250.56 | 0.07477%
IS7INV1M2SCB5 | 250.56 | 0.07477%
IS7INV1M2SCB6 | 250.56 | 0.07477%
IS7INV1M2SCB7 | 219.24 | 0.06543%
IS7INV1M2SCB8 | 250.56 | 0.07477%
IS7INV1M2SCB9 | 0 | 0%
IS7INV1M2SCB10 | 0 | 0%
IS7INV2M1SCB1 | 125.28 | 0.03739%
IS7INV2M1SCB2 | 250.56 | 0.07477%
IS7INV2M1SCB3 | 250.56 | 0.07477%
IS7INV2M1SCB4 | 250.56 | 0.07477%
IS7INV2M1SCB5 | 250.56 | 0.07477%
IS7INV2M1SCB6 | 250.56 | 0.07477%
IS7INV2M1SCB7 | 250.56 | 0.07477%
IS7INV2M1SCB8 | 250.56 | 0.07477%
IS7INV2M1SCB9 | 219.24 | 0.06543%
IS7INV2M1SCB10 | 0 | 0%
IS7INV2M2SCB1 | 250.56 | 0.07477%
IS7INV2M2SCB2 | 250.56 | 0.07477%
IS7INV2M2SCB3 | 250.56 | 0.07477%
IS7INV2M2SCB4 | 250.56 | 0.07477%
IS7INV2M2SCB5 | 250.56 | 0.07477%
IS7INV2M2SCB6 | 250.56 | 0.07477%
IS7INV2M2SCB7 | 250.56 | 0.07477%
IS7INV2M2SCB8 | 250.56 | 0.07477%
IS7INV2M2SCB9 | 0 | 0%
IS7INV2M2SCB10 | 0 | 0%
IS7INV3M1SCB1 | 250.56 | 0.07477%
IS7INV3M1SCB2 | 250.56 | 0.07477%
IS7INV3M1SCB3 | 250.56 | 0.07477%
IS7INV3M1SCB4 | 250.56 | 0.07477%
IS7INV3M1SCB5 | 250.56 | 0.07477%
IS7INV3M1SCB6 | 250.56 | 0.07477%
IS7INV3M1SCB7 | 250.56 | 0.07477%
IS7INV3M1SCB8 | 250.56 | 0.07477%
IS7INV3M1SCB9 | 219.24 | 0.06543%
IS7INV3M1SCB10 | 0 | 0%
IS7INV3M2SCB1 | 219.24 | 0.06543%
IS7INV3M2SCB2 | 250.56 | 0.07477%
IS7INV3M2SCB3 | 250.56 | 0.07477%
IS7INV3M2SCB4 | 250.56 | 0.07477%
IS7INV3M2SCB5 | 250.56 | 0.07477%
IS7INV3M2SCB6 | 250.56 | 0.07477%
IS7INV3M2SCB7 | 250.56 | 0.07477%
IS7INV3M2SCB8 | 250.56 | 0.07477%
IS7INV3M2SCB9 | 0 | 0%
IS7INV3M2SCB10 | 0 | 0%
IS7INV4M1SCB1 | 250.56 | 0.07477%
IS7INV4M1SCB2 | 250.56 | 0.07477%
IS7INV4M1SCB3 | 250.56 | 0.07477%
IS7INV4M1SCB4 | 250.56 | 0.07477%
IS7INV4M1SCB5 | 219.24 | 0.06543%
IS7INV4M1SCB6 | 250.56 | 0.07477%
IS7INV4M1SCB7 | 250.56 | 0.07477%
IS7INV4M1SCB8 | 250.56 | 0.07477%
IS7INV4M1SCB9 | 250.56 | 0.07477%
IS7INV4M1SCB10 | 0 | 0%
IS7INV4M2SCB1 | 250.56 | 0.07477%
IS7INV4M2SCB2 | 219.24 | 0.06543%
IS7INV4M2SCB3 | 250.56 | 0.07477%
IS7INV4M2SCB4 | 250.56 | 0.07477%
IS7INV4M2SCB5 | 250.56 | 0.07477%
IS7INV4M2SCB6 | 250.56 | 0.07477%
IS7INV4M2SCB7 | 250.56 | 0.07477%
IS7INV4M2SCB8 | 250.56 | 0.07477%
IS7INV4M2SCB9 | 0 | 0%
IS7INV4M2SCB10 | 0 | 0%
IS8INV1M1SCB1 | 250.56 | 0.07477%
IS8INV1M1SCB2 | 250.56 | 0.07477%
IS8INV1M1SCB3 | 250.56 | 0.07477%
IS8INV1M1SCB4 | 250.56 | 0.07477%
IS8INV1M1SCB5 | 250.56 | 0.07477%
IS8INV1M1SCB6 | 250.56 | 0.07477%
IS8INV1M1SCB7 | 250.56 | 0.07477%
IS8INV1M1SCB8 | 250.56 | 0.07477%
IS8INV1M1SCB9 | 0 | 0%
IS8INV1M1SCB10 | 0 | 0%
IS8INV1M2SCB1 | 250.56 | 0.07477%
IS8INV1M2SCB2 | 250.56 | 0.07477%
IS8INV1M2SCB3 | 250.56 | 0.07477%
IS8INV1M2SCB4 | 250.56 | 0.07477%
IS8INV1M2SCB5 | 250.56 | 0.07477%
IS8INV1M2SCB6 | 250.56 | 0.07477%
IS8INV1M2SCB7 | 250.56 | 0.07477%
IS8INV1M2SCB8 | 250.56 | 0.07477%
IS8INV1M2SCB9 | 250.56 | 0.07477%
IS8INV1M2SCB10 | 0 | 0%
IS8INV2M1SCB1 | 250.56 | 0.07477%
IS8INV2M1SCB2 | 250.56 | 0.07477%
IS8INV2M1SCB3 | 250.56 | 0.07477%
IS8INV2M1SCB4 | 250.56 | 0.07477%
IS8INV2M1SCB5 | 250.56 | 0.07477%
IS8INV2M1SCB6 | 250.56 | 0.07477%
IS8INV2M1SCB7 | 250.56 | 0.07477%
IS8INV2M1SCB8 | 250.56 | 0.07477%
IS8INV2M1SCB9 | 250.56 | 0.07477%
IS8INV2M1SCB10 | 0 | 0%
IS8INV2M2SCB1 | 250.56 | 0.07477%
IS8INV2M2SCB2 | 250.56 | 0.07477%
IS8INV2M2SCB3 | 250.56 | 0.07477%
IS8INV2M2SCB4 | 250.56 | 0.07477%
IS8INV2M2SCB5 | 250.56 | 0.07477%
IS8INV2M2SCB6 | 250.56 | 0.07477%
IS8INV2M2SCB7 | 250.56 | 0.07477%
IS8INV2M2SCB8 | 250.56 | 0.07477%
IS8INV2M2SCB9 | 0 | 0%
IS8INV2M2SCB10 | 0 | 0%
IS8INV3M1SCB1 | 250.56 | 0.07477%
IS8INV3M1SCB2 | 250.56 | 0.07477%
IS8INV3M1SCB3 | 250.56 | 0.07477%
IS8INV3M1SCB4 | 250.56 | 0.07477%
IS8INV3M1SCB5 | 250.56 | 0.07477%
IS8INV3M1SCB6 | 250.56 | 0.07477%
IS8INV3M1SCB7 | 250.56 | 0.07477%
IS8INV3M1SCB8 | 250.56 | 0.07477%
IS8INV3M1SCB9 | 250.56 | 0.07477%
IS8INV3M1SCB10 | 0 | 0%
IS8INV3M2SCB1 | 250.56 | 0.07477%
IS8INV3M2SCB2 | 250.56 | 0.07477%
IS8INV3M2SCB3 | 250.56 | 0.07477%
IS8INV3M2SCB4 | 250.56 | 0.07477%
IS8INV3M2SCB5 | 250.56 | 0.07477%
IS8INV3M2SCB6 | 250.56 | 0.07477%
IS8INV3M2SCB7 | 250.56 | 0.07477%
IS8INV3M2SCB8 | 250.56 | 0.07477%
IS8INV3M2SCB9 | 0 | 0%
IS8INV3M2SCB10 | 0 | 0%
IS8INV4M1SCB1 | 234.9 | 0.0701%
IS8INV4M1SCB2 | 234.9 | 0.0701%
IS8INV4M1SCB3 | 234.9 | 0.0701%
IS8INV4M1SCB4 | 234.9 | 0.0701%
IS8INV4M1SCB5 | 130.5 | 0.03894%
IS8INV4M1SCB6 | 156.6 | 0.04673%
IS8INV4M1SCB7 | 182.7 | 0.05452%
IS8INV4M1SCB8 | 234.9 | 0.0701%
IS8INV4M1SCB9 | 208.8 | 0.06231%
IS8INV4M1SCB10 | 234.9 | 0.0701%
IS8INV4M2SCB1 | 234.9 | 0.0701%
IS8INV4M2SCB2 | 234.9 | 0.0701%
IS8INV4M2SCB3 | 234.9 | 0.0701%
IS8INV4M2SCB4 | 234.9 | 0.0701%
IS8INV4M2SCB5 | 234.9 | 0.0701%
IS8INV4M2SCB6 | 208.8 | 0.06231%
IS8INV4M2SCB7 | 234.9 | 0.0701%
IS8INV4M2SCB8 | 234.9 | 0.0701%
IS8INV4M2SCB9 | 208.8 | 0.06231%
IS8INV4M2SCB10 | 0 | 0%
IS9INV1M1SCB1 | 268.685 | 0.08018%
IS9INV1M1SCB2 | 268.685 | 0.08018%
IS9INV1M1SCB3 | 0 | 0%
IS9INV1M1SCB4 | 268.685 | 0.08018%
IS9INV1M1SCB5 | 268.685 | 0.08018%
IS9INV1M1SCB6 | 268.685 | 0.08018%
IS9INV1M1SCB7 | 252.88 | 0.07547%
IS9INV1M1SCB8 | 252.88 | 0.07547%
IS9INV1M1SCB9 | 252.88 | 0.07547%
IS9INV1M1SCB10 | 0 | 0%
IS9INV1M2SCB1 | 252.88 | 0.07547%
IS9INV1M2SCB2 | 252.88 | 0.07547%
IS9INV1M2SCB3 | 252.88 | 0.07547%
IS9INV1M2SCB4 | 252.88 | 0.07547%
IS9INV1M2SCB5 | 252.88 | 0.07547%
IS9INV1M2SCB6 | 252.88 | 0.07547%
IS9INV1M2SCB7 | 252.88 | 0.07547%
IS9INV1M2SCB8 | 252.88 | 0.07547%
IS9INV1M2SCB9 | 0 | 0%
IS9INV1M2SCB10 | 0 | 0%
IS9INV2M1SCB1 | 268.685 | 0.08018%
IS9INV2M1SCB2 | 268.685 | 0.08018%
IS9INV2M1SCB3 | 268.685 | 0.08018%
IS9INV2M1SCB4 | 268.685 | 0.08018%
IS9INV2M1SCB5 | 268.685 | 0.08018%
IS9INV2M1SCB6 | 252.88 | 0.07547%
IS9INV2M1SCB7 | 252.88 | 0.07547%
IS9INV2M1SCB8 | 252.88 | 0.07547%
IS9INV2M1SCB9 | 0 | 0%
IS9INV2M1SCB10 | 0 | 0%
IS9INV2M2SCB1 | 252.88 | 0.07547%
IS9INV2M2SCB2 | 252.88 | 0.07547%
IS9INV2M2SCB3 | 252.88 | 0.07547%
IS9INV2M2SCB4 | 252.88 | 0.07547%
IS9INV2M2SCB5 | 221.27 | 0.06603%
IS9INV2M2SCB6 | 221.27 | 0.06603%
IS9INV2M2SCB7 | 252.88 | 0.07547%
IS9INV2M2SCB8 | 252.88 | 0.07547%
IS9INV2M2SCB9 | 252.88 | 0.07547%
IS9INV2M2SCB10 | 0 | 0%
IS9INV3M1SCB1 | 268.685 | 0.08018%
IS9INV3M1SCB2 | 252.88 | 0.07547%
IS9INV3M1SCB3 | 268.685 | 0.08018%
IS9INV3M1SCB4 | 252.88 | 0.07547%
IS9INV3M1SCB5 | 252.88 | 0.07547%
IS9INV3M1SCB6 | 252.88 | 0.07547%
IS9INV3M1SCB7 | 221.27 | 0.06603%
IS9INV3M1SCB8 | 252.88 | 0.07547%
IS9INV3M1SCB9 | 252.88 | 0.07547%
IS9INV3M1SCB10 | 0 | 0%
IS9INV3M2SCB1 | 252.88 | 0.07547%
IS9INV3M2SCB2 | 252.88 | 0.07547%
IS9INV3M2SCB3 | 252.88 | 0.07547%
IS9INV3M2SCB4 | 252.88 | 0.07547%
IS9INV3M2SCB5 | 252.88 | 0.07547%
IS9INV3M2SCB6 | 252.88 | 0.07547%
IS9INV3M2SCB7 | 252.88 | 0.07547%
IS9INV3M2SCB8 | 252.88 | 0.07547%
IS9INV3M2SCB9 | 0 | 0%
IS9INV3M2SCB10 | 0 | 0%
IS9INV4M1SCB1 | 221.27 | 0.06603%
IS9INV4M1SCB2 | 252.88 | 0.07547%
IS9INV4M1SCB3 | 252.88 | 0.07547%
IS9INV4M1SCB4 | 252.88 | 0.07547%
IS9INV4M1SCB5 | 252.88 | 0.07547%
IS9INV4M1SCB6 | 252.88 | 0.07547%
IS9INV4M1SCB7 | 252.88 | 0.07547%
IS9INV4M1SCB8 | 252.88 | 0.07547%
IS9INV4M1SCB9 | 252.88 | 0.07547%
IS9INV4M1SCB10 | 0 | 0%
IS9INV4M2SCB1 | 252.88 | 0.07547%
IS9INV4M2SCB2 | 252.88 | 0.07547%
IS9INV4M2SCB3 | 252.88 | 0.07547%
IS9INV4M2SCB4 | 252.88 | 0.07547%
IS9INV4M2SCB5 | 252.88 | 0.07547%
IS9INV4M2SCB6 | 221.27 | 0.06603%
IS9INV4M2SCB7 | 252.88 | 0.07547%
IS9INV4M2SCB8 | 221.27 | 0.06603%
IS9INV4M2SCB9 | 0 | 0%
IS9INV4M2SCB10 | 0 | 0%
IS10INV1M1SCB1 | 250.56 | 0.07477%
IS10INV1M1SCB2 | 250.56 | 0.07477%
IS10INV1M1SCB3 | 219.24 | 0.06543%
IS10INV1M1SCB4 | 219.24 | 0.06543%
IS10INV1M1SCB5 | 281.88 | 0.08412%
IS10INV1M1SCB6 | 281.88 | 0.08412%
IS10INV1M1SCB7 | 281.88 | 0.08412%
IS10INV1M1SCB8 | 281.88 | 0.08412%
IS10INV1M1SCB9 | 0 | 0%
IS10INV1M1SCB10 | 0 | 0%
IS10INV1M2SCB1 | 93.96 | 0.02804%
IS10INV1M2SCB2 | 250.56 | 0.07477%
IS10INV1M2SCB3 | 250.56 | 0.07477%
IS10INV1M2SCB4 | 250.56 | 0.07477%
IS10INV1M2SCB5 | 250.56 | 0.07477%
IS10INV1M2SCB6 | 250.56 | 0.07477%
IS10INV1M2SCB7 | 250.56 | 0.07477%
IS10INV1M2SCB8 | 250.56 | 0.07477%
IS10INV1M2SCB9 | 250.56 | 0.07477%
IS10INV1M2SCB10 | 0 | 0%
IS10INV2M1SCB1 | 250.56 | 0.07477%
IS10INV2M1SCB2 | 250.56 | 0.07477%
IS10INV2M1SCB3 | 250.56 | 0.07477%
IS10INV2M1SCB4 | 250.56 | 0.07477%
IS10INV2M1SCB5 | 250.56 | 0.07477%
IS10INV2M1SCB6 | 250.56 | 0.07477%
IS10INV2M1SCB7 | 219.24 | 0.06543%
IS10INV2M1SCB8 | 250.56 | 0.07477%
IS10INV2M1SCB9 | 0 | 0%
IS10INV2M1SCB10 | 0 | 0%
IS10INV2M2SCB1 | 250.56 | 0.07477%
IS10INV2M2SCB2 | 250.56 | 0.07477%
IS10INV2M2SCB3 | 250.56 | 0.07477%
IS10INV2M2SCB4 | 219.24 | 0.06543%
IS10INV2M2SCB5 | 250.56 | 0.07477%
IS10INV2M2SCB6 | 250.56 | 0.07477%
IS10INV2M2SCB7 | 250.56 | 0.07477%
IS10INV2M2SCB8 | 250.56 | 0.07477%
IS10INV2M2SCB9 | 250.56 | 0.07477%
IS10INV2M2SCB10 | 0 | 0%
IS10INV3M1SCB1 | 250.56 | 0.07477%
IS10INV3M1SCB2 | 250.56 | 0.07477%
IS10INV3M1SCB3 | 250.56 | 0.07477%
IS10INV3M1SCB4 | 250.56 | 0.07477%
IS10INV3M1SCB5 | 219.24 | 0.06543%
IS10INV3M1SCB6 | 250.56 | 0.07477%
IS10INV3M1SCB7 | 219.24 | 0.06543%
IS10INV3M1SCB8 | 250.56 | 0.07477%
IS10INV3M1SCB9 | 0 | 0%
IS10INV3M1SCB10 | 0 | 0%
IS10INV3M2SCB1 | 250.56 | 0.07477%
IS10INV3M2SCB2 | 250.56 | 0.07477%
IS10INV3M2SCB3 | 250.56 | 0.07477%
IS10INV3M2SCB4 | 250.56 | 0.07477%
IS10INV3M2SCB5 | 250.56 | 0.07477%
IS10INV3M2SCB6 | 250.56 | 0.07477%
IS10INV3M2SCB7 | 250.56 | 0.07477%
IS10INV3M2SCB8 | 250.56 | 0.07477%
IS10INV3M2SCB9 | 250.56 | 0.07477%
IS10INV3M2SCB10 | 0 | 0%
IS10INV4M1SCB1 | 250.56 | 0.07477%
IS10INV4M1SCB2 | 250.56 | 0.07477%
IS10INV4M1SCB3 | 250.56 | 0.07477%
IS10INV4M1SCB4 | 250.56 | 0.07477%
IS10INV4M1SCB5 | 250.56 | 0.07477%
IS10INV4M1SCB6 | 250.56 | 0.07477%
IS10INV4M1SCB7 | 250.56 | 0.07477%
IS10INV4M1SCB8 | 219.24 | 0.06543%
IS10INV4M1SCB9 | 0 | 0%
IS10INV4M1SCB10 | 0 | 0%
IS10INV4M2SCB1 | 250.56 | 0.07477%
IS10INV4M2SCB2 | 250.56 | 0.07477%
IS10INV4M2SCB3 | 250.56 | 0.07477%
IS10INV4M2SCB4 | 250.56 | 0.07477%
IS10INV4M2SCB5 | 250.56 | 0.07477%
IS10INV4M2SCB6 | 250.56 | 0.07477%
IS10INV4M2SCB7 | 250.56 | 0.07477%
IS10INV4M2SCB8 | 250.56 | 0.07477%
IS10INV4M2SCB9 | 219.24 | 0.06543%
IS10INV4M2SCB10 | 0 | 0%
IS11INV1M1SCB1 | 252.88 | 0.07547%
IS11INV1M1SCB2 | 252.88 | 0.07547%
IS11INV1M1SCB3 | 252.88 | 0.07547%
IS11INV1M1SCB4 | 252.88 | 0.07547%
IS11INV1M1SCB5 | 252.88 | 0.07547%
IS11INV1M1SCB6 | 252.88 | 0.07547%
IS11INV1M1SCB7 | 252.88 | 0.07547%
IS11INV1M1SCB8 | 252.88 | 0.07547%
IS11INV1M1SCB9 | 0 | 0%
IS11INV1M1SCB10 | 0 | 0%
IS11INV1M2SCB1 | 268.685 | 0.08018%
IS11INV1M2SCB2 | 268.685 | 0.08018%
IS11INV1M2SCB3 | 252.88 | 0.07547%
IS11INV1M2SCB4 | 252.88 | 0.07547%
IS11INV1M2SCB5 | 221.27 | 0.06603%
IS11INV1M2SCB6 | 221.27 | 0.06603%
IS11INV1M2SCB7 | 252.88 | 0.07547%
IS11INV1M2SCB8 | 252.88 | 0.07547%
IS11INV1M2SCB9 | 221.27 | 0.06603%
IS11INV1M2SCB10 | 0 | 0%
IS11INV2M1SCB1 | 252.88 | 0.07547%
IS11INV2M1SCB2 | 252.88 | 0.07547%
IS11INV2M1SCB3 | 252.88 | 0.07547%
IS11INV2M1SCB4 | 252.88 | 0.07547%
IS11INV2M1SCB5 | 252.88 | 0.07547%
IS11INV2M1SCB6 | 252.88 | 0.07547%
IS11INV2M1SCB7 | 252.88 | 0.07547%
IS11INV2M1SCB8 | 252.88 | 0.07547%
IS11INV2M1SCB9 | 252.88 | 0.07547%
IS11INV2M1SCB10 | 0 | 0%
IS11INV2M2SCB1 | 252.88 | 0.07547%
IS11INV2M2SCB2 | 252.88 | 0.07547%
IS11INV2M2SCB3 | 268.685 | 0.08018%
IS11INV2M2SCB4 | 252.88 | 0.07547%
IS11INV2M2SCB5 | 268.685 | 0.08018%
IS11INV2M2SCB6 | 252.88 | 0.07547%
IS11INV2M2SCB7 | 252.88 | 0.07547%
IS11INV2M2SCB8 | 237.075 | 0.07075%
IS11INV2M2SCB9 | 0 | 0%
IS11INV2M2SCB10 | 0 | 0%
IS11INV3M1SCB1 | 252.88 | 0.07547%
IS11INV3M1SCB2 | 252.88 | 0.07547%
IS11INV3M1SCB3 | 252.88 | 0.07547%
IS11INV3M1SCB4 | 252.88 | 0.07547%
IS11INV3M1SCB5 | 252.88 | 0.07547%
IS11INV3M1SCB6 | 252.88 | 0.07547%
IS11INV3M1SCB7 | 252.88 | 0.07547%
IS11INV3M1SCB8 | 252.88 | 0.07547%
IS11INV3M1SCB9 | 0 | 0%
IS11INV3M1SCB10 | 0 | 0%
IS11INV3M2SCB1 | 252.88 | 0.07547%
IS11INV3M2SCB2 | 252.88 | 0.07547%
IS11INV3M2SCB3 | 221.27 | 0.06603%
IS11INV3M2SCB4 | 252.88 | 0.07547%
IS11INV3M2SCB5 | 252.88 | 0.07547%
IS11INV3M2SCB6 | 221.27 | 0.06603%
IS11INV3M2SCB7 | 252.88 | 0.07547%
IS11INV3M2SCB8 | 252.88 | 0.07547%
IS11INV3M2SCB9 | 252.88 | 0.07547%
IS11INV3M2SCB10 | 0 | 0%
IS11INV4M1SCB1 | 252.88 | 0.07547%
IS11INV4M1SCB2 | 252.88 | 0.07547%
IS11INV4M1SCB3 | 252.88 | 0.07547%
IS11INV4M1SCB4 | 252.88 | 0.07547%
IS11INV4M1SCB5 | 252.88 | 0.07547%
IS11INV4M1SCB6 | 252.88 | 0.07547%
IS11INV4M1SCB7 | 252.88 | 0.07547%
IS11INV4M1SCB8 | 252.88 | 0.07547%
IS11INV4M1SCB9 | 0 | 0%
IS11INV4M1SCB10 | 0 | 0%
IS11INV4M2SCB1 | 252.88 | 0.07547%
IS11INV4M2SCB2 | 252.88 | 0.07547%
IS11INV4M2SCB3 | 221.27 | 0.06603%
IS11INV4M2SCB4 | 221.27 | 0.06603%
IS11INV4M2SCB5 | 221.27 | 0.06603%
IS11INV4M2SCB6 | 205.465 | 0.06132%
IS11INV4M2SCB7 | 252.88 | 0.07547%
IS11INV4M2SCB8 | 158.05 | 0.04717%
IS11INV4M2SCB9 | 0 | 0%
IS11INV4M2SCB10 | 0 | 0%
IS12INV1M1SCB1 | 266.22 | 0.07945%
IS12INV1M1SCB2 | 266.22 | 0.07945%
IS12INV1M1SCB3 | 250.56 | 0.07477%
IS12INV1M1SCB4 | 250.56 | 0.07477%
IS12INV1M1SCB5 | 250.56 | 0.07477%
IS12INV1M1SCB6 | 250.56 | 0.07477%
IS12INV1M1SCB7 | 250.56 | 0.07477%
IS12INV1M1SCB8 | 156.6 | 0.04673%
IS12INV1M1SCB9 | 250.56 | 0.07477%
IS12INV1M1SCB10 | 0 | 0%
IS12INV1M2SCB1 | 266.22 | 0.07945%
IS12INV1M2SCB2 | 266.22 | 0.07945%
IS12INV1M2SCB3 | 266.22 | 0.07945%
IS12INV1M2SCB4 | 266.22 | 0.07945%
IS12INV1M2SCB5 | 266.22 | 0.07945%
IS12INV1M2SCB6 | 266.22 | 0.07945%
IS12INV1M2SCB7 | 266.22 | 0.07945%
IS12INV1M2SCB8 | 250.56 | 0.07477%
IS12INV1M2SCB9 | 0 | 0%
IS12INV1M2SCB10 | 0 | 0%
IS12INV2M1SCB1 | 219.24 | 0.06543%
IS12INV2M1SCB2 | 250.56 | 0.07477%
IS12INV2M1SCB3 | 250.56 | 0.07477%
IS12INV2M1SCB4 | 250.56 | 0.07477%
IS12INV2M1SCB5 | 219.24 | 0.06543%
IS12INV2M1SCB6 | 250.56 | 0.07477%
IS12INV2M1SCB7 | 250.56 | 0.07477%
IS12INV2M1SCB8 | 250.56 | 0.07477%
IS12INV2M1SCB9 | 0 | 0%
IS12INV2M1SCB10 | 0 | 0%
IS12INV2M2SCB1 | 250.56 | 0.07477%
IS12INV2M2SCB2 | 250.56 | 0.07477%
IS12INV2M2SCB3 | 250.56 | 0.07477%
IS12INV2M2SCB4 | 250.56 | 0.07477%
IS12INV2M2SCB5 | 250.56 | 0.07477%
IS12INV2M2SCB6 | 250.56 | 0.07477%
IS12INV2M2SCB7 | 250.56 | 0.07477%
IS12INV2M2SCB8 | 250.56 | 0.07477%
IS12INV2M2SCB9 | 250.56 | 0.07477%
IS12INV2M2SCB10 | 0 | 0%
IS12INV3M1SCB1 | 250.56 | 0.07477%
IS12INV3M1SCB2 | 219.24 | 0.06543%
IS12INV3M1SCB3 | 219.24 | 0.06543%
IS12INV3M1SCB4 | 250.56 | 0.07477%
IS12INV3M1SCB5 | 250.56 | 0.07477%
IS12INV3M1SCB6 | 250.56 | 0.07477%
IS12INV3M1SCB7 | 250.56 | 0.07477%
IS12INV3M1SCB8 | 250.56 | 0.07477%
IS12INV3M1SCB9 | 250.56 | 0.07477%
IS12INV3M1SCB10 | 0 | 0%
IS12INV3M2SCB1 | 250.56 | 0.07477%
IS12INV3M2SCB2 | 250.56 | 0.07477%
IS12INV3M2SCB3 | 250.56 | 0.07477%
IS12INV3M2SCB4 | 250.56 | 0.07477%
IS12INV3M2SCB5 | 250.56 | 0.07477%
IS12INV3M2SCB6 | 250.56 | 0.07477%
IS12INV3M2SCB7 | 250.56 | 0.07477%
IS12INV3M2SCB8 | 250.56 | 0.07477%
IS12INV3M2SCB9 | 0 | 0%
IS12INV3M2SCB10 | 0 | 0%
IS12INV4M1SCB1 | 250.56 | 0.07477%
IS12INV4M1SCB2 | 250.56 | 0.07477%
IS12INV4M1SCB3 | 250.56 | 0.07477%
IS12INV4M1SCB4 | 250.56 | 0.07477%
IS12INV4M1SCB5 | 250.56 | 0.07477%
IS12INV4M1SCB6 | 250.56 | 0.07477%
IS12INV4M1SCB7 | 250.56 | 0.07477%
IS12INV4M1SCB8 | 250.56 | 0.07477%
IS12INV4M1SCB9 | 0 | 0%
IS12INV4M1SCB10 | 0 | 0%
IS12INV4M2SCB1 | 250.56 | 0.07477%
IS12INV4M2SCB2 | 250.56 | 0.07477%
IS12INV4M2SCB3 | 250.56 | 0.07477%
IS12INV4M2SCB4 | 250.56 | 0.07477%
IS12INV4M2SCB5 | 250.56 | 0.07477%
IS12INV4M2SCB6 | 187.92 | 0.05608%
IS12INV4M2SCB7 | 250.56 | 0.07477%
IS12INV4M2SCB8 | 250.56 | 0.07477%
IS12INV4M2SCB9 | 266.22 | 0.07945%
IS12INV4M2SCB10 | 0 | 0%
IS13INV1M1SCB1 | 250.56 | 0.07477%
IS13INV1M1SCB2 | 250.56 | 0.07477%
IS13INV1M1SCB3 | 250.56 | 0.07477%
IS13INV1M1SCB4 | 250.56 | 0.07477%
IS13INV1M1SCB5 | 250.56 | 0.07477%
IS13INV1M1SCB6 | 250.56 | 0.07477%
IS13INV1M1SCB7 | 250.56 | 0.07477%
IS13INV1M1SCB8 | 250.56 | 0.07477%
IS13INV1M1SCB9 | 0 | 0%
IS13INV1M1SCB10 | 0 | 0%
IS13INV1M2SCB1 | 250.56 | 0.07477%
IS13INV1M2SCB2 | 250.56 | 0.07477%
IS13INV1M2SCB3 | 250.56 | 0.07477%
IS13INV1M2SCB4 | 250.56 | 0.07477%
IS13INV1M2SCB5 | 250.56 | 0.07477%
IS13INV1M2SCB6 | 250.56 | 0.07477%
IS13INV1M2SCB7 | 250.56 | 0.07477%
IS13INV1M2SCB8 | 250.56 | 0.07477%
IS13INV1M2SCB9 | 0 | 0%
IS13INV1M2SCB10 | 0 | 0%
IS13INV2M1SCB1 | 250.56 | 0.07477%
IS13INV2M1SCB2 | 219.24 | 0.06543%
IS13INV2M1SCB3 | 250.56 | 0.07477%
IS13INV2M1SCB4 | 250.56 | 0.07477%
IS13INV2M1SCB5 | 250.56 | 0.07477%
IS13INV2M1SCB6 | 250.56 | 0.07477%
IS13INV2M1SCB7 | 250.56 | 0.07477%
IS13INV2M1SCB8 | 250.56 | 0.07477%
IS13INV2M1SCB9 | 219.24 | 0.06543%
IS13INV2M1SCB10 | 0 | 0%
IS13INV2M2SCB1 | 250.56 | 0.07477%
IS13INV2M2SCB2 | 250.56 | 0.07477%
IS13INV2M2SCB3 | 250.56 | 0.07477%
IS13INV2M2SCB4 | 250.56 | 0.07477%
IS13INV2M2SCB5 | 250.56 | 0.07477%
IS13INV2M2SCB6 | 250.56 | 0.07477%
IS13INV2M2SCB7 | 250.56 | 0.07477%
IS13INV2M2SCB8 | 250.56 | 0.07477%
IS13INV2M2SCB9 | 0 | 0%
IS13INV2M2SCB10 | 0 | 0%
IS13INV3M1SCB1 | 219.24 | 0.06543%
IS13INV3M1SCB2 | 250.56 | 0.07477%
IS13INV3M1SCB3 | 250.56 | 0.07477%
IS13INV3M1SCB4 | 250.56 | 0.07477%
IS13INV3M1SCB5 | 250.56 | 0.07477%
IS13INV3M1SCB6 | 250.56 | 0.07477%
IS13INV3M1SCB7 | 250.56 | 0.07477%
IS13INV3M1SCB8 | 219.24 | 0.06543%
IS13INV3M1SCB9 | 250.56 | 0.07477%
IS13INV3M1SCB10 | 0 | 0%
IS13INV3M2SCB1 | 250.56 | 0.07477%
IS13INV3M2SCB2 | 250.56 | 0.07477%
IS13INV3M2SCB3 | 250.56 | 0.07477%
IS13INV3M2SCB4 | 250.56 | 0.07477%
IS13INV3M2SCB5 | 250.56 | 0.07477%
IS13INV3M2SCB6 | 250.56 | 0.07477%
IS13INV3M2SCB7 | 250.56 | 0.07477%
IS13INV3M2SCB8 | 250.56 | 0.07477%
IS13INV3M2SCB9 | 0 | 0%
IS13INV3M2SCB10 | 0 | 0%
IS13INV4M1SCB1 | 250.56 | 0.07477%
IS13INV4M1SCB2 | 250.56 | 0.07477%
IS13INV4M1SCB3 | 219.24 | 0.06543%
IS13INV4M1SCB4 | 250.56 | 0.07477%
IS13INV4M1SCB5 | 250.56 | 0.07477%
IS13INV4M1SCB6 | 250.56 | 0.07477%
IS13INV4M1SCB7 | 250.56 | 0.07477%
IS13INV4M1SCB8 | 250.56 | 0.07477%
IS13INV4M1SCB9 | 219.24 | 0.06543%
IS13INV4M1SCB10 | 0 | 0%
IS13INV4M2SCB1 | 250.56 | 0.07477%
IS13INV4M2SCB2 | 250.56 | 0.07477%
IS13INV4M2SCB3 | 250.56 | 0.07477%
IS13INV4M2SCB4 | 250.56 | 0.07477%
IS13INV4M2SCB5 | 250.56 | 0.07477%
IS13INV4M2SCB6 | 250.56 | 0.07477%
IS13INV4M2SCB7 | 250.56 | 0.07477%
IS13INV4M2SCB8 | 250.56 | 0.07477%
IS13INV4M2SCB9 | 0 | 0%
IS13INV4M2SCB10 | 0 | 0%
IS14INV1M1SCB1 | 250.56 | 0.07477%
IS14INV1M1SCB2 | 250.56 | 0.07477%
IS14INV1M1SCB3 | 250.56 | 0.07477%
IS14INV1M1SCB4 | 250.56 | 0.07477%
IS14INV1M1SCB5 | 250.56 | 0.07477%
IS14INV1M1SCB6 | 250.56 | 0.07477%
IS14INV1M1SCB7 | 250.56 | 0.07477%
IS14INV1M1SCB8 | 219.24 | 0.06543%
IS14INV1M1SCB9 | 250.56 | 0.07477%
IS14INV1M1SCB10 | 0 | 0%
IS14INV1M2SCB1 | 219.24 | 0.06543%
IS14INV1M2SCB2 | 219.24 | 0.06543%
IS14INV1M2SCB3 | 219.24 | 0.06543%
IS14INV1M2SCB4 | 250.56 | 0.07477%
IS14INV1M2SCB5 | 250.56 | 0.07477%
IS14INV1M2SCB6 | 250.56 | 0.07477%
IS14INV1M2SCB7 | 250.56 | 0.07477%
IS14INV1M2SCB8 | 250.56 | 0.07477%
IS14INV1M2SCB9 | 0 | 0%
IS14INV1M2SCB10 | 0 | 0%
IS14INV2M1SCB1 | 250.56 | 0.07477%
IS14INV2M1SCB2 | 250.56 | 0.07477%
IS14INV2M1SCB3 | 250.56 | 0.07477%
IS14INV2M1SCB4 | 250.56 | 0.07477%
IS14INV2M1SCB5 | 250.56 | 0.07477%
IS14INV2M1SCB6 | 250.56 | 0.07477%
IS14INV2M1SCB7 | 219.24 | 0.06543%
IS14INV2M1SCB8 | 250.56 | 0.07477%
IS14INV2M1SCB9 | 250.56 | 0.07477%
IS14INV2M1SCB10 | 0 | 0%
IS14INV2M2SCB1 | 250.56 | 0.07477%
IS14INV2M2SCB2 | 250.56 | 0.07477%
IS14INV2M2SCB3 | 250.56 | 0.07477%
IS14INV2M2SCB4 | 250.56 | 0.07477%
IS14INV2M2SCB5 | 250.56 | 0.07477%
IS14INV2M2SCB6 | 250.56 | 0.07477%
IS14INV2M2SCB7 | 250.56 | 0.07477%
IS14INV2M2SCB8 | 250.56 | 0.07477%
IS14INV2M2SCB9 | 0 | 0%
IS14INV2M2SCB10 | 0 | 0%
IS14INV3M1SCB1 | 250.56 | 0.07477%
IS14INV3M1SCB2 | 250.56 | 0.07477%
IS14INV3M1SCB3 | 250.56 | 0.07477%
IS14INV3M1SCB4 | 219.24 | 0.06543%
IS14INV3M1SCB5 | 250.56 | 0.07477%
IS14INV3M1SCB6 | 250.56 | 0.07477%
IS14INV3M1SCB7 | 250.56 | 0.07477%
IS14INV3M1SCB8 | 219.24 | 0.06543%
IS14INV3M1SCB9 | 250.56 | 0.07477%
IS14INV3M1SCB10 | 0 | 0%
IS14INV3M2SCB1 | 250.56 | 0.07477%
IS14INV3M2SCB2 | 250.56 | 0.07477%
IS14INV3M2SCB3 | 250.56 | 0.07477%
IS14INV3M2SCB4 | 250.56 | 0.07477%
IS14INV3M2SCB5 | 250.56 | 0.07477%
IS14INV3M2SCB6 | 250.56 | 0.07477%
IS14INV3M2SCB7 | 250.56 | 0.07477%
IS14INV3M2SCB8 | 250.56 | 0.07477%
IS14INV3M2SCB9 | 0 | 0%
IS14INV3M2SCB10 | 0 | 0%
IS14INV4M1SCB1 | 219.24 | 0.06543%
IS14INV4M1SCB2 | 250.56 | 0.07477%
IS14INV4M1SCB3 | 250.56 | 0.07477%
IS14INV4M1SCB4 | 250.56 | 0.07477%
IS14INV4M1SCB5 | 250.56 | 0.07477%
IS14INV4M1SCB6 | 250.56 | 0.07477%
IS14INV4M1SCB7 | 250.56 | 0.07477%
IS14INV4M1SCB8 | 219.24 | 0.06543%
IS14INV4M1SCB9 | 250.56 | 0.07477%
IS14INV4M1SCB10 | 0 | 0%
IS14INV4M2SCB1 | 250.56 | 0.07477%
IS14INV4M2SCB2 | 250.56 | 0.07477%
IS14INV4M2SCB3 | 250.56 | 0.07477%
IS14INV4M2SCB4 | 250.56 | 0.07477%
IS14INV4M2SCB5 | 250.56 | 0.07477%
IS14INV4M2SCB6 | 250.56 | 0.07477%
IS14INV4M2SCB7 | 250.56 | 0.07477%
IS14INV4M2SCB8 | 250.56 | 0.07477%
IS14INV4M2SCB9 | 0 | 0%
IS14INV4M2SCB10 | 0 | 0%
IS15INV1M1SCB1 | 250.56 | 0.07477%
IS15INV1M1SCB2 | 250.56 | 0.07477%
IS15INV1M1SCB3 | 250.56 | 0.07477%
IS15INV1M1SCB4 | 250.56 | 0.07477%
IS15INV1M1SCB5 | 250.56 | 0.07477%
IS15INV1M1SCB6 | 250.56 | 0.07477%
IS15INV1M1SCB7 | 250.56 | 0.07477%
IS15INV1M1SCB8 | 250.56 | 0.07477%
IS15INV1M1SCB9 | 0 | 0%
IS15INV1M1SCB10 | 0 | 0%
IS15INV1M2SCB1 | 250.56 | 0.07477%
IS15INV1M2SCB2 | 250.56 | 0.07477%
IS15INV1M2SCB3 | 250.56 | 0.07477%
IS15INV1M2SCB4 | 250.56 | 0.07477%
IS15INV1M2SCB5 | 219.24 | 0.06543%
IS15INV1M2SCB6 | 250.56 | 0.07477%
IS15INV1M2SCB7 | 219.24 | 0.06543%
IS15INV1M2SCB8 | 250.56 | 0.07477%
IS15INV1M2SCB9 | 250.56 | 0.07477%
IS15INV1M2SCB10 | 0 | 0%
IS15INV2M1SCB1 | 250.56 | 0.07477%
IS15INV2M1SCB2 | 250.56 | 0.07477%
IS15INV2M1SCB3 | 250.56 | 0.07477%
IS15INV2M1SCB4 | 250.56 | 0.07477%
IS15INV2M1SCB5 | 250.56 | 0.07477%
IS15INV2M1SCB6 | 250.56 | 0.07477%
IS15INV2M1SCB7 | 250.56 | 0.07477%
IS15INV2M1SCB8 | 250.56 | 0.07477%
IS15INV2M1SCB9 | 0 | 0%
IS15INV2M1SCB10 | 0 | 0%
IS15INV2M2SCB1 | 219.24 | 0.06543%
IS15INV2M2SCB2 | 250.56 | 0.07477%
IS15INV2M2SCB3 | 250.56 | 0.07477%
IS15INV2M2SCB4 | 250.56 | 0.07477%
IS15INV2M2SCB5 | 250.56 | 0.07477%
IS15INV2M2SCB6 | 250.56 | 0.07477%
IS15INV2M2SCB7 | 250.56 | 0.07477%
IS15INV2M2SCB8 | 219.24 | 0.06543%
IS15INV2M2SCB9 | 0 | 0%
IS15INV2M2SCB10 | 0 | 0%
IS15INV3M1SCB1 | 250.56 | 0.07477%
IS15INV3M1SCB2 | 250.56 | 0.07477%
IS15INV3M1SCB3 | 250.56 | 0.07477%
IS15INV3M1SCB4 | 250.56 | 0.07477%
IS15INV3M1SCB5 | 250.56 | 0.07477%
IS15INV3M1SCB6 | 250.56 | 0.07477%
IS15INV3M1SCB7 | 219.24 | 0.06543%
IS15INV3M1SCB8 | 250.56 | 0.07477%
IS15INV3M1SCB9 | 250.56 | 0.07477%
IS15INV3M1SCB10 | 0 | 0%
IS15INV3M2SCB1 | 219.24 | 0.06543%
IS15INV3M2SCB2 | 250.56 | 0.07477%
IS15INV3M2SCB3 | 250.56 | 0.07477%
IS15INV3M2SCB4 | 250.56 | 0.07477%
IS15INV3M2SCB5 | 250.56 | 0.07477%
IS15INV3M2SCB6 | 250.56 | 0.07477%
IS15INV3M2SCB7 | 250.56 | 0.07477%
IS15INV3M2SCB8 | 250.56 | 0.07477%
IS15INV3M2SCB9 | 219.24 | 0.06543%
IS15INV3M2SCB10 | 0 | 0%
IS15INV4M1SCB1 | 250.56 | 0.07477%
IS15INV4M1SCB2 | 219.24 | 0.06543%
IS15INV4M1SCB3 | 250.56 | 0.07477%
IS15INV4M1SCB4 | 250.56 | 0.07477%
IS15INV4M1SCB5 | 250.56 | 0.07477%
IS15INV4M1SCB6 | 250.56 | 0.07477%
IS15INV4M1SCB7 | 219.24 | 0.06543%
IS15INV4M1SCB8 | 250.56 | 0.07477%
IS15INV4M1SCB9 | 250.56 | 0.07477%
IS15INV4M1SCB10 | 0 | 0%
IS15INV4M2SCB1 | 250.56 | 0.07477%
IS15INV4M2SCB2 | 250.56 | 0.07477%
IS15INV4M2SCB3 | 250.56 | 0.07477%
IS15INV4M2SCB4 | 250.56 | 0.07477%
IS15INV4M2SCB5 | 250.56 | 0.07477%
IS15INV4M2SCB6 | 250.56 | 0.07477%
IS15INV4M2SCB7 | 250.56 | 0.07477%
IS15INV4M2SCB8 | 250.56 | 0.07477%
IS15INV4M2SCB9 | 0 | 0%
IS15INV4M2SCB10 | 0 | 0%
IS16INV1M1SCB1 | 250.56 | 0.07477%
IS16INV1M1SCB2 | 219.24 | 0.06543%
IS16INV1M1SCB3 | 250.56 | 0.07477%
IS16INV1M1SCB4 | 250.56 | 0.07477%
IS16INV1M1SCB5 | 250.56 | 0.07477%
IS16INV1M1SCB6 | 250.56 | 0.07477%
IS16INV1M1SCB7 | 250.56 | 0.07477%
IS16INV1M1SCB8 | 219.24 | 0.06543%
IS16INV1M1SCB9 | 250.56 | 0.07477%
IS16INV1M1SCB10 | 0 | 0%
IS16INV1M2SCB1 | 250.56 | 0.07477%
IS16INV1M2SCB2 | 250.56 | 0.07477%
IS16INV1M2SCB3 | 250.56 | 0.07477%
IS16INV1M2SCB4 | 250.56 | 0.07477%
IS16INV1M2SCB5 | 250.56 | 0.07477%
IS16INV1M2SCB6 | 250.56 | 0.07477%
IS16INV1M2SCB7 | 250.56 | 0.07477%
IS16INV1M2SCB8 | 250.56 | 0.07477%
IS16INV1M2SCB9 | 0 | 0%
IS16INV1M2SCB10 | 0 | 0%
IS16INV2M1SCB1 | 250.56 | 0.07477%
IS16INV2M1SCB2 | 250.56 | 0.07477%
IS16INV2M1SCB3 | 250.56 | 0.07477%
IS16INV2M1SCB4 | 250.56 | 0.07477%
IS16INV2M1SCB5 | 219.24 | 0.06543%
IS16INV2M1SCB6 | 187.92 | 0.05608%
IS16INV2M1SCB7 | 250.56 | 0.07477%
IS16INV2M1SCB8 | 250.56 | 0.07477%
IS16INV2M1SCB9 | 250.56 | 0.07477%
IS16INV2M1SCB10 | 0 | 0%
IS16INV2M2SCB1 | 250.56 | 0.07477%
IS16INV2M2SCB2 | 250.56 | 0.07477%
IS16INV2M2SCB3 | 250.56 | 0.07477%
IS16INV2M2SCB4 | 250.56 | 0.07477%
IS16INV2M2SCB5 | 250.56 | 0.07477%
IS16INV2M2SCB6 | 250.56 | 0.07477%
IS16INV2M2SCB7 | 250.56 | 0.07477%
IS16INV2M2SCB8 | 250.56 | 0.07477%
IS16INV2M2SCB9 | 0 | 0%
IS16INV2M2SCB10 | 0 | 0%
IS16INV3M1SCB1 | 219.24 | 0.06543%
IS16INV3M1SCB2 | 219.24 | 0.06543%
IS16INV3M1SCB3 | 250.56 | 0.07477%
IS16INV3M1SCB4 | 250.56 | 0.07477%
IS16INV3M1SCB5 | 250.56 | 0.07477%
IS16INV3M1SCB6 | 250.56 | 0.07477%
IS16INV3M1SCB7 | 250.56 | 0.07477%
IS16INV3M1SCB8 | 250.56 | 0.07477%
IS16INV3M1SCB9 | 187.92 | 0.05608%
IS16INV3M1SCB10 | 0 | 0%
IS16INV3M2SCB1 | 219.24 | 0.06543%
IS16INV3M2SCB2 | 219.24 | 0.06543%
IS16INV3M2SCB3 | 219.24 | 0.06543%
IS16INV3M2SCB4 | 219.24 | 0.06543%
IS16INV3M2SCB5 | 250.56 | 0.07477%
IS16INV3M2SCB6 | 250.56 | 0.07477%
IS16INV3M2SCB7 | 250.56 | 0.07477%
IS16INV3M2SCB8 | 250.56 | 0.07477%
IS16INV3M2SCB9 | 0 | 0%
IS16INV3M2SCB10 | 0 | 0%
IS16INV4M1SCB1 | 219.24 | 0.06543%
IS16INV4M1SCB2 | 250.56 | 0.07477%
IS16INV4M1SCB3 | 187.92 | 0.05608%
IS16INV4M1SCB4 | 219.24 | 0.06543%
IS16INV4M1SCB5 | 250.56 | 0.07477%
IS16INV4M1SCB6 | 250.56 | 0.07477%
IS16INV4M1SCB7 | 250.56 | 0.07477%
IS16INV4M1SCB8 | 250.56 | 0.07477%
IS16INV4M1SCB9 | 250.56 | 0.07477%
IS16INV4M1SCB10 | 0 | 0%
IS16INV4M2SCB1 | 219.24 | 0.06543%
IS16INV4M2SCB2 | 250.56 | 0.07477%
IS16INV4M2SCB3 | 250.56 | 0.07477%
IS16INV4M2SCB4 | 250.56 | 0.07477%
IS16INV4M2SCB5 | 250.56 | 0.07477%
IS16INV4M2SCB6 | 250.56 | 0.07477%
IS16INV4M2SCB7 | 250.56 | 0.07477%
IS16INV4M2SCB8 | 250.56 | 0.07477%
IS16INV4M2SCB9 | 0 | 0%
IS16INV4M2SCB10 | 0 | 0%
IS17INV1M1SCB1 | 250.56 | 0.07477%
IS17INV1M1SCB2 | 250.56 | 0.07477%
IS17INV1M1SCB3 | 250.56 | 0.07477%
IS17INV1M1SCB4 | 250.56 | 0.07477%
IS17INV1M1SCB5 | 250.56 | 0.07477%
IS17INV1M1SCB6 | 250.56 | 0.07477%
IS17INV1M1SCB7 | 250.56 | 0.07477%
IS17INV1M1SCB8 | 219.24 | 0.06543%
IS17INV1M1SCB9 | 0 | 0%
IS17INV1M1SCB10 | 0 | 0%
IS17INV1M2SCB1 | 250.56 | 0.07477%
IS17INV1M2SCB2 | 250.56 | 0.07477%
IS17INV1M2SCB3 | 250.56 | 0.07477%
IS17INV1M2SCB4 | 250.56 | 0.07477%
IS17INV1M2SCB5 | 250.56 | 0.07477%
IS17INV1M2SCB6 | 250.56 | 0.07477%
IS17INV1M2SCB7 | 250.56 | 0.07477%
IS17INV1M2SCB8 | 250.56 | 0.07477%
IS17INV1M2SCB9 | 0 | 0%
IS17INV1M2SCB10 | 0 | 0%
IS17INV2M1SCB1 | 250.56 | 0.07477%
IS17INV2M1SCB2 | 250.56 | 0.07477%
IS17INV2M1SCB3 | 250.56 | 0.07477%
IS17INV2M1SCB4 | 250.56 | 0.07477%
IS17INV2M1SCB5 | 250.56 | 0.07477%
IS17INV2M1SCB6 | 250.56 | 0.07477%
IS17INV2M1SCB7 | 250.56 | 0.07477%
IS17INV2M1SCB8 | 250.56 | 0.07477%
IS17INV2M1SCB9 | 0 | 0%
IS17INV2M1SCB10 | 0 | 0%
IS17INV2M2SCB1 | 250.56 | 0.07477%
IS17INV2M2SCB2 | 250.56 | 0.07477%
IS17INV2M2SCB3 | 250.56 | 0.07477%
IS17INV2M2SCB4 | 250.56 | 0.07477%
IS17INV2M2SCB5 | 250.56 | 0.07477%
IS17INV2M2SCB6 | 250.56 | 0.07477%
IS17INV2M2SCB7 | 250.56 | 0.07477%
IS17INV2M2SCB8 | 0 | 0%
IS17INV2M2SCB9 | 0 | 0%
IS17INV2M2SCB10 | 0 | 0%
IS17INV3M1SCB1 | 250.56 | 0.07477%
IS17INV3M1SCB2 | 250.56 | 0.07477%
IS17INV3M1SCB3 | 250.56 | 0.07477%
IS17INV3M1SCB4 | 219.24 | 0.06543%
IS17INV3M1SCB5 | 250.56 | 0.07477%
IS17INV3M1SCB6 | 250.56 | 0.07477%
IS17INV3M1SCB7 | 234.9 | 0.0701%
IS17INV3M1SCB8 | 250.56 | 0.07477%
IS17INV3M1SCB9 | 0 | 0%
IS17INV3M1SCB10 | 0 | 0%
IS17INV3M2SCB1 | 250.56 | 0.07477%
IS17INV3M2SCB2 | 250.56 | 0.07477%
IS17INV3M2SCB3 | 250.56 | 0.07477%
IS17INV3M2SCB4 | 250.56 | 0.07477%
IS17INV3M2SCB5 | 250.56 | 0.07477%
IS17INV3M2SCB6 | 250.56 | 0.07477%
IS17INV3M2SCB7 | 250.56 | 0.07477%
IS17INV3M2SCB8 | 0 | 0%
IS17INV3M2SCB9 | 0 | 0%
IS17INV3M2SCB10 | 0 | 0%
IS17INV4M1SCB1 | 250.56 | 0.07477%
IS17INV4M1SCB2 | 250.56 | 0.07477%
IS17INV4M1SCB3 | 250.56 | 0.07477%
IS17INV4M1SCB4 | 250.56 | 0.07477%
IS17INV4M1SCB5 | 250.56 | 0.07477%
IS17INV4M1SCB6 | 250.56 | 0.07477%
IS17INV4M1SCB7 | 250.56 | 0.07477%
IS17INV4M1SCB8 | 250.56 | 0.07477%
IS17INV4M1SCB9 | 0 | 0%
IS17INV4M1SCB10 | 0 | 0%
IS17INV4M2SCB1 | 250.56 | 0.07477%
IS17INV4M2SCB2 | 250.56 | 0.07477%
IS17INV4M2SCB3 | 250.56 | 0.07477%
IS17INV4M2SCB4 | 250.56 | 0.07477%
IS17INV4M2SCB5 | 250.56 | 0.07477%
IS17INV4M2SCB6 | 250.56 | 0.07477%
IS17INV4M2SCB7 | 250.56 | 0.07477%
IS17INV4M2SCB8 | 250.56 | 0.07477%
IS17INV4M2SCB9 | 0 | 0%
IS17INV4M2SCB10 | 0 | 0%
IS18INV1M1SCB1 | 250.56 | 0.07477%
IS18INV1M1SCB2 | 250.56 | 0.07477%
IS18INV1M1SCB3 | 250.56 | 0.07477%
IS18INV1M1SCB4 | 250.56 | 0.07477%
IS18INV1M1SCB5 | 250.56 | 0.07477%
IS18INV1M1SCB6 | 250.56 | 0.07477%
IS18INV1M1SCB7 | 250.56 | 0.07477%
IS18INV1M1SCB8 | 250.56 | 0.07477%
IS18INV1M1SCB9 | 250.56 | 0.07477%
IS18INV1M1SCB10 | 0 | 0%
IS18INV1M2SCB1 | 250.56 | 0.07477%
IS18INV1M2SCB2 | 250.56 | 0.07477%
IS18INV1M2SCB3 | 219.24 | 0.06543%
IS18INV1M2SCB4 | 250.56 | 0.07477%
IS18INV1M2SCB5 | 250.56 | 0.07477%
IS18INV1M2SCB6 | 250.56 | 0.07477%
IS18INV1M2SCB7 | 250.56 | 0.07477%
IS18INV1M2SCB8 | 250.56 | 0.07477%
IS18INV1M2SCB9 | 0 | 0%
IS18INV1M2SCB10 | 0 | 0%
IS18INV2M1SCB1 | 250.56 | 0.07477%
IS18INV2M1SCB2 | 250.56 | 0.07477%
IS18INV2M1SCB3 | 250.56 | 0.07477%
IS18INV2M1SCB4 | 250.56 | 0.07477%
IS18INV2M1SCB5 | 250.56 | 0.07477%
IS18INV2M1SCB6 | 250.56 | 0.07477%
IS18INV2M1SCB7 | 250.56 | 0.07477%
IS18INV2M1SCB8 | 250.56 | 0.07477%
IS18INV2M1SCB9 | 250.56 | 0.07477%
IS18INV2M1SCB10 | 0 | 0%
IS18INV2M2SCB1 | 250.56 | 0.07477%
IS18INV2M2SCB2 | 250.56 | 0.07477%
IS18INV2M2SCB3 | 250.56 | 0.07477%
IS18INV2M2SCB4 | 250.56 | 0.07477%
IS18INV2M2SCB5 | 250.56 | 0.07477%
IS18INV2M2SCB6 | 250.56 | 0.07477%
IS18INV2M2SCB7 | 250.56 | 0.07477%
IS18INV2M2SCB8 | 219.24 | 0.06543%
IS18INV2M2SCB9 | 0 | 0%
IS18INV2M2SCB10 | 0 | 0%
IS18INV3M1SCB1 | 250.56 | 0.07477%
IS18INV3M1SCB2 | 250.56 | 0.07477%
IS18INV3M1SCB3 | 250.56 | 0.07477%
IS18INV3M1SCB4 | 250.56 | 0.07477%
IS18INV3M1SCB5 | 250.56 | 0.07477%
IS18INV3M1SCB6 | 250.56 | 0.07477%
IS18INV3M1SCB7 | 250.56 | 0.07477%
IS18INV3M1SCB8 | 219.24 | 0.06543%
IS18INV3M1SCB9 | 250.56 | 0.07477%
IS18INV3M1SCB10 | 0 | 0%
IS18INV3M2SCB1 | 250.56 | 0.07477%
IS18INV3M2SCB2 | 250.56 | 0.07477%
IS18INV3M2SCB3 | 250.56 | 0.07477%
IS18INV3M2SCB4 | 250.56 | 0.07477%
IS18INV3M2SCB5 | 250.56 | 0.07477%
IS18INV3M2SCB6 | 250.56 | 0.07477%
IS18INV3M2SCB7 | 250.56 | 0.07477%
IS18INV3M2SCB8 | 219.24 | 0.06543%
IS18INV3M2SCB9 | 0 | 0%
IS18INV3M2SCB10 | 0 | 0%
IS18INV4M1SCB1 | 0 | 0%
IS18INV4M1SCB2 | 250.56 | 0.07477%
IS18INV4M1SCB3 | 250.56 | 0.07477%
IS18INV4M1SCB4 | 250.56 | 0.07477%
IS18INV4M1SCB5 | 250.56 | 0.07477%
IS18INV4M1SCB6 | 250.56 | 0.07477%
IS18INV4M1SCB7 | 250.56 | 0.07477%
IS18INV4M1SCB8 | 250.56 | 0.07477%
IS18INV4M1SCB9 | 250.56 | 0.07477%
IS18INV4M1SCB10 | 0 | 0%
IS18INV4M2SCB1 | 250.56 | 0.07477%
IS18INV4M2SCB2 | 250.56 | 0.07477%
IS18INV4M2SCB3 | 250.56 | 0.07477%
IS18INV4M2SCB4 | 250.56 | 0.07477%
IS18INV4M2SCB5 | 250.56 | 0.07477%
IS18INV4M2SCB6 | 250.56 | 0.07477%
IS18INV4M2SCB7 | 250.56 | 0.07477%
IS18INV4M2SCB8 | 250.56 | 0.07477%
IS18INV4M2SCB9 | 0 | 0%
IS18INV4M2SCB10 | 0 | 0%
IS19INV1M1SCB1 | 219.24 | 0.06543%
IS19INV1M1SCB2 | 250.56 | 0.07477%
IS19INV1M1SCB3 | 250.56 | 0.07477%
IS19INV1M1SCB4 | 250.56 | 0.07477%
IS19INV1M1SCB5 | 219.24 | 0.06543%
IS19INV1M1SCB6 | 250.56 | 0.07477%
IS19INV1M1SCB7 | 219.24 | 0.06543%
IS19INV1M1SCB8 | 250.56 | 0.07477%
IS19INV1M1SCB9 | 250.56 | 0.07477%
IS19INV1M1SCB10 | 0 | 0%
IS19INV1M2SCB1 | 250.56 | 0.07477%
IS19INV1M2SCB2 | 250.56 | 0.07477%
IS19INV1M2SCB3 | 250.56 | 0.07477%
IS19INV1M2SCB4 | 250.56 | 0.07477%
IS19INV1M2SCB5 | 250.56 | 0.07477%
IS19INV1M2SCB6 | 250.56 | 0.07477%
IS19INV1M2SCB7 | 250.56 | 0.07477%
IS19INV1M2SCB8 | 250.56 | 0.07477%
IS19INV1M2SCB9 | 250.56 | 0.07477%
IS19INV1M2SCB10 | 0 | 0%
IS19INV2M1SCB1 | 250.56 | 0.07477%
IS19INV2M1SCB2 | 219.24 | 0.06543%
IS19INV2M1SCB3 | 250.56 | 0.07477%
IS19INV2M1SCB4 | 250.56 | 0.07477%
IS19INV2M1SCB5 | 250.56 | 0.07477%
IS19INV2M1SCB6 | 250.56 | 0.07477%
IS19INV2M1SCB7 | 250.56 | 0.07477%
IS19INV2M1SCB8 | 250.56 | 0.07477%
IS19INV2M1SCB9 | 250.56 | 0.07477%
IS19INV2M1SCB10 | 0 | 0%
IS19INV2M2SCB1 | 250.56 | 0.07477%
IS19INV2M2SCB2 | 250.56 | 0.07477%
IS19INV2M2SCB3 | 250.56 | 0.07477%
IS19INV2M2SCB4 | 250.56 | 0.07477%
IS19INV2M2SCB5 | 250.56 | 0.07477%
IS19INV2M2SCB6 | 250.56 | 0.07477%
IS19INV2M2SCB7 | 250.56 | 0.07477%
IS19INV2M2SCB8 | 250.56 | 0.07477%
IS19INV2M2SCB9 | 219.24 | 0.06543%
IS19INV2M2SCB10 | 0 | 0%
IS19INV3M1SCB1 | 250.56 | 0.07477%
IS19INV3M1SCB2 | 250.56 | 0.07477%
IS19INV3M1SCB3 | 250.56 | 0.07477%
IS19INV3M1SCB4 | 219.24 | 0.06543%
IS19INV3M1SCB5 | 250.56 | 0.07477%
IS19INV3M1SCB6 | 250.56 | 0.07477%
IS19INV3M1SCB7 | 250.56 | 0.07477%
IS19INV3M1SCB8 | 250.56 | 0.07477%
IS19INV3M1SCB9 | 250.56 | 0.07477%
IS19INV3M1SCB10 | 0 | 0%
IS19INV3M2SCB1 | 250.56 | 0.07477%
IS19INV3M2SCB2 | 250.56 | 0.07477%
IS19INV3M2SCB3 | 250.56 | 0.07477%
IS19INV3M2SCB4 | 250.56 | 0.07477%
IS19INV3M2SCB5 | 250.56 | 0.07477%
IS19INV3M2SCB6 | 250.56 | 0.07477%
IS19INV3M2SCB7 | 250.56 | 0.07477%
IS19INV3M2SCB8 | 250.56 | 0.07477%
IS19INV3M2SCB9 | 250.56 | 0.07477%
IS19INV3M2SCB10 | 0 | 0%
IS19INV4M1SCB1 | 250.56 | 0.07477%
IS19INV4M1SCB2 | 250.56 | 0.07477%
IS19INV4M1SCB3 | 250.56 | 0.07477%
IS19INV4M1SCB4 | 250.56 | 0.07477%
IS19INV4M1SCB5 | 250.56 | 0.07477%
IS19INV4M1SCB6 | 250.56 | 0.07477%
IS19INV4M1SCB7 | 250.56 | 0.07477%
IS19INV4M1SCB8 | 250.56 | 0.07477%
IS19INV4M1SCB9 | 0 | 0%
IS19INV4M1SCB10 | 0 | 0%
IS19INV4M2SCB1 | 219.24 | 0.06543%
IS19INV4M2SCB2 | 250.56 | 0.07477%
IS19INV4M2SCB3 | 250.56 | 0.07477%
IS19INV4M2SCB4 | 250.56 | 0.07477%
IS19INV4M2SCB5 | 250.56 | 0.07477%
IS19INV4M2SCB6 | 250.56 | 0.07477%
IS19INV4M2SCB7 | 250.56 | 0.07477%
IS19INV4M2SCB8 | 250.56 | 0.07477%
IS19INV4M2SCB9 | 250.56 | 0.07477%
IS19INV4M2SCB10 | 0 | 0%
IS20INV1M1SCB1 | 250.56 | 0.07477%
IS20INV1M1SCB2 | 250.56 | 0.07477%
IS20INV1M1SCB3 | 250.56 | 0.07477%
IS20INV1M1SCB4 | 250.56 | 0.07477%
IS20INV1M1SCB5 | 250.56 | 0.07477%
IS20INV1M1SCB6 | 250.56 | 0.07477%
IS20INV1M1SCB7 | 250.56 | 0.07477%
IS20INV1M1SCB8 | 250.56 | 0.07477%
IS20INV1M1SCB9 | 250.56 | 0.07477%
IS20INV1M1SCB10 | 0 | 0%
IS20INV1M2SCB1 | 250.56 | 0.07477%
IS20INV1M2SCB2 | 250.56 | 0.07477%
IS20INV1M2SCB3 | 250.56 | 0.07477%
IS20INV1M2SCB4 | 250.56 | 0.07477%
IS20INV1M2SCB5 | 250.56 | 0.07477%
IS20INV1M2SCB6 | 250.56 | 0.07477%
IS20INV1M2SCB7 | 250.56 | 0.07477%
IS20INV1M2SCB8 | 250.56 | 0.07477%
IS20INV1M2SCB9 | 250.56 | 0.07477%
IS20INV1M2SCB10 | 0 | 0%
IS20INV2M1SCB1 | 250.56 | 0.07477%
IS20INV2M1SCB2 | 250.56 | 0.07477%
IS20INV2M1SCB3 | 250.56 | 0.07477%
IS20INV2M1SCB4 | 250.56 | 0.07477%
IS20INV2M1SCB5 | 250.56 | 0.07477%
IS20INV2M1SCB6 | 250.56 | 0.07477%
IS20INV2M1SCB7 | 250.56 | 0.07477%
IS20INV2M1SCB8 | 250.56 | 0.07477%
IS20INV2M1SCB9 | 250.56 | 0.07477%
IS20INV2M1SCB10 | 0 | 0%
IS20INV2M2SCB1 | 250.56 | 0.07477%
IS20INV2M2SCB2 | 250.56 | 0.07477%
IS20INV2M2SCB3 | 250.56 | 0.07477%
IS20INV2M2SCB4 | 250.56 | 0.07477%
IS20INV2M2SCB5 | 250.56 | 0.07477%
IS20INV2M2SCB6 | 250.56 | 0.07477%
IS20INV2M2SCB7 | 250.56 | 0.07477%
IS20INV2M2SCB8 | 250.56 | 0.07477%
IS20INV2M2SCB9 | 250.56 | 0.07477%
IS20INV2M2SCB10 | 0 | 0%
IS20INV3M1SCB1 | 250.56 | 0.07477%
IS20INV3M1SCB2 | 250.56 | 0.07477%
IS20INV3M1SCB3 | 250.56 | 0.07477%
IS20INV3M1SCB4 | 250.56 | 0.07477%
IS20INV3M1SCB5 | 250.56 | 0.07477%
IS20INV3M1SCB6 | 250.56 | 0.07477%
IS20INV3M1SCB7 | 250.56 | 0.07477%
IS20INV3M1SCB8 | 250.56 | 0.07477%
IS20INV3M1SCB9 | 250.56 | 0.07477%
IS20INV3M1SCB10 | 0 | 0%
IS20INV3M2SCB1 | 250.56 | 0.07477%
IS20INV3M2SCB2 | 250.56 | 0.07477%
IS20INV3M2SCB3 | 250.56 | 0.07477%
IS20INV3M2SCB4 | 250.56 | 0.07477%
IS20INV3M2SCB5 | 250.56 | 0.07477%
IS20INV3M2SCB6 | 250.56 | 0.07477%
IS20INV3M2SCB7 | 250.56 | 0.07477%
IS20INV3M2SCB8 | 250.56 | 0.07477%
IS20INV3M2SCB9 | 0 | 0%
IS20INV3M2SCB10 | 0 | 0%
IS20INV4M1SCB1 | 250.56 | 0.07477%
IS20INV4M1SCB2 | 250.56 | 0.07477%
IS20INV4M1SCB3 | 250.56 | 0.07477%
IS20INV4M1SCB4 | 250.56 | 0.07477%
IS20INV4M1SCB5 | 250.56 | 0.07477%
IS20INV4M1SCB6 | 250.56 | 0.07477%
IS20INV4M1SCB7 | 250.56 | 0.07477%
IS20INV4M1SCB8 | 250.56 | 0.07477%
IS20INV4M1SCB9 | 250.56 | 0.07477%
IS20INV4M1SCB10 | 0 | 0%
IS20INV4M2SCB1 | 250.56 | 0.07477%
IS20INV4M2SCB2 | 250.56 | 0.07477%
IS20INV4M2SCB3 | 250.56 | 0.07477%
IS20INV4M2SCB4 | 250.56 | 0.07477%
IS20INV4M2SCB5 | 250.56 | 0.07477%
IS20INV4M2SCB6 | 250.56 | 0.07477%
IS20INV4M2SCB7 | 250.56 | 0.07477%
IS20INV4M2SCB8 | 250.56 | 0.07477%
IS20INV4M2SCB9 | 0 | 0%
IS20INV4M2SCB10 | 0 | 0%
IS1Tx | 16789.405 | 5.01%
IS2Tx | 16699.07 | 4.983%
IS3Tx | 16766.64 | 5.004%
IS4Tx | 16547.4 | 4.938%
IS5Tx | 16724.88 | 4.991%
IS6Tx | 17170.9 | 5.124%
IS7Tx | 16443 | 4.907%
IS8Tx | 16928.46 | 5.052%
IS9Tx | 16942.96 | 5.056%
IS10Tx | 16756.2 | 5%
IS11Tx | 16595.25 | 4.952%
IS12Tx | 16912.8 | 5.047%
IS13Tx | 16599.6 | 4.954%
IS14Tx | 16756.2 | 5%
IS15Tx | 16756.2 | 5%
IS16Tx | 16474.32 | 4.916%
IS17Tx | 15456.42 | 4.613%
IS18Tx | 16662.24 | 4.972%
IS19Tx | 17570.52 | 5.244%
IS20Tx | 17539.2 | 5.234%
IS1MVP | 16789.405 | 5.01%
IS2MVP | 16699.07 | 4.983%
IS3MVP | 16766.64 | 5.004%
IS4MVP | 16547.4 | 4.938%
IS5MVP | 16724.88 | 4.991%
IS6MVP | 17170.9 | 5.124%
IS7MVP | 16443 | 4.907%
IS8MVP | 16928.46 | 5.052%
IS9MVP | 16942.96 | 5.056%
IS10MVP | 16756.2 | 5%
IS11MVP | 16595.25 | 4.952%
IS12MVP | 16912.8 | 5.047%
IS13MVP | 16599.6 | 4.954%
IS14MVP | 16756.2 | 5%
IS15MVP | 16756.2 | 5%
IS16MVP | 16474.32 | 4.916%
IS17MVP | 15456.42 | 4.613%
IS18MVP | 16662.24 | 4.972%
IS19MVP | 17570.52 | 5.244%
IS20MVP | 17539.2 | 5.234%
IS1AuxTx | 16789.405 | 5.01%
IS2AuxTx | 16699.07 | 4.983%
IS3AuxTx | 16766.64 | 5.004%
IS4AuxTx | 16547.4 | 4.938%
IS5AuxTx | 16724.88 | 4.991%
IS6AuxTx | 17170.9 | 5.124%
IS7AuxTx | 16443 | 4.907%
IS8AuxTx | 16928.46 | 5.052%
IS9AuxTx | 16942.96 | 5.056%
IS10AuxTx | 16756.2 | 5%
IS11AuxTx | 16595.25 | 4.952%
IS12AuxTx | 16912.8 | 5.047%
IS13AuxTx | 16599.6 | 4.954%
IS14AuxTx | 16756.2 | 5%
IS15AuxTx | 16756.2 | 5%
IS16AuxTx | 16474.32 | 4.916%
IS17AuxTx | 15456.42 | 4.613%
IS18AuxTx | 16662.24 | 4.972%
IS19AuxTx | 17570.52 | 5.244%
IS20AuxTx | 17539.2 | 5.234%
MCR_MVP_Inc1 | 35109.72 | 10.48% | Incomer | Incomer 12 | Incomer 11 | Incomer 10 | Incomer 8 | Incomer 9 | Incomer 5 |  |  | Incomer 4 | Incomer 3 | Incomer 2 | Incomer 1
MCR_MVP_Inc2 | 32118.66 | 9.585% | DC Capacity (kwh) | 33307.805 | 33236.03 | 33870.55 | 33293.16 | 33667.26 | 33491.665 |  |  | 33340.14 | 33199.2 | 32103 | 35001.72
MCR_MVP_Inc3 | 33230.52 | 9.917% | Block | IR1-IR2 | IR3-IR4 | IR5-IR6 | IR8-IR7 | IR9-IR10 | IR12-IR11 |  |  | IR13-IR14 | IR15-IR16 | IR17-IR18 | IR19-IR20
MCR_MVP_Inc4 | 33355.8 | 9.954% | Full Load current | 613.4057 | 612.0839 | 623.7694 | 613.136 | 620.0256 | 616.7918 |  |  | 614.0012 | 611.4056 | 591.2177 | 644.6014
MCR_MVP_Inc5 | 33508.05 | 10%
MCR_MVP_Inc8 | 33371.46 | 9.959% | MCR_MVP_Inc1 | 35109.72 | Block | Full Load current
MCR_MVP_Inc9 | 33699.16 | 10.06% | MCR_MVP_Inc10 | 33895.78 | IR1-IR2 | 613.4057
MCR_MVP_Inc10 | 33895.78 | 10.12% | MCR_MVP_Inc11 | 33314.04 | IR3-IR4 | 612.0839
MCR_MVP_Inc11 | 33314.04 | 9.942% | MCR_MVP_Inc12 | 33488.475 | IR5-IR6 | 623.7694
MCR_MVP_Inc12 | 33488.475 | 9.994% | MCR_MVP_Inc2 | 32118.66 | IR8-IR7 | 613.136
MCR_MVP_OG1 | 167322.75 | 49.93% | MCR_MVP_Inc3 | 33230.52 | IR9-IR10 | 620.0256
MCR_MVP_OG2 | 167768.915 | 50.07% | MCR_MVP_Inc4 | 33355.8 | IR12-IR11 | 616.7918
Power_Tx1 | 167322.75 | 49.93% | MCR_MVP_Inc5 | 33508.05 | IR13-IR14 | 614.0012
Power_Tx2 | 167768.915 | 50.07% | MCR_MVP_Inc8 | 33371.46 | IR15-IR16 | 611.4056
Line_Bay1 | 335091.665 | 100% | MCR_MVP_Inc9 | 33699.16 | IR17-IR18 | 591.2177
Str_Typ1(445*29) | 12.905 | 0.003851% |  |  | IR19-IR20 | 644.6014
Str_Typ2 (450*29) | 13.05 | 0.003894%
Str_Typ3(535*29) | 15.515 | 0.00463%
Str_Typ4(540*29) | 15.66 | 0.004673%
Str_Typ5(545*29) | 15.805 | 0.004717%
Str_Typ6(445*58) | 25.81 | 0.007702%
Str_Typ7(450*58) | 26.1 | 0.007789%
Str_Typ8(535*58) | 31.03 | 0.00926%
Str_Typ9(540*58) | 31.32 | 0.009347%
Str_Typ10(545*58) | 31.61 | 0.009433%

## Inv_SY_B
| 2013.18 | 2090.61 | 2090.61 | 2077.705 | 2090.61 | 2090.61 | 2090.61 | 2193.85 | 2090.61 | 2116.42 | 2286.025 | 2090.61 | 2286.025 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2111.49 | 2114.1 | 2061.9 | 2088 | 2088 | 1853.1 | 2111.49 | 2114.1 | 2114.1 | 2088 | 2061.9 | 2114.1 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2090.61 | 2234.16 | 2238.72 | 2203.13 | 2239.29 | 2350.68 | 2442.96 | 2223.49 | 2234.16 | 2210.16 | 2209.74 | 2145.42 | 2004.48 | 2223.72 | 2181.72 | 2223.72 | 2225.96 | 1973.16 | 2270.84 | 1973.16 | 2239.52 | 2223.72 | 1973.16 | 2192.4 | 2088 | 2102.065 | 1991.43 | 2102.065 | 2212.7 | 2275.33 | 2023.04 | 2244.31 | 1959.82 | 2161.08 | 2129.76 | 1973.16 | 2239.38 | 1941.84 | 2255.04 | 1973.16 | 2223.72 | 2023.04 | 2196.595 | 2054.65 | 2275.92 | 2023.04 | 2181.09 | 2023.04 | 1785.965 | 2192.4 | 2129.76 | 1941.84 | 2255.04 | 2192.4 | 2004.48 | 2004.48 | 2208.06 | 1957.5 | 2035.8 | 2239.38 | 1941.84 | 2255.04 | 1941.84 | 2192.4 | 2004.48 | 2223.72 | 1910.52 | 2223.72 | 2004.48 | 2192.4 | 2004.48 | 2192.4 | 2004.48 | 1973.15 | 2192.4 | 2004.48 | 1941.84 | 2208.06 | 2223.72 | 2192.4 | 2004.48 | 2223.72 | 1973.16 | 2129.76 | 1973.16 | 2098.44 | 1847.88 | 2161.08 | 1973.16 | 2004.48 | 2004.48 | 1988.82 | 1722.6 | 1973.16 | 1753.92 | 2004.48 | 2004.48 | 2255.04 | 1941.84 | 2255.04 | 1973.16 | 2223.72 | 1973.16 | 2004.48 | 2004.48 | 2161.08 | 2255.04 | 2223.72 | 2223.72 | 2223.72 | 2255.04 | 2004.48 | 2223.72 | 2239.38 | 2255.04 | 2255.04 | 2255.04 | 2255.04 | 2004.48 | 2255.04 | 2004.48 | 337338.845
| 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 268
Date | IS1_INV1_M1 | IS1_INV1_M2 | IS1_INV2_M1 | IS1_INV2_M2 | IS1_INV3_M1 | IS1_INV3_M2 | IS1_INV4_M1 | IS1_INV4_M2 | IS2_INV1_M1 | IS2_INV1_M2 | IS2_INV2_M1 | IS2_INV2_M2 | IS2_INV3_M1 | IS2_INV3_M2 | IS2_INV4_M1 | IS2_INV4_M2 | IS3_INV1_M1 | IS3_INV1_M2 | IS3_INV2_M1 | IS3_INV2_M2 | IS3_INV3_M1 | IS3_INV3_M2 | IS3_INV4_M1 | IS3_INV4_M2 | IS4_INV1_M1 | IS4_INV1_M2 | IS4_INV2_M1 | IS4_INV2_M2 | IS4_INV3_M1 | IS4_INV3_M2 | IS4_INV4_M1 | IS4_INV4_M2 | IS5_INV1_M1 | IS5_INV1_M2 | IS5_INV2_M1 | IS5_INV2_M2 | IS5_INV3_M1 | IS5_INV3_M2 | IS5_INV4_M1 | IS5_INV4_M2 | IS6_INV1_M1 | IS6_INV1_M2 | IS6_INV2_M1 | IS6_INV2_M2 | IS6_INV3_M1 | IS6_INV3_M2 | IS6_INV4_M1 | IS6_INV4_M2 | IS7_INV1_M1 | IS7_INV1_M2 | IS7_INV2_M1 | IS7_INV2_M2 | IS7_INV3_M1 | IS7_INV3_M2 | IS7_INV4_M1 | IS7_INV4_M2 | IS8_INV1_M1 | IS8_INV1_M2 | IS8_INV2_M1 | IS8_INV2_M2 | IS8_INV3_M1 | IS8_INV3_M2 | IS8_INV4_M1 | IS8_INV4_M2 | IS9_INV1_M1 | IS9_INV1_M2 | IS9_INV2_M1 | IS9_INV2_M2 | IS9_INV3_M1 | IS9_INV3_M2 | IS9_INV4_M1 | IS9_INV4_M2 | IS10_INV1_M1 | IS10_INV1_M2 | IS10_INV2_M1 | IS10_INV2_M2 | IS10_INV3_M1 | IS10_INV3_M2 | IS10_INV4_M1 | IS10_INV4_M2 | IS11_INV1_M1 | IS11_INV1_M2 | IS11_INV2_M1 | IS11_INV2_M2 | IS11_INV3_M1 | IS11_INV3_M2 | IS11_INV4_M1 | IS11_INV4_M2 | IS12_INV1_M1 | IS12_INV1_M2 | IS12_INV2_M1 | IS12_INV2_M2 | IS12_INV3_M1 | IS12_INV3_M2 | IS12_INV4_M1 | IS12_INV4_M2 | IS13_INV1_M1 | IS13_INV1_M2 | IS13_INV2_M1 | IS13_INV2_M2 | IS13_INV3_M1 | IS13_INV3_M2 | IS13_INV4_M1 | IS13_INV4_M2 | IS14_INV1_M1 | IS14_INV1_M2 | IS14_INV2_M1 | IS14_INV2_M2 | IS14_INV3_M1 | IS14_INV3_M2 | IS14_INV4_M1 | IS14_INV4_M2 | IS15_INV1_M1 | IS15_INV1_M2 | IS15_INV2_M1 | IS15_INV2_M2 | IS15_INV3_M1 | IS15_INV3_M2 | IS15_INV4_M1 | IS15_INV4_M2 | IS16_INV1_M1 | IS16_INV1_M2 | IS16_INV2_M1 | IS16_INV2_M2 | IS16_INV3_M1 | IS16_INV3_M2 | IS16_INV4_M1 | IS16_INV4_M2 | IS17_INV1_M1 | IS17_INV1_M2 | IS17_INV2_M1 | IS17_INV2_M2 | IS17_INV3_M1 | IS17_INV3_M2 | IS17_INV4_M1 | IS17_INV4_M2 | IS18_INV1_M1 | IS18_INV1_M2 | IS18_INV2_M1 | IS18_INV2_M2 | IS18_INV3_M1 | IS18_INV3_M2 | IS18_INV4_M1 | IS18_INV4_M2 | IS19_INV1_M1 | IS19_INV1_M2 | IS19_INV2_M1 | IS19_INV2_M2 | IS19_INV3_M1 | IS19_INV3_M2 | IS19_INV4_M1 | IS19_INV4_M2 | IS20_INV1_M1 | IS20_INV1_M2 | IS20_INV2_M1 | IS20_INV2_M2 | IS20_INV3_M1 | IS20_INV3_M2 | IS20_INV4_M1 | IS20_INV4_M2 | Plant
2025-06-13 | 4.6664 | 4.5851 | 4.6019 | 4.6266 | 4.6366 | 4.633 | 4.6287 | 4.4782 | 4.6113 | 4.5385 | 4.1853 | 4.5892 | 4.2381 | 4.5757 | 4.6502 | 4.6557 | 4.612 | 4.6208 | 4.622 | 4.6765 | 4.5852 | 4.5896 | 4.6769 | 4.6249 | 4.585 | 4.9 | 4.5286 | 4.5147 | 4.5846 | 4.6166 | 4.6817 | 4.5823 | 6.0139 | 6.0388 | 6.1056 | 6.0412 | 4.6562 | 4.6237 | 4.6218 | 4.6068 | 4.4719 | 4.2891 | 4.5079 | 4.2603 | 4.1665 | 4.1881 | 4.2703 | 4.4653 | 4.3882 | 4.429 | 4.5444 | 4.7517 | 4.4412 | 4.4915 | 4.4214 | 4.3974 | 4.7372 | 4.3553 | 4.7725 | 4.4113 | 4.4137 | 4.739 | 4.3944 | 4.5153 | 4.5536 | 4.6974 | 4.5409 | 4.3975 | 4.3015 | 4.6475 | 4.336 | 4.7351 | 4.4548 | 4.4901 | 4.7368 | 4.3327 | 4.7734 | 4.3544 | 4.7403 | 4.3743 | 4.6701 | 4.4262 | 4.6188 | 4.3378 | 4.6775 | 4.4528 | 4.6527 | 5.0485 | 4.4592 | 4.5157 | 4.8216 | 4.4049 | 4.4659 | 4.7466 | 4.7067 | 4.4376 | 4.818 | 4.7177 | 4.4288 | 4.8498 | 4.4146 | 4.868 | 4.5169 | 4.7746 | 4.4396 | 4.88 | 4.463 | 4.7401 | 4.5032 | 4.7364 | 4.5164 | 4.8048 | 4.7768 | 4.4789 | 4.7471 | 4.8633 | 4.4774 | 4.4528 | 4.4873 | 4.7568 | 4.4367 | 4.7932 | 4.5991 | 4.8219 | 4.6353 | 5.0124 | 4.5395 | 4.8241 | 4.7554 | 4.7518 | 4.7669 | 5.1836 | 4.7522 | 5.1137 | 4.7158 | 4.7218 | 4.4587 | 4.8922 | 4.4626 | 4.8663 | 4.5023 | 4.8307 | 4.7876 | 4.7557 | 4.574 | 4.4326 | 4.4976 | 4.4882 | 4.5007 | 4.4477 | 4.8137 | 4.5002 | 4.4391 | 4.4116 | 4.4049 | 4.3987 | 4.4217 | 4.7739 | 4.4523 | 4.7866 | 4.6158
2025-06-14 | 1.5114 | 1.52 | 1.5244 | 1.5201 | 1.5358 | 1.5466 | 1.5545 | 1.5096 | 1.5494 | 1.5426 | 1.3844 | 1.5288 | 1.4048 | 1.5175 | 1.551 | 1.5546 | 1.5475 | 1.5308 | 1.5495 | 1.5672 | 1.5519 | 1.5244 | 1.5511 | 1.5459 | 1.5223 | 1.4996 | 1.4957 | 1.491 | 1.5486 | 1.5568 | 1.5684 | 1.5606 | 1.5868 | 1.5956 | 1.6045 | 1.5865 | 1.5917 | 1.5605 | 1.5765 | 1.5638 | 1.5929 | 1.4249 | 1.6212 | 1.4041 | 1.4341 | 1.557 | 1.4095 | 1.6112 | 1.4755 | 1.4996 | 1.5188 | 1.5431 | 1.5125 | 1.533 | 1.5259 | 1.5063 | 1.5054 | 1.5258 | 1.5028 | 1.5289 | 1.5205 | 1.5059 | 1.4936 | 1.4876 | 1.5251 | 1.5195 | 1.5154 | 1.5287 | 1.5145 | 1.5342 | 1.5127 | 1.4968 | 1.5279 | 1.5046 | 1.5333 | 1.5245 | 1.5224 | 1.5416 | 1.5159 | 1.5358 | 1.5389 | 1.5435 | 1.5465 | 1.5262 | 1.541 | 1.5366 | 1.553 | 1.5358 | 1.5819 | 1.558 | 1.5656 | 1.5816 | 1.5683 | 1.58 | 1.5594 | 1.5884 | 1.6038 | 1.5974 | 1.6017 | 1.6095 | 1.593 | 1.6074 | 1.5895 | 1.5947 | 1.6013 | 1.5909 | 1.6078 | 1.5968 | 1.6005 | 1.5905 | 1.6284 | 1.6154 | 1.5996 | 1.6065 | 1.6 | 1.6095 | 1.6197 | 1.6146 | 1.6168 | 1.609 | 1.6154 | 1.6194 | 1.6388 | 1.6229 | 1.6439 | 1.6172 | 1.6179 | 1.6298 | 1.6192 | 1.6403 | 1.6236 | 1.604 | 1.6025 | 1.6071 | 1.5936 | 1.6124 | 1.6589 | 1.6582 | 1.6805 | 1.6765 | 1.6783 | 1.6698 | 1.6559 | 1.6171 | 1.6556 | 1.6616 | 1.6394 | 1.6422 | 1.6484 | 1.6386 | 1.6606 | 1.6711 | 1.6449 | 1.6462 | 1.6613 | 1.644 | 1.6463 | 1.6466 | 1.6494 | 1.6474 | 1.5692
2025-06-15 | 2.6044 | 2.6407 | 2.6415 | 2.6296 | 2.6716 | 2.6736 | 2.6857 | 2.6386 | 2.6538 | 2.6411 | 2.3687 | 2.6151 | 2.408 | 2.5902 | 2.6696 | 2.6686 | 2.6578 | 2.6375 | 2.6534 | 2.6795 | 2.6492 | 2.6093 | 2.65 | 2.635 | 2.595 | 2.5533 | 2.5492 | 2.5471 | 2.631 | 2.6375 | 2.6487 | 2.6435 | 2.6476 | 2.669 | 2.7111 | 2.6759 | 2.6815 | 2.6323 | 2.6495 | 2.6178 | 2.6989 | 2.3929 | 2.7153 | 2.3557 | 2.413 | 2.6291 | 2.3805 | 2.7163 | 2.5168 | 2.5594 | 2.5949 | 2.6227 | 2.5997 | 2.6238 | 2.5933 | 2.5527 | 2.5537 | 2.5803 | 2.5687 | 2.5941 | 2.5811 | 2.574 | 2.528 | 2.5204 | 2.5726 | 2.5588 | 2.5605 | 2.5581 | 2.5616 | 2.5813 | 2.5017 | 2.5209 | 2.5828 | 2.5513 | 2.5982 | 2.5772 | 2.579 | 2.6105 | 2.5852 | 2.6011 | 2.5622 | 2.5778 | 2.5552 | 2.5299 | 2.5524 | 2.5338 | 2.5813 | 2.5346 | 2.6249 | 2.5706 | 2.5855 | 2.6174 | 2.5883 | 2.6096 | 2.5771 | 2.6187 | 2.604 | 2.5853 | 2.5958 | 2.6059 | 2.5956 | 2.6108 | 2.589 | 2.5943 | 2.5924 | 2.5807 | 2.5974 | 2.5705 | 2.5873 | 2.5657 | 2.6206 | 2.5904 | 2.5664 | 2.5895 | 2.5772 | 2.5982 | 2.5972 | 2.5809 | 2.5843 | 2.4987 | 2.5675 | 2.57 | 2.6171 | 2.5935 | 2.6236 | 2.556 | 2.5644 | 2.5694 | 2.5602 | 2.585 | 2.5607 | 2.5377 | 2.5294 | 2.5383 | 2.5442 | 2.5644 | 2.6669 | 2.6598 | 2.6896 | 2.6718 | 2.6675 | 2.6385 | 2.6279 | 2.6215 | 2.6752 | 2.6772 | 2.6583 | 2.651 | 2.6613 | 2.6363 | 2.6688 | 2.6849 | 2.6757 | 2.6852 | 2.709 | 2.6768 | 2.6852 | 2.6696 | 2.6778 | 2.6783 | 2.6003
2025-06-16 | 5.0201 | 5.0939 | 5.0972 | 5.0778 | 5.1446 | 5.1707 | 5.1643 | 5.0397 | 5.1247 | 5.0073 | 4.6213 | 5.053 | 4.6565 | 5.0163 | 5.1105 | 5.1395 | 5.092 | 5.1256 | 5.1119 | 5.1487 | 5.0884 | 5.0686 | 5.105 | 5.0803 | 4.999 | 4.9222 | 4.6958 | 4.8289 | 5.0858 | 5.0614 | 5.1016 | 5.0771 | 5.0834 | 5.1536 | 5.1852 | 5.141 | 5.1573 | 5.071 | 5.0773 | 5.0524 | 5.1006 | 4.6153 | 5.1265 | 4.5325 | 4.593 | 4.9031 | 4.6049 | 5.1478 | 4.8598 | 4.9389 | 5.0161 | 5.0582 | 4.9872 | 4.9945 | 4.9512 | 4.8866 | 4.9599 | 4.9437 | 4.9947 | 4.9829 | 4.9654 | 4.9907 | 4.8779 | 4.8801 | 4.9113 | 4.8333 | 4.8946 | 4.8025 | 4.8661 | 4.854 | 4.7162 | 4.7826 | 4.9373 | 4.862 | 5.0165 | 4.8676 | 4.9737 | 4.9635 | 5.004 | 4.933 | 4.8526 | 4.8359 | 4.8148 | 4.8094 | 4.8488 | 4.7861 | 4.8569 | 4.8565 | 4.9235 | 4.8558 | 4.9641 | 4.9264 | 4.9131 | 5.0113 | 4.9564 | 4.9268 | 4.9662 | 4.9673 | 4.9377 | 5.0279 | 4.9299 | 5.0379 | 4.9413 | 5.0005 | 4.9349 | 4.9753 | 4.9698 | 4.9372 | 4.9723 | 4.9607 | 5.0028 | 5.0228 | 4.9402 | 4.887 | 4.8695 | 4.9549 | 4.9047 | 4.859 | 4.8744 | 4.8789 | 4.825 | 4.876 | 4.9553 | 4.9866 | 4.9641 | 4.887 | 4.8404 | 4.8729 | 4.8561 | 4.88 | 4.8355 | 4.8377 | 4.7735 | 4.8368 | 4.7259 | 4.7648 | 4.8736 | 4.948 | 4.8543 | 4.9356 | 4.8963 | 4.8581 | 4.8713 | 4.8358 | 4.8204 | 4.7879 | 4.8247 | 4.8082 | 4.8503 | 4.829 | 4.8854 | 4.8346 | 4.7883 | 4.7656 | 4.7231 | 4.7168 | 4.74 | 4.7655 | 4.794 | 4.83 | 4.9273
2025-06-17 | 3.7051 | 3.6704 | 3.6633 | 3.6847 | 3.6817 | 3.6998 | 3.6973 | 3.5783 | 3.6752 | 3.6114 | 3.4344 | 3.6412 | 3.4517 | 3.6477 | 3.7442 | 3.75 | 3.7064 | 3.7086 | 3.7126 | 3.7656 | 3.6762 | 3.6764 | 3.72 | 3.6937 | 3.6467 | 3.893 | 3.6317 | 3.6157 | 3.6491 | 3.6404 | 3.703 | 3.6435 | 4.8313 | 4.8637 | 4.9386 | 4.8979 | 3.7008 | 3.6729 | 3.6741 | 3.6602 | 3.6 | 3.4153 | 3.6222 | 3.3901 | 3.3103 | 3.3626 | 3.3886 | 3.5921 | 3.5273 | 3.5529 | 3.6571 | 3.7752 | 3.5838 | 3.6182 | 3.5419 | 3.5298 | 3.7454 | 3.4955 | 3.7714 | 3.5263 | 3.5283 | 3.7488 | 3.5177 | 3.6091 | 3.6182 | 3.7084 | 3.6062 | 3.5006 | 3.4503 | 3.6718 | 3.4612 | 3.7287 | 3.5625 | 3.5801 | 3.7653 | 3.4945 | 3.8082 | 3.5087 | 3.779 | 3.5368 | 3.6895 | 3.5294 | 3.6681 | 3.466 | 3.7024 | 3.5491 | 3.6882 | 3.9652 | 3.6 | 3.6189 | 3.8351 | 3.5365 | 3.5766 | 3.7737 | 3.7367 | 3.5658 | 3.8176 | 3.743 | 3.5341 | 3.8202 | 3.517 | 3.8147 | 3.5604 | 3.7467 | 3.5123 | 3.8141 | 3.5303 | 3.713 | 3.5527 | 3.709 | 3.5639 | 3.7645 | 3.7628 | 3.5421 | 3.7082 | 3.799 | 3.5274 | 3.5079 | 3.5248 | 3.707 | 3.4906 | 3.7359 | 3.6092 | 3.7694 | 3.6417 | 3.8895 | 3.559 | 3.7626 | 3.7357 | 3.7491 | 3.6954 | 4.0112 | 3.746 | 4.0316 | 3.7811 | 3.8013 | 3.6065 | 3.9034 | 3.6372 | 3.9115 | 3.6681 | 3.881 | 3.8527 | 3.831 | 3.7509 | 3.6532 | 3.6903 | 3.6807 | 3.6725 | 3.615 | 3.8868 | 3.6887 | 3.6711 | 3.6386 | 3.628 | 3.6292 | 3.6442 | 3.8689 | 3.6801 | 3.892 | 3.6855
2025-06-18 | 5.482 | 5.4526 | 5.4789 | 5.4895 | 5.5244 | 5.5432 | 5.5273 | 5.3697 | 5.5022 | 5.4304 | 5.175 | 5.4226 | 5.3241 | 5.4098 | 5.5191 | 5.549 | 5.4858 | 5.4891 | 5.5008 | 5.5387 | 5.4525 | 5.45 | 5.4996 | 5.4659 | 5.4091 | 5.5733 | 5.3555 | 5.3356 | 5.4297 | 5.4107 | 5.5072 | 5.4486 | 5.9982 | 5.9986 | 6.0632 | 6.0031 | 5.5428 | 5.4789 | 5.4884 | 5.468 | 5.3819 | 5.0014 | 5.4128 | 4.935 | 4.9021 | 5.0813 | 4.9704 | 5.4032 | 5.2379 | 5.3066 | 5.4214 | 5.5606 | 5.3389 | 5.3664 | 5.3169 | 5.2548 | 5.5167 | 5.2739 | 5.5417 | 5.3423 | 5.3366 | 5.5168 | 5.2725 | 5.3372 | 5.3948 | 5.4631 | 5.378 | 5.2754 | 5.2118 | 5.4423 | 5.2297 | 5.4641 | 5.3283 | 5.3317 | 5.5375 | 5.2385 | 5.5471 | 5.2995 | 5.5344 | 5.2942 | 5.4653 | 5.2998 | 5.4212 | 5.2536 | 5.4706 | 5.299 | 5.454 | 5.6624 | 5.3649 | 5.3512 | 5.5868 | 5.3352 | 5.3587 | 5.5567 | 5.4978 | 5.3504 | 5.5792 | 5.5069 | 5.3108 | 5.5816 | 5.2674 | 5.57 | 5.3183 | 5.4918 | 5.2578 | 5.539 | 5.2914 | 5.4521 | 5.3068 | 5.4383 | 5.333 | 5.53 | 5.4996 | 5.3066 | 5.4657 | 5.5613 | 5.3042 | 5.2819 | 5.2923 | 5.4549 | 5.256 | 5.4877 | 5.4005 | 5.5435 | 5.4261 | 5.6049 | 5.3241 | 5.5037 | 5.4566 | 5.4605 | 5.6445 | 5.7226 | 5.3953 | 5.6601 | 5.4227 | 5.4469 | 5.3819 | 5.6829 | 5.3949 | 5.684 | 5.4342 | 5.6285 | 5.5936 | 5.5126 | 5.4783 | 5.3812 | 5.4275 | 5.4111 | 5.4205 | 5.3596 | 5.6343 | 5.4299 | 5.4042 | 5.3596 | 5.3563 | 5.3389 | 5.3524 | 5.5837 | 5.3854 | 5.6103 | 5.4266
2025-06-19 | 5.2286 | 5.2029 | 5.241 | 5.2391 | 5.3072 | 5.3086 | 5.2581 | 5.0996 | 5.2457 | 5.1674 | 4.8989 | 5.1408 | 5.1163 | 5.1629 | 5.2699 | 5.3026 | 5.2364 | 5.2328 | 5.2232 | 5.259 | 5.1695 | 5.1626 | 5.2407 | 5.1971 | 5.1293 | 5.2614 | 5.0682 | 5.0521 | 5.1594 | 5.149 | 5.2424 | 5.1783 | 5.6313 | 5.6207 | 5.6615 | 5.6031 | 5.2561 | 5.1735 | 5.2422 | 5.2307 | 5.279 | 4.8482 | 5.3004 | 4.8079 | 4.7673 | 4.9831 | 4.813 | 5.2804 | 4.9051 | 5.003 | 5.0337 | 5.1443 | 5.0735 | 5.1015 | 5.0319 | 4.9827 | 5.2036 | 5.0081 | 5.2614 | 5.0663 | 5.0781 | 5.2445 | 5.0262 | 5.0911 | 5.1024 | 5.1606 | 5.0801 | 4.9941 | 4.9557 | 5.142 | 4.9711 | 5.1758 | 5.0584 | 5.0632 | 5.2443 | 4.9896 | 5.2655 | 5.0547 | 5.2768 | 5.0578 | 5.1671 | 5.0285 | 5.1231 | 4.9826 | 5.1617 | 5.0167 | 5.13 | 5.2615 | 5.0753 | 5.0694 | 5.2711 | 5.0783 | 5.1087 | 5.2916 | 5.2521 | 5.1134 | 5.3157 | 5.2615 | 5.1036 | 5.3395 | 5.0499 | 5.3173 | 5.0881 | 5.2477 | 5.0321 | 5.2815 | 5.0563 | 5.2011 | 5.0652 | 5.173 | 5.1092 | 5.2854 | 5.2751 | 5.1048 | 5.2294 | 5.3258 | 5.0885 | 5.0731 | 5.0795 | 5.2211 | 5.0485 | 5.2533 | 5.166 | 5.301 | 5.2032 | 5.3985 | 5.116 | 5.2924 | 5.4807 | 5.5201 | 5.2257 | 5.4229 | 5.2081 | 5.4516 | 5.2408 | 5.256 | 5.2339 | 5.4828 | 5.2706 | 5.4999 | 5.2101 | 5.4162 | 5.4126 | 5.3184 | 5.3057 | 5.2341 | 5.2725 | 5.2531 | 5.2611 | 5.2194 | 5.4584 | 5.2953 | 5.2469 | 5.2144 | 5.2177 | 5.2156 | 5.2266 | 5.4087 | 5.2462 | 5.4451 | 5.188
2025-06-20 | 5.3221 | 5.4052 | 5.3874 | 5.3749 | 5.4364 | 5.4657 | 5.4999 | 5.3805 | 5.4148 | 5.383 | 5.1878 | 5.4266 | 5.3251 | 5.3816 | 5.4303 | 5.4239 | 5.3864 | 5.3722 | 5.393 | 5.4174 | 5.3495 | 5.3284 | 5.3545 | 5.3319 | 5.2626 | 5.2688 | 5.193 | 5.1814 | 5.3509 | 5.3971 | 5.3746 | 5.3426 | 5.5945 | 5.5722 | 5.6154 | 5.58 | 5.4676 | 5.3788 | 5.4061 | 5.3822 | 5.3666 | 4.7785 | 5.3819 | 4.7711 | 4.8248 | 5.1411 | 4.834 | 5.4015 | 5.1849 | 5.2398 | 0 | 0 | 5.2721 | 5.3293 | 5.2436 | 5.2325 | 5.2798 | 5.2252 | 5.2896 | 5.2659 | 5.2316 | 5.2642 | 5.2188 | 5.2078 | 5.2259 | 5.1818 | 5.1937 | 5.0988 | 5.1371 | 5.188 | 5.126 | 5.166 | 5.2002 | 5.1446 | 5.2852 | 5.1266 | 5.2649 | 5.2099 | 5.2807 | 5.1789 | 5.1873 | 5.1362 | 5.1828 | 5.1106 | 5.1941 | 5.1158 | 5.1879 | 5.2423 | 5.2329 | 5.1607 | 5.2927 | 5.2443 | 5.2514 | 5.3574 | 5.314 | 5.249 | 5.3418 | 5.2679 | 5.2257 | 5.3076 | 5.2152 | 5.3102 | 5.2083 | 5.2629 | 5.174 | 5.2632 | 5.1878 | 5.2054 | 5.1845 | 5.1979 | 5.2094 | 5.2582 | 5.1867 | 5.1555 | 5.2293 | 5.2909 | 5.1738 | 5.1478 | 5.1273 | 5.1412 | 5.1257 | 5.2067 | 5.2423 | 5.2598 | 5.2468 | 5.2638 | 5.141 | 5.2171 | 5.2502 | 5.2869 | 5.2297 | 5.2992 | 5.2636 | 5.308 | 5.2009 | 5.2226 | 5.3117 | 5.4305 | 5.3584 | 5.4225 | 4.9494 | 5.2899 | 5.4023 | 5.3048 | 5.4101 | 5.3774 | 5.3761 | 5.3568 | 5.3437 | 5.2904 | 5.4421 | 5.3999 | 5.4004 | 5.3745 | 5.3835 | 5.3649 | 5.3818 | 5.4592 | 5.3707 | 5.4759 | 5.21
2025-06-21 | 1.9639 | 2.0114 | 2.0116 | 2.0074 | 2.0378 | 2.0334 | 2.0512 | 2.022 | 2.0177 | 2.0045 | 1.9495 | 2.0161 | 2.0231 | 1.9984 | 2.0463 | 2.0398 | 2.0395 | 1.9639 | 2.0227 | 2.0227 | 2.0257 | 2.0045 | 2.0115 | 2.0056 | 1.9512 | 1.9208 | 1.9383 | 1.9266 | 2.0083 | 2.0388 | 2.014 | 1.999 | 2.0322 | 2.0307 | 2.0539 | 2.0335 | 2.0372 | 1.9936 | 2.0267 | 1.9946 | 2.0938 | 1.8263 | 2.103 | 1.8258 | 1.8613 | 2.0162 | 1.8336 | 2.1052 | 1.8361 | 1.8575 | 0 | 0 | 1.9386 | 1.986 | 1.9266 | 1.9164 | 1.9205 | 1.9419 | 1.9519 | 1.9573 | 1.9187 | 1.9425 | 1.9077 | 1.8945 | 1.9204 | 1.8912 | 1.9118 | 1.9001 | 1.9053 | 1.908 | 1.9003 | 1.8594 | 1.9384 | 1.8718 | 1.9234 | 1.8923 | 1.9053 | 1.9456 | 1.8569 | 1.866 | 1.8956 | 1.9065 | 1.9054 | 1.8889 | 1.9008 | 1.8867 | 1.9271 | 1.885 | 1.9602 | 1.9233 | 1.9431 | 1.9547 | 1.9559 | 1.9701 | 1.9477 | 1.9628 | 1.9775 | 1.9474 | 1.9522 | 1.951 | 1.9548 | 1.9519 | 1.9423 | 1.9297 | 1.9607 | 1.9319 | 1.9599 | 1.9229 | 1.9535 | 1.9347 | 1.9856 | 1.919 | 1.9259 | 1.9249 | 1.9204 | 1.9245 | 1.9364 | 1.9081 | 1.9277 | 1.8909 | 1.9074 | 1.9103 | 1.9635 | 1.9035 | 1.9704 | 1.897 | 1.8994 | 1.911 | 1.9103 | 1.9478 | 1.9263 | 1.8968 | 1.9218 | 1.8928 | 1.8633 | 1.8677 | 1.9219 | 1.9123 | 1.9354 | 1.9106 | 1.9197 | 1.922 | 1.9077 | 1.9024 | 1.9028 | 1.9064 | 1.8963 | 1.8988 | 1.9093 | 1.8893 | 1.9028 | 1.9186 | 1.9069 | 1.9075 | 1.9134 | 1.8831 | 1.8927 | 1.8843 | 1.9181 | 1.8985 | 1.9192
2025-06-22 | 5.0507 | 5.0528 | 5.0223 | 5.0293 | 5.0663 | 5.0592 | 5.0933 | 4.9407 | 5.0723 | 5.0387 | 4.8925 | 5.0692 | 4.8901 | 5.0149 | 4.9921 | 5.0535 | 5.0045 | 4.8449 | 5.0158 | 5.0422 | 5.0095 | 4.894 | 5.0857 | 5.0256 | 4.9693 | 5.0664 | 4.8471 | 4.864 | 5.0515 | 5.1069 | 5.107 | 5.0499 | 5.839 | 5.8099 | 5.8883 | 5.8694 | 5.1511 | 5.0795 | 5.0995 | 4.9727 | 5.0055 | 4.5287 | 5.0462 | 4.4532 | 4.5596 | 4.6894 | 4.62 | 5.0086 | 4.7919 | 4.8286 | 4.9307 | 5.086 | 4.6702 | 4.929 | 4.8575 | 4.7712 | 4.977 | 4.8102 | 5.0599 | 4.8785 | 4.7722 | 5.0353 | 4.8787 | 4.949 | 4.9579 | 5.0208 | 4.8602 | 4.7706 | 4.7859 | 4.9942 | 4.7694 | 4.8419 | 4.8973 | 4.8038 | 5.0586 | 4.8188 | 4.9601 | 4.8554 | 5.0681 | 4.8797 | 5.0108 | 4.8587 | 5.0128 | 4.6229 | 5.037 | 4.7111 | 5.0122 | 5.1653 | 4.9302 | 4.9491 | 5.1561 | 4.9202 | 4.9352 | 5.1124 | 5.0544 | 4.9282 | 5.1203 | 5.0641 | 4.8962 | 5.1079 | 4.8441 | 5.1259 | 4.8979 | 5.0477 | 4.8433 | 5.0054 | 4.8742 | 5.0118 | 4.8955 | 4.9644 | 4.9271 | 4.8919 | 5.0515 | 4.8956 | 4.9552 | 5.0435 | 4.9076 | 4.8823 | 4.9067 | 5.0427 | 4.8775 | 5.0862 | 5.0137 | 4.9303 | 5.0495 | 5.0166 | 4.9343 | 5.0871 | 4.9007 | 5.1099 | 5.0841 | 5.2587 | 5.0965 | 5.2335 | 4.987 | 5.0022 | 4.9338 | 5.1874 | 4.9445 | 5.1421 | 4.9468 | 5.1558 | 5.1275 | 5.0615 | 5.0396 | 4.9485 | 4.9266 | 4.9656 | 4.9609 | 4.908 | 5.14 | 4.9835 | 4.9908 | 4.9478 | 4.9799 | 4.8838 | 4.944 | 5.1408 | 4.9427 | 5.138 | 4.983
2025-06-23 | 4.8242 | 4.9037 | 4.8725 | 4.8638 | 4.9241 | 4.9348 | 4.9625 | 4.8907 | 4.9338 | 4.9147 | 4.9099 | 4.9293 | 4.9177 | 4.8617 | 4.89 | 4.9219 | 4.8911 | 4.829 | 4.8971 | 4.9186 | 4.8652 | 4.7999 | 4.8536 | 4.8398 | 4.783 | 4.7001 | 4.7033 | 4.6959 | 4.8543 | 4.9079 | 4.8773 | 4.8694 | 4.9438 | 4.9415 | 4.9773 | 4.94 | 4.9838 | 4.8841 | 4.916 | 4.846 | 4.9577 | 4.3921 | 4.9808 | 4.2881 | 4.3865 | 4.7647 | 4.3737 | 4.9869 | 4.6662 | 4.7344 | 4.7868 | 4.8374 | 4.7601 | 4.8381 | 4.7678 | 4.6947 | 4.7314 | 4.7936 | 4.7237 | 4.7937 | 4.7506 | 4.7394 | 4.7827 | 4.764 | 4.7959 | 4.7517 | 4.7478 | 4.7209 | 4.7505 | 4.7691 | 4.7462 | 4.6781 | 4.7794 | 4.6997 | 4.8157 | 4.7618 | 4.779 | 4.831 | 4.7844 | 4.7953 | 4.7739 | 4.7681 | 4.7586 | 4.761 | 4.7638 | 4.7257 | 4.7822 | 4.738 | 4.863 | 4.7782 | 4.8301 | 4.8718 | 4.8344 | 4.8655 | 4.812 | 4.8716 | 4.8989 | 4.8646 | 4.8746 | 4.8718 | 4.8344 | 4.8633 | 4.8113 | 4.825 | 4.8015 | 4.7977 | 4.82 | 4.7855 | 4.7944 | 4.7448 | 4.8503 | 4.8251 | 4.7982 | 4.8015 | 4.7946 | 4.8372 | 4.8385 | 4.8058 | 4.7986 | 4.7712 | 4.7765 | 4.781 | 4.8705 | 4.8367 | 4.8736 | 4.7906 | 4.77 | 4.7891 | 4.8125 | 4.8651 | 4.7944 | 4.7735 | 4.8406 | 4.818 | 4.7901 | 4.8053 | 4.9665 | 4.9951 | 4.9914 | 4.9785 | 5.0133 | 4.9979 | 5.0001 | 4.8953 | 4.9707 | 4.9693 | 4.9567 | 4.9565 | 4.9625 | 4.9168 | 4.9788 | 4.9997 | 5.0046 | 4.9884 | 5.0092 | 4.9715 | 4.9763 | 4.9582 | 4.9878 | 4.9883 | 4.8349
2025-06-24 | 5.385 | 5.4817 | 5.4834 | 5.4767 | 5.531 | 5.5253 | 5.548 | 5.4497 | 5.4928 | 5.4739 | 5.4643 | 5.4784 | 5.4719 | 5.4311 | 5.4768 | 5.4913 | 5.4379 | 5.4327 | 5.4445 | 5.489 | 5.396 | 5.3744 | 5.3971 | 5.3762 | 5.2976 | 5.2084 | 5.2273 | 5.2132 | 5.4092 | 5.4483 | 5.428 | 5.406 | 5.4494 | 5.4536 | 5.4938 | 5.4538 | 5.5242 | 5.4234 | 5.4505 | 5.421 | 5.5382 | 4.9243 | 5.5507 | 4.8445 | 4.9002 | 5.3025 | 4.8982 | 5.5752 | 5.2196 | 5.2832 | 5.3273 | 5.3661 | 5.325 | 5.3703 | 5.2691 | 5.2496 | 5.2366 | 5.2716 | 5.2795 | 5.3468 | 5.3204 | 5.2699 | 5.2945 | 5.2777 | 5.2562 | 5.2197 | 5.2279 | 5.2262 | 5.21 | 5.264 | 5.2083 | 5.2185 | 5.2449 | 5.2447 | 5.3166 | 5.2657 | 5.3285 | 5.3565 | 5.3547 | 5.3203 | 5.2936 | 5.284 | 5.2758 | 5.278 | 5.2744 | 5.2214 | 5.2462 | 5.2185 | 5.344 | 5.2444 | 5.3168 | 5.3534 | 5.3159 | 5.3499 | 5.2893 | 5.3472 | 5.4098 | 5.4097 | 5.4268 | 5.4429 | 5.4057 | 5.4412 | 5.3882 | 5.4056 | 5.3542 | 5.3679 | 5.3782 | 5.3439 | 5.347 | 5.2875 | 5.3935 | 5.4153 | 5.3612 | 5.3677 | 5.328 | 5.4068 | 5.3972 | 5.3779 | 5.3181 | 5.2985 | 5.3436 | 5.355 | 5.4334 | 5.4184 | 5.4406 | 5.3755 | 5.3498 | 5.3698 | 5.3866 | 5.4227 | 5.3528 | 5.3379 | 5.3936 | 5.3601 | 5.3378 | 5.3592 | 5.5577 | 5.5827 | 5.5752 | 5.5744 | 5.6054 | 5.588 | 5.5965 | 5.4723 | 5.5769 | 5.5725 | 5.5599 | 5.5472 | 5.5649 | 5.512 | 5.5589 | 5.5983 | 5.6032 | 5.5746 | 5.6093 | 5.5762 | 5.5829 | 5.5769 | 5.4801 | 5.592 | 5.3826
2025-06-25 | 5.0126 | 5.0752 | 5.0708 | 5.0589 | 5.1268 | 5.1458 | 5.1702 | 5.0899 | 5.1194 | 5.0902 | 5.0918 | 5.113 | 5.1399 | 5.0992 | 5.1628 | 5.1667 | 5.1472 | 5.0704 | 5.158 | 5.1798 | 5.1311 | 4.9874 | 5.1321 | 5.1169 | 5.0612 | 4.9802 | 4.9691 | 4.9715 | 5.1469 | 5.1475 | 5.1268 | 5.1336 | 5.1493 | 5.1541 | 5.2356 | 5.1824 | 5.2321 | 5.1096 | 5.1405 | 5.0448 | 5.153 | 4.5538 | 5.1767 | 4.4826 | 4.5857 | 4.943 | 4.5835 | 5.1849 | 4.875 | 4.9716 | 5.0343 | 5.0856 | 4.9224 | 5.079 | 4.9899 | 4.9563 | 4.9564 | 4.973 | 4.9663 | 5.0188 | 4.9378 | 4.9494 | 4.9461 | 4.9369 | 4.9519 | 4.9021 | 4.9071 | 4.8777 | 4.89 | 4.9116 | 4.8689 | 4.8321 | 4.9311 | 4.8493 | 4.9772 | 4.8921 | 4.9593 | 4.9874 | 4.8881 | 4.9634 | 4.9313 | 4.9179 | 4.9305 | 4.8144 | 4.936 | 4.8783 | 4.9353 | 4.8244 | 5.0414 | 4.9487 | 5.035 | 5.0514 | 5.0221 | 5.0433 | 4.913 | 5.0472 | 5.0752 | 5.0278 | 5.03 | 5.0234 | 5.0228 | 5.0382 | 4.9941 | 4.9815 | 4.9797 | 4.9434 | 5.0019 | 4.9678 | 5.0041 | 4.9788 | 5.0612 | 4.9258 | 4.9176 | 4.9457 | 4.9319 | 4.9882 | 5.0108 | 4.9724 | 4.9669 | 4.955 | 4.9704 | 4.9936 | 5.0794 | 4.9454 | 5.1078 | 4.9315 | 4.9915 | 5.0004 | 4.8679 | 5.0377 | 4.9822 | 4.9462 | 4.9993 | 4.9892 | 4.9572 | 4.9967 | 5.2457 | 5.3122 | 5.2649 | 5.2738 | 5.2565 | 5.2442 | 5.226 | 5.114 | 5.3086 | 5.2824 | 5.169 | 5.2466 | 5.2539 | 5.1958 | 5.2675 | 5.2748 | 5.2208 | 5.2815 | 5.3109 | 5.1898 | 5.2794 | 5.3117 | 5.2115 | 5.3158 | 5.0388
2025-06-26 | 4.6892 | 4.706 | 4.6165 | 4.6277 | 4.6395 | 4.6542 | 4.7236 | 4.6383 | 4.7681 | 4.76 | 4.6702 | 4.7462 | 4.6388 | 4.6916 | 4.6343 | 4.6624 | 4.5942 | 4.5829 | 4.6545 | 4.6992 | 4.5917 | 4.597 | 4.5902 | 4.5882 | 4.6055 | 4.5695 | 4.5396 | 4.5079 | 4.6508 | 4.6452 | 4.6597 | 4.6562 | 4.7865 | 4.7869 | 4.8035 | 4.7523 | 4.7841 | 4.6851 | 4.702 | 4.7151 | 4.5635 | 4.108 | 4.2054 | 4.1634 | 4.0955 | 4.3975 | 4.079 | 4.5856 | 4.4809 | 4.5776 | 4.6416 | 4.7286 | 4.6007 | 4.614 | 4.633 | 4.5783 | 4.6499 | 4.6311 | 4.6313 | 4.6802 | 4.6627 | 4.6347 | 4.6048 | 4.5958 | 4.6493 | 4.6271 | 4.6193 | 4.6032 | 4.5703 | 4.6427 | 4.5765 | 4.6 | 4.6174 | 4.6095 | 4.6773 | 4.5995 | 4.679 | 4.6404 | 4.6821 | 4.6379 | 4.6493 | 4.6291 | 4.5962 | 4.6111 | 4.6306 | 4.5712 | 4.6634 | 4.6149 | 4.6979 | 4.6398 | 4.7121 | 4.6906 | 4.68 | 4.7466 | 4.6827 | 4.6798 | 4.7232 | 4.6846 | 4.6445 | 4.6759 | 4.6467 | 4.6854 | 4.6342 | 4.6434 | 4.6151 | 4.6249 | 4.6277 | 4.602 | 4.6322 | 4.6095 | 4.6584 | 4.6773 | 4.4981 | 4.5651 | 4.5745 | 4.6239 | 4.6028 | 4.5763 | 4.565 | 4.5516 | 4.545 | 4.5741 | 4.648 | 4.6501 | 4.6564 | 4.5819 | 4.5548 | 4.5686 | 4.5692 | 4.6073 | 4.5243 | 4.5221 | 4.5651 | 4.5687 | 4.3957 | 4.4185 | 4.5466 | 4.6256 | 4.5284 | 4.5952 | 4.5634 | 4.5885 | 4.5894 | 4.5044 | 4.5275 | 4.5016 | 4.5348 | 4.5178 | 4.5449 | 4.5013 | 4.573 | 4.5336 | 4.503 | 4.4665 | 4.4488 | 4.4243 | 4.4372 | 4.4769 | 4.4655 | 4.5375 | 4.5963
2025-06-27 | 3.6974 | 3.7422 | 3.7157 | 3.7275 | 3.7353 | 3.7439 | 3.7776 | 3.7028 | 3.7424 | 3.7481 | 3.6825 | 3.7278 | 3.6939 | 3.6827 | 3.7302 | 3.7327 | 3.7082 | 3.6507 | 3.6947 | 3.7232 | 3.6726 | 3.5888 | 3.6586 | 3.6496 | 3.5866 | 3.5605 | 3.5501 | 3.5358 | 3.6641 | 3.6904 | 3.6576 | 3.6343 | 3.6574 | 3.6497 | 3.7285 | 3.6865 | 3.7061 | 3.6301 | 3.6011 | 3.5874 | 3.6613 | 3.2759 | 3.6586 | 3.5871 | 3.2636 | 3.4743 | 3.2519 | 3.6736 | 3.5242 | 3.5889 | 3.619 | 3.6566 | 3.5556 | 3.6656 | 3.5825 | 3.5507 | 3.5907 | 3.5666 | 3.6165 | 3.6071 | 3.544 | 3.6147 | 3.5576 | 3.556 | 3.5524 | 3.5267 | 3.5344 | 3.4851 | 3.4617 | 3.5286 | 2.9238 | 3.3681 | 3.5525 | 3.484 | 3.5968 | 3.5012 | 3.5713 | 3.5715 | 3.5833 | 3.5637 | 3.5052 | 3.4839 | 3.4859 | 3.341 | 3.487 | 3.423 | 3.5378 | 3.4529 | 3.5733 | 3.5124 | 3.5793 | 3.5448 | 3.5399 | 3.5989 | 3.5548 | 3.5458 | 3.5854 | 3.5167 | 3.4925 | 3.5175 | 3.4881 | 3.5365 | 3.4822 | 3.4921 | 3.4801 | 3.485 | 3.4862 | 3.4559 | 3.4112 | 3.4215 | 3.5173 | 3.0581 | 3.4119 | 3.4215 | 3.3755 | 3.4664 | 3.347 | 3.3684 | 3.337 | 3.3614 | 3.3435 | 3.371 | 3.4651 | 3.2875 | 3.4493 | 3.2915 | 3.3359 | 3.3421 | 3.1123 | 3.4104 | 3.3528 | 3.3358 | 3.3828 | 3.3801 | 3.3793 | 3.3988 | 3.4992 | 3.5391 | 3.5029 | 3.4488 | 3.5103 | 3.5164 | 3.4747 | 3.4475 | 3.5092 | 3.492 | 3.4521 | 3.4724 | 3.4825 | 3.407 | 3.5062 | 3.5065 | 3.4317 | 3.4718 | 3.4826 | 3.4022 | 3.4591 | 3.4908 | 3.4853 | 3.4945 | 3.5246
2025-06-28 | 4.9024 | 4.9189 | 4.9032 | 4.9411 | 4.9384 | 4.9147 | 4.954 | 4.9053 | 4.9798 | 5.0058 | 4.9399 | 5.0011 | 4.9374 | 4.9254 | 4.8676 | 4.9216 | 4.9272 | 4.7611 | 4.9323 | 4.9712 | 4.899 | 4.7694 | 4.8941 | 4.867 | 4.8532 | 4.8084 | 4.7502 | 4.7493 | 4.8656 | 5.0016 | 5.0029 | 4.9372 | 5.1312 | 5.0374 | 5.0254 | 4.9802 | 5.0534 | 4.9735 | 5.1013 | 5.0058 | 5.1952 | 4.6365 | 5.1486 | 5.0729 | 4.6336 | 4.9743 | 4.6814 | 5.2226 | 4.767 | 4.8293 | 4.8831 | 4.9724 | 4.7469 | 4.9012 | 4.8403 | 4.7216 | 4.827 | 4.8606 | 4.8591 | 4.8882 | 4.8465 | 4.8583 | 4.8859 | 4.9054 | 4.8887 | 4.886 | 4.8214 | 4.7964 | 4.814 | 4.9221 | 4.8309 | 4.8533 | 4.8932 | 4.8417 | 4.9874 | 4.8713 | 4.9579 | 4.9715 | 4.9621 | 4.9601 | 4.9456 | 4.903 | 4.9107 | 4.8186 | 4.9037 | 4.7879 | 4.9056 | 4.8308 | 5.05 | 4.9017 | 5.0494 | 5.0381 | 5.0541 | 5.1508 | 5.1131 | 5.116 | 5.2924 | 5.2432 | 5.1824 | 5.2796 | 5.1645 | 5.2718 | 5.1746 | 5.2251 | 5.1347 | 5.1939 | 5.1588 | 5.1769 | 5.151 | 5.184 | 5.2303 | 5.2371 | 5.1148 | 5.1845 | 5.1992 | 5.2825 | 5.2067 | 5.1582 | 5.1791 | 5.2057 | 5.1427 | 5.2466 | 5.2725 | 5.241 | 5.2646 | 5.2327 | 5.1916 | 5.2558 | 5.2505 | 5.344 | 5.3051 | 5.2697 | 5.3407 | 5.3322 | 5.1819 | 5.1901 | 5.276 | 5.3742 | 5.3042 | 5.3803 | 5.3124 | 5.3328 | 5.323 | 5.257 | 5.3973 | 5.3201 | 5.2844 | 5.3322 | 5.3236 | 5.2528 | 5.3488 | 5.3421 | 5.265 | 5.2801 | 5.3128 | 5.2728 | 5.3035 | 5.3913 | 5.2743 | 5.444 | 5.0527
2025-06-29 | 4.3579 | 4.4524 | 4.5019 | 4.4727 | 4.5871 | 4.5759 | 4.5573 | 4.4735 | 4.4338 | 4.4423 | 4.4092 | 4.4081 | 4.4796 | 4.4112 | 4.5543 | 4.5616 | 4.5425 | 4.4445 | 4.499 | 4.5047 | 4.5027 | 4.3803 | 4.5451 | 4.4997 | 4.3647 | 4.2778 | 4.271 | 4.3059 | 4.5017 | 4.5973 | 4.5831 | 4.4864 | 4.4876 | 4.4577 | 4.4966 | 4.4697 | 4.5532 | 4.5172 | 4.5603 | 4.4921 | 4.6287 | 4.5993 | 4.6238 | 4.5555 | 4.1879 | 4.4575 | 4.1849 | 4.6475 | 4.2235 | 4.2666 | 4.325 | 4.3527 | 4.3005 | 4.4382 | 4.2495 | 4.2608 | 4.2144 | 4.2304 | 4.2642 | 4.2571 | 4.2191 | 4.2522 | 4.2238 | 4.2441 | 4.1973 | 4.1687 | 4.1826 | 4.1436 | 4.1737 | 4.2151 | 4.1892 | 4.0989 | 4.244 | 4.2505 | 4.3063 | 4.256 | 4.3065 | 4.3098 | 4.355 | 4.3195 | 4.2147 | 4.2211 | 4.2098 | 4.0661 | 4.2019 | 4.1306 | 4.2097 | 4.0971 | 4.3067 | 4.2275 | 4.3289 | 4.3322 | 4.3565 | 4.4501 | 4.4078 | 4.3624 | 4.4283 | 4.3458 | 4.3419 | 4.3814 | 4.3481 | 4.4057 | 4.3685 | 4.392 | 4.3561 | 4.3781 | 4.373 | 4.3504 | 4.3529 | 4.3589 | 4.4618 | 4.3414 | 4.2432 | 4.3093 | 4.3019 | 4.3628 | 4.2995 | 4.3226 | 4.2651 | 4.2794 | 4.2918 | 4.3675 | 4.3973 | 4.3237 | 4.0221 | 4.3524 | 4.3305 | 4.3901 | 4.321 | 4.4476 | 4.4265 | 4.407 | 4.4279 | 4.4169 | 4.2638 | 4.2965 | 4.3569 | 4.4551 | 4.3615 | 4.4074 | 4.4133 | 4.4232 | 4.3263 | 4.3349 | 4.3786 | 4.3448 | 4.298 | 4.3293 | 4.3423 | 4.2621 | 4.286 | 4.3536 | 4.2795 | 4.3136 | 4.3077 | 4.2295 | 4.271 | 4.3549 | 4.264 | 4.3502 | 4.3557
2025-06-30 | 4.5151 | 4.587 | 4.5706 | 4.5531 | 4.6379 | 4.6678 | 4.6911 | 4.6132 | 4.6143 | 4.5975 | 4.6292 | 4.5993 | 4.6777 | 4.623 | 4.7027 | 4.6942 | 4.703 | 4.7 | 4.7157 | 4.7252 | 4.67 | 4.6642 | 4.6972 | 4.6643 | 4.6019 | 4.5279 | 4.519 | 4.5247 | 4.6999 | 4.7491 | 4.7317 | 4.7008 | 4.7461 | 4.7294 | 4.77 | 4.7157 | 4.796 | 4.7205 | 4.7362 | 4.7065 | 4.9295 | 4.9444 | 4.8683 | 4.8859 | 4.4201 | 4.7404 | 4.9507 | 4.9194 | 4.4631 | 4.5251 | 4.5752 | 4.5953 | 4.5941 | 4.6338 | 4.5103 | 4.542 | 4.4728 | 4.4976 | 4.4826 | 4.5303 | 4.4976 | 4.4581 | 4.4866 | 4.4955 | 4.4798 | 4.4673 | 4.4878 | 4.4739 | 4.4735 | 4.5279 | 4.5014 | 4.5154 | 4.4935 | 4.5134 | 4.5553 | 4.5272 | 4.5932 | 4.5596 | 4.5906 | 4.5542 | 4.5272 | 4.5412 | 4.513 | 4.4909 | 4.5028 | 4.4845 | 4.5112 | 4.5062 | 4.6459 | 4.5343 | 4.6267 | 4.642 | 4.632 | 4.698 | 4.645 | 4.6378 | 4.6961 | 4.6536 | 4.6412 | 4.6657 | 4.6423 | 4.6868 | 4.634 | 4.6732 | 4.6395 | 4.6464 | 4.6715 | 4.6442 | 4.694 | 4.6762 | 4.7514 | 4.7536 | 4.5285 | 4.6083 | 4.6251 | 4.6858 | 4.6831 | 4.6465 | 4.6678 | 4.6555 | 4.6509 | 4.6788 | 4.7407 | 4.7313 | 4.715 | 4.6629 | 4.6553 | 4.6628 | 4.6896 | 4.7134 | 4.6785 | 4.669 | 4.6741 | 4.6307 | 4.5201 | 4.587 | 4.6863 | 4.733 | 4.7283 | 4.7595 | 4.7568 | 4.7239 | 4.7248 | 4.6467 | 4.7452 | 4.7268 | 4.7492 | 4.732 | 4.7282 | 4.6715 | 4.782 | 4.7707 | 4.7246 | 4.7025 | 4.7299 | 4.7106 | 4.7129 | 4.7279 | 4.7343 | 4.7662 | 4.6441
2025-07-01 | 5.305 | 5.393 | 5.3748 | 5.3724 | 5.4181 | 5.4262 | 5.4603 | 5.338 | 5.4137 | 5.38 | 5.3853 | 5.3879 | 5.3684 | 5.357 | 5.3217 | 5.3589 | 5.2883 | 5.2739 | 5.3075 | 5.3447 | 5.2503 | 5.2434 | 5.2458 | 5.2276 | 5.1943 | 5.1227 | 5.1161 | 5.1093 | 5.2776 | 5.2974 | 5.2753 | 5.2741 | 5.3513 | 5.3435 | 5.3912 | 5.3282 | 5.3892 | 5.2756 | 5.3063 | 5.291 | 5.2782 | 5.2803 | 5.3097 | 5.3137 | 4.7239 | 5.0843 | 5.3103 | 5.2976 | 5.102 | 5.2228 | 5.265 | 5.3076 | 5.2425 | 5.2813 | 5.2216 | 5.1927 | 5.2018 | 5.2382 | 5.2253 | 5.2801 | 5.2518 | 5.2192 | 5.2234 | 5.1977 | 5.202 | 5.1499 | 5.1784 | 5.1314 | 5.1664 | 5.1668 | 5.1634 | 5.1067 | 5.2016 | 5.1363 | 5.2447 | 5.1425 | 5.1923 | 5.2496 | 5.2249 | 5.1714 | 5.1463 | 5.1376 | 5.123 | 5.1434 | 5.1449 | 5.1054 | 5.1547 | 5.1185 | 5.2496 | 5.1554 | 5.2359 | 5.2751 | 5.2528 | 5.2875 | 5.2284 | 5.27 | 5.2955 | 5.268 | 5.26 | 5.2561 | 5.1638 | 5.2469 | 5.2039 | 5.2169 | 5.1844 | 5.1837 | 5.1943 | 5.158 | 5.1679 | 5.1299 | 5.2043 | 5.2265 | 5.1106 | 5.1843 | 5.1627 | 5.2236 | 5.2155 | 5.182 | 5.1713 | 5.1519 | 5.1482 | 5.151 | 5.2419 | 5.2168 | 5.2027 | 5.1679 | 5.1388 | 5.1619 | 5.2148 | 5.2566 | 5.1706 | 5.1653 | 5.2274 | 5.1871 | 5.0454 | 5.1155 | 5.3432 | 5.3752 | 5.383 | 5.4179 | 5.3882 | 5.3411 | 5.3391 | 5.2099 | 5.3489 | 5.3481 | 5.3484 | 5.3372 | 5.3525 | 5.3025 | 5.3896 | 5.3884 | 5.3455 | 5.3193 | 5.3467 | 5.3192 | 5.3246 | 5.3234 | 5.2898 | 5.35 | 5.2474
2025-07-02 | 3.0798 | 3.1263 | 3.12 | 3.1142 | 3.1528 | 3.1607 | 3.1679 | 3.106 | 3.1434 | 3.1206 | 3.1336 | 3.1223 | 3.1458 | 3.1123 | 3.1516 | 3.1617 | 3.1383 | 3.1227 | 3.1323 | 3.148 | 3.1198 | 3.093 | 3.118 | 3.1087 | 3.054 | 3.0063 | 3.0079 | 3.0059 | 3.1197 | 3.1409 | 3.1269 | 3.1146 | 3.1394 | 3.1406 | 3.1751 | 3.1338 | 3.1624 | 3.1012 | 3.1263 | 3.1038 | 3.1748 | 3.1627 | 3.193 | 3.176 | 2.9632 | 3.0736 | 3.1926 | 3.1921 | 2.9831 | 3.0456 | 3.0747 | 3.0905 | 3.0692 | 3.1029 | 3.0511 | 3.0355 | 3.0176 | 3.0406 | 3.0381 | 3.0636 | 3.0405 | 3.0333 | 2.9962 | 2.9838 | 3.0196 | 3.0016 | 3.0056 | 2.9921 | 2.9995 | 3.0107 | 2.9885 | 2.9757 | 3.0276 | 2.9887 | 3.0401 | 3.0058 | 3.0243 | 3.0551 | 3.037 | 3.0327 | 3.0095 | 3.0151 | 3.0102 | 2.9851 | 3.0091 | 2.9924 | 3.0174 | 2.9987 | 3.0669 | 3.027 | 3.0497 | 3.0713 | 3.0598 | 3.083 | 3.0496 | 3.075 | 3.0959 | 3.0814 | 3.0841 | 3.0857 | 3.0214 | 3.0764 | 3.054 | 3.0562 | 3.0509 | 3.0419 | 3.0594 | 3.0339 | 3.0485 | 3.0248 | 3.0788 | 3.0473 | 3.0173 | 3.0502 | 3.0399 | 3.0698 | 3.0769 | 3.0516 | 3.0538 | 3.0297 | 3.0393 | 3.0418 | 3.0913 | 3.0604 | 3.0944 | 3.0443 | 3.0339 | 3.0455 | 3.0463 | 3.0784 | 3.0465 | 3.032 | 3.0526 | 3.0351 | 3.0141 | 3.0254 | 3.1292 | 3.1399 | 3.1491 | 3.1531 | 3.1573 | 3.1133 | 3.1312 | 3.0757 | 3.1342 | 3.1304 | 3.1277 | 3.1237 | 3.1273 | 3.0978 | 3.1415 | 3.15 | 3.1414 | 3.1278 | 3.1381 | 3.1147 | 3.1211 | 3.1232 | 3.1162 | 3.1387 | 3.0786
2025-07-03 | 2.2189 | 2.2721 | 2.2633 | 2.2496 | 2.2893 | 2.2839 | 2.2807 | 2.1766 | 2.2634 | 2.2512 | 2.2632 | 2.2582 | 2.2704 | 2.2568 | 2.1375 | 2.2271 | 2.244 | 2.0856 | 2.2478 | 2.2617 | 2.2266 | 2.0675 | 2.2098 | 2.2153 | 2.068 | 2.0244 | 1.8772 | 1.9837 | 2.1023 | 2.1055 | 2.0973 | 2.1034 | 2.2559 | 2.2604 | 2.2782 | 2.245 | 2.261 | 2.1648 | 2.2277 | 2.1865 | 2.2568 | 2.1235 | 2.2785 | 2.1319 | 2.1709 | 2.1071 | 2.2622 | 2.2638 | 2.0513 | 2.1303 | 2.2109 | 2.2268 | 2.0378 | 2.2177 | 2.1815 | 2.0395 | 2.1008 | 2.1683 | 2.1599 | 2.1985 | 2.0535 | 2.1844 | 2.142 | 2.1457 | 2.1666 | 2.1417 | 2.0565 | 2.0684 | 2.1258 | 2.1416 | 2.1575 | 2.0126 | 2.1921 | 2.0842 | 2.2038 | 2.1666 | 2.1595 | 2.2067 | 2.1147 | 2.1527 | 2.1463 | 2.158 | 2.1453 | 2.0072 | 2.1351 | 2.0051 | 2.1402 | 1.9865 | 2.1173 | 2.1235 | 2.1464 | 2.0741 | 2.1626 | 2.1844 | 2.1279 | 2.1713 | 2.1785 | 2.1524 | 2.1075 | 2.1714 | 2.0862 | 2.1693 | 2.1565 | 2.1418 | 2.1742 | 2.1478 | 2.1804 | 2.1571 | 2.1267 | 2.1124 | 2.2105 | 2.0705 | 2.1344 | 2.1267 | 2.0936 | 2.1062 | 2.1572 | 2.1267 | 2.1246 | 2.0625 | 2.1224 | 2.1421 | 2.2031 | 2.0472 | 2.2221 | 2.0356 | 2.1437 | 2.1464 | 1.9948 | 2.1499 | 2.1313 | 2.1038 | 2.1303 | 2.1072 | 2.1059 | 2.1307 | 2.1703 | 2.192 | 2.211 | 2.141 | 2.1558 | 2.1808 | 2.103 | 2.1646 | 2.2337 | 2.2333 | 2.1047 | 2.1954 | 2.1898 | 2.1035 | 2.1979 | 2.2243 | 2.1898 | 2.1693 | 2.2827 | 2.1793 | 2.2621 | 2.2549 | 2.2154 | 2.2357 | 2.1593
2025-07-04 | 4.0985 | 4.1744 | 4.1618 | 4.1701 | 4.2057 | 4.2214 | 4.1912 | 4.1541 | 4.1891 | 4.0522 | 4.2192 | 4.2025 | 4.2347 | 4.2764 | 4.2871 | 4.2924 | 3.8097 | 3.8265 | 3.8702 | 3.8846 | 3.8282 | 3.7992 | 3.8617 | 3.8268 | 4.168 | 4.0982 | 4.1079 | 4.091 | 4.2365 | 4.3892 | 4.3972 | 4.2855 | 4.3487 | 4.3346 | 4.3428 | 4.3252 | 4.4088 | 4.3258 | 4.4048 | 4.3671 | 4.8454 | 4.8631 | 4.8814 | 4.8102 | 4.6823 | 4.5171 | 4.8275 | 4.8159 | 4.118 | 4.1798 | 4.2282 | 4.2431 | 4.1908 | 4.2897 | 4.1357 | 4.1205 | 4.1228 | 4.0698 | 4.1675 | 4.1685 | 4.0479 | 4.0977 | 4.0245 | 4.0394 | 3.9975 | 3.8627 | 3.9152 | 3.7653 | 3.8541 | 3.764 | 3.7418 | 3.6675 | 3.9442 | 3.7152 | 3.948 | 3.7567 | 3.84 | 3.9481 | 3.9107 | 3.7908 | 3.75 | 3.7202 | 3.7961 | 3.713 | 3.8329 | 3.8033 | 3.9028 | 3.8588 | 4.0986 | 3.9573 | 4.0671 | 4.089 | 4.1307 | 4.2389 | 4.2212 | 4.1747 | 4.2758 | 4.2062 | 4.1702 | 4.2218 | 4.226 | 4.2543 | 4.3342 | 4.2673 | 4.3393 | 4.2641 | 4.3191 | 4.2474 | 4.345 | 4.3305 | 4.4121 | 4.2266 | 4.1383 | 4.0702 | 4.0821 | 4.1411 | 4.1551 | 4.0725 | 4.1077 | 4.0549 | 4.0966 | 4.15 | 4.2761 | 4.1965 | 4.3193 | 4.1491 | 4.1403 | 4.151 | 4.0771 | 4.126 | 4.1776 | 4.1192 | 4.0884 | 4.0764 | 4.0402 | 4.0714 | 4.2883 | 4.2682 | 4.4444 | 4.3583 | 4.258 | 4.2727 | 4.2423 | 4.1262 | 4.5981 | 4.5606 | 4.4407 | 4.4689 | 4.4821 | 4.3083 | 4.5542 | 4.5613 | 4.3625 | 4.3851 | 3.4441 | 4.0542 | 4.5394 | 4.6153 | 4.3309 | 4.5101 | 4.1762
2025-07-05 | 5.2316 | 5.2888 | 5.2266 | 5.2077 | 5.2787 | 5.2739 | 5.327 | 5.1825 | 5.3381 | 5.2925 | 5.1955 | 5.3011 | 5.1924 | 5.2566 | 5.3891 | 5.3403 | 5.3944 | 5.3808 | 5.3969 | 5.4162 | 5.3463 | 5.3408 | 5.3955 | 5.3456 | 5.3445 | 5.2703 | 5.2117 | 5.2173 | 5.4097 | 5.4927 | 5.4943 | 5.4561 | 5.5837 | 5.5396 | 5.553 | 5.5148 | 5.5882 | 5.5108 | 5.5206 | 5.4965 | 5.5275 | 5.5056 | 5.5419 | 5.4951 | 5.3325 | 5.2492 | 5.5711 | 5.531 | 5.0285 | 5.1438 | 5.2331 | 5.3683 | 5.2154 | 5.2488 | 5.2549 | 5.2475 | 5.2447 | 5.2222 | 5.153 | 5.1946 | 5.1521 | 5.1521 | 5.2023 | 5.1785 | 5.1788 | 5.1502 | 5.2232 | 5.1685 | 5.1646 | 5.2416 | 5.169 | 5.2103 | 5.2277 | 5.2184 | 5.2873 | 5.175 | 5.2792 | 5.1987 | 5.2593 | 5.1158 | 4.6889 | 4.6527 | 4.7474 | 4.6495 | 4.7297 | 4.6783 | 4.6886 | 4.7069 | 5.3886 | 5.2497 | 5.3966 | 5.3551 | 5.3851 | 5.5196 | 5.4878 | 5.4282 | 5.6046 | 5.5255 | 5.3947 | 5.4865 | 5.3095 | 5.4712 | 5.3616 | 5.3993 | 5.3072 | 5.3633 | 5.303 | 5.3141 | 5.2676 | 5.2716 | 5.2998 | 5.3633 | 5.3834 | 5.2878 | 5.318 | 5.3967 | 5.2861 | 5.2324 | 5.2678 | 5.2757 | 5.2369 | 5.3106 | 5.373 | 5.3776 | 5.3792 | 5.368 | 5.2844 | 5.3274 | 5.3139 | 5.376 | 5.3284 | 5.2728 | 5.2946 | 5.2818 | 5.3196 | 5.3636 | 5.5199 | 5.6437 | 5.5032 | 5.6534 | 5.5351 | 5.556 | 5.5898 | 5.4232 | 5.5862 | 5.5113 | 5.5031 | 5.4856 | 5.519 | 5.4682 | 5.6426 | 5.5243 | 5.4482 | 5.4028 | 5.3995 | 5.3819 | 5.4158 | 5.5464 | 5.4351 | 5.6015 | 5.322
2025-07-06 | 5.3474 | 5.3374 | 5.2921 | 5.3103 | 5.3221 | 5.3208 | 5.3647 | 5.1875 | 5.3456 | 5.3201 | 5.1551 | 5.3253 | 5.1396 | 5.2754 | 5.2905 | 5.3001 | 5.264 | 5.2441 | 5.2579 | 5.2994 | 5.2151 | 5.1924 | 5.2495 | 5.2195 | 5.1664 | 5.3221 | 5.1216 | 5.0971 | 5.2038 | 5.2451 | 5.2406 | 5.1829 | 5.5657 | 5.5666 | 5.6498 | 5.5717 | 5.2667 | 5.1929 | 5.2122 | 5.1801 | 5.1659 | 5.147 | 5.1985 | 5.1211 | 4.9908 | 4.9019 | 5.1902 | 5.1797 | 4.9955 | 5.1012 | 5.1865 | 5.3493 | 5.1019 | 5.1803 | 5.1201 | 5.0876 | 5.2775 | 5.0782 | 5.3009 | 5.1123 | 5.1109 | 5.2995 | 5.1439 | 5.2314 | 5.1959 | 5.2762 | 5.1825 | 5.0903 | 5.0341 | 5.2619 | 5.0438 | 5.2268 | 5.1605 | 5.1309 | 5.3558 | 5.0592 | 5.3368 | 5.1327 | 5.3278 | 5.0968 | 5.2685 | 5.1061 | 5.2281 | 5.0348 | 5.2788 | 5.122 | 5.2818 | 5.3759 | 4.6966 | 4.7054 | 4.8375 | 4.629 | 4.6352 | 4.7898 | 4.7167 | 4.6331 | 5.3663 | 5.2766 | 5.1039 | 5.3562 | 4.9988 | 5.3482 | 5.1055 | 5.2711 | 5.0632 | 5.3094 | 5.0771 | 5.2314 | 5.095 | 5.2208 | 5.1435 | 5.1989 | 5.2941 | 5.118 | 5.2336 | 5.3354 | 5.0922 | 5.0255 | 5.0811 | 5.2082 | 5.0693 | 5.2922 | 5.2063 | 5.2453 | 5.2638 | 5.3687 | 5.1471 | 5.3241 | 5.2094 | 5.3358 | 5.3199 | 5.4436 | 5.3453 | 5.4837 | 5.2791 | 5.2967 | 5.2172 | 5.4927 | 5.241 | 5.4946 | 5.293 | 5.447 | 5.4324 | 5.3534 | 5.2926 | 5.206 | 5.177 | 5.239 | 5.2626 | 5.1928 | 5.4385 | 5.2719 | 5.1693 | 5.1669 | 5.1708 | 5.1109 | 5.1816 | 5.3948 | 5.1921 | 5.3981 | 5.2024
2025-07-07 | 4.4709 | 4.5626 | 4.5652 | 4.5321 | 4.6202 | 4.6057 | 4.6018 | 4.4847 | 4.5426 | 4.489 | 4.48 | 4.5269 | 4.4564 | 4.5189 | 4.5485 | 4.548 | 4.5364 | 4.4662 | 4.5263 | 4.5644 | 4.5316 | 4.474 | 4.5639 | 4.5454 | 4.4681 | 4.4494 | 4.3483 | 4.3702 | 4.5283 | 4.5308 | 4.5003 | 4.4836 | 4.4753 | 4.4706 | 4.5834 | 4.5091 | 4.529 | 4.4564 | 4.4896 | 4.4552 | 4.5205 | 4.5276 | 4.5696 | 4.5196 | 4.4112 | 4.3163 | 4.5602 | 4.5587 | 4.2587 | 4.374 | 4.3946 | 4.4881 | 4.3462 | 4.4261 | 4.3451 | 4.3154 | 4.397 | 4.329 | 4.4553 | 4.3744 | 4.3442 | 4.4397 | 4.3461 | 4.398 | 4.3391 | 4.3216 | 4.3294 | 4.2343 | 4.2695 | 4.3439 | 4.2565 | 4.3235 | 4.3432 | 4.3071 | 4.4256 | 4.2852 | 4.4197 | 4.3737 | 4.4402 | 4.3543 | 4.332 | 4.281 | 4.2854 | 4.2095 | 4.2959 | 4.212 | 4.3274 | 4.2878 | 4.3461 | 4.2877 | 4.3578 | 4.3173 | 4.345 | 4.4616 | 4.4045 | 4.3529 | 4.0236 | 3.9774 | 3.9084 | 3.9679 | 3.8179 | 3.961 | 3.858 | 3.9103 | 4.2777 | 4.3611 | 4.2942 | 4.3105 | 4.2994 | 4.3251 | 4.3538 | 4.3629 | 4.3462 | 4.2529 | 4.3046 | 4.3516 | 4.2639 | 4.2174 | 4.2376 | 4.3128 | 4.2525 | 4.3802 | 4.3464 | 4.4207 | 4.3464 | 4.3987 | 4.3233 | 4.4124 | 4.3176 | 4.3928 | 4.415 | 4.3778 | 4.3971 | 4.3711 | 4.2973 | 4.307 | 4.2915 | 4.3816 | 4.2942 | 4.3773 | 4.3519 | 4.3796 | 4.4066 | 4.372 | 4.4177 | 4.3585 | 4.3518 | 4.3199 | 4.3283 | 4.2686 | 4.3543 | 4.3504 | 4.326 | 4.3567 | 4.2355 | 4.2892 | 4.3499 | 4.4108 | 4.3255 | 4.4434 | 4.3698
2025-07-08 | 4.3752 | 4.4018 | 4.3919 | 4.3981 | 4.452 | 4.4675 | 4.4728 | 4.3573 | 4.4133 | 4.4382 | 4.3644 | 4.3748 | 4.3724 | 4.3557 | 4.3778 | 4.4114 | 4.2929 | 4.2503 | 4.2693 | 4.3203 | 4.2165 | 4.2128 | 4.1571 | 4.1674 | 4.0971 | 4.0812 | 4.0991 | 4.0712 | 4.1642 | 4.1593 | 4.1338 | 4.1379 | 4.1199 | 4.1408 | 4.2376 | 4.1586 | 4.1832 | 4.1077 | 4.1227 | 4.0912 | 3.9827 | 3.9655 | 3.9961 | 3.9652 | 3.8772 | 3.8787 | 4.0549 | 4.0364 | 4.1355 | 4.2355 | 4.2646 | 4.2871 | 4.2381 | 4.2951 | 4.1988 | 4.1593 | 4.2271 | 4.2318 | 4.2405 | 4.2749 | 4.236 | 4.2259 | 4.1824 | 4.1962 | 4.2004 | 4.1542 | 4.1813 | 4.1373 | 4.1729 | 4.1955 | 4.1403 | 4.1461 | 4.2019 | 4.1692 | 4.237 | 4.1733 | 4.2303 | 4.243 | 4.2622 | 4.2377 | 4.1685 | 4.1764 | 4.1508 | 4.1432 | 4.1538 | 4.1058 | 4.1412 | 4.1119 | 4.1903 | 4.1158 | 4.1413 | 4.1198 | 4.0596 | 4.0722 | 4.019 | 4.0494 | 4.0331 | 4.0255 | 3.9928 | 4.0103 | 3.9085 | 3.9818 | 3.9183 | 3.9245 | 3.8714 | 3.8788 | 3.8812 | 3.8555 | 3.8555 | 3.819 | 3.8884 | 3.8816 | 3.9752 | 3.9396 | 3.8581 | 3.9276 | 3.9147 | 3.9049 | 3.8669 | 3.8092 | 3.8758 | 3.8952 | 3.9204 | 3.905 | 3.9188 | 3.8727 | 3.8764 | 3.9005 | 3.9372 | 4.0081 | 3.9233 | 3.9167 | 3.993 | 4.0072 | 4.0237 | 4.0388 | 4.2361 | 4.2465 | 4.275 | 4.2708 | 4.2413 | 4.164 | 4.1739 | 4.0955 | 4.308 | 4.2898 | 4.3089 | 4.2811 | 4.2791 | 4.2188 | 4.2875 | 4.2989 | 4.3278 | 4.3097 | 4.2863 | 4.2531 | 4.2712 | 4.291 | 4.3147 | 4.3384 | 4.1395
2025-07-09 | 4.5147 | 4.6516 | 4.6689 | 4.6342 | 4.7264 | 4.7554 | 4.7557 | 4.6646 | 4.6507 | 4.5117 | 4.6718 | 4.6587 | 4.6799 | 4.6809 | 4.7198 | 4.7363 | 4.6377 | 4.5898 | 4.6044 | 4.6728 | 4.5482 | 4.5346 | 4.5752 | 4.5502 | 4.4784 | 4.4435 | 4.4456 | 4.3995 | 4.5743 | 4.5983 | 4.5619 | 4.5741 | 4.5981 | 4.5944 | 4.6496 | 4.6008 | 4.6467 | 4.5518 | 4.5485 | 4.5316 | 4.6024 | 4.6226 | 4.6401 | 4.6498 | 4.4878 | 4.4262 | 4.6418 | 4.6169 | 4.4771 | 4.5454 | 4.5929 | 4.6282 | 4.5726 | 4.6195 | 4.5295 | 4.5176 | 4.5443 | 4.5308 | 4.5682 | 4.5729 | 4.5427 | 4.5398 | 4.4784 | 4.4438 | 4.522 | 4.4785 | 4.4946 | 4.4374 | 4.4613 | 4.4744 | 4.4407 | 4.4202 | 4.4988 | 4.4367 | 4.5275 | 4.4026 | 4.4746 | 4.4785 | 4.5021 | 4.4201 | 4.4577 | 4.4178 | 4.3877 | 4.4205 | 4.4383 | 4.3979 | 4.4849 | 4.4667 | 4.5469 | 4.4924 | 4.5318 | 4.5109 | 4.4814 | 4.5298 | 4.4951 | 4.4917 | 4.5609 | 4.5359 | 4.4919 | 4.5401 | 4.4347 | 4.5434 | 4.4768 | 4.5183 | 4.392 | 4.46 | 4.3957 | 4.3858 | 4.3647 | 4.3247 | 4.3964 | 4.4068 | 4.4856 | 4.4612 | 4.4448 | 4.5109 | 4.4632 | 4.4543 | 4.4095 | 4.4206 | 4.3885 | 4.3995 | 4.4317 | 4.409 | 4.4341 | 4.4062 | 4.367 | 4.4043 | 4.4921 | 4.5267 | 4.4098 | 4.4286 | 4.4853 | 4.4711 | 4.5248 | 4.5542 | 4.5791 | 4.6822 | 4.5959 | 4.7893 | 4.6706 | 4.6509 | 4.6965 | 4.6062 | 4.464 | 4.4243 | 4.4347 | 4.4328 | 4.5131 | 4.5095 | 4.5889 | 4.4979 | 4.4633 | 4.4289 | 4.4415 | 4.4219 | 4.4225 | 4.4518 | 4.4143 | 4.4746 | 4.5203
2025-07-10 | 4.0493 | 4.084 | 4.7523 | 4.7139 | 4.8652 | 4.8963 | 4.8336 | 4.7593 | 4.7031 | 4.531 | 4.724 | 4.6925 | 4.807 | 4.7424 | 4.8896 | 4.8904 | 4.8709 | 4.8362 | 4.8752 | 4.8867 | 4.7987 | 4.7964 | 4.7747 | 4.7738 | 4.7341 | 4.6731 | 4.6405 | 4.6648 | 4.785 | 4.79 | 4.7751 | 4.7553 | 4.7776 | 4.7943 | 4.8992 | 4.8045 | 4.8239 | 4.7318 | 4.7657 | 4.7306 | 4.9248 | 4.9381 | 4.9672 | 4.9463 | 4.7966 | 4.755 | 4.9971 | 4.9734 | 4.5402 | 4.5763 | 4.6763 | 4.6794 | 4.687 | 4.7402 | 4.5935 | 4.618 | 4.5032 | 4.502 | 4.5683 | 4.5443 | 4.5073 | 4.5451 | 4.399 | 4.3882 | 4.4535 | 4.4317 | 4.4131 | 4.4206 | 4.3749 | 4.4358 | 4.3798 | 4.3766 | 4.4121 | 4.3818 | 4.4546 | 4.3706 | 4.4184 | 4.4278 | 4.426 | 4.3778 | 4.469 | 4.435 | 4.3976 | 4.4595 | 4.4694 | 4.4338 | 4.4692 | 4.4362 | 4.5811 | 4.4716 | 4.6155 | 4.6314 | 4.6596 | 4.7299 | 4.6931 | 4.6788 | 4.7511 | 4.7025 | 4.7314 | 4.7429 | 4.6577 | 4.7598 | 4.7182 | 4.7301 | 4.6791 | 4.712 | 4.6847 | 4.6734 | 4.6317 | 4.5875 | 4.6478 | 4.6892 | 4.6556 | 4.6602 | 4.6536 | 4.7086 | 4.659 | 4.6326 | 4.6494 | 4.5609 | 4.6445 | 4.6775 | 4.7434 | 4.7351 | 4.7246 | 4.6874 | 4.6741 | 4.6821 | 4.6316 | 4.6651 | 4.6612 | 4.6219 | 4.6355 | 4.6067 | 4.5664 | 4.5943 | 4.7352 | 4.799 | 4.7396 | 5.3242 | 4.8027 | 4.7405 | 4.7579 | 4.7195 | 4.7315 | 4.7203 | 4.6994 | 4.6832 | 4.6851 | 4.6487 | 4.7472 | 4.7292 | 4.7507 | 4.7206 | 4.731 | 4.7162 | 4.7161 | 4.7395 | 4.7115 | 4.7503 | 4.6642
2025-07-11 | 5.2735 | 5.3688 | 5.3184 | 5.3204 | 5.3569 | 5.4156 | 5.4764 | 5.4059 | 5.4316 | 5.2543 | 5.4134 | 5.4566 | 5.4154 | 5.4722 | 5.4236 | 5.4652 | 5.3839 | 5.3305 | 5.4206 | 5.4676 | 5.319 | 5.3271 | 5.2834 | 5.2844 | 5.2423 | 5.1995 | 5.2149 | 5.1815 | 5.288 | 5.297 | 5.2922 | 5.2619 | 5.3005 | 5.2922 | 5.4204 | 5.3334 | 5.369 | 5.2768 | 5.3064 | 5.2999 | 5.2139 | 5.1977 | 5.2731 | 5.1937 | 5.1005 | 5.0745 | 5.348 | 5.3157 | 5.2277 | 5.2747 | 5.3431 | 5.3695 | 5.3071 | 5.359 | 5.2424 | 5.2373 | 5.2227 | 5.224 | 5.2856 | 5.2921 | 5.2817 | 5.2819 | 5.2102 | 5.1875 | 5.1014 | 4.9582 | 5.0473 | 4.9178 | 5.0559 | 4.9629 | 4.9808 | 4.9133 | 5.1252 | 4.9522 | 5.1593 | 4.9458 | 5.0435 | 5.1595 | 5.1606 | 5.0729 | 4.8933 | 4.906 | 4.7529 | 4.896 | 4.8874 | 4.8442 | 4.9793 | 4.9092 | 5.0899 | 4.9948 | 5.143 | 5.1911 | 5.2013 | 5.2501 | 5.1907 | 5.2188 | 5.2756 | 5.224 | 5.1941 | 5.2208 | 5.0486 | 5.2021 | 5.0996 | 5.1553 | 5.0502 | 5.0754 | 5.0527 | 5.0115 | 4.9757 | 4.9217 | 5.0537 | 5.0467 | 5.1161 | 5.0828 | 5.1156 | 5.1654 | 5.0872 | 5.0282 | 5.046 | 4.9904 | 4.9982 | 5.0149 | 5.1069 | 5.085 | 5.0862 | 5.0508 | 5.0043 | 5.0402 | 5.0304 | 5.066 | 5.0638 | 4.9945 | 5.0439 | 5.0135 | 4.9189 | 4.94 | 5.067 | 5.1482 | 5.0933 | 5.7473 | 5.1752 | 5.2069 | 5.1736 | 5.5773 | 5.0864 | 5.0507 | 5.0445 | 5.0273 | 5.0402 | 4.9988 | 5.1101 | 5.0527 | 5.0927 | 5.0807 | 5.0882 | 5.0833 | 5.1033 | 5.1162 | 5.0754 | 5.1403 | 5.167
2025-07-12 | 3.5909 | 3.6712 | 3.6414 | 3.6077 | 3.6875 | 3.6844 | 3.7202 | 3.6527 | 3.6891 | 3.6729 | 3.6816 | 3.6616 | 3.6847 | 3.6514 | 3.7058 | 3.7083 | 3.709 | 3.6271 | 3.6795 | 3.7089 | 3.701 | 3.5718 | 3.6836 | 3.6734 | 3.6059 | 3.5388 | 3.5393 | 3.5382 | 3.6883 | 3.7404 | 3.7213 | 3.6937 | 3.7449 | 3.7249 | 3.7665 | 3.7303 | 3.771 | 3.7036 | 3.7413 | 3.6852 | 3.7582 | 3.7067 | 3.829 | 3.4107 | 3.7401 | 3.7028 | 3.8142 | 3.8275 | 3.4883 | 3.5566 | 3.5801 | 3.6227 | 3.5568 | 3.6643 | 3.5924 | 3.5715 | 3.537 | 3.5988 | 3.5553 | 3.6013 | 3.5447 | 3.553 | 3.5513 | 3.5578 | 3.5627 | 3.5233 | 3.5185 | 3.4975 | 3.5186 | 3.528 | 3.5073 | 3.2112 | 3.595 | 3.4795 | 3.6146 | 3.5216 | 3.545 | 3.6379 | 3.5047 | 3.5973 | 3.5059 | 3.5118 | 3.453 | 3.3785 | 3.5075 | 3.4446 | 3.5409 | 3.46 | 3.6377 | 3.541 | 3.6043 | 3.6484 | 3.6326 | 3.6646 | 3.6082 | 3.6373 | 3.6921 | 3.6535 | 3.6591 | 3.6591 | 3.5365 | 3.6607 | 3.6247 | 3.6263 | 3.6113 | 3.6016 | 3.5112 | 3.5967 | 3.6387 | 3.5958 | 3.6949 | 3.1898 | 3.6241 | 3.6292 | 3.5811 | 3.6345 | 3.6083 | 3.6132 | 3.6233 | 3.5386 | 3.5979 | 3.6027 | 3.6816 | 3.4675 | 3.6894 | 3.5562 | 3.5861 | 3.586 | 3.4895 | 3.7119 | 3.6458 | 3.6043 | 3.6889 | 3.6652 | 3.2285 | 0 | 3.7521 | 3.7567 | 3.7787 | 4.2229 | 3.7904 | 4.079 | 3.7428 | 4.1253 | 3.7379 | 3.7476 | 3.7136 | 3.7391 | 3.7465 | 3.6998 | 3.7451 | 3.7713 | 3.7138 | 3.7659 | 3.7751 | 3.7248 | 3.7338 | 3.7201 | 3.7487 | 3.7506 | 3.6166
2025-07-13 | 5.661 | 5.777 | 5.737 | 5.7249 | 5.805 | 5.842 | 5.8806 | 5.7568 | 5.8135 | 5.7132 | 5.7394 | 5.8064 | 5.7719 | 5.795 | 5.8341 | 5.8366 | 5.7922 | 5.75 | 5.7698 | 5.804 | 5.7239 | 5.6994 | 5.6656 | 5.6749 | 5.5894 | 5.5239 | 5.5392 | 5.5202 | 5.6915 | 5.7114 | 5.6877 | 5.6648 | 5.7225 | 5.7134 | 5.7844 | 5.7197 | 5.7808 | 5.6814 | 5.7091 | 5.6763 | 5.6448 | 5.5958 | 5.2958 | 5.2374 | 5.5407 | 5.333 | 5.7352 | 5.741 | 2.8092 | 2.6317 | 0 | 0 | 2.7754 | 2.8377 | 2.7205 | 2.7133 | 5.5918 | 5.5769 | 5.6143 | 5.6838 | 5.6626 | 5.6099 | 5.6276 | 5.6139 | 5.5043 | 5.5361 | 5.5598 | 5.5162 | 5.4699 | 5.5517 | 5.477 | 5.4883 | 5.5637 | 5.5205 | 5.6274 | 5.5353 | 5.5979 | 5.6688 | 5.667 | 5.6312 | 5.4677 | 5.5401 | 5.455 | 5.5092 | 5.5422 | 5.4902 | 5.5491 | 5.4634 | 5.6284 | 5.5195 | 5.5721 | 5.5967 | 5.5642 | 5.6154 | 5.5722 | 5.6311 | 5.745 | 5.7075 | 5.709 | 5.7481 | 5.5425 | 5.7394 | 5.6615 | 5.6902 | 5.6026 | 5.5952 | 5.5496 | 5.6147 | 5.5961 | 5.5006 | 5.697 | 5.5934 | 5.6772 | 5.6843 | 5.5706 | 5.7201 | 5.7027 | 5.6839 | 5.6651 | 5.6441 | 5.6194 | 5.6337 | 5.7297 | 5.499 | 5.7225 | 5.6219 | 5.6258 | 5.6609 | 5.6494 | 5.7715 | 5.6483 | 5.6119 | 5.7566 | 5.7135 | 4.5992 | 0 | 5.8602 | 5.9518 | 5.874 | 6.6243 | 5.9248 | 6.4319 | 5.9481 | 6.4101 | 5.9879 | 5.9948 | 5.9258 | 5.919 | 5.905 | 5.8156 | 5.9691 | 5.9468 | 5.8413 | 5.8673 | 5.9147 | 5.8573 | 5.9149 | 5.9873 | 5.8758 | 5.9945 | 5.4695
2025-07-14 | 4.8258 | 4.8768 | 4.8734 | 4.8801 | 4.918 | 4.9134 | 4.9189 | 4.8184 | 4.8885 | 4.8413 | 4.848 | 4.8769 | 4.8414 | 4.8736 | 4.4577 | 0 | 4.9056 | 4.911 | 4.9594 | 4.9686 | 4.9855 | 4.9326 | 5.0334 | 4.9924 | 4.9272 | 4.8818 | 4.7949 | 4.8367 | 5.019 | 5.0538 | 5.0552 | 5.0069 | 5.116 | 5.1116 | 5.1206 | 5.0906 | 5.103 | 5.0349 | 5.063 | 5.0192 | 4.9827 | 4.9337 | 5.0553 | 4.9606 | 4.874 | 4.8314 | 5.0331 | 5.0482 | 4.3838 | 4.4293 | 1.0143 | 1.0438 | 4.4806 | 4.5091 | 4.4885 | 4.4666 | 4.8361 | 4.8246 | 4.777 | 4.8168 | 4.7863 | 4.7767 | 4.7706 | 4.7631 | 4.6927 | 4.8546 | 4.8773 | 4.8143 | 4.7894 | 4.9011 | 4.6956 | 4.8628 | 4.8385 | 4.8625 | 4.8948 | 4.8254 | 4.8903 | 4.825 | 4.858 | 4.8021 | 4.9011 | 4.8547 | 4.7718 | 4.7878 | 4.8366 | 4.7568 | 4.8472 | 4.7827 | 4.8631 | 4.8033 | 4.8888 | 4.8652 | 4.876 | 4.9759 | 4.9317 | 4.8852 | 4.9502 | 4.8978 | 4.8528 | 4.9527 | 4.7343 | 4.9517 | 4.8559 | 4.9076 | 4.7853 | 4.8764 | 4.8056 | 4.8504 | 4.8253 | 4.7092 | 4.91 | 4.9069 | 4.9002 | 4.862 | 4.7988 | 4.9175 | 4.791 | 4.8649 | 4.7749 | 4.8354 | 4.8726 | 4.9496 | 4.9445 | 4.9375 | 4.9974 | 4.9465 | 4.9126 | 4.9793 | 4.9346 | 5.0282 | 4.9937 | 4.979 | 5.0153 | 5.0161 | 4.8622 | 4.8322 | 4.9866 | 5.1516 | 10.9368 | 12.3632 | 5.1352 | 5.5501 | 5.15 | 5.5832 | 4.9609 | 4.9681 | 4.8395 | 4.8944 | 4.9198 | 4.9129 | 5.0964 | 5.0134 | 4.8893 | 4.8861 | 4.9327 | 4.8942 | 4.9119 | 4.9791 | 4.7685 | 4.9211 | 4.8967
2025-07-15 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-16 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-17 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-18 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-19 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-21 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-24 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-25 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-26 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-27 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-28 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-29 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-07-31 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2025-08-01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Formulas:
Date = [Date, row above]+1

## Curtailment records
Sr. No | Month | Date | Plant Name | Categoty | Equipment Name | Inverter No. | From | To | Duration in MIN | Total Breakdown Hrs. | Avg POA During BD time | Lost POA | Total POA | Net POA | Loss of Capacity in KWp | Estimated PR % (Pvsyst) | Loss of Generation kWh | Remark | Current Load befor Load Sheeding (AC MW) | Load to be maintain (AC Mw)
1 | Jun | 2022-06-10 | CSPPL | Load Shedding | All Block | All inverter | 11:08 | 13:08 | 2:00 | 47:59 | 1 | 1.89 | 7 | 5.11 | 40000 | 80 | 60480 | Load Shedding from 400 kv GSS side LD massage No. 287 | 218 | 198
2 | Sept | 2022-09-01 | CSPPL | Load Shedding | Block-5 | 1 | 12:29 | 14:19 | 1:50 | 43:59 |  | 1.81 | 7.2224 | 5.4124 | 4155.14 | 84.48 | 6353.5747 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
3 | Sept | 2022-09-01 | CSPPL | Load Shedding | Block-5 | 2 | 12:29 | 14:33 | 2:04 | 49:35 |  | 2.1 | 7.2224 | 5.1224 | 4181.22 | 84.48 | 7417.8188 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
4 | Sept | 2022-09-01 | CSPPL | Load Shedding | Block-5 | 3 | 12:29 | 14:48 | 2:19 | 55:35 |  | 2.28 | 7.2224 | 4.9424 | 4155.41 | 84.48 | 8003.918 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
5 | Sept | 2022-09-02 | CSPPL | Load Shedding | Block-5 | 1 | 12:55 | 13:17 | 0:22 | 8:48 |  | 0.4 | 7.0376 | 6.6376 | 4155.14 | 84.48 | 1404.1049 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
6 | Sept | 2022-09-02 | CSPPL | Load Shedding | Block-5 | 2 | 13:00 | 13:18 | 0:18 | 7:12 |  | 0.4 | 7.0376 | 6.6376 | 4181.22 | 84.48 | 1412.9179 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
7 | Sept | 2022-09-02 | CSPPL | Load Shedding | Block-5 | 3 | 13:01 | 13:19 | 0:18 | 7:12 |  | 0.4 | 7.0376 | 6.6376 | 4155.41 | 84.48 | 1404.1961 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
8 | Sept | 2022-09-03 | CSPPL | Load Shedding | Block-5 | 1 | 11:17 | 11:24 | 0:07 | 2:48 |  | 0.12 | 7.3589 | 7.2389 | 4155.14 | 84.48 | 421.2315 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
9 | Sept | 2022-09-03 | CSPPL | Load Shedding | Block-5 | 2 | 11:17 | 11:24 | 0:07 | 2:48 |  | 0.12 | 7.3589 | 7.2389 | 4181.22 | 84.48 | 423.8754 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
10 | Sept | 2022-09-03 | CSPPL | Load Shedding | Block-5 | 3 | 11:17 | 11:24 | 0:07 | 2:48 |  | 0.12 | 7.3589 | 7.2389 | 4155.41 | 84.48 | 421.2588 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
11 | Sept | 2022-09-03 | CSPPL | Load Shedding | Block-5 | 4 | 11:17 | 11:24 | 0:07 | 2:48 |  | 0.12 | 7.3589 | 7.2389 | 4129.6 | 84.48 | 418.6423 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
12 | Sept | 2022-09-07 | CSPPL | Load Shedding | Block-5 | 1 | 11:31 | 11:45 | 0:14 | 5:36 |  | 0.25 | 7.052 | 6.802 | 4155.14 | 84.48 | 877.5656 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
13 | Sept | 2022-09-07 | CSPPL | Load Shedding | Block-5 | 2 | 13:04 | 13:13 | 0:09 | 3:36 |  | 0.16 | 7.052 | 6.892 | 4181.22 | 84.48 | 565.1671 | Load Shedding from Plant Side due to Active Power control Purpose. | 253 | 250
14 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-1_M1 | 11:40 | 12:36 | 0:56 | 22:24 |  | 0.89 | 7.0699 | 6.1799 | 4189.05 | 84.48 | 3149.6294 | Inverter manual stop for Load reducing at peak time | 256 | 250
15 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-2_M1 | 11:54 | 12:36 | 0:42 | 16:48 |  | 0.67 | 7.0699 | 6.3999 | 2203.13 | 84.48 | 1247.0068 | Inverter manual stop for Load reducing at peak time | 256 | 250
16 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-2_M2 | 11:54 | 12:36 | 0:42 | 16:48 |  | 0.67 | 7.0699 | 6.3999 | 1954.89 | 84.48 | 1106.499 | Inverter manual stop for Load reducing at peak time | 256 | 250
17 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-1_M1 | 12:58 | 13:21 | 0:23 | 9:12 |  | 0.53 | 7.0699 | 6.5399 | 2234.16 | 84.48 | 1000.3317 | Inverter manual stop for Load reducing at peak time | 256 | 250
18 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-1_M2 | 12:58 | 13:21 | 0:23 | 9:12 |  | 0.53 | 7.0699 | 6.5399 | 1954.89 | 84.48 | 875.2903 | Inverter manual stop for Load reducing at peak time | 256 | 250
19 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-2_M1 | 12:58 | 13:21 | 0:23 | 9:12 |  | 0.53 | 7.0699 | 6.5399 | 2203.13 | 84.48 | 986.4382 | Inverter manual stop for Load reducing at peak time | 256 | 250
20 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-2_M2 | 12:58 | 13:21 | 0:23 | 9:12 |  | 0.53 | 7.0699 | 6.5399 | 1954.89 | 84.48 | 875.2903 | Inverter manual stop for Load reducing at peak time | 256 | 250
21 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-3_M1 | 12:58 | 13:21 | 0:23 | 9:12 |  | 0.53 | 7.0699 | 6.5399 | 2192.4 | 84.48 | 981.6339 | Inverter manual stop for Load reducing at peak time | 256 | 250
22 | Sept | 2022-09-08 | CSPPL | Load Shedding | Blk-6 | Inv-3_M2 | 12:58 | 13:21 | 0:23 | 9:12 |  | 0.53 | 7.0699 | 6.5399 | 2442.96 | 84.48 | 1093.8207 | Inverter manual stop for Load reducing at peak time | 256 | 250
23 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-1_M1 | 12:10 | 12:14 | 0:04 | 1:36 |  | 0.07 | 6.89 | 6.82 | 1973.16 | 84.48 | 116.6848 | Inverter manual stop for Load reducing at peak time | 256 | 250
24 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-1_M2 | 12:10 | 12:14 | 0:04 | 1:36 |  | 0.07 | 6.89 | 6.82 | 2192.4 | 84.48 | 129.6498 | Inverter manual stop for Load reducing at peak time | 256 | 250
25 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-2_M1 | 12:37 | 12:56 | 0:19 | 7:36 |  | 0.3 | 6.89 | 6.59 | 1973.16 | 84.48 | 500.0777 | Inverter manual stop for Load reducing at peak time | 256 | 250
26 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-2_M2 | 12:37 | 12:56 | 0:19 | 7:36 |  | 0.3 | 6.89 | 6.59 | 2223.72 | 84.48 | 563.5796 | Inverter manual stop for Load reducing at peak time | 256 | 250
27 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-3_M1 | 12:44 | 12:58 | 0:14 | 5:36 |  | 0.24 | 6.89 | 6.65 | 2223.72 | 84.48 | 450.8637 | Inverter manual stop for Load reducing at peak time | 256 | 250
28 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-3_M2 | 12:44 | 12:58 | 0:14 | 5:36 |  | 0.24 | 6.89 | 6.65 | 1941.84 | 84.48 | 393.7119 | Inverter manual stop for Load reducing at peak time | 256 | 250
29 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-4_M1 | 13:07 | 13:32 | 0:25 | 10:00 |  | 0.42 | 6.89 | 6.47 | 2322.9 | 84.48 | 824.2021 | Inverter manual stop for Load reducing at peak time | 256 | 250
30 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-8 | Inv-4_M2 | 13:07 | 13:32 | 0:25 | 10:00 |  | 0.42 | 6.89 | 6.47 | 2061.9 | 84.48 | 731.5951 | Inverter manual stop for Load reducing at peak time | 256 | 250
31 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-1 | Inv-2_M1 | 12:19 | 12:25 | 0:06 | 2:24 |  | 0.11 | 6.89 | 6.78 | 2090.61 | 84.48 | 194.2762 | Inverter manual stop for Load reducing at peak time | 256 | 250
32 | Sept | 2022-09-09 | CSPPL | Load Shedding | Blk-1 | Inv-2_M2 | 12:19 | 12:25 | 0:06 | 2:24 |  | 0.11 | 6.89 | 6.78 | 2090.61 | 84.48 | 194.2762 | Inverter manual stop for Load reducing at peak time | 256 | 250
33 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-1_M1 | 12:15 | 12:22 | 0:07 | 2:48 |  | 0.12 | 6.08 | 5.96 | 2102.065 | 84.48 | 213.0989 | Inverter manual stop for Load reducing at peak time | 256 | 250
34 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-1_M2 | 12:15 | 12:22 | 0:07 | 2:48 |  | 0.12 | 6.08 | 5.96 | 2007.235 | 84.48 | 203.4855 | Inverter manual stop for Load reducing at peak time | 256 | 250
35 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-2_M1 | 12:36 | 12:40 | 0:04 | 1:36 |  | 0.07 | 6.08 | 6.01 | 2102.065 | 84.48 | 124.3077 | Inverter manual stop for Load reducing at peak time | 256 | 250
36 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-2_M2 | 12:36 | 12:40 | 0:04 | 1:36 |  | 0.07 | 6.08 | 6.01 | 2212.7 | 84.48 | 130.8502 | Inverter manual stop for Load reducing at peak time | 256 | 250
37 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-3_M1 | 12:38 | 12:44 | 0:06 | 2:24 |  | 0.07 | 6.08 | 6.01 | 2275.92 | 84.48 | 134.5888 | Inverter manual stop for Load reducing at peak time | 256 | 250
38 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-3_M2 | 12:38 | 12:44 | 0:06 | 2:24 |  | 0.07 | 6.08 | 6.01 | 1991.43 | 84.48 | 117.7652 | Inverter manual stop for Load reducing at peak time | 256 | 250
39 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-4_M1 | 12:42 | 12:46 | 0:04 | 1:36 |  | 0.07 | 6.08 | 6.01 | 2244.31 | 84.48 | 132.7195 | Inverter manual stop for Load reducing at peak time | 256 | 250
40 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-9 | Inv-4_M2 | 12:42 | 12:46 | 0:04 | 1:36 |  | 0.07 | 6.08 | 6.01 | 1944.015 | 84.48 | 114.9613 | Inverter manual stop for Load reducing at peak time | 256 | 250
41 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-1 | Inv-2_M1 | 12:24 | 12:28 | 0:04 | 1:36 |  | 0.07 | 6.08 | 6.01 | 2090.61 | 84.48 | 123.6303 | Inverter manual stop for Load reducing at peak time | 256 | 250
42 | Sept | 2022-09-10 | CSPPL | Load Shedding | Blk-1 | Inv-2_M2 | 12:24 | 12:28 | 0:04 | 1:36 |  | 0.07 | 6.08 | 6.01 | 2090.61 | 84.48 | 123.6303 | Inverter manual stop for Load reducing at peak time | 256 | 250
43 | Sept | 2022-09-11 | CSPPL | Load Shedding | Blk-11 | Inv-1_M1 | 13:10 | 13:18 | 0:08 | 3:12 |  | 0.14 | 5.72 | 5.58 | 2023.04 | 84.48 | 239.269 | Inverter manual stop for Load reducing at peak time | 256 | 250
44 | Sept | 2022-09-11 | CSPPL | Load Shedding | Blk-11 | Inv-1_M2 | 13:10 | 13:18 | 0:08 | 3:12 |  | 0.14 | 5.72 | 5.58 | 2228.505 | 84.48 | 263.5697 | Inverter manual stop for Load reducing at peak time | 256 | 250
45 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-1 | Inv-1_M1 | 12:21 | 12:23 | 0:02 | 0:48 |  | 0.02 | 6.38 | 6.36 | 1884.13 | 84.48 | 31.8343 | Inverter manual stop for Load reducing at peak time | 256 | 250
46 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-1 | Inv-1_M2 | 12:21 | 12:23 | 0:02 | 0:48 |  | 0.02 | 6.38 | 6.36 | 2090.61 | 84.48 | 35.3229 | Inverter manual stop for Load reducing at peak time | 256 | 250
47 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-1_M1 | 12:21 | 12:32 | 0:11 | 4:24 |  | 0.11 | 6.38 | 6.27 | 1973.16 | 84.48 | 183.3618 | Inverter manual stop for Load reducing at peak time | 256 | 250
48 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-1_M2 | 12:21 | 12:32 | 0:11 | 4:24 |  | 0.11 | 6.38 | 6.27 | 2192.4 | 84.48 | 203.7353 | Inverter manual stop for Load reducing at peak time | 256 | 250
49 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-2_M1 | 12:22 | 12:36 | 0:14 | 5:36 |  | 0.25 | 6.38 | 6.13 | 1973.16 | 84.48 | 416.7314 | Inverter manual stop for Load reducing at peak time | 256 | 250
50 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-2_M2 | 12:22 | 12:36 | 0:14 | 5:36 |  | 0.25 | 6.38 | 6.13 | 2223.72 | 84.48 | 469.6497 | Inverter manual stop for Load reducing at peak time | 256 | 250
51 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-3_M1 | 12:23 | 12:35 | 0:12 | 4:48 |  | 0.21 | 6.38 | 6.17 | 2223.72 | 84.48 | 394.5057 | Inverter manual stop for Load reducing at peak time | 256 | 250
52 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-3_M2 | 12:23 | 12:35 | 0:12 | 4:48 |  | 0.21 | 6.38 | 6.17 | 1941.84 | 84.48 | 344.498 | Inverter manual stop for Load reducing at peak time | 256 | 250
53 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-4_M1 | 12:53 | 12:56 | 0:03 | 1:12 |  | 0.06 | 6.38 | 6.32 | 2322.9 | 84.48 | 117.7432 | Inverter manual stop for Load reducing at peak time | 256 | 250
54 | Sept | 2022-09-12 | CSPPL | Load Shedding | Blk-8 | Inv-4_M2 | 12:54 | 12:57 | 0:03 | 1:12 |  | 0.06 | 6.38 | 6.32 | 2061.9 | 84.48 | 104.5136 | Inverter manual stop for Load reducing at peak time | 256 | 250
55 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-1_M1 | 12:18 | 12:24 | 0:06 | 2:24 |  | 0.07 | 6.12 | 6.05 | 2004.48 | 84.48 | 118.5369 | Inverter manual stop for Load reducing at peak time | 256 | 250
56 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-1_M2 | 12:18 | 12:24 | 0:06 | 2:24 |  | 0.07 | 6.12 | 6.05 | 2161.08 | 84.48 | 127.7976 | Inverter manual stop for Load reducing at peak time | 256 | 250
57 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-2_M1 | 12:18 | 12:24 | 0:06 | 2:24 |  | 0.07 | 6.12 | 6.05 | 1973.16 | 84.48 | 116.6848 | Inverter manual stop for Load reducing at peak time | 256 | 250
58 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-2_M2 | 12:18 | 12:24 | 0:06 | 2:24 |  | 0.07 | 6.12 | 6.05 | 2255.04 | 84.48 | 133.354 | Inverter manual stop for Load reducing at peak time | 256 | 250
59 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-3_M1 | 12:33 | 12:40 | 0:07 | 2:48 |  | 0.09 | 6.12 | 6.03 | 1973.16 | 84.48 | 150.0233 | Inverter manual stop for Load reducing at peak time | 256 | 250
60 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-3_M2 | 12:33 | 12:40 | 0:07 | 2:48 |  | 0.09 | 6.12 | 6.03 | 2255.04 | 84.48 | 171.4552 | Inverter manual stop for Load reducing at peak time | 256 | 250
61 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-4_M1 | 12:33 | 12:37 | 0:04 | 1:36 |  | 0.06 | 6.12 | 6.06 | 1973.16 | 84.48 | 100.0155 | Inverter manual stop for Load reducing at peak time | 256 | 250
62 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-10 | Inv-4_M2 | 12:33 | 12:37 | 0:04 | 1:36 |  | 0.06 | 6.12 | 6.06 | 2192.4 | 84.48 | 111.1284 | Inverter manual stop for Load reducing at peak time | 256 | 250
63 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-11 | Inv-1_M1 | 12:35 | 12:40 | 0:05 | 2:00 |  | 0.07 | 6.12 | 6.05 | 2023.04 | 84.48 | 119.6345 | Inverter manual stop for Load reducing at peak time | 256 | 250
64 | Sept | 2022-09-13 | CSPPL | Load Shedding | Blk-11 | Inv-1_M2 | 12:35 | 12:40 | 0:05 | 2:00 |  | 0.07 | 6.12 | 6.05 | 2228.505 | 84.48 | 131.7849 | Inverter manual stop for Load reducing at peak time | 256 | 250
65 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-1_M1 | 11:02 | 11:09 | 0:07 | 2:48 |  | 0.14652 | 6.45 | 6.3035 | 2023.04 | 84.48 | 250.4199 | Inverter manual stop for Load reducing at peak time | 256 | 250
66 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-1_M2 | 11:02 | 11:09 | 0:07 | 2:48 |  | 0.14652 | 6.45 | 6.3035 | 2228.505 | 84.48 | 275.8532 | Inverter manual stop for Load reducing at peak time | 256 | 250
67 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-2_M1 | 11:03 | 11:11 | 0:08 | 3:12 |  | 0.17831 | 6.45 | 6.2717 | 2054.65 | 84.48 | 309.5092 | Inverter manual stop for Load reducing at peak time | 256 | 250
68 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-2_M2 | 11:03 | 11:11 | 0:08 | 3:12 |  | 0.17831 | 6.45 | 6.2717 | 2275.92 | 84.48 | 342.8409 | Inverter manual stop for Load reducing at peak time | 256 | 250
69 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-3_M1 | 11:05 | 11:12 | 0:07 | 2:48 |  | 0.12889 | 6.45 | 6.3211 | 2023.04 | 84.48 | 220.2789 | Inverter manual stop for Load reducing at peak time | 256 | 250
70 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-3_M2 | 11:05 | 11:12 | 0:07 | 2:48 |  | 0.12889 | 6.45 | 6.3211 | 2133.675 | 84.48 | 232.3254 | Inverter manual stop for Load reducing at peak time | 256 | 250
71 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-4_M1 | 11:33 | 11:45 | 0:12 | 4:48 |  | 0.23231 | 6.45 | 6.2177 | 2023.04 | 84.48 | 397.0244 | Inverter manual stop for Load reducing at peak time | 256 | 250
72 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-11 | Inv-4_M2 | 11:33 | 11:45 | 0:12 | 4:48 |  | 0.23231 | 6.45 | 6.2177 | 1754.355 | 84.48 | 344.2946 | Inverter manual stop for Load reducing at peak time | 256 | 250
73 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-1_M1 | 11:35 | 11:43 | 0:08 | 3:12 |  | 0.16475 | 6.45 | 6.2852 | 2302.02 | 84.48 | 320.4012 | Inverter manual stop for Load reducing at peak time | 256 | 250
74 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-1_M1 | 11:35 | 11:43 | 0:08 | 3:12 |  | 0.16475 | 6.45 | 6.2852 | 2145.42 | 84.48 | 298.6052 | Inverter manual stop for Load reducing at peak time | 256 | 250
75 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-2_M1 | 11:35 | 11:43 | 0:08 | 3:12 |  | 0.16475 | 6.45 | 6.2852 | 1910.52 | 84.48 | 265.9112 | Inverter manual stop for Load reducing at peak time | 256 | 250
76 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-2_M2 | 11:35 | 11:43 | 0:08 | 3:12 |  | 0.16475 | 6.45 | 6.2852 | 2192.4 | 84.48 | 305.144 | Inverter manual stop for Load reducing at peak time | 256 | 250
77 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-3_M1 | 11:36 | 11:44 | 0:08 | 3:12 |  | 0.16475 | 6.45 | 6.2852 | 2192.4 | 84.48 | 305.144 | Inverter manual stop for Load reducing at peak time | 256 | 250
78 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-3_M2 | 11:36 | 11:44 | 0:08 | 3:12 |  | 0.16475 | 6.45 | 6.2852 | 2004.48 | 84.48 | 278.9888 | Inverter manual stop for Load reducing at peak time | 256 | 250
79 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-4_M1 | 12:32 | 12:35 | 0:03 | 1:12 |  | 0.06389 | 6.45 | 6.3861 | 2004.48 | 84.48 | 108.1896 | Inverter manual stop for Load reducing at peak time | 256 | 250
80 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-4_M2 | 12:32 | 12:35 | 0:03 | 1:12 |  | 0.06389 | 6.45 | 6.3861 | 2223.72 | 84.48 | 120.0228 | Inverter manual stop for Load reducing at peak time | 256 | 250
81 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-2_M1 | 12:04 | 12:07 | 0:03 | 1:12 |  | 0.063414 | 6.45 | 6.3866 | 1910.52 | 84.48 | 102.3506 | Inverter manual stop for Load reducing at peak time | 256 | 250
82 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-2_M2 | 12:04 | 12:07 | 0:03 | 1:12 |  | 0.063414 | 6.45 | 6.3866 | 2192.4 | 84.48 | 117.4515 | Inverter manual stop for Load reducing at peak time | 256 | 250
83 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-3_M1 | 12:04 | 12:20 | 0:16 | 6:24 |  | 0.063414 | 6.45 | 6.3866 | 2192.4 | 84.48 | 117.4515 | Inverter manual stop for Load reducing at peak time | 256 | 250
84 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-12 | Inv-3_M2 | 12:04 | 12:20 | 0:16 | 6:24 |  | 0.063414 | 6.45 | 6.3866 | 2004.48 | 84.48 | 107.3842 | Inverter manual stop for Load reducing at peak time | 256 | 250
85 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-1_M1 | 12:18 | 12:33 | 0:15 | 6:00 |  | 0.063414 | 6.45 | 6.3866 | 2004.48 | 84.48 | 107.3842 | Inverter manual stop for Load reducing at peak time | 256 | 250
86 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-1_M2 | 12:18 | 12:33 | 0:15 | 6:00 |  | 0.063414 | 6.45 | 6.3866 | 2004.48 | 84.48 | 107.3842 | Inverter manual stop for Load reducing at peak time | 256 | 250
87 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-2_M1 | 12:18 | 12:33 | 0:15 | 6:00 |  | 0.047746 | 6.45 | 6.4023 | 2239.38 | 84.48 | 90.3265 | Inverter manual stop for Load reducing at peak time | 256 | 250
88 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-2_M2 | 12:18 | 12:33 | 0:15 | 6:00 |  | 0.047746 | 6.45 | 6.4023 | 1941.84 | 84.48 | 78.3251 | Inverter manual stop for Load reducing at peak time | 256 | 250
89 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-3_M1 | 12:32 | 12:34 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2255.04 | 84.48 | 90.9581 | Inverter manual stop for Load reducing at peak time | 256 | 250
90 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-3_M2 | 12:32 | 12:34 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 1941.84 | 84.48 | 78.3251 | Inverter manual stop for Load reducing at peak time | 256 | 250
91 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-4_M1 | 12:41 | 12:43 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2192.4 | 84.48 | 88.4315 | Inverter manual stop for Load reducing at peak time | 256 | 250
92 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-13 | Inv-4_M2 | 12:41 | 12:43 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2004.48 | 84.48 | 80.8517 | Inverter manual stop for Load reducing at peak time | 256 | 250
93 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-1_M1 | 12:42 | 12:45 | 0:03 | 1:12 |  | 0.069013 | 6.45 | 6.381 | 2223.72 | 84.48 | 129.6476 | Inverter manual stop for Load reducing at peak time | 256 | 250
94 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-1_M2 | 12:42 | 12:45 | 0:03 | 1:12 |  | 0.069013 | 6.45 | 6.381 | 1910.52 | 84.48 | 111.3874 | Inverter manual stop for Load reducing at peak time | 256 | 250
95 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-2_M1 | 12:44 | 12:46 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2223.72 | 84.48 | 89.6948 | Inverter manual stop for Load reducing at peak time | 256 | 250
96 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-2_M2 | 12:44 | 12:46 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2004.48 | 84.48 | 80.8517 | Inverter manual stop for Load reducing at peak time | 256 | 250
97 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-3_M1 | 12:50 | 12:52 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2192.4 | 84.48 | 88.4315 | Inverter manual stop for Load reducing at peak time | 256 | 250
98 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-3_M2 | 12:50 | 12:52 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2004.48 | 84.48 | 80.8517 | Inverter manual stop for Load reducing at peak time | 256 | 250
99 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-4_M1 | 12:55 | 13:01 | 0:06 | 2:24 |  | 0.10129 | 6.45 | 6.3487 | 2192.4 | 84.48 | 187.6105 | Inverter manual stop for Load reducing at peak time | 256 | 250
100 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-14 | Inv-4_M2 | 12:55 | 13:01 | 0:06 | 2:24 |  | 0.10129 | 6.45 | 6.3487 | 2004.48 | 84.48 | 171.5296 | Inverter manual stop for Load reducing at peak time | 256 | 250
101 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-15 | Inv-1_M1 | 12:59 | 13:01 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 1973.16 | 84.48 | 79.5884 | Inverter manual stop for Load reducing at peak time | 256 | 250
102 | Sept | 2022-09-14 | CSPPL | Load Shedding | Blk-15 | Inv-1_M2 | 12:59 | 13:01 | 0:02 | 0:48 |  | 0.047746 | 6.45 | 6.4023 | 2192.4 | 84.48 | 88.4315 | Inverter manual stop for Load reducing at peak time | 256 | 250
103 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-15 | Inv-2_M1 | 13:06 | 13:12 | 0:06 | 2:24 |  | 0.1125 | 6.47 | 6.3575 | 1973.16 | 84.48 | 187.5239 | Inverter manual stop for Load reducing at peak time | 256 | 250
104 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-15 | Inv-2_M2 | 13:06 | 13:12 | 0:06 | 2:24 |  | 0.1125 | 6.47 | 6.3575 | 2223.72 | 84.48 | 211.3364 | Inverter manual stop for Load reducing at peak time | 256 | 250
105 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-15 | Inv-3_M1 | 13:08 | 13:14 | 0:06 | 2:24 |  | 0.11348 | 6.47 | 6.3565 | 1973.16 | 84.48 | 189.1633 | Inverter manual stop for Load reducing at peak time | 256 | 250
106 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-15 | Inv-3_M2 | 13:08 | 13:14 | 0:06 | 2:24 |  | 0.11348 | 6.47 | 6.3565 | 2192.4 | 84.48 | 210.1814 | Inverter manual stop for Load reducing at peak time | 256 | 250
107 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-1 | Inv-4_M1 | 13:27 | 13:30 | 0:03 | 1:12 |  | 0.064171 | 6.47 | 6.4058 | 2090.61 | 84.48 | 113.3359 | Inverter manual stop for Load reducing at peak time | 256 | 250
108 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-1 | Inv-4_M2 | 13:27 | 13:30 | 0:03 | 1:12 |  | 0.064171 | 6.47 | 6.4058 | 2193.85 | 84.48 | 118.9328 | Inverter manual stop for Load reducing at peak time | 256 | 250
109 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-16 | Inv-1_M1 | 13:28 | 13:36 | 0:08 | 3:12 |  | 0.1411 | 6.47 | 6.3289 | 2223.72 | 84.48 | 265.0705 | Inverter manual stop for Load reducing at peak time | 256 | 250
110 | Sept | 2022-09-15 | CSPPL | Load Shedding | Blk-16 | Inv-2_M1 | 13:28 | 13:36 | 0:08 | 3:12 |  | 0.1411 | 6.47 | 6.3289 | 1941.84 | 84.48 | 231.47 | Inverter manual stop for Load reducing at peak time | 256 | 250
111 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-16 | Inv-2_M1 | 11:28 | 11:38 | 0:10 | 4:00 |  | 0.17162 | 6.9712 | 6.7996 | 2161.08 | 84.48 | 313.3163 | Inverter manual stop for Load reducing at peak time | 256 | 250
112 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-16 | Inv-2_M2 | 11:28 | 11:38 | 0:10 | 4:00 |  | 0.17162 | 6.9712 | 6.7996 | 1973.16 | 84.48 | 286.0714 | Inverter manual stop for Load reducing at peak time | 256 | 250
113 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-16 | Inv-3_M1 | 11:38 | 11:47 | 0:09 | 3:36 |  | 0.15838 | 6.9712 | 6.8128 | 2161.08 | 84.48 | 289.1539 | Inverter manual stop for Load reducing at peak time | 256 | 250
114 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-16 | Inv-3_M2 | 11:38 | 11:47 | 0:09 | 3:36 |  | 0.15838 | 6.9712 | 6.8128 | 1910.52 | 84.48 | 255.6288 | Inverter manual stop for Load reducing at peak time | 256 | 250
115 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-16 | Inv-4_M1 | 11:41 | 11:47 | 0:06 | 2:24 |  | 0.11114 | 6.9712 | 6.86 | 2161.08 | 84.48 | 202.8996 | Inverter manual stop for Load reducing at peak time | 256 | 250
116 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-16 | Inv-4_M2 | 11:41 | 11:47 | 0:06 | 2:24 |  | 0.11114 | 6.9712 | 6.86 | 1941.84 | 84.48 | 182.3155 | Inverter manual stop for Load reducing at peak time | 256 | 250
117 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-1_M1 | 11:48 | 11:52 | 0:04 | 1:36 |  | 0.079867 | 6.9712 | 6.8913 | 2004.48 | 84.48 | 135.2464 | Inverter manual stop for Load reducing at peak time | 256 | 250
118 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-1_M2 | 11:48 | 11:52 | 0:04 | 1:36 |  | 0.079867 | 6.9712 | 6.8913 | 2004.48 | 84.48 | 135.2464 | Inverter manual stop for Load reducing at peak time | 256 | 250
119 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-2_M1 | 11:48 | 11:52 | 0:04 | 1:36 |  | 0.079867 | 6.9712 | 6.8913 | 2004.48 | 84.48 | 135.2464 | Inverter manual stop for Load reducing at peak time | 256 | 250
120 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-2_M2 | 11:48 | 11:52 | 0:04 | 1:36 |  | 0.079867 | 6.9712 | 6.8913 | 1722.6 | 84.48 | 116.2274 | Inverter manual stop for Load reducing at peak time | 256 | 250
121 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-3_M1 | 12:22 | 12:40 | 0:18 | 7:12 |  | 0.30915 | 6.9712 | 6.662 | 1973.16 | 84.48 | 515.3291 | Inverter manual stop for Load reducing at peak time | 256 | 250
122 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-3_M2 | 12:22 | 12:40 | 0:18 | 7:12 |  | 0.30915 | 6.9712 | 6.662 | 1753.92 | 84.48 | 458.0703 | Inverter manual stop for Load reducing at peak time | 256 | 250
123 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-4_M1 | 12:22 | 12:41 | 0:19 | 7:36 |  | 0.32549 | 6.9712 | 6.6457 | 2004.48 | 84.48 | 551.1801 | Inverter manual stop for Load reducing at peak time | 256 | 250
124 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-17 | Inv-4_M2 | 12:22 | 12:41 | 0:19 | 7:36 |  | 0.32549 | 6.9712 | 6.6457 | 2004.48 | 84.48 | 551.1801 | Inverter manual stop for Load reducing at peak time | 256 | 250
125 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-1_M1 | 12:39 | 12:46 | 0:07 | 2:48 |  | 0.13069 | 6.9712 | 6.8405 | 2255.04 | 84.48 | 248.9772 | Inverter manual stop for Load reducing at peak time | 256 | 250
126 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-1_M2 | 12:39 | 12:46 | 0:07 | 2:48 |  | 0.13069 | 6.9712 | 6.8405 | 1941.84 | 84.48 | 214.3971 | Inverter manual stop for Load reducing at peak time | 256 | 250
127 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-2_M1 | 12:41 | 12:46 | 0:05 | 2:00 |  | 0.11437 | 6.9712 | 6.8568 | 2255.04 | 84.48 | 217.8747 | Inverter manual stop for Load reducing at peak time | 256 | 250
128 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-2_M2 | 12:41 | 12:46 | 0:05 | 2:00 |  | 0.11437 | 6.9712 | 6.8568 | 1973.16 | 84.48 | 190.6403 | Inverter manual stop for Load reducing at peak time | 256 | 250
129 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-3_M1 | 13:12 | 13:28 | 0:16 | 6:24 |  | 0.27343 | 6.9712 | 6.6977 | 2223.72 | 84.48 | 513.6668 | Inverter manual stop for Load reducing at peak time | 256 | 250
130 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-3_M2 | 13:12 | 13:28 | 0:16 | 6:24 |  | 0.27343 | 6.9712 | 6.6977 | 1973.16 | 84.48 | 455.7888 | Inverter manual stop for Load reducing at peak time | 256 | 250
131 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-4_M1 | 13:12 | 13:38 | 0:26 | 10:24 |  | 0.43189 | 6.9712 | 6.5393 | 2004.48 | 84.48 | 731.3537 | Inverter manual stop for Load reducing at peak time | 256 | 250
132 | Sept | 2022-09-16 | CSPPL | Load Shedding | Blk-18 | Inv-4_M2 | 13:12 | 13:38 | 0:26 | 10:24 |  | 0.43189 | 6.9712 | 6.5393 | 2004.48 | 84.48 | 731.3537 | Inverter manual stop for Load reducing at peak time | 256 | 250
133 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-1_M1 | 11:07 | 11:26 | 0:19 | 7:36 |  | 0.30569 | 6.9425 | 6.6368 | 2161.08 | 84.48 | 558.085 | Inverter manual stop for Load reducing at peak time | 256 | 250
134 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-1_M2 | 11:07 | 11:26 | 0:19 | 7:36 |  | 0.30569 | 6.9425 | 6.6368 | 2255.04 | 84.48 | 582.3496 | Inverter manual stop for Load reducing at peak time | 256 | 250
135 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-2_M1 | 11:24 | 11:48 | 0:24 | 9:36 |  | 0.39293 | 6.9425 | 6.5496 | 2223.72 | 84.48 | 738.1656 | Inverter manual stop for Load reducing at peak time | 256 | 250
136 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-2_M2 | 11:24 | 11:48 | 0:24 | 9:36 |  | 0.39293 | 6.9425 | 6.5496 | 2223.72 | 84.48 | 738.1656 | Inverter manual stop for Load reducing at peak time | 256 | 250
137 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-3_M1 | 11:25 | 11:43 | 0:18 | 7:12 |  | 0.31392 | 6.9425 | 6.6286 | 2223.72 | 84.48 | 589.7284 | Inverter manual stop for Load reducing at peak time | 256 | 250
138 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-3_M2 | 11:25 | 11:43 | 0:18 | 7:12 |  | 0.31392 | 6.9425 | 6.6286 | 2255.04 | 84.48 | 598.0344 | Inverter manual stop for Load reducing at peak time | 256 | 250
139 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-4_M1 | 11:43 | 12:02 | 0:19 | 7:36 |  | 0.322 | 6.9425 | 6.6205 | 2004.48 | 84.48 | 545.275 | Inverter manual stop for Load reducing at peak time | 256 | 250
140 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-19 | Inv-4_M2 | 11:43 | 12:02 | 0:19 | 7:36 |  | 0.322 | 6.9425 | 6.6205 | 2223.72 | 84.48 | 604.9144 | Inverter manual stop for Load reducing at peak time | 256 | 250
141 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-1_M1 | 11:46 | 12:16 | 0:30 | 12:00 |  | 0.50428 | 6.9425 | 6.4382 | 2255.04 | 84.48 | 960.6889 | Inverter manual stop for Load reducing at peak time | 256 | 250
142 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-1_M2 | 11:46 | 12:16 | 0:30 | 12:00 |  | 0.50428 | 6.9425 | 6.4382 | 2255.04 | 84.48 | 960.6889 | Inverter manual stop for Load reducing at peak time | 256 | 250
143 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-2_M1 | 11:47 | 12:23 | 0:36 | 14:24 |  | 0.60271 | 6.9425 | 6.3398 | 2223.72 | 84.48 | 1132.2485 | Inverter manual stop for Load reducing at peak time | 256 | 250
144 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-2_M2 | 11:47 | 12:23 | 0:36 | 14:24 |  | 0.60271 | 6.9425 | 6.3398 | 2161.08 | 84.48 | 1100.3541 | Inverter manual stop for Load reducing at peak time | 256 | 250
145 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-3_M1 | 11:56 | 12:35 | 0:39 | 15:36 |  | 0.65731 | 6.9425 | 6.2852 | 2223.72 | 84.48 | 1234.8134 | Inverter manual stop for Load reducing at peak time | 256 | 250
146 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-3_M2 | 11:56 | 12:35 | 0:39 | 15:36 |  | 0.65731 | 6.9425 | 6.2852 | 1816.56 | 84.48 | 1008.7208 | Inverter manual stop for Load reducing at peak time | 256 | 250
147 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-4_M1 | 12:02 | 12:35 | 0:33 | 13:12 |  | 0.55973 | 6.9425 | 6.3828 | 2176.74 | 84.48 | 1029.2939 | Inverter manual stop for Load reducing at peak time | 256 | 250
148 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-20 | Inv-4_M2 | 12:02 | 12:35 | 0:33 | 13:12 |  | 0.55973 | 6.9425 | 6.3828 | 2004.48 | 84.48 | 947.839 | Inverter manual stop for Load reducing at peak time | 256 | 250
149 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-1_M1 | 12:18 | 12:55 | 0:37 | 14:48 |  | 0.62784 | 6.9425 | 6.3147 | 2064.8 | 84.48 | 1095.1641 | Inverter manual stop for Load reducing at peak time | 256 | 250
150 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-1_M2 | 12:18 | 12:55 | 0:37 | 14:48 |  | 0.62784 | 6.9425 | 6.3147 | 2142.23 | 84.48 | 1136.2328 | Inverter manual stop for Load reducing at peak time | 256 | 250
151 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-2_M1 | 12:24 | 13:04 | 0:40 | 16:00 |  | 0.67714 | 6.9425 | 6.2654 | 2064.8 | 84.48 | 1181.1616 | Inverter manual stop for Load reducing at peak time | 256 | 250
152 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-2_M2 | 12:24 | 13:04 | 0:40 | 16:00 |  | 0.67714 | 6.9425 | 6.2654 | 2090.61 | 84.48 | 1195.9261 | Inverter manual stop for Load reducing at peak time | 256 | 250
153 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-3_M1 | 12:34 | 13:11 | 0:37 | 14:48 |  | 0.62645 | 6.9425 | 6.3161 | 2090.61 | 84.48 | 1106.4084 | Inverter manual stop for Load reducing at peak time | 256 | 250
154 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-3_M2 | 12:34 | 13:11 | 0:37 | 14:48 |  | 0.62645 | 6.9425 | 6.3161 | 2077.705 | 84.48 | 1099.5787 | Inverter manual stop for Load reducing at peak time | 256 | 250
155 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-4_M1 | 12:38 | 13:18 | 0:40 | 16:00 |  | 0.67569 | 6.9425 | 6.2668 | 2090.61 | 84.48 | 1193.3743 | Inverter manual stop for Load reducing at peak time | 256 | 250
156 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-2 | Inv-4_M2 | 12:38 | 13:18 | 0:40 | 16:00 |  | 0.67569 | 6.9425 | 6.2668 | 2064.8 | 84.48 | 1178.6413 | Inverter manual stop for Load reducing at peak time | 256 | 250
157 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-1_M1 | 12:56 | 13:32 | 0:36 | 14:24 |  | 0.60683 | 6.9425 | 6.3357 | 2064.8 | 84.48 | 1058.5131 | Inverter manual stop for Load reducing at peak time | 256 | 250
158 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-1_M2 | 12:56 | 13:32 | 0:36 | 14:24 |  | 0.60683 | 6.9425 | 6.3357 | 2090.61 | 84.48 | 1071.7445 | Inverter manual stop for Load reducing at peak time | 256 | 250
159 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-2_M1 | 13:06 | 13:45 | 0:39 | 15:36 |  | 0.65186 | 6.9425 | 6.2907 | 2090.61 | 84.48 | 1151.2787 | Inverter manual stop for Load reducing at peak time | 256 | 250
160 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-2_M2 | 13:06 | 13:45 | 0:39 | 15:36 |  | 0.65186 | 6.9425 | 6.2907 | 2090.61 | 84.48 | 1151.2787 | Inverter manual stop for Load reducing at peak time | 256 | 250
161 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-3_M1 | 13:11 | 13:49 | 0:38 | 15:12 |  | 0.63315 | 6.9425 | 6.3094 | 2114.1 | 84.48 | 1130.7931 | Inverter manual stop for Load reducing at peak time | 256 | 250
162 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-3_M2 | 13:11 | 13:49 | 0:38 | 15:12 |  | 0.63315 | 6.9425 | 6.3094 | 2088 | 84.48 | 1116.8327 | Inverter manual stop for Load reducing at peak time | 256 | 250
163 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-4_M1 | 13:19 | 13:49 | 0:30 | 12:00 |  | 0.50124 | 6.9425 | 6.4413 | 2114.1 | 84.48 | 895.2043 | Inverter manual stop for Load reducing at peak time | 256 | 250
164 | Sept | 2022-09-17 | CSPPL | Load Shedding | Blk-3 | Inv-4_M2 | 13:19 | 13:49 | 0:30 | 12:00 |  | 0.50124 | 6.9425 | 6.4413 | 2061.9 | 84.48 | 873.1005 | Inverter manual stop for Load reducing at peak time | 256 | 250
165 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-1_M1 | 12:00 | 12:17 | 0:17 | 6:48 |  | 0.29611 | 7.051 | 6.7549 | 2234.16 | 84.48 | 558.8908 | Inverter manual stop for Load reducing at peak time | 256 | 250
166 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-1_M2 | 12:00 | 12:17 | 0:17 | 6:48 |  | 0.29611 | 7.051 | 6.7549 | 1954.89 | 84.48 | 489.0295 | Inverter manual stop for Load reducing at peak time | 256 | 250
167 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-2_M1 | 12:03 | 12:18 | 0:15 | 6:00 |  | 0.26364 | 7.051 | 6.7873 | 2203.13 | 84.48 | 490.6797 | Inverter manual stop for Load reducing at peak time | 256 | 250
168 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-2_M2 | 12:03 | 12:18 | 0:15 | 6:00 |  | 0.26364 | 7.051 | 6.7873 | 1954.89 | 84.48 | 435.3918 | Inverter manual stop for Load reducing at peak time | 256 | 250
169 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-3_M1 | 12:20 | 12:27 | 0:07 | 2:48 |  | 0.12904 | 7.051 | 6.9219 | 2192.4 | 84.48 | 238.9966 | Inverter manual stop for Load reducing at peak time | 256 | 250
170 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-3_M2 | 12:20 | 12:27 | 0:07 | 2:48 |  | 0.12904 | 7.051 | 6.9219 | 2442.96 | 84.48 | 266.3105 | Inverter manual stop for Load reducing at peak time | 256 | 250
171 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-4_M1 | 12:38 | 12:48 | 0:10 | 4:00 |  | 0.18221 | 7.051 | 6.8688 | 1954.89 | 84.48 | 300.9216 | Inverter manual stop for Load reducing at peak time | 256 | 250
172 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-4_M2 | 12:38 | 12:48 | 0:10 | 4:00 |  | 0.18221 | 7.051 | 6.8688 | 2234.16 | 84.48 | 343.9104 | Inverter manual stop for Load reducing at peak time | 256 | 250
173 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-2_M1 | 12:32 | 12:44 | 0:12 | 4:48 |  | 0.21489 | 7.051 | 6.8361 | 2203.13 | 84.48 | 399.959 | Inverter manual stop for Load reducing at peak time | 256 | 250
174 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-2_M2 | 12:32 | 12:44 | 0:12 | 4:48 |  | 0.21489 | 7.051 | 6.8361 | 1954.89 | 84.48 | 354.8932 | Inverter manual stop for Load reducing at peak time | 256 | 250
175 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-3_M1 | 12:32 | 12:44 | 0:12 | 4:48 |  | 0.21489 | 7.051 | 6.8361 | 2192.4 | 84.48 | 398.011 | Inverter manual stop for Load reducing at peak time | 256 | 250
176 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-6 | Inv-3_M2 | 12:32 | 12:44 | 0:12 | 4:48 |  | 0.21489 | 7.051 | 6.8361 | 2442.96 | 84.48 | 443.498 | Inverter manual stop for Load reducing at peak time | 256 | 250
177 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-1_M1 | 12:39 | 13:05 | 0:26 | 10:24 |  | 0.44717 | 7.051 | 6.6038 | 1973.16 | 84.48 | 745.3976 | Inverter manual stop for Load reducing at peak time | 256 | 250
178 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-1_M2 | 12:39 | 13:05 | 0:26 | 10:24 |  | 0.44717 | 7.051 | 6.6038 | 1910.52 | 84.48 | 721.7342 | Inverter manual stop for Load reducing at peak time | 256 | 250
179 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-2_M1 | 12:45 | 13:09 | 0:24 | 9:36 |  | 0.4151 | 7.051 | 6.6359 | 2098.44 | 84.48 | 735.8744 | Inverter manual stop for Load reducing at peak time | 256 | 250
180 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-2_M2 | 12:45 | 13:09 | 0:24 | 9:36 |  | 0.4151 | 7.051 | 6.6359 | 2004.48 | 84.48 | 702.9248 | Inverter manual stop for Load reducing at peak time | 256 | 250
181 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-3_M1 | 12:47 | 13:09 | 0:22 | 8:48 |  | 0.38165 | 7.051 | 6.6693 | 2223.72 | 84.48 | 716.9748 | Inverter manual stop for Load reducing at peak time | 256 | 250
182 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-3_M2 | 12:47 | 13:09 | 0:22 | 8:48 |  | 0.38165 | 7.051 | 6.6693 | 1973.16 | 84.48 | 636.1889 | Inverter manual stop for Load reducing at peak time | 256 | 250
183 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-4_M1 | 12:50 | 13:09 | 0:19 | 7:36 |  | 0.33148 | 7.051 | 6.7195 | 2223.72 | 84.48 | 622.7095 | Inverter manual stop for Load reducing at peak time | 256 | 250
184 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-7 | Inv-4_M2 | 12:50 | 13:09 | 0:19 | 7:36 |  | 0.33148 | 7.051 | 6.7195 | 1973.16 | 84.48 | 552.545 | Inverter manual stop for Load reducing at peak time | 256 | 250
185 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-1_M1 | 13:16 | 13:24 | 0:08 | 3:12 |  | 0.14903 | 7.051 | 6.9019 | 1973.16 | 84.48 | 248.4161 | Inverter manual stop for Load reducing at peak time | 256 | 250
186 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-1_M2 | 13:16 | 13:24 | 0:08 | 3:12 |  | 0.14903 | 7.051 | 6.9019 | 2192.4 | 84.48 | 276.0179 | Inverter manual stop for Load reducing at peak time | 256 | 250
187 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-2_M1 | 13:16 | 13:24 | 0:08 | 3:12 |  | 0.14903 | 7.051 | 6.9019 | 1973.16 | 84.48 | 248.4161 | Inverter manual stop for Load reducing at peak time | 256 | 250
188 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-2_M2 | 13:16 | 13:24 | 0:08 | 3:12 |  | 0.14903 | 7.051 | 6.9019 | 2223.72 | 84.48 | 279.961 | Inverter manual stop for Load reducing at peak time | 256 | 250
189 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-3_M1 | 13:16 | 13:24 | 0:08 | 3:12 |  | 0.14903 | 7.051 | 6.9019 | 2223.72 | 84.48 | 279.961 | Inverter manual stop for Load reducing at peak time | 256 | 250
190 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-3_M2 | 13:16 | 13:24 | 0:08 | 3:12 |  | 0.14903 | 7.051 | 6.9019 | 1941.84 | 84.48 | 244.473 | Inverter manual stop for Load reducing at peak time | 256 | 250
191 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-4_M1 | 13:29 | 13:42 | 0:13 | 5:12 |  | 0.22805 | 7.051 | 6.8229 | 2322.9 | 84.48 | 447.522 | Inverter manual stop for Load reducing at peak time | 256 | 250
192 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-8 | Inv-4_M2 | 13:29 | 13:42 | 0:13 | 5:12 |  | 0.22805 | 7.051 | 6.8229 | 2061.9 | 84.48 | 397.2386 | Inverter manual stop for Load reducing at peak time | 256 | 250
193 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-9 | Inv-1_M1 | 13:30 | 13:31 | 0:01 | 0:24 |  | 0.032811 | 7.051 | 7.0182 | 2102.065 | 84.48 | 58.2659 | Inverter manual stop for Load reducing at peak time | 256 | 250
194 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-9 | Inv-1_M2 | 13:30 | 13:31 | 0:01 | 0:24 |  | 0.032811 | 7.051 | 7.0182 | 2007.235 | 84.48 | 55.6374 | Inverter manual stop for Load reducing at peak time | 256 | 250
195 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-9 | Inv-2_M1 | 13:31 | 13:41 | 0:10 | 4:00 |  | 0.17929 | 7.051 | 6.8717 | 2102.065 | 84.48 | 318.383 | Inverter manual stop for Load reducing at peak time | 256 | 250
196 | Sept | 2022-09-18 | CSPPL | Load Shedding | Blk-9 | Inv-2_M2 | 13:31 | 13:41 | 0:10 | 4:00 |  | 0.17929 | 7.051 | 6.8717 | 2212.7 | 84.48 | 335.14 | Inverter manual stop for Load reducing at peak time | 256 | 250
197 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-1_M1 | 11:11 | 11:20 | 0:09 | 3:36 |  | 0.15334 | 7.1588 | 7.0055 | 2102.065 | 84.48 | 272.3137 | Inverter manual stop for Load reducing at peak time | 256 | 250
198 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-1_M2 | 11:11 | 11:20 | 0:09 | 3:36 |  | 0.15334 | 7.1588 | 7.0055 | 2007.235 | 84.48 | 260.0289 | Inverter manual stop for Load reducing at peak time | 256 | 250
199 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-2_M1 | 11:20 | 11:49 | 0:29 | 11:36 |  | 0.47575 | 7.1588 | 6.6831 | 2102.065 | 84.48 | 844.8471 | Inverter manual stop for Load reducing at peak time | 256 | 250
200 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-2_M2 | 11:20 | 11:49 | 0:29 | 11:36 |  | 0.47575 | 7.1588 | 6.6831 | 2212.7 | 84.48 | 889.3128 | Inverter manual stop for Load reducing at peak time | 256 | 250
201 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-3_M1 | 11:23 | 11:56 | 0:33 | 13:12 |  | 0.54287 | 7.1588 | 6.616 | 2275.92 | 84.48 | 1043.7777 | Inverter manual stop for Load reducing at peak time | 256 | 250
202 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-3_M2 | 11:23 | 11:56 | 0:33 | 13:12 |  | 0.54287 | 7.1588 | 6.616 | 1991.43 | 84.48 | 913.3054 | Inverter manual stop for Load reducing at peak time | 256 | 250
203 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-4_M1 | 11:32 | 12:18 | 0:46 | 18:24 |  | 0.76227 | 7.1588 | 6.3966 | 2244.31 | 84.48 | 1445.2502 | Inverter manual stop for Load reducing at peak time | 256 | 250
204 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-9 | Inv-4_M2 | 11:32 | 12:18 | 0:46 | 18:24 |  | 0.76227 | 7.1588 | 6.3966 | 1944.015 | 84.48 | 1251.8716 | Inverter manual stop for Load reducing at peak time | 256 | 250
205 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-1_M1 | 11:50 | 12:19 | 0:29 | 11:36 |  | 0.49072 | 7.1588 | 6.6681 | 2004.48 | 84.48 | 830.9695 | Inverter manual stop for Load reducing at peak time | 256 | 250
206 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-1_M2 | 11:50 | 12:19 | 0:29 | 11:36 |  | 0.49072 | 7.1588 | 6.6681 | 2161.08 | 84.48 | 895.889 | Inverter manual stop for Load reducing at peak time | 256 | 250
207 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-2_M1 | 11:53 | 12:21 | 0:28 | 11:12 |  | 0.47527 | 7.1588 | 6.6836 | 1973.16 | 84.48 | 792.2424 | Inverter manual stop for Load reducing at peak time | 256 | 250
208 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-2_M2 | 11:53 | 12:21 | 0:28 | 11:12 |  | 0.47527 | 7.1588 | 6.6836 | 2255.04 | 84.48 | 905.4199 | Inverter manual stop for Load reducing at peak time | 256 | 250
209 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-3_M1 | 11:57 | 12:22 | 0:25 | 10:00 |  | 0.42673 | 7.1588 | 6.7321 | 1973.16 | 84.48 | 711.3335 | Inverter manual stop for Load reducing at peak time | 256 | 250
210 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-3_M2 | 11:57 | 12:22 | 0:25 | 10:00 |  | 0.42673 | 7.1588 | 6.7321 | 2255.04 | 84.48 | 812.9526 | Inverter manual stop for Load reducing at peak time | 256 | 250
211 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-4_M1 | 12:10 | 12:25 | 0:15 | 6:00 |  | 0.26406 | 7.1588 | 6.8948 | 1973.16 | 84.48 | 440.1661 | Inverter manual stop for Load reducing at peak time | 256 | 250
212 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-10 | Inv-4_M2 | 12:10 | 12:25 | 0:15 | 6:00 |  | 0.26406 | 7.1588 | 6.8948 | 2192.4 | 84.48 | 489.0734 | Inverter manual stop for Load reducing at peak time | 256 | 250
213 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-11 | Inv-1_M1 | 12:20 | 12:52 | 0:32 | 12:48 |  | 0.54738 | 7.1588 | 6.6115 | 2023.04 | 84.48 | 935.5122 | Inverter manual stop for Load reducing at peak time | 256 | 250
214 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-11 | Inv-1_M2 | 12:20 | 12:52 | 0:32 | 12:48 |  | 0.54738 | 7.1588 | 6.6115 | 2228.505 | 84.48 | 1030.5251 | Inverter manual stop for Load reducing at peak time | 256 | 250
215 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-11 | Inv-2_M1 | 12:20 | 12:55 | 0:35 | 14:00 |  | 0.54738 | 7.1588 | 6.6115 | 2054.65 | 84.48 | 950.1295 | Inverter manual stop for Load reducing at peak time | 256 | 250
216 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-11 | Inv-2_M2 | 12:20 | 12:55 | 0:35 | 14:00 |  | 0.54738 | 7.1588 | 6.6115 | 2275.92 | 84.48 | 1052.4512 | Inverter manual stop for Load reducing at peak time | 256 | 250
217 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-11 | Inv-3_M1 | 12:22 | 13:02 | 0:40 | 16:00 |  | 0.6802 | 7.1588 | 6.4787 | 2023.04 | 84.48 | 1162.5046 | Inverter manual stop for Load reducing at peak time | 256 | 250
218 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-11 | Inv-3_M2 | 12:22 | 13:02 | 0:40 | 16:00 |  | 0.6802 | 7.1588 | 6.4787 | 2133.675 | 84.48 | 1226.079 | Inverter manual stop for Load reducing at peak time | 256 | 250
219 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-1_M1 | 12:23 | 13:23 | 1:00 | 24:00 |  | 1.0085 | 7.1588 | 6.1504 | 2302.02 | 84.48 | 1961.2379 | Inverter manual stop for Load reducing at peak time | 256 | 250
220 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-1_M2 | 12:23 | 13:23 | 1:00 | 24:00 |  | 1.0085 | 7.1588 | 6.1504 | 2145.42 | 84.48 | 1827.8203 | Inverter manual stop for Load reducing at peak time | 256 | 250
221 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-2_M1 | 12:26 | 13:30 | 1:04 | 25:36 |  | 1.0722 | 7.1588 | 6.0867 | 1910.52 | 84.48 | 1730.4746 | Inverter manual stop for Load reducing at peak time | 256 | 250
222 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-2_M2 | 12:26 | 13:30 | 1:04 | 25:36 |  | 1.0722 | 7.1588 | 6.0867 | 2192.4 | 84.48 | 1985.7906 | Inverter manual stop for Load reducing at peak time | 256 | 250
223 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-3_M1 | 12:54 | 13:44 | 0:50 | 20:00 |  | 0.83196 | 7.1588 | 6.3269 | 2192.4 | 84.48 | 1540.9076 | Inverter manual stop for Load reducing at peak time | 256 | 250
224 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-3_M2 | 12:54 | 13:44 | 0:50 | 20:00 |  | 0.83196 | 7.1588 | 6.3269 | 2004.48 | 84.48 | 1408.8298 | Inverter manual stop for Load reducing at peak time | 256 | 250
225 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-4_M1 | 13:02 | 13:44 | 0:42 | 16:48 |  | 0.69914 | 7.1588 | 6.4597 | 2004.48 | 84.48 | 1183.9185 | Inverter manual stop for Load reducing at peak time | 256 | 250
226 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-12 | Inv-4_M2 | 13:02 | 13:44 | 0:42 | 16:48 |  | 0.69914 | 7.1588 | 6.4597 | 2223.72 | 84.48 | 1313.4096 | Inverter manual stop for Load reducing at peak time | 256 | 250
227 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-13 | Inv-1_M1 | 13:29 | 13:59 | 0:30 | 12:00 |  | 0.49209 | 7.1588 | 6.6668 | 2004.48 | 84.48 | 833.292 | Inverter manual stop for Load reducing at peak time | 256 | 250
228 | Sept | 2022-09-19 | CSPPL | Load Shedding | Blk-13 | Inv-1_M2 | 13:29 | 13:59 | 0:30 | 12:00 |  | 0.49209 | 7.1588 | 6.6668 | 2004.48 | 84.48 | 833.292 | Inverter manual stop for Load reducing at peak time | 256 | 250
228 | June | 2023-06-08 | CSPPL | Load Shedding | Plant |  | 11:48 | 14:42 | 2:54 | 69:36 |  | 2.77 | 7.5 | 4.73 | 25000 | 84.67 | 58633.975 | LD Msg No-230 for 250 to 225 and LD Msg No-236 for 225 to 250 | 250 | 225
229 | June | 2023-06-09 | CSPPL | Load Shedding | Plant |  | 10:30 | 11:00 | 0:30 | 12:00 |  | 0.41 | 7.0702 | 6.6602 | 50000 | 84.67 | 17357.35 | LD Msg No-261 for 250 to 200 | 250 | 200
230 | June | 2023-06-09 | CSPPL | Load Shedding | Plant |  | 11:00 | 15:42 | 4:42 | 112:48 |  | 4.05 | 7.0702 | 3.0202 | 100000 | 84.67 | 342913.5 | LD Msg No-262 for 250 to 150 and LD Msg No-265 for 225 to 250 | 200 | 150
231 | June | 2023-06-10 | CSPPL | Load Shedding | Plant |  | 10:00 | 15:19 | 5:19 | 127:36 |  | 4.1316 | 7.1785 | 3.0469 | 100000 | 84.67 | 349821.8218 | LD Msg No-282 for 250 to 150 and LD Msg No-287 for 150 to 250 | 250 | 150
232 | June | 2023-06-11 | CSPPL | Load Shedding | Plant |  | 10:38 | 15:30 | 4:52 | 116:48 |  | 3.67 | 7.7247 | 4.0547 | 100000 | 84.67 | 310738.9 | LD Msg No-323 for 250 to 150 and LD Msg No-329 for 150 to 251 | 250 | 150
233 | June | 2023-06-12 | CSPPL | Load Shedding | Plant |  | 10:58 | 15:10 | 4:12 | 100:48 |  | 3.7383 | 7.25 | 3.5117 | 100000 | 84.67 | 316525.9455 | LD Msg No-357 for 250 to 150 and LD Msg No-361 for 150 to 252 | 250 | 150
234 | June | 2023-06-13 | CSPPL | Load Shedding | Plant |  | 10:23 | 14:42 | 4:19 | 103:36 |  | 3.7343 | 7.2 | 3.4657 | 100000 | 84.67 | 316183.5606 | LD Msg No-386 for 250 to 150 and LD Msg No-392 for 150 to 252 | 250 | 150
235 | June | 2023-06-14 | CSPPL | Load Shedding | Plant |  | 11:05 | 11:09 | 0:04 | 1:36 |  | 0.064827 | 6.7454 | 6.6806 | 50000 | 84.67 | 2744.4601 | LD Msg No-420 for 250 to 200 | 250 | 200
236 | June | 2023-06-14 | CSPPL | Load Shedding | Plant |  | 11:09 | 13:50 | 2:41 | 64:24 |  | 2.2384 | 6.7454 | 4.507 | 75000 | 84.67 | 142144.8787 | LD Msg No-420 for 200 to 175 and LD Msg No-423 for 175 to 250 | 200 | 175
237 | June | 2023-06-15 | CSPPL | Load Shedding | Plant |  | 12:00 | 12:21 | 0:21 | 8:24 |  | 0.21266 | 4.9039 | 4.6912 | 50000 | 84.67 | 9003.0802 | LD Msg No-458 for 250 to 200 and LD Msg No-459 for 200 to 251 | 250 | 200
238 | June | 2023-06-20 | CSPPL | Load Shedding | Plant |  | 11:06 | 15:12 | 4:06 | 98:24 |  | 3.7045 | 7.3321 | 3.6275 | 50000 | 84.67 | 156831.8791 | LD Msg No-602 for 250 to 200 and LD Msg No-608 for 200 to 251 | 250 | 200
239 | June | 2023-06-22 | CSPPL | Load Shedding | Plant |  | 11:12 | 11:34 | 0:22 | 8:48 |  | 0.32748 | 7.0625 | 6.7351 | 25000 | 84.67 | 6931.8371 | LD Msg No-649 for 223 to 225 | 223 | 225
240 | June | 2023-06-22 | CSPPL | Load Shedding | Plant |  | 11:34 | 15:50 | 4:16 | 102:24 |  | 3.8191 | 7.0625 | 3.2434 | 45000 | 84.67 | 145514.9291 | LD Msg No-650 for 225 to 180 | 225 | 180
241 | June | 2023-06-23 | CSPPL | Load Shedding | Plant |  | 10:16 | 12:15 | 1:59 | 47:36 |  | 1.73 | 7.34 | 5.61 | 50000 | 84.67 | 73239.55 | LD Msg No- 670 for 200 | 198 | 200
242 | June | 2023-06-23 | CSPPL | Load Shedding | Plant |  | 12:15 | 13:46 | 1:31 | 36:24 |  | 1.49 | 7.34 | 5.85 | 75000 | 84.67 | 94618.725 | LD Msg No- 681 for 175 | 173 | 175
243 | June | 2023-06-23 | CSPPL | Load Shedding | Plant |  | 13:46 | 15:20 | 1:34 | 37:36 |  | 1.39 | 7.34 | 5.95 | 50000 | 84.67 | 58845.65 | LD Msg No- 683 for 200 | 189 | 200
244 | June | 2023-06-24 | CSPPL | Load Shedding | Plant |  | 12:35 | 14:00 | 1:25 | 34:00 |  | 1.35 | 7.1 | 5.75 | 25000 | 84.67 | 28576.125 | LD Msg No- 705 for 250 to 225 | 248 | 225
245 | July | 2023-07-01 | CSPPL | Load Shedding | Plant |  | 12:17 | 13:35 | 1:18 | 31:12 |  | 1.2627 | 7.22 | 5.9573 | 37000 | 85.6839 | 40031.7456 | LD Msg 13 for 250 to 213 and LD Msg 14 for 213 to 250 | 250 | 213
246 | July | 2023-07-13 | CSPPL | Load Shedding | Plant |  | 13:46 | 15:11 | 1:25 | 34:00 |  | 1.2594 | 7.39 | 6.1306 | 35000 | 85.6839 | 37769.5908 | LD Msg 301 for 250 to 215MW and LD Msg 308 for 250 | 250 | 215
247 | July | 2023-07-15 | CSPPL | Load Shedding | Plant |  | 10:56 | 12:33 | 1:37 | 38:48 |  | 1.4546 | 7.24 | 5.7854 | 50000 | 85.6839 | 62318.771 |  | 238 | 202
248 | July | 2023-07-15 | CSPPL | Load Shedding | Plant |  | 12:33 | 15:35 | 3:02 | 72:48 |  | 2.6247 | 7.24 | 4.6153 | 80000 | 85.6839 | 179913.2184 |  | 202 | 177
249 | Feb | 2024-02-19 | CSPPL | Load Shedding | Plant |  | 13:25 | 14:24 | 0:59 | 23:36 |  | 0.99456 | 5.72 | 4.7254 | 50000 | 87.08 | 43303.2875 | LD Msg 469 for 250 to 200Mw and LD Msg 472 for 250MW | 250 | 200
250 | April | 2024-04-07 | CSPPL | Load Shedding | Plant |  | 10:31 | 14:46 | 4:15 | 102:00 |  | 4.08 | 7.12 | 3.04 | 50000 | 80.7 | 164628 | LD Msg 178 for 250 to 200Mw and LD Msg 182 for 250MW | 250 | 200
251 | April | 2024-04-08 | CSPPL | Load Shedding | Plant |  | 10:34 | 15:15 | 4:41 | 112:24 |  | 4.31 | 7.45 | 3.14 | 50000 | 80.7 | 173908.5 | LD Msg 187 for 250 to 200Mw and LD Msg 191 for 250MW | 250 | 200
252 | April | 2024-04-19 | CSPPL | Load Shedding | Plant |  | 10:35 | 12:05 | 1:30 | 36:00 |  | 1.45 | 7.29 | 5.84 | 25000 | 80.7 | 29253.75 | LD Msg 466 for 250 to 225Mw | 250 | 225
253 | April | 2024-04-19 | CSPPL | Load Shedding | Plant |  | 12:05 | 14:49 | 2:44 | 65:36 |  | 2.679 | 7.29 | 4.611 | 50000 | 80.7 | 108097.65 | LD Msg 469 for 225 to 200Mw and LD Msg 474 for 250MW | 225 | 200
254 | Auguest | 2024-08-08 | CSPPL | Load Shedding | Plant |  | 11:57 | 13:30 | 1:33 | 37:12 |  | 0.53196 | 2.83 | 2.298 | 50000 | 86.32 | 22959.3936 | LD Msg 208 for 200Mw and LD Msg 210 for 250MW | 250 | 200
255 | Auguest | 2024-08-10 | CSPPL | Load Shedding | Plant |  | 11:08 | 14:54 | 3:46 | 18:24 |  | 2.71 | 5.42 | 2.71 | 17500 | 83.51 | 39567.82 | LD Msg 293 for 232.5MW and LD Msg 298 for 250MW | 250 | 232.5
256 | Auguest | 2024-08-11 | CSPPL | Load Shedding | Plant |  | 9:29 | 10:34 | 1:05 | 26:00 |  | 0.491 | 5.6774 | 5.1864 | 50000 | 62.87 | 15434.585 | LD Msg 320 for 250 to 200Mw | 250 | 200
257 | Auguest | 2024-08-11 | CSPPL | Load Shedding | Plant |  | 10:34 | 12:38 | 2:04 | 49:36 |  | 1.53 | 5.6774 | 4.1474 | 90000 | 62.87 | 86571.99 | LD Msg 324 for 200 to 160Mw | 200 | 160
258 | Auguest | 2024-08-11 | CSPPL | Load Shedding | Plant |  | 12:38 | 18:10 | 5:32 | 132:48 |  | 2.857 | 5.6774 | 2.8204 | 150000 | 62.87 | 269429.385 | LD Msg 331 for 160Mw and LD Msg 343 for 250MW | 250 | 100
259 | Auguest | 2024-08-15 | CSPPL | Load Shedding | Plant |  | 10:35 | 14:25 | 3:50 | 92:00 |  | 2.3275 | 3.54 | 1.2125 | 50000 | 85.61 | 99626.7113 | LD Msg 453 for 200Mw and LD Msg 454 for 250MW | 250 | 200
260 | Auguest | 2024-08-26 | CSPPL | Load Shedding | Plant |  | 12:00 | 14:50 | 2:50 | 68:00 |  | 1.96 | 5.24 | 3.28 | 38000 | 86.06 | 64097.488 | LD Msg 713 for 212Mw and LD Msg 736 for 250MW | 250 | 212
261 | Auguest | 2024-08-27 | CSPPL | Load Shedding | Plant |  | 9:53 | 13:00 | 3:07 | 74:48 |  | 0.7965 | 2.57 | 1.7735 | 18000 | 85.45 | 12250.9665 | LD Msg 768 for 250 to 232MW | 250 | 232
262 | Auguest | 2024-08-27 | CSPPL | Load Shedding | Plant |  | 13:00 | 13:20 | 0:20 | 8:00 |  | 0.1021 | 2.57 | 2.4679 | 36400 | 85.45 | 3175.698 | LD Msg 776 for 232 to 213.6MW | 232 | 213.6
263 | Auguest | 2024-08-27 | CSPPL | Load Shedding | Plant |  | 13:20 | 14:36 | 1:16 | 30:24 |  | 0.3402 | 2.57 | 2.2298 | 46400 | 85.45 | 13488.5218 | LD Msg 778 for 213 to 203.6MW | 213.6 | 203.6
264 | Auguest | 2024-08-27 | CSPPL | Load Shedding | Plant |  | 14:36 | 16:44 | 2:08 | 51:12 |  | 0.5023 | 2.57 | 2.0677 | 26000 | 85.45 | 11159.5991 | LD Msg 780 for 213.6 to 224MW | 213.6 | 224
265 | Auguest | 2024-08-29 | CSPPL | Load Shedding | Plant |  | 9:30 | 9:55 | 0:25 | 10:00 |  | 0.222 | 5.28 | 5.058 | 30000 | 83.48 | 5559.768 | LD Msg 837 for 220Mw and LD Msg 839 for 250MW | 250 | 220
266 | Auguest | 2024-08-29 | CSPPL | Load Shedding | Plant |  | 11:57 | 13:12 | 1:15 | 30:00 |  | 0.956 | 5.28 | 4.324 | 30000 | 83.48 | 23942.064 | LD Msg 844 for 250 to 220MW | 250 | 220
267 | Auguest | 2024-08-29 | CSPPL | Load Shedding | Plant |  | 13:12 | 13:55 | 0:43 | 17:12 |  | 0.545 | 5.28 | 4.735 | 99000 | 83.48 | 45041.634 | LD Msg 844 for 220 to 151MW and LD Msg 845 for 250MW | 220 | 151
268 | Sept. | 2024-09-05 | CSPPL | Load Shedding | Plant |  | 11:15 | 13:15 | 2:00 | 48:00 |  | 1.56 | 6.11 | 4.55 | 55000 | 84.33 | 72355.14 | LD Msg 96 for 250 to 195MW | 250 | 195
269 | Sept. | 2024-09-05 | CSPPL | Load Shedding | Plant |  | 13:15 | 14:45 | 1:30 | 36:00 |  | 1.46 | 6.11 | 4.65 | 75000 | 84.33 | 92341.35 | LD Msg 102 for 195 to 175MW and LD Msg 104 for 250MW | 195 | 175
270 | Sept. | 2024-09-08 | CSPPL | Load Shedding | Plant |  | 9:55 | 10:19 | 0:24 | 9:36 |  | 0.29764 | 6.78 | 6.4824 | 84000 | 81.63 | 20408.7272 | LD Msg 188 for 250 to 166MW | 250 | 166
271 | Sept. | 2024-09-08 | CSPPL | Load Shedding | Plant |  | 10:19 | 13:24 | 3:05 | 74:00 |  | 2.7376 | 6.78 | 4.0424 | 95000 | 81.63 | 212295.0934 | LD Msg 192 for 166 to 155MW | 166 | 155
272 | Sept. | 2024-09-08 | CSPPL | Load Shedding | Plant |  | 13:24 | 13:51 | 0:27 | 10:48 |  | 0.41255 | 6.78 | 6.3675 | 64000 | 81.63 | 21552.6855 | LD Msg 197 for 155 to 186MW and LD Msg 198 for 250MW | 155 | 186
273 | Sept. | 2024-09-11 | CSPPL | Load Shedding | Plant |  | 11:30 | 13:20 | 1:50 | 44:00 |  | 1.71 | 6 | 4.29 | 25000 | 84.03 | 35922.825 | LD Msg 263 for 250 to 225MW and LD Msg 266 for 250MW | 250 | 225
274 | Sept. | 2024-09-13 | CSPPL | Load Shedding | Plant |  | 10:20 | 11:10 | 0:50 | 20:00 |  | 0.7114 | 6.76 | 6.0486 | 38000 | 83.07 | 22456.6371 | LD Msg 318 for 250 to 212MW | 250 | 212
275 | Sept. | 2024-09-13 | CSPPL | Load Shedding | Plant |  | 11:10 | 14:30 | 3:20 | 80:00 |  | 2.933 | 6.76 | 3.827 | 30000 | 83.07 | 73093.293 | LD Msg 322 for 212 to 220MW | 212 | 220
276 | Sept. | 2024-09-13 | CSPPL | Load Shedding | Plant |  | 14:30 | 14:40 | 0:10 | 4:00 |  | 0.11965 | 6.76 | 6.6403 | 12000 | 83.07 | 1192.7191 | LD Msg 330 for 220 to 238MW and LD Msg 331 for 250MW | 220 | 238
277 | Sept. | 2024-09-14 | CSPPL | Load Shedding | Plant |  | 11:15 | 15:15 | 4:00 | 96:00 |  | 3.56 | 6.58 | 3.02 | 30000 | 81.67 | 87223.56 | LD Msg 357 for 250 to 220MW and LD Msg 363 for 250MW | 250 | 220
278 | Sept. | 2024-09-15 | CSPPL | Load Shedding | Plant |  | 11:00 | 15:20 | 4:20 | 104:00 |  | 3.83 | 6.73 | 2.9 | 30000 | 83.92 | 96424.08 | LD Msg 382 for 250 to 220MW and LD Msg 386 for 250MW | 250 | 220
279 | Sept. | 2024-09-16 | CSPPL | Load Shedding | Plant |  | 11:00 | 15:30 | 4:30 | 108:00 |  | 4.1 | 7.02 | 2.92 | 30000 | 79.35 | 97600.5 | LD Msg 397 for 250 to 220MW and LD Msg 404 for 250MW | 250 | 220
280 | Sept. | 2024-09-17 | CSPPL | Load Shedding | Plant |  | 10:05 | 14:40 | 4:35 | 110:00 |  | 4.2468 | 7.06 | 2.8132 | 30000 | 82.63 | 105272.9336 | LD Msg 430 for 250 to 220MW and LD Msg 435 for 250MW | 250 | 220
281 | Nov. | 2024-11-24 | CSPPL | Load Shedding | Plant |  | 12:50 | 17:50 | 5:00 | 120:00 |  | 2.35 | 5.19 | 2.84 | 25000 | 86.69 | 50930.375 | LD Msg 120 for 250 to 225MW | 250 | 225
282 | Nov. | 2024-11-25 | CSPPL | Load Shedding | Plant |  | 11:50 | 14:15 | 2:25 | 58:00 |  | 1.87 | 5.02 | 3.15 | 25000 | 86.78 | 40569.65 | LD Msg 123 for 250 to 225MW and LD Msg 124 for 250MW | 250 | 225
283 | Dec | 2024-12-08 | CSPPL | Load Shedding | Plant |  | 11:30 | 12:20 | 0:50 | 20:00 |  | 0.7219 | 5.41 | 4.6881 | 49000 | 85.76 | 30335.9706 | LD Msg 164 for 250 to 201MW and LD Msg 169 for 250MW | 250 | 201
284 | Jan | 2025-01-10 | CSPPL | Load Shedding | Plant |  | 11:06 | 14:58 | 3:52 | 92:48 |  | 3.0559 | 5.36 | 2.3041 | 25000 | 87.99 | 67222.2336 | LD Msg 186 for 250 to 225MW and LD Msg 189 for 250MW | 250 | 225
285 | Feb | 2025-02-23 | CSPPL | Load Shedding | Plant |  | 13:08 | 13:33 | 0:25 | 10:00 |  | 0.42483 | 6.8 | 6.3752 | 25000 | 85.12 | 9040.276 | LD Msg 579 for 250 to 225MW and LD Msg 580 for 250MW | 250 | 225
286 | April | 2025-04-06 | CSPPL | Load Shedding | Plant |  | 13:54 | 15:22 | 1:28 | 35:12 |  | 1.36 | 7.78 | 6.42 | 50000 | 79.15 | 53822 | LD Msg 110 for 250 to 200MW and LD Msg 118 for 250MW | 250 | 200
287 | April | 2025-04-07 | CSPPL | Load Shedding | Plant |  | 13:04 | 14:25 | 1:21 | 32:24 |  | 1.36 | 7.6 | 6.24 | 100000 | 75.61 | 102829.6 | LD Msg 148 for 250 to 150MW | 250 | 155
288 | April | 2025-04-07 | CSPPL | Load Shedding | Plant |  | 14:26 | 16:00 | 1:34 | 37:36 |  | 1.27 | 7.6 | 6.33 | 50000 | 75.61 | 48012.35 | LD Msg 157 for 150 to 200MW and LD Msg 160 for 250MW | 250 | 200
289 | April | 2025-04-12 | CSPPL | Load Shedding | Plant |  | 13:09 | 14:19 | 1:10 | 28:00 |  | 1.17 | 7.51 | 6.34 | 50000 | 78.05 | 45659.25 | LD Msg 276 for 250 to 200MW and LD Msg 278 for 250MW | 250 | 200
290 | April | 2025-04-18 | CSPPL | Load Shedding | Plant |  | 12:47 | 13:30 | 0:43 | 17:12 |  | 0.673 | 6.78 | 6.107 | 25000 | 81.53 | 13717.4225 | LD Msg 728 for 250 to 225MW and LD Msg 732 for 250MW | 250 | 225
291 | April | 2025-04-19 | CSPPL | Load Shedding | Plant |  | 11:28 | 12:24 | 0:56 | 22:24 |  | 0.898 | 7.12 | 6.222 | 38000 | 77.38 | 26405.1512 | LD Msg 764 for 250 to 212MW | 250 | 212
292 | April | 2025-04-19 | CSPPL | Load Shedding | Plant |  | 12:24 | 13:30 | 1:06 | 26:24 |  | 1.075 | 7.12 | 6.045 | 62000 | 77.38 | 51573.77 | LD Msg 768 for 212 to 188MW and LD Msg 771 for 250MW | 212 | 188
293 | May | 2025-05-12 | CSPPL | Load Shedding | Plant |  | 12:48 | 15:07 | 2:19 | 55:36 |  | 2.125 | 7.46 | 5.335 | 50000 | 77.95 | 82821.875 | LD Msg 366 for 250 to 200MW and LD Msg 373 for 250MW | 250 | 200
294 | May | 2025-05-13 | CSPPL | Load Shedding | Plant |  | 12:03 | 13:53 | 1:50 | 44:00 |  | 1.79 | 7.42 | 5.63 | 25000 | 80.62 | 36077.45 | LD Msg 401 for 250 to 225MW and LD Msg 404 for 250MW | 250 | 225
295 | May | 2025-05-18 | CSPPL | Load Shedding | Plant |  | 12:05 | 14:15 | 2:10 | 52:00 |  | 2.08 | 7.51 | 5.43 | 25000 | 80.03 | 41615.6 | LD Msg 603 for 250 to 225MW and LD Msg 605 for 250MW | 250 | 225
296 | May | 2025-05-19 | CSPPL | Load Shedding | Plant |  | 10:15 | 15:04 | 4:49 | 115:36 |  | 4.445 | 7.56 | 3.115 | 25000 | 78.52 | 87255.35 | LD Msg 622 for 250 to 225MW and LD Msg 627 for 250MW | 228 | 225
297 | May | 2025-05-23 | CSPPL | Load Shedding | Plant |  | 11:21 | 13:34 | 2:13 | 53:12 |  | 2.207 | 7.6 | 5.393 | 25000 | 79.55 | 43891.7125 | LD Msg 743 for 250 to 225MW and LD Msg 745 for 250MW | 250 | 225
298 | May | 2025-05-31 | CSPPL | Load Shedding | Plant |  | 11:45 | 13:50 | 2:05 | 50:00 |  | 1.912 | 6.9 | 4.988 | 25000 | 80.22 | 38345.16 | LD Msg 966 for 250 to 225MW and LD Msg 970 for 250MW | 250 | 225
299 | June | 2025-06-01 | CSPPL | Load Shedding | Plant |  | 10:06 | 13:45 | 3:39 | 87:36 |  | 3.1 | 6.75 | 3.65 | 90000 | 70.3 | 196137 | LD Msg 09 for 200 to 160MW and LD Msg 15 for 250MW | 200 | 160
300 | June | 2025-06-02 | CSPPL | Load Shedding | Plant |  | 11:50 | 14:10 | 2:20 | 56:00 |  | 2.16 | 7.23 | 5.07 | 25000 | 79.96 | 43178.4 | LD Msg 30 for 250 to 225MW and LD Msg 38 for 250MW | 250 | 225
301 | June | 2025-06-03 | CSPPL | Load Shedding | Plant |  | 12:25 | 14:01 | 1:36 | 38:24 |  | 1.46 | 6.97 | 5.51 | 25000 | 81.89 | 29889.85 | LD Msg 60 for 250 to 225MW and LD Msg 62 for 250MW | 250 | 225
302 | June | 2025-06-04 | CSPPL | Load Shedding | Plant |  | 10:31 | 12:59 | 2:28 | 59:12 |  | 2.2 | 7.26 | 5.06 | 50000 | 76.84 | 84524 | LD Msg 90 for 250 to 200MW | 250 | 200
303 | June | 2025-06-04 | CSPPL | Load Shedding | Plant |  | 12:59 | 14:44 | 1:45 | 42:00 |  | 1.55 | 7.26 | 5.71 | 25000 | 76.84 | 29775.5 | LD Msg 91 for 200 to 225MW and LD Msg 99 for 250MW | 200 | 225
304 | June | 2025-06-08 | CSPPL | Load Shedding | Plant |  | 15:27 | 16:55 | 1:28 | 35:12 |  | 0.881 | 7.75 | 6.869 | 41000 | 81.55 | 29456.6755 | LD Msg 211 for 207 to 166MW and LD Msg 213 for 250MW | 207 | 166
305 | June | 2025-06-12 | CSPPL | Load Shedding | Plant |  | 13:49 | 14:43 | 0:54 | 21:36 |  | 0.842 | 7.69 | 6.848 | 50000 | 79.12 | 33309.52 | LD Msg 313 for 250 to 200MW | 250 | 200
306 | June | 2025-06-12 | CSPPL | Load Shedding | Plant |  | 14:44 | 16:27 | 1:43 | 41:12 |  | 1.24 | 7.69 | 6.45 | 70000 | 79.12 | 68676.16 | LD Msg 316 for 200 to 180MW and LD Msg 317 for 250MW | 200 | 180
307 | June | 2025-06-13 | CSPPL | Load Shedding | Plant |  | 9:33 | 16:07 | 6:34 | 157:36 |  | 5.487 | 7.35 | 1.863 | 95000 | 82.99 | 432597.8235 | LD Msg 341 for 178.95 to 155MW and LD Msg 359 for 250MW | 178.95 | 155
308 | June | 2025-06-17 | CSPPL | Load Shedding | Plant |  | 9:38 | 15:03 | 5:25 | 130:00 |  | 2.56 | 5.75 | 3.19 | 115000 | 82.99 | 244322.56 | LD Msg 484 for 168 to 135MW and LD Msg 498 for 250MW | 168 | 135
309 | June | 2025-06-18 | CSPPL | Load Shedding | Plant |  | 11:56 | 15:33 | 3:37 | 86:48 |  | 3.22 | 7.2 | 3.98 | 50000 | 82.99 | 133613.9 | LD Msg 529 for 250 to 200MW and LD Msg 533 for 250MW | 250 | 200
310 | June | 2025-06-19 | CSPPL | Load Shedding | Plant |  | 11:18 | 14:00 | 2:42 | 64:48 |  | 2.46 | 6.79 | 4.33 | 50000 | 82.99 | 102077.7 | LD Msg 555 for 232 to 200MW and LD Msg 562 for 250MW | 232 | 200
311 | June | 2025-06-20 | CSPPL | Load Shedding | Plant |  | 12:32 | 13:30 | 0:58 | 23:12 |  | 0.925 | 6.62 | 5.695 | 50000 | 82.99 | 38382.875 | LD Msg 605 for 250 to 200MW and LD Msg 607 for 250MW | 250 | 200
312 | June | 2025-06-22 | CSPPL | Load Shedding | Plant |  | 10:14 | 11:33 | 1:19 | 31:36 |  | 1.072 | 7.04 | 5.968 | 50000 | 82.99 | 44482.64 | LD Msg 659 for 250 to 200MW | 202 | 200
313 | June | 2025-06-22 | CSPPL | Load Shedding | Plant |  | 11:34 | 14:05 | 2:31 | 60:24 |  | 2.31 | 7.04 | 4.73 | 90000 | 82.99 | 172536.21 | LD Msg for 663 to 160MW and LD Msg 659 for 250MW | 200 | 160
314 | July | 2025-07-06 | CSPPL | Load Shedding | Plant |  | 11:21 | 14:58 | 3:37 | 86:48 |  | 3.09 | 6.65 | 3.56 | 50000 | 84 | 129780 | LD Msg 162 for 250 to 200MW and LD Msg 164 for 250MW | 250 | 200
315 | July | 2025-07-14 | CSPPL | Load Shedding | Plant |  | 13:31 | 13:55 | 0:24 | 9:36 |  | 0.30105 | 5.94 | 5.639 | 40000 | 84 | 10115.28 | LD Msg 400 for 200 to 160MW and LD Msg 160 for 250MW | 200 | 160

## WMS Graph
| POA UPWARD | POA DOWNWARD
180 | AMB. TEMP | WIND SPEED

## Modelling New (hidden)
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | CC*Bugt (MTD) | CC*Bugt (YTD) | Capacity | 335.091
1 | April | 4 | 2022-04-01 | 2022 | FY23 | 30 | 208.9997 | 215.9 |  | 29.1001 | 52.2965 | 59637.6 | 335.091 | 82.43% | 7.1967 | 27 | 194.31 | 194.31 | 1987.92 | 53673.84 | 53673.84 | 24.72% | 24.72% | 24.72% | 94.2319 | 94.2319 |  |  |  | 99.75% | 99.75%
2 | May | 5 | 2022-05-01 | 2022 | FY23 | 31 | 221.9002 | 217.9 |  | 33.4 | 55.4377 | 61013.7 | 335.091 | 83.56% | 7.029 | 31 | 217.9 | 412.21 | 1968.1839 | 61013.7 | 114687.54 | 24.47% | 24.47% | 24.59% | 228.4373 | 161.3346 |  |  |  | 99.75% | 99.75%
3 | June | 6 | 2022-06-01 | 2022 | FY23 | 30 | 200.2009 | 192.8 |  | 34.8001 | 54.6583 | 54806.4 | 335.091 | 84.83% | 6.4267 | 30 | 192.8 | 192.8 | 1826.88 | 54806.4 | 54806.4 | 22.72% | 22.72% | 7.744% | 312.8771 | 211.8488 |  |  |  | 99.75% | 99.75%
4 | July | 7 | 2022-07-01 | 2022 | FY23 | 31 | 173.5997 | 168.9 |  | 33.0999 | 51.5649 | 48598.11 | 335.091 | 85.87% | 5.4484 | 31 | 168.9 | 168.9 | 1567.681 | 48598.11 | 48598.11 | 19.49% | 19.49% | 5.078% | 330.6118 | 241.5395 |  |  |  | 99.75% | 99.75%
5 | August | 8 | 2022-08-01 | 2022 | FY23 | 31 | 172.6002 | 174.2 |  | 31.8 | 50.3366 | 49476.24 | 335.091 | 84.76% | 5.6194 | 31 | 174.2 | 174.2 | 1596.0077 | 49476.24 | 49476.24 | 19.85% | 19.85% | 4.101% | 333.3537 | 259.9024 |  |  |  | 99.75% | 99.75%
6 | September | 9 | 2022-09-01 | 2022 | FY23 | 30 | 178.8993 | 192.1 |  | 31.1999 | 52.2506 | 53840.16 | 335.091 | 83.64% | 6.4033 | 30 | 192.1 | 366.3 | 1794.672 | 53840.16 | 103316.4 | 22.32% | 22.32% | 7.137% | 334.1964 | 272.2847 |  |  |  | 99.75% | 99.75%
7 | October | 10 | 2022-10-01 | 2022 | FY23 | 31 | 174.6008 | 202.3 |  | 27.1001 | 49.7239 | 56487.42 | 335.091 | 83.33% | 6.5258 | 31 | 202.3 | 568.6 | 1822.1748 | 56487.42 | 159803.82 | 22.66% | 22.66% | 9.417% | 334.1957 | 281.1291 |  |  |  | 99.75% | 99.75%
8 | November | 11 | 2022-11-01 | 2022 | FY23 | 30 | 133.6994 | 162.9 |  | 20.9 | 42.1871 | 47868.48 | 335.091 | 87.69% | 5.43 | 30 | 162.9 | 731.5 | 1595.616 | 47868.48 | 207672.3 | 19.84% | 19.84% | 10.71% | 334.1957 | 287.7625 |  |  |  | 99.75% | 99.75%
9 | December | 12 | 2022-12-01 | 2022 | FY23 | 31 | 124.4 | 158.6 |  | 15.8915 | 36.0769 | 47682.36 | 335.091 | 89.72% | 5.1161 | 31 | 158.6 | 890.1 | 1538.1406 | 47682.36 | 255354.66 | 19.13% | 19.13% | 11.67% | 334.3514 | 292.939 |  |  |  | 99.75% | 99.75%
10 | January | 1 | 2023-01-01 | 2023 | FY23 | 31 | 133.8993 | 169.0285 |  | 14.3999 | 34.9703 | 50622.66 | 335.091 | 89.38% | 5.4525 | 31 | 169.0285 | 1059.1285 | 1632.989 | 50622.66 | 305977.32 | 20.31% | 20.31% | 12.56% | 334.7318 | 297.1183 |  |  |  | 99.75% | 99.75%
11 | February | 2 | 2023-02-01 | 2023 | FY23 | 28 | 145.4008 | 172.5591 |  | 17.8001 | 40.2521 | 49925.7 | 335.091 | 86.34% | 6.1628 | 28 | 172.5591 | 1231.6877 | 1783.0607 | 49925.7 | 355903.02 | 22.17% | 22.17% | 13.37% | 334.8139 | 300.5452 |  |  |  | 99.75% | 99.75%
12 | March | 3 | 2023-03-01 | 2023 | FY23 | 31 | 195.5989 | 215.7458 |  | 23.6002 | 47.1796 | 59767.29 | 335.091 | 82.67% | 6.9595 | 31 | 215.7458 | 1447.4334 | 1927.9771 | 59767.29 | 415670.31 | 23.97% | 23.97% | 14.28% | 335.0909 | 303.424 |  |  |  | 99.75% | 99.75%
13 | April | 4 | 2023-04-01 | 2023 | FY24 | 30 | 208.9997 | 215.9 |  | 29.1001 | 52.2965 | 58630 | 335.091 | 81.04% | 7.1967 | 30 | 215.9 | 215.9 | 1954.3333 | 58630 | 58630 | 24.3% | 24.3% | 24.3% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
14 | May | 5 | 2023-05-01 | 2023 | FY24 | 31 | 221.9002 | 217.9 |  | 33.4 | 55.4377 | 61780 | 335.091 | 84.61% | 7.029 | 31 | 217.9 | 433.8 | 1992.9032 | 61780 | 120410 | 24.78% | 24.78% | 24.54% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
15 | June | 6 | 2023-06-01 | 2023 | FY24 | 30 | 200.2009 | 192.8 |  | 34.8001 | 54.6583 | 53700 | 335.091 | 83.12% | 6.4267 | 30 | 192.8 | 626.6 | 1790 | 53700 | 637610 | 22.26% | 22.26% | 87.12% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
16 | July | 7 | 2023-07-01 | 2023 | FY24 | 31 | 173.5997 | 168.9 |  | 33.0999 | 51.5649 | 49210 | 335.091 | 86.95% | 5.4484 | 31 | 168.9 | 2242.9334 | 1587.4194 | 49210 | 637610 | 19.74% | 19.74% | 64.99% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
17 | August | 8 | 2023-08-01 | 2023 | FY24 | 31 | 172.6002 | 174.2 |  | 31.8 | 50.3366 | 50100 | 335.091 | 85.83% | 5.6194 | 31 | 174.2 | 969.7 | 1616.129 | 50100 | 273420 | 20.1% | 20.1% | 22.22% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
18 | September | 9 | 2023-09-01 | 2023 | FY24 | 30 | 178.8993 | 192.1 |  | 31.1999 | 52.2506 | 52760 | 335.091 | 81.96% | 6.4033 | 30 | 192.1 | 1161.8 | 1758.6667 | 52760 | 326180 | 21.87% | 21.87% | 22.16% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
19 | October | 10 | 2023-10-01 | 2023 | FY24 | 31 | 174.6008 | 202.3 |  | 27.1001 | 49.7239 | 57190 | 335.091 | 84.36% | 6.5258 | 31 | 202.3 | 1364.1 | 1844.8387 | 57190 | 383370 | 22.94% | 22.94% | 22.28% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
20 | November | 11 | 2023-11-01 | 2023 | FY24 | 30 | 133.6994 | 162.9 |  | 20.9 | 42.1871 | 46900 | 335.091 | 85.92% | 5.43 | 30 | 162.9 | 1527 | 1563.3333 | 46900 | 430270 | 19.44% | 19.44% | 21.93% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
21 | December | 12 | 2023-12-01 | 2023 | FY24 | 31 | 124.4 | 158.6 |  | 15.8915 | 36.0769 | 48280 | 335.091 | 90.85% | 5.1161 | 31 | 158.6 | 1685.6 | 1557.4194 | 48280 | 478550 | 19.37% | 19.37% | 21.64% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
22 | January | 1 | 2024-01-01 | 2024 | FY24 | 31 | 133.8993 | 169.0285 |  | 14.3999 | 34.9703 | 51260 | 335.091 | 90.5% | 5.4525 | 31 | 169.0285 | 1854.6285 | 1653.5484 | 51260 | 529810 | 20.56% | 20.56% | 21.53% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
23 | February | 2 | 2024-02-01 | 2024 | FY24 | 29 | 145.4008 | 172.5591 |  | 17.8001 | 40.2521 | 47290 | 335.091 | 81.78% | 5.9503 | 29 | 172.5591 | 2027.1877 | 1630.6897 | 47290 | 577100 | 20.28% | 20.28% | 21.42% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
24 | March | 3 | 2024-03-01 | 2024 | FY24 | 31 | 195.5989 | 215.7458 |  | 23.6002 | 47.1796 | 60510 | 335.091 | 83.7% | 6.9595 | 31 | 215.7458 | 2242.9334 | 1951.9355 | 60510 | 637610 | 24.27% | 24.27% | 21.66% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
25 | April | 4 | 2024-04-01 | 2024 | FY25 | 30 | 208.9997 | 215.9 |  | 29.1001 | 52.2965 | 59074 | 335.091 | 81.65% | 7.1967 | 30 | 215.9 | 215.9 | 1969.1333 | 59074 | 59074 | 24.49% | 24.49% | 24.49% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
26 | May | 5 | 2024-05-01 | 2024 | FY25 | 31 | 221.9002 | 217.9 |  | 33.4 | 55.4377 | 60423.7 | 335.091 | 82.75% | 7.029 | 31 | 217.9 | 433.8 | 1949.1516 | 60423.7 | 119497.7 | 24.24% | 24.24% | 24.36% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
27 | June | 6 | 2024-06-01 | 2024 | FY25 | 30 | 200.2009 | 192.8 |  | 34.8001 | 54.6583 | 54283.7 | 335.091 | 84.02% | 6.4267 | 30 | 192.8 | 626.6 | 1809.4567 | 54283.7 | 173781.4 | 22.5% | 22.5% | 23.75% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
28 | July | 7 | 2024-07-01 | 2024 | FY25 | 31 | 173.5997 | 168.9 |  | 33.0999 | 51.5649 | 48128.2 | 335.091 | 85.04% | 5.4484 | 31 | 168.9 | 2242.9334 | 1552.5226 | 48128.2 | 633273.4 | 19.3% | 19.3% | 64.54% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
29 | August | 8 | 2024-08-01 | 2024 | FY25 | 31 | 172.6002 | 174.2 |  | 31.8 | 50.3366 | 48997.8 | 335.091 | 83.94% | 5.6194 | 31 | 174.2 | 969.7 | 1580.5742 | 48997.8 | 270907.4 | 19.65% | 19.65% | 22.02% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
30 | September | 9 | 2024-09-01 | 2024 | FY25 | 30 | 178.8993 | 192.1 |  | 31.1999 | 52.2506 | 53326.7 | 335.091 | 82.84% | 6.4033 | 30 | 192.1 | 1161.8 | 1777.5567 | 53326.7 | 324234.1 | 22.1% | 22.1% | 22.03% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
31 | October | 10 | 2024-10-01 | 2024 | FY25 | 31 | 174.6008 | 202.3 |  | 27.1001 | 49.7239 | 55941.2 | 335.091 | 82.52% | 6.5258 | 31 | 202.3 | 1364.1 | 1804.5548 | 55941.2 | 380175.3 | 22.44% | 22.44% | 22.09% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
32 | November | 11 | 2024-11-01 | 2024 | FY25 | 30 | 133.6994 | 162.9 |  | 20.9 | 42.1871 | 47411.9 | 335.091 | 86.86% | 5.43 | 30 | 162.9 | 1527 | 1580.3967 | 47411.9 | 427587.2 | 19.65% | 19.65% | 21.79% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
33 | December | 12 | 2024-12-01 | 2024 | FY25 | 31 | 124.4 | 158.6 |  | 15.8915 | 36.0769 | 47221.3 | 335.091 | 88.85% | 5.1161 | 31 | 158.6 | 1685.6 | 1523.2677 | 47221.3 | 474808.5 | 18.94% | 18.94% | 21.47% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
34 | January | 1 | 2025-01-01 | 2025 | FY25 | 31 | 133.8993 | 169.0285 |  | 14.3999 | 34.9703 | 50133.1 | 335.091 | 88.51% | 5.4525 | 31 | 169.0285 | 1854.6285 | 1617.1968 | 50133.1 | 524941.6 | 20.11% | 20.11% | 21.33% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
35 | February | 2 | 2025-02-01 | 2025 | FY25 | 28 | 145.4008 | 172.5591 |  | 17.8001 | 40.2521 | 49142.5 | 335.091 | 84.99% | 6.1628 | 28 | 172.5591 | 2027.1877 | 1755.0893 | 49142.5 | 574084.1 | 21.82% | 21.82% | 21.37% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
36 | March | 3 | 2025-03-01 | 2025 | FY25 | 31 | 195.5989 | 215.7458 |  | 23.6002 | 47.1796 | 59189.3 | 335.091 | 81.87% | 6.9595 | 31 | 215.7458 | 2242.9334 | 1909.3323 | 59189.3 | 633273.4 | 23.74% | 23.74% | 21.57% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
37 | April | 4 | 2025-04-01 | 2025 | FY26 | 30 | 208.9997 | 215.9 |  | 29.1001 | 52.2965 | 58341.8915 | 335.091 | 80.64% | 7.1967 | 30 | 215.9 | 215.9 | 1944.7297 | 58341.8915 | 58341.8915 | 24.18% | 24.18% | 24.18% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
38 | May | 5 | 2025-05-01 | 2025 | FY26 | 31 | 221.9002 | 217.9 |  | 33.4 | 55.4377 | 59688.0938 | 335.091 | 81.75% | 7.029 | 31 | 217.9 | 433.8 | 1925.4224 | 59688.0938 | 118029.9853 | 23.94% | 23.94% | 24.06% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
39 | June | 6 | 2025-06-01 | 2025 | FY26 | 30 | 200.2009 | 192.8 |  | 34.8001 | 54.6583 | 53615.6559 | 335.091 | 82.99% | 6.4267 | 30 | 192.8 | 626.6 | 1787.1885 | 53615.6559 | 171645.6412 | 22.22% | 22.22% | 23.45% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
40 | July | 7 | 2025-07-01 | 2025 | FY26 | 31 | 173.5997 | 168.9 |  | 33.0999 | 51.5649 | 47542.2495 | 335.091 | 84% | 5.4484 | 14 | 76.2774 | 702.8774 | 1533.621 | 21470.6933 | 193116.3345 | 19.07% | 19.07% | 22.87% | 335.0909 | 335.0909 |  |  |  | 99.75% | 99.75%
41 | August | 8 | 2025-08-01 | 2025 | FY26 | 31 | 172.6002 | 174.2 |  | 31.8 | 50.3366 | 48401.3009 | 335.091 | 82.92% | 5.6194 | 0 | 0 | 702.8774 | 1561.3323 | 0 | 193116.3345 | 19.41% |  | 22.87% |  | 335.0909 |  |  |  | 99.75% | 99.75%
42 | September | 9 | 2025-09-01 | 2025 | FY26 | 30 | 178.8993 | 192.1 |  | 31.1999 | 52.2506 | 52670.4088 | 335.091 | 81.82% | 6.4033 | 0 | 0 | 702.8774 | 1755.6803 | 0 | 193116.3345 | 21.83% |  | 22.87% |  | 335.0909 |  |  |  | 99.75% | 99.75%
43 | October | 10 | 2025-10-01 | 2025 | FY26 | 31 | 174.6008 | 202.3 |  | 27.1001 | 49.7239 | 55260.1534 | 335.091 | 81.52% | 6.5258 | 0 | 0 | 702.8774 | 1782.5856 | 0 | 193116.3345 | 22.17% |  | 22.87% |  | 335.0909 |  |  |  | 99.75% | 99.75%
44 | November | 11 | 2025-11-01 | 2025 | FY26 | 30 | 133.6994 | 162.9 |  | 20.9 | 42.1871 | 46828.4717 | 335.091 | 85.79% | 5.43 | 0 | 0 | 702.8774 | 1560.9491 | 0 | 193116.3345 | 19.41% |  | 22.87% |  | 335.0909 |  |  |  | 99.75% | 99.75%
45 | December | 12 | 2025-12-01 | 2025 | FY26 | 31 | 124.4 | 158.6 |  | 15.8915 | 36.0769 | 46646.3954 | 335.091 | 87.77% | 5.1161 | 0 | 0 | 702.8774 | 1504.7224 | 0 | 193116.3345 | 18.71% |  | 22.87% |  | 335.0909 |  |  |  | 99.75% | 99.75%
46 | January | 1 | 2026-01-01 | 2026 | FY26 | 31 | 133.8993 | 169.0285 |  | 14.3999 | 34.9703 | 49522.8134 | 335.091 | 87.43% | 5.4525 | 0 | 0 | 702.8774 | 1597.5101 | 0 | 193116.3345 | 19.86% |  | 22.87% |  | 335.0909 |  |  |  | 99.75% | 99.75%
47 | February | 2 | 2026-02-01 | 2026 | FY26 | 28 | 145.4008 | 172.5591 |  | 17.8001 | 40.2521 | 48840.9958 | 335.091 | 84.47% | 6.1628 | 0 | 0 | 702.8774 | 1744.3213 | 0 | 193116.3345 | 21.69% |  | 22.87% |  | 335.0909 |  |  |  | 99.75% | 99.75%
48 | March | 3 | 2026-03-01 | 2026 | FY26 | 31 | 195.5989 | 215.7458 |  | 23.6002 | 47.1796 | 58468.7638 | 335.091 | 80.88% | 6.9595 | 0 | 0 | 702.8774 | 1886.0892 | 0 | 193116.3345 | 23.45% |  | 22.87% |  | 335.0909 |  |  |  | 99.75% | 99.75%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## Sheet1 (hidden)
Generation loss Due to Load Shedding
Sr. No | Date | From | To | Generation loss(Kwh)
1 | 2023-06-08 | 11:48 | 14:42 | 58633.975
2 | 2023-06-09 | 10:30 | 11:00 | 17357.35
3 | 2023-06-09 | 11:00 | 15:42 | 342913.5
4 | 2023-06-10 | 10:00 | 15:19 | 349821.8218
5 | 2023-06-11 | 10:38 | 15:30 | 310738.9
6 | 2023-06-12 | 10:58 | 15:10 | 316525.9455
7 | 2023-06-13 | 10:23 | 14:42 | 316183.5606
8 | 2023-06-14 | 11:05 | 13:50 | 144889.3388
9 | 2023-06-15 | 12:00 | 12:21 | 9003.0802
10 | 2023-06-20 | 11:06 | 15:12 | 156831.8791
11 | 2023-06-22 | 11:12 | 11:34 | 6931.8371
12 | 2023-06-22 | 11:34 | 15:50 | 145514.9291
13 | 2023-06-23 | 10:16 | 12:15 | 73239.55
14 | 2023-06-23 | 12:15 | 13:46 | 94618.725
15 | 2023-06-23 | 13:46 | 15:20 | 58845.65
16 | 2023-06-24 | 12:35 | 14:00 | 28576.125
17 | 2023-07-01 | 12:17 | 13:35 | 40031.7456
18 | 2023-07-13 | 13:46 | 15:11 | 37769.5908
19 | 2023-07-15 | 10:56 | 12:33 | 62318.771
20 | 2023-07-15 | 12:33 | 15:35 | 179913.2184

## CSPPL_PVS (hidden)
Year Number | OP. year | Year Number | Month | POA(kWh/m2) | GHI (kWh/m2) | Budgeted Energy (MWh) | Tmod | Irradiationce Losses (IAM+NearShadding+Solining) | Bifacial Gain | Temperature Loss | Mismatch Loss | DC Ohmic Loss | Inverter Conversion Loss | MPPT Mismatch Losse | AC Ohmic Loss | Clipping Loss | Plant Uptime | Grid Uptime | Tracker Uptime
Year-0 | 0 | Year-0 | Apr | 215.9 | 208.9997 | 59637.6 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0% |  | YOY Degradation(2nd Year Onwards) | 0.45%
Year-0 | 0 | Year-0 | May | 217.9 | 221.9002 | 61013.7 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0% |  | DC Capacity | 335.096
Year-0 | 0 | Year-0 | Jun | 192.8 | 200.2009 | 54806.4 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Jul | 168.9 | 173.5997 | 48598.11 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Aug | 174.2 | 172.6002 | 49476.24 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Sep | 192.1 | 178.8993 | 53840.16 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Oct | 202.3 | 174.6008 | 56487.42 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Nov | 162.9 | 133.6994 | 47868.48 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Dec | 158.6 | 124.4 | 47682.36 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Jan | 169.0285 | 133.8993 | 50622.66 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Feb | 172.5591 | 145.4008 | 49925.7 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-0 | 0 | Year-0 | Mar | 215.7458 | 195.5989 | 59767.29 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-04-01 | 215.9 | 208.9997 | 59637.6 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-05-01 | 217.9 | 221.9002 | 61013.7 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-06-01 | 192.8 | 200.2009 | 54806.4 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-07-01 | 168.9 | 173.5997 | 48598.11 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-08-01 | 174.2 | 172.6002 | 49476.24 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-09-01 | 192.1 | 178.8993 | 53840.16 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-10-01 | 202.3 | 174.6008 | 56487.42 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-11-01 | 162.9 | 133.6994 | 47868.48 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2022-12-01 | 158.6 | 124.4 | 47682.36 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2023-01-01 | 169.0285 | 133.8993 | 50622.66 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2023-02-01 | 172.5591 | 145.4008 | 49925.7 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-1 | 1 | Year-1 | 2023-03-01 | 215.7458 | 195.5989 | 59767.29 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-04-01 | 215.9 | 208.9997 | 58630 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-05-01 | 217.9 | 221.9002 | 61780 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-06-01 | 192.8 | 200.2009 | 53700 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-07-01 | 168.9 | 173.5997 | 49210 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-08-01 | 174.2 | 172.6002 | 50100 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-09-01 | 192.1 | 178.8993 | 52760 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-10-01 | 202.3 | 174.6008 | 57190 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2023-11-01 | 162.9 | 133.6994 | 46900 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0% | 1000
Year-2 | 2 | Year-2 | 2023-12-01 | 158.6 | 124.4 | 48280 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2024-01-01 | 169.0285 | 133.8993 | 51260 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2024-02-01 | 172.5591 | 145.4008 | 47290 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-2 | 2 | Year-2 | 2024-03-01 | 215.7458 | 195.5989 | 60510 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-04-01 | 215.9 | 208.9997 | 58366.165 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-05-01 | 217.9 | 221.9002 | 61501.99 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-06-01 | 192.8 | 200.2009 | 53458.35 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-07-01 | 168.9 | 173.5997 | 48988.555 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-08-01 | 174.2 | 172.6002 | 49874.55 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-09-01 | 192.1 | 178.8993 | 52522.58 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-10-01 | 202.3 | 174.6008 | 56932.645 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-11-01 | 162.9 | 133.6994 | 46688.95 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2024-12-01 | 158.6 | 124.4 | 48062.74 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2025-01-01 | 169.0285 | 133.8993 | 51029.33 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2025-02-01 | 172.5591 | 145.4008 | 47077.195 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-3 | 3 | Year-3 | 2025-03-01 | 215.7458 | 195.5989 | 60237.705 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-04-01 | 215.9 | 208.9997 | 58103.5173 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-05-01 | 217.9 | 221.9002 | 61225.231 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-06-01 | 192.8 | 200.2009 | 53217.7874 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-07-01 | 168.9 | 173.5997 | 48768.1065 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-08-01 | 174.2 | 172.6002 | 49650.1145 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-09-01 | 192.1 | 178.8993 | 52286.2284 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-10-01 | 202.3 | 174.6008 | 56676.4481 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-11-01 | 162.9 | 133.6994 | 46478.8497 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2025-12-01 | 158.6 | 124.4 | 47846.4577 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2026-01-01 | 169.0285 | 133.8993 | 50799.698 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2026-02-01 | 172.5591 | 145.4008 | 46865.3476 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-4 | 4 | Year-4 | 2026-03-01 | 215.7458 | 195.5989 | 59966.6353 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-04-01 | 215.9 | 208.9997 | 57842.0514 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-05-01 | 217.9 | 221.9002 | 60949.7175 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-06-01 | 192.8 | 200.2009 | 52978.3074 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-07-01 | 168.9 | 173.5997 | 48548.65 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-08-01 | 174.2 | 172.6002 | 49426.689 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-09-01 | 192.1 | 178.8993 | 52050.9404 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-10-01 | 202.3 | 174.6008 | 56421.4041 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-11-01 | 162.9 | 133.6994 | 46269.6949 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2026-12-01 | 158.6 | 124.4 | 47631.1486 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2027-01-01 | 169.0285 | 133.8993 | 50571.0994 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2027-02-01 | 172.5591 | 145.4008 | 46654.4536 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-5 | 5 | Year-5 | 2027-03-01 | 215.7458 | 195.5989 | 59696.7855 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-04-01 | 215.9 | 208.9997 | 57581.7622 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-05-01 | 217.9 | 221.9002 | 60675.4438 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-06-01 | 192.8 | 200.2009 | 52739.905 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-07-01 | 168.9 | 173.5997 | 48330.1811 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-08-01 | 174.2 | 172.6002 | 49204.2689 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-09-01 | 192.1 | 178.8993 | 51816.7111 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-10-01 | 202.3 | 174.6008 | 56167.5078 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-11-01 | 162.9 | 133.6994 | 46061.4813 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2027-12-01 | 158.6 | 124.4 | 47416.8084 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2028-01-01 | 169.0285 | 133.8993 | 50343.5294 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2028-02-01 | 172.5591 | 145.4008 | 46444.5085 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-6 | 6 | Year-6 | 2028-03-01 | 215.7458 | 195.5989 | 59428.1499 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-04-01 | 215.9 | 208.9997 | 57322.6443 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-05-01 | 217.9 | 221.9002 | 60402.4043 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-06-01 | 192.8 | 200.2009 | 52502.5754 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-07-01 | 168.9 | 173.5997 | 48112.6953 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-08-01 | 174.2 | 172.6002 | 48982.8497 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-09-01 | 192.1 | 178.8993 | 51583.5359 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-10-01 | 202.3 | 174.6008 | 55914.754 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-11-01 | 162.9 | 133.6994 | 45854.2046 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2028-12-01 | 158.6 | 124.4 | 47203.4328 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2029-01-01 | 169.0285 | 133.8993 | 50116.9835 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2029-02-01 | 172.5591 | 145.4008 | 46235.5082 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-7 | 7 | Year-7 | 2029-03-01 | 215.7458 | 195.5989 | 59160.7233 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-04-01 | 215.9 | 208.9997 | 57064.6924 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-05-01 | 217.9 | 221.9002 | 60130.5935 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-06-01 | 192.8 | 200.2009 | 52266.3138 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-07-01 | 168.9 | 173.5997 | 47896.1882 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-08-01 | 174.2 | 172.6002 | 48762.4269 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-09-01 | 192.1 | 178.8993 | 51351.41 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-10-01 | 202.3 | 174.6008 | 55663.1376 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-11-01 | 162.9 | 133.6994 | 45647.8607 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2029-12-01 | 158.6 | 124.4 | 46991.0174 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2030-01-01 | 169.0285 | 133.8993 | 49891.4571 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2030-02-01 | 172.5591 | 145.4008 | 46027.4484 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-8 | 8 | Year-8 | 2030-03-01 | 215.7458 | 195.5989 | 58894.5 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-04-01 | 215.9 | 208.9997 | 56807.9013 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-05-01 | 217.9 | 221.9002 | 59860.0058 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-06-01 | 192.8 | 200.2009 | 52031.1154 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-07-01 | 168.9 | 173.5997 | 47680.6553 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-08-01 | 174.2 | 172.6002 | 48542.996 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-09-01 | 192.1 | 178.8993 | 51120.3287 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-10-01 | 202.3 | 174.6008 | 55412.6535 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-11-01 | 162.9 | 133.6994 | 45442.4453 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2030-12-01 | 158.6 | 124.4 | 46779.5578 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2031-01-01 | 169.0285 | 133.8993 | 49666.9456 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2031-02-01 | 172.5591 | 145.4008 | 45820.3249 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-9 | 9 | Year-9 | 2031-03-01 | 215.7458 | 195.5989 | 58629.4748 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-04-01 | 215.9 | 208.9997 | 56552.2657 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-05-01 | 217.9 | 221.9002 | 59590.6358 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-06-01 | 192.8 | 200.2009 | 51796.9754 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-07-01 | 168.9 | 173.5997 | 47466.0924 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-08-01 | 174.2 | 172.6002 | 48324.5525 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-09-01 | 192.1 | 178.8993 | 50890.2872 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-10-01 | 202.3 | 174.6008 | 55163.2965 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-11-01 | 162.9 | 133.6994 | 45237.9543 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2031-12-01 | 158.6 | 124.4 | 46569.0498 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2032-01-01 | 169.0285 | 133.8993 | 49443.4443 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2032-02-01 | 172.5591 | 145.4008 | 45614.1335 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-10 | 10 | Year-10 | 2032-03-01 | 215.7458 | 195.5989 | 58365.6421 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-04-01 | 215.9 | 208.9997 | 56297.7805 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-05-01 | 217.9 | 221.9002 | 59322.4779 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-06-01 | 192.8 | 200.2009 | 51563.889 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-07-01 | 168.9 | 173.5997 | 47252.4949 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-08-01 | 174.2 | 172.6002 | 48107.092 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-09-01 | 192.1 | 178.8993 | 50661.2809 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-10-01 | 202.3 | 174.6008 | 54915.0617 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-11-01 | 162.9 | 133.6994 | 45034.3835 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2032-12-01 | 158.6 | 124.4 | 46359.489 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2033-01-01 | 169.0285 | 133.8993 | 49220.9488 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2033-02-01 | 172.5591 | 145.4008 | 45408.8699 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-11 | 11 | Year-11 | 2033-03-01 | 215.7458 | 195.5989 | 58102.9967 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-04-01 | 215.9 | 208.9997 | 56044.4405 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-05-01 | 217.9 | 221.9002 | 59055.5268 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-06-01 | 192.8 | 200.2009 | 51331.8515 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-07-01 | 168.9 | 173.5997 | 47039.8587 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-08-01 | 174.2 | 172.6002 | 47890.6101 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-09-01 | 192.1 | 178.8993 | 50433.3051 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-10-01 | 202.3 | 174.6008 | 54667.9439 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-11-01 | 162.9 | 133.6994 | 44831.7288 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2033-12-01 | 158.6 | 124.4 | 46150.8713 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2034-01-01 | 169.0285 | 133.8993 | 48999.4545 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2034-02-01 | 172.5591 | 145.4008 | 45204.5299 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-12 | 12 | Year-12 | 2034-03-01 | 215.7458 | 195.5989 | 57841.5332 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-04-01 | 215.9 | 208.9997 | 55792.2405 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-05-01 | 217.9 | 221.9002 | 58789.7769 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-06-01 | 192.8 | 200.2009 | 51100.8582 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-07-01 | 168.9 | 173.5997 | 46828.1794 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-08-01 | 174.2 | 172.6002 | 47675.1023 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-09-01 | 192.1 | 178.8993 | 50206.3553 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-10-01 | 202.3 | 174.6008 | 54421.9382 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-11-01 | 162.9 | 133.6994 | 44629.986 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2034-12-01 | 158.6 | 124.4 | 45943.1924 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2035-01-01 | 169.0285 | 133.8993 | 48778.957 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2035-02-01 | 172.5591 | 145.4008 | 45001.1096 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-13 | 13 | Year-13 | 2035-03-01 | 215.7458 | 195.5989 | 57581.2463 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-04-01 | 215.9 | 208.9997 | 55541.1754 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-05-01 | 217.9 | 221.9002 | 58525.2229 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-06-01 | 192.8 | 200.2009 | 50870.9043 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-07-01 | 168.9 | 173.5997 | 46617.4525 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-08-01 | 174.2 | 172.6002 | 47460.5644 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-09-01 | 192.1 | 178.8993 | 49980.4267 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-10-01 | 202.3 | 174.6008 | 54177.0394 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-11-01 | 162.9 | 133.6994 | 44429.1511 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2035-12-01 | 158.6 | 124.4 | 45736.4481 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2036-01-01 | 169.0285 | 133.8993 | 48559.4517 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2036-02-01 | 172.5591 | 145.4008 | 44798.6046 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-14 | 14 | Year-14 | 2036-03-01 | 215.7458 | 195.5989 | 57322.1307 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-04-01 | 215.9 | 208.9997 | 55291.2401 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-05-01 | 217.9 | 221.9002 | 58261.8594 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-06-01 | 192.8 | 200.2009 | 50641.9853 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-07-01 | 168.9 | 173.5997 | 46407.674 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-08-01 | 174.2 | 172.6002 | 47246.9918 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-09-01 | 192.1 | 178.8993 | 49755.5147 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-10-01 | 202.3 | 174.6008 | 53933.2428 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-11-01 | 162.9 | 133.6994 | 44229.2199 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2036-12-01 | 158.6 | 124.4 | 45530.634 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2037-01-01 | 169.0285 | 133.8993 | 48340.9342 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2037-02-01 | 172.5591 | 145.4008 | 44597.0108 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-15 | 15 | Year-15 | 2037-03-01 | 215.7458 | 195.5989 | 57064.1811 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-04-01 | 215.9 | 208.9997 | 55042.4296 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-05-01 | 217.9 | 221.9002 | 57999.681 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-06-01 | 192.8 | 200.2009 | 50414.0963 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-07-01 | 168.9 | 173.5997 | 46198.8395 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-08-01 | 174.2 | 172.6002 | 47034.3804 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-09-01 | 192.1 | 178.8993 | 49531.6149 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-10-01 | 202.3 | 174.6008 | 53690.5432 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-11-01 | 162.9 | 133.6994 | 44030.1884 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2037-12-01 | 158.6 | 124.4 | 45325.7462 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2038-01-01 | 169.0285 | 133.8993 | 48123.3999 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2038-02-01 | 172.5591 | 145.4008 | 44396.3243 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-16 | 16 | Year-16 | 2038-03-01 | 215.7458 | 195.5989 | 56807.3923 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-04-01 | 215.9 | 208.9997 | 54794.7386 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-05-01 | 217.9 | 221.9002 | 57738.6825 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-06-01 | 192.8 | 200.2009 | 50187.2329 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-07-01 | 168.9 | 173.5997 | 45990.9447 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-08-01 | 174.2 | 172.6002 | 46822.7257 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-09-01 | 192.1 | 178.8993 | 49308.7227 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-10-01 | 202.3 | 174.6008 | 53448.9357 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-11-01 | 162.9 | 133.6994 | 43832.0526 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2038-12-01 | 158.6 | 124.4 | 45121.7803 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2039-01-01 | 169.0285 | 133.8993 | 47906.8446 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2039-02-01 | 172.5591 | 145.4008 | 44196.5408 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-17 | 17 | Year-17 | 2039-03-01 | 215.7458 | 195.5989 | 56551.7591 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-04-01 | 215.9 | 208.9997 | 54548.1623 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-05-01 | 217.9 | 221.9002 | 57478.8584 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-06-01 | 192.8 | 200.2009 | 49961.3903 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-07-01 | 168.9 | 173.5997 | 45783.9854 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-08-01 | 174.2 | 172.6002 | 46612.0234 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-09-01 | 192.1 | 178.8993 | 49086.8334 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-10-01 | 202.3 | 174.6008 | 53208.4155 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-11-01 | 162.9 | 133.6994 | 43634.8083 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2039-12-01 | 158.6 | 124.4 | 44918.7323 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2040-01-01 | 169.0285 | 133.8993 | 47691.2638 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2040-02-01 | 172.5591 | 145.4008 | 43997.6564 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-18 | 18 | Year-18 | 2040-03-01 | 215.7458 | 195.5989 | 56297.2762 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-04-01 | 215.9 | 208.9997 | 54302.6956 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-05-01 | 217.9 | 221.9002 | 57220.2035 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-06-01 | 192.8 | 200.2009 | 49736.5641 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-07-01 | 168.9 | 173.5997 | 45577.9575 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-08-01 | 174.2 | 172.6002 | 46402.2693 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-09-01 | 192.1 | 178.8993 | 48865.9427 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-10-01 | 202.3 | 174.6008 | 52968.9776 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-11-01 | 162.9 | 133.6994 | 43438.4517 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2040-12-01 | 158.6 | 124.4 | 44716.598 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2041-01-01 | 169.0285 | 133.8993 | 47476.6532 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2041-02-01 | 172.5591 | 145.4008 | 43799.667 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-19 | 19 | Year-19 | 2041-03-01 | 215.7458 | 195.5989 | 56043.9384 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-04-01 | 215.9 | 208.9997 | 54058.3334 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-05-01 | 217.9 | 221.9002 | 56962.7126 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-06-01 | 192.8 | 200.2009 | 49512.7495 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-07-01 | 168.9 | 173.5997 | 45372.8567 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-08-01 | 174.2 | 172.6002 | 46193.4591 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-09-01 | 192.1 | 178.8993 | 48646.0459 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-10-01 | 202.3 | 174.6008 | 52730.6172 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-11-01 | 162.9 | 133.6994 | 43242.9787 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2041-12-01 | 158.6 | 124.4 | 44515.3733 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2042-01-01 | 169.0285 | 133.8993 | 47263.0082 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2042-02-01 | 172.5591 | 145.4008 | 43602.5685 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-20 | 20 | Year-20 | 2042-03-01 | 215.7458 | 195.5989 | 55791.7407 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-04-01 | 215.9 | 208.9997 | 53815.0709 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-05-01 | 217.9 | 221.9002 | 56706.3804 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-06-01 | 192.8 | 200.2009 | 49289.9422 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-07-01 | 168.9 | 173.5997 | 45168.6788 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-08-01 | 174.2 | 172.6002 | 45985.5885 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-09-01 | 192.1 | 178.8993 | 48427.1387 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-10-01 | 202.3 | 174.6008 | 52493.3295 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-11-01 | 162.9 | 133.6994 | 43048.3852 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2042-12-01 | 158.6 | 124.4 | 44315.0542 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2043-01-01 | 169.0285 | 133.8993 | 47050.3247 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2043-02-01 | 172.5591 | 145.4008 | 43406.3569 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-21 | 21 | Year-21 | 2043-03-01 | 215.7458 | 195.5989 | 55540.6779 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-04-01 | 215.9 | 208.9997 | 53572.9031 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-05-01 | 217.9 | 221.9002 | 56451.2017 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-06-01 | 192.8 | 200.2009 | 49068.1374 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-07-01 | 168.9 | 173.5997 | 44965.4198 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-08-01 | 174.2 | 172.6002 | 45778.6534 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-09-01 | 192.1 | 178.8993 | 48209.2166 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-10-01 | 202.3 | 174.6008 | 52257.1095 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-11-01 | 162.9 | 133.6994 | 42854.6675 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2043-12-01 | 158.6 | 124.4 | 44115.6364 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2044-01-01 | 169.0285 | 133.8993 | 46838.5982 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2044-02-01 | 172.5591 | 145.4008 | 43211.0283 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-22 | 22 | Year-22 | 2044-03-01 | 215.7458 | 195.5989 | 55290.7448 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-04-01 | 215.9 | 208.9997 | 53331.8251 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-05-01 | 217.9 | 221.9002 | 56197.1713 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-06-01 | 192.8 | 200.2009 | 48847.3308 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-07-01 | 168.9 | 173.5997 | 44763.0754 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-08-01 | 174.2 | 172.6002 | 45572.6494 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-09-01 | 192.1 | 178.8993 | 47992.2751 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-10-01 | 202.3 | 174.6008 | 52021.9525 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-11-01 | 162.9 | 133.6994 | 42661.8215 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2044-12-01 | 158.6 | 124.4 | 43917.116 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2045-01-01 | 169.0285 | 133.8993 | 46627.8245 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2045-02-01 | 172.5591 | 145.4008 | 43016.5787 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-23 | 23 | Year-23 | 2045-03-01 | 215.7458 | 195.5989 | 55041.9364 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-04-01 | 215.9 | 208.9997 | 53091.8318 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-05-01 | 217.9 | 221.9002 | 55944.284 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-06-01 | 192.8 | 200.2009 | 48627.5178 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-07-01 | 168.9 | 173.5997 | 44561.6416 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-08-01 | 174.2 | 172.6002 | 45367.5725 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-09-01 | 192.1 | 178.8993 | 47776.3099 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-10-01 | 202.3 | 174.6008 | 51787.8537 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-11-01 | 162.9 | 133.6994 | 42469.8433 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2045-12-01 | 158.6 | 124.4 | 43719.489 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2046-01-01 | 169.0285 | 133.8993 | 46417.9993 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2046-02-01 | 172.5591 | 145.4008 | 42823.0041 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-24 | 24 | Year-24 | 2046-03-01 | 215.7458 | 195.5989 | 54794.2477 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-04-01 | 215.9 | 208.9997 | 52852.9186 | 52.2965 | 1.666% | 29% | 11.72% | 1.523% | 1.611% | 1.863% | 0% | 2.28% | 2.8% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-05-01 | 217.9 | 221.9002 | 55692.5347 | 55.4377 | 1.787% | 30% | 13.07% | 1.609% | 1.525% | 1.576% | 0% | 2.228% | 1.12% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-06-01 | 192.8 | 200.2009 | 48408.694 | 54.6583 | 1.914% | 30% | 12.65% | 1.64% | 1.393% | 1.406% | 0% | 2.168% | 0.4052% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-07-01 | 168.9 | 173.5997 | 44361.1142 | 51.5649 | 2.185% | 28% | 10.89% | 1.587% | 1.232% | 1.35% | 0% | 2.127% | 0.1556% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-08-01 | 174.2 | 172.6002 | 45163.4184 | 50.3366 | 2.02% | 27% | 10.49% | 1.508% | 1.279% | 1.412% | 0% | 2.157% | 0.6282% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-09-01 | 192.1 | 178.8993 | 47561.3165 | 52.2506 | 1.72% | 26% | 11.39% | 1.396% | 1.453% | 1.448% | 0% | 2.247% | 1.139% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-10-01 | 202.3 | 174.6008 | 51554.8084 | 49.7239 | 1.587% | 27% | 10.39% | 1.404% | 1.526% | 1.532% | 0% | 2.304% | 2.118% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-11-01 | 162.9 | 133.6994 | 42278.729 | 42.1871 | 1.595% | 27% | 6.902% | 1.42% | 1.325% | 1.398% | 0% | 2.302% | 0.8348% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2046-12-01 | 158.6 | 124.4 | 43522.7513 | 36.0769 | 1.58% | 27% | 4.479% | 1.414% | 1.237% | 1.396% | 0% | 2.306% | 0.3698% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2047-01-01 | 169.0285 | 133.8993 | 46209.1183 | 34.9703 | 1.72% | 27% | 4.003% | 1.41% | 1.268% | 1.39% | 0% | 2.298% | 1.064% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2047-02-01 | 172.5591 | 145.4008 | 42630.3005 | 40.2521 | 1.511% | 27% | 6.211% | 1.418% | 1.438% | 1.592% | 0% | 2.327% | 2.505% | 99.5% | 99.5% | 0%
Year-25 | 25 | Year-25 | 2047-03-01 | 215.7458 | 195.5989 | 54547.6736 | 47.1796 | 1.531% | 28% | 9.442% | 1.464% | 1.621% | 2.072% | 0% | 2.325% | 3.922% | 99.5% | 99.5% | 0%