## Dashboard
Performance Summary of JPPL Assam as on date and YTD
Month | 2025-06-01
Date | 2025-07-06
Operation Year | FY26
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 312.1483 | 242 | -22.47%
| E_Grid MTD(MWh) | 9261.3973 | 9996 | 7.932%
| E_Grid YTD (MWh) | 29481.6914 | 30826 | 4.56%
2 | CUF Daily(%) | 14.24% | 11.04% | -22.47%
| CUF MTD(%) | 70.43% | 76.01% | 7.932%
| CUF YTD(%) | 13.87% | 14.5% | 4.56%
3 | PR_Daily (%) | 78.84% | 80.8% | 2.486% | Cloudy Weathear & Radition Fluctution,Only MCR Pyranometer data avaliable, other 3nos pyranometer opened due to send for Calibration.
| PR_MTD (%) | 78.19% | 79.8% | 2.057%
| PR_YTD (%) | 79.32% | 80.94% | 2.04%
4 | POA Daily (KWh/m2) | 4.3355 | 3.26 | -24.81% | Only MCR Pyranometer data avaliable, other 3nos pyranometer opened due to send for Calibration.
| POA MTD(KWh/m2) | 129.7 | 137.1665 | 5.757%
| POA YTD(KWh/m2) | 407 | 417.0522 | 2.47%
5 | PA Daily | 99.75% | 99.9% | 0.1538%
| PA MTD | 99.75% | 99.89% | 0.1376%
| PA YTD | 99.75% | 99.72% | -0.03442%
6 | GA Daily | 99.75% | 100% | 0.2506%
| GA MTD | 99.75% | 100% | 0.2506%
| GA YTD | 99.75% | 100% | 0.2506%
7 | WPR_Daily | 78.84%
| WPR_MTD | 78.19%
| WPR_YTD | 79.32%

## Annual_KPI
Till Date | 2025-07-06 | 2025-06-01
Jakson Power Private Limited (70MW) Private Limited Performance Summary-YTD
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
1905-07-18 | 97 | 407 | 417.0522 | 29481.6914 | 30826 | 79.32% | 80.94% | 13.87% | 14.5% | 99.5% | 100% | 99.5% | 99.72% | 0 | 0
Jakson Power Private Limited (70MW) Private Limited Performance Summary Month Wise
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-04-01 | 30 | 136.5 | 131.185 | 9969.4971 | 9810 | 79.98% | 81.89% | 15.16% | 14.92% | 99.75% | 100% | 99.75% | 99.29% | 0 | 0
2025-05-01 | 31 | 140.8 | 121.3207 | 10250.797 | 9090 | 79.72% | 82.05% | 15.09% | 13.38% | 99.75% | 100% | 99.75% | 99.92% | 0 | 0
2025-06-01 | 30 | 129.7 | 137.1665 | 9261.3973 | 9996 | 78.19% | 79.8% | 14.09% | 15.2% | 99.75% | 100% | 99.75% | 99.89% | 0 | 0
2025-07-01 | 6 | 26.0129 | 27.38 | 1872.8898 | 1930 | 78.84% | 77.19% | 14.24% | 14.68% | 99.75% | 100% | 99.75% | 99.97% | 0 | 0
2025-08-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0
2025-09-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0
2025-10-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0
2025-11-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0
2025-12-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0
2026-01-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0
2026-02-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0
2026-03-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.75% |  | 99.75% |  | 0 | 0

## Monthly_KPI
Till Date | 2025-07-06
Jakson Power Private Limited (70 MW) Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-06-01 | 6 | 129.7 | 137.1665 | 9261.3973 | 9996 | 78.19% | 79.8% | 70.43% | 76.01% | 99.75% | 100% | 99.75% | 99.89% | 0 | 0
Start Date | 2025-06-30
End Date | 2025-07-06
Jakson Power Private Limited (70 MW) Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-06-01 | 7 | 30.3362 | 33.11 | 2181.603 | 2336 | 78.75% | 77.26% | 14.22% | 15.23% | 99.75% | 100% | 99.75% | 99.98% | 0 | 0
Formulas:
Days = [Days, row below]-6

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 11.1667 | 2.11 |  | 2.03 |  | 0 | 27.78 | 0 | 0 | [9 empty] | 159590.4 |  |  |  | 91.87 | 4.7903 | 352764.5161 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 11.4833 | 4.76 |  | 4.8 |  | 0 | 35.32 | 0 | 0 | 100% |  |  | 100% |  |  | 82.09% |  | 16.52% | 370480.6 | 362000 |  | 362000 | 91.87 | 4.7903 | 352764.5161 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 11.3 | 4.69 |  | 4.77 |  | 0 | 35.81 | 0 | 0 | 100% |  |  | 100% |  |  | 82.15% |  | 16.43% | 364659.4 | 360000 |  | 360000 | 91.87 | 4.7903 | 352764.5161 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 12.05 | 4.76 |  | 4.88 |  | 0 | 35.18 | 0 | 0 | 100% |  |  | 100% |  |  | 79.85% |  | 16.33% | 364755.5 | 358000 |  | 358000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 11.3333 | 3.73 |  | 3.7 |  | 0 | 33.29 | 0 | 0 | 99.46% |  |  | 100% |  |  | 82.96% |  | 12.87% | 289746.9 | 282000 |  | 282000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 11.4167 | 4.77 |  | 4.81 |  | 0 | 36.62 | 0 | 0 | 100% |  |  | 100% |  |  | 81.92% |  | 16.52% | 369831.2 | 362000 |  | 362000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 11.5 | 3.91 |  | 3.84 |  | 0 | 34.17 | 0 | 0 | 98.8% |  |  | 100% |  |  | 83.34% |  | 13.41% | 303045.9 | 294000 |  | 294000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 11.75 | 5.03 |  | 5.08 |  | 0 | 37.27 | 0 | 0 | 100% |  |  | 100% |  |  | 82.71% |  | 17.61% | 397002.9 | 386000 |  | 386000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 11.6833 | 4.539 |  | 4.63 |  | 0 | 32.84 | 0 | 0 | 100% |  |  | 100% |  |  | 80.87% |  | 15.7% | 350812.5 | 344000 |  | 344000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 11.7333 | 4.54 |  | 4.48 |  | 0 | 35.7 | 0 | 0 | 100% |  |  | 100% |  |  | 83.09% |  | 15.6% | 349321.6 | 342000 |  | 342000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 11.7833 | 5.58 |  | 5.61 |  | 0 | 39.4 | 0 | 0 | 100% |  |  | 100% |  |  | 79.94% |  | 18.8% | 423540.3 | 412000 |  | 412000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 10.4667 | 2.89 |  | 2.87 |  | 0 | 32.76 | 0 | 0 | 100% |  |  | 100% |  |  | 81.16% |  | 9.764% | 221218.7 | 214000 |  | 214000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 11.6667 | 4.72 |  | 4.67 |  | 0 | 38.33 | 0 | 0 | 100% |  |  | 100% |  |  | 81.11% |  | 15.88% | 356948.5 | 348000 |  | 348000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 11.8833 | 2.55 |  | 2.395 |  | 0 | 29.76 | 0 | 0 | 100% |  |  | 100% |  |  | 87.26% |  | 8.76% | 194808.1 | 192000 |  | 192000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 11.65 | 4.53 |  | 4.47 |  | 0 | 36.04 | 0 | 0 | 99.93% |  |  | 100% |  |  | 82.31% |  | 15.42% | 345096 | 338000 |  | 338000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 11.9833 | 5.5 |  | 5.4 |  | 0 | 37.77 | 0 | 0 | 100% |  |  | 100% |  |  | 81.84% |  | 18.52% | 416596.5995 | 406000 |  | 406000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 12.3667 | 5.19 |  | 5.09 |  | 0 | 38.67 | 0 | 0 | 91.4% |  |  | 100% |  |  | 75.28% |  | 16.06% | 359625 | 352000 |  | 352000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 11.4 | 5.03 |  | 4.92 |  | 0 | 39.89 | 0 | 0 | 91.2% |  |  | 100% |  |  | 73.45% |  | 15.15% | 339780.6 | 332000 |  | 332000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 11.5167 | 4.14 |  | 4.15 |  | 0 | 36.09 | 0 | 0 | 99.04% |  |  | 100% |  |  | 81.83% |  | 14.24% | 320232.1 | 312000 |  | 312000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 11.8167 | 4.99 |  | 4.86 |  | 0 | 37.46 | 0 | 0 | 100% |  |  | 100% |  |  | 80.63% |  | 16.43% | 366898.7 | 360000 |  | 360000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 12.1 | 5.97 |  | 5.77 |  | 0 | 40.77 | 0 | 0 | 100% |  |  | 100% |  |  | 80.36% |  | 19.44% | 436966.5 | 426000 |  | 426000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 11.9833 | 5.73 |  | 5.43 |  | 0 | 41.8 | 0 | 0 | 100% |  |  | 100% |  |  | 80.58% |  | 18.34% | 412752.1 | 402000 |  | 402000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 11.4167 | 3.77 |  | 3.59 |  | 0 | 32.04 | 0 | 0 | 100% |  |  | 100% |  |  | 83.08% |  | 12.5% | 280346.4 | 274000 |  | 274000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 11.9 | 5.15 |  | 5 |  | 0 | 38.05 | 0 | 0 | 100% |  |  | 100% |  |  | 80.55% |  | 16.88% | 379476.4 | 370000 |  | 370000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 10.7333 | 1.06 |  | 0.98 |  | 0 | 26.78 | 0 | 0 | 99.84% |  |  | 100% |  |  | 88.86% |  | 3.65% | 83165.5 | 80000 |  | 80000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 11.85 | 3.45 |  | 3.31 |  | 0 | 33.31 | 0 | 0 | 99.99% |  |  | 100% |  |  | 82.21% |  | 11.41% | 257857.4 | 250000 |  | 250000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 11.65 | 3.85 |  | 3.81 |  | 0 | 31.62 | 0 | 0 | 99.96% |  |  | 100% |  |  | 84.57% |  | 13.51% | 302338.1 | 296000 |  | 296000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 12.1833 | 5.9 |  | 5.6 |  | 0 | 37.02 | 0 | 0 | 100% |  |  | 100% |  |  | 81.25% |  | 19.07% | 430181.3 | 418000 |  | 418000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 12.2833 | 6.02 |  | 5.79 |  | 0 | 37.72 | 0 | 0 | 100% |  |  | 100% |  |  | 81.59% |  | 19.8% | 444233.9 | 434000 |  | 434000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 11.2833 | 6.01 |  | 5.9 |  | 0 | 38.15 | 0 | 0 | 99.59% |  |  | 100% |  |  | 79.33% |  | 19.62% | 442091.5 | 430000 |  | 430000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 11.9167 | 1.78 |  | 1.63 |  | 0 | 25.69 | 0 | 0 | 99.72% |  |  | 100% |  |  | 89.48% |  | 6.114% | 134866.8 | 134000 |  | 134000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 10.9333 | 2.97 |  | 2.76 |  | 0 | 31.02 | 0 | 0 | 99.82% |  |  | 100% |  |  | 88.34% |  | 10.22% | 229985.6 | 224000 |  | 224000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 12.3833 | 6.05 |  | 5.76 |  | 0 | 36.85 | 0 | 0 | 99.83% |  |  | 100% |  |  | 82.77% |  | 19.98% | 449792.7 | 438000 |  | 438000 | 91.87 | 4.55 | 332316.5693 | 79.98% | 15.16% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 12.1333 | 1.99 |  | 1.84 |  | 0 | 29.4 | 0 | 0 | 99.84% |  |  | 100% |  |  | 87.55% |  | 6.753% | 152874.6 | 148000 |  | 148000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 12.3 | 5.32 |  | 5.07 |  | 0 | 35.56 | 0 | 0 | 99.43% |  |  | 100% |  |  | 79.87% |  | 16.97% | 379071.8 | 372000 |  | 372000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 12.4333 | 6.66 |  | 6.3 |  | 0 | 39.53 | 0 | 0 | 99.28% |  |  | 100% |  |  | 77.06% |  | 20.35% | 457274.0003 | 446000 |  | 446000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 12.4167 | 6.23 |  | 5.84 |  | 0 | 39.96 | 0 | 0 | 99.8% |  |  | 100% |  |  | 79.4% |  | 19.44% | 436792.9 | 426000 |  | 426000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 12.3667 | 5.26 |  | 4.93 |  | 0 | 36.63 | 0 | 0 | 99.75% |  |  | 100% |  |  | 79.48% |  | 16.43% | 367064.7 | 360000 |  | 360000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 12.1 | 3.99 |  | 3.74 |  | 0 | 36.28 | 0 | 0 | 99.92% |  |  | 100% |  |  | 80.91% |  | 12.68% | 285034.5 | 278000 |  | 278000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 12.6 | 5.14 |  | 4.91 |  | 0 | 37.26 | 0 | 0 | 99.97% |  |  | 100% |  |  | 81.14% |  | 16.7% | 372286.1 | 366000 |  | 366000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 11.8667 | 3.44 |  | 3.26 |  | 0 | 33.35 | 0 | 0 | 99.97% |  |  | 100% |  |  | 80.13% |  | 10.95% | 248854.6 | 240000 |  | 240000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 12.35 | 5.83 |  | 5.56 |  | 0 | 41.19 | 0 | 0 | 99.97% |  |  | 100% |  |  | 80.27% |  | 18.71% | 421144.6 | 410000 |  | 410000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 12.4667 | 6.12 |  | 5.75 |  | 0 | 42.15 | 0 | 0 | 99.96% |  |  | 100% |  |  | 81.02% |  | 19.53% | 438872.6 | 428000 |  | 428000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 12.1 | 3.46 |  | 3.28 |  | 0 | 33.11 | 0 | 0 | 99.76% |  |  | 100% |  |  | 83.63% |  | 11.5% | 261207.5 | 252000 |  | 252000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 12.4833 | 5.38 |  | 5.12 |  | 0 | 38.47 | 0 | 0 | 99.98% |  |  | 100% |  |  | 79.09% |  | 16.97% | 379993.1 | 372000 |  | 372000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 12.55 | 3.4 |  | 3.23 |  | 0 | 33.39 | 0 | 0 | 99.98% |  |  | 100% |  |  | 82.23% |  | 11.13% | 251049.7 | 244000 |  | 244000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 12.4 | 4.74 |  | 4.52 |  | 0 | 35.24 | 0 | 0 | 99.98% |  |  | 100% |  |  | 81.88% |  | 15.51% | 345926.8 | 340000 |  | 340000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 2.412 |  | 2.2107 |  | 0 | 27.646 | 0 | 0 | 99.98% |  |  | 100% |  |  | 87.64% |  | 8.122% | 184356.7 | 178000 |  | 178000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 12.3333 | 3.76 |  | 3.53 |  | 0 | 32 | 0 | 0 | 99.98% |  |  | 100% |  |  | 84.49% |  | 12.5% | 278251.9 | 274000 |  | 274000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 12.4167 | 3.22 |  | 3 |  | 0 | 30.13 | 0 | 0 | 99.97% |  |  | 100% |  |  | 86.35% |  | 10.86% | 242923.9 | 238000 |  | 238000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 12.1333 | 1.96 |  | 1.79 |  | 0 | 27.2893 | 0 | 0 | 99.99% |  |  | 100% |  |  | 88.78% |  | 6.662% | 147793.8 | 146000 |  | 146000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 10.6333 | 3.97 |  | 3.63 |  | 0 | 34.79 | 0 | 0 | 100% |  |  | 100% |  |  | 85.76% |  | 13.05% | 293791.3 | 286000 |  | 286000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 12.7333 | 2.26 |  | 2.06 |  | 0 | 28.83 | 0 | 0 | 99.99% |  |  | 100% |  |  | 91.94% |  | 7.939% | 178420.3 | 174000 |  | 174000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 0.51667 | 1.65 |  | 1.51 |  | 0 | 27.83 | 0 | 0 | 100% |  |  | 100% |  |  | 86.5% |  | 5.475% | 124193.2 | 120000 |  | 120000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 12.3167 | 3.91 |  | 3.5 |  | 0 | 35.66 | 0 | 0 | 100% |  |  | 100% |  |  | 77.75% |  | 11.41% | 258606.3 | 250000 |  | 250000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 12.9333 | 6.56 |  | 6.05 |  | 0 | 42.2 | 0 | 0 | 99.95% |  |  | 100% |  |  | 79.88% |  | 20.26% | 453488.8 | 444000 |  | 444000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 12.5833 | 5.33 |  | 4.87 |  | 0 | 38.97 | 0 | 0 | 99.98% |  |  | 100% |  |  | 79.12% |  | 16.15% | 363339.9 | 354000 |  | 354000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 12.6 | 4.58 |  | 4.13 |  | 0 | 38.5 | 0 | 0 | 99.99% |  |  | 100% |  |  | 82.76% |  | 14.33% | 321675.4 | 314000 |  | 314000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 11.3833 | 2.71 |  | 2.48 |  | 0 | 31.05 | 0 | 0 | 99.99% |  |  | 100% |  |  | 89.54% |  | 9.308% | 209033.7 | 204000 |  | 204000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 12.9 | 6.52 |  | 5.9 |  | 0 | 39.98 | 0 | 0 | 99.98% |  |  | 100% |  |  | 77.86% |  | 19.25% | 432604.2 | 422000 |  | 422000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 12.8333 | 6.92 |  | 6.37 |  | 0 | 42.69 | 0 | 0 | 100% |  |  | 100% |  |  | 77.58% |  | 20.71% | 466944.9997 | 454000 |  | 454000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 11.9833 | 2.1 |  | 1.88 |  | 0 | 20.38 | 0 | 0 | 100% |  |  | 100% |  |  | 92.64% |  | 7.3% | 165598.3 | 160000 |  | 160000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 12.0833 | 1.2 |  | 1.08 |  | 0 | 26.06 | 0 | 0 | 100% |  |  | 100% |  |  | 90.71% |  | 4.106% | 92993.4 | 90000 |  | 90000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 11.95 | 4.41 |  | 3.98 |  | 0 | 32.64 | 0 | 0 | 100% |  |  | 100% |  |  | 82.05% |  | 13.69% | 308085.8 | 300000 |  | 300000 | 91.87 | 4.5419 | 330670.8709 | 79.72% | 15.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 12.4167 | 3.7 |  | 3.35 |  | 0 | 36.9 | 0 | 0 | 100% |  |  | 100% |  |  | 86.43% |  | 12.14% | 272689.4 | 266000 |  | 266000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 12.9333 | 3.49 |  | 3.16 |  | 0 | 34.45 | 0 | 0 | 99.96% |  |  | 100% |  |  | 84.05% |  | 11.13% | 248944.7 | 244000 |  | 244000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 13 | 2.78 |  | 2.49 |  | 0 | 32.94 | 0 | 0 | 100% |  |  | 100% |  |  | 89.18% |  | 9.308% | 210051.5 | 204000 |  | 204000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 12.2833 | 4.79 |  | 4.51 |  | 0 | 37.12 | 0 | 0 | 100% |  |  | 100% |  |  | 81.58% |  | 15.42% | 346019.6 | 338000 |  | 338000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 12.6667 | 4.34 |  | 4.02 |  | 0 | 35.24 | 0 | 0 | 100% |  |  | 100% |  |  | 81.23% |  | 13.69% | 306002.7 | 300000 |  | 300000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 12.0833 | 4.52 |  | 4.25 |  | 0 | 37.01 | 0 | 0 | 100% |  |  | 100% |  |  | 78.88% |  | 14.05% | 316890.6 | 308000 |  | 308000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 12.4833 | 5.87 |  | 5.14 |  | 0 | 40.89 | 0 | 0 | 100% |  |  | 100% |  |  | 80.05% |  | 17.25% | 384478.2 | 378000 |  | 378000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 12.9 | 6.97 |  | 6.27 |  | 0 | 43.91 | 0 | 0 | 100% |  |  | 100% |  |  | 78.12% |  | 20.53% | 463613.8 | 450000 |  | 450000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 12.7667 | 6.68 |  | 5.96 |  | 0 | 43.69 | 0 | 0 | 99.98% |  |  | 100% |  |  | 78.53% |  | 19.62% | 439500.2 | 430000 |  | 430000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 12.2333 | 6.81 |  | 6.17 |  | 0 | 45.65 | 0 | 0 | 100% |  |  | 100% |  |  | 77.62% |  | 20.08% | 451487 | 440000 |  | 440000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 12.7333 | 7.41 |  | 6.62 |  | 0 | 44.68 | 0 | 0 | 100% |  |  | 100% |  |  | 79.25% |  | 21.99% | 493931.8 | 482000 |  | 482000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 12.8667 | 7.12 |  | 6.41 |  | 0 | 46.25 | 0 | 0 | 99.97% |  |  | 100% |  |  | 77.43% |  | 20.81% | 468705.6 | 456000 |  | 456000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 13.0167 | 6.56 |  | 5.85 |  | 0 | 45.83 | 0 | 0 | 99.99% |  |  | 100% |  |  | 78.15% |  | 19.16% | 430540.7999 | 420000 |  | 420000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 12.2667 | 4.84 |  | 4.42 |  | 0 | 38.19 | 0 | 0 | 100% |  |  | 100% |  |  | 81.76% |  | 15.15% | 338811.8 | 332000 |  | 332000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 12.7667 | 5.92 |  | 5.32 |  | 0 | 42.6 | 0 | 0 | 99.98% |  |  | 100% |  |  | 78.98% |  | 17.61% | 395786 | 386000 |  | 386000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 12.15 | 1.96 |  | 1.79 |  | 0 | 30.98 | 0 | 0 | 100% |  |  | 100% |  |  | 88.78% |  | 6.662% | 150699.8 | 146000 |  | 146000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 12.65 | 1.94 |  | 1.83 |  | 0 | 31.31 | 0 | 0 | 99.99% |  |  | 100% |  |  | 84.46% |  | 6.479% | 148282.2 | 142000 |  | 142000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 12 | 5.56 |  | 5 |  | 0 | 41.15 | 0 | 0 | 99.97% |  |  | 100% |  |  | 82.29% |  | 17.25% | 387842.28 | 378000 |  | 378000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 12.25 | 4.54 |  | 4.15 |  | 0 | 39.56 | 0 | 0 | 99.61% |  |  | 100% |  |  | 81.31% |  | 14.14% | 318890.5 | 310000 |  | 310000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 12.7 | 4.56 |  | 4.28 |  | 31.6 | 37.42 | 0 | 0 | 100% |  |  | 100% |  |  | 78.84% |  | 14.14% | 317374.3 | 310000 |  | 310000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 12.7 | 5.02 |  | 4.54 |  | 30.6 | 38.75 | 0 | 0 | 99.99% |  |  | 100% |  |  | 82% |  | 15.6% | 346720.2 | 342000 |  | 342000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 12.2667 | 6.29 |  | 5.51 |  | 31.4 | 41.12 | 0 | 0 | 100% |  |  | 100% |  |  | 80.6% |  | 18.62% | 420997 | 408000 |  | 408000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 11.7 | 1.52 |  | 1.39 |  | 27.27 | 29.59 | 0 | 0 | 99.82% |  |  | 100% |  |  | 83.01% |  | 4.836% | 108742.2 | 106000 |  | 106000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 12.3333 | 3.11 |  | 2.97 |  | 28.25 | 33.03 | 0 | 0 | 99.74% |  |  | 100% |  |  | 79.9% |  | 9.947% | 226808.3 | 218000 |  | 218000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 12.2667 | 5.03 |  | 4.93 |  | 28.71 | 37.2 | 0 | 0 | 99.09% |  |  | 100% |  |  | 74.63% |  | 15.42% | 343933.3 | 338000 |  | 338000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 12.8 | 6.62 |  | 6.1865 |  | 32.74 | 43.94 | 0 | 0 | 99.08% |  |  | 100% |  |  | 72.84% |  | 18.89% | 427586.6 | 414000 |  | 414000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 11.6 | 4.18 |  | 4.13 |  | 31.82 | 39.19 | 0 | 0 | 99.48% |  |  | 100% |  |  | 73.27% |  | 12.68% | 284710.2 | 278000 |  | 278000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 12.9167 | 6.04 |  | 5.69 |  | 32.33 | 41.77 | 0 | 0 | 100% |  |  | 100% |  |  | 74.99% |  | 17.89% | 402152.8 | 392000 |  | 392000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 13.3 | 5.3 |  | 5.1 |  | 31.18 | 39.68 | 0 | 0 | 100% |  |  | 100% |  |  | 79.82% |  | 17.06% | 380887.6 | 374000 |  | 374000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 13.0333 | 6.01 |  | 5.73 |  | 33.35 | 43.29 | 0 | 0 | 100% |  |  | 100% |  |  | 77.13% |  | 18.52% | 416348.1 | 406000 |  | 406000 | 91.87 | 4.3233 | 308713.2429 | 78.19% | 14.09% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | 12.9 | 5.45 |  | 5.29 |  | 30.82 | 39.25 | 0 | 0 | 100% |  |  | 100% |  |  | 78.19% |  | 17.34% | 390721.7 | 380000 |  | 380000 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | 13.1 | 4.99 |  | 4.91 |  | 30.75 | 38.79 | 0 | 0 | 99.99% |  |  | 100% |  |  | 75.37% |  | 15.51% | 349612.5 | 340000 |  | 340000 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | 12.4167 | 6.14 |  | 5.95 |  | 30.98 | 41.52 | 0 | 0 | 100% |  |  | 100% |  |  | 72.08% |  | 17.98% | 403457.4 | 394000 |  | 394000 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | 12.35 | 4.53 |  | 4.39 |  | 29.6 | 36.49 | 0 | 0 | 99.99% |  |  | 100% |  |  | 77.86% |  | 14.33% | 320777.3 | 314000 |  | 314000 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | 11.4333 | 3.71 |  | 3.58 |  | 29.27 | 35.81 | 0 | 0 | 99.97% |  |  | 100% |  |  | 79.05% |  | 11.86% | 266861.6 | 260000 |  | 260000 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | 10.5833 | 3.35 |  | 3.26 |  | 28.82 | 34.42 | 0 | 0 | 99.9% |  |  | 100% |  |  | 80.8% |  | 11.04% | 247589.6 | 242000 |  | 242000 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 91.87 | 4.3355 | 312148.2956 | 78.84% | 14.24% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.5355 | 325490.2272 | 78.59% | 14.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 4.67 | 334526.5686 | 78.44% | 15.26% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.0129 | 364432.1513 | 79.61% | 16.63% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.19 | 383173.2211 | 80.85% | 17.48% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.9258 | 369209.5692 | 82.08% | 16.85% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.4935 | 338025.7074 | 82.37% | 15.42% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.7893 | 354767.7532 | 81.12% | 16.19% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.7903 | 352764.4128 | 80.64% | 16.1% | 99.75% | 99.75% | [9 empty] | 91.32
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Grass_Ct
Sr. No. | Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Cycle Number | Resources | Blk1 | Blk2 | Blk3 | Blk4 | Blk5 | Blk6 | Blk7 | Blk8 | Blk9 | Blk10 | Blk11 | Blk12 | Total No.Table GC done | Mrthod of Cutting | Remarks for the day
1 | 2023-10-01 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
2 | 2023-10-02 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
3 | 2023-10-03 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
4 | 2023-10-04 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
5 | 2023-10-05 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
6 | 2023-10-06 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
7 | 2023-10-07 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
8 | 2023-10-08 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
9 | 2023-10-09 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
10 | 2023-10-10 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
11 | 2023-10-11 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
12 | 2023-10-12 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
13 | 2023-10-13 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
14 | 2023-10-14 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
15 | 2023-10-15 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
16 | 2023-10-16 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
17 | 2023-10-17 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
18 | 2023-10-18 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
19 | 2023-10-19 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
20 | 2023-10-20 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
21 | 2023-10-21 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
22 | 2023-10-22 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
23 | 2023-10-23 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
24 | 2023-10-24 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
25 | 2023-10-25 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
26 | 2023-10-26 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
27 | 2023-10-27 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
28 | 2023-10-28 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
29 | 2023-10-29 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
30 | 2023-10-30 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
31 | 2023-10-31 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [14 empty] | 0
32 | 2023-11-01 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
33 | 2023-11-02 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
34 | 2023-11-03 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
35 | 2023-11-04 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
36 | 2023-11-05 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
37 | 2023-11-06 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
38 | 2023-11-07 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
39 | 2023-11-08 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
40 | 2023-11-09 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
41 | 2023-11-10 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
42 | 2023-11-11 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
43 | 2023-11-12 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
44 | 2023-11-13 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
45 | 2023-11-14 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
46 | 2023-11-15 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
47 | 2023-11-16 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
48 | 2023-11-17 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
49 | 2023-11-18 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
50 | 2023-11-19 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
51 | 2023-11-20 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
52 | 2023-11-21 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
53 | 2023-11-22 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
54 | 2023-11-23 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
55 | 2023-11-24 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
56 | 2023-11-25 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
57 | 2023-11-26 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
58 | 2023-11-27 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
59 | 2023-11-28 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
60 | 2023-11-29 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
61 | 2023-11-30 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [14 empty] | 0
62 | 2023-12-01 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
63 | 2023-12-02 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
64 | 2023-12-03 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
65 | 2023-12-04 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
66 | 2023-12-05 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
67 | 2023-12-06 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
68 | 2023-12-07 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
69 | 2023-12-08 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
70 | 2023-12-09 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
71 | 2023-12-10 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
72 | 2023-12-11 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
73 | 2023-12-12 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
74 | 2023-12-13 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
75 | 2023-12-14 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
76 | 2023-12-15 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
77 | 2023-12-16 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
78 | 2023-12-17 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
79 | 2023-12-18 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
80 | 2023-12-19 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
81 | 2023-12-20 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
82 | 2023-12-21 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
83 | 2023-12-22 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
84 | 2023-12-23 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
85 | 2023-12-24 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
86 | 2023-12-25 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
87 | 2023-12-26 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
88 | 2023-12-27 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
89 | 2023-12-28 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
90 | 2023-12-29 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
91 | 2023-12-30 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
92 | 2023-12-31 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [14 empty] | 0
93 | 2024-01-01 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
94 | 2024-01-02 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
95 | 2024-01-03 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
96 | 2024-01-04 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
97 | 2024-01-05 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
98 | 2024-01-06 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
99 | 2024-01-07 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
100 | 2024-01-08 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
101 | 2024-01-09 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
102 | 2024-01-10 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
103 | 2024-01-11 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
104 | 2024-01-12 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
105 | 2024-01-13 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
106 | 2024-01-14 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
107 | 2024-01-15 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
108 | 2024-01-16 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
109 | 2024-01-17 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
110 | 2024-01-18 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
111 | 2024-01-19 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
112 | 2024-01-20 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
113 | 2024-01-21 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
114 | 2024-01-22 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
115 | 2024-01-23 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
116 | 2024-01-24 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
117 | 2024-01-25 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
118 | 2024-01-26 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
119 | 2024-01-27 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
120 | 2024-01-28 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
120 | 2024-01-29 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
122 | 2024-01-30 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
123 | 2024-01-31 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [14 empty] | 0
124 | 2024-02-01 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
125 | 2024-02-02 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
126 | 2024-02-03 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
127 | 2024-02-04 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
127 | 2024-02-05 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
127 | 2024-02-06 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
127 | 2024-02-07 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
127 | 2024-02-08 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
127 | 2024-02-09 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
127 | 2024-02-10 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
127 | 2024-02-11 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
127 | 2024-02-12 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
127 | 2024-02-13 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
127 | 2024-02-14 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
127 | 2024-02-15 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
139 | 2024-02-16 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
140 | 2024-02-17 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
141 | 2024-02-18 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
142 | 2024-02-19 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
143 | 2024-02-20 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
144 | 2024-02-21 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
145 | 2024-02-22 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
146 | 2024-02-23 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
147 | 2024-02-24 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
148 | 2024-02-25 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
149 | 2024-02-26 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
150 | 2024-02-27 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
151 | 2024-02-28 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
152 | 2024-02-29 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [14 empty] | 0
153 | 2024-03-01 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
154 | 2024-03-02 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
155 | 2024-03-03 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
156 | 2024-03-04 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
157 | 2024-03-05 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
158 | 2024-03-06 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
159 | 2024-03-07 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
160 | 2024-03-08 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
161 | 2024-03-09 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
162 | 2024-03-10 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
163 | 2024-03-11 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
164 | 2024-03-12 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
165 | 2024-03-13 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
166 | 2024-03-14 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
167 | 2024-03-15 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
168 | 2024-03-16 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
169 | 2024-03-17 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
170 | 2024-03-18 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
171 | 2024-03-19 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
172 | 2024-03-20 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
173 | 2024-03-21 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
174 | 2024-03-22 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
175 | 2024-03-23 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
176 | 2024-03-24 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
177 | 2024-03-25 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
177 | 2024-03-26 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
179 | 2024-03-27 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0
180 | 2024-03-28 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk12: 171 | 171 | Manually
181 | 2024-03-29 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk12: 122 | 122 | Manually
182 | 2024-03-30 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk11: 54; Blk12: 26 | 80 | Manually
183 | 2024-03-31 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [14 empty] | 0 |  | Sunday
184 | 2024-04-01 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
185 | 2024-04-02 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 |  |  | Blk11: 98 | 98 | Manually
186 | 2024-04-03 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
187 | 2024-04-04 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 |  |  | Blk11: 60 | 60 | Manually
188 | 2024-04-05 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
189 | 2024-04-06 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
190 | 2024-04-07 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0 |  | Sunday
191 | 2024-04-08 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 |  |  | Blk9: 2; Blk10: 26; Blk11: 50 | 78 | Manually
192 | 2024-04-09 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 |  |  | Blk10: 80 | 80 | Manually
193 | 2024-04-10 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 |  |  | Blk10: 80 | 80 | Manually
194 | 2024-04-11 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 |  |  | Blk10: 80 | 80 | Manually
195 | 2024-04-12 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0
196 | 2024-04-13 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0
197 | 2024-04-14 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0
198 | 2024-04-15 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0
199 | 2024-04-16 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0
200 | 2024-04-17 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0
201 | 2024-04-18 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0
202 | 2024-04-19 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0
203 | 2024-04-20 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0
204 | 2024-04-21 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0
205 | 2024-04-22 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 |  |  | Blk10: 40 | 40 | Manually
206 | 2024-04-23 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 |  |  | Blk9: 80; Blk10: 20 | 100 | Manually
207 | 2024-04-24 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 |  |  | Blk9: 120 | 120 | Manually
208 | 2024-04-25 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 |  |  | Blk9: 120 | 120 | Manually
209 | 2024-04-26 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 |  |  | Blk4: 68 | 68 | Manually
210 | 2024-04-27 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 |  |  | Blk4: 53 | 53 | Manually
211 | 2024-04-28 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 | [14 empty] | 0 |  | Sunday
212 | 2024-04-29 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 |  |  | Blk4: 60 | 60 | Manually
213 | 2024-04-30 | 2025 | 2024 | Year_3 | Year_3 | Apr-24 | 30 |  |  | Blk1: 26; Blk4: 30; Blk5: 24 | 80 | Manually
214 | 2024-05-01 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 | [14 empty] | 0
215 | 2024-05-02 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk6: 40; Blk7: 60 | 100 | Manually
216 | 2024-05-03 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk7: 100 | 100 | Manually
217 | 2024-05-04 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk6: 50; Blk7: 40 | 90 | Manually
218 | 2024-05-05 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 | [14 empty] | 0
219 | 2024-05-06 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 | [14 empty] | 0
220 | 2024-05-07 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk7: 70 | 70 | Manually
221 | 2024-05-08 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk6: 80 | 80
222 | 2024-05-09 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 | [14 empty] | 0
223 | 2024-05-10 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 | [14 empty] | 0
224 | 2024-05-11 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 | [14 empty] | 0
225 | 2024-05-12 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 | [14 empty] | 0
226 | 2024-05-13 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk6: 100 | 100 | Manually
227 | 2024-05-14 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk1: 40; Blk2: 40; Blk3: 40 | 120 | Manually
228 | 2024-05-15 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk2: 60 | 60 | Manually
229 | 2024-05-16 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk1: 60; Blk2: 20; Blk3: 24 | 104 | Manually
230 | 2024-05-17 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 | [14 empty] | 0
231 | 2024-05-18 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk2: 92 | 92 | Manually
232 | 2024-05-19 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 | [14 empty] | 0
233 | 2024-05-20 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk2: 30; Blk3: 80 | 110 | Manually
234 | 2024-05-21 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk3: 104 | 104
235 | 2024-05-22 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk3: 96 | 96
236 | 2024-05-23 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk2: 96 | 96
237 | 2024-05-24 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk1: 72 | 72
238 | 2024-05-25 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk1: 72 | 72
239 | 2024-05-26 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 | [14 empty] | 0
240 | 2024-05-27 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
241 | 2024-05-28 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 | [14 empty] | 0
242 | 2024-05-29 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk6: 56; Blk7: 40 | 96 | Manually
243 | 2024-05-30 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 |  |  | Blk8: 120 | 120 | Manually
244 | 2024-05-31 | 2025 | 2024 | Year_3 | Year_3 | May-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
245 | 2024-06-01 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
246 | 2024-06-02 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
247 | 2024-06-03 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
248 | 2024-06-04 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
249 | 2024-06-05 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | [14 empty] | 0
250 | 2024-06-06 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 |  |  | Blk5: 80 | 80 | Manually
251 | 2024-06-07 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 |  |  | Blk5: 20 | 20 | Manually
252 | 2024-06-08 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 |  |  | Blk1: 120 | 120
253 | 2024-06-09 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | [14 empty] | 0
254 | 2024-06-10 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 |  |  | Blk1: 96 | 96 | Manually
255 | 2024-06-11 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 |  |  | Blk1: 104 | 104 | Manually
256 | 2024-06-12 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 |  |  | Blk1: 112 | 112 | Manually
257 | 2024-06-13 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
258 | 2024-06-14 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
259 | 2024-06-15 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | [14 empty] | 0
260 | 2024-06-16 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | [14 empty] | 0
261 | 2024-06-17 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 |  |  | Blk1: 45; Blk5: 51 | 96
262 | 2024-06-18 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 |  |  | Blk5: 80 | 80
263 | 2024-06-19 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 |  |  | Blk5: 60 | 60
264 | 2024-06-20 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
265 | 2024-06-21 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
266 | 2024-06-22 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
267 | 2024-06-23 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | [14 empty] | 0 |  | Sunday
268 | 2024-06-24 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | 1 | 12 | Blk5: 80 | 80 | Manually
269 | 2024-06-25 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | 1 | 10 | Blk8: 15 | 15 | Manually | Non PV Area also.
270 | 2024-06-26 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | 1 | 8 | [12 empty] | 0 | Manually | ONGC Gas pipe line & Non PV Area also.
271 | 2024-06-27 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | 1 | 8 | Blk5: 20 | 20 | Manually | ONGC Gas pipe line & Non PV Area also.
272 | 2024-06-28 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | 1 | 12 | Blk5: 16; Blk8: 40 | 56 | Manually
273 | 2024-06-29 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | 1 | 13 | Blk5: 6; Blk7: 15; Blk8: 10 | 31 | Manually | Non PV Area also.
274 | 2024-06-30 | 2025 | 2024 | Year_3 | Year_3 | Jun-24 | 30 | 1 | 7 | [12 empty] | 0 | Manually | Block 11 ONGC Gas pipe line & Non PV Area also.
275 | 2024-07-01 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
276 | 2024-07-02 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | 1 | 9 | [12 empty] | 0 | Manually | Block 1,2 &3 LA surrounding area.
277 | 2024-07-03 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
278 | 2024-07-04 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
279 | 2024-07-05 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
280 | 2024-07-06 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
281 | 2024-07-07 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
282 | 2024-07-08 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
283 | 2024-07-09 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
284 | 2024-07-10 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
285 | 2024-07-11 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
286 | 2024-07-12 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
287 | 2024-07-13 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
288 | 2024-07-14 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
289 | 2024-07-15 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
290 | 2024-07-16 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
291 | 2024-07-17 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
292 | 2024-07-18 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
293 | 2024-07-19 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
294 | 2024-07-20 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
295 | 2024-07-21 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
296 | 2024-07-22 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
297 | 2024-07-23 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
298 | 2024-07-24 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
299 | 2024-07-25 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
300 | 2024-07-26 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
301 | 2024-07-27 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
302 | 2024-07-28 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
303 | 2024-07-29 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
304 | 2024-07-30 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
305 | 2024-07-31 | 2025 | 2024 | Year_3 | Year_3 | Jul-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
306 | 2024-08-01 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
307 | 2024-08-02 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
308 | 2024-08-03 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
309 | 2024-08-04 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
310 | 2024-08-05 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
311 | 2024-08-06 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
312 | 2024-08-07 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | [14 empty] | 0 |  | Grass cutting not done due to rainfall at site
313 | 2024-08-08 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 23 | Blk10: 70; Blk12: 28 | 98 | Manually
314 | 2024-08-09 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 18 | Blk10: 40; Blk12: 32 | 72 | Manually
315 | 2024-08-10 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 18 | Blk10: 67; Blk12: 56 | 123 | Manually
316 | 2024-08-11 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | [14 empty] | 0 |  | Sunday
317 | 2024-08-12 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 15 | Blk10: 64; Blk12: 16 | 80 | Manually
318 | 2024-08-13 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 18 | Blk10: 60; Blk12: 16 | 76 | Manually
319 | 2024-08-14 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 15 | Blk7: 38; Blk10: 2; Blk11: 19; Blk12: 6 | 65 | Manually
320 | 2024-08-15 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | [14 empty] | 0 |  | Holiday
321 | 2024-08-16 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 14 | Blk7: 54; Blk11: 16 | 70 | Manually
322 | 2024-08-17 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 13 | Blk7: 62; Blk11: 36 | 98 | Manually
323 | 2024-08-18 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | [14 empty] | 0 |  | Sunday
324 | 2024-08-19 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 15 | Blk7: 50 | 50 | Manually
325 | 2024-08-20 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 18 | Blk7: 100; Blk11: 34 | 134 | Manually
326 | 2024-08-21 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 16 | Blk6: 60; Blk11: 40 | 100 | Manually
327 | 2024-08-22 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 15 | Blk6: 27; Blk7: 24; Blk11: 22 | 73 | Manually
328 | 2024-08-23 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 10 | Blk9: 56 | 56 | Manually
329 | 2024-08-24 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 13 | Blk9: 51; Blk11: 27 | 78 | Manually
330 | 2024-08-25 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | [14 empty] | 0 |  | Sunday
331 | 2024-08-26 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | [14 empty] | 0 |  | Holiday
332 | 2024-08-27 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 5 | Blk9: 23; Blk11: 18 | 41 | Manually
333 | 2024-08-28 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 14 | Blk8: 30; Blk9: 40 | 70 | Manually
334 | 2024-08-29 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 12 | Blk4: 57; Blk8: 20; Blk9: 2 | 79 | Manually
335 | 2024-08-30 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 9 | Blk4: 40; Blk8: 20 | 60 | Manually
336 | 2024-08-31 | 2025 | 2024 | Year_3 | Year_3 | Aug-24 | 31 | 2 | 2 | Blk8: 25 | 25 | Manually
337 | 2024-09-01 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | [14 empty] | 0 |  | Sunday
338 | 2024-09-02 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 6 | Blk4: 42 | 42 | Manually
339 | 2024-09-03 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 6 | Blk4: 34 | 34 | Manually
340 | 2024-09-04 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 10 | Blk1: 16; Blk4: 34; Blk8: 26 | 76 | Manually
341 | 2024-09-05 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 8 | Blk4: 10 | 10 | Manually | Switchyard and ICR's surrounding area.
342 | 2024-09-06 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 8 | [12 empty] | 0 | Manually | Switchyard and Non-PV area.
343 | 2024-09-07 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 6 | [12 empty] | 0 | Manually | Switchyard and Non-PV area.
344 | 2024-09-08 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | [14 empty] | 0 |  | Sunday
345 | 2024-09-09 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 9 | Blk2: 48; Blk8: 20 | 68 | Manually
346 | 2024-09-10 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 9 | Blk2: 46; Blk8: 20 | 66 | Manually
347 | 2024-09-11 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 6 | Blk2: 40 | 40 | Manually
348 | 2024-09-12 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 8 | Blk1: 5; Blk2: 35 | 40 | Manually
349 | 2024-09-13 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 13 | Blk2: 37; Blk8: 30 | 67 | Manually
350 | 2024-09-14 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 10 | Blk2: 26; Blk3: 28; Blk8: 35 | 89 | Manually
351 | 2024-09-15 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | [14 empty] | 0 |  | Sunday
352 | 2024-09-16 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 12 | Blk2: 30; Blk3: 27; Blk8: 40 | 97 | Manually
353 | 2024-09-17 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | [14 empty] | 0 |  | Grass Cutting not done due to Viswakarma Puja.
354 | 2024-09-18 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | [14 empty] | 0 |  | Grass Cutting not done due to Viswakarma Puja.
355 | 2024-09-19 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 14 | Blk6: 45 | 45 |  | Switchyard Area.
356 | 2024-09-20 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 10 | Blk5: 40 | 40 | Manually | Switchyard Area.
357 | 2024-09-21 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 12 | Blk5: 48 | 48 | Manually | Switchyard Area.
358 | 2024-09-22 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | [14 empty] | 0 |  | Sunday
359 | 2024-09-23 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 6 | Blk3: 40 | 40 | Manually
360 | 2024-09-24 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 17 | Blk3: 42; Blk6: 40 | 82 | Manually
361 | 2024-09-25 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 6 | Blk3: 105 | 105 | Manually
362 | 2024-09-26 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | [14 empty] | 0 |  | Grass Cutting not done due to rain.
363 | 2024-09-27 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | [14 empty] | 0 |  | Grass Cutting not done due to rain.
364 | 2024-09-28 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 8 | Blk1: 65 | 65 | Manually
365 | 2024-09-29 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 8 | Blk1: 94 | 94 | Manually
366 | 2024-09-30 | 2025 | 2024 | Year_3 | Year_3 | Sep-24 | 30 | 2 | 8 | Blk1: 80 | 80 | Manually
367 | 2024-10-01 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0
368 | 2024-10-02 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | 2 | 8 | Blk1: 48 | 48 | Manually
369 | 2024-10-03 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | 2 | 7 | Blk1: 48 | 48 | Manually
370 | 2024-10-04 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | 2 | 7 | Blk1: 46 | 46 | Manually
371 | 2024-10-05 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | 2 | 7 | Blk1: 50 | 50 | Manually
372 | 2024-10-06 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Sunday
373 | 2024-10-07 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | 2 | 8 | Blk1: 100 | 100 | Manually
374 | 2024-10-08 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | 2 | 6 | Blk1: 48 | 48 | Manually
375 | 2024-10-09 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
376 | 2024-10-10 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
377 | 2024-10-11 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
378 | 2024-10-12 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
379 | 2024-10-13 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Sunday
380 | 2024-10-14 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 | Manually
381 | 2024-10-15 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | 2 | 5 | Blk5: 49 | 49 | Manually
382 | 2024-10-16 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | 2 | 9 | Blk5: 75 | 75 | Manually | Work is not done
383 | 2024-10-17 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
384 | 2024-10-18 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
385 | 2024-10-19 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
386 | 2024-10-20 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
387 | 2024-10-21 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
388 | 2024-10-22 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
389 | 2024-10-23 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
390 | 2024-10-24 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
391 | 2024-10-25 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
392 | 2024-10-26 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
393 | 2024-10-27 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
394 | 2024-10-28 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
395 | 2024-10-29 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
396 | 2024-10-30 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
397 | 2024-10-31 | 2025 | 2024 | Year_3 | Year_3 | Oct-24 | 31 | [14 empty] | 0 |  | Work is not done
398 | 2024-11-01 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0 |  | Work is not done
399 | 2024-11-02 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0 |  | Work is not done
400 | 2024-11-03 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0 |  | Work is not done
401 | 2024-11-04 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0 |  | Work is not done
402 | 2024-11-05 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0 |  | Work is not done
403 | 2024-11-06 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0 |  | Work is not done
404 | 2024-11-07 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0 |  | Work is not done
405 | 2024-11-08 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0 |  | Work is not done
406 | 2024-11-09 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0 |  | Work is not done
407 | 2024-11-10 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0 |  | Work is not done
408 | 2024-11-11 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0 |  | Work is not done
409 | 2024-11-12 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0 |  | Work is not done
410 | 2024-11-13 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
411 | 2024-11-14 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
412 | 2024-11-15 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
413 | 2024-11-16 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
414 | 2024-11-17 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
415 | 2024-11-18 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
416 | 2024-11-19 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
417 | 2024-11-20 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
418 | 2024-11-21 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
419 | 2024-11-22 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
420 | 2024-11-23 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
421 | 2024-11-24 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
422 | 2024-11-25 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
423 | 2024-11-26 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
424 | 2024-11-27 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
425 | 2024-11-28 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
426 | 2024-11-29 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
427 | 2024-11-30 | 2025 | 2024 | Year_3 | Year_3 | Nov-24 | 30 | [14 empty] | 0
428 | 2024-12-01 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
429 | 2024-12-02 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
430 | 2024-12-03 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
431 | 2024-12-04 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
432 | 2024-12-05 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
433 | 2024-12-06 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
434 | 2024-12-07 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
435 | 2024-12-08 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
436 | 2024-12-09 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
437 | 2024-12-10 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
438 | 2024-12-11 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
439 | 2024-12-12 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
440 | 2024-12-13 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
441 | 2024-12-14 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
442 | 2024-12-15 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
443 | 2024-12-16 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
444 | 2024-12-17 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
445 | 2024-12-18 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
446 | 2024-12-19 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
447 | 2024-12-20 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
448 | 2024-12-21 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
449 | 2024-12-22 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
450 | 2024-12-23 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
451 | 2024-12-24 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
452 | 2024-12-25 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0
453 | 2024-12-26 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | 3 | 5 | Blk7: 40 | 40 | Manually
454 | 2024-12-27 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | 3 | 5 | Blk7: 32 | 32 | Manually
455 | 2024-12-28 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | 3 | 5 | Blk7: 37 | 37 | Manually
456 | 2024-12-29 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | [14 empty] | 0 |  | Sunday
457 | 2024-12-30 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | 3 | 5 | Blk7: 35 | 35 | Manually
458 | 2024-12-31 | 2025 | 2024 | Year_3 | Year_3 | Dec-24 | 31 | 3 | 3 | Blk7: 24 | 24 | Manually
459 | 2025-01-01 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | [14 empty] | 0 |  | Holiday
460 | 2025-01-02 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 2 | [12 empty] | 0 | Manually | Block- 6 & 7 , ICR Surrounding area cleaned.
461 | 2025-01-03 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 8 | Blk7: 30; Blk10: 20 | 50 | Manually
462 | 2025-01-04 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 6 | Blk11: 20; Blk12: 20 | 40 | Manually | Switchyard Area cleaned.
463 | 2025-01-05 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 4 | Blk12: 20 | 20 | Manually | Block- 11 & 12 , ICR Surrounding area cleaned.
464 | 2025-01-06 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 6 | Blk4: 24 | 24 | Manually | Block- 04 ICR Surrounding area cleaned.
465 | 2025-01-07 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 8 | Blk7: 56 | 56 | Manually
466 | 2025-01-08 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 7 | Blk7: 40 | 40 | Manually
467 | 2025-01-09 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 9 | Blk10: 60 | 60 | Manually
468 | 2025-01-10 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 8 | Blk9: 25; Blk10: 25 | 50 | Manually
469 | 2025-01-11 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 7 | Blk7: 35 | 35 | Manually
470 | 2025-01-12 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | [14 empty] | 0 |  | Sunday
471 | 2025-01-13 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | [14 empty] | 0 |  | Work is not done due to BIHU Festival
472 | 2025-01-14 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | [14 empty] | 0 |  | Work is not done due to BIHU Festival
473 | 2025-01-15 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | [14 empty] | 0 |  | Work is not done due to BIHU Festival
474 | 2025-01-16 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | [14 empty] | 0 |  | Work is not done due to BIHU Festival
475 | 2025-01-17 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | [14 empty] | 0 |  | Work is not done due to BIHU Festival
476 | 2025-01-18 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | [14 empty] | 0 |  | Work is not done due to BIHU Festival
477 | 2025-01-19 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | [14 empty] | 0 |  | Sunday
478 | 2025-01-20 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 6 | Blk11: 40 | 40 | Manually
479 | 2025-01-21 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 9 | Blk11: 25 | 25 | Manually | Boundary Area grass cutting.
480 | 2025-01-22 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 5 | Blk12: 25 | 25 | Manually | Boundary Area grass cutting.
481 | 2025-01-23 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 4 | Blk12: 30 | 30 | Manually
482 | 2025-01-24 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 4 | Blk12: 30 | 30 | Manually
483 | 2025-01-25 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 4 | Blk12: 30 | 30 | Manually
484 | 2025-01-26 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | [14 empty] | 0 |  | Sunday
485 | 2025-01-27 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | [14 empty] | 0 |  | Work is not done today.
486 | 2025-01-28 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 5 | Blk12: 40 | 40 | Manually
487 | 2025-01-29 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 5 | Blk12: 40 | 40 | Manually
488 | 2025-01-30 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 5 | Blk12: 40 | 40 | Manually
489 | 2025-01-31 | 2025 | 2025 | Year_3 | Year_3 | Jan-25 | 31 | 3 | 4 | Blk12: 40 | 40 | Manually
490 | 2025-02-01 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 4 | Blk12: 40 | 40 | Manually
491 | 2025-02-02 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 4 | Blk11: 40 | 40 | Manually
492 | 2025-02-03 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 4 | Blk11: 32 | 32 | Manually
493 | 2025-02-04 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 8 | Blk11: 38 | 38 | Manually | LA Area grass cutting done
494 | 2025-02-05 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 7 | Blk11: 24 | 24 | Manually | LA Area grass cutting done
495 | 2025-02-06 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 7 | Blk11: 24 | 24 | Manually | Switchyard area grass cutting done.
496 | 2025-02-07 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 5 | Blk11: 32 | 32 | Manually
497 | 2025-02-08 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 3 | Blk10: 22 | 22 | Manually
498 | 2025-02-09 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | [14 empty] | 0 |  | Sunday
499 | 2025-02-10 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 10 | Blk9: 52; Blk10: 20 | 72 | Manually
500 | 2025-02-11 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 8 | Blk10: 52 | 52 | Manually
501 | 2025-02-12 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 9 | Blk10: 48 | 48 | Manually | Switchyard area grass cutting done.
502 | 2025-02-13 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 9 | Blk10: 48 | 48 | Manually
503 | 2025-02-14 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 9 | Blk10: 48 | 48 | Manually
504 | 2025-02-15 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 9 | Blk9: 69 | 69 | Manually
505 | 2025-02-16 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | [14 empty] | 0 |  | Sunday
506 | 2025-02-17 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 6 | Blk9: 50 | 50 | Manually
507 | 2025-02-18 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 8 | Blk8: 60; Blk9: 40 | 100 | Manually
508 | 2025-02-19 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 9 | Blk6: 55; Blk9: 15 | 70 | Manually
509 | 2025-02-20 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 14 | Blk5: 76; Blk6: 100 | 176 | Manually
510 | 2025-02-21 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 26 | Blk5: 157; Blk6: 167; Blk8: 96 | 420 | Manually
511 | 2025-02-22 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 37 | Blk1: 30; Blk2: 20; Blk4: 258; Blk5: 97; Blk8: 54 | 459 | Manually
512 | 2025-02-23 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | [14 empty] | 0 |  | Sunday
513 | 2025-02-24 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 36 | Blk1: 250; Blk2: 68; Blk3: 13; Blk8: 120 | 451 | Manually
514 | 2025-02-25 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 30 | Blk1: 290; Blk2: 150; Blk3: 20 | 460 | Manually
515 | 2025-02-26 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | [14 empty] | 0 |  | Holiday
516 | 2025-02-27 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 22 | Blk2: 82; Blk3: 230 | 312 | Manually
517 | 2025-02-28 | 2025 | 2025 | Year_3 | Year_3 | Feb-25 | 28 | 3 | 22 | [12 empty] | 0 | Manually | Non PV Area, ONGC Pipe Line and Boundary Fencing area Grass Cutting done.
518 | 2025-03-01 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
519 | 2025-03-02 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
520 | 2025-03-03 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0 |  | 3rd Cycle grass cutting compleated.
521 | 2025-03-04 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
522 | 2025-03-05 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
523 | 2025-03-06 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
524 | 2025-03-07 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
525 | 2025-03-08 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
526 | 2025-03-09 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
527 | 2025-03-10 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
528 | 2025-03-11 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
529 | 2025-03-12 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
530 | 2025-03-13 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
531 | 2025-03-14 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
532 | 2025-03-15 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
533 | 2025-03-16 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
534 | 2025-03-17 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
535 | 2025-03-18 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
536 | 2025-03-19 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
537 | 2025-03-20 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
538 | 2025-03-21 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
539 | 2025-03-22 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
540 | 2025-03-23 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
541 | 2025-03-24 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
542 | 2025-03-25 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
543 | 2025-03-26 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
544 | 2025-03-27 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
545 | 2025-03-28 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
546 | 2025-03-29 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
547 | 2025-03-30 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
548 | 2025-03-31 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0
549 | 2025-04-01 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
550 | 2025-04-02 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
551 | 2025-04-03 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
552 | 2025-04-04 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
553 | 2025-04-05 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
554 | 2025-04-06 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
555 | 2025-04-07 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
556 | 2025-04-08 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
557 | 2025-04-09 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
558 | 2025-04-10 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
559 | 2025-04-11 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
560 | 2025-04-12 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
561 | 2025-04-13 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
562 | 2025-04-14 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
563 | 2025-04-15 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
564 | 2025-04-16 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
565 | 2025-04-17 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
566 | 2025-04-18 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
567 | 2025-04-19 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
568 | 2025-04-20 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
569 | 2025-04-21 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
570 | 2025-04-22 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
571 | 2025-04-23 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
572 | 2025-04-24 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
573 | 2025-04-25 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0
574 | 2025-04-26 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | Manually | Grass Cutting at Switchyard area. (WIP)
575 | 2025-04-27 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 |  | Work is not done today.
576 | 2025-04-28 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 1 | 12 | [12 empty] | 0 | Manually | Grass Cutting at Boundary fancing area. (WIP)
577 | 2025-04-29 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 1 | 19 | [12 empty] | 0 | Manually | Grass Cutting at Boundary fancing area. 500 meters (WIP) & Grass Cutting at Switchyard area(WIP)
578 | 2025-04-30 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 1 | 21 | [12 empty] | 0 | Manually | Grass Cutting at Boundary fancing area. 600 meters (WIP) & Grass Cutting at Switchyard area(WIP)
579 | 2025-05-01 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 |  | Holiday
580 | 2025-05-02 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 |  | Work is not done today Due to local Election.
581 | 2025-05-03 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 19 | [12 empty] | 0 | Manually | Grass Cutting at Boundary fancing area. 400 meters (WIP) & Grass Cutting at Switchyard area(WIP)
582 | 2025-05-04 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 |  | Sunday
583 | 2025-05-05 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 |  | Work is not done today.
583 | 2025-05-06 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 16 | [12 empty] | 0 | Manually | Grass Cutting at Boundary fancing area. 400 meters (WIP) & Grass Cutting at Switchyard area(WIP)
584 | 2025-05-07 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 27 | [12 empty] | 0 | Manually | Grass Cutting at Boundary fancing area (WIP) & Grass Cutting at Switchyard area(WIP)
585 | 2025-05-08 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 25 | [12 empty] | 0 | Manually | Grass Cutting at Boundary fancing area (WIP) & Grass Cutting at Switchyard area(WIP)
586 | 2025-05-09 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 31 | [12 empty] | 0 | Manually | Grass Cutting at Boundary fancing area (WIP) & Grass Cutting at Switchyard area(WIP)
587 | 2025-05-10 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 30 | [12 empty] | 0 | Manually | Grass Cutting at Boundary fancing area (WIP) & Grass Cutting at Switchyard area(WIP)
588 | 2025-05-11 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 |  | Sunday
589 | 2025-05-12 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 2 | [12 empty] | 0 | Manually | Grass Cutting at Boundary fancing area (WIP)
590 | 2025-05-13 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 10 | Blk12: 60 | 60 | Manually | Grass Cutting at Block-12 Total 60 nos Table done. (WIP)
591 | 2025-05-14 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 18 | Blk7: 33; Blk12: 73 | 106 | Manually | Grass Cutting at Block-07 & Block-12 Total 106 nos Table done. (WIP)
592 | 2025-05-15 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 25 | Blk7: 0 | 0 | Manually | Due to heavy rain from morning Manpower has return back to home.
593 | 2025-05-16 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 23 | Blk6: 16; Blk7: 124 | 140 | Manually | Grass Cutting at Block-07 & Block-06 Total 142 nos Table done. (WIP)
594 | 2025-05-17 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | Manually | Work is not done today.( Due to rain at site morning)
595 | 2025-05-18 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 |  | Sunday
596 | 2025-05-19 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 |  | Work is not done today.
597 | 2025-05-20 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 22 | Blk6: 72; Blk7: 95 | 167 | Manually | Grass Cutting at Block-07 & Block-06 Total 167 nos Table done. (WIP)
598 | 2025-05-21 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 16 | Blk5: 10; Blk6: 70; Blk7: 14 | 94 | Manually | Grass Cutting at Block-05,06 & Block-06 Total 94 nos Table done. (WIP)
599 | 2025-05-22 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 25 | Blk9: 64; Blk10: 122 | 186 | Manually | Grass Cutting at Block-09 & Block-10 Total 186 nos Table done. (WIP)
599 | 2025-05-23 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 30 | Blk11: 41; Blk12: 169 | 210 | Manually | Grass Cutting at Block-11 & Block-12 Total 210 nos Table done. (WIP)
600 | 2025-05-24 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 32 | Blk10: 16; Blk11: 217; Blk12: 17 | 250 | Manually | Grass Cutting at Block-10, Block-11 & Block-12 Total 250 nos Table done. (WIP)
601 | 2025-05-25 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 |  | Sunday
602 | 2025-05-26 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 |  | Work not done due to heavy rain from morning.
603 | 2025-05-27 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 12 | Blk10: 70 | 70 | Manually | Grass Cutting at Block-10 Total 70 nos Table done. (WIP)
603 | 2025-05-28 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 28 | Blk9: 78; Blk10: 102 | 180 | Manually | Grass Cutting at Block-09 & 10 Total 180 nos Table done. (WIP)
604 | 2025-05-29 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 33 | Blk8: 200; Blk9: 100; Blk10: 10 | 310 | Manually | Grass Cutting at Block-08 & 10 Total 310 nos Table done. (WIP)
604 | 2025-05-30 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 |  | Work not done due to heavy rain from morning.
605 | 2025-05-31 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | 1 | 33 | Blk1: 10; Blk4: 210 | 220 | Manually | Grass Cutting at Block-01 & 04 Total 220 nos Table done. (WIP)
606 | 2025-06-01 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 |  | Sunday
607 | 2025-06-02 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 28 | Blk1: 250 | 250 |  | Grass Cutting at Block-01 Total 250 nos Table done. (WIP)
608 | 2025-06-03 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 37 | Blk1: 80; Blk2: 150; Blk3: 71 | 301 |  | Grass Cutting at Block-02 & 03 Total 255 nos Table done. (WIP)
609 | 2025-06-04 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 36 | Blk2: 63; Blk3: 192 | 255 |  | Grass Cutting at Block-01 ,02 & 03 Total 301 nos Table done. (WIP)
610 | 2025-06-05 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 38 | Blk1: 215; Blk2: 107; Blk4: 31 | 353 |  | Grass Cutting at Block-01 ,02 & 04 Total 353 nos Table done. (WIP)
611 | 2025-06-06 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 11 | Blk1: 28; Blk4: 22 | 50 |  | Grass Cutting at Block-01 & 04 Total 50 nos Table done. (WIP)
612 | 2025-06-07 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 38 | Blk1: 67; Blk5: 163 | 230 |  | Grass Cutting at Block-01 & 04 Total 50 nos Table done. (WIP)
613 | 2025-06-08 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 |  | Sunday
614 | 2025-06-09 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 2 | Blk5: 14 | 14 |  | Grass Cutting at Block-05 Total 14 nos Table done. (WIP)
615 | 2025-06-10 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 10 | Blk5: 38; Blk6: 23 | 61 |  | Grass Cutting at Block-05 & Block-06 Total 61 nos Table done. (WIP)
616 | 2025-06-11 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 14 | Blk5: 54; Blk6: 48 | 102 |  | Grass Cutting at Block-05 & Block-06 Total 102 nos Table done. (WIP)
617 | 2025-06-12 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 |  | Grass Cutting not done today.
618 | 2025-06-13 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 13 | Blk5: 53; Blk8: 43 | 96 |  | Grass Cutting at Block-05 & Block-08 Total 96 nos Table done. (WIP)
619 | 2025-06-14 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 |  | Blk6: 68; Blk8: 20 | 88 |  | Grass Cutting at Block-06 & Block-08 Total 88 nos Table done. (WIP)
620 | 2025-06-15 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | [13 empty] | 0 |  | Sunday
621 | 2025-06-16 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 |  | Grass Cutting not done today.
622 | 2025-06-17 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 17 | Blk6: 25; Blk7: 63; Blk8: 53 | 141 |  | Grass Cutting at Block-06,Block-07 & Block-08 Total 141 nos Table done.
623 | 2025-06-18 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 26 | [12 empty] | 0 |  | Grass Cutting at Boundary fancing area (WIP).
624 | 2025-06-19 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 27 | [12 empty] | 0 |  | Grass cutting done at Non-PV area at B-4
625 | 2025-06-20 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 21 | [12 empty] | 0 |  | Grass cutting done at Non-PV area at B-3
626 | 2025-06-21 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 23 | [12 empty] | 0 |  | Grass cutting done at Non-PV area at B-1
627 | 2025-06-22 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 |  | Sunday
628 | 2025-06-23 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 |  | 1st cycle Grass Cutting done.
629 | 2025-06-24 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 |  | 1st cycle Grass Cutting done.
630 | 2025-06-25 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 |  | 1st cycle Grass Cutting done.
631 | 2025-06-26 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 |  | 1st cycle Grass Cutting done.
632 | 2025-06-27 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 |  | 1st cycle Grass Cutting done.
633 | 2025-06-28 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 |  | 1st cycle Grass Cutting done.
634 | 2025-06-29 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 2 | [12 empty] | 0 |  | Grass cutting work done at MCR Surrounding.
635 | 2025-06-30 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 |  | 1st cycle Grass Cutting done.
636 | 2025-07-01 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0 |  | 1st cycle Grass Cutting done.
637 | 2025-07-02 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0 |  | 1st cycle Grass Cutting done.
638 | 2025-07-03 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0 |  | 1st cycle Grass Cutting done.
639 | 2025-07-04 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0 |  | 1st cycle Grass Cutting done.
640 | 2025-07-05 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0 |  | 1st cycle Grass Cutting done.
641 | 2025-07-06 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0 |  | 1st cycle Grass Cutting done.
Formulas:
Days = DAY(EOMONTH(GC_17[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## Mod_CL
Sr. No. | Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Cycle Number | Resources | Blk1 | Blk2 | Blk3 | Blk4 | Blk5 | Blk6 | Blk7 | Blk8 | Blk9 | Blk10 | Blk11 | Blk12 | Total NO. Module cleaned | Morning Start Time | Morning End Time | Evening Start Time | Evening End time | Brush/MOP Replcemnet | Water Test Report | Remarks for the day | Column1
1 | 2025-03-29 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | 6 | 20 | Blk4: 5784; Blk6: 7280 | 13064 | 0.22917 | 0.36111 | 0.65625 | 0.84375 | MOP
2 | 2025-03-30 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0 | [6 empty] | Module cleaning not done today.
3 | 2025-03-31 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | [14 empty] | 0 | [6 empty] | Module cleaning not done today.
4 | 2025-04-01 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 1 | 12 | Blk4: 3640; Blk5: 3640 | 7280 |  |  | 0.65625 | 0.84375 | MOP
5 | 2025-04-02 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module cleaning not done today due to rain.
6 | 2025-04-03 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done today.
7 | 2025-04-04 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 1 | 11 | Blk8: 3136; Blk11: 3416 | 6552 |  |  | 0.65625 | 0.84375 | MOP
8 | 2025-04-05 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 1 | 19 | Blk3: 4368; Blk8: 3640 | 8008 | 0.22917 | 0.36111 | 0.65625 | 0.84375 | MOP
9 | 2025-04-06 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done today.
10 | 2025-04-07 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 1 | 14 | Blk3: 4368; Blk5: 4368 | 8736 |  |  | 0.65625 | 0.84375 | MOP
11 | 2025-04-08 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 1 | 13 | Blk3: 3900; Blk10: 3610 | 7510 |  |  | 0.65625 | 0.84375 | MOP
12 | 2025-04-09 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 1 | 11 | Blk2: 672; Blk3: 3696; Blk10: 2240 | 6608 |  |  | 0.65625 | 0.84375 | MOP
13 | 2025-04-10 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 1 | 8 | Blk2: 2800 | 2800 |  |  | 0.65625 | 0.75 | MOP
14 | 2025-04-11 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Rain cleaning done on yestarday Night(Rain-21.79 mm)
15 | 2025-04-12 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done today(1 mm)
16 | 2025-04-13 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
17 | 2025-04-14 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
18 | 2025-04-15 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
19 | 2025-04-16 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
20 | 2025-04-17 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
21 | 2025-04-18 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
22 | 2025-04-19 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
23 | 2025-04-20 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Rain cleaning done by Rain(Rain-4.39mm)
24 | 2025-04-21 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
25 | 2025-04-22 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Rain cleaning done by Rain(Rain-6.6mm)
26 | 2025-04-23 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Rain cleaning done by Rain(Rain-16.99mm)
27 | 2025-04-24 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.(Rain-1.0mm)
28 | 2025-04-25 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
29 | 2025-04-26 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
30 | 2025-04-27 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.(Rain-10.60mm)
31 | 2025-04-28 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.(Rain-3.60mm)
32 | 2025-04-29 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
33 | 2025-04-30 | 2026 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
34 | 2025-05-01 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Holiday
35 | 2025-05-02 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done Due to local Election.
36 | 2025-05-03 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
37 | 2025-05-04 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Sunday
38 | 2025-05-05 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.(Rain-0.60mm)
39 | 2025-05-06 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.(Rain-3.0mm)
40 | 2025-05-07 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
41 | 2025-05-08 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.(Rain-12.39mm)
42 | 2025-05-09 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.(Rain-2.40mm)
43 | 2025-05-10 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
44 | 2025-05-11 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Sunday (Rain-1.0mm)
45 | 2025-05-12 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
46 | 2025-05-13 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.(16.8mm)
47 | 2025-05-14 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.(0.4 mm)
48 | 2025-05-15 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.(20 mm)
49 | 2025-05-16 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
50 | 2025-05-17 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.(7mm)
51 | 2025-05-18 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.(11mm)
52 | 2025-05-19 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.(2.80mm)
53 | 2025-05-20 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.(2.20mm)
54 | 2025-05-21 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.(4.80mm)
55 | 2025-05-22 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
56 | 2025-05-23 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
57 | 2025-05-24 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
58 | 2025-05-25 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 4.40 mm)
59 | 2025-05-26 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 7.80 mm)
60 | 2025-05-27 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
61 | 2025-05-28 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
62 | 2025-05-29 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 10.20 mm)
63 | 2025-05-30 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 12.20 mm)
64 | 2025-05-31 | 2026 | 2025 | Year_3 | Year_3 | May-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 21.6 mm)
65 | 2025-06-01 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 0.4 mm)
66 | 2025-06-02 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 1.6 mm)
67 | 2025-06-03 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
68 | 2025-06-04 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
69 | 2025-06-05 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 11.2 mm)
70 | 2025-06-06 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
71 | 2025-06-07 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
72 | 2025-06-08 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
73 | 2025-06-09 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
74 | 2025-06-10 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
75 | 2025-06-11 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
76 | 2025-06-12 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
77 | 2025-06-13 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
78 | 2025-06-14 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
79 | 2025-06-15 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
80 | 2025-06-16 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 1 | 8 | Blk7: 2296 | 2296 | 0.22917 | 0.44444 |  |  | MOP |  | Module Cleaning not done.( Rain 8.8 mm)
81 | 2025-06-17 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 29.40 mm)
82 | 2025-06-18 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 8.0 mm)
83 | 2025-06-19 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 25.4 mm)
84 | 2025-06-20 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 8.6 mm)
85 | 2025-06-21 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 2.2 mm)
86 | 2025-06-22 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 6.20 mm)
87 | 2025-06-23 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 35.40 mm)
88 | 2025-06-24 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 51.0 mm)
89 | 2025-06-25 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 4.80 mm)
90 | 2025-06-26 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
91 | 2025-06-27 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 2.2 mm)
92 | 2025-06-28 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
93 | 2025-06-29 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
94 | 2025-06-30 | 2026 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
95 | 2025-07-01 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 14.00 mm)
96 | 2025-07-02 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.
97 | 2025-07-03 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 11.00 mm)
98 | 2025-07-04 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 20.60 mm)
99 | 2025-07-05 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 10.40 mm)
100 | 2025-07-06 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0 | [6 empty] | Module Cleaning not done.( Rain 7 mm)
101 | 2025-07-07 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
102 | 2025-07-08 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
103 | 2025-07-09 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
104 | 2025-07-10 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
105 | 2025-07-11 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
106 | 2025-07-12 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
107 | 2025-07-13 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
108 | 2025-07-14 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
109 | 2025-07-15 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
110 | 2025-07-16 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
111 | 2025-07-17 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
112 | 2025-07-18 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
113 | 2025-07-19 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
114 | 2025-07-20 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
115 | 2025-07-21 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
116 | 2025-07-22 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
117 | 2025-07-23 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
118 | 2025-07-24 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
119 | 2025-07-25 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
120 | 2025-07-26 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
121 | 2025-07-27 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
122 | 2025-07-28 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
123 | 2025-07-29 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
124 | 2025-07-30 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
125 | 2025-07-31 | 2026 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | [14 empty] | 0
126 | 2025-08-01 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
127 | 2025-08-02 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
128 | 2025-08-03 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
129 | 2025-08-04 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
130 | 2025-08-05 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
131 | 2025-08-06 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
132 | 2025-08-07 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
133 | 2025-08-08 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
134 | 2025-08-09 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
135 | 2025-08-10 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
136 | 2025-08-11 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
137 | 2025-08-12 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
138 | 2025-08-13 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
139 | 2025-08-14 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
140 | 2025-08-15 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
141 | 2025-08-16 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
142 | 2025-08-17 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
143 | 2025-08-18 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
144 | 2025-08-19 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
145 | 2025-08-20 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
146 | 2025-08-21 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
147 | 2025-08-22 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
148 | 2025-08-23 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
149 | 2025-08-24 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
150 | 2025-08-25 | 2026 | 2025 | Year_3 | Year_3 | Aug-25 | 31 | [14 empty] | 0
Formulas:
Days = DAY(EOMONTH(MC_16[[#This Row],[Month Year]],0))

## Modelling New (hidden)
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | CC*Bugt (MTD) | CC*Bugt (YTD) | Capacity | 91.32
1 | April | 4 | 2024-04-01 | 2024 | FY25 | 30 | 135 | 136.5 |  | 24.6 |  | 9969.5 | 91.32 | 79.98% | 4.55 | 0 | 0 | 0 | 332.3167 | 0 | 0 | 15.16% | [7 empty] | 99.75% | 99.75%
2 | May | 5 | 2024-05-01 | 2024 | FY25 | 31 | 146.1 | 140.8 |  | 26.9 |  | 10250.8 | 91.32 | 79.72% | 4.5419 | 0 | 0 | 0 | 330.671 | 0 | 0 | 15.09% | [7 empty] | 99.75% | 99.75%
3 | June | 6 | 2024-06-01 | 2024 | FY25 | 30 | 138.5 | 129.7 |  | 28.7 |  | 9261.4 | 91.32 | 78.19% | 4.3233 | 0 | 0 | 0 | 308.7133 | 0 | 0 | 14.09% | [7 empty] | 99.75% | 99.75%
4 | July | 7 | 2024-07-01 | 2024 | FY25 | 31 | 141.9 | 134.4 |  | 29.2 |  | 9676.6 | 91.32 | 78.84% | 4.3355 | 0 | 0 | 0 | 312.1484 | 0 | 0 | 14.24% | [7 empty] | 99.75% | 99.75%
5 | August | 8 | 2024-08-01 | 2024 | FY25 | 31 | 141.2 | 140.6 |  | 29.3 |  | 10090.2 | 91.32 | 78.59% | 4.5355 | 0 | 0 | 0 | 325.4903 | 0 | 0 | 14.85% | [7 empty] | 99.75% | 99.75%
6 | September | 9 | 2024-09-01 | 2024 | FY25 | 30 | 132.4 | 140.1 |  | 28.5 |  | 10035.8 | 91.32 | 78.44% | 4.67 | 0 | 0 | 0 | 334.5267 | 0 | 0 | 15.26% | [7 empty] | 99.75% | 99.75%
7 | October | 10 | 2024-10-01 | 2024 | FY25 | 31 | 133.5 | 155.4 |  | 26.4 |  | 11297.4 | 91.32 | 79.61% | 5.0129 | 0 | 0 | 0 | 364.4323 | 0 | 0 | 16.63% | [7 empty] | 99.75% | 99.75%
8 | November | 11 | 2024-11-01 | 2024 | FY25 | 30 | 121.1 | 155.7 |  | 22.2 |  | 11495.2 | 91.32 | 80.85% | 5.19 | 0 | 0 | 0 | 383.1733 | 0 | 0 | 17.48% | [7 empty] | 99.75% | 99.75%
9 | December | 12 | 2024-12-01 | 2024 | FY25 | 31 | 113.3 | 152.7 |  | 18.39 |  | 11445.5 | 91.32 | 82.08% | 4.9258 | 0 | 0 | 0 | 369.2097 | 0 | 0 | 16.85% | [7 empty] | 99.75% | 99.75%
10 | January | 1 | 2025-01-01 | 2025 | FY25 | 31 | 109.7 | 139.3 |  | 17.2 |  | 10478.8 | 91.32 | 82.37% | 4.4935 | 0 | 0 | 0 | 338.0258 | 0 | 0 | 15.42% | [7 empty] | 99.75% | 99.75%
11 | February | 2 | 2025-02-01 | 2025 | FY25 | 28 | 113.9 | 134.1 |  | 19.5 |  | 9933.5 | 91.32 | 81.12% | 4.7893 | 0 | 0 | 0 | 354.7679 | 0 | 0 | 16.19% | [7 empty] | 99.75% | 99.75%
12 | March | 3 | 2025-03-01 | 2025 | FY25 | 31 | 137.9 | 148.5 |  | 22.5 |  | 10935.7 | 91.32 | 80.64% | 4.7903 | 3 | 14.371 | 14.371 | 352.7645 | 1058.2935 | 1058.2935 | 16.1% | 16.1% | 16.1% | 91.87 | 91.87 |  |  |  | 99.75% | 99.75%
13 | April | 4 | 2025-04-01 | 2025 | FY26 | 30 | 167.2997 | 136.5 |  | 24.6 |  | 9969.4971 | 91.32 | 79.98% | 4.55 | 30 | 136.5 | 136.5 | 332.3166 | 9969.4971 | 9969.4971 | 15.16% | 15.16% | 15.16% | 91.87 | 91.87 |  |  |  | 99.75% | 99.75%
14 | May | 5 | 2025-05-01 | 2025 | FY26 | 31 | 203.1012 | 140.8 |  | 26.9 |  | 10250.797 | 91.32 | 79.72% | 4.5419 | 31 | 140.8 | 277.3 | 330.6709 | 10250.797 | 20220.2941 | 15.09% | 15.09% | 15.12% | 91.87 | 91.87 |  |  |  | 99.75% | 99.75%
15 | June | 6 | 2025-06-01 | 2025 | FY26 | 30 | 138.5 | 129.7 |  | 28.7 |  | 9261.3973 | 91.32 | 78.19% | 4.3233 | 30 | 129.7 | 407 | 308.7132 | 9261.3973 | 29481.6914 | 14.09% | 14.09% | 14.78% | 91.87 | 91.87 |  |  |  | 99.75% | 99.75%
16 | July | 7 | 2025-07-01 | 2025 | FY26 | 31 | 141.9 | 134.4 |  | 29.2 |  | 9676.5972 | 91.32 | 78.84% | 4.3355 | 6 | 26.0129 | 433.0129 | 312.1483 | 1872.8898 | 31354.5811 | 14.24% | 14.24% | 14.75% | 91.87 | 91.87 |  |  |  | 99.75% | 99.75%
17 | August | 8 | 2025-08-01 | 2025 | FY26 | 31 | 141.2 | 140.6 |  | 29.3 |  | 10090.197 | 91.32 | 78.59% | 4.5355 | 0 | 0 | 433.0129 | 325.4902 | 0 | 31354.5811 | 14.85% |  | 14.75% |  | 91.87 |  |  |  | 99.75% | 99.75%
18 | September | 9 | 2025-09-01 | 2025 | FY26 | 30 | 132.4 | 140.1 |  | 28.5 |  | 10035.7971 | 91.32 | 78.44% | 4.67 | 0 | 0 | 433.0129 | 334.5266 | 0 | 31354.5811 | 15.26% |  | 14.75% |  | 91.87 |  |  |  | 99.75% | 99.75%
19 | October | 10 | 2025-10-01 | 2025 | FY26 | 31 | 133.5 | 155.4 |  | 26.4 |  | 11297.3967 | 91.32 | 79.61% | 5.0129 | 0 | 0 | 433.0129 | 364.4322 | 0 | 31354.5811 | 16.63% |  | 14.75% |  | 91.87 |  |  |  | 99.75% | 99.75%
20 | November | 11 | 2025-11-01 | 2025 | FY26 | 30 | 121.1 | 155.7 |  | 22.2 |  | 11495.1966 | 91.32 | 80.85% | 5.19 | 0 | 0 | 433.0129 | 383.1732 | 0 | 31354.5811 | 17.48% |  | 14.75% |  | 91.87 |  |  |  | 99.75% | 99.75%
21 | December | 12 | 2025-12-01 | 2025 | FY26 | 31 | 113.3 | 152.7 |  | 18.39 |  | 11445.4966 | 91.32 | 82.08% | 4.9258 | 0 | 0 | 433.0129 | 369.2096 | 0 | 31354.5811 | 16.85% |  | 14.75% |  | 91.87 |  |  |  | 99.75% | 99.75%
22 | January | 1 | 2026-01-01 | 2026 | FY26 | 31 | 109.7 | 139.3 |  | 17.2 |  | 10478.7969 | 91.32 | 82.37% | 4.4935 | 0 | 0 | 433.0129 | 338.0257 | 0 | 31354.5811 | 15.42% |  | 14.75% |  | 91.87 |  |  |  | 99.75% | 99.75%
23 | February | 2 | 2026-02-01 | 2026 | FY26 | 28 | 113.9 | 134.1 |  | 19.5 |  | 9933.4971 | 91.32 | 81.12% | 4.7893 | 0 | 0 | 433.0129 | 354.7678 | 0 | 31354.5811 | 16.19% |  | 14.75% |  | 91.87 |  |  |  | 99.75% | 99.75%
24 | March | 3 | 2026-03-01 | 2026 | FY26 | 31 | 137.9 | 148.5 |  | 22.5 |  | 10935.6968 | 91.32 | 80.64% | 4.7903 | 0 | 0 | 433.0129 | 352.7644 | 0 | 31354.5811 | 16.1% |  | 14.75% |  | 91.87 |  |  |  | 99.75% | 99.75%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## Sheet1 (hidden)
| GlobHor | DiffHor | T_Amb | GlobInc | GlobEff | EArray | E_Grid | PR |  | 124870.36
| kWh/m² | kWh/m² | °C | kWh/m² | kWh/m² | MWh | MWh | ratio
January | 109.7 | 52 | 17.2 | 139.3 | 132.6 | 11330 | 10889 | 0.851 | 0.084772 | 10585.5457
February | 113.9 | 59.2 | 19.5 | 134.1 | 127.6 | 10805 | 10386 | 0.843 | 0.080856 | 10096.5633
March | 137.9 | 80.9 | 22.5 | 148.5 | 140.8 | 11820 | 11364 | 0.833 | 0.08847 | 11047.3085
April | 135 | 81.4 | 24.6 | 136.5 | 129 | 10763 | 9471 | 0.755 | 0.073733 | 9207.0625
May | 146.1 | 87.4 | 26.9 | 140.8 | 132.9 | 11067 | 10652 | 0.824 | 0.082927 | 10355.1504
June | 138.5 | 84.9 | 28.7 | 129.7 | 121.8 | 10014 | 9623 | 0.808 | 0.074916 | 9354.8266
July | 141.9 | 83.4 | 29.2 | 134.4 | 126.7 | 10455 | 10055 | 0.814 | 0.078279 | 9774.7876
August | 141.2 | 80.6 | 29.3 | 140.6 | 133 | 10902 | 10485 | 0.812 | 0.081627 | 10192.8044
September | 132.4 | 69.2 | 28.5 | 140.1 | 133 | 10862 | 10427 | 0.81 | 0.081176 | 10136.4207
October | 133.5 | 56.6 | 26.4 | 155.4 | 148.5 | 12221 | 11740 | 0.822 | 0.091397 | 11412.8301
November | 121.1 | 43.4 | 22.2 | 155.7 | 148.8 | 12424 | 11465 | 0.801 | 0.089257 | 11145.4938
December | 113.3 | 43.4 | 18.39 | 152.6 | 145.4 | 12374 | 11893 | 0.848 | 0.092589 | 11561.5663
Year | 1564.5 | 822.39 | 24.47 | 1707.7 | 1620.2 | 135037 | 128450 | 0.819

## GA
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
Sr. No. | Date | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Breakdown Description | Fault Time | Work Completion time on fault | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(Wh/m2) | Approximate Energy Loss (KWh)
1 | 2025-04-06 | 2026 | 2025 | Year-3 | Year-3 | 2025-04-01 | 30 | 0.22361 | 0.71042 | 11.6833 | 220KV_Line | 91872.5 | 100% | GSS Auto Reclose operated. | 5:35 | 6:06 | 0.51667 | After grid voltage coming charged the Breaker | Close | 0.51668 | 0.03
2 | 2025-06-26 | 2026 | 2025 | Year-3 | Year-3 | 2025-06-01 | 30 | 0.20694 | 0.74028 | 12.8 | 220KV_Line | 91872.5 | 100% | GSS Auto Reclose operated. | 15:19 | 16:08 | 0.81667 | After grid voltage coming charged the Breaker | Close | 0.81669 | 0.3635
Formulas:
Month Year = GA_18[[#This Row],[Date]]-DAY(GA_18[[#This Row],[Date]])+1
Days = DAY(EOMONTH(GA_18[[#This Row],[Month Year]],0))
Sunrise Time (POA>20 W/m2) = XLOOKUP(GA_18[[#This Row],[Date]],Raw_Data!$B:$B,Raw_Data!J:J)
Sunset Time (POA<20 W/m2) = XLOOKUP(GA_18[[#This Row],[Date]],Raw_Data!$B:$B,Raw_Data!K:K)

## PA
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Sr. No. | Date | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Inverter Station Number (if Bd in filed) | Inverter number (If Inv or Str BD) | LT Number (If breakdwon in Below LT Panel) | String Type(If String BD, No other filed to be inserted) | Equipment (If any BD above LT panel) | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Fault Category | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgement Time | Work Start time on Fault | Work Completion time on fault | Acknow. time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(KWh/m2) | Approximate Energy Loss (KWh) | PTW No. | Job Card No. | SCOPE
#REF! | 2024-02-09 | 2024 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.02773% | String Fuses |  | Fruse burn | 10:55 | NA | NA | 11:35 |  |  |  | 0.66667 | Fuse Replaced | Close | 0.0001849 | 0.56 |  |  |  | MTPL
#REF! | 2024-07-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 11:30 | NA | NA | 15:35 |  |  |  | 4.0833 | Restored to normal | Close | 0.0011325 | 2.58 | 51.8295
#REF! | 2024-07-28 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:07 | NA | NA | 15:25 |  |  |  | 10.3 | Restored to normal | Close | 0.0028567 | 6.15 | 123.547
#REF! | 2024-07-28 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:07 | NA | NA | 15:26 |  |  |  | 10.3167 | Restored to normal | Close | 0.0028613 | 6.16 | 123.7479
#REF! | 2024-07-28 | 2025 | 2024 | Year_3 | Year_3 | 2024-07-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:07 | NA | NA | 15:26 |  |  |  | 10.3167 | Restored to normal | Close | 0.0028613 | 6.16 | 123.7479
#REF! | 2024-08-04 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 9:56 | NA | NA | 11:13 |  |  |  | 1.2833 | Restored to normal | Close | 0.00035593 | 0.71 | 14.2169
#REF! | 2024-08-09 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:07 | NA | NA | 17:28 |  |  |  | 12.35 | Not Restored | Open | 0.0034253 | 5.58 | 111.7332
#REF! | 2024-08-09 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:07 | NA | NA | 17:28 |  |  |  | 12.35 | Not Restored | Open | 0.0034253 | 5.58 | 111.7332
#REF! | 2024-08-09 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:07 | NA | NA | 17:28 |  |  |  | 12.35 | Not Restored | Open | 0.0034253 | 5.58 | 111.7332
#REF! | 2024-08-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:11 | NA | NA | 9:36 |  |  |  | 4.4167 | Restored to normal | Close | 0.001225 | 1.05 | 21.0251
#REF! | 2024-08-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:11 | NA | NA | 9:57 |  |  |  | 4.7667 | Restored to normal | Close | 0.001322 | 1.24 | 24.8296
#REF! | 2024-08-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:11 | NA | NA | 17:26 |  |  |  | 12.25 | Not Restored | Open | 0.0033975 | 4.11 | 82.2981
#REF! | 2024-08-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:11 | NA | NA | 17:26 |  |  |  | 12.25 | Not Restored | Open | 0.0033975 | 4.11 | 82.2981
#REF! | 2024-08-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:11 | NA | NA | 17:26 |  |  |  | 12.25 | Not Restored | Open | 0.0033975 | 4.11 | 82.2981
#REF! | 2024-08-11 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | Inverter |  | String Fault | 5:23 | NA | NA | 17:16 |  |  |  | 11.8833 | Not Restored | Open | 0.0032958 | 2.01 | 40.248
#REF! | 2024-08-11 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | Inverter |  | String Fault | 5:23 | NA | NA | 17:16 |  |  |  | 11.8833 | Not Restored | Open | 0.0032958 | 2.01 | 40.248
#REF! | 2024-08-11 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | Inverter |  | String Fault | 5:23 | NA | NA | 17:16 |  |  |  | 11.8833 | Not Restored | Open | 0.0032958 | 2.01 | 40.248
#REF! | 2024-08-12 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:57 | NA | NA | 17:25 |  |  |  | 11.4667 | Restored to normal | Open | 0.0031803 | 4.71 | 94.3124
#REF! | 2024-08-12 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:57 | NA | NA | 17:25 |  |  |  | 11.4667 | Restored to normal | Open | 0.0031803 | 4.71 | 94.3124
#REF! | 2024-08-12 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:57 | NA | NA | 17:25 |  |  |  | 11.4667 | Restored to normal | Open | 0.0031803 | 4.71 | 94.3124
#REF! | 2024-08-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:01 | NA | NA | 17:36 |  |  |  | 12.5833 | Not Restored | Open | 0.00349 | 6.03 | 120.7439
#REF! | 2024-08-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:01 | NA | NA | 17:36 |  |  |  | 12.5833 | Not Restored | Open | 0.00349 | 6.03 | 120.7439
#REF! | 2024-08-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:01 | NA | NA | 17:36 |  |  |  | 12.5833 | Not Restored | Open | 0.00349 | 6.03 | 120.7439
#REF! | 2024-08-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 10:20 | NA | NA | 10:50 |  |  |  | 0.5 | Restored to normal | Close | 0.00013867 | 0.48 | 9.6115
#REF! | 2024-08-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 10:44 | NA | NA | 11:15 |  |  |  | 0.51667 | Restored to normal | Close | 0.0001433 | 0.51 | 10.2122
#REF! | 2024-08-14 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:13 | NA | NA | 17:24 |  |  |  | 12.1833 | Not Restored | Open | 0.003379 | 5.61 | 112.3339
#REF! | 2024-08-14 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:13 | NA | NA | 17:24 |  |  |  | 12.1833 | Not Restored | Open | 0.003379 | 5.61 | 112.3339
#REF! | 2024-08-14 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:13 | NA | NA | 17:24 |  |  |  | 12.1833 | Not Restored | Open | 0.003379 | 5.61 | 112.3339
#REF! | 2024-08-15 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 7:47 | NA | NA | 17:36 |  |  |  | 9.8167 | Not Restored | Open | 0.0027226 | 3.14 | 62.8749
#REF! | 2024-08-15 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 7:47 | NA | NA | 17:36 |  |  |  | 9.8167 | Not Restored | Open | 0.0027226 | 3.14 | 62.8749
#REF! | 2024-08-15 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 7:47 | NA | NA | 17:36 |  |  |  | 9.8167 | Not Restored | Open | 0.0027226 | 3.14 | 62.8749
#REF! | 2024-08-16 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:21 | NA | NA | 17:24 |  |  |  | 12.05 | Not Restored | Open | 0.003342 | 6.14 | 122.9465
#REF! | 2024-08-16 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:21 | NA | NA | 17:24 |  |  |  | 12.05 | Not Restored | Open | 0.003342 | 7.14 | 142.9704
#REF! | 2024-08-16 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:21 | NA | NA | 17:24 |  |  |  | 12.05 | Not Restored | Open | 0.003342 | 8.14 | 162.9943
#REF! | 2024-08-17 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:08 | NA | NA | 17:13 |  |  |  | 12.0833 | Not Restored | Open | 0.0033513 | 4.44 | 88.906
#REF! | 2024-08-17 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:08 | NA | NA | 17:13 |  |  |  | 12.0833 | Not Restored | Open | 0.0033513 | 4.44 | 88.906
#REF! | 2024-08-17 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:08 | NA | NA | 17:13 |  |  |  | 12.0833 | Not Restored | Open | 0.0033513 | 4.44 | 88.906
#REF! | 2024-08-18 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:36 | NA | NA | 17:08 |  |  |  | 11.5333 | Not Restored | Open | 0.0031988 | 2.52 | 50.4601
#REF! | 2024-08-18 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:36 | NA | NA | 17:08 |  |  |  | 11.5333 | Not Restored | Open | 0.0031988 | 2.52 | 50.4601
#REF! | 2024-08-18 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:36 | NA | NA | 17:08 |  |  |  | 11.5333 | Not Restored | Open | 0.0031988 | 2.52 | 50.4601
#REF! | 2024-08-19 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:17 | NA | NA | 17:09 |  |  |  | 11.8667 | Not Restored | Open | 0.0032912 | 3.66 | 73.2874
#REF! | 2024-08-19 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:17 | NA | NA | 17:09 |  |  |  | 11.8667 | Not Restored | Open | 0.0032912 | 3.66 | 73.2874
#REF! | 2024-08-19 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:17 | NA | NA | 17:09 |  |  |  | 11.8667 | Not Restored | Open | 0.0032912 | 3.66 | 73.2874
#REF! | 2024-08-20 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:35 | NA | NA | 17:11 |  |  |  | 11.6 | Not Restored | Open | 0.0032172 | 2.17 | 43.4518
#REF! | 2024-08-20 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:35 | NA | NA | 17:11 |  |  |  | 11.6 | Not Restored | Open | 0.0032172 | 2.17 | 43.4518
#REF! | 2024-08-20 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:35 | NA | NA | 17:11 |  |  |  | 11.6 | Not Restored | Open | 0.0032172 | 2.17 | 43.4518
#REF! | 2024-08-21 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:09 | NA | NA | 17:37 |  |  |  | 12.4667 | Not Restored | Open | 0.0034576 | 4.39 | 87.9048
#REF! | 2024-08-21 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:09 | NA | NA | 17:37 |  |  |  | 12.4667 | Not Restored | Open | 0.0034576 | 4.39 | 87.9048
#REF! | 2024-08-21 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:09 | NA | NA | 17:37 |  |  |  | 12.4667 | Not Restored | Open | 0.0034576 | 4.39 | 87.9048
#REF! | 2024-08-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:26 | NA | NA | 17:31 |  |  |  | 12.0833 | Not Restored | Open | 0.0033513 | 5.52 | 110.5318
#REF! | 2024-08-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:26 | NA | NA | 17:31 |  |  |  | 12.0833 | Not Restored | Open | 0.0033513 | 5.52 | 110.5318
#REF! | 2024-08-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:26 | NA | NA | 17:31 |  |  |  | 12.0833 | Not Restored | Open | 0.0033513 | 5.52 | 110.5318
#REF! | 2024-08-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:26 | NA | NA | 8:25 |  |  |  | 2.9833 | Restored to normal | Close | 0.00082742 | 1.07 | 21.4255
#REF! | 2024-08-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:26 | NA | NA | 9:05 |  |  |  | 3.65 | Restored to normal | Close | 0.0010123 | 1.55 | 31.037
#REF! | 2024-08-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:26 | NA | NA | 9:05 |  |  |  | 3.65 | Restored to normal | Close | 0.0010123 | 1.55 | 31.037
#REF! | 2024-08-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 10:06 | NA | NA | 15:22 |  |  |  | 5.2667 | Restored to normal | Close | 0.0014607 | 3.6 | 72.0859
#REF! | 2024-08-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:16 | NA | NA | 17:23 |  |  |  | 11.1167 | Not Restored | Open | 0.0030832 | 6 | 120.1432
#REF! | 2024-08-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:16 | NA | NA | 17:23 |  |  |  | 11.1167 | Not Restored | Open | 0.0030832 | 6 | 120.1432
#REF! | 2024-08-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:16 | NA | NA | 17:23 |  |  |  | 11.1167 | Not Restored | Open | 0.0030832 | 6 | 120.1432
#REF! | 2024-08-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:16 | NA | NA | 13:10 |  |  |  | 6.9 | Restored to normal | Close | 0.0019137 | 4.37 | 87.5043
#REF! | 2024-08-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String Fuses |  | String Fault | 9:00 | NA | NA | 12:09 |  |  |  | 3.15 | Restored to normal | Close | 0.00030859 | 2.84 | 20.0867
#REF! | 2024-08-23 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String Fuses |  | String Fault | 12:03 | NA | NA | 17:10 |  |  |  | 5.1167 | Restored to normal | Close | 0.00050125 | 2.83 | 20.016
#REF! | 2024-08-24 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:46 | NA | NA | 17:22 |  |  |  | 11.6 | Not Restored | Open | 0.0032172 | 6.73 | 134.7606
#REF! | 2024-08-24 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:46 | NA | NA | 17:22 |  |  |  | 11.6 | Not Restored | Open | 0.0032172 | 6.73 | 134.7606
#REF! | 2024-08-24 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:46 | NA | NA | 17:22 |  |  |  | 11.6 | Not Restored | Open | 0.0032172 | 6.73 | 134.7606
#REF! | 2024-08-24 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 10:36 | NA | NA | 15:18 |  |  |  | 4.7 | Restored to normal | Close | 0.0013035 | 3.81 | 76.2909
#REF! | 2024-08-24 | 2025 | 2024 | Year_3 | Year_3 | 2024-08-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 10:42 | NA | NA | 15:05 |  |  |  | 4.3833 | Restored to normal | Close | 0.0012157 | 3.62 | 72.4864
#REF! | 2024-09-01 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:12 | NA | NA | 17:21 |  |  |  | 12.15 | Not Restored | Open | 0.0033698 | 5.42 | 108.3295
#REF! | 2024-09-01 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:12 | NA | NA | 17:21 |  |  |  | 12.15 | Not Restored | Open | 0.0033698 | 5.42 | 108.3295
#REF! | 2024-09-02 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:11 | NA | NA | 17:17 |  |  |  | 12.1 | Not Restored | Open | 0.0033559 | 5.35 | 106.9304
#REF! | 2024-09-02 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:11 | NA | NA | 17:17 |  |  |  | 12.1 | Not Restored | Open | 0.0033559 | 5.35 | 106.9304
#REF! | 2024-09-02 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 11:07 | NA | NA | 13:14 |  |  |  | 2.1167 | Not Restored | Close | 0.00058705 | 1.67 | 33.3783
#REF! | 2024-09-03 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:13 | NA | NA | 17:21 |  |  |  | 12.1333 | Not Restored | Open | 0.0033652 | 4.98 | 99.5352
#REF! | 2024-09-03 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:13 | NA | NA | 17:21 |  |  |  | 12.1333 | Not Restored | Open | 0.0033652 | 4.98 | 99.5352
#REF! | 2024-09-04 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:08 | NA | NA | 17:07 |  |  |  | 10.9833 | Not Restored | Open | 0.0030462 | 4.32 | 86.3438
#REF! | 2024-09-04 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:08 | NA | NA | 17:07 |  |  |  | 10.9833 | Not Restored | Open | 0.0030462 | 4.32 | 86.3438
#REF! | 2024-09-05 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:10 | NA | NA | 17:18 |  |  |  | 12.1333 | Not Restored | Open | 0.0033652 | 4.4 | 87.9428
#REF! | 2024-09-05 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:10 | NA | NA | 17:18 |  |  |  | 12.1333 | Not Restored | Open | 0.0033652 | 4.4 | 87.9428
#REF! | 2024-09-06 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:13 | NA | NA | 17:07 |  |  |  | 11.9 | Not Restored | Open | 0.0033004 | 5.35 | 106.9304
#REF! | 2024-09-06 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:13 | NA | NA | 17:07 |  |  |  | 11.9 | Not Restored | Open | 0.0033004 | 5.35 | 106.9304
#REF! | 2024-09-07 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:11 | NA | NA | 17:07 |  |  |  | 11.9333 | Not Restored | Open | 0.0033097 | 6.49 | 129.7156
#REF! | 2024-09-07 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:11 | NA | NA | 17:07 |  |  |  | 11.9333 | Not Restored | Open | 0.0033097 | 6.49 | 129.7156
#REF! | 2024-09-08 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:21 | NA | NA | 17:11 |  |  |  | 10.8333 | Not Restored | Open | 0.0030046 | 5.58 | 111.5274
#REF! | 2024-09-08 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:21 | NA | NA | 17:11 |  |  |  | 10.8333 | Not Restored | Open | 0.0030046 | 5.58 | 111.5274
#REF! | 2024-09-09 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:32 | NA | NA | 17:05 |  |  |  | 11.55 | Not Restored | Open | 0.0032034 | 5.63 | 112.5268
#REF! | 2024-09-09 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:32 | NA | NA | 17:05 |  |  |  | 11.55 | Not Restored | Open | 0.0032034 | 5.63 | 112.5268
#REF! | 2024-09-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:23 | NA | NA | 16:56 |  |  |  | 11.55 | Not Restored | Open | 0.0032034 | 5.26 | 105.1316
#REF! | 2024-09-10 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:23 | NA | NA | 16:56 |  |  |  | 11.55 | Not Restored | Open | 0.0032034 | 5.26 | 105.1316
#REF! | 2024-09-11 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 7:32 | NA | NA | 16:55 |  |  |  | 9.3833 | Not Restored | Open | 0.0026025 | 3.74 | 74.7513
#REF! | 2024-09-11 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 7:32 | NA | NA | 16:55 |  |  |  | 9.3833 | Not Restored | Open | 0.0026025 | 3.74 | 74.7513
#REF! | 2024-09-12 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:45 | NA | NA | 17:01 |  |  |  | 11.2667 | Not Restored | Open | 0.0031248 | 3.13 | 62.5593
#REF! | 2024-09-12 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:45 | NA | NA | 17:01 |  |  |  | 11.2667 | Not Restored | Open | 0.0031248 | 4.13 | 82.5463
#REF! | 2024-09-12 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 12:00 | NA | NA | 15:30 |  |  |  | 3.5 | Restored to normal | Close | 0.00097072 | 7.13 | 142.5072
#REF! | 2024-09-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:17 | NA | NA | 16:59 |  |  |  | 11.7 | Not Restored | Open | 0.003245 | 6.42 | 128.3165
#REF! | 2024-09-13 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:17 | NA | NA | 16:59 |  |  |  | 11.7 | Not Restored | Open | 0.003245 | 6.42 | 128.3165
#REF! | 2024-09-14 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:26 | NA | NA | 17:01 |  |  |  | 11.5833 | Not Restored | Open | 0.0032126 | 6.5 | 129.9154
#REF! | 2024-09-14 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:26 | NA | NA | 17:01 |  |  |  | 11.5833 | Not Restored | Open | 0.0032126 | 6.5 | 129.9154
#REF! | 2024-09-15 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:15 | NA | NA | 17:00 |  |  |  | 11.75 | Not Restored | Open | 0.0032588 | 6.19 | 123.7195
#REF! | 2024-09-15 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:15 | NA | NA | 17:00 |  |  |  | 11.75 | Not Restored | Open | 0.0032588 | 6.19 | 123.7195
#REF! | 2024-09-16 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:11 | NA | NA | 16:58 |  |  |  | 11.7833 | Not Restored | Open | 0.0032681 | 5.36 | 107.1303
#REF! | 2024-09-16 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:11 | NA | NA | 16:58 |  |  |  | 11.7833 | Not Restored | Open | 0.0032681 | 5.36 | 107.1303
#REF! | 2024-09-17 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:11 | NA | NA | 17:08 |  |  |  | 11.95 | Not Restored | Open | 0.0033143 | 5.07 | 101.334
#REF! | 2024-09-17 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:11 | NA | NA | 17:08 |  |  |  | 11.95 | Not Restored | Open | 0.0033143 | 5.07 | 101.334
#REF! | 2024-09-18 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:22 | NA | NA | 16:55 |  |  |  | 11.55 | Not Restored | Open | 0.0032034 | 7.07 | 141.308
#REF! | 2024-09-18 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:22 | NA | NA | 16:55 |  |  |  | 11.55 | Not Restored | Open | 0.0032034 | 8.07 | 161.295
#REF! | 2024-09-19 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:29 | NA | NA | 16:52 |  |  |  | 11.3833 | Not Restored | Open | 0.0031571 | 5.82 | 116.3243
#REF! | 2024-09-19 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:29 | NA | NA | 16:52 |  |  |  | 11.3833 | Not Restored | Open | 0.0031571 | 5.82 | 116.3243
#REF! | 2024-09-20 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:25 | NA | NA | 16:49 |  |  |  | 11.4 | Not Restored | Open | 0.0031618 | 5.49 | 109.7286
#REF! | 2024-09-20 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:25 | NA | NA | 16:49 |  |  |  | 11.4 | Not Restored | Open | 0.0031618 | 5.49 | 109.7286
#REF! | 2024-09-21 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:23 | NA | NA | 16:43 |  |  |  | 11.3333 | Not Restored | Open | 0.0031433 | 5.02 | 100.3347
#REF! | 2024-09-21 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:23 | NA | NA | 16:43 |  |  |  | 11.3333 | Not Restored | Open | 0.0031433 | 5.02 | 100.3347
#REF! | 2024-09-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:27 | NA | NA | 16:52 |  |  |  | 11.4167 | Restored to normal | Close | 0.0031664 | 5.43 | 108.5294
#REF! | 2024-09-22 | 2025 | 2024 | Year_3 | Year_3 | 2024-09-01 | 30 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 5:27 | NA | NA | 16:52 |  |  |  | 11.4167 | Restored to normal | Close | 0.0031664 | 5.43 | 108.5294
#REF! | 2025-01-06 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 13:50 | NA | NA | 14:50 |  |  |  | 1 | Restored | Close | 0.00027735 | 0.95 | 19.9397
#REF! | 2025-01-11 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String Fuses |  | String Fault | 6:19 | NA | NA | 10:30 |  |  |  | 4.1833 | Restored | Close | 0.00040982 | 1.75 | 12.974
#REF! | 2025-01-11 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:19 | NA | NA | 16:20 |  |  |  | 10.0167 | Not Restored | Open | 0.0027781 | 5.03 | 105.5752
#REF! | 2025-01-11 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:19 | NA | NA | 16:20 |  |  |  | 10.0167 | Not Restored | Open | 0.0027781 | 5.03 | 105.5752
#REF! | 2025-01-11 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:19 | NA | NA | 16:20 |  |  |  | 10.0167 | Not Restored | Open | 0.0027781 | 5.03 | 105.5752
#REF! | 2025-01-11 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:19 | NA | NA | 16:20 |  |  |  | 10.0167 | Not Restored | Open | 0.0027781 | 5.03 | 105.5752
#REF! | 2025-01-12 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:18 | NA | NA | 14:09 |  |  |  | 7.85 | Restored | Close | 0.0021772 | 4.4 | 92.3521
#REF! | 2025-01-12 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:18 | NA | NA | 14:09 |  |  |  | 7.85 | Restored | Close | 0.0021772 | 4.4 | 92.3521
#REF! | 2025-01-12 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:18 | NA | NA | 14:09 |  |  |  | 7.85 | restored | Close | 0.0021772 | 4.4 | 92.3521
#REF! | 2025-01-12 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:18 | NA | NA | 14:09 |  |  |  | 7.85 | Restored | Close | 0.0021772 | 4.4 | 92.3521
#REF! | 2025-01-14 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String Fuses |  | String Fault | 6:23 | NA | NA | 8:56 |  |  |  | 2.55 | Restored | Close | 0.00024981 | 0.36 | 2.6689
#REF! | 2025-01-14 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String Fuses |  | String Fault | 6:23 | NA | NA | 9:00 |  |  |  | 2.6167 | Restored | Close | 0.00025634 | 0.39 | 2.8914
#REF! | 2025-01-16 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String Fuses |  | String Fault | 6:19 | NA | NA | 8:35 |  |  |  | 2.2667 | Restored | Close | 0.00022205 | 0.54 | 4.0034
#REF! | 2025-01-16 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String Fuses |  | String Fault | 9:52 | NA | NA | 11:39 |  |  |  | 1.7833 | Restored | Close | 0.0001747 | 1.41 | 10.4534
#REF! | 2025-01-17 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String Fuses |  | String Fault | 10:40 | NA | NA | 13:22 |  |  |  | 2.7 | Restored | Close | 0.0002645 | 2.01 | 14.9016
#REF! | 2025-01-25 | 2025 | 2025 | Year_3 | Year_3 | 2025-01-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:27 | NA | NA | 10:19 |  |  |  | 3.8667 | Restored | Close | 0.0010724 | 0.89 | 18.6803
#REF! | 2025-02-06 | 2025 | 2025 | Year_3 | Year_3 | 2025-02-01 | 28 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 6:30 | NA | NA | 8:39 |  |  |  | 2.15 | Restored | Close | 0.0005963 | 0.18 | 3.7203
#REF! | 2025-03-04 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 0 | #N/A |  |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String Fuses |  | String Fault | 11:00 | NA | NA | 13:09 |  |  |  | 2.15 | Fuse and Y-Connecter Replaced Restored. | Close | 0.0005963 | 1.85 | 38.0124
1 | 2025-04-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.23542 | 0.70764 | 11.3333 | BLK8 | INV23 |  |  |  | BLK8INV23 | 254.8 | 0.0027735 | Inverter |  | Inverter Flashed over. | 0.23542 | NA | NA | 0.68056 |  |  |  | 10.6833 | Inverter replace with new inverter. | Close | 0.02963 | 3.68 | 749.9321
2 | 2025-04-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.23542 | 0.70764 | 11.3333 | BLK8 | INV24 |  |  |  | BLK8INV24 | 267.54 | 0.0029122 | Inverter |  | ACCB MCCB Tripped | 0.23542 | NA | NA | 0.68056 |  |  |  | 10.6833 | Reset and started | Close | 0.031112 | 3.68 | 787.4287 |  |  | Client
3 | 2025-04-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22778 | 0.70694 | 11.5 | BLK8 | Inv13 |  |  |  | BLK8Inv13 | 267.54 | 0.0029122 | Inverter |  | Inverter down due to over grid voltage | 0.41667 | NA | NA | 0.52431 |  |  |  | 2.5833 | Reset and started | Close | 0.0075231 | 1.3 | 278.1677 |  |  | Client
4 | 2025-04-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22778 | 0.70694 | 11.5 | BLK8 | inv15 |  |  |  | BLK8inv15 | 267.54 | 0.0029122 | Inverter |  | Inverter down due to over grid voltage | 0.41667 | NA | NA | 0.52431 |  |  |  | 2.5833 | Reset and started | Close | 0.0075231 | 1.3 | 278.1677 |  |  | Client
5 | 2025-04-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22778 | 0.70694 | 11.5 | BLK8 | inv27 |  |  |  | BLK8inv27 | 267.54 | 0.0029122 | Inverter |  | Inverter down due to over grid voltage | 0.41667 | NA | NA | 0.52431 |  |  |  | 2.5833 | Reset and started | Close | 0.0075231 | 1.3 | 278.1677 |  |  | Client
6 | 2025-04-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22778 | 0.70694 | 11.5 | BLK11 | Inv2 |  |  |  | BLK11Inv2 | 293.02 | 0.0031895 | Inverter |  | Inverter down due to over grid voltage | 0.41667 | NA | NA | 0.52431 |  |  |  | 2.5833 | Reset and started | Close | 0.0082396 | 1.3 | 304.6599 |  |  | Client
7 | 2025-04-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22778 | 0.70694 | 11.5 | BLK11 | Inv3 |  |  |  | BLK11Inv3 | 252 | 0.002743 | Inverter |  | Inverter down due to over grid voltage | 0.41667 | NA | NA | 0.52431 |  |  |  | 2.5833 | Reset and started | Close | 0.0070861 | 1.3 | 262.0104 |  |  | Client
8 | 2025-04-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22778 | 0.70694 | 11.5 | BLK11 | Inv9 |  |  |  | BLK11Inv9 | 267.54 | 0.0029122 | Inverter |  | Inverter down due to over grid voltage | 0.41667 | NA | NA | 0.52431 |  |  |  | 2.5833 | Reset and started | Close | 0.0075231 | 1.3 | 278.1677 |  |  | Client
9 | 2025-04-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22778 | 0.70694 | 11.5 | BLK11 | inv12 |  |  |  | BLK11inv12 | 254.8 | 0.0027735 | Inverter |  | Inverter down due to over grid voltage | 0.41667 | NA | NA | 0.52431 |  |  |  | 2.5833 | Reset and started | Close | 0.0071648 | 1.3 | 264.9217 |  |  | Client
10 | 2025-04-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22778 | 0.70694 | 11.5 | BLK11 | Inv14 |  |  |  | BLK11Inv14 | 267.54 | 0.0029122 | Inverter |  | Inverter down due to over grid voltage | 0.41667 | NA | NA | 0.52431 |  |  |  | 2.5833 | Reset and started | Close | 0.0075231 | 1.3 | 278.1677 |  |  | Client
11 | 2025-04-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22778 | 0.70694 | 11.5 | BLK11 | Inv16 |  |  |  | BLK11Inv16 | 267.54 | 0.0029122 | Inverter |  | Inverter down due to over grid voltage | 0.41667 | NA | NA | 0.52431 |  |  |  | 2.5833 | Reset and started | Close | 0.0075231 | 1.3 | 278.1677 |  |  | Client
12 | 2025-04-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22778 | 0.70694 | 11.5 | BLK11 | Inv18 |  |  |  | BLK11Inv18 | 267.54 | 0.0029122 | Inverter |  | Inverter down due to over grid voltage | 0.41667 | NA | NA | 0.52431 |  |  |  | 2.5833 | Reset and started | Close | 0.0075231 | 1.3 | 278.1677 |  |  | Client
13 | 2025-04-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22778 | 0.70694 | 11.5 | BLK11 | Inv22 |  |  |  | BLK11Inv22 | 254.8 | 0.0027735 | Inverter |  | Inverter down due to over grid voltage | 0.41667 | NA | NA | 0.52431 |  |  |  | 2.5833 | Reset and started | Close | 0.0071648 | 1.3 | 264.9217 |  |  | Client
14 | 2025-04-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22778 | 0.70694 | 11.5 | BLK11 | Inv23 |  |  |  | BLK11Inv23 | 254.8 | 0.0027735 | Inverter |  | Inverter down due to over grid voltage | 0.41667 | NA | NA | 0.52431 |  |  |  | 2.5833 | Reset and started | Close | 0.0071648 | 1.3 | 264.9217 |  |  | Client
15 | 2025-04-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22778 | 0.70694 | 11.5 | BLK11 | Inv25 |  |  |  | BLK11Inv25 | 254.8 | 0.0027735 | Inverter |  | Inverter down due to over grid voltage | 0.41667 | NA | NA | 0.52431 |  |  |  | 2.5833 | Reset and started | Close | 0.0071648 | 1.3 | 264.9217 |  |  | Client
16 | 2025-04-12 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.23194 | 0.71736 | 11.65 | BLK8 | Inv18 |  |  |  | BLK8Inv18 | 254.8 | 0.0027735 | Inverter |  | Inverter Issue | 0.30556 | NA | NA | 0.4375 |  |  |  | 3.1667 | Manually clear fault data after sungrow support. | Close | 0.0087827 | 1.1 | 224.1645 |  |  | MTPL
17 | 2025-04-14 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.20625 | 0.72153 | 12.3667 | BLK12 |  |  |  | Tx | BLK12Tx | 8140.9 | 0.088613 | IDT Breakdown |  | 33 kV HT Cable fault | 0.20625 | NA | NA | 0.72153 |  |  |  | 12.3667 | Fault identification done, Cable jointing work in progress. | Open | 1.0959 | 5.09 | 33140.9458 |  |  | Client
18 | 2025-04-15 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21736 | 0.69236 | 11.4 | BLK12 |  |  |  | Tx | BLK12Tx | 8140.9 | 0.088613 | IDT Breakdown |  | 33 kV HT Cable fault | 0.21736 | NA | NA | 0.69236 |  |  |  | 11.4 | Fault identification done, Cable jointing work in progress. | Open | 1.0102 | 4.92 | 32034.0773 |  |  | Client
19 | 2025-04-16 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.23472 | 0.71458 | 11.5167 | BLK12 |  |  |  | Tx | BLK12Tx | 8140.9 | 0.088613 | IDT Breakdown |  | 33 kV HT Cable fault | 0.23472 | NA | NA | 0.34306 |  |  |  | 2.6 | Cable jointing work done,Now plant running with full load. | Close | 0.23039 | 0.3 | 1953.2974 |  |  | Client
20 | 2025-04-16 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.23472 | 0.71458 | 11.5167 | BLK10 |  |  |  | Tx | BLK10Tx | 8152.2 | 0.088736 | IDT Shutdown |  | Take Shutdown for Cable connection | 0.3125 | NA | NA | 0.34028 |  |  |  | 0.66667 | Restored | Close | 0.059158 | 0.09 | 586.8026 |  |  | Client
21 | 2025-04-16 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.23472 | 0.71458 | 11.5167 | Blk11 |  |  |  | Tx | Blk11Tx | 6567.3 | 0.071485 | IDT Shutdown |  | Take Shutdown for Cable connection | 0.3125 | NA | NA | 0.34028 |  |  |  | 0.66667 | Restored | Close | 0.047656 | 0.09 | 472.7201 |  |  | Client
22 | 2025-04-21 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22014 | 0.71597 | 11.9 |  |  |  | Str_Typ4(455*28) |  | Str_Typ4(455*28) | 0 | 0 | String Fuses |  | String Fault | 0.375 | NA | NA | 0.47222 |  |  |  | 2.3333 | DC fuse replacement done | Close | 0 | 1 | 0 |  |  | MTPL
23 | 2025-04-21 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22014 | 0.71597 | 11.9 |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | Y-Connector Burnt |  | String Fault | 0.375 | NA | NA | 0.45833 |  |  |  | 2 | Y-Connector Replacement Done | Close | 0.0005547 | 0.9 | 18.3407 |  |  | MTPL
24 | 2025-04-21 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22014 | 0.71597 | 11.9 |  |  |  | Str_Typ4(455*28) |  | Str_Typ4(455*28) | 0 | 0 | String Fuses |  | String Fault | 0.4375 | NA | NA | 0.49306 |  |  |  | 1.3333 | DC fuse replacement done | Close | 0 | 1.1 | 0 |  |  | MTPL
25 | 2025-04-21 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22014 | 0.71597 | 11.9 |  |  |  | Str_Typ4(455*28) |  | Str_Typ4(455*28) | 0 | 0 | String Fuses |  | String Fault | 0.45486 | NA | NA | 0.52778 |  |  |  | 1.75 | DC fuse replacement done | Close | 0 | 1.32 | 0 |  |  | MTPL
26 | 2025-04-21 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.22014 | 0.71597 | 11.9 |  |  |  | Str_Typ4(455*28) |  | Str_Typ4(455*28) | 0 | 0 | String Fuses |  | MC-4 Open | 0.53472 | NA | NA | 0.61458 |  |  |  | 1.9167 | Restored | Close | 0 | 1.34 | 0 |  |  | MTPL
27 | 2025-04-22 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21528 | 0.6625 | 10.7333 | BLK8 | Inv18 |  |  |  | BLK8Inv18 | 254.8 | 0.0027735 | Inverter |  | Inverter Issue | 0.27083 | NA | NA | 0.42153 |  |  |  | 3.6167 | Manually clear fault data after sungrow support. | Close | 0.010031 | 0.48 | 97.8172 |  |  | MTPL
28 | 2025-04-22 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21528 | 0.6625 | 10.7333 | BLK8 | Inv18 |  |  |  | BLK8Inv18 | 254.8 | 0.0027735 | Inverter |  | Inverter Issue | 0.46528 | NA | NA | 0.50833 |  |  |  | 1.0333 | Manually clear fault data after sungrow support. | Close | 0.0028659 | 0.15 | 30.5679 |  |  | MTPL
29 | 2025-04-23 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21458 | 0.70833 | 11.85 | BLK8 | Inv18 |  |  |  | BLK8Inv18 | 254.8 | 0.0027735 | Inverter |  | Inverter Issue | 0.25556 | NA | NA | 0.34028 |  |  |  | 2.0333 | Manually clear fault data after sungrow support. | Close | 0.0056394 | 0.1698 | 34.6028 |  |  | MTPL
30 | 2025-04-24 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.23264 | 0.71806 | 11.65 | BLK8 | Inv18 |  |  |  | BLK8Inv18 | 254.8 | 0.0027735 | Inverter |  | Inverter Issue | 0.23611 | NA | NA | 0.34444 |  |  |  | 2.6 | Manually clear fault data after sungrow support. | Close | 0.0072111 | 0.38 | 77.4386 |  |  | MTPL
31 | 2025-04-24 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.23264 | 0.71806 | 11.65 | BLK8 | Inv18 |  |  |  | BLK8Inv18 | 254.8 | 0.0027735 | Inverter |  | Manually Tripped for Inverter inter change | 0.65556 | NA | NA | 0.69722 |  |  |  | 1 | Inverter Inter-change after sungrow service Engineer called | Close | 0.0027735 | 0.09 | 18.3407 |  |  | MTPL
32 | 2025-04-24 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.23264 | 0.71806 | 11.65 | BLK8 | Inv17 |  |  |  | BLK8Inv17 | 254.8 | 0.0027735 | Inverter |  | Manually Tripped for Inverter inter change | 0.65556 | NA | NA | 0.69722 |  |  |  | 1 | Inverter Inter-change after sungrow service Engineer called | Close | 0.0027735 | 0.09 | 18.3407 |  |  | MTPL
33 | 2025-04-27 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.25417 | 0.72431 | 11.2833 | BLK4 | Inv18 |  |  |  | BLK4Inv18 | 289.8 | 0.0031545 | Inverter |  | Inverter flash over | 0.40278 | NA | NA | 0.61458 |  |  |  | 5.0833 | Inverter replace with new inverter. | Close | 0.016035 | 4.05 | 938.7028 |  |  | Client
34 | 2025-04-27 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.63264 | 0.72431 | 2.2 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 0 | 0.0002743 | Inverter |  | Module damage Due to Lighting | 0.40278 | NA | NA | 0.72431 |  |  |  | 7.7167 | Not Restored | open | 0.0021167 | 0.3 | 0 |  |  | MTPL
35 | 2025-04-27 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.25417 | 0.72431 | 11.2833 | BLK5 | Inv20 |  |  |  | BLK5Inv20 | 289.8 | 0.0031545 | Inverter |  | Inverter flash over | 0.4375 | NA | NA | 0.72431 |  |  |  | 6.8833 | Not Restored | open | 0.021713 | 3.67 | 850.627 |  |  | Client
36 | 2025-04-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.70694 | 11.9167 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-01 Module damage Due to Lighting | 0.21042 | NA | NA | 0.70694 |  |  |  | 11.9167 | Not Restored | open | 0.0032687 | 1.63 | 32.8521 |  |  | MTPL
37 | 2025-04-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.70694 | 11.9167 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.21042 | NA | NA | 0.70694 |  |  |  | 11.9167 | Not Restored | open | 0.0032687 | 1.63 | 32.8521 |  |  | MTPL
38 | 2025-04-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.70694 | 11.9167 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.21042 | NA | NA | 0.70694 |  |  |  | 11.9167 | Block-05 inv-20 St-06 Module damage Due to Lighting | open | 0.0032687 | 1.63 | 32.8521 |  |  | MTPL
39 | 2025-04-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.70694 | 11.9167 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-07Inverter flash over | 0.21042 | NA | NA | 0.70694 |  |  |  | 11.9167 | Block-05 inv-20 St-07Inverter flash over | open | 0.0032687 | 1.63 | 32.8521 |  |  | MTPL
40 | 2025-04-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.70694 | 11.9167 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-08Inverter flash over | 0.21042 | NA | NA | 0.70694 |  |  |  | 11.9167 | Block-05 inv-20 St-08Inverter flash over | open | 0.0032687 | 1.63 | 32.8521 |  |  | MTPL
41 | 2025-04-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.70694 | 11.9167 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-09Inverter flash over | 0.21042 | NA | NA | 0.70694 |  |  |  | 11.9167 | Block-05 inv-20 St-09Inverter flash over | open | 0.0032687 | 1.63 | 32.8521 |  |  | MTPL
42 | 2025-04-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.70694 | 11.9167 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-10 Inverter flash over | 0.21042 | NA | NA | 0.70694 |  |  |  | 11.9167 | Block-05 inv-20 St-10 Inverter flash over | open | 0.0032687 | 1.63 | 32.8521 |  |  | MTPL
43 | 2025-04-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.70694 | 11.9167 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-11 Inverter flash over | 0.21042 | NA | NA | 0.70694 |  |  |  | 11.9167 | Block-05 inv-20 St-11 Inverter flash over | open | 0.0032687 | 1.63 | 32.8521 |  |  | MTPL
44 | 2025-04-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.70694 | 11.9167 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-12Inverter flash over | 0.21042 | NA | NA | 0.70694 |  |  |  | 11.9167 | Block-05 inv-20 St-12Inverter flash over | open | 0.0032687 | 1.63 | 32.8521 |  |  | MTPL
45 | 2025-04-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.70694 | 11.9167 | BLK5 | Inv19 |  |  |  | BLK5Inv19 | 289.8 | 0.0031545 | Inverter |  | ACCB Manually Tripped Due to Burn Inverter Data restoration as required for Solis Services engineer | 0.40972 | NA | NA | 0.45 |  |  |  | 0.96667 | Restored | Close | 0.0030493 | 0.088 | 20.3965 |  |  | MTPL
46 | 2025-04-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.70694 | 11.9167 | BLK8 | Inv18 |  |  |  | BLK8Inv18 | 254.8 | 0.0027735 | Inverter |  | Inverter Internal Fault | 0.52778 | NA | NA | 0.68403 |  |  |  | 3.75 | We Have Replaced a nerw Relay card | Close | 0.010401 | 0.288 | 58.6903 |  |  | MTPL
47 | 2025-04-29 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.66597 | 10.9333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-01 Module damage Due to Lighting | 0.21042 | NA | NA | 0.66597 |  |  |  | 10.9333 | Block-04 inv-18 St-01 Module damage Due to Lighting | Open | 0.002999 | 2.76 | 55.6268 |  |  | Client
48 | 2025-04-29 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.66597 | 10.9333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.21042 | NA | NA | 0.66597 |  |  |  | 10.9333 | Block-04 inv-18 St-02 Module damage Due to Lighting | Open | 0.002999 | 2.76 | 55.6268 |  |  | Client
49 | 2025-04-29 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.66597 | 10.9333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.21042 | NA | NA | 0.66597 |  |  |  | 10.9333 | Block-05 inv-20 St-06 Module damage Due to Lighting | Open | 0.002999 | 2.76 | 55.6268 |  |  | Client
50 | 2025-04-29 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.66597 | 10.9333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-07Inverter flash over | 0.21042 | NA | NA | 0.66597 |  |  |  | 10.9333 | Block-05 inv-20 St-07Inverter flash over | Open | 0.002999 | 2.76 | 55.6268 |  |  | Client
51 | 2025-04-29 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.66597 | 10.9333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-08Inverter flash over | 0.21042 | NA | NA | 0.66597 |  |  |  | 10.9333 | Block-05 inv-20 St-08Inverter flash over | Open | 0.002999 | 2.76 | 55.6268 |  |  | Client
52 | 2025-04-29 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.66597 | 10.9333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-09Inverter flash over | 0.21042 | NA | NA | 0.66597 |  |  |  | 10.9333 | Block-05 inv-20 St-09Inverter flash over | Open | 0.002999 | 2.76 | 55.6268 |  |  | Client
53 | 2025-04-29 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.66597 | 10.9333 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-10 Inverter flash over | 0.21042 | NA | NA | 0.66597 |  |  |  | 10.9333 | Block-05 inv-20 St-10 Inverter flash over | Open | 0.0010711 | 2.76 | 19.8667 |  |  | Client
54 | 2025-04-29 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.66597 | 10.9333 | BLK11 | Inv22 |  |  |  | BLK11Inv22 | 254.8 | 0.0027735 | Inverter |  | Grid Over Voltage | 0.39861 | NA | NA | 0.40833 |  |  |  | 0.23333 | Restored | Close | 0.00064715 | 0.147 | 29.9565 |  |  | GRID
55 | 2025-04-29 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.21042 | 0.66597 | 10.9333 | BLK11 | Inv22 |  |  |  | BLK11Inv22 | 254.8 | 0.0027735 | Inverter |  | Grid Over Voltage | 0.47361 | NA | NA | 0.48611 |  |  |  | 0.3 | Restored | Close | 0.00083205 | 0.1 | 20.3786 |  |  | GRID
56 | 2025-04-30 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.20347 | 0.71944 | 12.3833 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-01 Module damage Due to Lighting | 0.20347 | NA | NA | 0.71944 |  |  |  | 12.3833 | Block-04 inv-18 St-01 Module damage Due to Lighting | Open | 0.0033968 | 5.76 | 116.0908 |  |  | Client
57 | 2025-04-30 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.20347 | 0.71944 | 12.3833 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.20347 | NA | NA | 0.71944 |  |  |  | 12.3833 | Block-04 inv-18 St-02 Module damage Due to Lighting | Open | 0.0033968 | 5.76 | 116.0908 |  |  | Client
58 | 2025-04-30 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.20347 | 0.71944 | 12.3833 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.20347 | NA | NA | 0.71944 |  |  |  | 12.3833 | Block-05 inv-20 St-06 Module damage Due to Lighting | Open | 0.0033968 | 5.76 | 116.0908 |  |  | Client
59 | 2025-04-30 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.20347 | 0.71944 | 12.3833 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-07Inverter flash over | 0.20347 | NA | NA | 0.71944 |  |  |  | 12.3833 | Block-05 inv-20 St-07Inverter flash over | Open | 0.0033968 | 5.76 | 116.0908 |  |  | Client
60 | 2025-04-30 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.20347 | 0.71944 | 12.3833 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-08Inverter flash over | 0.20347 | NA | NA | 0.71944 |  |  |  | 12.3833 | Block-05 inv-20 St-08Inverter flash over | Open | 0.0033968 | 5.76 | 116.0908 |  |  | Client
61 | 2025-04-30 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.20347 | 0.71944 | 12.3833 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-09Inverter flash over | 0.20347 | NA | NA | 0.71944 |  |  |  | 12.3833 | Block-05 inv-20 St-09Inverter flash over | Open | 0.0033968 | 5.76 | 116.0908 |  |  | Client
62 | 2025-04-30 | 2026 | 2025 | Year_4 | Year_4 | 2025-04-01 | 30 | 0.20347 | 0.71944 | 12.3833 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-10 Inverter flash over | 0.20347 | NA | NA | 0.71944 |  |  |  | 12.3833 | Block-05 inv-20 St-10 Inverter flash over | Open | 0.0012131 | 5.76 | 41.461 |  |  | Client
63 | 2025-05-01 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21389 | 0.71944 | 12.1333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-01 Module damage Due to Lighting | 0.21389 | NA | NA | 0.71944 |  |  |  | 12.1333 | Block-04 inv-18 St-01 Module damage Due to Lighting | Open | 0.0033282 | 1.84 | 36.9664 |  |  | Client
64 | 2025-05-01 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21389 | 0.71944 | 12.1333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.21389 | NA | NA | 0.71944 |  |  |  | 12.1333 | Block-04 inv-18 St-02 Module damage Due to Lighting | Open | 0.0033282 | 1.84 | 36.9664 |  |  | Client
65 | 2025-05-01 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21389 | 0.71944 | 12.1333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.21389 | NA | NA | 0.71944 |  |  |  | 12.1333 | Block-05 inv-20 St-06 Module damage Due to Lighting | Open | 0.0033282 | 1.84 | 36.9664 |  |  | Client
66 | 2025-05-01 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21389 | 0.71944 | 12.1333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-07Inverter flash over | 0.21389 | NA | NA | 0.71944 |  |  |  | 12.1333 | Block-05 inv-20 St-07Inverter flash over | Open | 0.0033282 | 1.84 | 36.9664 |  |  | Client
67 | 2025-05-01 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21389 | 0.71944 | 12.1333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-08Inverter flash over | 0.21389 | NA | NA | 0.71944 |  |  |  | 12.1333 | Block-05 inv-20 St-08Inverter flash over | Open | 0.0033282 | 1.84 | 36.9664 |  |  | Client
68 | 2025-05-01 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21389 | 0.71944 | 12.1333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-09Inverter flash over | 0.21389 | NA | NA | 0.71944 |  |  |  | 12.1333 | Block-05 inv-20 St-09Inverter flash over | Open | 0.0033282 | 1.84 | 36.9664 |  |  | Client
69 | 2025-05-01 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21389 | 0.71944 | 12.1333 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-10 Inverter flash over | 0.21389 | NA | NA | 0.71944 |  |  |  | 12.1333 | Block-05 inv-20 St-10 Inverter flash over | Open | 0.0011886 | 1.84 | 13.2023 |  |  | Client
70 | 2025-05-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21042 | 0.72292 | 12.3 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-01 Module damage Due to Lighting | 0.21042 | NA | NA | 0.72292 |  |  |  | 12.3 | Block-04 inv-18 St-01 Module damage Due to Lighting | Open | 0.0033739 | 5.07 | 101.8586 |  |  | Client
71 | 2025-05-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21042 | 0.72292 | 12.3 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.21042 | NA | NA | 0.72292 |  |  |  | 12.3 | Block-04 inv-18 St-02 Module damage Due to Lighting | Open | 0.0033739 | 5.07 | 101.8586 |  |  | Client
72 | 2025-05-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21042 | 0.72292 | 12.3 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.21042 | NA | NA | 0.72292 |  |  |  | 12.3 | Block-05 inv-20 St-06 Module damage Due to Lighting | Open | 0.0033739 | 5.07 | 101.8586 |  |  | Client
73 | 2025-05-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21042 | 0.72292 | 12.3 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-07Inverter flash over | 0.21042 | NA | NA | 0.72292 |  |  |  | 12.3 | Block-05 inv-20 St-07Inverter flash over | Open | 0.0033739 | 5.07 | 101.8586 |  |  | Client
74 | 2025-05-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21042 | 0.72292 | 12.3 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-08Inverter flash over | 0.21042 | NA | NA | 0.72292 |  |  |  | 12.3 | Block-05 inv-20 St-08Inverter flash over | Open | 0.0033739 | 5.07 | 101.8586 |  |  | Client
75 | 2025-05-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21042 | 0.72292 | 12.3 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-09Inverter flash over | 0.21042 | NA | NA | 0.72292 |  |  |  | 12.3 | Block-05 inv-20 St-09Inverter flash over | Open | 0.0033739 | 5.07 | 101.8586 |  |  | Client
76 | 2025-05-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21042 | 0.72292 | 12.3 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-10 Inverter flash over | 0.21042 | NA | NA | 0.72292 |  |  |  | 12.3 | Block-05 inv-20 St-10 Inverter flash over | Open | 0.001205 | 5.07 | 36.3781 |  |  | Client
77 | 2025-05-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21042 | 0.72292 | 12.3 | BLK8 | Inv23 |  |  |  | BLK8Inv23 | 254.8 | 0.0027735 | Inverter |  | Grid Over Voltage | 0.40972 | NA | NA | 0.63264 |  |  |  | 5.35 | we have replace a new DSP card As per Solis Services Engineer Instruction. | Close | 0.014838 | 3.61 | 733.3237 |  |  | Client
78 | 2025-05-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21042 | 0.72292 | 12.3 | BLK8 | Inv24 |  |  |  | BLK8Inv24 | 267.54 | 0.0029122 | String |  | Grid Over Voltage | 0.40972 | NA | NA | 0.63264 |  |  |  | 5.35 | Normally Restore | Close | 0.01558 | 3.61 | 769.9898 |  |  | Client
79 | 2025-05-03 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20764 | 0.72569 | 12.4333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-01 Module damage Due to Lighting | 0.20069 | NA | NA | 0.72569 |  |  |  | 12.6 | Block-04 inv-18 St-01 Module damage Due to Lighting | Open | 0.0034562 | 6.3 | 126.5698 |  |  | Client
80 | 2025-05-03 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20764 | 0.72569 | 12.4333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.20069 | NA | NA | 0.72569 |  |  |  | 12.6 | Block-04 inv-18 St-02 Module damage Due to Lighting | Open | 0.0034562 | 6.3 | 126.5698 |  |  | Client
81 | 2025-05-03 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20764 | 0.72569 | 12.4333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.20069 | NA | NA | 0.72569 |  |  |  | 12.6 | Block-05 inv-20 St-06 Module damage Due to Lighting | Open | 0.0034562 | 6.3 | 126.5698 |  |  | Client
82 | 2025-05-03 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20764 | 0.72569 | 12.4333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-07Inverter flash over | 0.20069 | NA | NA | 0.72569 |  |  |  | 12.6 | Block-05 inv-20 St-07Inverter flash over | Close | 0.0034562 | 6.3 | 126.5698 |  |  | Client
83 | 2025-05-03 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20764 | 0.72569 | 12.4333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-08Inverter flash over | 0.20069 | NA | NA | 0.72569 |  |  |  | 12.6 | Block-05 inv-20 St-08Inverter flash over | Close | 0.0034562 | 6.3 | 126.5698 |  |  | Client
84 | 2025-05-03 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20764 | 0.72569 | 12.4333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-09Inverter flash over | 0.20069 | NA | NA | 0.72569 |  |  |  | 12.6 | Block-05 inv-20 St-09Inverter flash over | Close | 0.0034562 | 6.3 | 126.5698 |  |  | Client
85 | 2025-05-03 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20764 | 0.72569 | 12.4333 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-10 Inverter flash over | 0.20069 | NA | NA | 0.72569 |  |  |  | 12.6 | Block-05 inv-20 St-10 Inverter flash over | Close | 0.0012344 | 6.3 | 45.2035 |  |  | Client
86 | 2025-05-03 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20764 | 0.72569 | 12.4333 | BLK1 | Inv46 |  |  |  | BLK1Inv46 | 132 | 0.0014368 | Inverter |  | Inverter relay card fault | 0.24514 | NA | NA | 0.47917 |  |  |  | 5.6167 | Replaced a new inverter | Close | 0.0080701 | 3.15 | 331.4924 |  |  | MTPL
87 | 2025-05-03 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20764 | 0.72569 | 12.4333 | BLK8 | Inv23 |  |  |  | BLK8Inv23 | 254.8 | 0.0027735 | MCCB |  | MCCB fault | 0.39097 | NA | NA | 0.72569 |  |  |  | 8.0333 | Replaced a new MCCB | Close | 0.02228 | 5.08 | 1031.9347 |  |  | Client
88 | 2025-05-03 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20764 | 0.72569 | 12.4333 | BLK8 | Inv24 |  |  |  | BLK8Inv24 | 267.54 | 0.0029122 | MCCB |  | MCCB fault | 0.39097 | NA | NA | 0.72569 |  |  |  | 8.0333 | Replaced a new MCCB | Close | 0.023394 | 5.08 | 1083.5314 |  |  | Client
89 | 2025-05-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20694 | 0.72431 | 12.4167 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-01 Module damage Due to Lighting | 0.20694 | NA | NA | 0.72431 |  |  |  | 12.4167 | Block-04 inv-18 St-01 Module damage Due to Lighting | Open | 0.0034059 | 5.96 | 119.7391 |  |  | Client
90 | 2025-05-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20694 | 0.72431 | 12.4167 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.20694 | NA | NA | 0.72431 |  |  |  | 12.4167 | Block-04 inv-18 St-02 Module damage Due to Lighting | Open | 0.0034059 | 5.96 | 119.7391 |  |  | Client
91 | 2025-05-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20694 | 0.72431 | 12.4167 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.20694 | NA | NA | 0.72431 |  |  |  | 12.4167 | Block-05 inv-20 St-06 Module damage Due to Lighting | Open | 0.0034059 | 5.96 | 119.7391 |  |  | Client
92 | 2025-05-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20694 | 0.72431 | 12.4167 | BLK8 | Inv23 |  |  |  | BLK8Inv23 | 254.8 | 0.0027735 | Inverter |  | MCCB Tripped | 0.49792 | NA | NA | 0.55556 |  |  |  | 1.3833 | manually restore | Close | 0.0038367 | 1.2 | 243.7641 |  |  | MTPL
93 | 2025-05-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20694 | 0.72431 | 12.4167 | BLK8 | Inv24 |  |  |  | BLK8Inv24 | 267.54 | 0.0029122 | Inverter |  | MCCB Tripped | 0.49792 | NA | NA | 0.55556 |  |  |  | 1.3833 | manually restore | Close | 0.0040285 | 1.2 | 255.9523 |  |  | MTPL
94 | 2025-05-05 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20347 | 0.71875 | 12.3667 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-01 Module damage Due to Lighting | 0.20347 | NA | NA | 0.71875 |  |  |  | 12.3667 | Block-04 inv-18 St-01 Module damage Due to Lighting | Open | 0.0033922 | 4.93 | 99.0459 |  |  | Client
95 | 2025-05-05 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20347 | 0.71875 | 12.3667 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.20347 | NA | NA | 0.71875 |  |  |  | 12.3667 | Block-04 inv-18 St-02 Module damage Due to Lighting | Open | 0.0033922 | 4.93 | 99.0459 |  |  | Client
96 | 2025-05-05 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20347 | 0.71875 | 12.3667 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.20347 | NA | NA | 0.71875 |  |  |  | 12.3667 | Block-05 inv-20 St-06 Module damage Due to Lighting | Open | 0.0033922 | 4.93 | 99.0459 |  |  | Client
97 | 2025-05-05 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20347 | 0.71875 | 12.3667 | BLK8 | Inv23 |  |  |  | BLK8Inv23 | 254.8 | 0.0027735 | Inverter |  | MCCB Tripped | 0.20833 | NA | NA | 0.32847 |  |  |  | 2.8833 | manually restore | Close | 0.0079969 | 0.7 | 142.1957 |  |  | MTPL
98 | 2025-05-05 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20347 | 0.71875 | 12.3667 | BLK8 | Inv24 |  |  |  | BLK8Inv24 | 267.54 | 0.0029122 | Inverter |  | MCCB Tripped | 0.20833 | NA | NA | 0.32847 |  |  |  | 2.8833 | manually restore | Close | 0.0083967 | 0.7 | 149.3055 |  |  | MTPL
99 | 2025-05-05 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20347 | 0.71875 | 12.3667 | BLK8 | Inv23 |  |  |  | BLK8Inv23 | 254.8 | 0.0027735 | Inverter |  | MCCB Tripped | 0.5 | NA | NA | 0.5375 |  |  |  | 0.9 | manually restore | Close | 0.0024961 | 0.74 | 150.3212 |  |  | MTPL
100 | 2025-05-05 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20347 | 0.71875 | 12.3667 | BLK8 | Inv24 |  |  |  | BLK8Inv24 | 267.54 | 0.0029122 | Inverter |  | MCCB Tripped | 0.5 | NA | NA | 0.5375 |  |  |  | 0.9 | manually restore | Close | 0.0026209 | 0.74 | 157.8373 |  |  | MTPL
101 | 2025-05-06 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21389 | 0.71806 | 12.1 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-01 Module damage Due to Lighting | 0.21111 | NA | NA | 0.71806 |  |  |  | 12.1667 | Block-04 inv-18 St-01 Module damage Due to Lighting | Open | 0.0033373 | 3.74 | 75.1383 |  |  | MTPL
102 | 2025-05-06 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21389 | 0.71806 | 12.1 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.21111 | NA | NA | 0.71806 |  |  |  | 12.1667 | Block-04 inv-18 St-02 Module damage Due to Lighting | Open | 0.0033373 | 3.74 | 75.1383 |  |  | MTPL
103 | 2025-05-06 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21389 | 0.71806 | 12.1 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.21111 | NA | NA | 0.71806 |  |  |  | 12.1667 | Block-05 inv-20 St-06 Module damage Due to Lighting | Open | 0.0033373 | 3.74 | 75.1383 |  |  | MTPL
104 | 2025-05-07 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.2 | 0.725 | 12.6 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 inv-18 St-01 Module damage Due to Lighting | 0.2 | NA | NA | 0.725 |  |  |  | 12.6 | Block-04 inv-18 St-01 Module damage Due to Lighting | Open | 0.0012344 | 4.91 | 35.23 |  |  | MTPL
105 | 2025-05-07 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.2 | 0.725 | 12.6 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.2 | NA | NA | 0.725 |  |  |  | 12.6 | Block-04 inv-18 St-02 Module damage Due to Lighting | Open | 0.0012344 | 4.91 | 35.23 |  |  | MTPL
106 | 2025-05-07 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.2 | 0.725 | 12.6 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.2 | NA | NA | 0.725 |  |  |  | 12.6 | Block-05 inv-20 St-06 Module damage Due to Lighting | Open | 0.0012344 | 4.91 | 35.23 |  |  | MTPL
107 | 2025-05-08 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.23194 | 0.72639 | 11.8667 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 inv-18 St-01 Module damage Due to Lighting | 0.23194 | NA | NA | 0.72639 |  |  |  | 11.8667 | Block-04 inv-18 St-01 Module damage Due to Lighting | Open | 0.0011625 | 3.26 | 23.391 |  |  | MTPL
108 | 2025-05-08 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.23194 | 0.72639 | 11.8667 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.23194 | NA | NA | 0.72639 |  |  |  | 11.8667 | Block-04 inv-18 St-02 Module damage Due to Lighting | Open | 0.0011625 | 3.26 | 23.391 |  |  | MTPL
109 | 2025-05-08 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.23194 | 0.72639 | 11.8667 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.23194 | NA | NA | 0.72639 |  |  |  | 11.8667 | Block-05 inv-20 St-06 Module damage Due to Lighting | Open | 0.0011625 | 3.26 | 23.391 |  |  | MTPL
110 | 2025-05-09 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20486 | 0.71944 | 12.35 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 inv-18 St-01 Module damage Due to Lighting | 0.20486 | NA | NA | 0.71944 |  |  |  | 12.35 | Block-04 inv-18 St-01 Module damage Due to Lighting | Open | 0.0012099 | 5.56 | 39.8939 |  |  | MTPL
111 | 2025-05-09 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20486 | 0.71944 | 12.35 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.20486 | NA | NA | 0.71944 |  |  |  | 12.35 | Block-04 inv-18 St-02 Module damage Due to Lighting | Open | 0.0012099 | 5.56 | 39.8939 |  |  | MTPL
112 | 2025-05-09 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20486 | 0.71944 | 12.35 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.20486 | NA | NA | 0.71944 |  |  |  | 12.35 | Block-05 inv-20 St-06 Module damage Due to Lighting | Open | 0.0012099 | 5.56 | 39.8939 |  |  | MTPL
113 | 2025-05-10 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20417 | 0.72361 | 12.4667 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 inv-18 St-01 Module damage Due to Lighting | 0.20417 | NA | NA | 0.72361 |  |  |  | 12.4667 | Block-04 inv-18 St-01 Module damage Due to Lighting | Close | 0.0012213 | 5.75 | 41.2572 |  |  | MTPL
114 | 2025-05-10 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20417 | 0.72361 | 12.4667 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.20417 | NA | NA | 0.72361 |  |  |  | 12.4667 | Block-04 inv-18 St-02 Module damage Due to Lighting | Open | 0.0012213 | 5.75 | 41.2572 |  |  | MTPL
115 | 2025-05-10 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20417 | 0.72361 | 12.4667 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.20417 | NA | NA | 0.72361 |  |  |  | 12.4667 | Block-05 inv-20 St-06 Module damage Due to Lighting | Open | 0.0012213 | 5.75 | 41.2572 |  |  | MTPL
116 | 2025-05-10 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20417 | 0.72361 | 12.4667 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Fuse burn | 0.38194 | NA | NA | 0.41319 |  |  |  | 0.75 | Replace a new Fuse | Close | 7.3473e-05 | 0.56 | 4.0181 |  |  | MTPL
117 | 2025-05-10 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20417 | 0.72361 | 12.4667 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Fuse burn | 0.42222 | NA | NA | 0.62292 |  |  |  | 4.8167 | Replace a new Fuse | Close | 0.00047186 | 3.25 | 23.3193 |  |  | MTPL
118 | 2025-05-10 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20417 | 0.72361 | 12.4667 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Fuse burn | 0.43194 | NA | NA | 0.63056 |  |  |  | 4.7667 | Replace a new Fuse | Close | 0.00046696 | 3.24 | 23.2475 |  |  | MTPL
119 | 2025-05-11 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.22778 | 0.73194 | 12.1 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.22778 | NA | NA | 0.73194 |  |  |  | 12.1 | Block-04 inv-18 St-02 Module damage Due to Lighting | Open | 0.0011854 | 3.28 | 23.5345 |  |  | MTPL
120 | 2025-05-11 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.22778 | 0.73194 | 12.1 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.22778 | NA | NA | 0.73194 |  |  |  | 12.1 | Block-05 inv-20 St-06 Module damage Due to Lighting | Open | 0.0011854 | 3.28 | 23.5345 |  |  | MTPL
121 | 2025-05-11 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.22778 | 0.73194 | 12.1 | blk8 | inv13 |  |  |  | blk8inv13 | 267.54 | 0.0029122 | inverter |  | Grid Over Voltage | 0.22778 | NA | NA | 0.35 |  |  |  | 2.9333 | Normally Restore | Close | 0.0085423 | 0.35 | 74.6528 |  |  | Client
122 | 2025-05-11 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.22778 | 0.73194 | 12.1 | blk8 | inv15 |  |  |  | blk8inv15 | 267.54 | 0.0029122 | inverter |  | Grid Over Voltage | 0.22778 | NA | NA | 0.36042 |  |  |  | 3.1833 | Normally Restore | Close | 0.0092704 | 0.46 | 98.1151 |  |  | Client
123 | 2025-05-11 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.22778 | 0.73194 | 12.1 | blk11 | inv2 |  |  |  | blk11inv2 | 293.02 | 0.0031895 | inverter |  | Grid Over Voltage | 0.22778 | NA | NA | 0.32847 |  |  |  | 2.4167 | Normally Restore | Close | 0.007708 | 0.22 | 51.3936 |  |  | Client
124 | 2025-05-11 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.22778 | 0.73194 | 12.1 | blk11 | inv9 |  |  |  | blk11inv9 | 267.54 | 0.0029122 | inverter |  | Grid Over Voltage | 0.22778 | NA | NA | 0.32847 |  |  |  | 2.4167 | Normally Restore | Close | 0.0070377 | 0.22 | 46.9246 |  |  | Client
125 | 2025-05-11 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.22778 | 0.73194 | 12.1 | blk11 | inv14 |  |  |  | blk11inv14 | 267.54 | 0.0029122 | inverter |  | Grid Over Voltage | 0.22778 | NA | NA | 0.32778 |  |  |  | 2.4 | Normally Restore | Close | 0.0069892 | 0.21 | 44.7917 |  |  | Client
126 | 2025-05-11 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.22778 | 0.73194 | 12.1 | blk11 | inv18 |  |  |  | blk11inv18 | 267.54 | 0.0029122 | inverter |  | Grid Over Voltage | 0.22778 | NA | NA | 0.32778 |  |  |  | 2.4 | Normally Restore | Close | 0.0069892 | 0.21 | 44.7917 |  |  | Client
127 | 2025-05-11 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.22778 | 0.73194 | 12.1 | blk11 | inv22 |  |  |  | blk11inv22 | 254.8 | 0.0027735 | inverter |  | Grid Over Voltage | 0.23611 | NA | NA | 0.36528 |  |  |  | 3.1 | Normally Restore | Close | 0.0085978 | 0.51 | 103.5997 |  |  | Client
128 | 2025-05-11 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.22778 | 0.73194 | 12.1 | blk11 | inv25 |  |  |  | blk11inv25 | 254.8 | 0.0027735 | inverter |  | Grid Over Voltage | 0.23611 | NA | NA | 0.36528 |  |  |  | 3.1 | Normally Restore | Close | 0.0085978 | 0.51 | 103.5997 |  |  | Client
129 | 2025-05-12 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20486 | 0.725 | 12.4833 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.20486 | NA | NA | 0.725 |  |  |  | 12.4833 | Block-04 inv-18 St-02 Module damage Due to Lighting | open | 0.0012229 | 5.12 | 36.7368 |  |  | MTPL
130 | 2025-05-12 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20486 | 0.725 | 12.4833 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.20486 | NA | NA | 0.725 |  |  |  | 12.4833 | Block-05 inv-20 St-06 Module damage Due to Lighting | open | 0.0012229 | 5.12 | 36.7368 |  |  | MTPL
131 | 2025-05-13 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20833 | 0.73125 | 12.55 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.20833 | NA | NA | 0.73125 |  |  |  | 12.55 | Block-04 inv-18 St-02 Module damage Due to Lighting | open | 0.0012295 | 3.23 | 23.1758 |  |  | MTPL
132 | 2025-05-13 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20833 | 0.73125 | 12.55 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.20833 | NA | NA | 0.73125 |  |  |  | 12.55 | Block-05 inv-20 St-06 Module damage Due to Lighting | open | 0.0012295 | 3.23 | 23.1758 |  |  | MTPL
133 | 2025-05-13 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20833 | 0.73125 | 12.55 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-11 Inv-21 string fuse burnt | 0.33333 | NA | NA | 0.39583 |  |  |  | 1.5 | Fault fuse replacement done | Close | 0.00014695 | 0.3 | 2.1525 | PTW_3632 | 150 | MTPL
134 | 2025-05-13 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20833 | 0.73125 | 12.55 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-4 Inv-12 string fuse burnt | 0.33333 | NA | NA | 0.41667 |  |  |  | 2 | Fault fuse replacement done | Close | 0.00019593 | 0.31 | 2.2243 | PTW_3638 | 152 | MTPL
135 | 2025-05-14 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20625 | 0.72292 | 12.4 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.20625 | NA | NA | 0.72292 |  |  |  | 12.4 | Block-04 inv-18 St-02 Module damage Due to Lighting | open | 0.0012148 | 4.52 | 32.4317 |  |  | MTPL
136 | 2025-05-14 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20625 | 0.72292 | 12.4 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.20625 | NA | NA | 0.72292 |  |  |  | 12.4 | Block-05 inv-20 St-06 Module damage Due to Lighting | open | 0.0012148 | 4.52 | 32.4317 |  |  | MTPL
137 | 2025-05-14 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20625 | 0.72292 | 12.4 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-5 Inv-13 string fuse burnt | 0.20625 | NA | NA | 0.34236 |  |  |  | 0.31 | Fault fuse replacement done | Close | 3.0369e-05 | 2.57 | 18.4402 | PTW_3650 | 157 | MTPL
138 | 2025-05-15 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.22847 | 0.72847 | 12 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.22847 | NA | NA | 0.72847 |  |  |  | 12 | Block-04 inv-18 St-02 Module damage Due to Lighting | open | 0.0011756 | 2.21 | 15.8571 |  |  | MTPL
139 | 2025-05-15 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.22847 | 0.72847 | 12 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.22847 | NA | NA | 0.72847 |  |  |  | 12 | Block-05 inv-20 St-06 Module damage Due to Lighting | open | 0.0011756 | 2.21 | 15.8571 |  |  | MTPL
140 | 2025-05-15 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.22847 | 0.72847 | 12 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-02 inv-7 St-12 string fuse burnt | 0.4375 | NA | NA | 0.51597 |  |  |  | 1.8833 | One Y connector & 2 number 20A fuse replacement done | Close | 0.0001845 | 0.1 | 0.71752 | PTW_3669 | 165 | MTPL
141 | 2025-05-16 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20972 | 0.72361 | 12.3333 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.20972 | NA | NA | 0.72361 |  |  |  | 12.3333 | Block-04 inv-18 St-02 Module damage Due to Lighting | open | 0.0012082 | 3.53 | 25.3283 |  |  | MTPL
142 | 2025-05-16 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20972 | 0.72361 | 12.3333 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.20972 | NA | NA | 0.72361 |  |  |  | 12.3333 | Block-05 inv-20 St-06 Module damage Due to Lighting | open | 0.0012082 | 3.53 | 25.3283 |  |  | MTPL
143 | 2025-05-16 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20972 | 0.72361 | 12.3333 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-01 inv-41 St-12 string fuse burnt | 0.21111 | NA | NA | 0.36319 |  |  |  | 3.65 | Fault fuse replacement done | Close | 0.00035757 | 0.58 | 4.1616 | 3683 | 169 | MTPL
144 | 2025-05-17 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21181 | 0.72917 | 12.4167 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 inv-18 St-02 Module damage Due to Lighting | 0.21181 | NA | NA | 0.52083 |  |  |  | 7.4167 | New module Replaced | Close | 0.00072657 | 1.96 | 14.0633 |  |  | MTPL
145 | 2025-05-17 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21181 | 0.72917 | 12.4167 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.21181 | NA | NA | 0.72917 |  |  |  | 12.4167 | Block-05 inv-20 St-06 Module damage Due to Lighting | Open | 0.0012164 | 3 | 21.5255 |  |  | MTPL
146 | 2025-05-17 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21181 | 0.72917 | 12.4167 | blk5 | inv20 |  |  |  | blk5inv20 | 289.8 | 0.0031545 | Inverter |  | Inverter Internal Fault | 0.21181 | NA | NA | 0.33611 |  |  |  | 2.9833 | Normally Restore | Close | 0.0094108 | 0.15 | 34.656 |  |  | MTPL
147 | 2025-05-18 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21667 | 0.72222 | 12.1333 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 inv-20 St-06 Module damage Due to Lighting | 0.21667 | NA | NA | 0.5 |  |  |  | 6.8 | Block-05 inv-20 St-06 Module damage Due to Lighting | Close | 0.00066616 | 1.1 | 7.8927 |  |  | MTPL
148 | 2025-05-20 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20139 | 0.73194 | 12.7333 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-12 Inv-11 string-9 One Y connector and one 20A fuse burnt | 0.35417 | NA | NA | 0.40972 |  |  |  | 1.3333 | Fault fuse replacement done | Close | 0.00013062 | 0.3 | 2.1525 | PTW_3754 | 188 | MTPL
149 | 2025-05-20 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20139 | 0.73194 | 12.7333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-3 Inv-8 string-9 fuse burnt | 0.4375 | NA | NA | 0.54514 |  |  |  | 2.5833 | Y connector & Fault fuse replacement done | Close | 0.00070861 | 0.5 | 10.0452 | PTW_3760 | 194 | MTPL
150 | 2025-05-22 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20417 | 0.71736 | 12.3167 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-12 Inv-21 string-5 fuse & Y-connector burnt | 0.25278 | NA | NA | 0.34028 |  |  |  | 2.1 | Y connector & Fault fuse replacement done | Close | 0.00057603 | 0.5 | 10.0452 | PTW_3796 | 201 | MTPL
151 | 2025-05-23 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.19306 | 0.73194 | 12.9333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-02 Inv-26 string-9 fuse burnt | 0.49722 | NA | NA | 0.64931 |  |  |  | 3.65 | Y connector & Fault fuse replacement done | Close | 0.0010012 | 2.35 | 47.2126 | 208 | 208 | MTPL
152 | 2025-05-23 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.19306 | 0.73194 | 12.9333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-04 Inv-11 string-3 fuse burnt | 0.48542 | NA | NA | 0.67222 |  |  |  | 4.4833 | Y connector & Fault fuse replacement done | Close | 0.0012298 | 2.72 | 54.646 | 208 | 208 | MTPL
153 | 2025-05-23 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.19306 | 0.73194 | 12.9333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-05 Inv-9 string-7 fuse burnt | 0.47917 | NA | NA | 0.66181 |  |  |  | 4.3833 | Y connector & Fault fuse replacement done | Close | 0.0012024 | 2.82 | 56.6551 | 208 | 208 | MTPL
154 | 2025-05-23 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.19306 | 0.73194 | 12.9333 |  |  |  | Str_Typ4(450*56) |  | Str_Typ4(450*56) | 25.2 | 0.0002743 | String |  | Block-10 Inv-15 string-10 fuse burnt | 0.46181 | NA | NA | 0.68264 |  |  |  | 5.3 | Y connector & Fault fuse replacement done | Close | 0.0014538 | 3.31 | 66.4994 | 208 | 208 | MTPL
155 | 2025-05-24 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21458 | 0.73889 | 12.5833 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-05 Inv-9 string-11 fuse burnt | 0.35417 | NA | NA | 0.4375 |  |  |  | 2 | Y connector & Fault fuse replacement done | Close | 0.00019593 | 0.89 | 6.3859 | 216 | 216 | MTPL
156 | 2025-05-24 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21458 | 0.73889 | 12.5833 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-10 Inv-5 string-01 fuse burnt | 0.45556 | NA | NA | 0.57292 |  |  |  | 2.8167 | Y connector & Fault fuse replacement done | Close | 0.00027593 | 2.26 | 16.2159 | 216 | 216 | MTPL
157 | 2025-05-24 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21458 | 0.73889 | 12.5833 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-08 Inv-4 string-01 fuse burnt | 0.52083 | NA | NA | 0.65972 |  |  |  | 3.3333 | Fault fuse replacement done | Close | 0.00032655 | 2.13 | 15.2831 | 216 | 216 | MTPL
158 | 2025-05-24 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21458 | 0.73889 | 12.5833 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 Inv-05 string-08 fuse burnt | 0.525 | NA | NA | 0.63056 |  |  |  | 2.5333 | Y connector & Fault fuse replacement done | Close | 0.00024818 | 1.78 | 12.7718 | 216 | 216 | MTPL
159 | 2025-05-24 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.21458 | 0.73889 | 12.5833 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | Block-04 Inv-18 string-8 fuse burnt | 0.54028 | NA | NA | 0.68125 |  |  |  | 3.3833 | Fault fuse replacement done | Close | 0.00033145 | 1.83 | 13.1305 | 216 | 216 | MTPL
160 | 2025-05-25 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20139 | 0.72639 | 12.6 | Blk2 | inv12 |  |  |  | Blk2inv12 | 289.8 | 0.0031545 | Inverter |  | Inverter Fan Fault | 0.50347 | NA | NA | 0.51042 |  |  |  | 0.16667 | Replace a new Fan | Close | 0.00052574 | 0.087 | 20.1005 | 219 | 219 | MTPL
161 | 2025-05-26 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.25069 | 0.725 | 11.3833 | Blk10 | INV16 |  |  |  | Blk10INV16 | 252 | 0.002743 | Inverter |  | Inverter Fan Fault | 0.25069 | NA | NA | 0.33333 |  |  |  | 1.9833 | Replace a new Fan | Close | 0.0054403 | 0.13 | 26.1176 |  |  | MTPL
162 | 2025-05-27 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.19792 | 0.73542 | 12.9 | Blk10 | inv6 |  |  |  | Blk10inv6 | 264.6 | 0.0028802 | Inverter |  | Inverter Fan Fault | 0.57292 | NA | NA | 0.58333 |  |  |  | 0.25 | Replace a new Fan | Close | 0.00072004 | 0.107 | 22.5716 | 230 | 230 | MTPL
163 | 2025-05-27 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.19792 | 0.73542 | 12.9 | Blk10 | inv29 |  |  |  | Blk10inv29 | 264.6 | 0.0028802 | Inverter |  | Inverter Fan Fault | 0.59028 | NA | NA | 0.60069 |  |  |  | 0.25 | Replace a new Fan | Close | 0.00072004 | 0.17 | 35.8614 | 230 | 230 | MTPL
164 | 2025-05-27 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.19792 | 0.73542 | 12.9 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | Block-08 Inv-14 string-07 fuse burnt | 0.525 | NA | NA | 0.60764 |  |  |  | 1.9833 | Y connector & Fault fuse replacement done | Close | 0.00019646 | 1.3 | 9.4313 | 229 | 229 | MTPL
165 | 2025-05-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.19931 | 0.73403 | 12.8333 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | Block-7 Inv-2 string-06 fuse burnt | 0.51667 | NA | NA | 0.57153 |  |  |  | 1.3167 | Y connector & Fault fuse replacement done | Close | 0.00013042 | 0.93 | 6.747 | 236 | 236 | MTPL
166 | 2025-05-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.19931 | 0.73403 | 12.8333 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | Block-11 Inv-2 string-02 fuse burnt | 0.56944 | NA | NA | 0.63194 |  |  |  | 1.5 | Y connector & Fault fuse replacement done | Close | 0.00014858 | 0.98 | 7.1098 | 238 | 238 | MTPL
167 | 2025-05-29 | 2026 | 2025 | Year_4 | Year_4 | 2025-05-01 | 31 | 0.20903 | 0.70833 | 11.9833 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-3,Inv-22 String-6 MC-4 found open | 0.25 | NA | NA | 0.29167 |  |  |  | 1 | Fault rectification done | Close | 9.9053e-05 | 0.1 | 0.72549 | 252 | 252 | MTPL
168 | 2025-06-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19375 | 0.73264 | 12.9333 | blk7 |  |  | inv14 |  | blk7inv14 | 293.02 | 0.0031895 | Inverter |  | Inverter Fan Fault |  | NA | NA |  |  |  |  | 0 | Replace with new inverter | Close | 0 | 0.4 | 91.649 | 259 | 259 | MTPL
169 | 2025-06-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19375 | 0.73264 | 12.9333 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-8,Inv-5 String-8 MC-4 found open |  | NA | NA |  |  |  |  | 0 | Fault rectification done | Close | 0 | 0.4 | 2.8462 | 260 | 260 | MTPL
170 | 2025-06-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20972 | 0.72153 | 12.2833 |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String |  | B-9,Inv-15 String 5 MC-4 & Y connector burnt | 0.25 | NA | NA | 0.30208 |  |  |  | 1.25 | Y connector & 1 pair MC-4 connector replacement done | Close | 0.00034669 | 0.3 | 5.9771 | 271 | 271 | MTPL
171 | 2025-06-05 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20694 | 0.73472 | 12.6667 |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String |  | B-4,Inv-16 String 6 MC-4 &Two 20A fuse, Y connector burnt | 0.41667 | NA | NA | 0.45833 |  |  |  | 1 | B-4,Inv-16 String 6 MC-4 &Two 20A fuse, Y connector replacement done | Close | 0.00027735 | 0.6 | 11.9542 | PTW_4067 |  | MTPL
172 | 2025-06-06 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.22639 | 0.72986 | 12.0833 |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String |  | B-12,Inv-11 String 6 MC-4 &Two 20A fuse, Y connector burnt | 0.59028 | NA | NA | 0.63125 |  |  |  | 0.98333 | B-12,Inv-11, String 6 MC-4 &Two 20A fuse, Y connector replacement done | Close | 0.00027273 | 0.53 | 10.5596 | PTW_4093 |  | MTPL
173 | 2025-06-08 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19653 | 0.73403 | 12.9 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-8,Inv-19 String 9 ,0ne inline fuse holder & 20A fuse, burnt | 0.53472 | NA | NA | 0.57986 |  |  |  | 1.0833 | B-8,Inv-19 String 9 ,0ne inline fuse holder & 20A fuse replacement done | Close | 0.00010731 | 1 | 7.1156 | PTW_4143 |  | MTPL
174 | 2025-06-08 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19653 | 0.73403 | 12.9 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-11,Inv-1 String 8 ,0ne inline fuse holder & 20A fuse burnt | 0.56944 | NA | NA | 0.61111 |  |  |  | 1 | B-11,Inv-1 String 8 ,0ne inline fuse holder & 20A fuse replacement done | Close | 9.9053e-05 | 0.71 | 5.0521 | PTW_4143 |  | MTPL
175 | 2025-06-09 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20208 | 0.73403 | 12.7667 |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String |  | B-6,Inv-20 String 10 ,two inline fuse holder & two 20A fuse,one MC-4 connector & one Y-connector burnt | 0.36111 | NA | NA | 0.41667 |  |  |  | 1.3333 | Y connector & Fault fuse & inline fuse holder & Mc-4 and Y-conncetor replacement done | Close | 0.0003698 | 0.91 | 18.1306 | PTW_4151 |  | MTPL
176 | 2025-06-09 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20208 | 0.73403 | 12.7667 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-10,Inv-9 String 8 ,0ne inline fuse holder & 20A fuse & one Y-connector got burnt | 0.54167 | NA | NA | 0.57292 |  |  |  | 0.75 | Y connector & Fault fuse & inline fuse holder & Mc-4 and Y-conncetor replacement done | Close | 7.429e-05 | 0.55 | 3.9136 | PTW_4157 |  | MTPL
177 | 2025-06-09 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20208 | 0.73403 | 12.7667 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | Block-4 Inv-7 string-07 one 20A fuse burnt | 0.28819 | NA | NA | 0.32292 |  |  |  | 0.83333 | Restored after 20A fuse replacement | Close | 8.2544e-05 | 0.3 | 2.1347 | PTW_4151 |  | MTPL
178 | 2025-06-09 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20208 | 0.73403 | 12.7667 | blk6 | inv28 |  |  |  | blk6inv28 | 264.6 | 0.0028802 | Inverter |  | Inverter Fan Fault | 0.22917 | NA | NA | 0.26389 |  |  |  | 0.83333 | Replace with new inverter | Close | 0.0024001 | 0.1 | 20.69 | PTW_4150 |  | MTPL
179 | 2025-06-09 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20208 | 0.73403 | 12.7667 | blk6 | inv14 |  |  |  | blk6inv14 | 252 | 0.002743 | Inverter |  | Inverter Fan Fault | 0.52431 | NA | NA | 0.53542 |  |  |  | 0.26667 | Replace with new inverter | Close | 0.00073147 | 0.175 | 34.4833 | PTW_4160 |  | MTPL
180 | 2025-06-10 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20486 | 0.71458 | 12.2333 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-4,Inv-7 String 3 ,one inline fuse holder & 0ne 20A fuse, one Y-connector burnt | 0.22917 | NA | NA | 0.33333 |  |  |  | 2.5 | Rectification done | Close | 0.00024763 | 0.7 | 4.9809 | PTW_4174 |  | MTPL
181 | 2025-06-10 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20486 | 0.71458 | 12.2333 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-4,Inv-4 ,String 7 ,one inline fuse holder & 0ne 20A fuse | 0.24306 | NA | NA | 0.34375 |  |  |  | 2.4167 | Rectification done | Close | 0.00023938 | 0.6 | 4.2694 | PTW_4174 |  | MTPL
182 | 2025-06-10 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20486 | 0.71458 | 12.2333 |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String |  | B-4,Inv-15 ,String 7 ,one inline fuse holder & two 20A fuse & one Y-connector got burnt | 0.30208 | NA | NA | 0.35764 |  |  |  | 1.3333 | Rectification done | Close | 0.0003698 | 0.61 | 12.1535 | PTW_4174 |  | MTPL
183 | 2025-06-11 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20417 | 0.73472 | 12.7333 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-2,Inv-10 ,String 7 one MC4-connector got burnt | 0.52083 | NA | NA | 0.54861 |  |  |  | 0.66667 | Rectification done | Close | 6.6035e-05 | 0.53 | 3.7713 | PTW_4201 |  | MTPL
184 | 2025-06-11 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20417 | 0.73472 | 12.7333 |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String |  | B-5,Inv-25 ,String 12 ,two inline fuse holder & two 20A fuse got burnt | 0.63194 | NA | NA | 0.67708 |  |  |  | 1.0833 | Rectification done | Close | 0.00030046 | 0.41 | 8.1687 | PTW_4202 |  | MTPL
185 | 2025-06-12 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19514 | 0.73125 | 12.8667 | blk7 |  |  | inv13 |  | blk7inv13 | 267.54 | 0.0029122 | Inverter |  | We turn off inverter for Solis customer support for inverter fault rectification | 0.65972 | NA | NA | 0.72222 |  |  |  | 1.5 | Rectification done after Inverter internal cable change from new spare inverter.Also case lodge for Faulty cable replacement. | Close | 0.0043682 | 0.32 | 66.9436 | PTW_4220 |  | MTPL
186 | 2025-06-12 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19514 | 0.73125 | 12.8667 | Blk7 |  |  | Inv14 |  | Blk7Inv14 | 293.02 | 0.0031895 | Inverter |  | We turn off inverter for Solis customer support for inverter fault rectification | 0.65972 | NA | NA | 0.72222 |  |  |  | 1.5 | Restored | Close | 0.0047843 | 0.32 | 73.3192 | PTW_4220 |  | MTPL
187 | 2025-06-12 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19514 | 0.73125 | 12.8667 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-3,Inv-3 ,String 1 ,one inline fuse holder & one 20A fuse & one Y-connector got burnt | 0.59028 | NA | NA | 0.65972 |  |  |  | 1.6667 | Rectification done of faulty string | Close | 0.00016509 | 0.8 | 5.6925 | PTW_4221 |  | MTPL
188 | 2025-06-13 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19653 | 0.73889 | 13.0167 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-4,Inv-5 ,String 11 ,one inline fuse holder & one 20A fuse got burnt | 0.24375 | NA | NA | 0.34167 |  |  |  | 2.35 | Rectification done of faulty string | Close | 0.00023277 | 0.78 | 5.5502 | PTW_4239 |  | MTPL
189 | 2025-06-13 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19653 | 0.73889 | 13.0167 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-8,Inv-12 ,String 2 ,one inline fuse holder & one 20A fuse got burnt | 0.30556 | NA | NA | 0.37361 |  |  |  | 1.6333 | Rectification done of faulty string | Close | 0.00016179 | 0.83 | 5.906 | PTW_4239 |  | MTPL
190 | 2025-06-13 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19653 | 0.73889 | 13.0167 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-7,Inv-27 ,String 10 ,one inline fuse holder & one 20A fuse got burnt | 0.59028 | NA | NA | 0.66667 |  |  |  | 1.8333 | Rectification done of faulty string | Close | 0.0001816 | 0.8 | 5.6925 | PTW_4251 |  | MTPL
191 | 2025-06-13 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19653 | 0.73889 | 13.0167 |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String |  | B-4,Inv-13 ,String 7 ,two inline fuse holder & two 20A fuse & one Y,MC-4-connector got burnt | 0.59722 | NA | NA | 0.62847 |  |  |  | 0.75 | Rectification done of faulty string | Close | 0.00020801 | 1.02 | 20.3222 | PTW_4251 |  | MTPL
192 | 2025-06-14 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.22986 | 0.74097 | 12.2667 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-11,Inv-18 ,String 5 ,MC-4-connector got burnt | 0.24306 | NA | NA | 0.29306 |  |  |  | 1.2 | Rectification done of faulty string | Close | 0.00011886 | 0.23 | 1.6366 | PTW_4260 |  | MTPL
193 | 2025-06-14 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.22986 | 0.74097 | 12.2667 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-6,Inv-9 ,String 9 ,one inline fuse holder & 20A fuse & one Y,MC-4-connector got burnt | 0.35417 | NA | NA | 0.39583 |  |  |  | 1 | Rectification done of faulty string | Close | 9.9053e-05 | 0.41 | 2.9174 | PTW_4267 |  | MTPL
194 | 2025-06-15 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19722 | 0.72917 | 12.7667 | Blk8 | Inv31 |  |  |  | Blk8Inv31 | 267.54 | 0.0029122 | Inverter |  | Inverter Fan Fault | 0.27083 | NA | NA | 0.29167 |  |  |  | 0.5 | 2 Number Inverter cooling fan replaced | Close | 0.0014561 | 0.18 | 37.6558 | PTW_4280 |  | MTPL
195 | 2025-06-15 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19722 | 0.72917 | 12.7667 | Blk1 | inv48 |  |  |  | Blk1inv48 | 144.9 | 0.0015772 | Inverter |  | Inverter replacement | 0.36111 | NA | NA | 0.40278 |  |  |  | 1 | Inverter replaced of B-1 inv48 | Close | 0.0015772 | 0.36 | 40.7889 | PTW_4281 |  | MTPL
196 | 2025-06-16 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.21944 | 0.72569 | 12.15 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-5,Inv-3 ,String 12 ,one inline fuse holder & 20A fuse & one Y,MC-4-connector got burnt | 0.41667 | NA | NA | 0.54167 |  |  |  | 3 | String Rectification Done | Close | 0.00029716 | 0.31 | 2.2058 | PTW_4309 |  | MTPL
197 | 2025-06-16 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.21944 | 0.72569 | 12.15 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-5,Inv-23 ,String 3 ,one inline fuse holder & 20A fuse & one Y,MC-4-connector got burnt | 0.40972 | NA | NA | 0.52778 |  |  |  | 2.8333 | String Rectification Done | Close | 0.00028065 | 0.36 | 2.5616 | PTW_4309 |  | MTPL
198 | 2025-06-17 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.21736 | 0.74444 | 12.65 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-2_Inv-5_String-05 (one inline fuse holder & 20A fuse & one Y,MC-4-connector got burnt) | 0.25 | NA | NA | 0.32639 |  |  |  | 1.8333 | String Rectification Done | Close | 0.0001816 | 0.22 | 1.5654 | PTW_4328 |  | MTPL
199 | 2025-06-17 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.21736 | 0.74444 | 12.65 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-2_Inv-24 _String-03 (two inline fuse holder & Two 20A fuse & one Y got burnt) | 0.60417 | NA | NA | 0.71875 |  |  |  | 2.75 | String Rectification Done | Close | 0.0002724 | 0.45 | 3.202 | PTW_4341 |  | MTPL
200 | 2025-06-17 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.21736 | 0.74444 | 12.65 |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String |  | B-8-Inv-18_String-01- fuse burn.( Used 1nos 20 amp DC fuse) | 0.63194 | NA | NA | 0.73264 |  |  |  | 2.4167 | String Rectification Done | Close | 0.00067026 | 0.38 | 7.571 | PTW_4341 |  | MTPL
201 | 2025-06-18 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.2125 | 0.7125 | 12 | Blk10 | inv22 |  |  |  | Blk10inv22 | 288.9 | 0.0031447 | Inverter |  | Inverter Standby Due To Execessive Leakage current | 0.25347 | NA | NA | 0.34167 |  |  |  | 2.1167 | Restore | Close | 0.0066562 | 0.34 | 76.8063 | PTW_4353 |  | MTPL
202 | 2025-06-18 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.2125 | 0.7125 | 12 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-10,Inv-31 ,String 2 ,one inline fuse holder & 20A fuse & one Y,MC-4-connector got burnt | 0.39583 | NA | NA | 0.4375 |  |  |  | 1 | String Rectification Done | Close | 9.9053e-05 | 0.658 | 4.6821 | PTW_4357 |  | MTPL
203 | 2025-06-18 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.2125 | 0.7125 | 12 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-6,Inv-4 ,String 1 ,one inline fuse holder & 20A fuse & one Y,MC-4-connector got burnt | 0.39722 | NA | NA | 0.44792 |  |  |  | 1.2167 | String Rectification Done | Close | 0.00012051 | 0.795 | 5.6569 | PTW_4357 |  | MTPL
204 | 2025-06-18 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.2125 | 0.7125 | 12 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-6,Inv-27 ,String 5 ,one inline fuse holder & 20A fuse & one Y,MC-4-connector got burnt | 0.40764 | NA | NA | 0.50903 |  |  |  | 2.4333 | String Rectification Done | Close | 0.00024103 | 1.88 | 13.3773 | PTW_4363 |  | MTPL
205 | 2025-06-19 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.22431 | 0.73472 | 12.25 | Blk7 | Inv29 |  |  |  | Blk7Inv29 | 330.26 | 0.0035949 | inverter |  | Inverter Internal Failure | 0.25 | NA | NA | 0.63194 |  |  |  | 9.1667 | Faulty inverter replaced from spare inverter | Close | 0.032953 | 3.7 | 955.4948 | PTW_4380 |  | MTPL
206 | 2025-06-19 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.22431 | 0.73472 | 12.25 | Blk7 | Inv28 |  |  |  | Blk7Inv28 | 329.28 | 0.0035842 | inverter |  | Inverter-28 turn off due to Inverter-29 IGBT testing suggedted by Solis Support team | 0.39583 | NA | NA | 0.47222 |  |  |  | 1.8333 | Inverter turn on after testing of inv-29 | Close | 0.006571 | 0.79 | 203.4057 | PTW_4380 |  | MTPL
207 | 2025-06-19 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.22431 | 0.73472 | 12.25 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-2,Inv-2 ,String 9 ,one inline fuse holder & 20A fuse & one Y got burnt | 0.55208 | NA | NA | 0.70833 |  |  |  | 3.75 | String Rectification Done | Close | 0.00037145 | 1.5 | 10.6734 | PTW_4400 |  | MTPL
208 | 2025-06-19 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.22431 | 0.73472 | 12.25 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-3,Inv-21 ,String 4 ,one inline fuse holder & 20A fuse got burnt | 0.61458 | NA | NA | 0.72917 |  |  |  | 2.75 | String Rectification Done | Close | 0.0002724 | 0.59 | 4.1982 | PTW_4400 |  | MTPL
209 | 2025-06-19 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.22431 | 0.73472 | 12.25 | Blk7 | Inv28 |  |  |  | Blk7Inv28 | 329.28 | 0.0035842 | inverter |  | Inverter turn off for new inverter installation in same ACCB | 0.61458 | NA | NA | 0.63194 |  |  |  | 0.41667 | Turn on after new inverter installation | Close | 0.0014934 | 0.18 | 46.3456 | PTW_4398 |  | MTPL
210 | 2025-06-20 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19931 | 0.72847 | 12.7 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-8,Inv-16 ,String 4 ,one inline fuse holder & 20A fuse got burnt | 0.25 | NA | NA | 0.29306 |  |  |  | 1.0333 | String Rectification Done | Close | 0.00010235 | 0.33 | 2.3482 | PTW_4414 |  | MTPL
211 | 2025-06-20 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19931 | 0.72847 | 12.7 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-1,Inv-59 ,String 3 ,one inline fuse holder & 15A fuse got burnt | 0.36111 | NA | NA | 0.42361 |  |  |  | 1.5 | String Rectification Done | Close | 0.00014858 | 0.51 | 3.629 | PTW_4416 |  | MTPL
212 | 2025-06-21 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20694 | 0.73611 | 12.7 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-2,Inv-14 ,String 5 ,one inline fuse holder & 20A fuse got burnt | 0.25 | NA | NA | 0.3125 |  |  |  | 1.5 | String Rectification Done | Close | 0.00014858 | 0.17 | 1.2097 | PTW_4435 |  | MTPL
213 | 2025-06-21 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20694 | 0.73611 | 12.7 |  |  |  | Str_Typ4(455*56) |  | Str_Typ4(455*56) | 25.48 | 0.00027735 | String |  | B-3,Inv-7 ,String 3 ,two inline fuse holder & 20A fuse got burnt | 0.50694 | NA | NA | 0.5625 |  |  |  | 1.3333 | String Rectification Done | Close | 0.0003698 | 1.02 | 20.3222 | PTW_4447 |  | MTPL
214 | 2025-06-23 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.24444 | 0.73194 | 11.7 | blk3 | inv9 |  |  |  | blk3inv9 | 277.2 | 0.0030173 | Inverter |  | B-3,Inv-9 Display not working due to DC Ground Fault( found 2strings 2 nos of module damaged) | 0.54514 | NA | NA | 0.61806 |  |  |  | 1.75 | Normally Restore(Replace 2 nos Module) | Close | 0.0052803 | 0.71 | 153.8942 | PTW_4484 |  | MTPL
215 | 2025-06-23 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.24444 | 0.73194 | 11.7 | blk3 | inv10 |  |  |  | blk3inv10 | 277.2 | 0.0030173 | Inverter |  | ACCB Manually Tripped Due to restoration as required for fault identify. | 0.60417 | NA | NA | 0.61806 |  |  |  | 0.33333 | Normally Restore | Close | 0.0010058 | 0.1669 | 36.176 | PTW_4484 |  | MTPL
216 | 2025-06-23 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.24444 | 0.73194 | 11.7 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-12,Inv-17 ,String 10 ,one inline fuse holder & 20A fuse got burnt | 0.56944 | NA | NA | 0.59028 |  |  |  | 0.5 | Normally Restore | Close | 4.9527e-05 | 0.22 | 1.5654 | PTW_4486 |  | MTPL
217 | 2025-06-24 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20694 | 0.72083 | 12.3333 | blk8 | inv23 |  |  |  | blk8inv23 | 254.8 | 0.0027735 | Inverter |  | inverter remove due to water level increase upto inverter mc4 base connector | 0.40278 | NA | NA | 0.72083 |  |  |  | 7.6333 | Currently inverter are removed from Field due to water level increase for Heavy rain. | open | 0.021171 | 1.86 | 370.5809 | PTW_4500 |  | Client
218 | 2025-06-24 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20694 | 0.72083 | 12.3333 | blk8 | inv24 |  |  |  | blk8inv24 | 267.54 | 0.0029122 | Inverter |  | Manuall accb Tripped for Inverter Removed perpose | 0.40278 | NA | NA | 0.47222 |  |  |  | 1.6667 | Currently inverter are removed from Field due to water level increase for Heavy rain. | open | 0.0048536 | 0.98 | 205.0149 | PTW_4500 |  | Client
219 | 2025-06-25 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.22431 | 0.73542 | 12.2667 | blk8 | inv23 |  |  |  | blk8inv23 | 254.8 | 0.0027735 | Inverter |  | inverter remove due to water level increase upto inverter mc4 base connector | 0.22431 | NA | NA | 0.73542 |  |  |  | 12.2667 | Currently inverter are removed from Field due to water level increase for Heavy rain. | open | 0.034021 | 4.93 | 982.2386 | PTW_4500 |  | Client
220 | 2025-06-25 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.22431 | 0.73542 | 12.2667 | blk8 | inv24 |  |  |  | blk8inv24 | 267.54 | 0.0029122 | Inverter |  | inverter remove due to water level increase upto inverter mc4 base connector | 0.22431 | NA | NA | 0.73542 |  |  |  | 12.2667 | Currently inverter are removed from Field due to water level increase for Heavy rain. | open | 0.035722 | 4.93 | 1031.3505 | PTW_4500 |  | Client
221 | 2025-06-25 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.22431 | 0.73542 | 12.2667 | blk6 | inv3 |  |  |  | blk6inv3 | 264.6 | 0.0028802 | Inverter |  | inverter remove due to water level increase upto inverter mc4 base connector | 0.22431 | NA | NA | 0.73542 |  |  |  | 12.2667 | Currently inverter are removed from Field due to water level increase for Heavy rain. | open | 0.03533 | 4.93 | 1020.017 | PTW_4500 |  | Client
222 | 2025-06-25 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.22431 | 0.73542 | 12.2667 | blk3 | inv9 |  |  |  | blk3inv9 | 277.2 | 0.0030173 | Inverter |  | B-3,Inv-9 Display not working due to internal fault | 0.34722 | NA | NA | 0.43056 |  |  |  | 2 | Normally Restore | Close | 0.0060346 | 0.37 | 80.1984 | PTW_4524 |  | MTPL
223 | 2025-06-25 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.22431 | 0.73542 | 12.2667 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | B-5,Inv-11 ,String 5 ,Two inline fuse holder & 20A fuse got burnt | 0.46528 | NA | NA | 0.50139 |  |  |  | 0.86667 | String Rectification Done | Close | 8.4903e-05 | 0.37 | 2.6038 | PTW_4526 |  | MTPL
224 | 2025-06-25 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.22431 | 0.73542 | 12.2667 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-7,Inv-20 ,String 2 ,Mc4 connector open | 0.45833 | NA | NA | 0.48611 |  |  |  | 0.66667 | String Rectification Done | Close | 6.6035e-05 | 0.25 | 1.7789 | PTW_4526 |  | MTPL
225 | 2025-06-26 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20694 | 0.74028 | 12.8 | blk8 | inv23 |  |  |  | blk8inv23 | 254.8 | 0.0027735 | Inverter |  | inverter remove due to water level increase upto inverter mc4 base connector | 0.20694 | NA | NA | 0.74028 |  |  |  | 12.8 | Currently inverter are removed from Field due to water level increase for Heavy rain. | open | 0.035501 | 6.19 | 1233.2772 | PTW_4500 |  | Client
226 | 2025-06-26 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20694 | 0.74028 | 12.8 | blk8 | inv24 |  |  |  | blk8inv24 | 267.54 | 0.0029122 | Inverter |  | inverter remove due to water level increase upto inverter mc4 base connector | 0.20694 | NA | NA | 0.74028 |  |  |  | 12.8 | Currently inverter are removed from Field due to water level increase for Heavy rain. | open | 0.037276 | 6.19 | 1294.9411 | PTW_4500 |  | Client
227 | 2025-06-26 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20694 | 0.74028 | 12.8 | blk6 | inv3 |  |  |  | blk6inv3 | 264.6 | 0.0028802 | Inverter |  | inverter remove due to water level increase upto inverter mc4 base connector | 0.20694 | NA | NA | 0.74028 |  |  |  | 12.8 | Currently inverter are removed from Field due to water level increase for Heavy rain. | open | 0.036866 | 6.19 | 1280.711 | PTW_4500 |  | Client
228 | 2025-06-26 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20694 | 0.74028 | 12.8 | blk3 | inv9 |  |  |  | blk3inv9 | 277.2 | 0.0030173 | Inverter |  | B-3,Inv-9 Display not working due to internal fault | 0.36111 | NA | NA | 0.38889 |  |  |  | 0.66667 | Normally Restore | Close | 0.0020115 | 0.14 | 30.3453 |  |  | MTPL
229 | 2025-06-26 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20694 | 0.74028 | 12.8 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | B-10,Inv-06 ,String 8 ,one inline fuse holder & 20A fuse got burnt | 0.20694 | NA | NA | 0.28194 |  |  |  | 1.8 | String Rectification Done | Close | 0.00017634 | 0.2 | 1.4075 |  |  | MTPL
230 | 2025-06-26 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20694 | 0.74028 | 12.8 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-11,Inv-5 ,String 11 ,one inline fuse holder & 20A fuse got burnt | 0.20694 | NA | NA | 0.29861 |  |  |  | 2.2 | String Rectification Done | Close | 0.00021792 | 0.31 | 2.2058 |  |  | MTPL
231 | 2025-06-26 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.20694 | 0.74028 | 12.8 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | B-5,Inv-10 ,String 4 ,one inline fuse holder & 20A fuse got burnt | 0.20694 | NA | NA | 0.32292 |  |  |  | 2.7833 | String Rectification Done | Close | 0.00027267 | 0.57 | 4.0113 |  |  | MTPL
232 | 2025-06-27 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.25625 | 0.73958 | 11.6 | blk8 | inv23 |  |  |  | blk8inv23 | 254.8 | 0.0027735 | Inverter |  | inverter remove due to water level increase upto inverter mc4 base connector | 0.25625 | NA | NA | 0.54167 |  |  |  | 6.85 | Restore | Close | 0.018998 | 2 | 398.4741 |  |  | Client
233 | 2025-06-27 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.25625 | 0.73958 | 11.6 | blk8 | inv24 |  |  |  | blk8inv24 | 267.54 | 0.0029122 | Inverter |  | inverter remove due to water level increase upto inverter mc4 base connector | 0.25625 | NA | NA | 0.54167 |  |  |  | 6.85 | Restore | Close | 0.019948 | 2 | 418.3978 |  |  | Client
234 | 2025-06-27 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.25625 | 0.73958 | 11.6 | blk6 | inv3 |  |  |  | blk6inv3 | 264.6 | 0.0028802 | Inverter |  | inverter remove due to water level increase upto inverter mc4 base connector | 0.25625 | NA | NA | 0.60139 |  |  |  | 8.2833 | Restore | Close | 0.023857 | 3.12 | 645.528 |  |  | Client
235 | 2025-06-27 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.25625 | 0.73958 | 11.6 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-11,Inv-3 ,String 4 ,two inline fuse holder & 20A fuse got burnt | 0.25625 | NA | NA | 0.34236 |  |  |  | 2.0667 | String Rectification Done | Close | 0.00020471 | 0.09 | 0.6404 |  |  | MTPL
236 | 2025-06-27 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.25625 | 0.73958 | 11.6 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | B-3,Inv-19 ,String 3 ,two inline fuse holder & 20A fuse got burnt | 0.32569 | NA | NA | 0.36736 |  |  |  | 1 | String Rectification Done | Close | 9.7965e-05 | 0.14 | 0.98524 |  |  | MTPL
237 | 2025-06-27 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.25625 | 0.73958 | 11.6 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | B-1,Inv-47 ,String 8 ,Y-connector & 15A fuse got burnt | 0.32986 | NA | NA | 0.40278 |  |  |  | 1.75 | String Rectification Done | Close | 0.00017144 | 0.31 | 2.1816 |  |  | MTPL
238 | 2025-06-28 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19514 | 0.73333 | 12.9167 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | B-4,Inv-5 ,String 7 ,Y-connector & 20A fuse got burnt | 0.34028 | NA | NA | 0.4375 |  |  |  | 2.3333 | String Rectification Done | Close | 0.00022858 | 0.867 | 6.1014 |  |  | MTPL
239 | 2025-06-30 | 2026 | 2025 | Year_4 | Year_4 | 2025-06-01 | 30 | 0.19931 | 0.74236 | 13.0333 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | B-1,Inv-2 ,String 8 ,Y-connector & 15A fuse got burnt | 0.21875 | NA | NA | 0.34306 |  |  |  | 2.9833 | String Rectification Done | Close | 0.00029226 | 0.64 | 4.5039 | PTW_4622 |  | MTPL
240 | 2025-07-01 | 2026 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 0.20069 | 0.73819 | 12.9 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-8,Inv-30 ,String 11 ,Y-connector & 20A fuse got burnt | 0.30556 | NA | NA | 0.37222 |  |  |  | 1.6 | String Rectification Done | Close | 0.00015848 | 0.58 | 4.1613 | PTW_4656 |  | MTPL
241 | 2025-07-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 0.19931 | 0.74514 | 13.1 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | B-5,Inv-25 ,String 11 ,Y-connector & 20A fuse got burnt | 0.43194 | NA | NA | 0.61111 |  |  |  | 4.3 | String Rectification Done | Close | 0.00042125 | 2.62 | 18.5909 |  |  | MTPL
242 | 2025-07-02 | 2026 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 0.19931 | 0.74514 | 13.1 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | B-7,Inv-14 ,String 10 ,Y-connector & 20A fuse got burnt | 0.50694 | NA | NA | 0.625 |  |  |  | 2.8333 | String Rectification Done | Close | 0.00027757 | 1.55 | 10.9985 |  |  | MTPL
243 | 2025-07-03 | 2026 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 0.22431 | 0.74167 | 12.4167 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | B-4,Inv-11 ,String 6 ,Y-connector & 20A fuse got burnt | 0.47639 | NA | NA | 0.62222 |  |  |  | 3.5 | String Rectification Done | Close | 0.00034288 | 2.72 | 19.3005 | PTW_4702 |  | MTPL
244 | 2025-07-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 0.22639 | 0.74097 | 12.35 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-8,Inv-12 ,String 2 ,MC4 Connector open | 0.38542 | NA | NA | 0.43403 |  |  |  | 1.1667 | String Rectification Done | Close | 0.00011556 | 0.33 | 2.3676 | PTW_4725 |  | MTPL
245 | 2025-07-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 0.22639 | 0.74097 | 12.35 |  |  |  | Str_Typ4(450*26) |  | Str_Typ4(450*26) | 9 | 9.7965e-05 | String |  | B-7,Inv-17 ,String 2 ,MC4 Connector open | 0.52083 | NA | NA | 0.57639 |  |  |  | 1.3333 | String Rectification Done | Close | 0.00013062 | 1.02 | 7.2377 | PTW_4732 |  | MTPL
246 | 2025-07-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 0.22639 | 0.74097 | 12.35 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-12,Inv-3 ,String 9 ,MC4 Connector open | 0.53125 | NA | NA | 0.59028 |  |  |  | 1.4167 | String Rectification Done | Close | 0.00014033 | 1.01 | 7.2464 | PTW_4732 |  | MTPL
247 | 2025-07-04 | 2026 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 0.22639 | 0.74097 | 12.35 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | String |  | B-8,Inv-24 ,String 2 ,two inline fuse holder & 20A fuse got burnt | 0.54861 | NA | NA | 0.60417 |  |  |  | 1.3333 | String Rectification Done | Close | 0.00013207 | 0.94 | 6.7441 | PTW_4732 |  | MTPL
248 | 2025-07-05 | 2026 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 0.2625 | 0.73889 | 11.4333 | blk2 | inv26 |  |  |  | blk2inv26 | 289.8 | 0.0031545 | Inverter |  | Inverter down due to Inverter software issue | 0.35139 | NA | NA | 0.43194 |  |  |  | 1.9333 | Restore | Close | 0.0060986 | 0.35 | 79.9694 | PTW_4743 |  | MTPL
249 | 2025-07-05 | 2026 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 0.2625 | 0.73889 | 11.4333 |  |  |  | Str_Typ4(455*26) |  | Str_Typ4(455*26) | 9.1 | 9.9053e-05 | string |  | B-8,Inv-29 ,String 11 ,two inline fuse holder found open | 0.54861 | NA | NA | 0.58333 |  |  |  | 0.83333 | String Rectification Done | Close | 8.2544e-05 | 0.5 | 3.5873 | PTW_4754 |  | MTPL
250 | 2025-07-06 | 2026 | 2025 | Year_4 | Year_4 | 2025-07-01 | 31 | 0.27431 | 0.71528 | 10.5833 | Blk3 | Inv9 |  |  |  | Blk3Inv9 | 277.2 | 0.0030173 | Inverter |  | Inverter down due to Inverter software issue | 0.47778 | NA | NA | 0.53819 |  |  |  | 1.45 | Restore | Close | 0.0043751 | 1.07 | 233.8484 | PTW_4771 |  | MTPL
Formulas:
Month Year = PA_19[[#This Row],[Date]]-DAY(PA_19[[#This Row],[Date]])+1
Days = DAY(EOMONTH(PA_19[[#This Row],[Month Year]],0))
Sunrise Time (POA>20 W/m2) = XLOOKUP(PA_19[[#This Row],[Date]],Raw_Data!B:B,Raw_Data!J:J,0)
Sunset Time (POA<20 W/m2) = XLOOKUP(PA_19[[#This Row],[Date]],Raw_Data!B:B,Raw_Data!K:K)

## Raw_Data
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 | 237 | 238 | 239 | 240 | 241 | 242 | 243 | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273 | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304 | 305 | 306 | 307 | 308 | 309 | 310 | 311 | 312 | 313 | 314 | 315 | 316 | 317 | 318 | 319 | 320 | 321 | 322 | 323 | 324 | 325 | 326 | 327 | 328 | 329 | 330 | 331 | 332 | 333 | 334 | 335 | 336 | 337 | 338 | 339 | 340 | 341 | 342 | 343 | 344 | 345 | 346 | 347 | 348 | 349 | 350 | 351 | 352 | 353 | 354 | 355 | 356 | 357 | 358 | 359 | 360 | 361 | 362 | 363 | 364 | 365 | 366 | 367 | 368 | 369 | 370 | 371 | 372 | 373 | 374 | 375 | 376 | 377 | 378 | 379 | 380 | 381 | 382 | 383 | 384 | 385 | 386 | 387 | 388 | 389 | 390 | 391 | 392 | 393 | 394 | 395 | 396 | 397 | 398 | 399 | 400 | 401 | 402 | 403 | 404 | 405 | 406 | 407 | 408 | 409 | 410 | 411 | 412 | 413 | 414 | 415 | 416 | 417 | 418 | 419 | 420 | 421 | 422
Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Plant DC Capcity (MW) | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | BLK1_INV1 | BLK1_INV2 | BLK1_INV3 | BLK1_INV4 | BLK1_INV5 | BLK1_INV6 | BLK1_INV7 | BLK1_INV8 | BLK1_INV9 | BLK1_INV10 | BLK1_INV11 | BLK1_INV12 | BLK1_INV13 | BLK1_INV14 | BLK1_INV15 | BLK1_INV16 | BLK1_INV17 | BLK1_INV18 | BLK1_INV19 | BLK1_INV20 | BLK1_INV21 | BLK1_INV22 | BLK1_INV23 | BLK1_INV24 | BLK1_INV25 | BLK1_INV26 | BLK1_INV27 | BLK1_INV28 | BLK1_INV29 | BLK1_INV30 | BLK1_INV31 | BLK1_INV32 | BLK1_INV33 | BLK1_INV34 | BLK1_INV35 | BLK1_INV36 | BLK1_INV37 | BLK1_INV38 | BLK1_INV39 | BLK1_INV40 | BLK1_INV41 | BLK1_INV42 | BLK1_INV43 | BLK1_INV44 | BLK1_INV45 | BLK1_INV46 | BLK1_INV47 | BLK1_INV48 | BLK1_INV49 | BLK1_INV50 | BLK1_INV51 | BLK1_INV52 | BLK1_INV53 | BLK1_INV54 | BLK1_INV55 | BLK1_INV56 | BLK1_INV57 | BLK1_INV58 | BLK1_INV59 | BLK1_INV60 | BLK1_INV61 | BLK1_INV62 | BLK1_INV63 | BLK2_INV1 | BLK2_INV2 | BLK2_INV3 | BLK2_INV4 | BLK2_INV5 | BLK2_INV6 | BLK2_INV7 | BLK2_INV8 | BLK2_INV9 | BLK2_INV10 | BLK2_INV11 | BLK2_INV12 | BLK2_INV13 | BLK2_INV14 | BLK2_INV15 | BLK2_INV16 | BLK2_INV17 | BLK2_INV18 | BLK2_INV19 | BLK2_INV20 | BLK2_INV21 | BLK2_INV22 | BLK2_INV23 | BLK2_INV24 | BLK2_INV25 | BLK2_INV26 | BLK2_INV27 | BLK2_INV28 | BLK3_INV1 | BLK3_INV2 | BLK3_INV3 | BLK3_INV4 | BLK3_INV5 | BLK3_INV6 | BLK3_INV7 | BLK3_INV8 | BLK3_INV9 | BLK3_INV10 | BLK3_INV11 | BLK3_INV12 | BLK3_INV13 | BLK3_INV14 | BLK3_INV15 | BLK3_INV16 | BLK3_INV17 | BLK3_INV18 | BLK3_INV19 | BLK3_INV20 | BLK3_INV21 | BLK3_INV22 | BLK3_INV23 | BLK4_INV1 | BLK4_INV2 | BLK4_INV3 | BLK4_INV4 | BLK4_INV5 | BLK4_INV6 | BLK4_INV7 | BLK4_INV8 | BLK4_INV9 | BLK4_INV10 | BLK4_INV11 | BLK4_INV12 | BLK4_INV13 | BLK4_INV14 | BLK4_INV15 | BLK4_INV16 | BLK4_INV17 | BLK4_INV18 | BLK4_INV19 | BLK4_INV20 | BLK4_INV21 | BLK4_INV22 | BLK4_INV23 | BLK5_INV1 | BLK5_INV2 | BLK5_INV3 | BLK5_INV4 | BLK5_INV5 | BLK5_INV6 | BLK5_INV7 | BLK5_INV8 | BLK5_INV9 | BLK5_INV10 | BLK5_INV11 | BLK5_INV12 | BLK5_INV13 | BLK5_INV14 | BLK5_INV15 | BLK5_INV16 | BLK5_INV17 | BLK5_INV18 | BLK5_INV19 | BLK5_INV20 | BLK5_INV21 | BLK5_INV22 | BLK5_INV23 | BLK5_INV24 | BLK5_INV25 | BLK5_INV26 | BLK5_INV27 | BLK5_INV28 | BLK5_INV29 | BLK6_INV1 | BLK6_INV2 | BLK6_INV3 | BLK6_INV4 | BLK6_INV5 | BLK6_INV6 | BLK6_INV7 | BLK6_INV8 | BLK6_INV9 | BLK6_INV10 | BLK6_INV11 | BLK6_INV12 | BLK6_INV13 | BLK6_INV14 | BLK6_INV15 | BLK6_INV16 | BLK6_INV17 | BLK6_INV18 | BLK6_INV19 | BLK6_INV20 | BLK6_INV21 | BLK6_INV22 | BLK6_INV23 | BLK6_INV24 | BLK6_INV25 | BLK6_INV26 | BLK6_INV27 | BLK6_INV28 | BLK6_INV29 | BLK6_INV30 | BLK6_INV31 | BLK7_INV1 | BLK7_INV2 | BLK7_INV3 | BLK7_INV4 | BLK7_INV5 | BLK7_INV6 | BLK7_INV7 | BLK7_INV8 | BLK7_INV9 | BLK7_INV10 | BLK7_INV11 | BLK7_INV12 | BLK7_INV13 | BLK7_INV14 | BLK7_INV15 | BLK7_INV16 | BLK7_INV17 | BLK7_INV18 | BLK7_INV19 | BLK7_INV20 | BLK7_INV21 | BLK7_INV22 | BLK7_INV23 | BLK7_INV24 | BLK7_INV25 | BLK7_INV26 | BLK7_INV27 | BLK7_INV28 | BLK7_INV29 | BLK8_INV1 | BLK8_INV2 | BLK8_INV3 | BLK8_INV4 | BLK8_INV5 | BLK8_INV6 | BLK8_INV7 | BLK8_INV8 | BLK8_INV9 | BLK8_INV10 | BLK8_INV11 | BLK8_INV12 | BLK8_INV13 | BLK8_INV14 | BLK8_INV15 | BLK8_INV16 | BLK8_INV17 | BLK8_INV18 | BLK8_INV19 | BLK8_INV20 | BLK8_INV21 | BLK8_INV22 | BLK8_INV23 | BLK8_INV24 | BLK8_INV25 | BLK8_INV26 | BLK8_INV27 | BLK8_INV28 | BLK8_INV29 | BLK8_INV30 | BLK8_INV31 | BLK9_INV1 | BLK9_INV2 | BLK9_INV3 | BLK9_INV4 | BLK9_INV5 | BLK9_INV6 | BLK9_INV7 | BLK9_INV8 | BLK9_INV9 | BLK9_INV10 | BLK9_INV11 | BLK9_INV12 | BLK9_INV13 | BLK9_INV14 | BLK9_INV15 | BLK9_INV16 | BLK9_INV17 | BLK9_INV18 | BLK9_INV19 | BLK9_INV20 | BLK9_INV21 | BLK9_INV22 | BLK10_INV1 | BLK10_INV2 | BLK10_INV3 | BLK10_INV4 | BLK10_INV5 | BLK10_INV6 | BLK10_INV7 | BLK10_INV8 | BLK10_INV9 | BLK10_INV10 | BLK10_INV11 | BLK10_INV12 | BLK10_INV13 | BLK10_INV14 | BLK10_INV15 | BLK10_INV16 | BLK10_INV17 | BLK10_INV18 | BLK10_INV19 | BLK10_INV20 | BLK10_INV21 | BLK10_INV22 | BLK10_INV23 | BLK10_INV24 | BLK10_INV25 | BLK10_INV26 | BLK10_INV27 | BLK10_INV28 | BLK10_INV29 | BLK10_INV30 | BLK10_INV31 | BLK11_INV1 | BLK11_INV2 | BLK11_INV3 | BLK11_INV4 | BLK11_INV5 | BLK11_INV6 | BLK11_INV7 | BLK11_INV8 | BLK11_INV9 | BLK11_INV10 | BLK11_INV11 | BLK11_INV12 | BLK11_INV13 | BLK11_INV14 | BLK11_INV15 | BLK11_INV16 | BLK11_INV17 | BLK11_INV18 | BLK11_INV19 | BLK11_INV20 | BLK11_INV21 | BLK11_INV22 | BLK11_INV23 | BLK11_INV24 | BLK11_INV25 | BLK12_INV1 | BLK12_INV2 | BLK12_INV3 | BLK12_INV4 | BLK12_INV5 | BLK12_INV6 | BLK12_INV7 | BLK12_INV8 | BLK12_INV9 | BLK12_INV10 | BLK12_INV11 | BLK12_INV12 | BLK12_INV13 | BLK12_INV14 | BLK12_INV15 | BLK12_INV16 | BLK12_INV17 | BLK12_INV18 | BLK12_INV19 | BLK12_INV20 | BLK12_INV21 | BLK12_INV22 | BLK12_INV23 | BLK12_INV24 | BLK12_INV25 | BLK12_INV26 | BLK12_INV27 | BLK12_INV28 | BLK12_INV29 | BLK12_INV30 | BLK12_INV31 | Amb_Temp | MT_Temp | WS_Avg | WS_Max | GHI | POA | GHI_Lost | POA_Lost | 33kV_IC1_ExPort | 33kV_IC1_Import | 33kV_IC2_ExPort | 33kV_IC2_Import | 33kV_IC3_ExPort | 33kV_IC3_Import | 33kV_IC4_ExPort | 33kV_IC4_Import | 220kV_PQM1_Ex | 220kV_PQM1_Im | 220kV_PQM2_Ex | 220kV_PQM2_Im | 33kV_IC1_ExPort(KWh) | 33kV_IC1_Import(KWh) | 33kV_IC2_ExPort(KWh) | 33kV_IC2_Import(KWh) | 33kV_IC3_ExPort(KWh) | 33kV_IC3_Import(KWh) | 33kV_IC4_ExPort(kWh) | 33kV_IC4_Import(KWh) | 220kV_PQM1_Ex(KWh) | 220kV_PQM1_Im(KWh) | 220kV_PQM2_Ex(KWh) | 220kV_PQM2_Im(KWh) | 33kV_Net_Ex (kWh) | 220kV_Net_Ex (kWh) | Operating Hours | GHI (KWh/m2) | POA(KWh/m2) | Amm_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | Inv_Exp(KWh) | WPR_Eac | WPR_Edc | WPR | Forecasting Data count received on Forecasting Portal | Forecasting Penalties (INR)
2025-03-29 | 2025 | 2025 |  |  | Mar-25 | 31 | 91870 | 5:40 | 16:50 | 190.4 | 184 | 206.4 | 206.8 | 206 | 193.8 | 210.4 | 202.2 | 209.7 | 210.6 | 209.8 | 209.4 | 210.4 | 210.6 | 213.4 | 212 | 197.8 | 201 | 210.5 | 212.7 | 219.1 | 217.6 | 218.5 | 217.1 | 219.5 | 219.3 | 220.4 | 219 | 220.6 | 221.4 | 218.8 | 219 | 206.3 | 192.1 | 194.2 | 197.7 | 200.8 | 200 | 207.7 | 199 | 203 | 225.5 | 236.4 | 223.6 | 224.9 | 232.5 | 251.5 | 249.7 | 267.5 | 238.7 | 227.5 | 223.8 | 222.3 | 234 | 229.9 | 233.3 | 241.7 | 221.3 | 193.7 | 221.4 | 209.8 | 200.9 | 217.8 | 511.2 | 512.7 | 499.9 | 504.3 | 512.7 | 502.4 | 493.7 | 503.9 | 514.1 | 492.9 | 493.8 | 490.9 | 473.9 | 462.6 | 506.5 | 509.7 | 510.4 | 503.8 | 536.6 | 507.2 | 493.1 | 514.9 | 487.4 | 487.2 | 506.7 | 509.5 | 500.4 | 502.3 | 467.8 | 489 | 492 | 500.6 | 506.2 | 545.6 | 505.8 | 502 | 474.6 | 475.6 | 500.9 | 488.3 | 508.7 | 503.9 | 489 | 511.1 | 499.7 | 498.2 | 513 | 514 | 517.7 | 462.8 | 488.1 | 505.8 | 523.6 | 511.2 | 514.7 | 516.8 | 515.3 | 514.7 | 515.1 | 491.4 | 493.2 | 519.8 | 516.9 | 517.2 | 514.7 | 510.6 | 505.5 | 506.1 | 518.1 | 508.1 | 515.2 | 502.4 | 516.6 | 497 | 526.6 | 563.3 | 506 | 505.4 | 519.7 | 520.6 | 514.2 | 519.7 | 524.8 | 510.1 | 493.5 | 528.8 | 481.2 | 441.9 | 507.5 | 477.4 | 512.1 | 522.9 | 510.2 | 517.9 | 515.7 | 518.5 | 508.2 | 509.6 | 509.2 | 506.3 | 550.1 | 537.7 | 486 | 451.1 | 459.9 | 446.3 | 446.9 | 451.6 | 451.7 | 452.4 | 465.6 | 467.4 | 455.7 | 458.1 | 461.3 | 467.1 | 421.4 | 389 | 472 | 461.5 | 452.6 | 460.5 | 468.5 | 457.7 | 467.5 | 457.6 | 461.3 | 456.6 | 465.9 | 456 | 458.8 | 438 | 435.5 | 441.2 | 502.8 | 489.8 | 447.8 | 511.7 | 513.9 | 512.9 | 529.1 | 521.3 | 573 | 527.5 | 573 | 499.3 | 462.8 | 510.6 | 573 | 543.6 | 573 | 450.5 | 493 | 430.8 | 400.1 | 526.1 | 518.5 | 532.2 | 522.6 | 514 | 510.5 | 570.1 | 563.5 | 466.3 | 480.5 | 437.2 | 436.1 | 433.3 | 451.8 | 441.5 | 455.4 | 432.5 | 438.7 | 437.1 | 438.2 | 456.6 | 454.1 | 453.7 | 455.3 | 444.4 | 444.2 | 437.8 | 458.2 | 435.4 | 453.4 | 436.9 | 457 | 457 | 456.3 | 468.4 | 462.4 | 456.9 | 458.3 | 460.1 | 483.1 | 504.7 | 516.6 | 493.2 | 521.5 | 546.3 | 520.8 | 520.7 | 500.7 | 518.4 | 513.3 | 496 | 550.1 | 523 | 485 | 546.1 | 540.4 | 409.9 | 411.3 | 520.6 | 437.1 | 496.2 | 452.5 | 448.6 | 446.3 | 443 | 454.3 | 441.6 | 451.8 | 441 | 446.2 | 453.1 | 492.4 | 447 | 450.5 | 434.3 | 423.9 | 420.3 | 441.5 | 450 | 446.7 | 447.1 | 448.5 | 1233.7 | 446.5 | 442.4 | 451.8 | 448 | 400.1 | 448.2 | 451.5 | 431.5 | 431.7 | 448 | 503.8 | 436.9 | 459.8 | 457.8 | 453.5 | 431.1 | 404.2 | 456.5 | 477.6 | 427.9 | 429.8 | 466.8 | 460.5 | 457.1 | 457.2 | 458.1 | 459.8 | 488.4 | 430.5 | 429.4 | 445.5 | 447.7 | 429.4 | 451.5 | 454.3 | 468.7 | 463.5 | 466 | 468.7 | 464.9 | 458.9 | 464.4 | 470.7 | 459.4 | 443.7 | 468.7 | 465.2 | 409.4 | 438 | 468.7 | 487.1 | 453.5 | 454.9 | 447.1 | 479.1 | 467.7 | 490.5 | 433.5 | 462.6 | 432.1 | 440.2 | 422.8 | 432.1 | 448.5 | 445.9 | 0 | 27.78 | 0 | 0 | 2.11 | 2.03 | 0 | 0 | 83748550 | 249493 | 85026540 | 290067 | 69025210 | 144776 | 83465240 | 124393 | 789320 | 9860 | 71870 | 400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 11.1667 | 2.11 | 2.03 |  | 27.78 | 0 | 159590.4
2025-03-30 | 2025 | 2025 |  |  | Mar-25 | 31 | 91870 | 5:32 | 17:01 | 452.2 | 435.8 | 488.1 | 489 | 487.7 | 457.5 | 493.5 | 478.3 | 493.7 | 494.6 | 496.1 | 495 | 494.3 | 495.3 | 501.1 | 499.9 | 466.4 | 469.8 | 488.2 | 496.9 | 510.2 | 505.4 | 511.1 | 509.8 | 508.6 | 508.5 | 508.9 | 506.2 | 509.6 | 511.7 | 506.4 | 507.7 | 483 | 453.2 | 458.7 | 465 | 472.2 | 474 | 491.4 | 468.3 | 481.1 | 527.2 | 553.3 | 521.7 | 524.6 | 542.5 | 584 | 576.8 | 625 | 552.2 | 526.1 | 519.8 | 518.4 | 543 | 533.4 | 538.3 | 560.1 | 513.4 | 449.9 | 514.7 | 494.5 | 464.5 | 509.3 | 1190 | 1165.3 | 1158.9 | 1177 | 1194.9 | 1173.7 | 1150.7 | 1174.9 | 1198.3 | 1152.9 | 1151.1 | 1149.7 | 1109.9 | 1085.9 | 1175 | 1180.2 | 1180.4 | 1138.8 | 1244.1 | 1177 | 1145.7 | 1196.2 | 1134.9 | 1132.8 | 1177.5 | 1180 | 1165.7 | 1170.2 | 1123.5 | 1150.6 | 1156.1 | 1175.1 | 1183 | 1278.7 | 1175.2 | 1176.6 | 1114.5 | 1116.2 | 1169.2 | 1138.8 | 1188.1 | 1181.4 | 1135.9 | 1193.7 | 1172.8 | 1170.2 | 1196.2 | 1198.4 | 1209.9 | 1079.6 | 1135.6 | 1186.7 | 1220 | 1197.5 | 1203 | 1213 | 1207.5 | 1194.6 | 1194.5 | 1141.5 | 1145.8 | 1200.1 | 1194.3 | 1162.4 | 1189.4 | 1187.3 | 1173.2 | 1173.9 | 1199 | 1178.5 | 1193.2 | 1167.3 | 1198.9 | 1146.7 | 1217.8 | 1305.3 | 1175.3 | 1170.2 | 1202.1 | 1205 | 1187.4 | 1174.8 | 1213.6 | 1185 | 1144.6 | 1229.5 | 1119.6 | 1027.9 | 1178.6 | 1107.6 | 1190.6 | 1211 | 1185.1 | 1201.9 | 1196.3 | 1203.5 | 1179.4 | 1182.1 | 1182.1 | 1171.3 | 1273.2 | 1239.7 | 1129.7 | 1063.9 | 1079.4 | 1054.3 | 1056.4 | 1067.4 | 1066.9 | 1071.9 | 1098.2 | 1099.3 | 1067.9 | 1079.3 | 1082 | 1093 | 995.6 | 919.8 | 1115.3 | 1091.3 | 1081.1 | 1079.6 | 1097.1 | 1077.9 | 1100 | 1078.1 | 1089.6 | 1074.3 | 1080 | 1073.5 | 1083.4 | 1040.9 | 1034.6 | 1037.1 | 1167.2 | 1133.1 | 1034.2 | 1185.6 | 1189 | 1186.2 | 1230.7 | 1204.3 | 1314.4 | 1217.9 | 1129.1 | 1151.4 | 1066.2 | 1172.4 | 1151.4 | 1247.6 | 1037.4 | 1042.4 | 1138.2 | 993.6 | 928.9 | 1227.3 | 1205.1 | 1205.2 | 1211.5 | 1193.2 | 1186.3 | 1319.8 | 1271.4 | 1101.3 | 1130.4 | 1026.4 | 1027.4 | 1019.2 | 1068 | 1041.2 | 1072.5 | 1036.8 | 1035.2 | 1031.6 | 1035.4 | 1080.5 | 1075.2 | 1073.2 | 1075.1 | 1027.8 | 1031.9 | 1017.3 | 1080.6 | 1026.8 | 1072 | 1031.6 | 1076.2 | 1079.7 | 1077.5 | 1088.6 | 1085.9 | 1083.1 | 1080.9 | 1087.5 | 1122.2 | 1171.3 | 1197.2 | 1143.5 | 1212.2 | 1266.4 | 1206.6 | 1207.7 | 1162.1 | 1204.7 | 1192.5 | 1151.8 | 1273.1 | 1231.8 | 1118.5 | 1260.9 | 1247.6 | 948.1 | 952.3 | 1207.6 | 1009.9 | 1148.7 | 1066.4 | 1062.3 | 1061.4 | 1054 | 1027.3 | 1043.6 | 1070 | 1048.1 | 1034.1 | 1072.9 | 1166.5 | 1059.9 | 1067.4 | 1026.7 | 1005.1 | 1005.2 | 1050.8 | 1062 | 1060.3 | 1062.8 | 1063.3 | 1233.7 | 1055.6 | 1052 | 1068.4 | 1059.5 | 954.5 | 1058.2 | 1066.9 | 1018.7 | 1021 | 1046.1 | 1179.5 | 1033.6 | 1085.2 | 1083.3 | 1074.5 | 1019.5 | 961.2 | 1070.5 | 1109.5 | 1015.4 | 1015.4 | 1084.7 | 1071 | 1064.9 | 1063 | 1064.1 | 1066.3 | 1136.3 | 1007.2 | 998.6 | 1035.9 | 1035.3 | 1035.3 | 1044.8 | 1061.4 | 1097 | 1080.9 | 1091 | 1084.1 | 1088.3 | 1078.3 | 1090.4 | 1103.2 | 1082.2 | 1043.5 | 1082.2 | 1090.9 | 963.1 | 1033.5 | 1049.4 | 1139.7 | 1066.6 | 1071.5 | 1049 | 1124.2 | 1095.2 | 1147.4 | 1019.5 | 1087.1 | 1021.5 | 1026.3 | 995.1 | 1044.2 | 1054.2 | 1049.8 | 0 | 35.32 | 0 | 0 | 4.76 | 4.8 | 0 | 0 | 83838380 | 249701 | 85120020 | 290317 | 69116340 | 144888 | 83556380 | 124453 | 790230 | 9860 | 72770 | 400 | 89830 | 208 | 93480 | 250 | 91130 | 112 | 91140 | 60 | 182000 | 0 | 180000 | 0 | 365580 | 362000 | 11.4833 | 4.76 | 4.8 |  | 35.32 | 0 | 370480.6
2025-03-31 | 2025 | 2025 |  |  | Mar-25 | 31 | 91870 | 5:28 | 16:46 | 445.5 | 428.3 | 479.9 | 480.7 | 480.3 | 451.3 | 484.6 | 470 | 485.9 | 486.5 | 487.3 | 486.8 | 486.4 | 487.1 | 492.8 | 491.4 | 458.4 | 461.6 | 481.1 | 488.3 | 500.4 | 496.3 | 502.3 | 498.7 | 499.7 | 499.8 | 499.7 | 497.1 | 500.3 | 502.2 | 497 | 498.2 | 475.3 | 446.4 | 451.3 | 457.7 | 464.3 | 466.5 | 484.5 | 460.6 | 472.7 | 518.7 | 545.2 | 513.6 | 516 | 533.8 | 574.2 | 567.3 | 616.5 | 542.2 | 516.4 | 510.5 | 508.8 | 533.2 | 523.3 | 531.2 | 549.9 | 503.6 | 441.3 | 504.8 | 484.8 | 457.5 | 500.6 | 1171.7 | 1146.5 | 1141 | 1157.6 | 1175.9 | 1155.5 | 1132.9 | 1156.1 | 1157.6 | 1070.4 | 1155.5 | 1132.7 | 1093 | 1070.4 | 1154.5 | 1159.3 | 1160.2 | 1154.6 | 1222.8 | 1158.3 | 1126.4 | 1176.7 | 1118.4 | 1114.2 | 1158.6 | 1161 | 1146.7 | 1151.1 | 1114.8 | 1132 | 1137.3 | 1154.1 | 1162.7 | 1257.7 | 1156 | 1154.9 | 1095.8 | 1098.4 | 1149.9 | 1121 | 1167.9 | 1133.2 | 1166.5 | 1174.2 | 1155.1 | 1150.2 | 1176.6 | 1179.2 | 1190.5 | 1062.4 | 1119 | 1166.6 | 1197.6 | 1177.2 | 1181.4 | 1192 | 1184.5 | 1173.7 | 1174 | 1121.2 | 1125.3 | 1180 | 1173.5 | 1176.3 | 1167.5 | 1165.8 | 1152.4 | 1154 | 1176.8 | 1158 | 1171.9 | 1147.3 | 1178.4 | 1126.8 | 1206.6 | 1292.5 | 1162.6 | 1156.8 | 1191.2 | 1225.1 | 1172.4 | 1159.8 | 1196.9 | 1169.1 | 1129.4 | 1213.4 | 1103.8 | 1011.8 | 1162.9 | 1092 | 1173.8 | 1190.7 | 1166.2 | 1182.3 | 1175.9 | 1182.5 | 1160.9 | 1162.9 | 1163.4 | 1152.8 | 1251.7 | 1218.9 | 1112.1 | 1059.1 | 1074.2 | 1049.6 | 1052.3 | 1061.9 | 1062.3 | 1065.2 | 1090.8 | 1091 | 1064.4 | 1073.7 | 1076.1 | 1085.6 | 989.5 | 916.2 | 1105.6 | 1082.9 | 1072.9 | 1074.1 | 1091.2 | 1069.3 | 1089.6 | 1067.8 | 1080 | 1063.6 | 1068.4 | 1058.6 | 1069.7 | 1028.8 | 1021 | 1026.4 | 1180.3 | 1124.2 | 1147 | 1178 | 1181.9 | 1180.3 | 1223.5 | 1197 | 1306.6 | 1180.3 | 1129.7 | 1129.7 | 1062.2 | 1169 | 1129.7 | 1235.9 | 1028.6 | 1031.8 | 1129.7 | 984.8 | 923.3 | 1218.7 | 1199.2 | 1216.8 | 1204.6 | 1184.7 | 1178.7 | 1310.6 | 1297.2 | 1081.5 | 1111.5 | 1008.7 | 1014.1 | 1006 | 1051.1 | 1023.1 | 1054.8 | 1020.4 | 1020.6 | 1015.3 | 1017.6 | 1063 | 1058 | 1057.4 | 1059.4 | 1013.2 | 1018 | 1005.4 | 1069 | 1012.4 | 1058 | 1017.8 | 1064.4 | 1064.4 | 1064.6 | 1076 | 1078.7 | 1069.6 | 1068.1 | 1075.6 | 1099.2 | 1148.9 | 1173.6 | 1120.9 | 1187.3 | 1241.2 | 1184.5 | 1183 | 1139.6 | 1182.1 | 1170.2 | 1130.1 | 1250.4 | 1210.8 | 1099.1 | 1237 | 1224.4 | 931.2 | 934.4 | 1183.9 | 991.1 | 1127 | 1045.7 | 1038.1 | 1039.1 | 1031.7 | 1046.5 | 1025 | 1046.3 | 1025.4 | 1012.7 | 1051.9 | 1143.2 | 1039.5 | 1045.7 | 1006.3 | 984.9 | 986.1 | 1031.2 | 1045.2 | 1040.4 | 1042.8 | 1043.7 | 1106.2 | 1035.3 | 1032.1 | 1044.9 | 1038.7 | 934.9 | 1040.1 | 1047.2 | 1000.7 | 1000.5 | 1021.2 | 1153.4 | 1008.4 | 1059.1 | 1058 | 1050 | 997.9 | 939.7 | 1039.2 | 1083.9 | 990.6 | 991 | 1059.2 | 1045.2 | 1040.4 | 1039 | 1036.3 | 1038.6 | 1109.5 | 984 | 975 | 1010.4 | 1009 | 1010.4 | 1019 | 1030 | 1065.9 | 1055.8 | 1059.5 | 1056.3 | 1057.7 | 1047.8 | 1059.9 | 1073.1 | 1053 | 1016 | 1059.9 | 1062.2 | 939.9 | 1005.8 | 1021.3 | 1111.1 | 1035.1 | 1041.8 | 1022.8 | 1095.1 | 1070.3 | 1113 | 993.1 | 1058.5 | 1059.9 | 998.1 | 968.4 | 1017.5 | 1026 | 1020.6 | 0 | 35.81 | 0 | 0 | 4.69 | 4.77 | 0 | 0 | 83926780 | 249909 | 85212320 | 290547 | 69206350 | 145018 | 83645390 | 124515 | 791130 | 9860 | 73670 | 410 | 88400 | 208 | 92300 | 230 | 90010 | 130 | 89010 | 62 | 180000 | 0 | 180000 | 2000 | 359720 | 360000 | 11.3 | 4.69 | 4.77 |  | 35.81 | 0 | 364659.4
2025-04-01 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:11 | 17:14 | 447.3 | 430.6 | 482.4 | 483.2 | 482.2 | 453.5 | 487.4 | 472.4 | 488.1 | 488.7 | 489.8 | 489.2 | 488.9 | 489.2 | 495.5 | 493.8 | 460.8 | 464.1 | 483.9 | 491 | 502.9 | 498.7 | 502.1 | 503.3 | 501.7 | 501.7 | 502.5 | 499.9 | 502.4 | 504.7 | 499.6 | 501.1 | 476.9 | 448.1 | 453.2 | 460.2 | 467 | 468.4 | 486.2 | 463.2 | 476.1 | 522.2 | 548.6 | 516.4 | 519 | 537 | 577.9 | 570.7 | 617.6 | 545.5 | 518.5 | 513.8 | 512.2 | 536.7 | 527.2 | 534.6 | 553.6 | 507.2 | 444.8 | 508.6 | 487.9 | 460 | 505.8 | 1176.2 | 1152.3 | 1145.1 | 1163.8 | 1182.1 | 1161.6 | 1139.3 | 1163.5 | 1186.4 | 1142 | 1139.6 | 1139.2 | 1099 | 1076.2 | 1158.3 | 1164.6 | 1166.1 | 1160.8 | 1227.8 | 1161.1 | 1131.5 | 1180.3 | 1120.1 | 1118.2 | 1162.4 | 1165.1 | 1165.1 | 1131.5 | 1083.9 | 1132.2 | 1139 | 1157.6 | 1164.8 | 1259.4 | 1157.4 | 1157.9 | 1098.1 | 1100.1 | 1152.7 | 1121.6 | 1171.2 | 1184.4 | 1168.6 | 1177.8 | 1159.3 | 1153.9 | 1181.6 | 1183.5 | 1193.5 | 1065.1 | 1121.9 | 1172.2 | 1206.1 | 1182.4 | 1188.9 | 1197.3 | 1191.6 | 1182 | 1182.5 | 1129.3 | 1132.1 | 1188.5 | 1182.6 | 1185.9 | 1177.3 | 1174.9 | 1161.5 | 1163 | 1186 | 1167.4 | 1181.5 | 1155.9 | 1186.4 | 1135.5 | 1161.5 | 1188.5 | 1165.6 | 1161.1 | 1177.3 | 1195.1 | 1176.9 | 1165.1 | 1201.9 | 1175.1 | 1134.4 | 1219.4 | 1109.3 | 1018.3 | 1169 | 1098.7 | 1181.2 | 1200 | 1175.8 | 1192.1 | 1185.8 | 1192.4 | 1168.3 | 1172.2 | 1170.3 | 1159 | 1260.9 | 1227.8 | 1119.3 | 1050.8 | 1066.4 | 1043.2 | 1046.2 | 1055.9 | 1056.4 | 1060.2 | 1086.2 | 1086.1 | 1059.1 | 1066.7 | 1069.9 | 1080.3 | 985.3 | 911.2 | 1100.6 | 1077.9 | 1067.8 | 1070.1 | 1086.5 | 1064.8 | 1085.8 | 1063.6 | 1076.8 | 1060.3 | 1065.6 | 1058 | 1067.2 | 1026.2 | 1019.4 | 1022.3 | 1158.4 | 1124.3 | 1027.5 | 1178.9 | 1183.1 | 1180.6 | 1224.6 | 1197.9 | 1306.6 | 1210.1 | 1121.5 | 1143.3 | 1059 | 1163.9 | 1210.7 | 1238.6 | 1029.8 | 1034.1 | 1130.5 | 986.1 | 923.4 | 1219.3 | 1219.3 | 1204.6 | 1218 | 1204.6 | 1185.3 | 1177.7 | 1311.8 | 1082.3 | 1111.8 | 1008.7 | 1013.9 | 1005.6 | 1051.5 | 1025 | 1055.8 | 1019.9 | 1018.9 | 1014.8 | 1017.4 | 1063.7 | 1057.4 | 1057.1 | 1059.6 | 1011 | 1016.7 | 1001.2 | 1065.3 | 1010.6 | 1056.4 | 1015.9 | 1061.5 | 1063.1 | 1062.7 | 1072.9 | 1074.3 | 1067.7 | 1065.9 | 1073.4 | 1103.4 | 1153.5 | 1178.4 | 1125.6 | 1193.4 | 1246.6 | 1192 | 1189.3 | 1146.3 | 1190.5 | 1178.9 | 1138.8 | 1258.5 | 1218.3 | 1105.2 | 1246.1 | 1233.8 | 931.7 | 935 | 941.7 | 1194.9 | 999.7 | 1045 | 1038.1 | 1037.3 | 1031.4 | 979.2 | 1022.3 | 1047.1 | 1024.4 | 1010.9 | 1049 | 1141.8 | 1037 | 1043.3 | 1003.9 | 979.7 | 981.1 | 1028.8 | 1042.9 | 1038.1 | 1040.9 | 1042.3 | 1233.7 | 1035.7 | 1029.9 | 1049.6 | 1038.8 | 931.1 | 1039.7 | 1045.8 | 1000.3 | 1001.3 | 1016.6 | 1147.4 | 1005.4 | 1058.3 | 1055.8 | 1047.1 | 994.1 | 935.9 | 1039.3 | 1080.1 | 989.2 | 987.3 | 1046.8 | 1041 | 1036 | 1036.7 | 1034.5 | 1037.3 | 1107.7 | 979.4 | 969 | 1007.1 | 1002.8 | 1009 | 1015.3 | 1015.3 | 1061.1 | 1049.8 | 1055 | 1053.1 | 1050.5 | 1047.8 | 1055.1 | 1072.1 | 1050.5 | 1014.7 | 1047.8 | 1063 | 941.2 | 1005.7 | 1022.2 | 1104.2 | 1031.5 | 1040.8 | 1020.7 | 1096.1 | 1069.8 | 1116.6 | 992.1 | 1059 | 994.3 | 998.8 | 969.4 | 1019.2 | 1026.3 | 1022.9 | 0 | 35.18 | 0 | 0 | 4.76 | 4.88 | 0 | 0 | 84015530 | 250071 | 85304860 | 290759.4 | 69296470 | 145079.2 | 83732500 | 124551.8 | 792030 | 9870 | 74560 | 420 | 88750 | 162 | 92540 | 212.4 | 90120 | 61.2 | 87110 | 36.8 | 180000 | 2000 | 178000 | 2000 | 358520 | 358000 | 12.05 | 4.76 | 4.88 |  | 35.18 | 0 | 364755.5
2025-04-02 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:39 | 16:59 | 362.6 | 349.4 | 384.7 | 384.5 | 383.5 | 365.7 | 389 | 376.4 | 388.7 | 389.3 | 389.1 | 387.9 | 388 | 389.4 | 393 | 391.6 | 366.4 | 370.5 | 387.8 | 391.7 | 401.4 | 398.5 | 401 | 400.3 | 402.1 | 401.4 | 402.9 | 400.9 | 403.6 | 404.5 | 400.7 | 401 | 382.6 | 358.5 | 360.9 | 365.5 | 370.5 | 370.6 | 385.2 | 367 | 371.2 | 412.2 | 434.2 | 408.1 | 412.1 | 426 | 458.6 | 454.2 | 490.4 | 433.4 | 414.4 | 408.4 | 407.1 | 427.1 | 419.7 | 423.6 | 440.2 | 403.5 | 354.1 | 404.6 | 386.1 | 365.3 | 400.1 | 932 | 912 | 911 | 919.9 | 935.6 | 922.3 | 904.3 | 922.3 | 940.7 | 906.2 | 907.6 | 905.1 | 878.9 | 861 | 920 | 927.6 | 926 | 801.6 | 973.2 | 922 | 895.8 | 936 | 888.2 | 887.3 | 922.7 | 925.4 | 914.3 | 917.3 | 897.3 | 910.8 | 902.4 | 924.4 | 931.8 | 1009.8 | 926.2 | 920 | 873.8 | 877.5 | 914.5 | 892.5 | 932.2 | 965.8 | 932.1 | 935.7 | 926.1 | 919.7 | 938.6 | 937.6 | 947.9 | 846.6 | 890 | 925.3 | 950.3 | 936.9 | 937.2 | 945.1 | 936.7 | 934.8 | 918.3 | 886 | 893.3 | 938.9 | 934.2 | 934.9 | 933.4 | 922.8 | 921.9 | 919.1 | 936.2 | 925.2 | 936.4 | 917.7 | 938.3 | 907.7 | 949.7 | 1020.2 | 930 | 917.3 | 940.5 | 943.4 | 930 | 919.6 | 946.5 | 927.2 | 893.5 | 961.1 | 873.9 | 801 | 923.3 | 865.8 | 933.4 | 946.8 | 926.3 | 937.8 | 938.5 | 943.9 | 922.9 | 926.3 | 925.5 | 914.1 | 997.5 | 970.8 | 881.7 | 832.9 | 850.5 | 829 | 828.8 | 841.4 | 838.4 | 844.7 | 864.6 | 867 | 844.8 | 851.7 | 856.2 | 858 | 785.7 | 724.8 | 882 | 859.8 | 855 | 855.2 | 862.7 | 851.8 | 865.3 | 849.4 | 855 | 843.6 | 853 | 841.4 | 851.5 | 817.2 | 810.5 | 819.5 | 910 | 900 | 880 | 930.9 | 930.9 | 928.5 | 969.9 | 922 | 986.4 | 952.7 | 885.2 | 863 | 837.5 | 920.4 | 890 | 974.9 | 815.1 | 816.7 | 901.4 | 781.4 | 726.8 | 957.1 | 940 | 955.7 | 946.1 | 925.7 | 923.1 | 1029.7 | 1017.1 | 863.3 | 887.9 | 806.8 | 807.9 | 806.7 | 839.7 | 818.3 | 842.5 | 812.8 | 814.6 | 811.7 | 813 | 849 | 844 | 844.9 | 844.3 | 811.5 | 811.7 | 803.5 | 850.2 | 807.5 | 836.8 | 9 | 5.4 | 850.1 | 846.7 | 859 | 856.7 | 850.2 | 847.8 | 854.1 | 878.7 | 918 | 934.2 | 893.5 | 930.4 | 997.3 | 945 | 946.7 | 911.5 | 944.5 | 936.4 | 903.7 | 994.9 | 963.8 | 875 | 981.5 | 973 | 902 | 737.3 | 738.8 | 941.5 | 787.2 | 816 | 833.3 | 833.1 | 832.2 | 815.4 | 827.5 | 841.3 | 828.7 | 819.3 | 848 | 921.3 | 836.4 | 842 | 811.1 | 799 | 795.5 | 829.7 | 841 | 836.2 | 836.6 | 840 | 1233.7 | 832 | 831.1 | 841.4 | 836.8 | 756.7 | 836.6 | 849.9 | 804.9 | 804.9 | 823.8 | 935.6 | 815.7 | 855.2 | 852.3 | 845.7 | 805.4 | 759.7 | 824.2 | 881.1 | 800.4 | 803.3 | 861.7 | 849.9 | 844.4 | 840.6 | 840.2 | 844.8 | 898.7 | 797.8 | 800.4 | 812.9 | 826.4 | 823 | 823.9 | 845.6 | 866.8 | 861.7 | 856.8 | 855.8 | 861.4 | 846.3 | 861.4 | 867 | 848.8 | 822.4 | 860 | 857.9 | 758.7 | 815.9 | 829.1 | 906.7 | 843.3 | 844.4 | 828.7 | 888.8 | 868.2 | 902.3 | 804.3 | 857.1 | 805.5 | 812.9 | 783.9 | 823.2 | 832.8 | 826.8 | 0 | 33.29 | 0 | 0 | 3.73 | 3.7 | 0 | 0 | 84086320 | 250266 | 85377950 | 291024 | 69365890 | 145286 | 83805130 | 124737 | 792740 | 9870 | 75260 | 420 | 70790 | 195 | 73090 | 264.6 | 69420 | 206.8 | 72630 | 185.2 | 142000 | 0 | 140000 | 0 | 285930 | 282000 | 11.3333 | 3.73 | 3.7 |  | 33.29 | 0 | 289746.9
2025-04-03 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:46 | 17:11 | 464.7 | 449.5 | 493 | 493.2 | 490.7 | 468.1 | 497.2 | 482.1 | 495.8 | 496.1 | 498.1 | 496.1 | 495.6 | 496.1 | 501.2 | 501.2 | 468.2 | 471.3 | 492.8 | 498.7 | 510.8 | 506.4 | 512.4 | 508.8 | 509.8 | 509.8 | 511.2 | 509.1 | 512.9 | 514 | 509 | 510.4 | 487.8 | 456.9 | 461.9 | 466.7 | 474 | 474.7 | 493.3 | 469.6 | 477.8 | 526.8 | 553.6 | 523.2 | 525.1 | 543.5 | 583.9 | 576.9 | 625.4 | 551.5 | 526.6 | 519.2 | 518 | 543.1 | 533.1 | 539 | 558.9 | 512.6 | 449.4 | 514.3 | 494.4 | 465.6 | 509 | 1187.4 | 1165.3 | 1160.8 | 1175.8 | 1194.3 | 1177.7 | 1176 | 1177.7 | 1186 | 1157.8 | 1154.6 | 1156 | 1121.7 | 1096 | 1153 | 1182.9 | 1179.7 | 1131.7 | 1239.9 | 1172.6 | 1141.6 | 1191.6 | 1129.7 | 1130.7 | 1175.4 | 1177.4 | 1167.2 | 1171.4 | 1145 | 1164.4 | 1171.5 | 1181.9 | 1184.7 | 1284.9 | 1172.2 | 1173.9 | 1119 | 1117.9 | 1168 | 1134.9 | 1188.9 | 1232.9 | 1185.5 | 1194.8 | 1183.3 | 1179.4 | 1198.4 | 1197 | 1207.9 | 1080.2 | 1133.9 | 1179.6 | 1211.8 | 1163.8 | 1196.9 | 1201.1 | 1196.1 | 1191.5 | 1189.6 | 1129.8 | 1139.7 | 1195 | 1191.1 | 1192.5 | 1190.7 | 1179 | 1178.1 | 1175.8 | 1197 | 1182.7 | 1196 | 1173.3 | 1198.4 | 1157.1 | 1211.3 | 1298 | 1174.5 | 1170.4 | 1197.1 | 1180 | 1184.9 | 1176.7 | 1207.6 | 1184.6 | 1141.5 | 1228.5 | 1116.9 | 1025.5 | 1180.6 | 1104.6 | 1191.3 | 1209.4 | 1183.8 | 1198.5 | 1200.8 | 1204.8 | 1179.2 | 1183.1 | 1181.8 | 1167.3 | 1271 | 1234.9 | 1127.2 | 1052.4 | 1070.7 | 1046.5 | 1044.6 | 1058.8 | 1057.6 | 1067.3 | 1090.5 | 1093.9 | 1065 | 1074.5 | 1078.1 | 1078.5 | 995.1 | 914.8 | 1109.3 | 1083.4 | 1077.4 | 1081.3 | 1089.5 | 1075.8 | 1092.6 | 1072.2 | 1082.7 | 1067.7 | 1082.2 | 1065.7 | 1077.2 | 1033.9 | 1026.8 | 1031.3 | 1123 | 1134.1 | 1031.6 | 1189.2 | 1187.9 | 1183.1 | 1237.9 | 1203.4 | 1289 | 1212.4 | 1124.5 | 1120 | 1066.2 | 1168.8 | 1122 | 1244.6 | 1050 | 1045.1 | 1148.4 | 995.7 | 927.6 | 1201 | 1199.7 | 1219.5 | 1207.2 | 1188.6 | 1180.7 | 1314.8 | 1297.8 | 1096 | 1120.6 | 1019.7 | 1021.8 | 1017.1 | 1063 | 1035.7 | 1065.6 | 1026 | 1026.8 | 1024.8 | 1026.6 | 1076.3 | 1069.6 | 1068.3 | 1068 | 1018.5 | 1022.8 | 1008.8 | 1069.8 | 1016.9 | 1062.9 | 1022 | 1066.4 | 1072.2 | 1070.2 | 1080.8 | 1081.8 | 1075.1 | 1072.8 | 1079.6 | 1126.8 | 1173.4 | 1195.2 | 1143.4 | 1214.1 | 1274 | 1185.3 | 1181.8 | 1165.4 | 1208.4 | 1197.5 | 1157.1 | 1270.3 | 1231.8 | 1115.7 | 1252.6 | 1242.1 | 1152 | 941.9 | 943.6 | 1207 | 1005.6 | 1065.6 | 1057 | 1057.6 | 1056.2 | 1024.3 | 1044.8 | 1067.6 | 1050.3 | 1034 | 1070.6 | 1168.2 | 1057.7 | 1066.1 | 1023.6 | 1006.7 | 1005.7 | 1050.9 | 1061.2 | 1057.4 | 1057 | 1059.9 | 1233.7 | 1053 | 1050.7 | 1067.3 | 1057.2 | 956.7 | 1058.9 | 1074 | 1019.8 | 1019.2 | 1036.9 | 1171.5 | 1026.9 | 1078.8 | 1076.6 | 1068.5 | 1014.3 | 959 | 1067.6 | 1108 | 1011.1 | 1009.5 | 1078.8 | 1063.5 | 1055.1 | 1058.1 | 1056.7 | 1063 | 1133.5 | 1001.8 | 1003.7 | 1034.1 | 1035.3 | 1022 | 1038.1 | 1067.3 | 1097.1 | 1084.3 | 1089.9 | 1080.6 | 1089.8 | 1076.3 | 1091.6 | 1096.4 | 1079.2 | 1038.2 | 1077 | 1086.7 | 961.9 | 1032.4 | 1046.5 | 1138.6 | 1069.4 | 1073.3 | 1045.2 | 1128.7 | 1096 | 1142.5 | 1016.4 | 1079.6 | 1018.4 | 1025.2 | 991.8 | 1042.5 | 1049.2 | 1046.4 | 0 | 36.62 | 0 | 0 | 4.77 | 4.81 | 0 | 0 | 84176360 | 250471 | 85470910 | 291310.5 | 69456460 | 145443.9 | 83895580 | 124845 | 793650 | 9880 | 76160 | 420 | 90040 | 205 | 92960 | 286.5 | 90570 | 157.9 | 90450 | 108 | 182000 | 2000 | 180000 | 0 | 364020 | 362000 | 11.4167 | 4.77 | 4.81 |  | 36.62 | 0 | 369831.2
2025-04-04 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:28 | 16:58 | 384.7 | 370.7 | 407.3 | 407.1 | 406.9 | 389.5 | 411.4 | 398.9 | 412.1 | 412.1 | 411.6 | 410.7 | 410.7 | 411.1 | 411.9 | 416 | 414.3 | 387.7 | 392.1 | 410.3 | 414.2 | 424.7 | 421.7 | 424.6 | 423.6 | 424.7 | 423.9 | 425.2 | 423.3 | 426.1 | 426.8 | 422.9 | 423.2 | 405 | 380 | 382.8 | 387.2 | 392.3 | 392.1 | 408.7 | 388.9 | 393.4 | 435.5 | 458.6 | 432.3 | 435.8 | 435.8 | 450.7 | 484.9 | 480.6 | 517.6 | 458.6 | 437.5 | 431.8 | 430.3 | 451.7 | 443.6 | 448.3 | 464.3 | 425.1 | 373.2 | 425.3 | 408 | 983.3 | 961.9 | 962.4 | 969.5 | 986.9 | 975.1 | 955.1 | 974.5 | 992.6 | 957.7 | 959.6 | 957.1 | 929.5 | 911.2 | 968.6 | 977.6 | 976.9 | 977.6 | 1025 | 971.4 | 944 | 986.2 | 936.7 | 934.2 | 973.6 | 976.7 | 963.8 | 967.4 | 953.1 | 966.9 | 972.9 | 842.3 | 984.2 | 1066.7 | 979.9 | 972.2 | 925.9 | 929.9 | 966.2 | 941.1 | 953 | 1020.4 | 987.6 | 988 | 979.4 | 971.6 | 990.2 | 988 | 1000.3 | 894.5 | 938.5 | 975 | 1000.1 | 988.4 | 988 | 996.2 | 986.2 | 985.6 | 985.4 | 934.4 | 942.8 | 965.5 | 986.3 | 988.3 | 985.3 | 974.1 | 973.1 | 971.7 | 991.4 | 978.6 | 991.5 | 969.6 | 990 | 959.3 | 999.5 | 1073.5 | 969.9 | 967.2 | 989 | 992.4 | 974 | 992 | 995.8 | 985 | 943.3 | 1015.9 | 922.5 | 967 | 973.9 | 914.6 | 986.2 | 998.3 | 976.9 | 985 | 992.2 | 996.1 | 973.9 | 977 | 976.7 | 964.5 | 1050.6 | 1021.1 | 930.8 | 877.9 | 893.2 | 874.3 | 874.3 | 885.2 | 883.1 | 888.4 | 907.4 | 909.3 | 889.7 | 896.4 | 898.5 | 899.6 | 829.9 | 762.7 | 921.4 | 901.7 | 897.3 | 899.5 | 904.5 | 895.2 | 906.9 | 889.4 | 900.7 | 885.4 | 899.1 | 883.9 | 892.8 | 858.1 | 851.6 | 859.9 | 960 | 934.9 | 853 | 982 | 983.9 | 983.2 | 1024.2 | 996.3 | 1085.4 | 1006.6 | 937 | 948.3 | 888.2 | 973.1 | 979 | 983 | 858.4 | 860 | 949.8 | 822.3 | 767.1 | 1008 | 1005 | 1008.2 | 998 | 979.1 | 975.7 | 1084.4 | 998 | 904.8 | 929.1 | 845.7 | 845.8 | 840.6 | 879.7 | 833.7 | 885.1 | 851.1 | 854.3 | 852.1 | 837.3 | 536.9 | 883.6 | 521.6 | 883.6 | 849.2 | 851.7 | 842 | 892.5 | 845 | 874.9 | 899 | 887.5 | 888.7 | 889 | 558.1 | 875.4 | 847.1 | 884.7 | 883.1 | 925 | 966.6 | 982 | 939.9 | 996.6 | 1048.8 | 994.1 | 995.5 | 959.6 | 995.2 | 985.9 | 951.8 | 1046.3 | 1012.8 | 918.7 | 1029.8 | 1023.9 | 1033 | 1011 | 778 | 993.6 | 949.8 | 882.2 | 872.1 | 873.6 | 871.5 | 856.5 | 866.7 | 879.7 | 866.8 | 857.8 | 883.2 | 963.7 | 876 | 879 | 846 | 837.2 | 833.8 | 869.8 | 876.7 | 874 | 874.6 | 877 | 1233.7 | 869.9 | 871.4 | 878.6 | 874.4 | 791.7 | 874.2 | 889.1 | 843.9 | 841.4 | 692.7 | 683.8 | 790.5 | 879.8 | 876.5 | 869.1 | 818.6 | 785.3 | 613.3 | 856.7 | 830.1 | 703.4 | 897.3 | 684.3 | 885.3 | 749.6 | 862.2 | 577.8 | 939.5 | 836.5 | 737.4 | 446 | 565.5 | 980 | 437.2 | 880.2 | 904.7 | 897.5 | 896 | 894.7 | 897.3 | 885.4 | 901.1 | 905.8 | 889.6 | 858.9 | 992 | 898.7 | 796.2 | 855 | 867.3 | 945.6 | 773.7 | 875.7 | 866.5 | 926.2 | 908.3 | 941.5 | 841.2 | 896.7 | 840.9 | 847.3 | 820.7 | 859.8 | 869.5 | 864.7 | 0 | 34.17 | 0 | 0 | 3.91 | 3.84 | 0 | 0 | 84251140 | 250672.9 | 85548060 | 291600.7 | 69530260 | 145631.1 | 83967300 | 125045 | 794400 | 9880 | 76880 | 430 | 74780 | 201.9 | 77150 | 290.2 | 73800 | 187.2 | 71720 | 200 | 150000 | 0 | 144000 | 2000 | 297450 | 294000 | 11.5 | 3.91 | 3.84 |  | 34.17 | 0 | 303045.9
2025-04-05 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:23 | 17:08 | 495.7 | 478 | 525.5 | 524.8 | 524 | 500.9 | 528.2 | 512.2 | 529.2 | 529.3 | 530.5 | 528.7 | 528.9 | 529 | 534.8 | 534.5 | 499.1 | 502.4 | 525 | 531.1 | 545.1 | 540.1 | 547.2 | 542.6 | 543.5 | 543.2 | 544.4 | 542.4 | 545.7 | 546.2 | 541.6 | 542.9 | 521.2 | 488.7 | 493.5 | 498 | 505.4 | 506 | 526.9 | 501.1 | 511.6 | 561.8 | 591.6 | 557.2 | 559.3 | 578.8 | 622.6 | 615 | 665.8 | 586.7 | 560.9 | 553.1 | 551.7 | 578.6 | 568.3 | 576.4 | 595.8 | 544.4 | 478.5 | 545.9 | 527.1 | 493.7 | 542.4 | 1267.1 | 1242.5 | 1237.9 | 1252 | 1273.1 | 1255.6 | 1231.5 | 1256.8 | 1278.8 | 1235.6 | 1231.4 | 1235.9 | 1199 | 1177 | 1251.3 | 1262.1 | 1258.2 | 1251.3 | 1322.2 | 1251.6 | 1217.7 | 1272 | 1206.8 | 1205.4 | 1252.1 | 1256 | 1244.7 | 1250 | 1223.5 | 1243.6 | 1251.7 | 1069.5 | 1266.5 | 1373.3 | 1257.8 | 1256.1 | 1168.6 | 1195.9 | 1246.9 | 1214.1 | 1268.9 | 1317 | 1269.7 | 1275 | 1264.6 | 1256.8 | 1277.5 | 1276 | 1289.5 | 1153.6 | 1210.5 | 1258.2 | 1292.1 | 1274.1 | 1276 | 1282 | 1273.5 | 1270.4 | 1269.2 | 1205.4 | 1215 | 1275.8 | 1270.2 | 1272.5 | 1269.2 | 1258.3 | 1255.8 | 1255.1 | 1279.4 | 1263.6 | 1278 | 1253 | 1278.3 | 1234.8 | 1292.8 | 1387.6 | 1101.4 | 1249.6 | 1278 | 1281.7 | 1264.2 | 1257 | 1286.8 | 1264.2 | 1219.3 | 1313.4 | 1193.7 | 1095.4 | 1259.8 | 1180.5 | 1275.3 | 1290.3 | 1262.8 | 1279 | 1282 | 1262.1 | 1259.7 | 1262.4 | 1262.9 | 1246.2 | 1357.2 | 1317.1 | 1203.6 | 1145.2 | 1163.3 | 1139.6 | 1138.8 | 1151.7 | 1150.3 | 1156.6 | 1178 | 1181.3 | 1155.6 | 1166.5 | 1169 | 1169.8 | 1082 | 993.7 | 1202.7 | 1172.8 | 1167.7 | 1169.7 | 1174.8 | 1165 | 1179.6 | 1159.8 | 1171.8 | 1153.1 | 1171.5 | 1149.8 | 1162.7 | 1117.3 | 1108.4 | 1115.6 | 1248.2 | 1212.9 | 1105.7 | 1274.1 | 1274.7 | 1271.6 | 1328.8 | 1291.3 | 1402.1 | 1302.1 | 1210.9 | 1224.4 | 1148.4 | 1258.3 | 1265 | 1330.5 | 1108.3 | 1117.5 | 1228.1 | 1064.7 | 993.9 | 1312.2 | 1289.3 | 1306.3 | 1295.3 | 1272.1 | 1266 | 1408.5 | 1392.6 | 1214.9 | 1226.7 | 1102.1 | 1110.9 | 1115.5 | 1154.7 | 1128.5 | 1154 | 1120.8 | 1112.4 | 1108.6 | 1111.2 | 1158.1 | 1154.7 | 1151.7 | 1155 | 1119.3 | 1132.2 | 1103.8 | 1165.7 | 1106.3 | 1149 | 1162 | 1156.7 | 1161.8 | 1158.3 | 1168.6 | 1171.7 | 1163.1 | 1159.8 | 1168.5 | 1207.3 | 1252.3 | 1275.1 | 1219.3 | 1294.4 | 1359.4 | 1288.3 | 1263.9 | 1242.5 | 1287.3 | 1276.1 | 1232 | 1356.2 | 1317.6 | 1193.9 | 1337.5 | 1325 | 1226.6 | 1003.6 | 1005.7 | 1288.8 | 1071.9 | 1150.6 | 1140.3 | 1140.5 | 1138.5 | 1108.2 | 1129.7 | 1150 | 1133 | 1114.7 | 1155.6 | 1257.1 | 1141.8 | 1149.4 | 1106.1 | 1088 | 1084.9 | 1132.9 | 1144.8 | 1141.2 | 1139.4 | 1144.4 | 1177.8 | 1135 | 1134.3 | 1147.7 | 1141.2 | 1032.3 | 1141.2 | 1158.7 | 1099.3 | 1097.8 | 1124.7 | 1273.6 | 1114.1 | 1166.8 | 1163.7 | 1155.1 | 1099.2 | 1036.1 | 1153 | 1197 | 1096.7 | 1099.7 | 1172.2 | 1159.4 | 1151 | 1148 | 1146.5 | 1149.7 | 1224.6 | 1091 | 1093.3 | 1111.1 | 1129.6 | 1128 | 1127.3 | 1141.9 | 1177.4 | 1167.7 | 1171.8 | 1164.8 | 1172.8 | 1157.3 | 1175.2 | 1183.7 | 1163.7 | 1125.5 | 1162 | 1173 | 1040.4 | 1104.6 | 1128.8 | 1225.7 | 1198 | 1153 | 1125 | 1213 | 1179.5 | 1225 | 1095 | 1167 | 1098.9 | 1106.3 | 1068.5 | 1098 | 1133.1 | 1126.9 | 0 | 37.27 | 0 | 0 | 5.03 | 5.08 | 0 | 0 | 84347060 | 250897 | 85647410 | 291910 | 69627430 | 145849 | 84064300 | 125199 | 795370 | 9880 | 77840 | 430 | 95920 | 224.1 | 99350 | 309.3 | 97170 | 217.9 | 97000 | 154 | 194000 | 0 | 192000 | 0 | 389440 | 386000 | 11.75 | 5.03 | 5.08 |  | 37.27 | 0 | 397002.9
2025-04-06 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:22 | 17:03 | 433.2 | 418.9 | 459 | 459 | 458.8 | 439.1 | 463.4 | 449.7 | 463.9 | 465.3 | 464.4 | 463.6 | 464 | 466.1 | 470.1 | 469.1 | 438.1 | 442.8 | 462.4 | 468 | 480 | 476.6 | 482.9 | 482.9 | 480.2 | 479.6 | 481.1 | 479.1 | 481.6 | 483.6 | 478.6 | 481 | 457.3 | 429 | 432.3 | 437.3 | 443.6 | 445.3 | 462.4 | 439.8 | 448.9 | 493.4 | 519.3 | 492.2 | 493.9 | 510.7 | 549.5 | 544.5 | 590.8 | 520.7 | 497.6 | 492.6 | 489.4 | 512.9 | 503.3 | 510.1 | 526.4 | 482.9 | 423.5 | 484.4 | 461.2 | 439.3 | 483 | 1116.8 | 1093.2 | 1088 | 1098.6 | 1115.7 | 1099.3 | 1084 | 1104.7 | 1122.8 | 1085.3 | 1082.2 | 1084.3 | 1050.7 | 1031.4 | 1105.3 | 1154 | 1112.1 | 1162 | 1166.5 | 1105.9 | 1090 | 1122.3 | 1065.6 | 1064 | 1104.5 | 1106.7 | 1104 | 1100.4 | 1065.3 | 1090.1 | 1091.9 | 1109.7 | 1119.2 | 1210.2 | 1106.3 | 1097.1 | 1008.6 | 1048.4 | 1093.6 | 1065 | 1111.2 | 1124.1 | 1110.4 | 1115 | 1105 | 1095.7 | 1119 | 1118.6 | 1129.9 | 1010.8 | 1065.2 | 1097.4 | 1127.5 | 1111.8 | 1112.7 | 1119.9 | 1112 | 1110.4 | 1110.6 | 1053.7 | 1061.6 | 1117.3 | 1111.9 | 1113.5 | 1111.1 | 1099.1 | 1099.1 | 1098.6 | 1121.1 | 1106.3 | 1121.4 | 1096 | 1116.3 | 1083.1 | 1112 | 1223.6 | 1034 | 1120 | 1129.8 | 1131.8 | 1115.4 | 1104.2 | 1136.2 | 1122 | 1075.5 | 1156.9 | 1053.6 | 965.3 | 1107.8 | 1039.8 | 1122.5 | 1135 | 1113.9 | 1125.9 | 1129.3 | 1133.5 | 1111.7 | 1113.6 | 1115.7 | 1100 | 1192.3 | 1158.5 | 1061.3 | 1018.8 | 1036.7 | 1015 | 1013.4 | 1026.1 | 1022.3 | 1028.7 | 1047 | 1052 | 1030.2 | 1042.8 | 1043 | 1043.1 | 964.4 | 885.8 | 1072.7 | 1047.5 | 1041.9 | 1043.4 | 1048.5 | 1039.9 | 1052.5 | 1034.4 | 1045.9 | 1029.1 | 1044.6 | 1023.9 | 1035.2 | 996.8 | 987.7 | 993.6 | 1112.6 | 1083.9 | 985.8 | 1139.2 | 1141.2 | 1140 | 1187.5 | 1155.5 | 1257.7 | 1165.5 | 1083.9 | 1094.6 | 1028.2 | 1126.5 | 1129 | 1191.1 | 995 | 999.2 | 1100.5 | 953.7 | 889.1 | 1170 | 1153.3 | 1170.7 | 1165 | 1140.3 | 1135 | 1244 | 1239 | 1063.7 | 1078.8 | 985.1 | 990 | 975.3 | 1021.4 | 987.8 | 1013.3 | 993.7 | 978.1 | 977.5 | 981.7 | 1011.7 | 1014.4 | 1001.2 | 1012.6 | 981.3 | 993.2 | 968.1 | 1025 | 979.1 | 1010.3 | 1008 | 1018.4 | 1020.4 | 1017.8 | 1023.5 | 1030.8 | 1021.3 | 1018.4 | 1026.7 | 1062.7 | 1103.2 | 1122.5 | 1074.8 | 1140.5 | 1200.1 | 1139 | 1138.8 | 1099.1 | 1140 | 1130.3 | 1092.7 | 1200.3 | 1161.8 | 1054.4 | 1184.3 | 1173.4 | 1088.5 | 892.6 | 892 | 1142 | 951.7 | 1011.3 | 1002.6 | 1005.2 | 1004.2 | 981 | 995.8 | 1012.2 | 996.7 | 985 | 1017.9 | 1108.8 | 1006.6 | 1013.5 | 973.7 | 959.2 | 959.8 | 1000.9 | 1011.7 | 1007.7 | 1007 | 1012 | 1012 | 1233.7 | 1002.8 | 1003.1 | 1017.3 | 1009.7 | 911.8 | 1008.7 | 1023.1 | 971 | 984.1 | 1121.2 | 978.8 | 1026.6 | 1024 | 1017.5 | 967.5 | 914.9 | 1016.3 | 1056.9 | 964.3 | 964.2 | 1033.2 | 1017.3 | 1012.8 | 1011.2 | 1008.3 | 1009.7 | 1079.4 | 961.8 | 967 | 976 | 998.1 | 990 | 987.5 | 1003.2 | 1034.3 | 1025.8 | 1027.6 | 1026.3 | 1030.1 | 1017 | 1033.2 | 1040.2 | 1022.9 | 991.2 | 1001 | 1031.8 | 914.3 | 981.9 | 993.1 | 1076.4 | 1004.9 | 1012.2 | 988.8 | 1066.1 | 1037.7 | 1075.6 | 960.9 | 1026.5 | 965.3 | 974.1 | 939.2 | 984.1 | 995.2 | 992.1 | 0 | 32.84 | 0 | 0 | 4.57 | 4.66 | 0.031 | 0.03 | 84431660 | 251105.4 | 85735410 | 292186.4 | 69713780 | 145886.8 | 84149820 | 125233.6 | 796230 | 9890 | 78700 | 440 | 84600 | 208.4 | 88000 | 276.4 | 86350 | 37.8 | 85520 | 34.6 | 172000 | 2000 | 172000 | 2000 | 344470 | 344000 | 11.6833 | 4.539 | 4.63 |  | 32.84 | 0 | 350812.5
2025-04-07 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:21 | 17:05 | 433.9 | 422.8 | 461.9 | 462.1 | 458.8 | 438.5 | 465.6 | 450.5 | 463 | 464.8 | 466.7 | 464.2 | 464.7 | 465.5 | 469.4 | 470 | 438.7 | 442.8 | 463.3 | 468.5 | 481.5 | 477.3 | 482.6 | 479.6 | 478.4 | 480 | 477.9 | 480.1 | 483.3 | 484.4 | 479.4 | 481.1 | 456.7 | 427.4 | 432.8 | 436.9 | 444.5 | 444.7 | 460.6 | 439.7 | 449.8 | 494.8 | 519.2 | 491.5 | 492.7 | 510.2 | 548.5 | 541.6 | 590.3 | 519.7 | 494.9 | 488.2 | 486.7 | 510.9 | 502.1 | 508 | 527.3 | 484.8 | 425 | 485.5 | 465.3 | 437.6 | 477.8 | 1117.3 | 1096.9 | 1091.9 | 1108.3 | 1124.1 | 1107 | 1090 | 1107.9 | 1124.5 | 1087.7 | 1079.4 | 1085.5 | 1050.5 | 1030.8 | 1104.9 | 1114.5 | 1111 | 1103.3 | 1167.7 | 1105.1 | 1075.1 | 1123.5 | 1064.4 | 1063.4 | 1106.7 | 1109.4 | 1098.2 | 1102.8 | 1070.7 | 1099.9 | 1101 | 1123.4 | 1126.9 | 1220.3 | 1108.3 | 1105.9 | 1055.7 | 1052.7 | 1102.2 | 1072.1 | 1119.8 | 1160.4 | 1113.1 | 1125.3 | 1111.4 | 1110.4 | 1129.1 | 1127.7 | 1136.2 | 1017.1 | 1068 | 1109.3 | 1141.3 | 1123.6 | 1127.5 | 1129.9 | 1126.7 | 1121.7 | 1117.9 | 1061.8 | 1069.7 | 1123 | 1118.6 | 1120.3 | 1118.6 | 1108.2 | 1105.2 | 1104.3 | 1126.8 | 1112.2 | 1124.6 | 1100.6 | 1122.3 | 1087.2 | 1131.8 | 1212.8 | 1053.1 | 1091.2 | 1116.3 | 1120.1 | 1106.7 | 1061.6 | 1128.4 | 1106.2 | 1060 | 1148.4 | 1045 | 961.2 | 1101.8 | 1032.8 | 1115.8 | 1134.4 | 1110.4 | 1125 | 1126 | 1130.5 | 1103.9 | 1108.2 | 1106.8 | 1092.1 | 1194 | 1158.2 | 1055.1 | 992.6 | 1011.2 | 989.6 | 988.9 | 1000.3 | 1001.3 | 1008.9 | 1025.7 | 1031 | 1007 | 1012.3 | 1016.7 | 1021.7 | 940.6 | 865.1 | 1047.9 | 1023.8 | 1018 | 1021.8 | 1028.4 | 1017.1 | 1032.4 | 1012.1 | 1023 | 1006.5 | 1024.5 | 1006.4 | 1019.1 | 977.7 | 970.4 | 973.7 | 1088 | 1059 | 963.4 | 1110.1 | 1109.5 | 1104.5 | 1157.2 | 1124.2 | 1221.7 | 1132.8 | 1050.6 | 1061.5 | 998.5 | 1089.9 | 1091 | 1164.3 | 966.9 | 978.3 | 1071 | 930.5 | 863.2 | 1137.2 | 1116 | 1136.6 | 1124 | 1110 | 1097.9 | 1225.3 | 1212.9 | 1073.9 | 1084.1 | 987.2 | 990.1 | 981.9 | 1024.7 | 990.7 | 1013.7 | 997.7 | 973.3 | 975.5 | 984.2 | 1010.2 | 1013.2 | 1002.8 | 1011.5 | 985.8 | 994.2 | 967.5 | 1014.5 | 977.9 | 1008.9 | 1010 | 1009.3 | 1015.9 | 1010.5 | 1018.9 | 1021.9 | 1014.9 | 1013.6 | 1018.7 | 1063.9 | 1100 | 1124.6 | 1074.6 | 1142.7 | 1197.2 | 1131.7 | 1133.9 | 1092.6 | 1131.7 | 1121.8 | 1085.1 | 1192.2 | 1159.6 | 1055.9 | 1182.2 | 1169.2 | 882.4 | 881.9 | 1134.7 | 943.4 | 1078.7 | 1013 | 1005.3 | 1005.3 | 1004.8 | 977.1 | 993.4 | 1014.6 | 998.1 | 982 | 1015 | 1105.1 | 1003.9 | 1013.3 | 973.1 | 956.1 | 954.2 | 996.4 | 1006.6 | 1003.4 | 1000.5 | 1007.5 | 1030.4 | 997.2 | 997.6 | 1010.7 | 1003.3 | 907.7 | 1002.1 | 1019.2 | 966.4 | 965.7 | 999.2 | 1123.3 | 986.1 | 1029.7 | 1027.5 | 1020.3 | 969.5 | 915.3 | 981.5 | 1063.6 | 966.8 | 969.4 | 1035.6 | 1025.6 | 1013.6 | 1020.1 | 1015.5 | 1021.6 | 1084.8 | 965.9 | 965.5 | 998.4 | 1003.7 | 998 | 1006.8 | 1008.6 | 1044.8 | 1029.7 | 1042.2 | 1030.9 | 1038.3 | 1029.9 | 1040.7 | 1050.9 | 1033.3 | 995.3 | 1000 | 1042.3 | 921.9 | 986.7 | 1001.5 | 1082 | 1020.6 | 1026.9 | 993.9 | 1078.6 | 1043.5 | 1092.2 | 971.4 | 1035.5 | 974 | 981.3 | 947.6 | 1001.4 | 1004.8 | 1000.2 | 0 | 35.7 | 0 | 0 | 4.54 | 4.48 | 0 | 0 | 84516590 | 251354.5 | 85822710 | 292521.3 | 69799020 | 146031 | 84235460 | 125378.2 | 797090 | 9900 | 79550 | 440 | 84930 | 249.1 | 87300 | 334.9 | 85240 | 144.2 | 85640 | 144.6 | 172000 | 2000 | 170000 | 0 | 343110 | 342000 | 11.7333 | 4.54 | 4.48 |  | 35.7 | 0 | 349321.6
2025-04-08 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:17 | 17:04 | 528.7 | 512.7 | 561.9 | 561.2 | 560.2 | 536.2 | 565.1 | 547.3 | 565.7 | 566.2 | 567.4 | 565.4 | 566 | 566.2 | 571.9 | 571.9 | 534.2 | 535.5 | 559.3 | 566.5 | 582 | 575.4 | 581.7 | 579.9 | 577.7 | 579.6 | 581 | 578.7 | 581.4 | 582.3 | 577.7 | 579.3 | 557 | 522.7 | 528.2 | 532.4 | 540.8 | 541.5 | 564 | 535.6 | 548.1 | 600.9 | 632.6 | 597.7 | 595.9 | 617.5 | 663.1 | 653.9 | 710.4 | 626.2 | 597.2 | 590 | 588.2 | 614.8 | 605.7 | 611.9 | 620.7 | 580.7 | 508.7 | 581.9 | 561 | 526.4 | 577.6 | 1353.5 | 1327.1 | 1320.3 | 1336.8 | 1358.8 | 1340.4 | 1315.6 | 1342.5 | 1365.2 | 1321.2 | 1314.2 | 1321.6 | 1280.1 | 1257.6 | 1335.3 | 1321.6 | 1342.3 | 1336.3 | 1411.2 | 1337.2 | 1300.1 | 1322 | 1290.1 | 1287 | 1330 | 1340.1 | 1328.7 | 1334.6 | 1311.9 | 1342.6 | 1339.8 | 1356.4 | 1364.7 | 1473.1 | 1346.3 | 1338.9 | 1303.1 | 1282.6 | 1331.4 | 1297 | 1353.3 | 1418.2 | 1360.3 | 1360.6 | 1349.3 | 1342.2 | 1363.2 | 1361.6 | 1375.2 | 658.2 | 1291.6 | 1339.2 | 1376.8 | 1358.5 | 1361.7 | 1366.6 | 1358.7 | 1356.3 | 1354.8 | 1286.3 | 1295.6 | 1361.8 | 1355.1 | 1357.8 | 1355.3 | 1343.5 | 1340.6 | 1341 | 1366 | 1349.5 | 1363 | 1337.8 | 1362.8 | 1316.7 | 1381.2 | 1469.5 | 1175.8 | 1320 | 1365.7 | 1369.1 | 1350.9 | 1336.2 | 1375.6 | 1365.3 | 1307.6 | 1431.6 | 1276.1 | 1176.6 | 1372.9 | 1285.5 | 1360 | 1377.3 | 1349.4 | 1366.2 | 1368.2 | 1373.6 | 1346.3 | 1348.8 | 1347.5 | 1329.8 | 1438.2 | 1399.8 | 1286.7 | 1225.2 | 1243.7 | 1220.5 | 1219.2 | 1231.6 | 1231.7 | 1239.2 | 1260.2 | 1264.7 | 1237.2 | 1246.5 | 1248.9 | 1251.5 | 1157.6 | 1062.5 | 1283.8 | 1252.4 | 1247.7 | 1251.4 | 1258.3 | 1245.7 | 1261.8 | 1239.4 | 1253.5 | 1232.3 | 1252 | 1228.5 | 1242.7 | 1193.8 | 1184.5 | 1191.4 | 1334 | 1295.3 | 1182.3 | 1361.5 | 1361.8 | 1358.1 | 1421.4 | 1380.6 | 1496.8 | 1391.6 | 1292 | 1307.1 | 1228.2 | 1342.4 | 1344 | 1420.4 | 1181.6 | 1195.3 | 1310.9 | 1136.9 | 1060.9 | 1399.6 | 1376.3 | 1393.3 | 1381.7 | 1360 | 1350.7 | 1501.7 | 1480 | 1307.4 | 1320.7 | 1201.7 | 1208.2 | 1195.9 | 1249.9 | 1206.5 | 1234.3 | 1214 | 1188.3 | 1189.5 | 1197.5 | 1240.1 | 1233.4 | 1232.1 | 1232.5 | 1199.8 | 1213.1 | 1180.5 | 1245.4 | 1193 | 1228.3 | 1225 | 1234.7 | 1240 | 1236.5 | 1250.4 | 1252.7 | 1241.9 | 1238.8 | 1248.5 | 1287.9 | 1334.1 | 1361.2 | 1300.2 | 1380 | 1445.4 | 1374.5 | 1374.7 | 1324.6 | 1372.2 | 1360.4 | 1314.4 | 1444 | 1403 | 1278.5 | 1417.7 | 1419 | 1072.8 | 1072.9 | 1375.3 | 1144.9 | 1306 | 1224.6 | 1215.1 | 1215.1 | 1213.1 | 1176.1 | 1201.7 | 1225.7 | 1206.7 | 1187.6 | 1230.4 | 1338.3 | 1216.5 | 1226.8 | 1179.1 | 1157.1 | 1156.7 | 1206.8 | 1220.3 | 1216 | 1214.3 | 1220.8 | 1303.3 | 1210.3 | 1209.1 | 1225.8 | 1216.4 | 1099.3 | 1215.2 | 1233.8 | 1171.6 | 1170.8 | 1199.3 | 1356.3 | 1187.3 | 1241.4 | 1239.4 | 1231.4 | 1171.3 | 1104.1 | 1237.8 | 1276.1 | 1166.4 | 1170.6 | 1247.5 | 1234.3 | 1225 | 1223.6 | 1221.4 | 1228.4 | 1304.8 | 1163.6 | 1167.4 | 1190.5 | 1202.1 | 1190 | 1209.5 | 1212.1 | 1251.8 | 1241.7 | 1245.6 | 1239.8 | 1243.7 | 1233.2 | 1246.1 | 1261.3 | 1239 | 1197.8 | 1193 | 1252.1 | 1110.1 | 1186 | 1202.3 | 1304.7 | 1219.3 | 1201.8 | 1199.6 | 1292.9 | 1257.6 | 1307.8 | 1168.6 | 1245.1 | 1171.7 | 1178 | 1138.6 | 1197.6 | 1207.2 | 1201 | 0 | 39.4 | 0 | 0 | 5.58 | 5.61 | 0 | 0 | 84619140 | 251563.2 | 85928860 | 292796.6 | 69902910 | 146209.3 | 84338660 | 125507.2 | 798120 | 9900 | 80580 | 450 | 102550 | 208.7 | 106150 | 275.3 | 103890 | 178.3 | 103200 | 129 | 206000 | 0 | 206000 | 2000 | 415790 | 412000 | 11.7833 | 5.58 | 5.61 |  | 39.4 | 0 | 423540.3
2025-04-09 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 6:39 | 17:07 | 273 | 265.9 | 289.9 | 289.5 | 287.9 | 275.9 | 292.5 | 281.9 | 290.2 | 290.6 | 292.2 | 289.8 | 292.1 | 290.1 | 293.3 | 294.7 | 273.8 | 276.6 | 289.2 | 292.3 | 301.2 | 298.1 | 301.5 | 301.4 | 300.3 | 300.1 | 302.3 | 301.1 | 303.2 | 302.3 | 300.4 | 300.4 | 288.4 | 267.2 | 271.4 | 274.5 | 279 | 277.5 | 289 | 276.7 | 282.9 | 314.3 | 329.3 | 314.1 | 311.6 | 323.7 | 346.6 | 341.3 | 366.6 | 325.8 | 310.3 | 304.3 | 303.9 | 319.6 | 314.9 | 317.2 | 325.4 | 303.4 | 266.3 | 304.9 | 292.2 | 274.7 | 298 | 699.1 | 688.3 | 686.4 | 696 | 704.1 | 692.2 | 679.6 | 694.3 | 703.1 | 681.9 | 675.1 | 681.1 | 659.4 | 648.5 | 694.2 | 701.2 | 699 | 691 | 732.9 | 693.1 | 673 | 703.7 | 664.4 | 665.8 | 692.4 | 696.2 | 689.4 | 691.8 | 672.3 | 687.5 | 687.2 | 701.5 | 698.4 | 759.1 | 686.4 | 697.6 | 668.7 | 655.8 | 696.2 | 686 | 699.5 | 733.9 | 692.2 | 705.4 | 709.1 | 713.1 | 714.9 | 707.7 | 710.5 | 636.2 | 668.5 | 696 | 717.2 | 705.3 | 709.9 | 709.7 | 710.1 | 704.4 | 701.9 | 666.3 | 671.7 | 706.9 | 705.2 | 704.5 | 705.7 | 697.6 | 695.5 | 687.1 | 711.6 | 702.6 | 711.9 | 695.3 | 706.8 | 689.1 | 728.3 | 777.3 | 701.1 | 699 | 716 | 717.2 | 709 | 702.1 | 722.5 | 712.6 | 682.3 | 743.5 | 666.1 | 614.8 | 715 | 664.2 | 708 | 718.4 | 705.2 | 713.2 | 712 | 713.6 | 702.4 | 703.9 | 705.5 | 697.8 | 754 | 732.5 | 671.7 | 639.4 | 654.1 | 634.9 | 634 | 625.1 | 638.9 | 644.5 | 652.4 | 661.7 | 646.7 | 650.4 | 658.3 | 660.4 | 607.6 | 559.4 | 676.3 | 656.8 | 656.4 | 657.4 | 655.2 | 651.7 | 657.3 | 650.4 | 651.8 | 643.9 | 654.5 | 641.2 | 650.1 | 620.8 | 615.2 | 621.8 | 701.5 | 655 | 624.1 | 683.8 | 720.2 | 715.8 | 750.1 | 729.2 | 794.4 | 734.6 | 682.1 | 685.8 | 648.3 | 703.9 | 689 | 753.4 | 623.8 | 632.1 | 692 | 599.5 | 558.5 | 739.9 | 724.5 | 741.5 | 729.9 | 723.7 | 713.3 | 780 | 788.1 | 683.4 | 691.1 | 631.2 | 629.3 | 622.2 | 643.9 | 630.5 | 646.9 | 639.8 | 620.7 | 623.3 | 629.3 | 646.3 | 643.2 | 642.8 | 646 | 635.8 | 639.5 | 622.6 | 647 | 627.4 | 649.2 | 650 | 646.9 | 649.1 | 646.2 | 665.3 | 658.2 | 644.8 | 649.1 | 652.6 | 674.3 | 694.3 | 713.4 | 680.7 | 725.3 | 762.5 | 715.2 | 721 | 689.8 | 713.2 | 707.5 | 660 | 752 | 735.8 | 670 | 749.6 | 741.4 | 559.1 | 556.7 | 717.4 | 596.5 | 681.4 | 635.9 | 633.9 | 625.9 | 623.9 | 610.1 | 620.3 | 637.4 | 624 | 610.6 | 636.7 | 714.9 | 635.3 | 645.4 | 613.9 | 600.5 | 591.8 | 619.5 | 629.6 | 627.4 | 623.1 | 629.3 | 563.2 | 625.4 | 622.5 | 632.5 | 629.2 | 577.8 | 633.9 | 657.9 | 622.3 | 605.7 | 633.5 | 700.3 | 623.6 | 650.2 | 645.6 | 640.4 | 612.2 | 573.1 | 647.2 | 677.7 | 602.4 | 609.9 | 656.5 | 651.1 | 641.4 | 646.7 | 645.2 | 649.8 | 691.4 | 609.1 | 611.9 | 632.2 | 637 | 640 | 640.2 | 639.4 | 659.9 | 651.2 | 660.2 | 641.6 | 656.7 | 660 | 655.9 | 665.2 | 650.4 | 626.7 | 630 | 660.4 | 580.7 | 619 | 632.3 | 680.1 | 644.3 | 615.2 | 621.2 | 677.9 | 651.3 | 691.1 | 609.1 | 646.9 | 608.9 | 616.3 | 594 | 632.9 | 633.1 | 626 | 0 | 32.76 | 0 | 0 | 2.89 | 2.87 | 0 | 0 | 84672360 | 251797.8 | 85984260 | 293039.3 | 69957260 | 146285.3 | 84392050 | 125637 | 798660 | 9910 | 81110 | 450 | 53220 | 234.6 | 55400 | 242.7 | 54350 | 76 | 53390 | 129.8 | 108000 | 2000 | 106000 | 0 | 216360 | 214000 | 10.4667 | 2.89 | 2.87 |  | 32.76 | 0 | 221218.7
2025-04-10 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:16 | 16:56 | 445.2 | 433.8 | 472.9 | 473 | 472.1 | 451.6 | 477.3 | 461.9 | 477.3 | 478.2 | 478.1 | 476.4 | 477.9 | 478.2 | 483 | 482.3 | 450.6 | 453.2 | 473.6 | 479.5 | 492.3 | 487.4 | 492.9 | 490.6 | 490.9 | 490.7 | 492.2 | 490.3 | 492.8 | 494 | 489.6 | 491.5 | 470.5 | 441.2 | 445.4 | 449.6 | 456.7 | 456.6 | 474.9 | 452.3 | 462 | 508 | 534.8 | 504 | 505.5 | 523.5 | 562.4 | 555.5 | 601.2 | 531.3 | 507.6 | 500.7 | 498.3 | 521.7 | 513.1 | 518.6 | 538 | 492.9 | 432.2 | 492.4 | 475.8 | 446.1 | 490.2 | 1142.2 | 1119.6 | 1114.7 | 1129.9 | 1146.4 | 1131 | 1109.7 | 1131.6 | 1149.8 | 1112.7 | 1107 | 1111 | 1078 | 1057.3 | 1126.1 | 1137.4 | 1134.2 | 1127.2 | 1191.4 | 1128.5 | 1097.5 | 1146.4 | 1087.8 | 1086.6 | 1130.1 | 1131.3 | 1121.1 | 1126.3 | 1104.8 | 1125.9 | 1127.2 | 1141.3 | 1149.1 | 1241.9 | 1142.8 | 1147.9 | 1087.9 | 1078.7 | 1152.3 | 1123 | 1146 | 1199.9 | 1140.1 | 1164.5 | 1159.7 | 1156.6 | 1165.1 | 1150.3 | 1173.7 | 1046.7 | 1091.3 | 1134 | 1164 | 1147.4 | 1151.4 | 1154.1 | 1147.5 | 1146.2 | 1145.1 | 1087 | 1094.4 | 1151.2 | 1144.7 | 1147.4 | 1145.4 | 1134.2 | 1131.8 | 1132.4 | 1158 | 1140.8 | 1156.7 | 1129.9 | 1150.4 | 1115.9 | 1173.1 | 1253 | 1135.9 | 1128.9 | 1158.1 | 1161.5 | 1145.8 | 1161.5 | 1158.1 | 1155.6 | 1106.9 | 1207.4 | 1078.6 | 993.5 | 1158.1 | 1082.6 | 1151.2 | 1165.1 | 1140.6 | 1155.9 | 1156.1 | 1161.4 | 1137.7 | 1139.5 | 1139.3 | 1124.3 | 1219.6 | 1185.7 | 1086.2 | 1028.8 | 1045 | 1025.4 | 1024.2 | 1033.4 | 1033.1 | 1039.4 | 1057.7 | 1061.8 | 1039.2 | 1049.3 | 1050.6 | 1052 | 974.6 | 892.4 | 1075.8 | 1051 | 1048.5 | 1052.2 | 1057.3 | 1045.5 | 1058.7 | 1014.7 | 1052.5 | 1032.9 | 1049.1 | 1029.2 | 1042 | 999.3 | 991.7 | 998.2 | 1128.2 | 1099.1 | 1128.2 | 1099.1 | 1159.2 | 1157.8 | 1207.4 | 1150.1 | 1275.6 | 1183.6 | 1100.4 | 1111.8 | 1045.4 | 1143 | 1171.3 | 1203.4 | 1003.1 | 1012.4 | 1115.1 | 965.6 | 946 | 1189.2 | 1171.3 | 1187.2 | 1177 | 1159.4 | 1150.5 | 1275.6 | 1258 | 1088.7 | 1099.3 | 997.9 | 1005.3 | 995.8 | 1039.6 | 1007.3 | 1030.1 | 1009.7 | 991 | 992.1 | 996.3 | 1039.4 | 1032.5 | 1031 | 1032.1 | 999.6 | 1010.7 | 983.3 | 1038.3 | 990.9 | 1025.1 | 1026 | 1029.2 | 1035.9 | 1032.5 | 1044.7 | 1042.7 | 1039.6 | 1036.8 | 1044.1 | 1082.3 | 1120.3 | 1144.7 | 1093.4 | 1161.7 | 1223.5 | 1157.1 | 1162.6 | 1115.8 | 1156.2 | 1145.7 | 1108.9 | 1217.1 | 1180.7 | 1076.5 | 1196.8 | 1197.9 | 906.3 | 903.5 | 1160.2 | 966 | 1103.8 | 1017.8 | 1009 | 1009.6 | 1007.1 | 969.3 | 998.7 | 1017.5 | 1002.1 | 989.4 | 1027 | 1147.6 | 1028.5 | 1033.9 | 978.4 | 962 | 960.7 | 1004.9 | 1015.5 | 1013.3 | 1010.3 | 1014.3 | 1111.3 | 1006.8 | 1004.4 | 1021.7 | 1011 | 930.9 | 1024.3 | 1052.4 | 1000.1 | 974.8 | 992.5 | 1124.2 | 981.8 | 1028.6 | 1026.5 | 1014.4 | 967.2 | 912.3 | 1022.9 | 1054.5 | 966.9 | 968.4 | 1031.7 | 1019.4 | 1010.4 | 1011.7 | 1012.8 | 1016.4 | 1080.2 | 958.2 | 963.6 | 974.1 | 994.9 | 990 | 992.3 | 1012.5 | 1043 | 1032.2 | 1037.9 | 1031.1 | 1036.3 | 1025.9 | 1036 | 1047.9 | 1028.6 | 992.8 | 995 | 1040.1 | 922.6 | 985.3 | 999.2 | 1085 | 1015.5 | 984.3 | 997 | 1070.1 | 1046.2 | 1085.8 | 971 | 1036.9 | 972.8 | 978.9 | 947.1 | 996.6 | 1002.3 | 999.2 | 0 | 38.33 | 0 | 0 | 4.72 | 4.67 | 0 | 0 | 84759280 | 252021 | 86074230 | 293346.1 | 70045020 | 146475.1 | 84478450 | 125767.3 | 799530 | 9910 | 81980 | 460 | 86920 | 223.2 | 89970 | 306.8 | 87760 | 189.8 | 86400 | 130.3 | 174000 | 0 | 174000 | 2000 | 351050 | 348000 | 11.6667 | 4.72 | 4.67 |  | 38.33 | 0 | 356948.5
2025-04-11 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:08 | 17:01 | 244.4 | 236.3 | 259 | 259.2 | 258.8 | 245.5 | 263 | 253.3 | 262.7 | 263.2 | 262 | 261.1 | 262.8 | 263.5 | 266.1 | 264.4 | 247.1 | 250.8 | 263.1 | 265.2 | 272.9 | 270.5 | 273 | 271.2 | 273.4 | 272.5 | 274.2 | 272.9 | 274.6 | 275.2 | 272.1 | 272.6 | 260.1 | 243 | 243.3 | 247.4 | 250.8 | 250 | 260.7 | 248.5 | 252.7 | 279.8 | 294.5 | 277 | 279.5 | 289.3 | 311.1 | 309 | 330.7 | 294.9 | 283 | 279.2 | 276.2 | 289.8 | 284.9 | 287.5 | 297.9 | 273.3 | 239.9 | 274.2 | 243.3 | 248.7 | 271.5 | 633 | 620 | 616.5 | 620.5 | 629.7 | 623.7 | 611.1 | 624.9 | 632.2 | 611.7 | 611.8 | 610.9 | 594.3 | 581.9 | 619.8 | 625.1 | 620 | 621 | 652.8 | 628.8 | 602.2 | 633.7 | 608.4 | 600.9 | 621.4 | 625.8 | 568 | 618.9 | 607 | 616.4 | 621 | 625.3 | 630.7 | 680.6 | 629.6 | 627 | 594 | 593.8 | 627.8 | 614.6 | 627.7 | 656.6 | 628.8 | 635.8 | 632.9 | 629.8 | 636.7 | 628.4 | 640.1 | 574.1 | 594.8 | 622.8 | 639.4 | 631.3 | 633 | 640.7 | 633.6 | 632.3 | 632.8 | 598.4 | 605.6 | 640.1 | 637 | 621.6 | 635.5 | 624.6 | 624 | 624.6 | 641.1 | 631.4 | 643 | 624.5 | 636.3 | 621.6 | 646.2 | 690.5 | 627.1 | 625.6 | 640.1 | 641.7 | 637.5 | 635 | 638 | 634 | 613 | 666.3 | 596.2 | 548.8 | 638.2 | 598.5 | 633.7 | 641.7 | 629.2 | 637.3 | 627.2 | 630.4 | 627.3 | 629.1 | 629.7 | 625.9 | 673.1 | 656.7 | 601.3 | 549.8 | 561 | 554.1 | 556.7 | 561.2 | 557.7 | 561.1 | 573 | 576.2 | 565.8 | 569.1 | 569.5 | 572.4 | 533 | 488.2 | 583.3 | 570.9 | 570.5 | 573.5 | 573.9 | 570.4 | 574.1 | 563.6 | 573.4 | 560.9 | 571.4 | 558 | 563.7 | 541.7 | 536.9 | 543.7 | 623.6 | 610.4 | 558.5 | 639.9 | 641.7 | 644 | 641.4 | 649.3 | 711.3 | 654.8 | 613 | 618.8 | 585.1 | 637.6 | 640 | 669.6 | 562.1 | 561.9 | 622.6 | 538.2 | 501.5 | 654.7 | 646.4 | 658.4 | 648.7 | 634.8 | 634.3 | 702.7 | 693.4 | 584 | 593.1 | 539.9 | 543.2 | 538.3 | 560.7 | 546.4 | 558.4 | 546.7 | 537 | 537.2 | 538.7 | 556.4 | 555.5 | 553.8 | 557.6 | 548.4 | 553.3 | 538.5 | 563.9 | 537.8 | 552.2 | 545 | 559.1 | 560.4 | 559.8 | 568.6 | 568.9 | 560.9 | 561.2 | 564.7 | 595.4 | 617.1 | 628.9 | 601 | 635.4 | 671 | 635.5 | 637.8 | 613.3 | 635.7 | 629.5 | 610.2 | 668.7 | 646.4 | 593.9 | 658.6 | 656.8 | 501.9 | 501.2 | 636.4 | 535 | 609 | 548.4 | 542.7 | 540.9 | 540.3 | 526.4 | 537 | 546.3 | 537 | 531.6 | 550.3 | 610.5 | 549.6 | 552.3 | 526.6 | 519.6 | 514.7 | 539.3 | 546.9 | 544.1 | 544.3 | 546.1 | 568.7 | 542.5 | 539 | 549.8 | 544.3 | 498.7 | 550 | 562.5 | 562.5 | 535.4 | 528.7 | 597.8 | 520.7 | 548.6 | 545.3 | 540.9 | 514.6 | 485.5 | 547 | 564.6 | 513.4 | 515.9 | 552.6 | 544.9 | 539.5 | 537 | 540.4 | 546.3 | 576.6 | 508.8 | 519 | 533.2 | 534.3 | 535 | 536.3 | 547.1 | 560.8 | 566 | 557 | 553.7 | 559.2 | 549.9 | 558.5 | 561.5 | 551.3 | 534.2 | 540 | 558.1 | 494.5 | 528.8 | 537.9 | 585.1 | 545.9 | 544.9 | 537.4 | 573.9 | 562.7 | 583.1 | 521.3 | 555.5 | 519.5 | 529.1 | 509.1 | 532.2 | 537.7 | 536 | 0 | 29.76 | 0 | 0 | 2.55 | 2.395 | 0 | 0 | 84807270 | 252223.6 | 86123860 | 293629.9 | 70093340 | 146706.8 | 84525060 | 125960.8 | 800020 | 9910 | 82450 | 460 | 47990 | 202.6 | 49630 | 283.8 | 48320 | 231.7 | 46610 | 193.5 | 98000 | 0 | 94000 | 0 | 192550 | 192000 | 11.8833 | 2.55 | 2.395 |  | 29.76 | 0 | 194808.1
2025-04-12 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:34 | 17:13 | 440.4 | 428.7 | 466.6 | 467 | 463.9 | 444 | 472.3 | 456.2 | 468.8 | 470.3 | 472 | 469.5 | 469.1 | 470.9 | 474.3 | 474.3 | 443.4 | 447.7 | 480 | 473.4 | 486.6 | 482.1 | 486.5 | 483.8 | 484.4 | 485.1 | 486.2 | 484.9 | 487.6 | 488.6 | 483.8 | 485.9 | 461.5 | 432.4 | 436.6 | 441.1 | 448.1 | 448.7 | 464.8 | 443.5 | 453.5 | 496.6 | 521.6 | 493.9 | 496 | 513.4 | 550 | 544.3 | 587.4 | 523.3 | 496.6 | 491 | 489.7 | 514.1 | 505.9 | 512.2 | 528.6 | 486.9 | 426.9 | 487.1 | 421.5 | 440.9 | 481.8 | 1114.5 | 1096.7 | 1097.9 | 1108.6 | 1118.8 | 1108.9 | 1085.8 | 1112.3 | 1118.6 | 1089 | 1078.3 | 1085.8 | 1056.6 | 1039.3 | 1065.9 | 1108.2 | 1109 | 1104 | 1110 | 1121 | 1069.5 | 1121.4 | 1080.3 | 1066.4 | 1102.9 | 1112.6 | 1090 | 1103.9 | 1085.8 | 1105.2 | 1111.7 | 1123.7 | 1121.6 | 1211.8 | 1115.4 | 1115.7 | 1067.1 | 1061 | 1121.5 | 1097.9 | 1119.9 | 1173.1 | 1117.8 | 1135.8 | 1125.6 | 1126.9 | 1137.8 | 1125.1 | 1108.4 | 982.5 | 1057.9 | 1103.6 | 1128.1 | 1113.7 | 1121.4 | 1058.4 | 1121.6 | 1121.3 | 1030.9 | 1059.3 | 1070.3 | 1129.2 | 1123.5 | 1099.2 | 1121.7 | 1105 | 1102.8 | 1102.5 | 1129.1 | 1112.4 | 1131.8 | 1100.8 | 1085.5 | 1067.1 | 1126 | 1203.5 | 1097.4 | 1094.3 | 1112.4 | 1118.3 | 1120 | 1121 | 1109 | 1115 | 1072.9 | 1167.1 | 1046 | 965.6 | 1119 | 1047.6 | 1110.2 | 1125.7 | 1089.3 | 1106.2 | 1093.3 | 1091.4 | 1045.7 | 1108.6 | 1047.7 | 1095.2 | 1179 | 1148 | 1056.6 | 972.4 | 989.9 | 979.4 | 982 | 987.5 | 988.6 | 996.3 | 1011.2 | 1016.3 | 997 | 999.3 | 1003 | 1006.7 | 939.8 | 860.1 | 1027.4 | 1007.1 | 1005.7 | 1013.2 | 1013.8 | 1007.3 | 1016.4 | 995.8 | 1013.1 | 991.1 | 1013.3 | 992.5 | 1003.1 | 963.4 | 957.3 | 961.5 | 1085.1 | 1058.4 | 966.4 | 1105.5 | 1107.9 | 1109.7 | 1153.9 | 1077.1 | 1224.1 | 1074.4 | 1050.4 | 1050.5 | 1005.4 | 1091.5 | 1090 | 1157 | 980 | 977 | 1073.5 | 929.4 | 866.4 | 1111.4 | 1098 | 1110 | 1117.2 | 1097.8 | 1094.9 | 1210.7 | 1193 | 1046.8 | 1057.5 | 968.9 | 969.7 | 968.4 | 1006.8 | 979.9 | 999.1 | 975 | 956.9 | 959.9 | 965.7 | 999.2 | 995.8 | 992.7 | 995.4 | 956.1 | 611 | 945.5 | 994.9 | 957.9 | 985 | 990 | 991.2 | 996.8 | 993.6 | 1003 | 1006.6 | 999.7 | 995.6 | 1001.7 | 1054.6 | 1086.3 | 1109.4 | 1059.3 | 1088.8 | 1176.6 | 1113.7 | 1121.2 | 1082.3 | 1124.7 | 1110.4 | 1079.7 | 1169.6 | 1132.7 | 1043.6 | 1153 | 1154 | 885.2 | 880.1 | 1121.2 | 941 | 1074 | 989.2 | 981.8 | 980.9 | 982.9 | 958.7 | 971.5 | 988.6 | 971.2 | 961.4 | 993.2 | 1087.8 | 990.2 | 995.4 | 948.6 | 936.9 | 934.9 | 974.3 | 985.4 | 981 | 983 | 984.9 | 1042.5 | 976.6 | 974 | 989.8 | 979.8 | 902.7 | 988.2 | 1007.2 | 962.8 | 945.3 | 966.7 | 1076.2 | 956.6 | 1001.4 | 996.7 | 990 | 940.2 | 891.2 | 992.1 | 1023.5 | 940.9 | 942.8 | 1001.7 | 991 | 977.4 | 983.8 | 983.7 | 993.7 | 1045.2 | 931.2 | 947.1 | 966.6 | 971.8 | 970 | 973.4 | 989.8 | 1014.6 | 1004.5 | 1008.8 | 999 | 1009.9 | 999.3 | 1011.1 | 1015.4 | 999.4 | 966.2 | 970 | 1010.4 | 901.9 | 961.9 | 974.5 | 1052.4 | 995.7 | 996.2 | 971.3 | 1043.1 | 1014.2 | 1057.1 | 947.5 | 1007.6 | 947.4 | 955.8 | 925 | 970.2 | 975.2 | 974.4 | 0 | 36.04 | 0 | 0 | 4.53 | 4.47 | 0 | 0 | 84892410 | 252424.3 | 86210580 | 293952.3 | 70177402 | 146947.6 | 84609290 | 126134.2 | 800870 | 9920 | 83290 | 460 | 85140 | 200.7 | 86720 | 322.4 | 84062 | 240.8 | 84230 | 173.4 | 170000 | 2000 | 168000 | 0 | 340152 | 338000 | 11.65 | 4.53 | 4.47 |  | 36.04 | 0 | 345096
2025-04-13 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:15 | 17:14 | 530.4 | 512.8 | 561.4 | 559.8 | 560.2 | 540 | 567 | 547.5 | 566 | 566.6 | 567.4 | 565.5 | 566.1 | 567.3 | 572.3 | 570.7 | 533 | 536.2 | 560.5 | 567.4 | 582.8 | 576 | 582.5 | 579.8 | 579.9 | 580.1 | 580.7 | 579.1 | 582.9 | 583.5 | 577.8 | 580.4 | 558.5 | 524.9 | 528.5 | 532.9 | 551 | 541.4 | 563.5 | 535.3 | 547.1 | 597.8 | 630 | 595.3 | 596.3 | 617.5 | 661.6 | 655.5 | 704.3 | 644 | 580 | 590 | 587.5 | 614 | 604.8 | 609.1 | 631.2 | 578.5 | 752.5 | 580.4 | 504.8 | 525.5 | 579.2 | 1337 | 1311.7 | 1311.5 | 1322.9 | 1329.9 | 1329 | 1297.6 | 1334.3 | 1335.5 | 1303 | 1290.4 | 1303.7 | 1272.5 | 1253.4 | 1325.7 | 1331.2 | 1334.4 | 1310.7 | 1380.9 | 1347 | 1284.4 | 1335.3 | 1300.7 | 1274.3 | 1312.1 | 1330.9 | 1320.6 | 1322 | 1298.2 | 1324.3 | 1332.8 | 1346.3 | 1339.4 | 1432.2 | 1333.9 | 1337.6 | 1282.5 | 1277.6 | 1339.1 | 1317.2 | 1332.7 | 1411.1 | 1411 | 1361.1 | 1340.4 | 1343.5 | 1358.8 | 1358.6 | 1362.6 | 1344.9 | 1253 | 1326.7 | 1337.9 | 1331.2 | 1344.5 | 1360.5 | 1352 | 1342.3 | 1340.9 | 1272.4 | 1290.4 | 1353.2 | 1344.6 | 1319.4 | 1341.9 | 1331 | 1324.4 | 1323 | 1347.1 | 1322.6 | 1354.5 | 1320.7 | 1341.2 | 1308.9 | 1341.7 | 1418.8 | 1320.4 | 1320 | 1330 | 1340.4 | 1339.6 | 1328.2 | 1354.1 | 1304.3 | 1297.6 | 1414.1 | 1265.4 | 1165.4 | 1338.6 | 1263.4 | 1316.5 | 1342.2 | 1331.8 | 1347.9 | 1345.6 | 1335.9 | 1263.9 | 1328.6 | 1298.7 | 1321.4 | 1390.3 | 1358.1 | 1277.1 | 1200.7 | 1220.3 | 1145.5 | 1206.7 | 1205.6 | 1212.3 | 1218.4 | 1236.4 | 1239.1 | 1219.4 | 1226.6 | 1228 | 1229.1 | 1148.9 | 1048.7 | 1251.5 | 1227.6 | 1226.5 | 1232.5 | 1233.1 | 1226 | 1234.2 | 1212.4 | 1233.3 | 1206.6 | 1230.1 | 1204 | 1215.7 | 1168.6 | 1160 | 1155 | 1311.1 | 1284.6 | 1256.3 | 1334.2 | 1345.1 | 1357.6 | 1390.9 | 1349.8 | 1489.6 | 1361.4 | 1268.6 | 1292.2 | 1221.4 | 1325.1 | 1330 | 1390.4 | 1171.2 | 1183.4 | 1281.3 | 1127.5 | 1296.2 | 1362.9 | 1289.3 | 1381.5 | 1358 | 1330.5 | 1340.1 | 1459.5 | 1422.7 | 1263 | 1274.8 | 1169.9 | 1175.3 | 1156 | 1219.6 | 1139.9 | 1209.3 | 1179.5 | 1162.2 | 1164 | 1157.9 | 1050.7 | 1206.6 | 1143.7 | 1206.2 | 1170.4 | 1184.7 | 1149.8 | 1219.5 | 1161.5 | 1197.7 | 1200 | 1206.5 | 1211.9 | 1210.2 | 1069.4 | 1202.3 | 1136.9 | 1211 | 1176.6 | 1272.3 | 1312.6 | 1340 | 1276.1 | 1339.2 | 1398.3 | 1337.9 | 1333.1 | 1307.4 | 1359.6 | 1336.3 | 1298.1 | 1395.6 | 1349.4 | 1258.7 | 1359.9 | 1394.2 | 1064.1 | 1060.2 | 1338.1 | 1132.9 | 1291 | 1190.2 | 1188.9 | 1190.4 | 1190.3 | 1153.7 | 1178.3 | 1197.4 | 1171.4 | 1164.9 | 1201.8 | 1314.3 | 1205.6 | 1210.6 | 1144.7 | 1136.5 | 1135.4 | 1185.7 | 1199.2 | 1190.4 | 1189 | 1195.9 | 1281 | 1186.9 | 1185.2 | 1194.2 | 1189.9 | 1092.2 | 1202.2 | 1215.7 | 1168.4 | 1140.8 | 1156.9 | 1288.6 | 1152.7 | 1211.3 | 1206.4 | 1199.3 | 1137.7 | 1075 | 1192.7 | 1232.7 | 1136.4 | 1137 | 1211.5 | 1191.2 | 1187.5 | 1183.6 | 1177.8 | 1180.4 | 1260.2 | 1127.5 | 1140 | 1105.7 | 1154.8 | 1040 | 1037.3 | 1171.4 | 1217.8 | 1209.8 | 1215.1 | 1209.5 | 1217.6 | 1195.9 | 1218.2 | 1223.5 | 1205 | 1166 | 1170 | 1217.9 | 1084.9 | 1157.9 | 1172.6 | 1267.4 | 1092.7 | 1154.8 | 1174.6 | 1223.3 | 1227.9 | 1263.3 | 1134.8 | 1216.1 | 1135.6 | 1143.7 | 1112.2 | 1158 | 1175.1 | 1172.3 | 0 | 37.77 | 0 | 0 | 5.5 | 5.4 | 0 | 0 | 84994300 | 252728 | 86315300 | 294337 | 70278820 | 147235 | 84710450 | 126285 | 801900 | 9920 | 84290 | 470 | 101890 | 303.7 | 104720 | 384.7 | 101418 | 287.4 | 101160 | 150.8 | 206000 | 0 | 200000 | 2000 | 409188 | 406000 | 11.9833 | 5.5 | 5.4 |  | 37.77 | 0 | 416596.5995
2025-04-14 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 4:57 | 17:19 | 496.4 | 482 | 525.9 | 525.5 | 524.1 | 504.9 | 531.6 | 514.1 | 530 | 530.9 | 532.5 | 530 | 529.8 | 531.7 | 535.7 | 535 | 500.4 | 504.4 | 527.2 | 533.4 | 548.2 | 542.8 | 547.7 | 546.3 | 545.3 | 546.1 | 547 | 545.4 | 548.7 | 549.4 | 544.2 | 546.4 | 522.1 | 490.8 | 493.8 | 498.4 | 505.8 | 506.8 | 526.2 | 500.5 | 512.4 | 561.4 | 591.3 | 557.8 | 559.5 | 579.2 | 622.3 | 615.2 | 665.6 | 588.7 | 561.1 | 554.2 | 552.2 | 578.6 | 569.7 | 574.4 | 595.9 | 545.5 | 479 | 547.7 | 474.9 | 496.2 | 543.1 | 1232 | 1233 | 1237.7 | 1252.7 | 1269.6 | 1253.6 | 1231.4 | 1257.6 | 1273.8 | 1236.2 | 1228 | 1235.3 | 1196.9 | 1176.6 | 1253.1 | 1264.1 | 1258.6 | 1250 | 1319 | 1270.6 | 1217.8 | 1282 | 1230.3 | 1214.7 | 1253.7 | 1255.2 | 1244.7 | 1249.6 | 1232.3 | 1256.9 | 1256.5 | 1268.7 | 1277.1 | 1380.4 | 1266.1 | 1270.3 | 1212 | 1201.8 | 1273.4 | 1243.5 | 1273.1 | 1334 | 1274.8 | 1287.9 | 1282.2 | 1278.2 | 1289.2 | 1274.9 | 1296.5 | 1159.8 | 1204.1 | 1258.5 | 1285.3 | 1272.9 | 1277.9 | 1284.6 | 1247.7 | 1270.4 | 1271.1 | 1204.9 | 1218.5 | 1277 | 1268.9 | 1244.8 | 1267.3 | 1259.1 | 1255.5 | 1254.9 | 1282.3 | 1264.3 | 1283.2 | 1250.4 | 1250.9 | 1232.7 | 1283.9 | 1372 | 1248.9 | 1241.7 | 1270.6 | 1275.4 | 1261.4 | 1253.6 | 1283.5 | 1250 | 1220.4 | 1333.4 | 1190 | 1095.6 | 1273.1 | 1193.5 | 1266.8 | 1279.1 | 1259.1 | 1274.6 | 1277.5 | 1279.2 | 1203 | 1260.2 | 1258.9 | 1242.4 | 1339.5 | 1303.1 | 1200.6 | 1128.1 | 1147.7 | 1132.4 | 1132 | 1136.7 | 1137.7 | 1143.5 | 1162.9 | 1166.4 | 1146 | 1153.1 | 1154.8 | 1157 | 1078 | 985.5 | 1183.3 | 1155.5 | 1154.9 | 1161.3 | 1162.2 | 1154.1 | 1163.8 | 1143 | 1163 | 1163.9 | 1160.9 | 1133.4 | 1146.5 | 1100.1 | 1091.8 | 1098.3 | 1244.3 | 1209.4 | 1105 | 1269.1 | 1273.1 | 1274.2 | 1325.7 | 1286.6 | 1402 | 1296.4 | 1207.4 | 1220.7 | 1151.8 | 1255.2 | 1230 | 1324.5 | 1103.2 | 1115.3 | 1171.6 | 1061 | 993.3 | 1299 | 1281.9 | 1299.1 | 1287.3 | 1261.7 | 1256.7 | 1395.2 | 1376.9 | 1202.2 | 1215.5 | 1105.3 | 1110.1 | 1105.3 | 1152.4 | 1117.2 | 1142.2 | 1114.7 | 1095.8 | 1097.3 | 1100.8 | 1137 | 1137.9 | 1129.5 | 1137.4 | 1106.6 | 1117.7 | 1086 | 1150.8 | 1096.7 | 1131.6 | 1137 | 1136.6 | 1142.2 | 1141.3 | 1143 | 1151.5 | 1144 | 1142.1 | 1151.2 | 1204.4 | 1246.6 | 1272.1 | 1214.7 | 1286.4 | 1352.1 | 1278.5 | 1285.9 | 1238.8 | 1282.6 | 1270.1 | 1229.2 | 1344.8 | 1303.6 | 1194.7 | 1321.4 | 1321.6 | 1004.4 | 998.1 | 1280.3 | 1069.8 | 1224.2 | 1131.6 | 1076.3 | 1123.6 | 1122.7 | 1094.5 | 1113 | 1131.8 | 1113.2 | 1100.9 | 1143.5 | 1263 | 1139.4 | 1145.6 | 1088.1 | 1072.1 | 1070 | 1117.7 | 1131 | 1125.4 | 1126.3 | 1128.7 | 1233.7 | 1090.7 | 1117.5 | 1134.3 | 1123.4 | 1031.1 | 1135.4 | 1157.5 | 1104.1 | 1082.3 | 1099.5 | 1245.8 | 1090.3 | 1145.8 | 1141.7 | 1134.4 | 1075.7 | 1015.3 | 1122.4 | 1176.7 | 1073.6 | 1076.1 | 1147.3 | 1133.9 | 1123.5 | 1122.4 | 1120.9 | 1127.9 | 1200 | 1065.2 | 1065.2 | 1081 | 1082.9 | 1109.4 | 1102.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.67 | 0 | 0 | 5.19 | 5.09 | 0 | 0 | 85090780 | 252860 | 86414520 | 294526.2 | 70375640 | 147337 | 84772060 | 126338.6 | 802870 | 9930 | 85080 | 470 | 96480 | 132 | 99220 | 189.2 | 96820 | 102 | 61610 | 53.6 | 194000 | 2000 | 158000 | 0 | 354130 | 352000 | 12.3667 | 5.19 | 5.09 |  | 38.67 | 0 | 359625
2025-04-15 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:13 | 16:37 | 473.2 | 461.6 | 502 | 502 | 498.9 | 479.9 | 507.7 | 490.9 | 504.3 | 505.4 | 507.7 | 505.1 | 504.7 | 506.2 | 510.3 | 511 | 476.9 | 480.5 | 502.5 | 508.2 | 523 | 517.4 | 523.2 | 520.9 | 519.4 | 520.7 | 521.6 | 520.5 | 523.5 | 524.1 | 518.6 | 521.6 | 497.8 | 466 | 470.5 | 474.8 | 482.4 | 484 | 501.5 | 478.6 | 490 | 535.6 | 562.9 | 535.4 | 534.1 | 553 | 591.9 | 585 | 630.5 | 562 | 536.2 | 529.4 | 510.3 | 552 | 544.2 | 548.9 | 568.3 | 522 | 457.6 | 524.2 | 453.9 | 474 | 518.6 | 1201.1 | 1179.9 | 1178.6 | 1192.1 | 1200.6 | 1191.6 | 1167.9 | 1197.4 | 1202.1 | 1171 | 1160 | 1168.7 | 1137.4 | 1120.9 | 1141.6 | 1169.7 | 1198.4 | 1182.3 | 1243.4 | 1204.2 | 1153.9 | 1207.4 | 1163.5 | 1148.1 | 1184.2 | 1194.4 | 1180 | 1188.7 | 1164.9 | 1186.7 | 1192.9 | 1205.2 | 1200.2 | 1294.6 | 1197.7 | 1197.6 | 1146.1 | 1138.5 | 1201.6 | 1176.1 | 1199.8 | 1230.8 | 1199.4 | 1218.3 | 1205.6 | 1207.7 | 1220.8 | 1208 | 1169.5 | 1077.6 | 1137.9 | 1113.5 | 1215 | 1181.1 | 1212.2 | 1107.4 | 1164.7 | 1207.6 | 1206 | 1145.7 | 1159 | 1218.2 | 1212.8 | 1188.8 | 1211.5 | 1169.9 | 1192.7 | 1191.5 | 1216.2 | 1197.5 | 1218.9 | 1187.7 | 1208.2 | 1148.8 | 1217.4 | 1295 | 1187 | 1185.8 | 1194 | 1207.7 | 1197 | 1190 | 1219.8 | 1206.4 | 1165 | 1265.6 | 1135.6 | 1048.3 | 1206.1 | 1133.1 | 1195.9 | 1213.1 | 1168.6 | 1212.6 | 1186.8 | 1156.9 | 1125.1 | 1196.2 | 768 | 1188.1 | 1266.3 | 1232.2 | 1146.5 | 1075.8 | 1093 | 1078.6 | 1078.9 | 1080 | 1083.3 | 1089.1 | 1103.9 | 1107.3 | 1089.6 | 1096.2 | 1098.8 | 1099.9 | 1031 | 944.2 | 1120 | 1098.8 | 1096.9 | 1103.2 | 1103.1 | 1095.8 | 1104.6 | 1086 | 1102.8 | 1080.3 | 1101.5 | 1076.4 | 1088.4 | 1047.3 | 1039.9 | 1045.2 | 1181.8 | 1156.6 | 1057.6 | 1205.6 | 1211.1 | 1218.6 | 1257.2 | 1199 | 1340.6 | 1121.1 | 1147 | 1144.7 | 1104.1 | 1197.6 | 1195 | 1190 | 1052.7 | 1066.9 | 1079.1 | 1015.6 | 949.2 | 1181.7 | 1192.7 | 1198 | 1223.3 | 1200 | 1207.4 | 1318 | 1296.6 | 1135.2 | 1145.7 | 1051 | 1053.9 | 1049.5 | 1090.7 | 1058.4 | 1082.3 | 1060.8 | 1041.3 | 1042.8 | 1041.2 | 1062.6 | 1080.4 | 1056.4 | 1079.5 | 1051.1 | 1062.3 | 1030.4 | 1088.2 | 1044.5 | 1076.1 | 1077 | 1083.6 | 1082.7 | 1080.5 | 1073.3 | 1094.6 | 1077.8 | 1082.1 | 1087.9 | 1118.2 | 1152.1 | 1205.4 | 1149.7 | 1157.2 | 1271.9 | 1170.5 | 1186.2 | 1175.1 | 1221.3 | 1203.9 | 1168.4 | 1268.3 | 1228.9 | 1135.2 | 1247.3 | 1258.5 | 959.1 | 952.3 | 1212.8 | 1020.7 | 1162.6 | 1067.9 | 1014.4 | 1062.2 | 1061.3 | 1038.6 | 1051.2 | 1070.1 | 1054.6 | 1043.1 | 1079 | 1183.2 | 1076.3 | 1082.9 | 1031.6 | 1015.2 | 1012.6 | 1056.4 | 1068.5 | 1064.7 | 1064.9 | 1068 | 1233.7 | 1011.8 | 1055.3 | 1075.8 | 1063.7 | 978 | 1074.1 | 1092.6 | 1046.2 | 1028.6 | 1036.2 | 1162.7 | 1033.9 | 1080.9 | 1078.8 | 1072.1 | 1021.3 | 966.7 | 1040.5 | 1110.6 | 1017.6 | 1019.7 | 1081.6 | 1070.6 | 1061.1 | 1064.3 | 1062.3 | 1061.5 | 1130.6 | 1010.7 | 1024.3 | 1015.3 | 1054.1 | 1076 | 1042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.89 | 0 | 0 | 5.03 | 4.92 | 0 | 0 | 85182060 | 253083.9 | 86507940 | 294859.1 | 70467000 | 147646.4 | 84830270 | 126474.8 | 803790 | 9930 | 85820 | 470 | 91280 | 223.9 | 93420 | 332.9 | 91360 | 309.4 | 58210 | 136.2 | 184000 | 0 | 148000 | 0 | 334270 | 332000 | 11.4 | 5.03 | 4.92 |  | 39.89 | 0 | 339780.6
2025-04-16 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:38 | 17:09 | 394.8 | 387.1 | 418.3 | 418.5 | 418.7 | 403 | 423.9 | 408.2 | 421.7 | 424 | 424 | 421.1 | 424.4 | 425.4 | 429.1 | 429.7 | 398.3 | 403.4 | 422.3 | 426.6 | 440.1 | 434.4 | 440.4 | 438 | 438.3 | 438 | 439.9 | 439.9 | 442.8 | 442.5 | 437.6 | 441 | 420.9 | 394.6 | 396.5 | 400.4 | 406.6 | 407.8 | 423.2 | 403.9 | 412.6 | 452.5 | 477.8 | 454.1 | 452.3 | 469.4 | 502.1 | 496.3 | 538.2 | 478.1 | 453.2 | 447.1 | 409.1 | 470.3 | 462.1 | 465 | 481.3 | 441.4 | 388.1 | 388.1 | 443.5 | 383.4 | 401.6 | 1022 | 1000.6 | 1002.4 | 1008.7 | 1022 | 1003.6 | 988.1 | 1004.7 | 1017.9 | 987.6 | 983.5 | 985.5 | 951.5 | 934.2 | 960 | 1035.6 | 1026.3 | 1009.2 | 1076.7 | 1035.1 | 988.3 | 1047.6 | 1000.6 | 986.3 | 1020.8 | 1021.5 | 1006.3 | 1004.6 | 1015.4 | 1030.3 | 1036 | 1040.6 | 1049.2 | 1138.8 | 1043.2 | 1041.5 | 985.4 | 980.9 | 1038.9 | 1013.9 | 1039.4 | 1095.1 | 1033 | 1043.9 | 1028.7 | 1037.5 | 1040 | 1030.9 | 1050.4 | 945.5 | 984.2 | 1015.8 | 1043.6 | 1038.7 | 1041.4 | 1052.2 | 995.5 | 1026.3 | 1026.9 | 981.5 | 991 | 1035.2 | 1024.6 | 1016.4 | 1031.1 | 1035.9 | 1029.2 | 1021.8 | 1041.3 | 1025.8 | 1036.9 | 1007.3 | 1020.5 | 974.7 | 1066.4 | 1126.3 | 1028.3 | 996.2 | 1054.2 | 1052.5 | 1041 | 1024.9 | 1062.1 | 1045.8 | 1009.5 | 1091.9 | 985.2 | 901.2 | 1042.8 | 969.3 | 1032 | 1038.9 | 1030.4 | 1031.4 | 1044.8 | 1040.9 | 988.9 | 1035.2 | 1021 | 1027.7 | 1080.1 | 1050.6 | 985.5 | 946.5 | 964.2 | 951.9 | 950.4 | 949.9 | 953.5 | 952 | 966.4 | 968 | 957.2 | 971.4 | 969.1 | 972.6 | 905.6 | 832.6 | 994.2 | 974.5 | 968.9 | 972.6 | 965.3 | 969.4 | 971.1 | 955.9 | 974.5 | 950.5 | 965.1 | 936 | 950.4 | 916.4 | 909.8 | 908.6 | 1039.9 | 1017.9 | 930.4 | 1066.2 | 1065 | 1063.9 | 1116 | 1082.3 | 1177.8 | 1063.1 | 1015.5 | 1029.6 | 972.2 | 1061.7 | 1060 | 1107.4 | 923.6 | 934.8 | 980.5 | 892.4 | 832.4 | 1092.8 | 1062.6 | 1084.6 | 1080.7 | 1066.3 | 1065.6 | 1160.4 | 1143.8 | 985 | 998 | 905.4 | 905.4 | 909 | 894.4 | 938.5 | 905.3 | 937.8 | 919.6 | 908.2 | 900.7 | 891.8 | 923.1 | 941.8 | 919.8 | 944.5 | 915.4 | 926.6 | 901.4 | 956.2 | 913.4 | 945.3 | 950 | 947.7 | 945.4 | 947.3 | 936.6 | 960.7 | 935 | 949.9 | 991.4 | 1024.7 | 1042.1 | 993 | 1053.9 | 1105.4 | 1044.2 | 1050.1 | 1005.9 | 1042.7 | 1035.7 | 1000.7 | 1103 | 1063.8 | 968.9 | 1073.9 | 1070.1 | 816.2 | 808.1 | 1047.4 | 868 | 997 | 904 | 854.8 | 897.4 | 900.1 | 878.5 | 889.6 | 906.1 | 886.2 | 879.6 | 904.7 | 999.9 | 904 | 883.6 | 870 | 855.6 | 852.3 | 892.3 | 894.9 | 893.6 | 892.7 | 894.7 | 1233.7 | 842.5 | 887.8 | 900.8 | 887.5 | 816.3 | 898 | 924.4 | 873.7 | 856.5 | 866 | 980.4 | 880.6 | 920.2 | 914.8 | 909.6 | 854.8 | 815.8 | 885.9 | 955.9 | 865.4 | 865.5 | 932.8 | 916.8 | 914.4 | 917.3 | 917.3 | 884.8 | 976 | 868.3 | 880.8 | 850.1 | 904 | 918 | 873.3 | 852.9 | 883.2 | 854.7 | 878.3 | 875.3 | 873 | 871.2 | 876.2 | 888.4 | 874.6 | 848.2 | 850 | 886.4 | 778.5 | 840.9 | 850.7 | 920.1 | 847.3 | 851.8 | 841.9 | 902.3 | 889.3 | 926.4 | 826.8 | 882.8 | 819.9 | 818.9 | 802.2 | 839.9 | 849.2 | 847.5 | 0 | 36.09 | 0 | 0 | 4.14 | 4.15 | 0 | 0 | 85260010 | 253283.9 | 86588460 | 295144.5 | 70546900 | 147910.3 | 84905690 | 126608.7 | 804570 | 9940 | 86600 | 480 | 77950 | 200 | 80520 | 285.4 | 79900 | 263.9 | 75420 | 133.9 | 156000 | 2000 | 156000 | 2000 | 313790 | 312000 | 11.5167 | 4.14 | 4.15 |  | 36.09 | 0 | 320232.1
2025-04-17 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:25 | 17:14 | 467.9 | 456.2 | 497.5 | 498.4 | 495.6 | 473.5 | 507.3 | 489.2 | 502.3 | 504.8 | 509.6 | 505.4 | 504 | 506.6 | 509.7 | 510.2 | 477.9 | 481.4 | 504.9 | 510.4 | 526.3 | 519.1 | 524.9 | 519.9 | 522.7 | 523.9 | 525.1 | 522.4 | 527.6 | 528 | 521.8 | 523.3 | 492.4 | 462.7 | 468 | 471.8 | 480 | 481.7 | 496.4 | 474.9 | 483.1 | 527.4 | 552.7 | 520.4 | 526.3 | 542.2 | 583.2 | 578.8 | 616.5 | 560.5 | 531.9 | 526.1 | 481.2 | 550.6 | 543 | 545.5 | 566.7 | 520.7 | 457.6 | 522.1 | 454.8 | 472.8 | 514.7 | 1190.1 | 1173.1 | 1179 | 1183.5 | 1172.8 | 1183.2 | 1180 | 1185 | 1172.9 | 1150.7 | 1130.5 | 1144.1 | 1124.1 | 1104.6 | 1174 | 1181.1 | 1203.5 | 1165.3 | 1224.2 | 1200 | 1144.1 | 1180.8 | 1153.3 | 1130.4 | 1162 | 1167.5 | 1189.5 | 1195 | 1130.7 | 1152.7 | 1166.8 | 1182.5 | 1168.2 | 1252.6 | 1177.6 | 1170.9 | 1118 | 1115.3 | 1180.9 | 1162.6 | 1172.1 | 1236 | 1167.8 | 1197.3 | 1171.4 | 1176.6 | 1198.7 | 1195 | 1146.7 | 1098 | 1112.8 | 1174.7 | 1180.4 | 1173.2 | 1191.6 | 1216.8 | 1168.4 | 1193.3 | 1184.6 | 1125.7 | 1145.6 | 1214.8 | 1208 | 1183.4 | 1208.7 | 1181.7 | 1173.3 | 1167 | 1187.6 | 1161.9 | 1194 | 1165.1 | 1178.1 | 1150.6 | 1169.7 | 1233.1 | 1155.2 | 1171.4 | 1158.8 | 1171.9 | 1194.7 | 1169.7 | 1189.3 | 1175.1 | 1157.9 | 1249.3 | 1130.8 | 1048.9 | 1177.1 | 1120.1 | 1155.8 | 1181.2 | 1183 | 1194.2 | 1155.4 | 1177.7 | 1145.2 | 1177.2 | 1113 | 1151.4 | 1219.6 | 1194.7 | 1142.9 | 1056.3 | 1064.2 | 1046.6 | 1046 | 1035.5 | 1047.6 | 1051.7 | 1069.6 | 1077.2 | 1056.7 | 1069.2 | 1069.6 | 1065 | 1010.1 | 932.4 | 1090.6 | 1066.9 | 1073.7 | 1077.8 | 1071.3 | 1069 | 1074.7 | 1066.4 | 1078.3 | 1055.7 | 1076.8 | 1060.5 | 1067.5 | 1035 | 1029.5 | 1031.3 | 1144 | 1130 | 1033 | 1168.2 | 1144 | 1199.3 | 1210.9 | 1178.6 | 1319.5 | 1192.2 | 1116.3 | 1128 | 1099.5 | 1177.8 | 1177 | 1225.6 | 1041.8 | 1059.5 | 1110.1 | 1007.1 | 940 | 1193.9 | 1151.3 | 1203.3 | 1189.3 | 1170.5 | 1188.3 | 1278 | 1249.1 | 1100.8 | 1113.6 | 1034.8 | 1032.8 | 1040 | 1064 | 1052.3 | 1066.7 | 1044 | 1025.8 | 1027.7 | 1032.6 | 1062.5 | 1057.1 | 1057.9 | 1062.7 | 1043 | 1049.8 | 1018.8 | 1062.2 | 1033.9 | 1056.3 | 1070 | 1075.2 | 1064 | 1061.5 | 1075.6 | 1089.8 | 1064.8 | 1063.7 | 1068.8 | 1125.3 | 1150.2 | 1181.1 | 1119.2 | 1152.8 | 1228.7 | 1181.8 | 1193.4 | 1162.5 | 1219.3 | 1186.8 | 1157 | 1226.3 | 1158 | 1129.3 | 1230 | 1237 | 958 | 949.9 | 1175.2 | 1018.7 | 1146.6 | 1040.7 | 1003.6 | 1035.8 | 1044.5 | 1016.2 | 1031.3 | 1047.5 | 1027.4 | 1023 | 1050.5 | 1140.8 | 1048.6 | 1027.5 | 1005.8 | 1004.1 | 998.7 | 1034.6 | 1044.2 | 1043.7 | 1043.9 | 1046 | 788.7 | 1014.8 | 1041.3 | 1060.7 | 1048 | 968.5 | 1054.4 | 1066.1 | 1035.4 | 1020.8 | 1009.8 | 1110 | 1008.7 | 1050.1 | 1047.7 | 1046.5 | 996.6 | 944.8 | 1028.4 | 1076.4 | 996.9 | 996.5 | 1056.9 | 1040 | 1035.9 | 1038.5 | 1032.9 | 1025.4 | 1097.4 | 989 | 1003.6 | 992.6 | 1025.4 | 1011 | 1002.8 | 1063.6 | 1079.7 | 1074.5 | 1074.6 | 1063.5 | 1065.7 | 1051.6 | 1060.8 | 1063.8 | 1047.7 | 1019.3 | 1020 | 1055 | 947.4 | 1005.5 | 1020.8 | 1116.7 | 1063 | 1058.5 | 1031.9 | 1101.1 | 1070 | 1108.8 | 1000 | 1059.3 | 1003.4 | 1011.8 | 973 | 1021.3 | 1022.9 | 1021.2 | 0 | 37.46 | 0 | 0 | 4.99 | 4.86 | 0 | 0 | 85350240 | 253508.6 | 86680690 | 295435.1 | 70636970 | 148122.6 | 84994630 | 126828.9 | 805480 | 9940 | 87490 | 480 | 90230 | 224.7 | 92230 | 290.6 | 90070 | 212.3 | 88940 | 220.2 | 182000 | 0 | 178000 | 0 | 361470 | 360000 | 11.8167 | 4.99 | 4.86 |  | 37.46 | 0 | 366898.7
2025-04-18 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:08 | 17:14 | 559.2 | 543.7 | 593.8 | 592.4 | 591.1 | 570.6 | 602.6 | 579 | 597.7 | 598.6 | 604.3 | 599.8 | 598.2 | 600 | 605 | 605.2 | 566 | 567.7 | 595.6 | 602.2 | 621.3 | 612.9 | 621.1 | 614.8 | 616.5 | 619.2 | 618.7 | 613.4 | 620.4 | 621.8 | 616.4 | 619.1 | 592.2 | 555.7 | 558.8 | 563.4 | 572.2 | 573.3 | 596.4 | 567.2 | 582 | 632.7 | 666.4 | 630.9 | 630.2 | 651.9 | 691.2 | 683.7 | 726.1 | 660.7 | 631.4 | 624.6 | 569.4 | 648.8 | 640.1 | 637.2 | 666.4 | 611.7 | 538.8 | 614 | 540.4 | 559.4 | 610.4 | 1393.6 | 1370.5 | 1390.2 | 1389.8 | 1379.2 | 1396 | 1357.3 | 1411 | 1385 | 1360.8 | 1336.6 | 1359.9 | 1335.6 | 1318.9 | 1380 | 1395.7 | 1426.9 | 1367.8 | 1437.5 | 1423.8 | 1343.5 | 1384.6 | 1359.4 | 1325 | 1357.3 | 1407.2 | 1389 | 1385.9 | 1314.2 | 1347 | 1369.5 | 1385.2 | 1368.1 | 1460.3 | 1401.7 | 1375.5 | 1309.8 | 1316.5 | 1384.8 | 1374.9 | 1365.3 | 1417.9 | 1369.6 | 1401.5 | 1382.5 | 1376.8 | 1407.8 | 1366.1 | 1404.7 | 1297.9 | 1302.6 | 1367 | 1394.4 | 1385.4 | 1409.7 | 1381.4 | 1431.8 | 1412.2 | 1379 | 1333.3 | 1361.5 | 1436.1 | 1427.7 | 1401.4 | 1426.4 | 1392.5 | 1384.3 | 1377.3 | 1399.4 | 1371.4 | 1407.3 | 1374.6 | 1387.7 | 1320.9 | 1333 | 1486.4 | 1390.6 | 1409.1 | 1389.5 | 1402.3 | 1434.6 | 1394.3 | 1421 | 1392.9 | 1380 | 1469.4 | 1330.3 | 1228 | 1390.2 | 1313.5 | 1360.4 | 1384.4 | 1386.3 | 1401.4 | 1392.3 | 1384.5 | 1385 | 1382.7 | 1384.9 | 1393.9 | 1428.3 | 1402.4 | 1340.3 | 1262.3 | 1275.6 | 1263.5 | 1265.3 | 1255.9 | 1274.5 | 1283.2 | 1302.8 | 1303 | 1276.3 | 1273.7 | 1278 | 1280.4 | 1209.3 | 1111.5 | 1293.4 | 1276.4 | 1275.7 | 1286.9 | 1293.7 | 1279.5 | 1290.7 | 1263.4 | 1285 | 1257.6 | 1280.9 | 1257.2 | 1275.2 | 1230.3 | 1219.6 | 1234.1 | 1360.8 | 1343.6 | 1240.5 | 1377.7 | 1387.6 | 1415.2 | 1435.5 | 1396.8 | 1555.6 | 1407.8 | 1316.8 | 1345.4 | 1296.1 | 1389.9 | 1380 | 1438.6 | 1224.5 | 1244 | 1333.1 | 1188.6 | 1160 | 1401.1 | 1398.3 | 1410 | 1398.7 | 1369.1 | 1393.2 | 1491 | 1460 | 1313.1 | 1320.8 | 1230.5 | 1218.5 | 1223.4 | 1268.7 | 1234.3 | 1254.6 | 1235.8 | 1220.3 | 1222 | 1212.5 | 1232.4 | 1255.2 | 1229.4 | 1250.9 | 1226.2 | 1235.7 | 1195.7 | 1266.8 | 1215.4 | 1246.4 | 1250 | 1268.6 | 1257.5 | 1258.7 | 1244.6 | 1281.5 | 1248.2 | 1260.9 | 1262.2 | 1322 | 1374.1 | 1405.8 | 1333.9 | 1390.5 | 1456 | 1399.6 | 1416.9 | 1377.9 | 1440.7 | 1399 | 1364.2 | 1454.8 | 1360 | 1340.6 | 1411.1 | 1466.3 | 1131.7 | 1124.3 | 1386.8 | 1203.2 | 1355.9 | 1265 | 1256.8 | 1257.3 | 1252 | 1224.8 | 1242.7 | 1267.7 | 1243.6 | 1239.4 | 1268.2 | 1361.2 | 1269.3 | 1270.2 | 1216.9 | 1208 | 1209.2 | 1254.4 | 1267.9 | 1261.4 | 1260.4 | 1265.5 | 1233.7 | 1255.7 | 1255.1 | 1265 | 1255.3 | 1167.8 | 1266.3 | 1266.4 | 1237.5 | 1221.1 | 1218.1 | 1335.4 | 1234.9 | 1285.9 | 1278 | 1269.8 | 1207.8 | 1147 | 1218.5 | 1295.5 | 1222.8 | 1220.9 | 1287.9 | 1260.6 | 1268.1 | 1264.8 | 1255.4 | 1253.7 | 1328.8 | 1214.6 | 1213 | 1220.2 | 1238.2 | 1220 | 1225 | 1274.6 | 1296.9 | 1284.6 | 1291.4 | 1280.1 | 1297.4 | 1277.6 | 1296.2 | 1298.3 | 1284.6 | 1247.7 | 1250 | 1291.3 | 1165 | 1230.8 | 1235.8 | 1334 | 1271.6 | 1269.6 | 1250.3 | 1318.5 | 1293.4 | 1329.1 | 1217.6 | 1280.8 | 1217.3 | 1223 | 1186.8 | 1238.7 | 1249.5 | 1244.1 | 0 | 40.77 | 0 | 0 | 5.97 | 5.77 | 0 | 0 | 85456460 | 253705.8 | 86790140 | 295709.1 | 70743140 | 148306.3 | 85102200 | 126973 | 806550 | 9940 | 88550 | 490 | 106220 | 197.2 | 109450 | 274 | 106170 | 183.7 | 107570 | 144.1 | 214000 | 0 | 212000 | 2000 | 429410 | 426000 | 12.1 | 5.97 | 5.77 |  | 40.77 | 0 | 436966.5
2025-04-19 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:16 | 17:15 | 521.7 | 510.2 | 554.8 | 555.5 | 551.2 | 531.8 | 562.1 | 540.2 | 555.7 | 558.2 | 562.4 | 558.2 | 558.8 | 559 | 563.7 | 565.1 | 527.5 | 530 | 553.7 | 560.9 | 578 | 570.7 | 577.9 | 573.9 | 572.5 | 574.5 | 575.8 | 574.5 | 577.5 | 577.7 | 571.2 | 575.3 | 549.8 | 515.5 | 520.6 | 524.2 | 533.6 | 534.8 | 553.3 | 527.8 | 544.1 | 592.9 | 623.5 | 590.2 | 588.2 | 610.2 | 653.8 | 644.7 | 696.5 | 618.6 | 587.7 | 580.1 | 529 | 605.7 | 597.5 | 596 | 626.9 | 575.3 | 504.6 | 577.3 | 502.3 | 521.5 | 569.2 | 1325 | 1310.3 | 1304.9 | 1326 | 1318.4 | 1287.1 | 1290.5 | 1327.9 | 1317.1 | 1293.3 | 1266.4 | 1288.5 | 1257.6 | 1240.2 | 1233 | 1220 | 1321.7 | 1293.8 | 1360.1 | 1331.7 | 1274.1 | 1317.7 | 1290.8 | 1263.3 | 1297.6 | 1322.4 | 1315.4 | 1317.9 | 1280.9 | 1309.2 | 1318 | 1337.2 | 1322.5 | 1411.9 | 1321.5 | 1324.8 | 1273.8 | 1260.2 | 1331.1 | 1307.4 | 1320.2 | 1404.2 | 1314.6 | 1353.5 | 1319.2 | 1332.2 | 1351.1 | 1342.7 | 1350 | 1223.4 | 1244.9 | 1312.6 | 1320.2 | 1264.3 | 1331.3 | 1341.1 | 1338.4 | 1333.3 | 1328.9 | 1260.9 | 1276.6 | 1337.4 | 1331.5 | 1304.4 | 1330 | 1318.2 | 1310.6 | 1307.2 | 1330.6 | 1303.7 | 1336.1 | 1303.3 | 1321.6 | 1205.1 | 1334.4 | 1405.5 | 1311.7 | 1311.6 | 1315.8 | 1322 | 1329.5 | 1320.6 | 1346.2 | 1323.5 | 1285 | 1397 | 1253.3 | 1156.9 | 1323.7 | 1247.5 | 1295.8 | 1319.9 | 1318 | 1330.5 | 1326.9 | 1288.4 | 1296.2 | 1312.9 | 1318.1 | 1307.3 | 1366.5 | 1335.2 | 1264.1 | 1201.1 | 1219.3 | 1202 | 1200.7 | 1191.2 | 1208.3 | 1215.7 | 1227.9 | 1228.4 | 1207.1 | 1219.2 | 1222.4 | 1226.3 | 1145.2 | 1039 | 1242 | 1221.6 | 1216 | 1226.1 | 1226.9 | 1215.6 | 1226.9 | 1205.4 | 1224.1 | 1197.1 | 1223.4 | 1194.9 | 1210 | 1159.6 | 1151.5 | 1156.4 | 1299.4 | 1276.3 | 1164.5 | 1324.5 | 1329.3 | 1342.8 | 1377.7 | 1341.9 | 1482.8 | 1348.7 | 1257.6 | 1290.9 | 1221.3 | 1322.9 | 1403 | 1377.1 | 1377.1 | 1156.6 | 1174.8 | 1289.7 | 1114.5 | 1043.2 | 1349.2 | 1346.8 | 1370.7 | 1340.4 | 1319 | 1330.7 | 1434.4 | 1261.6 | 1262.4 | 1162.3 | 1163.7 | 1160.1 | 1206.5 | 1172.2 | 1197.7 | 1174 | 1148.2 | 1150.5 | 1156 | 1197.8 | 1197.5 | 1188.1 | 1198.1 | 1162.2 | 1173.5 | 1137 | 1200.9 | 1151.4 | 1194.2 | 1190 | 1190 | 1198.2 | 1193.5 | 1200.3 | 1209.5 | 1199.4 | 1201.5 | 1205.7 | 1263.7 | 1293 | 1328.1 | 1262.7 | 1320.2 | 1378.3 | 1320.1 | 1332.9 | 1295.1 | 1345.9 | 1320.7 | 1286.6 | 1376.7 | 1333.8 | 1257.2 | 1343.9 | 1389.4 | 1052.3 | 1043.5 | 1319.4 | 1121 | 1279.3 | 1150.6 | 1174 | 1170.4 | 1169.7 | 1126.8 | 1153.4 | 1181.2 | 1159.9 | 1144.4 | 1187.3 | 1291.2 | 1186.1 | 1197.9 | 1135.6 | 1112.7 | 1113.8 | 1165.9 | 1180 | 1154.3 | 1175.9 | 1179.7 | 1087.1 | 1171.3 | 1168.1 | 1190.2 | 1175 | 1076.1 | 1186.2 | 1192.3 | 1155.6 | 1135.4 | 1132.2 | 1259.1 | 1141.2 | 1194.4 | 1191.3 | 1184.9 | 1126 | 1059.9 | 1166.8 | 1232.9 | 1121.5 | 1124 | 1196.3 | 1179 | 1173 | 1182.1 | 1174.1 | 1159.4 | 1249.9 | 1118.1 | 1132.4 | 1121.8 | 1161.2 | 1150 | 1130.2 | 1203.9 | 1236.6 | 1218 | 1227.6 | 1209.4 | 1221.5 | 1208.7 | 1220.6 | 1226.8 | 1208.7 | 1159.6 | 1160 | 1215.4 | 1078.4 | 1150.4 | 1165.1 | 1274 | 1185 | 1212.5 | 1173.8 | 1266 | 1226.2 | 1279.2 | 1111.4 | 1216.9 | 1142.2 | 1146.5 | 1107.9 | 1172.1 | 1171.2 | 1165.7 | 0 | 41.8 | 0 | 0 | 5.73 | 5.43 | 0 | 0 | 85557100 | 253908.3 | 86893750 | 296015.9 | 70844080 | 148530.4 | 85202660 | 127184 | 807560 | 9950 | 89550 | 490 | 100640 | 202.5 | 103610 | 306.8 | 100940 | 224.1 | 100460 | 211 | 202000 | 2000 | 200000 | 0 | 405650 | 402000 | 11.9833 | 5.73 | 5.43 |  | 41.8 | 0 | 412752.1
2025-04-20 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:50 | 17:15 | 359.3 | 351.9 | 381.4 | 381.5 | 377 | 365.3 | 386.7 | 369.5 | 379.1 | 381 | 385.8 | 382.8 | 381.3 | 381.5 | 383.8 | 387 | 361.1 | 364.7 | 381.5 | 385.7 | 397.2 | 392.9 | 396.4 | 392.4 | 394.6 | 395.2 | 395.6 | 395.2 | 399.3 | 399.3 | 392.9 | 394.2 | 376.1 | 351.3 | 354.9 | 358.6 | 365.2 | 365.3 | 377 | 361.9 | 373.6 | 406.8 | 425 | 406.2 | 405 | 419.5 | 448 | 442.4 | 472.4 | 424.4 | 404.4 | 396 | 363.5 | 416.8 | 411.1 | 415.7 | 429.9 | 396.5 | 348.3 | 397.9 | 344.2 | 360.4 | 390.4 | 907.9 | 898.6 | 900.9 | 909.5 | 906.8 | 899.5 | 885 | 875 | 872 | 880 | 865.3 | 883.8 | 859.3 | 848.1 | 897.9 | 903.5 | 910 | 886.9 | 936.9 | 912.1 | 871.7 | 906.3 | 878.5 | 864.2 | 891.7 | 910.9 | 900.8 | 904.7 | 882 | 901 | 906.3 | 918.8 | 907.5 | 976.3 | 910.3 | 908.2 | 871.6 | 861.5 | 912.7 | 895.8 | 906.4 | 956.9 | 900.3 | 924.9 | 904.5 | 914.6 | 928.6 | 922.4 | 922 | 839.7 | 855.2 | 896.1 | 905.9 | 865.3 | 911 | 854.5 | 915.9 | 909.3 | 906.3 | 858.9 | 871.1 | 920.1 | 915.8 | 897.8 | 916 | 899.1 | 899.5 | 895.1 | 910.7 | 896.6 | 914.2 | 891.7 | 902.9 | 825.2 | 910 | 954.8 | 885 | 889.9 | 889.3 | 896 | 903.7 | 897.1 | 913.7 | 901.8 | 882 | 946.5 | 852.9 | 789.5 | 901.6 | 846.5 | 887.2 | 904.4 | 899 | 908.1 | 905.3 | 898.1 | 895.9 | 898.3 | 900.4 | 893.6 | 941.3 | 921.2 | 860.2 | 793.7 | 807.2 | 792.6 | 792.4 | 792.1 | 795.4 | 800.8 | 807.4 | 815.4 | 803.1 | 807.8 | 812 | 812.5 | 764.3 | 702.1 | 828.5 | 811.4 | 811.6 | 817.4 | 814.8 | 810.8 | 816.1 | 805.9 | 812.5 | 800.7 | 815.6 | 802.2 | 807.8 | 775.8 | 773.2 | 775.4 | 885.1 | 868.1 | 860 | 888 | 909 | 913 | 933.9 | 909.9 | 1007.2 | 913.7 | 853.8 | 868.2 | 828.6 | 894.2 | 939 | 944.3 | 933 | 803.2 | 879.1 | 762.8 | 714.6 | 919.2 | 913.1 | 937.1 | 915 | 885.8 | 903.6 | 981.3 | 962.8 | 839 | 841.6 | 783.9 | 782 | 779.6 | 804.5 | 791 | 810 | 791.3 | 773.1 | 778.1 | 783.1 | 791 | 803.2 | 781.5 | 805.4 | 782.3 | 789.9 | 766.3 | 799.7 | 777 | 804.8 | 802 | 805.3 | 805.2 | 801.8 | 806.4 | 817.5 | 800.1 | 806.1 | 807.7 | 862.3 | 858.9 | 906.5 | 864.8 | 877.3 | 949.3 | 868.6 | 909.7 | 881.4 | 918.8 | 901.4 | 880.8 | 943.2 | 916.7 | 856.6 | 925.7 | 937.9 | 719.3 | 720 | 902.9 | 764.5 | 874.5 | 766.8 | 803.2 | 797.6 | 798.1 | 774.3 | 790.3 | 805 | 786.8 | 779.7 | 807.5 | 870.9 | 767.9 | 808.6 | 771.2 | 764.3 | 756.3 | 790.7 | 798 | 761.8 | 795 | 797.3 | 851.9 | 791 | 786.9 | 802.2 | 792.4 | 730.5 | 795.4 | 804.8 | 777.3 | 763.6 | 785.5 | 862.2 | 778.6 | 810.2 | 807.5 | 801.8 | 764 | 719 | 802.4 | 834 | 758.4 | 760.8 | 809.9 | 802 | 788.9 | 799.6 | 798.4 | 803.6 | 847.2 | 756.2 | 764.8 | 782.4 | 786.7 | 780 | 787.7 | 789.4 | 814.3 | 803.8 | 816.2 | 797.1 | 810.4 | 811 | 813.5 | 821 | 809 | 775.8 | 773 | 817 | 728.3 | 775.3 | 787.6 | 831.8 | 766.6 | 804.1 | 773.4 | 842 | 809.9 | 846.6 | 721.4 | 809.3 | 759.2 | 772.8 | 745.5 | 787 | 785.8 | 783.2 | 0 | 32.04 | 0 | 0 | 3.77 | 3.59 | 0 | 0 | 85626200 | 254100 | 86963800 | 296282.4 | 70912370 | 148739.1 | 85270320 | 127351.8 | 808250 | 9950 | 90230 | 500 | 69100 | 191.7 | 70050 | 266.5 | 68290 | 208.7 | 67660 | 167.8 | 138000 | 0 | 136000 | 2000 | 275100 | 274000 | 11.4167 | 3.77 | 3.59 |  | 32.04 | 0 | 280346.4
2025-04-21 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:17 | 17:11 | 482.5 | 472.1 | 511.9 | 512.9 | 508.2 | 488.5 | 518.3 | 498.3 | 511.7 | 514.9 | 516.5 | 513.6 | 515 | 515 | 518.6 | 519.6 | 485.5 | 488.6 | 510.4 | 516.6 | 530.5 | 525.4 | 530.6 | 527.8 | 526.3 | 527.3 | 529.1 | 529.1 | 531.3 | 532.2 | 525.3 | 529.2 | 508 | 475.6 | 479.5 | 484.4 | 492.5 | 492.7 | 510 | 487.4 | 501.9 | 546.9 | 574.2 | 544.9 | 545.1 | 564.5 | 604 | 595.7 | 644 | 569.9 | 543.7 | 534.8 | 489.9 | 559.9 | 550.7 | 557.1 | 577.4 | 532 | 466.7 | 532.5 | 462.9 | 479.9 | 526.2 | 1217 | 1199.9 | 1194.9 | 1213.6 | 1224.4 | 1172.7 | 1188 | 1217.3 | 1222.8 | 1193.8 | 1156.9 | 1190.9 | 1182 | 1139.3 | 1198.1 | 1210.7 | 1209.5 | 1198.9 | 1262.7 | 1217.4 | 1168.2 | 1226.7 | 1172.4 | 1164.1 | 1201.6 | 1208.9 | 1201.7 | 1204 | 1180 | 1206.3 | 1207.9 | 1224.2 | 1220.6 | 1318.6 | 1205.8 | 1213.6 | 1163.2 | 1148.7 | 1222 | 1186.8 | 1222.3 | 1278.5 | 1216.3 | 1239.8 | 1228 | 1228.3 | 1247 | 1234.2 | 1243.6 | 1117.5 | 1155.5 | 1206.8 | 1232.4 | 1217.6 | 1228.6 | 1228.2 | 1227.3 | 1224.4 | 1220.5 | 1156.3 | 1169.6 | 1229.6 | 1225.2 | 1199.8 | 1222.7 | 1209 | 1205.9 | 1204 | 1229.7 | 1213.1 | 1232.6 | 1202 | 1217.4 | 1137 | 1241.5 | 1320.7 | 1207.5 | 1204.2 | 1222 | 1218 | 1222.5 | 1213 | 1237.8 | 1226.7 | 1179.6 | 1281.5 | 1170 | 1062.3 | 1227.3 | 1166 | 1212 | 1212.4 | 1212.2 | 1226.4 | 1224.3 | 1223.7 | 1206.6 | 1209.8 | 1211.9 | 1201.3 | 1285.2 | 1245.8 | 1158.7 | 1094.8 | 1112.9 | 1098 | 1097.3 | 1096.9 | 1101.1 | 1109 | 1119.5 | 1125.9 | 1107.6 | 1115.2 | 1117.4 | 1120.1 | 1049.5 | 959.6 | 1140 | 1119.6 | 1116.7 | 1124.5 | 1121.6 | 1114.4 | 1123.7 | 1105.4 | 1120.5 | 1096.1 | 1120.5 | 1094.8 | 1108.1 | 1063.4 | 1056.5 | 1060.6 | 1199.2 | 1173.7 | 1069.7 | 1225.1 | 1230.4 | 1233.6 | 1279.1 | 1243.1 | 1361.9 | 1245.7 | 1160.4 | 1180.9 | 1118.2 | 1210.9 | 1266 | 1275.4 | 1065.6 | 1081.3 | 1191.1 | 1028.1 | 1016 | 1240 | 1238.6 | 1270 | 1242.9 | 1228.6 | 1233 | 1237 | 1325.2 | 1152.5 | 1160.1 | 1063.8 | 1065.3 | 1058.9 | 1100.3 | 1071.7 | 1098 | 1074.4 | 1054 | 1056.8 | 1057.8 | 1078.2 | 1098.3 | 1073 | 1098.7 | 1060.4 | 1071.6 | 1038 | 1096.6 | 1058.1 | 1096.2 | 1097 | 1094.9 | 1100.7 | 1095.3 | 1090.4 | 1109.8 | 1095.2 | 1101.2 | 1106 | 1157.1 | 1186.3 | 1218.3 | 1164.9 | 1234.6 | 1293.4 | 1221.3 | 1230.2 | 1187.6 | 1232.9 | 1218 | 1178.4 | 1281.5 | 1243.1 | 1141.7 | 1261.3 | 1265.7 | 964.9 | 953.7 | 1227.6 | 1027.2 | 1175.4 | 1057.4 | 1075.6 | 1074.6 | 1075.6 | 1048.1 | 1061 | 1084.3 | 1064.9 | 1055.9 | 1095.4 | 1202.2 | 1068 | 1101.8 | 1044 | 1025.1 | 1025.2 | 1071.5 | 1084.5 | 1054.5 | 1080.4 | 1084.2 | 1172.2 | 1076 | 1073.3 | 1090.4 | 1079.3 | 991.2 | 1088.1 | 1111.7 | 1059.9 | 1040.5 | 1042.5 | 1163.6 | 1044.8 | 1091.8 | 1089.2 | 1084.4 | 1030.9 | 973.3 | 1074.2 | 1129.7 | 1024.5 | 1025 | 1092.4 | 1077.2 | 1065.5 | 1078.1 | 1072.8 | 1060.3 | 1150.3 | 1020.6 | 1037.4 | 1026.4 | 1065.3 | 1066 | 1020.2 | 1079.8 | 1108.5 | 1093.4 | 1099 | 1088.9 | 1103.4 | 1095.5 | 1096 | 1110.5 | 1096 | 1052.1 | 1051 | 1104.1 | 981 | 1047.6 | 1060.3 | 1146.9 | 1060 | 1093.7 | 1066 | 1146.7 | 1104.3 | 1158 | 992.9 | 1100.2 | 1033.5 | 1040.4 | 1004.4 | 1061.4 | 1061.7 | 1060.4 | 0 | 38.05 | 0 | 0 | 5.15 | 5 | 0 | 0 | 85719080 | 254318.3 | 87059360 | 296585 | 71005360 | 148970.8 | 85362030 | 127525.9 | 809190 | 9960 | 91140 | 500 | 92880 | 218.3 | 95560 | 302.6 | 92990 | 231.7 | 91710 | 174.1 | 188000 | 2000 | 182000 | 0 | 373140 | 370000 | 11.9 | 5.15 | 5 |  | 38.05 | 0 | 379476.4
2025-04-22 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:10 | 15:54 | 102.2 | 97.8 | 108.5 | 108 | 107.7 | 103 | 110.5 | 104.8 | 109.8 | 108.7 | 109.8 | 109.2 | 109.6 | 109 | 110.8 | 110.4 | 102.5 | 105.3 | 111 | 111.1 | 115.8 | 114.5 | 116.1 | 115 | 116.1 | 115.4 | 116.7 | 116.2 | 117.7 | 116 | 115.7 | 115.1 | 108.4 | 100 | 99.9 | 102.1 | 103.9 | 102.5 | 107.2 | 104.1 | 104.9 | 117.5 | 123.5 | 115.6 | 117.1 | 121.2 | 131.2 | 130.9 | 138.3 | 125 | 118.7 | 114.1 | 114.8 | 122.2 | 120.8 | 119.9 | 126.2 | 113.6 | 101.3 | 115 | 109.6 | 105.3 | 110.8 | 267.4 | 261.8 | 263.7 | 262.9 | 267.3 | 262 | 260.6 | 265.1 | 268.7 | 260.1 | 259 | 259.3 | 251.1 | 246.7 | 265.7 | 268.4 | 269.5 | 264 | 281.1 | 269.6 | 257.2 | 272.3 | 258.6 | 256.4 | 266 | 264 | 262.8 | 263.7 | 254.7 | 259 | 260.3 | 262.3 | 265.9 | 287.6 | 266.5 | 263.7 | 249.2 | 248.6 | 265.3 | 258.1 | 267.2 | 271.5 | 266.6 | 269 | 266.8 | 263.6 | 269.8 | 268.9 | 272.1 | 244.3 | 255.3 | 266.3 | 274.2 | 271.6 | 271.8 | 274.9 | 271.3 | 269.4 | 270.4 | 255.9 | 259.2 | 273.9 | 271.7 | 266.5 | 271.9 | 267.6 | 267 | 266.5 | 273.1 | 270 | 273.1 | 265.2 | 267.8 | 251.6 | 273 | 281 | 271 | 264 | 270 | 270.2 | 269.3 | 265 | 271.9 | 269.6 | 258.3 | 281.2 | 251.1 | 231 | 269.5 | 251.6 | 268.4 | 271 | 266 | 269.2 | 270.9 | 272.2 | 266 | 267 | 267 | 264.7 | 285.2 | 278 | 253.9 | 233.5 | 241 | 232.4 | 233.4 | 234.5 | 231.3 | 235.7 | 240.3 | 245.4 | 241 | 237.4 | 242.9 | 246.2 | 224.3 | 209.1 | 253.8 | 243.6 | 245.9 | 245.1 | 241.8 | 243.4 | 243.4 | 242.6 | 240.6 | 238.5 | 240.4 | 238.2 | 239.3 | 227.2 | 225.8 | 234.8 | 263 | 255.6 | 235.1 | 267 | 268.9 | 268.7 | 280.7 | 272.5 | 299.3 | 273.6 | 257.2 | 258.8 | 244.8 | 267 | 251 | 283.9 | 236.5 | 235.1 | 261.1 | 224.2 | 207.6 | 273.5 | 272 | 275.6 | 269.8 | 268.4 | 269.8 | 294.1 | 290.6 | 249.9 | 256.6 | 234.3 | 232 | 228.8 | 235.6 | 233.1 | 240.5 | 236.6 | 229.8 | 231.3 | 231.7 | 234.1 | 233.8 | 233.5 | 238.1 | 244.5 | 80.1 | 239.1 | 243.2 | 233.1 | 235.7 | 231 | 238.9 | 242.2 | 239.3 | 251.4 | 242.3 | 233.4 | 240 | 240.6 | 257.8 | 266.2 | 271.7 | 259.7 | 276.3 | 290.4 | 273 | 274 | 263 | 272.9 | 269.3 | 260.5 | 287.1 | 279.7 | 254.6 | 283.9 | 282.2 | 212.8 | 210.4 | 272 | 227.7 | 261 | 240.8 | 238.2 | 231.7 | 230.9 | 231.4 | 235.1 | 237.8 | 234.4 | 230.8 | 242.6 | 263.1 | 238.3 | 241.4 | 233.6 | 228.6 | 229.4 | 229.8 | 238.2 | 235.1 | 233.8 | 240.1 | 262.5 | 236.9 | 231.5 | 236.3 | 238.8 | 212.5 | 235.6 | 246.1 | 230.7 | 226.4 | 239 | 264.3 | 234.1 | 244 | 240.9 | 239.1 | 230.9 | 212 | 236.2 | 259.8 | 222 | 230.1 | 256.3 | 252.6 | 251.4 | 246.1 | 249 | 245.1 | 264.4 | 231.6 | 236.3 | 220.5 | 240.2 | 241.3 | 244.7 | 240.6 | 244.7 | 247.5 | 244 | 236.7 | 243.5 | 238.5 | 241.5 | 247.7 | 237 | 232.8 | 235.9 | 246.2 | 213.3 | 226.8 | 237.1 | 254 | 235.6 | 235.3 | 231.9 | 248.3 | 242.3 | 254.7 | 224.3 | 237.7 | 223.5 | 234.8 | 219.7 | 234.5 | 238 | 228.9 | 0 | 26.78 | 0 | 0 | 1.06 | 0.98 | 0 | 0 | 85739320 | 254524 | 87080120 | 296870 | 71025360 | 149192 | 85381760 | 127727 | 809390 | 9970 | 91340 | 500 | 20240 | 205.7 | 20760 | 285 | 20000 | 221.2 | 19730 | 201.1 | 40000 | 2000 | 40000 | 0 | 80730 | 80000 | 10.7333 | 1.06 | 0.98 |  | 26.78 | 0 | 83165.5
2025-04-23 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:09 | 17:00 | 326.5 | 315.9 | 346.1 | 346.3 | 344.5 | 330.2 | 350.9 | 337.5 | 349.1 | 348 | 350.1 | 347.9 | 349.3 | 348.5 | 352.9 | 352.3 | 328.5 | 331.8 | 347 | 350.5 | 360.7 | 356.3 | 360.1 | 356.6 | 356.6 | 357.2 | 360.1 | 358.8 | 361 | 360.2 | 357.3 | 357.6 | 346.1 | 322.5 | 324.7 | 328 | 333 | 331.2 | 346.3 | 331.5 | 339.7 | 371.4 | 392.3 | 368.7 | 370.3 | 383.7 | 412.2 | 407.5 | 431.8 | 387.7 | 370.4 | 363.3 | 362.7 | 381.5 | 374.2 | 375.7 | 393 | 359.1 | 316.1 | 359.7 | 347.1 | 325.6 | 356.8 | 825.9 | 811.8 | 810 | 818.9 | 828.1 | 820.3 | 808.6 | 826.7 | 830.1 | 813 | 805.1 | 811.4 | 787.6 | 774.3 | 803.5 | 825.6 | 822 | 793 | 857.5 | 829.7 | 793.2 | 830.1 | 797.4 | 790.1 | 815.3 | 819.2 | 815.3 | 817.8 | 805.4 | 816.9 | 821.8 | 826.4 | 830 | 882.7 | 827.4 | 827.4 | 783.7 | 781.2 | 827.9 | 807.1 | 828.3 | 862.8 | 827.7 | 838.7 | 828.8 | 825.1 | 843.7 | 836.6 | 843 | 760.8 | 783.3 | 802.3 | 833.3 | 786.7 | 834.8 | 836 | 833.1 | 831.3 | 793.4 | 789.4 | 796.8 | 837.9 | 834.3 | 818.2 | 834.4 | 790.3 | 824.5 | 823 | 840.1 | 826.9 | 844.1 | 823.8 | 830.8 | 776.1 | 848.2 | 898.1 | 850.3 | 826.8 | 846.9 | 841.8 | 837.8 | 834.3 | 850.4 | 808.3 | 809.4 | 895.6 | 774.7 | 727.4 | 841.2 | 756.7 | 826.9 | 838.9 | 830.9 | 812.7 | 807.9 | 804 | 828.4 | 831.3 | 828 | 822.6 | 871.2 | 850.7 | 776.7 | 748.1 | 758.4 | 746.1 | 745.8 | 745.2 | 745.8 | 744.2 | 759.1 | 765.5 | 754.7 | 759.4 | 761.9 | 762.7 | 714.8 | 653 | 776.6 | 760.2 | 761.3 | 764.3 | 759.8 | 756.9 | 760.1 | 752.6 | 760.8 | 746.4 | 758.2 | 743.9 | 744.5 | 717.8 | 709.1 | 722.5 | 826.8 | 807.6 | 736 | 843.5 | 849 | 852.9 | 878 | 821.3 | 940.8 | 861.2 | 806.2 | 818.3 | 774.5 | 843.8 | 801.3 | 880.5 | 736.2 | 741.7 | 821.7 | 706.6 | 661.2 | 863.4 | 821.6 | 872.4 | 860.8 | 848 | 845.9 | 922.5 | 905.2 | 776.1 | 785.3 | 721.1 | 712.3 | 717.7 | 740.8 | 730.8 | 746.9 | 730.1 | 717 | 717.9 | 721 | 741.9 | 740.9 | 741 | 745.4 | 726.5 | 666 | 712.6 | 752.3 | 720.5 | 740.2 | 723.2 | 746.6 | 750.1 | 746.8 | 757.9 | 760.3 | 746.3 | 749.7 | 754.6 | 794 | 818.4 | 835.4 | 797.5 | 804.8 | 876.5 | 800.8 | 841.4 | 812.2 | 843.4 | 829.5 | 808.4 | 873.2 | 835.3 | 782.4 | 853.3 | 869.4 | 660.9 | 653.2 | 834.7 | 703 | 804.2 | 734.6 | 728.3 | 721.4 | 721.1 | 714.9 | 718.1 | 734.2 | 719.9 | 716.4 | 744.1 | 799.3 | 736.6 | 742.4 | 710 | 695.6 | 686.4 | 722.1 | 732.5 | 728 | 726.9 | 729.5 | 779.1 | 727.3 | 716.5 | 736.5 | 729.5 | 659.6 | 732.6 | 748.5 | 713.9 | 701.2 | 707.2 | 789.2 | 706.4 | 741 | 734.7 | 729.9 | 697.3 | 654.9 | 715 | 761.7 | 691.8 | 698.7 | 746.5 | 735.6 | 730.5 | 729.1 | 733.9 | 728.9 | 777.1 | 689.6 | 707.8 | 685.4 | 717.7 | 703.6 | 698.5 | 742 | 755.7 | 753.1 | 753.4 | 741.3 | 754 | 740.2 | 751.9 | 753.6 | 742.6 | 718.4 | 719.3 | 755 | 670 | 712.3 | 726.6 | 777 | 737.7 | 737.7 | 720.4 | 772 | 752.7 | 779 | 698.3 | 746.1 | 699.9 | 709.1 | 684 | 720 | 726 | 720.9 | 0 | 33.31 | 0 | 0 | 3.45 | 3.31 | 0 | 0 | 85802220 | 254763 | 87145020 | 297195 | 71088790 | 149387 | 85444060 | 127922 | 810020 | 9970 | 91960 | 510 | 62900 | 239 | 64900 | 325 | 63430 | 195 | 62300 | 195 | 126000 | 0 | 124000 | 2000 | 253530 | 250000 | 11.85 | 3.45 | 3.31 |  | 33.31 | 0 | 257857.4
2025-04-24 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:35 | 17:14 | 382 | 370.5 | 406.3 | 405 | 401.4 | 384.8 | 414.2 | 394.8 | 406.4 | 407.2 | 413.8 | 408 | 407 | 406 | 410.9 | 408.6 | 383.4 | 389.7 | 412.8 | 413.6 | 429.4 | 423 | 425.1 | 420.5 | 428 | 424.1 | 425.3 | 421.9 | 432.2 | 431.3 | 422.4 | 423.3 | 399.2 | 375.1 | 378 | 382.6 | 388 | 386.9 | 400.5 | 383.7 | 392.1 | 428.7 | 450.8 | 420.8 | 426.1 | 439.8 | 474.4 | 467.7 | 510.5 | 450.5 | 425.2 | 419.2 | 418.8 | 442.3 | 435.9 | 440.1 | 457.8 | 420 | 370.3 | 422.1 | 405 | 380.1 | 410.8 | 989.9 | 973.3 | 972.8 | 983.6 | 995.9 | 974 | 962.8 | 983.7 | 999.1 | 966 | 958.9 | 959.9 | 930.1 | 909.9 | 975.4 | 985.6 | 978.9 | 967.8 | 1032.9 | 996.5 | 947.3 | 1007.8 | 960.3 | 951.5 | 985.7 | 985.3 | 971.5 | 976.4 | 1008.1 | 1019.8 | 1028 | 1026.2 | 1037 | 1126.3 | 1031 | 1023 | 964.2 | 964 | 1014.8 | 991.6 | 1017 | 1016 | 1011.3 | 1013.9 | 1000.3 | 995.8 | 1016.1 | 1008 | 1025.4 | 921.3 | 952.2 | 971.3 | 987.3 | 959.7 | 985.8 | 995.3 | 984.1 | 971.1 | 948.8 | 922.2 | 936.5 | 968.3 | 957.1 | 948.2 | 959.9 | 960.8 | 953.9 | 948.4 | 970.8 | 956.9 | 972.8 | 939.9 | 943.4 | 885.2 | 955.4 | 1018.5 | 923.2 | 919.5 | 942 | 942.3 | 934.3 | 929 | 949.8 | 955.1 | 885 | 988.1 | 887.4 | 818.4 | 945.7 | 867.6 | 946.7 | 957.1 | 948.9 | 940.8 | 965.3 | 915.7 | 950 | 954.9 | 941.6 | 933.7 | 1006.9 | 975.6 | 901.9 | 845.5 | 860.1 | 847.7 | 852.9 | 856 | 855.4 | 858.6 | 866.6 | 873.3 | 863 | 860 | 863.5 | 872.7 | 810.5 | 742.2 | 886.9 | 872.4 | 869.1 | 873.3 | 867.9 | 865 | 871.2 | 859 | 872.3 | 853 | 872.8 | 854.1 | 859.3 | 827.1 | 821.3 | 824 | 923.7 | 897.7 | 816.4 | 937 | 940.9 | 941.2 | 984.1 | 938.9 | 1044.1 | 918.5 | 903 | 913.6 | 862.8 | 936.5 | 890 | 978.8 | 824 | 824.7 | 890.9 | 784.4 | 728.7 | 979.3 | 956.5 | 978.9 | 968 | 961.8 | 959.5 | 1033.7 | 1039.3 | 913.7 | 924.5 | 850.6 | 843 | 848.9 | 882.6 | 858.7 | 877 | 842.2 | 829.8 | 838.3 | 844.1 | 857.1 | 864.1 | 849.4 | 860.8 | 784.1 | 697.6 | 823.1 | 850 | 823.1 | 848.3 | 825.3 | 847.1 | 868.5 | 859.3 | 849.7 | 861.4 | 859.1 | 861.3 | 865.3 | 929.8 | 958 | 979.7 | 936.7 | 995.9 | 1043.5 | 965.6 | 988.9 | 951.2 | 985.9 | 973 | 940.7 | 1030.4 | 999.2 | 908.4 | 1012.7 | 1007.9 | 763.9 | 754.4 | 979.3 | 813.8 | 937.5 | 889.6 | 880.3 | 876.8 | 884.6 | 860.9 | 876.1 | 882.4 | 863.7 | 859.9 | 891.4 | 966.7 | 885.5 | 890.3 | 848.6 | 845.6 | 836.7 | 878.3 | 887.2 | 884.7 | 883.2 | 883.3 | 962.3 | 874 | 873.1 | 875.1 | 876.2 | 804.2 | 882.2 | 903.2 | 855.7 | 841 | 853.2 | 952.1 | 858.4 | 892.7 | 887.3 | 879.9 | 840.5 | 793.5 | 872.8 | 915.2 | 837.7 | 844.6 | 897.8 | 882.9 | 880.5 | 881.6 | 873.3 | 860 | 937.5 | 836.4 | 855.1 | 820.5 | 848.3 | 849 | 819.6 | 886.9 | 904.4 | 896 | 898.8 | 890.4 | 900.8 | 886.2 | 901.7 | 903.8 | 888.6 | 858.2 | 861.1 | 897.7 | 795.6 | 851 | 862.4 | 935.2 | 881.2 | 882.3 | 856 | 925.3 | 894.6 | 940.6 | 841.3 | 888.1 | 842.5 | 845.3 | 811.7 | 859 | 863.4 | 858.7 | 0 | 31.62 | 0 | 0 | 3.85 | 3.81 | 0 | 0 | 85877860 | 255013 | 87219390 | 297526 | 71161030 | 149621 | 85518130 | 128146 | 810770 | 9970 | 92690 | 510 | 75640 | 250 | 74370 | 331 | 72240 | 234 | 74070 | 224 | 150000 | 0 | 146000 | 0 | 296320 | 296000 | 11.65 | 3.85 | 3.81 |  | 31.62 | 0 | 302338.1
2025-04-25 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 4:57 | 17:08 | 547.5 | 534 | 580.6 | 581.3 | 576.3 | 556.1 | 587.6 | 564.5 | 581.1 | 583.8 | 586.2 | 582.6 | 584.9 | 583.2 | 589.9 | 590.4 | 551.5 | 554.1 | 578.4 | 585.5 | 602.3 | 594.4 | 602.2 | 599.3 | 596.7 | 596.3 | 600.3 | 599.3 | 603.4 | 603.4 | 596.7 | 601 | 576.4 | 539.6 | 544.4 | 549.8 | 558.1 | 558.4 | 579.3 | 553.3 | 570.6 | 620.2 | 652.2 | 617.6 | 616.5 | 639.6 | 684.8 | 658 | 725.6 | 646.8 | 618.2 | 608.5 | 606.5 | 636.4 | 625.2 | 632.6 | 654 | 600.7 | 528.6 | 604.7 | 583.4 | 544.9 | 597.1 | 1378.2 | 1357.7 | 1355.6 | 1373.9 | 1378 | 1369.6 | 1343.7 | 1378.1 | 1373.9 | 1350.2 | 1324.2 | 1348 | 1311.2 | 1293.3 | 1371.6 | 1379.8 | 1376.1 | 1354.2 | 1434 | 1393.3 | 1329.3 | 1384.9 | 1311.6 | 1318.3 | 1358.4 | 1373.5 | 1367.8 | 1369.8 | 1340.1 | 1368.5 | 1377.1 | 1392.4 | 1381.8 | 1479.3 | 1377 | 1382.2 | 1322.5 | 1310.5 | 1388.4 | 1351.6 | 1381.7 | 1422.4 | 1379 | 1409.7 | 1381.2 | 1388 | 1413.3 | 1404.5 | 1409.4 | 1279.5 | 1301.6 | 1369.2 | 1381.7 | 1374.5 | 1392.6 | 1334 | 1394.7 | 1387.6 | 1384.8 | 1315.7 | 1329.3 | 1394.9 | 1390.7 | 1363.5 | 1388.9 | 1345.6 | 1371.5 | 1368.3 | 1395.6 | 1370.3 | 1403.7 | 1368.3 | 1348.7 | 1291.5 | 1388.5 | 1463.5 | 1364.7 | 1343.7 | 1368.4 | 1379.5 | 1384 | 1378.9 | 1401.1 | 1306.6 | 1341.6 | 1460.5 | 1308.6 | 1209.2 | 1385.7 | 1301.9 | 1331 | 1384.6 | 1348.7 | 1375 | 1394.6 | 1356 | 1373.5 | 1379.7 | 1377 | 1363.7 | 1437.2 | 1405.1 | 1320.4 | 1244.1 | 1246 | 1248.3 | 1246 | 1208.7 | 1245.5 | 1250.8 | 1259.9 | 1269.1 | 1251.7 | 1257.5 | 1263.5 | 1265.8 | 1191.8 | 1087.8 | 1288.8 | 1265 | 1263.1 | 1269.6 | 1264.5 | 1259.5 | 1265.8 | 1252.3 | 1268.2 | 1243.8 | 1269.9 | 1244.2 | 1253.9 | 1203.2 | 1197.5 | 1199.2 | 1366.3 | 1336.5 | 1213 | 1383.6 | 1393.2 | 1400.6 | 1438.4 | 1346.1 | 1540.8 | 1408.2 | 1307.7 | 1339.7 | 1265.8 | 1370 | 1279 | 1449.3 | 1211.4 | 1231 | 1321.1 | 1166.7 | 1090.1 | 1409.1 | 1398.9 | 1433.9 | 1406 | 1389.1 | 1386.5 | 1513.4 | 1481 | 1305.8 | 1312.9 | 1207.2 | 1212.5 | 1202.8 | 1248.9 | 1217.7 | 1248.1 | 1218.8 | 1199.6 | 1202 | 1203.3 | 1235.8 | 1241.6 | 1226.6 | 1242.7 | 1223 | 1207.2 | 1184.1 | 1253.4 | 1205.2 | 1247.4 | 1205 | 1247.9 | 1250.5 | 1245.2 | 1247.1 | 1262.6 | 1247.8 | 1250.9 | 1257.3 | 1308.4 | 1315.4 | 1383.6 | 1319.4 | 1384.5 | 1446.2 | 1385.9 | 1393.3 | 1352.2 | 1406.5 | 1381.1 | 1344.8 | 1448.4 | 1398.1 | 1296.2 | 1411.3 | 1442.1 | 1100.9 | 1088.2 | 1391.8 | 1172.5 | 1337.6 | 1231.1 | 1226 | 1223.8 | 1229.8 | 1190.4 | 1213.2 | 1233.4 | 1210.1 | 1198.9 | 1244.5 | 1329.7 | 1239.2 | 1244.7 | 1184.6 | 1171.1 | 1168.4 | 1222.2 | 1235.5 | 1233.6 | 1230.9 | 1229.4 | 1333.7 | 1224.2 | 1220.4 | 1235.2 | 1221.3 | 1125.8 | 1234.8 | 1250.8 | 1193 | 1182.2 | 1181.3 | 1314.2 | 1191.3 | 1241.7 | 1237.7 | 1233.2 | 1172.2 | 1106.4 | 1218.6 | 1275 | 1171.5 | 1173 | 1242.9 | 1225.1 | 1215 | 1223.5 | 1221 | 1210.6 | 1296.7 | 1161 | 1183 | 1163.1 | 1207.8 | 1207 | 1170.1 | 1235.3 | 1266.5 | 1253.3 | 1261.9 | 1247.6 | 1255.4 | 1251.7 | 1262.1 | 1268.2 | 1250.9 | 1201.8 | 1207 | 1260.4 | 1124.8 | 1197.2 | 1212.4 | 1299.3 | 1243.4 | 1247.1 | 1210.6 | 1304.1 | 1265.2 | 1311.8 | 1178 | 1254.8 | 1181.5 | 1190.7 | 1150.3 | 1211.8 | 1212.9 | 1212.6 | 0 | 37.02 | 0 | 0 | 5.9 | 5.6 | 0 | 0 | 85983100 | 255217 | 87326960 | 297807 | 71266270 | 149850 | 85622660 | 128245 | 811820 | 9980 | 93730 | 520 | 105240 | 204 | 107570 | 281 | 105240 | 229 | 104530 | 99 | 210000 | 2000 | 208000 | 2000 | 422580 | 418000 | 12.1833 | 5.9 | 5.6 |  | 37.02 | 0 | 430181.3
2025-04-26 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 4:58 | 17:15 | 564.9 | 550.8 | 598.3 | 598.5 | 595.7 | 575.3 | 605.8 | 581.7 | 600.6 | 602.9 | 604.2 | 601.1 | 602.9 | 601.8 | 608.6 | 607.5 | 568.8 | 571.7 | 596.7 | 604 | 621.3 | 613.1 | 622 | 617.7 | 615 | 614.1 | 617.9 | 616.2 | 620.4 | 621 | 613.6 | 618.5 | 594.9 | 557.3 | 561.8 | 566.7 | 574.3 | 574.8 | 598 | 569.3 | 587.1 | 638.7 | 674 | 636.3 | 635.3 | 659.2 | 705 | 674.5 | 752.2 | 666.6 | 636.6 | 625.9 | 623.9 | 655.8 | 643.3 | 652.4 | 673.5 | 617.2 | 544.1 | 620.2 | 600 | 559.4 | 616.4 | 1424.9 | 1401.4 | 1384.9 | 1413.6 | 1429.5 | 1409.6 | 1393.6 | 1422.1 | 1430.8 | 1402.3 | 1379.5 | 1400.6 | 1356.4 | 1336.7 | 1405.9 | 1411 | 1413.6 | 1403.2 | 1482.1 | 1428.5 | 1369.5 | 1431.9 | 1344.1 | 1363.7 | 1405.3 | 1401.5 | 1407.3 | 1413.7 | 1393.6 | 1423.2 | 1421.2 | 1434.1 | 1435.9 | 1539.2 | 1420.2 | 1430 | 1368.6 | 1352.9 | 1431.5 | 1387.7 | 1431.3 | 1468.9 | 1434.3 | 1451.4 | 1435 | 1434.8 | 1459.4 | 1446.6 | 1457.7 | 1259.1 | 1347 | 1414.2 | 1433.4 | 1426.1 | 1437.7 | 1437.9 | 1432.7 | 1429.6 | 1431 | 1357.9 | 1369.1 | 1437.1 | 1430.5 | 1404.4 | 1418.1 | 1385.3 | 1417 | 1413.6 | 1440.9 | 1419.4 | 1446.6 | 1411.6 | 1388.1 | 1324.4 | 1443.2 | 1523.9 | 1414.2 | 1407.4 | 1422.6 | 1419 | 1415.6 | 1423.8 | 1445 | 1403.9 | 1376.9 | 1521 | 1343.5 | 1244 | 1435 | 1341.4 | 1410.8 | 1429.5 | 1421.2 | 1437.2 | 1405.3 | 1431.2 | 1412.5 | 1418.7 | 1390.7 | 1390.7 | 1489.1 | 1452.4 | 1330.4 | 1272.5 | 1294.9 | 1281.6 | 1281.1 | 1281.3 | 1287 | 1295.4 | 1310 | 1316.6 | 1295.2 | 1297.5 | 1296.7 | 1305.1 | 1221.8 | 1114.4 | 1329.1 | 1305.2 | 1302.7 | 1311.2 | 1309.3 | 1298.5 | 1310.2 | 1289 | 1309.9 | 1277.6 | 1307.8 | 1280.6 | 1293.9 | 1237.4 | 1230.5 | 1239 | 1398.5 | 1362.9 | 1240.7 | 1423.5 | 1430.8 | 1434.4 | 1486.8 | 1442.4 | 1579.6 | 1449.5 | 1348.3 | 1340 | 1293.2 | 1407.5 | 1315 | 1487.2 | 1235.5 | 1252.9 | 1381.4 | 1190 | 1112.2 | 1454.8 | 1438.3 | 1460.3 | 1443.9 | 1432.9 | 1422.8 | 1554.6 | 1531.7 | 1347.7 | 1359.6 | 1238.1 | 1243.4 | 1233.9 | 1283 | 1253.3 | 1281.7 | 1250.2 | 1231.1 | 1234.2 | 1234.5 | 1270.8 | 1281 | 1263.9 | 1282.6 | 1247.9 | 1231.8 | 1204.3 | 1284.1 | 1229.4 | 1271.2 | 1228 | 1271.3 | 1288.3 | 1279.3 | 1259.5 | 1292.3 | 1283.3 | 1286.9 | 1292.5 | 1364.6 | 1405.5 | 1438.5 | 1372.6 | 1446.9 | 1510.2 | 1436.6 | 1447.9 | 1397.4 | 1450.8 | 1431.4 | 1385.9 | 1498.8 | 1439.7 | 1314.8 | 1458.5 | 1482.8 | 1125.8 | 1113.7 | 1437.4 | 1200.1 | 1378.5 | 1281 | 1272.3 | 1271.5 | 1275.5 | 1239.4 | 1256.2 | 1282.3 | 1257.8 | 1247.7 | 1297.5 | 1402.5 | 1290.9 | 1297.7 | 1233.1 | 1207.6 | 1209.6 | 1261.6 | 1280.3 | 1273.6 | 1274.2 | 1276.3 | 1401 | 1267.6 | 1264.4 | 1283.5 | 1270.1 | 1165.6 | 1282.1 | 1307.1 | 1242.6 | 1223.8 | 1227 | 1374 | 1235.4 | 1291.4 | 1288.8 | 1283.1 | 1218.5 | 1147.8 | 1249.2 | 1329.8 | 1216.4 | 1216.7 | 1296.1 | 1268.6 | 1267 | 1272.6 | 1267.1 | 1256.5 | 1356.3 | 1209 | 1227.1 | 1213.4 | 1251 | 1235 | 1229.8 | 1274.3 | 1306.8 | 1294.8 | 1300.7 | 1290.1 | 1303.1 | 1290.9 | 1305.3 | 1313.3 | 1293.1 | 1244 | 1241 | 1308.1 | 1163.3 | 1237.8 | 1254.4 | 1352.1 | 1282.2 | 1286.1 | 1247.9 | 1351.8 | 1307.5 | 1358.4 | 1215.8 | 1300.5 | 1220.6 | 1227 | 1186.2 | 1247.9 | 1254.2 | 1253.8 | 0 | 37.72 | 0 | 0 | 6.02 | 5.79 | 0 | 0 | 86091540 | 255420 | 87438180 | 298088 | 71374420 | 150105 | 85730930 | 128509 | 812910 | 9980 | 94810 | 520 | 108440 | 203 | 111220 | 281 | 108150 | 255 | 108270 | 264 | 218000 | 0 | 216000 | 0 | 436080 | 434000 | 12.2833 | 6.02 | 5.79 |  | 37.72 | 0 | 444233.9
2025-04-27 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 6:06 | 17:23 | 579.9 | 561.9 | 614.8 | 612.3 | 608.6 | 588.5 | 624.1 | 598.6 | 615.1 | 618.8 | 624.1 | 621.9 | 616.4 | 621 | 624.7 | 625.8 | 587 | 591.1 | 618.2 | 625.2 | 643.6 | 634.9 | 640 | 638.8 | 635.8 | 634.9 | 637.3 | 636.8 | 641.1 | 640.4 | 632.5 | 637.3 | 603.7 | 567.5 | 571.8 | 578.5 | 588.6 | 593 | 611.1 | 584.5 | 599 | 647.7 | 678.1 | 634.7 | 644.2 | 660.9 | 709.3 | 703.5 | 745.9 | 682.2 | 648.4 | 638.5 | 638.3 | 673.1 | 661.5 | 663.6 | 690.9 | 634.1 | 560.4 | 638.8 | 620.3 | 579.1 | 629.2 | 1451.1 | 1426.4 | 1449.6 | 1454.9 | 1439.8 | 1449.5 | 1413.5 | 1468.6 | 1439.4 | 1415.1 | 1387.1 | 1412.8 | 1395.6 | 1373.8 | 1457 | 1453.4 | 1472.2 | 1357.4 | 1503 | 1488.4 | 1401 | 1443.2 | 1422.1 | 1378.8 | 1420.7 | 1468.6 | 1449.2 | 1439.4 | 1434.4 | 1452 | 1493.7 | 1489.3 | 1465.6 | 1566.2 | 1494.4 | 1462.6 | 1387.4 | 1404.1 | 1454.7 | 1437.9 | 1440.5 | 1499.6 | 1440.7 | 1472.9 | 1437.7 | 1440.1 | 1477.3 | 1476.3 | 1427 | 1306.3 | 1361.6 | 1354.3 | 1399.3 | 1431.4 | 1452.5 | 1397.1 | 1471.5 | 1451.7 | 1441.5 | 1370.3 | 1398.5 | 1469.5 | 1460 | 1433.7 | 1454.2 | 1427.5 | 1419.6 | 1247.9 | 411 | 1404.4 | 1430.9 | 1406.4 | 1409.3 | 1291.6 | 1382.5 | 1461.2 | 1374 | 1392.9 | 1359.7 | 1373.7 | 1401.6 | 1393 | 1398.1 | 1360.9 | 1357.3 | 1479.2 | 1328.6 | 1233.6 | 1389.8 | 1323.7 | 1374.2 | 1397.7 | 1350.2 | 443.5 | 1380 | 1396.5 | 1338.4 | 1401.4 | 1376.4 | 1392.9 | 1459.5 | 1427.2 | 1351.1 | 1259.9 | 1281.9 | 1276.5 | 1275.8 | 1266.1 | 1265.4 | 1262.1 | 1264.7 | 1264.6 | 1258.7 | 1279.6 | 1284.7 | 1277.8 | 1228.3 | 1118.9 | 1286.6 | 1272.8 | 1267.2 | 1264.9 | 1257.5 | 1253.2 | 1255 | 1253 | 1260.4 | 1249.1 | 1258.2 | 1236.3 | 1241.4 | 1205.1 | 1197.2 | 1202.5 | 1379.5 | 1364.1 | 1244.6 | 1398.7 | 1410.5 | 1437.5 | 1453.6 | 1363.3 | 1571.1 | 1359.2 | 1329 | 1321.4 | 1306.9 | 1418.3 | 1310 | 1479 | 1249.3 | 1247 | 1353.4 | 1204.9 | 1125.8 | 1436 | 1432.7 | 1472.4 | 1434.9 | 1425.1 | 1433.1 | 1532.7 | 1524.4 | 1315.2 | 1327.3 | 1241.3 | 1244.3 | 1240.3 | 1276.8 | 1251.9 | 1273.4 | 1253.6 | 1232.2 | 1231.3 | 1237.8 | 1262.4 | 1248.9 | 1245.7 | 1243.3 | 1255.7 | 1242.7 | 1220.2 | 1282.5 | 1241.3 | 1274 | 1237 | 1297 | 1259.4 | 1260.8 | 1276.9 | 1314.1 | 1245.4 | 1251.7 | 1267.1 | 1336 | 1403.5 | 1437 | 1364.6 | 1388.6 | 1484.7 | 1396.2 | 1408.7 | 1399.3 | 1461.6 | 1419.8 | 1383 | 1472.5 | 1426.4 | 1341.2 | 1427 | 1473.9 | 1133.6 | 1119.1 | 1407.5 | 1202.4 | 1375.2 | 1292.9 | 1285 | 1288.4 | 1290.4 | 1255.6 | 1277.5 | 1286.5 | 1263.7 | 1262.6 | 1297 | 1366.7 | 1292.7 | 1287.2 | 1239.8 | 1237.6 | 1239.3 | 1286.2 | 1286.4 | 1288.4 | 1290.2 | 1280.4 | 1361 | 1264.4 | 1266.1 | 1276.8 | 1264.3 | 1185.1 | 1273.4 | 1288.3 | 1245.1 | 1226.2 | 1263 | 1377.4 | 1254.4 | 1298.4 | 1291.5 | 1286.4 | 1230.3 | 1162.2 | 1240.4 | 1306.1 | 1238.7 | 1237.1 | 1295.8 | 1288.3 | 1272.3 | 1273.1 | 1275.3 | 1283 | 1330.8 | 1216.7 | 1236.5 | 1258.7 | 1254.3 | 1257 | 1262.9 | 1257 | 1255.6 | 1247 | 1285.1 | 1285.5 | 1284.2 | 1283.1 | 1290.7 | 1299 | 1290.4 | 1253.1 | 1249 | 1299.6 | 1160.3 | 1247.6 | 1258.2 | 1332.8 | 1245 | 1238.7 | 1243.9 | 1299.9 | 1308.9 | 1347.1 | 1220.3 | 1303.8 | 1223.4 | 1230.5 | 1202.1 | 1262.9 | 1266.7 | 1228.6 | 0 | 38.15 | 0 | 0 | 6.01 | 5.9 | 0 | 0 | 86202180 | 255697 | 87544860 | 298400 | 71481730 | 150425 | 85838510 | 128924 | 813990 | 9990 | 95880 | 530 | 110640 | 277 | 106680 | 312 | 107310 | 320 | 107580 | 415 | 216000 | 2000 | 214000 | 2000 | 432210 | 430000 | 11.2833 | 6.01 | 5.9 |  | 38.15 | 0 | 442091.5
2025-04-28 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:03 | 16:58 | 173.9 | 166.6 | 184.3 | 183.9 | 183.9 | 176.2 | 187.4 | 179.4 | 187.3 | 187.8 | 186.2 | 185.8 | 187 | 187.5 | 189.5 | 187.5 | 176.1 | 179.9 | 189.1 | 190.2 | 197 | 194.7 | 196.6 | 194.5 | 196.8 | 195.3 | 197.8 | 196.3 | 198.4 | 198.5 | 195.6 | 196 | 185.1 | 172.8 | 173.1 | 175.8 | 177.4 | 176.8 | 183.7 | 175.8 | 179.1 | 198 | 209.5 | 195.3 | 198.8 | 205.1 | 222.4 | 221.7 | 237.1 | 211.4 | 202 | 198.3 | 195.8 | 207.8 | 203.8 | 204.6 | 213.8 | 194.8 | 171.8 | 195.6 | 184.7 | 177.6 | 192.7 | 449.6 | 438.7 | 441.9 | 442.3 | 451.1 | 441.9 | 438.1 | 446.5 | 454 | 438.5 | 438.1 | 437.4 | 424.9 | 408.4 | 443 | 447.5 | 448 | 443 | 469.8 | 452.6 | 430.5 | 456.3 | 435.5 | 430.6 | 446.1 | 448.7 | 440.2 | 442.3 | 439.9 | 446 | 449 | 448.2 | 457 | 493.5 | 455.2 | 450.2 | 424.7 | 427.4 | 449.3 | 438.5 | 453.2 | 471.3 | 456.3 | 455.6 | 452.3 | 444.8 | 458.6 | 454.5 | 460.3 | 414.1 | 429.2 | 430.6 | 456.6 | 452.4 | 451.2 | 456.6 | 448.4 | 448.4 | 452 | 427 | 431.2 | 456.4 | 452 | 443.7 | 451.4 | 444.7 | 444.1 | 415.2 | 344.3 | 449.7 | 456.1 | 444.1 | 447.6 | 419.5 | 453.9 | 489.1 | 441.7 | 441.3 | 450.3 | 451.3 | 448.9 | 444 | 453 | 451.9 | 431.4 | 470.9 | 419.5 | 385.5 | 451.9 | 422.6 | 450.4 | 452.6 | 364.6 | 0 | 483.2 | 486.7 | 443.5 | 445.1 | 444.5 | 439.3 | 472.6 | 458.7 | 423.5 | 379.1 | 377.7 | 379.5 | 379.9 | 379.5 | 378.9 | 377.8 | 385.5 | 387 | 380.7 | 380.2 | 380.9 | 382.4 | 367.1 | 323.9 | 398 | 381.7 | 381.9 | 385.9 | 385.7 | 382 | 384.9 | 377.3 | 386.3 | 375.5 | 384.2 | 378.2 | 379 | 361 | 360.4 | 364.7 | 436.7 | 425.2 | 388 | 444 | 446.6 | 448.7 | 466.7 | 454.4 | 496.9 | 458.1 | 428.3 | 430.9 | 405.8 | 443.7 | 401 | 467.7 | 391.5 | 390.4 | 433.8 | 373.3 | 346.3 | 455.6 | 447.5 | 456.6 | 450.8 | 435.3 | 434.1 | 490.2 | 480 | 398.3 | 401.3 | 363.3 | 365.2 | 367 | 379.7 | 369.7 | 379.4 | 365.8 | 364.3 | 366.3 | 364.7 | 381.1 | 379 | 379.9 | 379.2 | 371.4 | 260 | 362.4 | 380.8 | 368.9 | 379 | 367 | 387.8 | 384.6 | 385.2 | 384.5 | 383.4 | 379.1 | 379.1 | 379.5 | 422.2 | 440.5 | 440.1 | 427.1 | 454.6 | 477.9 | 452.2 | 452.5 | 434.8 | 449.9 | 448.6 | 431.9 | 475.3 | 460.8 | 418.1 | 466.5 | 462.1 | 353.4 | 349.5 | 451 | 377.2 | 431.9 | 383.9 | 379.6 | 379.6 | 379.9 | 379.4 | 378.7 | 379.1 | 376 | 378 | 381 | 416.4 | 378.1 | 376.4 | 361.5 | 359.1 | 358.8 | 375.8 | 374.5 | 375.9 | 372.4 | 372.7 | 413 | 372.2 | 375.7 | 376.8 | 377 | 346.1 | 375.2 | 381.9 | 363.8 | 357.2 | 345.1 | 403.5 | 342 | 365.7 | 360.9 | 359.2 | 338.8 | 315.6 | 351.6 | 372.8 | 341.1 | 342.1 | 368 | 361.4 | 355.6 | 352.2 | 360.6 | 367.1 | 385.9 | 330.9 | 343.1 | 352.3 | 351.4 | 349 | 355.9 | 370.5 | 381.4 | 383.2 | 376.9 | 378.2 | 379.9 | 374.1 | 379.3 | 381.5 | 373.6 | 360.7 | 359 | 381.8 | 334.8 | 358.7 | 365.5 | 401 | 371.1 | 370.3 | 369.6 | 392.3 | 386.3 | 399 | 355 | 381.7 | 352.6 | 361.9 | 345.4 | 359.2 | 361.8 | 344.2 | 0 | 25.69 | 0 | 0 | 1.78 | 1.63 | 0 | 0 | 86236610 | 255917 | 87579010 | 298718 | 71515250 | 150645 | 85870600 | 129136 | 814330 | 9990 | 96210 | 530 | 34430 | 220 | 34150 | 318 | 33520 | 220 | 32090 | 212 | 68000 | 0 | 66000 | 0 | 134190 | 134000 | 11.9167 | 1.78 | 1.63 |  | 25.69 | 0 | 134866.8
2025-04-29 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 5:03 | 15:59 | 288.2 | 277.1 | 305.2 | 304.5 | 304.3 | 291.1 | 310.4 | 297.8 | 309.7 | 309.8 | 309.4 | 307.9 | 308.8 | 309.6 | 312.8 | 310.4 | 291.1 | 296.2 | 310 | 312.5 | 322.8 | 319.2 | 323.6 | 319.4 | 320.5 | 318.1 | 323 | 321.2 | 324.3 | 323.7 | 319.8 | 319.4 | 304.2 | 284.5 | 286.3 | 289.9 | 293.2 | 292.6 | 304.7 | 291.4 | 296.1 | 326.2 | 344.6 | 322.1 | 326.9 | 337.7 | 364.4 | 361 | 386.8 | 343.7 | 329.6 | 324.1 | 321.9 | 339.4 | 333.9 | 335.4 | 349.6 | 318.4 | 282.5 | 321.3 | 307.1 | 290.3 | 316.8 | 740 | 722.9 | 725 | 728 | 741.2 | 727.9 | 720.5 | 733.9 | 745.6 | 721.5 | 720.5 | 720.8 | 699 | 684.9 | 724.9 | 732 | 730.9 | 726.9 | 769.2 | 741.4 | 708.7 | 750.6 | 717.7 | 711.1 | 737.9 | 736.7 | 727.2 | 728.5 | 722.7 | 733.9 | 737.4 | 738.3 | 752 | 812.8 | 749.8 | 743.7 | 699.8 | 702.2 | 742.4 | 724.5 | 747.7 | 777.6 | 750 | 750.8 | 745.2 | 735.1 | 754.9 | 748.3 | 760.5 | 683.4 | 709.4 | 730.2 | 747.5 | 740.9 | 739.9 | 745 | 736.7 | 735.6 | 740.2 | 700.5 | 706.3 | 745 | 739.1 | 725.8 | 738.8 | 731.6 | 730.6 | 729.7 | 611.4 | 738.5 | 748.8 | 728.5 | 733.6 | 687.1 | 742.5 | 798.4 | 721 | 719.9 | 736.3 | 738.3 | 731.8 | 726 | 741.1 | 740.4 | 707.2 | 773.2 | 692 | 637.6 | 740.2 | 694.8 | 807.1 | 835.2 | 831.8 | 0 | 840.3 | 845.5 | 732.6 | 734.4 | 735.3 | 724.5 | 785.1 | 762.3 | 699.4 | 654.9 | 669.8 | 659.2 | 661.1 | 663.2 | 660.3 | 662.6 | 672.3 | 678.5 | 669.9 | 670.7 | 672.1 | 677.8 | 629.2 | 577.7 | 695.9 | 674.8 | 676.9 | 677.4 | 673.2 | 671.6 | 675.3 | 669.9 | 678.2 | 663.5 | 679 | 663.9 | 667.3 | 639.6 | 635.1 | 644.9 | 720.5 | 700.1 | 637.4 | 732 | 735.3 | 739.1 | 767.7 | 745.9 | 816.9 | 754.1 | 703.3 | 707.8 | 667.6 | 729.2 | 678 | 768.9 | 642.3 | 643.7 | 714.1 | 613.5 | 571.7 | 751.8 | 738.3 | 752 | 743.4 | 736.7 | 732.5 | 808.8 | 804.5 | 700.6 | 714.1 | 647.8 | 646.8 | 646 | 668.7 | 652.7 | 667.7 | 652.8 | 644.6 | 645.7 | 639.9 | 656 | 663.3 | 655.8 | 666.2 | 661.5 | 642 | 640 | 678 | 645.7 | 656.3 | 641 | 665.9 | 674.5 | 667.6 | 668.5 | 671.4 | 663.7 | 669.9 | 673.5 | 698.7 | 723.9 | 722.8 | 702.8 | 748.8 | 786.3 | 746.7 | 746 | 720.6 | 749.1 | 738.6 | 717.3 | 785.3 | 750.5 | 679.1 | 770.2 | 766 | 584.8 | 578.2 | 747.9 | 622.4 | 715 | 667.2 | 658.8 | 654 | 656.1 | 640.7 | 656.5 | 660.1 | 649.9 | 646.5 | 675.2 | 732.1 | 669 | 670.1 | 643.4 | 634.3 | 625.7 | 654.1 | 666 | 659.5 | 659.4 | 664.4 | 712.7 | 658.3 | 655.6 | 661.1 | 663.3 | 604.7 | 665.8 | 679.1 | 644.8 | 635.8 | 622.3 | 709.9 | 643.7 | 672.6 | 667.6 | 664.1 | 635 | 595 | 649.7 | 690.5 | 631.2 | 640.3 | 685.9 | 658.9 | 673.9 | 664.4 | 664.7 | 648.2 | 711.1 | 633.4 | 640.6 | 567.8 | 653.1 | 659 | 628.1 | 672.3 | 682.7 | 685.6 | 675 | 674.2 | 681.3 | 666.8 | 678 | 685.2 | 667.3 | 650.9 | 659 | 682 | 604 | 643.3 | 656.9 | 715.5 | 668.1 | 656.8 | 655.3 | 699.1 | 684.4 | 709.7 | 634 | 674.8 | 635.9 | 642.5 | 617.4 | 649.9 | 658.9 | 639.8 | 0 | 31.02 | 0 | 0 | 2.97 | 2.76 | 0 | 0 | 86293160 | 256105 | 87636250 | 298973 | 71571280 | 150826 | 85926150 | 129297 | 814900 | 9990 | 96760 | 530 | 56550 | 188 | 57240 | 255 | 56030 | 181 | 55550 | 161 | 114000 | 0 | 110000 | 0 | 225370 | 224000 | 10.9333 | 2.97 | 2.76 |  | 31.02 | 0 | 229985.6
2025-04-30 | 2026 | 2025 |  |  | Apr-25 | 30 | 91870 | 4:53 | 17:16 | 571 | 553.7 | 603.8 | 602.7 | 603.5 | 584.5 | 612 | 588.4 | 610.4 | 612.5 | 611 | 609.5 | 610.7 | 612.2 | 617.2 | 614.6 | 576.5 | 580.4 | 605.2 | 613.2 | 629.3 | 623.1 | 628.1 | 627.4 | 623.4 | 618.2 | 626 | 623.4 | 628.1 | 628.8 | 621 | 624 | 602.2 | 566.6 | 568 | 574.3 | 580.1 | 583.2 | 606 | 575.3 | 592.7 | 643.9 | 681.1 | 643.4 | 643.9 | 666.4 | 716.2 | 708.6 | 765.3 | 673.4 | 645.1 | 634.7 | 630.9 | 662.9 | 651.2 | 655.4 | 679.9 | 622.5 | 548.2 | 625.6 | 604.5 | 565.7 | 626.5 | 1443.7 | 1416.3 | 1411.8 | 1426.2 | 1448.7 | 1419.8 | 1411.4 | 1438 | 1456.3 | 1418.7 | 1402.9 | 1418.4 | 1370.1 | 1350.2 | 1425.2 | 1440.4 | 1430.6 | 1422.5 | 1509.2 | 1454.5 | 1388.1 | 1464.1 | 1381 | 1385.3 | 1430.8 | 1430.7 | 1421 | 1426.3 | 1416.3 | 1442.6 | 1441.6 | 1446.7 | 1461 | 1579 | 1446.7 | 1445 | 1379.7 | 1372.9 | 1451 | 1412 | 1456.9 | 1518.2 | 1462.1 | 1467.9 | 1455.9 | 1443.4 | 1474.2 | 1462.9 | 1484.2 | 1332.6 | 1378.7 | 1433.9 | 1459.5 | 1453.1 | 1453.2 | 1458.8 | 1445.9 | 1440.6 | 1451.1 | 1375.4 | 1387.8 | 1457.2 | 1445.8 | 1422.8 | 1444.3 | 1436.1 | 1435.7 | 1433.4 | 1195.4 | 1445.4 | 1467.5 | 1431.2 | 1438.9 | 1343.3 | 1467.7 | 1569.7 | 1434.2 | 1426.7 | 1454.6 | 1459.8 | 1446 | 1441.5 | 1452 | 1462.2 | 1399.8 | 1526.7 | 1366.4 | 1256 | 1460.4 | 1364.4 | 1514.6 | 1559.9 | 1615.6 | 0 | 1622.9 | 1608.6 | 1441.1 | 1443.7 | 1445.2 | 1421.5 | 1527.7 | 1487.4 | 1374 | 1294.8 | 1316.4 | 1305.9 | 1304.8 | 1306.9 | 1306 | 1313.5 | 1331.4 | 1335.4 | 1317.3 | 1318.5 | 1317.3 | 1326 | 1240.8 | 1132.6 | 1356.9 | 1323.7 | 1326.4 | 1331.1 | 1329.7 | 1320 | 1333 | 1312.8 | 1335.7 | 1302 | 1332.6 | 1303 | 1315.6 | 1259.3 | 1251.5 | 1263.5 | 1426.7 | 1387.7 | 1261.2 | 1448 | 1453.8 | 1460.4 | 1517.2 | 1475.4 | 1607.7 | 1421.1 | 1383.3 | 1399.1 | 1318.9 | 1437 | 1383 | 1514.2 | 1263.1 | 1273.9 | 1408.8 | 1212.5 | 1137.8 | 1454.9 | 1462.5 | 1484 | 1473.2 | 1449.8 | 1437.9 | 1602.2 | 1589 | 1369.6 | 1387.3 | 1260.8 | 1267 | 1257.4 | 1311.9 | 1272.8 | 1307.4 | 1271.3 | 1258.2 | 1258.3 | 1254.9 | 1301.1 | 1300.8 | 1295.5 | 1305.5 | 1275.8 | 1276 | 1235.3 | 1321.2 | 1254.9 | 1290.9 | 1268 | 1300.8 | 1313 | 1307.3 | 1307.4 | 1321.8 | 1311 | 1312.2 | 1322.6 | 1372.7 | 1422.3 | 1388.4 | 1383.7 | 1464.8 | 1535.4 | 1455.2 | 1459.1 | 1409.5 | 1464 | 1447.2 | 1400.3 | 1529.4 | 1481.4 | 1327.8 | 1493 | 1498.5 | 1144.4 | 1129.9 | 1458.7 | 1214.6 | 1349 | 1292.8 | 1279.9 | 1281.5 | 1285.6 | 1248.5 | 1268.7 | 1286.6 | 1262.9 | 1258.1 | 1312.1 | 1421.4 | 1303.6 | 1302.3 | 1244.1 | 1219.7 | 1221 | 1276.9 | 1292.6 | 1282.3 | 1289.1 | 1288.5 | 1426 | 1277.8 | 1274.2 | 1294.9 | 1281.8 | 1174.8 | 1293.3 | 1317.8 | 1252.7 | 1232.6 | 1235.3 | 1407.2 | 1238.9 | 1299.8 | 1295.1 | 1292 | 1225.7 | 1151.8 | 1277.6 | 1337.9 | 1225.1 | 1229.3 | 1307.9 | 1279.6 | 1280.5 | 1277.1 | 1278.4 | 1275.4 | 1363.1 | 1215.4 | 1240.9 | 1231.8 | 1256.3 | 1258 | 1242.9 | 1293.1 | 1315.8 | 1315.3 | 1303.9 | 1306 | 1312.6 | 1294.2 | 1313.7 | 1320.9 | 1300 | 1255.9 | 1257 | 1315.9 | 1170.8 | 1248.5 | 1262.6 | 1380.1 | 1294.6 | 1294.3 | 1268.6 | 1360.4 | 1326.3 | 1375 | 1231.5 | 1315.9 | 1231.9 | 1236.9 | 1195.5 | 1249.3 | 1263.7 | 1261.6 | 0 | 36.85 | 0 | 0 | 6.05 | 5.76 | 0 | 0 | 86403340 | 256319 | 87748670 | 299261 | 71681530 | 151028 | 86035560 | 129456 | 816000 | 10000 | 97850 | 540 | 110180 | 214 | 112420 | 288 | 110250 | 202 | 109410 | 159 | 220000 | 2000 | 218000 | 2000 | 442260 | 438000 | 12.3833 | 6.05 | 5.76 |  | 36.85 | 0 | 449792.7
2025-05-01 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 5:08 | 17:16 | 193 | 186.7 | 205.1 | 204.9 | 203.6 | 195.1 | 208.5 | 199.5 | 207.4 | 208 | 207.1 | 206 | 207.7 | 207.8 | 210 | 208.6 | 195.3 | 199.1 | 208.9 | 210.4 | 217.6 | 215.5 | 217.6 | 215.7 | 216.9 | 213.9 | 218.5 | 217.2 | 219.5 | 219.3 | 216 | 216.3 | 205.5 | 191.9 | 192.6 | 195.2 | 197.3 | 196.6 | 204.9 | 196.5 | 200.3 | 221.4 | 233.5 | 218.6 | 221.3 | 229 | 247 | 245 | 262.2 | 234 | 223.4 | 219.4 | 216.6 | 229.1 | 225.4 | 227 | 236.8 | 216.8 | 190.3 | 217.4 | 206 | 196 | 213.4 | 496.8 | 486.5 | 488.1 | 490.5 | 499.5 | 489 | 485.4 | 494.9 | 501.5 | 486.2 | 484.3 | 485.5 | 469.5 | 462 | 490.8 | 496.7 | 495.5 | 489.8 | 520 | 500.5 | 477.3 | 505.6 | 480.7 | 477 | 494.4 | 495.6 | 488.7 | 490.4 | 484.2 | 491.8 | 493.9 | 496.6 | 503.6 | 545 | 501.4 | 497.2 | 470.6 | 470 | 498.1 | 484.3 | 501.9 | 505.6 | 501.8 | 505.6 | 499.9 | 494.1 | 508.9 | 504.3 | 510.3 | 458.2 | 475.6 | 493.2 | 506.4 | 501.4 | 501.1 | 504.5 | 497.8 | 497.1 | 500.5 | 472.4 | 476.6 | 504.3 | 500.3 | 489.9 | 499.8 | 471.3 | 492 | 490.6 | 412.9 | 498 | 505 | 492.2 | 494.7 | 464.5 | 508 | 545.5 | 492.3 | 492.3 | 501.7 | 502.8 | 498.9 | 495 | 504.5 | 502.2 | 478.7 | 521.9 | 465.8 | 428.7 | 503.4 | 468.7 | 543.8 | 545.4 | 558.3 | 0 | 564.5 | 568.5 | 490.8 | 492.7 | 492.2 | 486.4 | 531.2 | 515.8 | 469.5 | 444.1 | 454.8 | 449 | 449.4 | 452.1 | 450.2 | 452.3 | 459.1 | 461.7 | 455.3 | 454 | 455.8 | 461.6 | 427 | 392 | 471.2 | 459.2 | 458.7 | 459.9 | 458.7 | 456.1 | 459.5 | 453.3 | 458.5 | 447.3 | 458.6 | 447.1 | 452.3 | 432.8 | 428.9 | 438.1 | 486.1 | 474.7 | 432.7 | 496.1 | 497.2 | 499 | 521.7 | 507.5 | 554.8 | 511.4 | 477.1 | 468 | 453.6 | 494.1 | 479 | 518.9 | 433 | 434.1 | 481.5 | 415 | 386 | 506.7 | 494.9 | 507.3 | 499.9 | 497.3 | 495.1 | 545.3 | 538.6 | 468 | 478.5 | 433.6 | 429.3 | 413.4 | 447.4 | 397.1 | 432.5 | 438.3 | 432.3 | 432.7 | 356.3 | 275.2 | 445.9 | 273.3 | 450 | 446.6 | 449 | 422.6 | 450.7 | 431.9 | 439.6 | 444 | 444.7 | 454 | 448.8 | 338.7 | 422.3 | 399.9 | 449.1 | 448.5 | 466.8 | 482.8 | 485.5 | 470.7 | 501.5 | 527 | 485.6 | 498.6 | 480.2 | 499.7 | 494.6 | 478.5 | 524.9 | 509.1 | 453.8 | 517.8 | 514.5 | 390.2 | 385.2 | 499.1 | 415.9 | 476.8 | 443.4 | 437.9 | 437 | 440.5 | 429.8 | 436.7 | 439.1 | 433.3 | 431.8 | 450.1 | 486.1 | 446.1 | 445.6 | 428.5 | 421.4 | 417.5 | 436.7 | 443.5 | 441.4 | 443.2 | 444.1 | 485 | 438.3 | 437.7 | 440.1 | 441.5 | 402.3 | 443.2 | 455 | 428.8 | 422.6 | 304.1 | 402.3 | 429.7 | 445.8 | 445.5 | 444.1 | 424.1 | 397.7 | 322.8 | 453.8 | 418.4 | 424.6 | 459.2 | 416.6 | 450.9 | 447.6 | 431.1 | 263.6 | 478 | 427.2 | 417.9 | 194.7 | 422.4 | 448 | 270.2 | 439.2 | 446.5 | 447.4 | 442.8 | 442.7 | 446.1 | 438 | 446 | 451 | 439.8 | 427.7 | 429 | 448.3 | 395.4 | 423 | 431.1 | 467.8 | 436.8 | 437.6 | 427.2 | 461.2 | 448.2 | 465.8 | 417.6 | 443.3 | 418.2 | 428.7 | 404.5 | 427.4 | 432.7 | 428.2 | 0 | 29.4 | 0 | 0 | 1.99 | 1.84 | 0 | 0 | 86441450 | 256532 | 87787320 | 299572 | 71718170 | 151204 | 86071260 | 129654 | 816380 | 10010 | 98210 | 540 | 38110 | 213 | 38650 | 311 | 36640 | 176 | 35700 | 198 | 76000 | 2000 | 72000 | 0 | 149100 | 148000 | 12.1333 | 1.99 | 1.84 |  | 29.4 | 0 | 152874.6
2025-05-02 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 5:03 | 17:21 | 504 | 491.2 | 535.3 | 535.8 | 530.1 | 514.9 | 542.5 | 519.7 | 537.4 | 538.5 | 540.9 | 538.2 | 537.4 | 538.1 | 543.1 | 541.4 | 507.9 | 510.4 | 533.6 | 540.7 | 554.3 | 548.5 | 554.7 | 550 | 548.3 | 544.4 | 551.8 | 544.4 | 553.3 | 553.9 | 547.3 | 550.3 | 526.6 | 495.4 | 498.8 | 503.4 | 510.2 | 513.5 | 530 | 507.1 | 522.1 | 562.6 | 586.7 | 563.6 | 563.5 | 579.6 | 608.4 | 604 | 634.8 | 586.4 | 563.3 | 555.5 | 552.5 | 577.8 | 570.6 | 560.3 | 592.7 | 548.6 | 483 | 549.8 | 534.6 | 499 | 546.1 | 1215.9 | 1205.2 | 1243.5 | 1226.1 | 1211.5 | 1235.3 | 1189.6 | 1246.4 | 1211.1 | 1196 | 1174.7 | 1193.8 | 1178.4 | 1170.5 | 1181.2 | 1179.1 | 1256.9 | 1187 | 1250.3 | 1249.9 | 1168.6 | 1203.2 | 1185.4 | 1153.6 | 1186.6 | 1187 | 1219.4 | 1214.8 | 1182.6 | 1199.5 | 1235.3 | 1242.9 | 1203.7 | 1284.4 | 1254.1 | 1205.6 | 1161 | 1169.8 | 1211.9 | 1216 | 1206.1 | 1282.7 | 1206.8 | 1239.8 | 1203.7 | 1209.4 | 1241.8 | 1236.5 | 1233.1 | 1154.2 | 1129.8 | 1206.6 | 1206.2 | 1168.2 | 1224.5 | 1220 | 1249.8 | 1227.2 | 1225.8 | 1167.7 | 1187.1 | 1279.3 | 1271.5 | 1250.7 | 1271.3 | 1187.5 | 1211.8 | 1207.4 | 1050.9 | 1197.3 | 1234.7 | 1205.7 | 1209.2 | 1177.4 | 1230 | 1292.9 | 1215 | 1243.7 | 1212.6 | 1218 | 1276.5 | 1217.6 | 1216 | 1218.1 | 1220 | 1290.4 | 1184.1 | 1089 | 1212.7 | 1152 | 1253.8 | 1269.1 | 1316.6 | 0 | 1293.3 | 1304.6 | 1216.5 | 1210.9 | 1221.9 | 1249.2 | 1251.2 | 1228.7 | 1156.5 | 1106.3 | 1116.6 | 1107.4 | 1106.7 | 1099.6 | 1107.5 | 1112.4 | 1121.2 | 1123.9 | 1115.2 | 1115.3 | 1116.7 | 1121.9 | 1075.8 | 1002.8 | 1129.9 | 1119.5 | 1117.8 | 1123.6 | 1120 | 1113.5 | 1118.7 | 1109.5 | 1120.1 | 1102.2 | 1118.1 | 1099.5 | 1106.4 | 1077 | 1072 | 1077 | 1210.4 | 1208.9 | 1129.5 | 1224.3 | 1217.1 | 1277 | 1270.2 | 1189.7 | 1403 | 1250 | 1170 | 1183.4 | 1179.9 | 1244.5 | 1187 | 1280 | 1098.2 | 1123.5 | 1156.5 | 1083.5 | 1016.5 | 1229 | 1226.6 | 1258 | 1254.2 | 1238.2 | 1267.7 | 1332.6 | 1329.6 | 1129.5 | 1139.3 | 1072.3 | 1061 | 1060.6 | 1091.1 | 1076 | 1095.5 | 1084.8 | 1072.8 | 1072.2 | 1070 | 1099.9 | 1095.7 | 1097.5 | 1099.9 | 1085.1 | 1081 | 1059.2 | 1101.5 | 1073 | 1094.9 | 269 | 278.3 | 1102.3 | 1098.1 | 1113.1 | 1151.6 | 1102.6 | 1103.8 | 1108.9 | 1175.9 | 1170.8 | 1225.4 | 1164.3 | 1174.8 | 1263.4 | 1211.6 | 1221.5 | 1195.3 | 1260.2 | 1215.2 | 1191.6 | 1260.5 | 1226 | 1156.8 | 1226.6 | 1276.8 | 1001.8 | 988.3 | 1207.6 | 1062 | 1183.6 | 1077.2 | 1074.9 | 1075.3 | 1074.9 | 1059.3 | 1056.3 | 1079.5 | 1061.3 | 1061.2 | 1089.8 | 1163 | 1087.8 | 1088 | 1052.9 | 1038.1 | 1039 | 1073.4 | 1083.6 | 1076.5 | 1078.2 | 1082 | 1161 | 1079.3 | 1073.1 | 1086.9 | 1078.7 | 1014.2 | 1085.9 | 1087.1 | 1065.1 | 1053.8 | 1049.6 | 1179.9 | 1042.4 | 1075.5 | 1074.3 | 1078.9 | 1034 | 986.9 | 1076.2 | 1120.8 | 1031.2 | 1031.7 | 1077.6 | 1067 | 1065.9 | 1063 | 1062.9 | 1071.5 | 1115.1 | 1024.2 | 1042.9 | 1057.3 | 1057.8 | 1059 | 1058.4 | 1069 | 1087.6 | 1080.5 | 1085.5 | 1078 | 1088.8 | 1079.1 | 1087 | 1092.6 | 1084 | 1054.4 | 1059 | 1090.6 | 1001.1 | 1047.6 | 1056.4 | 1127.4 | 1073.7 | 1073.9 | 1053 | 1120.2 | 1086.2 | 1116.3 | 1033 | 1083.1 | 1034.7 | 1040.5 | 1015.5 | 1044 | 1054.3 | 1056.7 | 0 | 35.56 | 0 | 0 | 5.32 | 5.07 | 0 | 0 | 86535490 | 256750 | 87882370 | 299874 | 71810300 | 151393 | 86163280 | 129856 | 817320 | 10010 | 99130 | 550 | 94040 | 218 | 95050 | 302 | 92130 | 189 | 92020 | 202 | 188000 | 0 | 184000 | 2000 | 373240 | 372000 | 12.3 | 5.32 | 5.07 |  | 35.56 | 0 | 379071.8
2025-05-03 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:59 | 17:25 | 579.9 | 566.8 | 618 | 620.1 | 613.9 | 594.9 | 629.7 | 602.4 | 622.6 | 626.9 | 630 | 626.6 | 629.7 | 629.7 | 636.6 | 638.3 | 594.1 | 596.6 | 621.7 | 630.7 | 651.7 | 642.6 | 652 | 647.7 | 643.9 | 641.3 | 649.6 | 646.7 | 653.1 | 652.7 | 645.5 | 649.7 | 621 | 581.3 | 585.1 | 591.2 | 601.8 | 605.5 | 626.8 | 599.4 | 619.8 | 670.6 | 702.4 | 669.5 | 670.5 | 237.9 | 735.2 | 728.7 | 766.3 | 702.2 | 672 | 663.4 | 659.6 | 690.1 | 680 | 664.3 | 703.6 | 648 | 568.5 | 653.6 | 635.3 | 590.8 | 651.1 | 1458 | 1433.2 | 1459.1 | 1456.4 | 1432.6 | 1447 | 1412.4 | 1474.4 | 1431.7 | 1409.8 | 1375.3 | 1403.5 | 1375.9 | 1363.3 | 1442.3 | 1470 | 1505.7 | 1421.6 | 1508.1 | 1513.2 | 1412.1 | 1441.7 | 1431.2 | 1423 | 1419.6 | 1484.1 | 1466.5 | 1453.1 | 1390.3 | 1402.7 | 1431.4 | 1454.7 | 1417 | 1512.4 | 1460.9 | 1432.7 | 1371.1 | 1376.4 | 1446.4 | 1441.7 | 1421.3 | 1521 | 1418.2 | 1465.6 | 1418.6 | 1424.7 | 1467.7 | 1470 | 1460.2 | 1370.7 | 1350.4 | 1428.4 | 1442.9 | 1443.4 | 1480.1 | 1533.9 | 1518.1 | 1475.9 | 1446 | 1410.1 | 1435.9 | 1526.7 | 1518.2 | 1497.5 | 1521 | 1481 | 1471.6 | 1459.5 | 1249.8 | 1439.9 | 1486.8 | 1456.6 | 1427.6 | 1409.4 | 1443.3 | 1506.1 | 1436.3 | 1475.9 | 1429.2 | 1449.3 | 1504.4 | 1459.9 | 1484.8 | 1421.6 | 1459.3 | 1555.2 | 1419 | 1311.3 | 1453 | 1385.7 | 1461.9 | 1495 | 1544.8 | 0 | 1551.8 | 1521.4 | 1467.4 | 1453.9 | 1438.8 | 1487 | 1487 | 1459 | 1424.2 | 1320.9 | 1335.7 | 1327.2 | 1326.9 | 1314.2 | 1330.6 | 1337.7 | 1347.1 | 1354.8 | 1343.3 | 1333.4 | 1341.4 | 1354.8 | 1288.2 | 1184.2 | 1367.4 | 1351.6 | 1352.6 | 1358.6 | 1355.7 | 1350.6 | 1359.2 | 1342.6 | 1358.1 | 1331.9 | 1355.5 | 1338 | 1350.7 | 1304.9 | 1299.8 | 1305.6 | 1433.1 | 1431.2 | 1317.3 | 1444.2 | 1453 | 1493.2 | 1499.8 | 1455.4 | 1640.6 | 1428 | 1365.5 | 1386.5 | 1361.8 | 1452.2 | 1380 | 1504.5 | 1326 | 1323.3 | 1429.3 | 1262.5 | 1177.2 | 1469.8 | 1454.9 | 1477.6 | 1464.4 | 1466.3 | 1464.9 | 1579.6 | 1569.2 | 1371.6 | 1373.4 | 1306.9 | 1250 | 1296.4 | 1339.9 | 1319.5 | 1344.5 | 1315 | 1301.4 | 1308.1 | 1303.9 | 1330 | 1340.4 | 1321 | 1339.5 | 1304.5 | 1309 | 1262.8 | 1318.5 | 1286 | 1311.7 | 277 | 286.4 | 1345.4 | 1332.5 | 1329.2 | 1366.8 | 1331.1 | 1340.5 | 1339.8 | 1435 | 1431 | 1478.1 | 1420.7 | 1438.6 | 1529.3 | 1425.1 | 1459.5 | 1454.1 | 1532.2 | 1477.7 | 1443 | 1512.9 | 1483.6 | 1403.7 | 1464.8 | 1539.3 | 1193.3 | 1179.7 | 1450.5 | 1269.3 | 1432 | 1345.9 | 1349.4 | 1354 | 1346.3 | 1317.6 | 1311.8 | 1354 | 1324.1 | 1334.4 | 1363.4 | 1441.8 | 1368.8 | 1364.7 | 1298 | 1295.5 | 1305.7 | 1348.1 | 1359.6 | 1348.2 | 1344.7 | 1353.4 | 1440 | 1346.1 | 1349.2 | 1350.5 | 1347.2 | 1264.5 | 1361.4 | 1348.1 | 1329.3 | 1308.3 | 1314.4 | 1418.5 | 1314 | 1355.8 | 1353.8 | 1347.2 | 1294.1 | 1215.3 | 1307.2 | 1384.5 | 1292.9 | 1287.6 | 1359.3 | 1335.5 | 1330.8 | 1342.8 | 1335.4 | 1325.5 | 1399.4 | 1290.9 | 1304.4 | 1296 | 1325.8 | 1304 | 1298 | 1356.3 | 1381.4 | 1369 | 1373.8 | 1358.2 | 1374.7 | 1356.7 | 1324.2 | 1374.2 | 1361.6 | 1320 | 1318 | 1370.8 | 1240.9 | 1308 | 1324.8 | 1398.8 | 1363.2 | 1360.4 | 1328.1 | 1397.3 | 1365.4 | 1403.4 | 1295.4 | 1361.7 | 1296.3 | 1298.8 | 1258.7 | 1306.6 | 1324.8 | 1325.9 | 0 | 39.53 | 0 | 0 | 6.66 | 6.3 | 0 | 0 | 86646310 | 256956 | 87996150 | 300183 | 71919740 | 151591 | 86277510 | 130033 | 818440 | 10020 | 100240 | 550 | 110820 | 206 | 113780 | 309 | 109440 | 198 | 114230 | 177 | 224000 | 2000 | 222000 | 0 | 448270 | 446000 | 12.4333 | 6.66 | 6.3 |  | 39.53 | 0 | 457274.0003
2025-05-04 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:58 | 17:23 | 564.4 | 551.9 | 600.8 | 602 | 596.6 | 578.2 | 610.4 | 583 | 601.7 | 605.8 | 606.9 | 603.4 | 605.6 | 603.5 | 609 | 606.1 | 571.5 | 571.5 | 597.6 | 605.3 | 623 | 614.5 | 620.9 | 614.9 | 615.2 | 612.6 | 617.7 | 613.7 | 621 | 620.6 | 612.3 | 615.7 | 594.5 | 559.4 | 563.9 | 566.7 | 574.4 | 573.5 | 596.7 | 568.1 | 587.3 | 638.7 | 673.2 | 636.9 | 632.7 | 654.6 | 701.2 | 689.2 | 739.9 | 657.1 | 627.6 | 617 | 612.3 | 642.5 | 635.3 | 635.9 | 666.8 | 612.9 | 538.2 | 615.6 | 595.8 | 554.2 | 607.6 | 1421.3 | 1401.9 | 1406.9 | 1427.6 | 1430.3 | 1418.6 | 1389.1 | 1431.6 | 1428.4 | 1400.6 | 1370.8 | 1397.9 | 1357.1 | 1340.7 | 1397.9 | 1408.2 | 1412 | 1386.2 | 1462.6 | 1428 | 1361.7 | 1415.9 | 1372 | 1355.1 | 1394.2 | 1422.4 | 1408 | 1412.8 | 1389.7 | 1425.3 | 1432.1 | 1449.7 | 1431.5 | 1532.3 | 1423.4 | 1423.7 | 1380.3 | 1363.7 | 1435.1 | 1397.9 | 1432.9 | 1474.5 | 1433.4 | 1464.5 | 1425.2 | 1437.6 | 1467.2 | 1456.2 | 1462.3 | 1298.4 | 1337.7 | 1402.6 | 1407.9 | 1369.8 | 1420.7 | 1388.2 | 1425.9 | 1408.1 | 1380.3 | 1339.4 | 1356.8 | 1417.7 | 1408.8 | 1387.5 | 1411.4 | 1400.8 | 1390.5 | 1384.9 | 1163.5 | 1385 | 1416.4 | 1382.5 | 1388.6 | 1277.2 | 1423.6 | 1501.6 | 1398 | 1405 | 1403.9 | 1412.8 | 1418.7 | 1406.1 | 1428.5 | 1385.4 | 1369.5 | 1484.7 | 1335.1 | 1230 | 1411.4 | 1320.7 | 1341 | 1398.8 | 1370.7 | 1321 | 1407.7 | 1366 | 1396 | 1393.3 | 1362.6 | 1389 | 1449.1 | 1415.5 | 1340.7 | 1273 | 1287.9 | 1276.1 | 1269.7 | 1260.6 | 1275.7 | 1283.1 | 1297.6 | 1300.6 | 1282.5 | 1282.5 | 1283.3 | 1293.7 | 1214.2 | 1108.2 | 1310.9 | 1290.1 | 1287.9 | 1297.6 | 1296.3 | 1283.4 | 1294.2 | 1276.3 | 1296.2 | 1265.8 | 1296.2 | 1265.9 | 1279.2 | 1225 | 1219.3 | 1224.6 | 1389.9 | 1365.6 | 1242.4 | 1408.8 | 1416.5 | 1433.4 | 1466.2 | 1428.2 | 1582.8 | 1437.2 | 1340.7 | 1377.8 | 1305.5 | 1410.1 | 1312 | 1471.5 | 1231.8 | 1259 | 1373.7 | 1192.2 | 1114.8 | 1440.1 | 1399.5 | 1465.1 | 1434 | 1411 | 1412.4 | 1540.1 | 1522.7 | 1322 | 1322.1 | 1218.4 | 1206.8 | 1211.2 | 1257.3 | 1231.4 | 1259.1 | 1235.7 | 1211.8 | 1212.6 | 1217.8 | 1271.1 | 1258.5 | 1263.6 | 1265.3 | 1235.7 | 1201 | 1194.4 | 1264.5 | 1186.5 | 1231.4 | 756.4 | 798 | 1265.8 | 1260.3 | 1278.6 | 1288.5 | 1270.1 | 1273.2 | 1279.3 | 1310.9 | 1337.3 | 1354.2 | 1340.7 | 1407.7 | 1460.9 | 1392.9 | 1411 | 1367.7 | 1424.3 | 1399.2 | 1356.5 | 1450.6 | 1410.2 | 1297 | 1413.6 | 1461 | 1111.4 | 1097 | 1394.4 | 1178.8 | 1344.4 | 1243.7 | 1241.9 | 1241.7 | 1241.9 | 1201.2 | 1214.3 | 1247.3 | 1215.7 | 1213.4 | 1258.9 | 1354.8 | 1258.6 | 1263.1 | 1200.1 | 1172 | 1177.7 | 1236.1 | 1249.4 | 1242 | 1242.7 | 1251.5 | 1349 | 1241.6 | 1232.8 | 1257 | 1241.2 | 1137 | 1251.4 | 1258.4 | 1212.2 | 1194.2 | 1212.2 | 1341.2 | 1197.9 | 1248 | 1249.8 | 1245.6 | 1181 | 1105.7 | 1241.2 | 1292.3 | 1177.9 | 1174.8 | 1251 | 1236.8 | 1219.9 | 1235.6 | 1234.2 | 1240.9 | 1313.1 | 1172 | 1191.9 | 1216.9 | 1216.6 | 1219 | 1219.7 | 1229.1 | 1261.4 | 1248.6 | 1260.8 | 1245.9 | 1263.5 | 1252.9 | 1206.2 | 1273.5 | 1258.7 | 1204.8 | 1212 | 1269 | 1130.6 | 1197.9 | 1212.8 | 1301.2 | 1246.1 | 1249.1 | 1207.1 | 1305.8 | 1261.1 | 1314.5 | 1181.4 | 1260.2 | 1254 | 1186.2 | 1149.8 | 1207.7 | 1212.4 | 1215.6 | 0 | 39.96 | 0 | 0 | 6.23 | 5.84 | 0 | 0 | 86754680 | 257155 | 88105410 | 300469 | 72025860 | 151724 | 86383380 | 130209 | 819510 | 10020 | 101300 | 560 | 108370 | 199 | 109260 | 286 | 106120 | 133 | 105870 | 176 | 214000 | 0 | 212000 | 2000 | 429620 | 426000 | 12.4167 | 6.23 | 5.84 |  | 39.96 | 0 | 436792.9
2025-05-05 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:53 | 17:15 | 469.1 | 462.1 | 501.8 | 503.3 | 499.3 | 482.2 | 508.6 | 488.1 | 504.4 | 507.5 | 505.7 | 504.1 | 507.8 | 507.2 | 511.8 | 510.7 | 478.4 | 480.9 | 500.2 | 507.7 | 520.7 | 515.6 | 521.3 | 520.2 | 514.7 | 511.1 | 520 | 517.9 | 520.8 | 521.7 | 514.6 | 519 | 500.9 | 470.7 | 473 | 477 | 483.3 | 483.6 | 502.4 | 479.3 | 494.8 | 537.6 | 565 | 534.1 | 535.3 | 552.1 | 589.9 | 583.6 | 618.1 | 558.5 | 535.8 | 527.6 | 523.9 | 547.5 | 540.2 | 538 | 565.1 | 520.8 | 456.7 | 522 | 502.3 | 470.7 | 519.1 | 1172.4 | 1153.7 | 1169 | 1176.5 | 1168.5 | 1176.3 | 1144.6 | 1188.1 | 1169.6 | 1150.3 | 1130.7 | 1150.6 | 1128.3 | 1091.8 | 1139.2 | 1174.6 | 1187.6 | 1148.3 | 1215.6 | 1200.1 | 1129.7 | 1170.3 | 1141 | 1117.4 | 1153.5 | 1184.4 | 1170.4 | 1166 | 1124.5 | 1151.7 | 1166.6 | 1179.9 | 1156.6 | 1239.1 | 1159.9 | 1157.8 | 1113.3 | 1113.2 | 1171.4 | 1153 | 1163.2 | 1229.1 | 1164 | 1193.7 | 1162.7 | 1164.2 | 1196.9 | 1193 | 1168.6 | 1084.1 | 1102.3 | 1144.4 | 1142.1 | 1145.5 | 1181.6 | 1120 | 1198 | 1178.1 | 1146.9 | 1127.3 | 1142.1 | 1209 | 1201.5 | 1181.6 | 1202.4 | 1115.2 | 1176.2 | 1170 | 993.1 | 1168 | 1199.7 | 1171.7 | 1158.6 | 1102.5 | 1189.9 | 1258.9 | 1173.6 | 1185.1 | 1176.6 | 1189.8 | 1177.9 | 1185.3 | 1206.6 | 1158.8 | 1164.8 | 1253.2 | 1134.6 | 1047.3 | 1190.2 | 1122.3 | 1119 | 1181 | 1183.9 | 1107.4 | 1150.9 | 1143.1 | 1142 | 1175.7 | 1182.3 | 1179.4 | 1228.5 | 1202.7 | 1138.2 | 1070.7 | 1084 | 1074.3 | 1072.4 | 1065.4 | 1074.3 | 1079.1 | 1088.7 | 1091.8 | 1081.6 | 1084.3 | 1082.2 | 1091.3 | 1033.8 | 947.1 | 1099.2 | 1087.4 | 1085.5 | 1091.9 | 1091.6 | 1084.1 | 1092.5 | 1073.6 | 1089.9 | 1062.2 | 1088.8 | 1069.9 | 1082.3 | 1040.3 | 1034.4 | 1046.8 | 1161.2 | 1152.3 | 1051.1 | 1179.5 | 1190.7 | 1218.5 | 1227.5 | 1196.1 | 1340.3 | 1187.7 | 1129.6 | 1162.5 | 1089.2 | 1188.4 | 1094 | 1235.5 | 1049.2 | 1047 | 1164.8 | 1012 | 949.2 | 1190 | 1180.1 | 1244.8 | 1202.8 | 1179.2 | 1193 | 1291.9 | 1261.2 | 1111.6 | 1119.9 | 1038.3 | 1038 | 1033.8 | 1066.9 | 1043.2 | 1065.6 | 1052.9 | 1032.5 | 1031.9 | 1029.1 | 1055.8 | 1065.4 | 1053.7 | 1070.2 | 1054.1 | 1028 | 1024.4 | 1076 | 1037.8 | 1067.4 | 638.2 | 665.4 | 1069.1 | 1059.2 | 1065 | 1093.7 | 1070.9 | 1071.6 | 1072 | 1097.4 | 1158.3 | 1146.8 | 1125.2 | 1162.4 | 1229 | 1176 | 1187.9 | 1155.2 | 1212.3 | 1178.2 | 1150.9 | 1226.5 | 1179.7 | 1107.4 | 1200.1 | 1232.5 | 948 | 934.4 | 1172.6 | 1006 | 1141.1 | 1046.7 | 1045 | 1046.9 | 1049.4 | 1029.6 | 1031.4 | 1050.2 | 1034.9 | 1031.4 | 1066.1 | 1131.9 | 1063.3 | 1066.9 | 1023.4 | 1006.2 | 1008.5 | 1049.8 | 1059.6 | 1053.2 | 1052.7 | 1057.9 | 1131.2 | 1050.3 | 1048 | 1065 | 1054.8 | 974.1 | 1061.8 | 1067.1 | 1033.2 | 1020.2 | 1015.8 | 1131.9 | 1013.5 | 1052.8 | 1053.8 | 1053.4 | 1010.1 | 951.6 | 1046.7 | 1088.9 | 1001.1 | 1001.1 | 1061.4 | 1046.7 | 1040.5 | 1053.4 | 1042.9 | 1038.1 | 1105 | 1006.6 | 1024 | 1002 | 1039 | 1023 | 1022.2 | 1047.9 | 1069.7 | 1065 | 1067.6 | 1040 | 1069.9 | 1057.9 | 1040.6 | 1074.1 | 1062.3 | 1028.3 | 1027.8 | 1072.8 | 967.2 | 1023.2 | 1035 | 1092.3 | 1057.5 | 1058.2 | 1027.4 | 1097.4 | 1067.3 | 1096.1 | 1006.7 | 1065.7 | 1008.5 | 1015.8 | 982.4 | 1025.3 | 1034.1 | 1035.1 | 0 | 36.63 | 0 | 0 | 5.26 | 4.93 | 0 | 0 | 86844690 | 257343 | 88197580 | 300747 | 72115360 | 151860 | 86472620 | 130364 | 820420 | 10030 | 102190 | 560 | 90010 | 188 | 92170 | 278 | 89500 | 136 | 89240 | 155 | 182000 | 2000 | 178000 | 0 | 360920 | 360000 | 12.3667 | 5.26 | 4.93 |  | 36.63 | 0 | 367064.7
2025-05-06 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 5:08 | 17:14 | 360.6 | 351.8 | 383.5 | 385.7 | 382.8 | 367.2 | 391.3 | 376.2 | 389.6 | 391.1 | 391.3 | 389.9 | 390.1 | 390.6 | 394.3 | 390.8 | 369.3 | 373.2 | 389.5 | 394.9 | 405.1 | 401.8 | 404.9 | 400.6 | 401.4 | 398.5 | 404.9 | 401.2 | 405.9 | 407.3 | 401 | 402 | 384.6 | 360.8 | 362 | 366.4 | 370.8 | 368.6 | 384.8 | 366.9 | 377 | 412.6 | 436.2 | 411 | 411.4 | 426.2 | 454.5 | 449.9 | 480.9 | 427.7 | 408.8 | 401.7 | 398.7 | 416.5 | 412.8 | 416.4 | 435.4 | 397.8 | 351.9 | 399.2 | 385.4 | 361.2 | 395 | 919.5 | 904.4 | 907.1 | 911.5 | 923.5 | 906.3 | 905.3 | 924.8 | 929.6 | 902.6 | 890.5 | 896.1 | 860.9 | 850.7 | 902.6 | 922.4 | 922.2 | 906 | 959.3 | 900.4 | 882.6 | 925.6 | 887.4 | 878.3 | 908.4 | 917.5 | 910.1 | 913.1 | 894 | 910.8 | 914.1 | 917.2 | 923.4 | 999.9 | 925.1 | 914.7 | 869.3 | 866.1 | 920.7 | 898 | 921 | 959.2 | 921.8 | 933.1 | 923 | 916.5 | 939.3 | 931.4 | 942.9 | 852.5 | 877.8 | 913.2 | 926 | 888.4 | 924.9 | 933.5 | 923.4 | 915.7 | 920 | 872.8 | 884.3 | 923.7 | 912.1 | 901.7 | 911.1 | 880.9 | 898.3 | 891.3 | 749.2 | 900.6 | 914.7 | 894.9 | 887.3 | 842.9 | 926.6 | 987.7 | 901.3 | 906.6 | 914.4 | 917.8 | 908 | 907.5 | 920.2 | 913.4 | 874.5 | 948.5 | 851.4 | 783.1 | 913.6 | 851.2 | 901.5 | 906.5 | 900 | 857.1 | 908.9 | 910.4 | 893.6 | 899 | 865.9 | 885.7 | 958.6 | 929.6 | 854.7 | 816.9 | 828.8 | 818.6 | 817.7 | 818.8 | 819.6 | 822.6 | 834.1 | 835.2 | 829.7 | 831.2 | 829.9 | 837.4 | 784.1 | 716.7 | 852.9 | 834.6 | 834.9 | 840.2 | 832.8 | 831.9 | 833.2 | 826.7 | 835.1 | 817.1 | 829.2 | 805.6 | 817.4 | 783.6 | 775.7 | 789.9 | 905.5 | 888.8 | 806.8 | 920.4 | 928.3 | 939 | 960.3 | 938.4 | 1037.2 | 947 | 885.8 | 859.5 | 849.9 | 924.9 | 859 | 968.9 | 812.3 | 816.5 | 904.3 | 776.3 | 728.8 | 948.3 | 935.9 | 960.6 | 939.7 | 924.1 | 920.3 | 1020 | 1002 | 864.3 | 873 | 793.8 | 796.7 | 791.1 | 817.5 | 788.3 | 813 | 809.6 | 793.8 | 772.7 | 774.3 | 795.2 | 804.2 | 799.2 | 802.4 | 812.2 | 818 | 778.8 | 829 | 796.5 | 798 | 790.8 | 826 | 812.2 | 814.3 | 812.2 | 831.6 | 812 | 814 | 821.7 | 854.7 | 904.1 | 883.8 | 878.6 | 906.8 | 967.9 | 911.7 | 919.3 | 887 | 922.3 | 908.3 | 880.2 | 961.8 | 933.7 | 843.7 | 946.2 | 947.2 | 718 | 709.3 | 912.4 | 764.3 | 876.5 | 813.5 | 807.3 | 807.6 | 810 | 792.2 | 800.8 | 810.3 | 794.2 | 792.8 | 821.6 | 885.2 | 818.1 | 816.3 | 783.8 | 773.9 | 770.6 | 808.2 | 817 | 813 | 813.9 | 817.8 | 888 | 803.9 | 798.3 | 809.2 | 801.1 | 738 | 809.3 | 825.2 | 784.4 | 772.5 | 773.1 | 884.4 | 780.6 | 816.2 | 810.7 | 810.5 | 772.4 | 727.7 | 797.8 | 852.4 | 773.7 | 774 | 828.2 | 807.3 | 812.4 | 818.4 | 810 | 811.1 | 867 | 776 | 800.8 | 779.1 | 816.1 | 801 | 798.4 | 832 | 841.1 | 843.7 | 836.8 | 812 | 842.8 | 839.1 | 837.6 | 855.4 | 839.7 | 813.2 | 817 | 852.3 | 757.9 | 809.4 | 819.1 | 884.3 | 838.4 | 837.6 | 819.9 | 877.5 | 851.3 | 886 | 797.1 | 845.1 | 790.1 | 805 | 772.2 | 802 | 810.4 | 816 | 0 | 36.28 | 0 | 0 | 3.99 | 3.74 | 0 | 0 | 86915060 | 257549 | 88268700 | 301041 | 72185230 | 152015 | 86542460 | 130527 | 821120 | 10030 | 102880 | 560 | 70370 | 206 | 71120 | 294 | 69870 | 155 | 69840 | 163 | 140000 | 0 | 138000 | 0 | 281200 | 278000 | 12.1 | 3.99 | 3.74 |  | 36.28 | 0 | 285034.5
2025-05-07 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:48 | 17:24 | 468.2 | 456.3 | 498.6 | 498.4 | 490.4 | 470.6 | 507.2 | 482 | 496.9 | 500.9 | 504.9 | 500.5 | 500.2 | 500.7 | 505.5 | 506.5 | 474.1 | 479 | 501.4 | 507 | 522.8 | 516.7 | 521.7 | 518.5 | 517.7 | 515.2 | 521.9 | 518.5 | 526.2 | 525.5 | 518.1 | 520.3 | 489.5 | 459.1 | 465.2 | 467.9 | 476.4 | 477.7 | 492.2 | 473.3 | 487.5 | 529.5 | 556.2 | 525.2 | 527.5 | 544.5 | 588.2 | 580.9 | 629.2 | 558.3 | 531 | 522.5 | 518.7 | 544.3 | 539 | 545.7 | 565.6 | 519.3 | 457.2 | 522.7 | 503.1 | 470.7 | 512.6 | 1199.4 | 1177.5 | 1176 | 1190.6 | 1202.6 | 1178.5 | 1171.5 | 1193.2 | 1202.6 | 1172.2 | 1155.4 | 1169.7 | 1127.7 | 1110.1 | 1161.1 | 1206.6 | 1197.2 | 1184.2 | 1257.7 | 1160.9 | 1158 | 1218.6 | 1159.3 | 1154.4 | 1190.5 | 1192.2 | 1189.1 | 1190.2 | 1158.9 | 1188.9 | 1191.6 | 1206.4 | 1209.8 | 1306.9 | 1192.1 | 1202.5 | 1144.7 | 1132.9 | 1209.1 | 1172 | 1209.6 | 1238.2 | 1199.4 | 1219.8 | 1199.6 | 1198 | 1228.9 | 1220.4 | 1182.2 | 1109.2 | 1146.9 | 1193.6 | 1218.9 | 1173.4 | 1214.9 | 1211.2 | 1210.3 | 1195 | 1201.5 | 1142.7 | 1154.6 | 1203 | 1194.7 | 1178.6 | 1199.3 | 1195.3 | 1190.6 | 1185.3 | 1108.8 | 1194.1 | 1210.3 | 1181.1 | 1181.2 | 1106.8 | 1204.1 | 1285.2 | 1167.2 | 1163.9 | 1187.4 | 1190 | 1180.2 | 1177.8 | 1200 | 1196.7 | 1144.1 | 1247.1 | 1119.4 | 1035.1 | 1198.8 | 1114.8 | 1189.3 | 1200 | 1160 | 1129 | 1201.4 | 1203.3 | 1170.5 | 1188.6 | 1189.1 | 1167.6 | 1259.6 | 1221.9 | 1131.9 | 1050.7 | 1068.1 | 1056.8 | 1053.4 | 1055.2 | 1057 | 1065.6 | 1077 | 1086.5 | 1073.1 | 1070.6 | 1071.4 | 1082.9 | 1013.2 | 927.7 | 1107.6 | 1084 | 1082.7 | 1090.2 | 1082.9 | 1075 | 1087.6 | 1074.8 | 1089.7 | 1064.2 | 1093.1 | 1066 | 1074.7 | 1030.6 | 1025.7 | 1026.1 | 1170 | 1144 | 1033.6 | 1189.3 | 1191.6 | 1193.4 | 1241.9 | 1178.7 | 1317.5 | 1212.3 | 1128.5 | 1135.9 | 1078.3 | 1171.9 | 1110 | 1248.4 | 1036.3 | 1051.8 | 1156.6 | 997.2 | 930.9 | 1221.7 | 1199.8 | 1223 | 1208.1 | 1195 | 1213.3 | 1323 | 1304.6 | 1133.6 | 1143.6 | 1043.1 | 1042.6 | 1037.3 | 1076.7 | 1050.6 | 1078.4 | 1055.9 | 1035.9 | 1030.4 | 1034.5 | 1049 | 1073.7 | 1036.2 | 1072.5 | 1055 | 1056 | 1014.8 | 1076.9 | 1039.4 | 1052.2 | 1027.2 | 1067.4 | 1079.7 | 1069.7 | 1053.5 | 1077.9 | 1062.7 | 1076.1 | 1077.9 | 1154.4 | 1183.3 | 1165.4 | 1160.7 | 1232.5 | 1287.4 | 1178.9 | 1223.6 | 1182 | 1225 | 1210.1 | 1169.2 | 1273.5 | 1225.5 | 1116.7 | 1258 | 1255 | 946.7 | 935.6 | 1214.1 | 1008.8 | 1161.8 | 1070.7 | 1068.1 | 1069.2 | 1071.6 | 1043.7 | 1052.7 | 1072.5 | 1052.1 | 1050.6 | 1089.5 | 1184.3 | 1087.7 | 1092.8 | 1041.5 | 1013.5 | 1018.6 | 1066.1 | 1080.1 | 1071.6 | 1072.7 | 1079.4 | 1167.5 | 1069.6 | 1066.9 | 1085.1 | 1073.4 | 986.3 | 1083.3 | 1104.2 | 1050.1 | 1035 | 1023.9 | 1141.5 | 1034.8 | 1077 | 1044.6 | 1076.2 | 1025.4 | 960.6 | 1049.2 | 1121.3 | 1018.5 | 1021.4 | 1084.5 | 1066.7 | 1057.7 | 1073.6 | 1067.6 | 1039.5 | 1141 | 1014.6 | 1035 | 987.8 | 1053.7 | 1023 | 1011.2 | 1075.4 | 1099.4 | 1092.4 | 1098.1 | 1066.7 | 1098.7 | 1089.4 | 1099.1 | 1104.3 | 1089.7 | 1044.8 | 1045.7 | 1101.5 | 980.7 | 1041.1 | 1054.6 | 1133 | 1089.1 | 1093.1 | 1048.5 | 1145 | 1087.6 | 1146.7 | 1027.8 | 1098.5 | 1030.8 | 1036 | 999.8 | 1056.8 | 1057.6 | 1056.9 | 0 | 37.26 | 0 | 0 | 5.14 | 4.91 | 0 | 0 | 87006340 | 257713 | 88361710 | 301268 | 72276300 | 152178 | 86633740 | 130653 | 822040 | 10030 | 103790 | 570 | 91280 | 164 | 93010 | 227 | 91070 | 163 | 91280 | 126 | 184000 | 0 | 182000 | 2000 | 366640 | 366000 | 12.6 | 5.14 | 4.91 |  | 37.26 | 0 | 372286.1
2025-05-08 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 5:34 | 17:26 | 311.2 | 304.2 | 331.1 | 331.3 | 326.5 | 312.8 | 336 | 319.1 | 330 | 333 | 333.5 | 331 | 333.5 | 332.7 | 335.9 | 336.5 | 313.7 | 318.8 | 332.4 | 336.1 | 346 | 343.5 | 346.2 | 344.8 | 342.1 | 340.2 | 347.4 | 346.2 | 348.7 | 349.6 | 343.8 | 347.3 | 328.6 | 306.7 | 310.1 | 312.5 | 318.2 | 317.2 | 328.6 | 316.5 | 327.1 | 357.5 | 374.8 | 354 | 355.6 | 367.4 | 396 | 390.5 | 423.3 | 373.4 | 354.4 | 348.2 | 345 | 363 | 360.2 | 363.8 | 378.7 | 348.4 | 305.8 | 350 | 333.4 | 314.2 | 342.6 | 789.5 | 778.1 | 778.4 | 786.6 | 798.6 | 779.4 | 773.9 | 790.5 | 796.6 | 777.2 | 765 | 775.3 | 746 | 737.3 | 781.8 | 793.1 | 789.5 | 781.7 | 827.6 | 760.6 | 760.8 | 761 | 763.5 | 763 | 788.5 | 789.1 | 782.8 | 785.4 | 769.2 | 789.8 | 791.5 | 801.3 | 804.3 | 873.7 | 792.2 | 795.8 | 757.2 | 748.6 | 800.2 | 774.3 | 803.9 | 835.9 | 792.2 | 808 | 794.9 | 794.5 | 814.6 | 807.6 | 813.5 | 732 | 761.1 | 788.4 | 812.4 | 800 | 804.3 | 795.9 | 797.1 | 795.4 | 799.7 | 756.6 | 762.9 | 801.8 | 797.9 | 782.9 | 800.1 | 791.2 | 790.4 | 786.2 | 735.4 | 796.9 | 806.3 | 787.6 | 789.4 | 740.4 | 810.4 | 866.5 | 783.9 | 784 | 796.8 | 798.5 | 793.8 | 791.4 | 805.6 | 803.5 | 764.6 | 832.2 | 746.7 | 690.1 | 804.8 | 743.9 | 795.4 | 801.2 | 793.3 | 765.8 | 797.9 | 800.9 | 785.1 | 789.2 | 789 | 779.4 | 847.6 | 786 | 750.8 | 708.1 | 724 | 715.9 | 710 | 715.4 | 718 | 722.6 | 728.2 | 734.6 | 724.1 | 720.5 | 724.7 | 733.6 | 681.6 | 622.8 | 742.7 | 730.7 | 728.4 | 735.3 | 731.8 | 726.2 | 734.8 | 722.2 | 731.1 | 712.7 | 733.4 | 716.7 | 727.7 | 692.6 | 688.8 | 694.8 | 771.1 | 753.8 | 684.2 | 785.5 | 787.4 | 788.4 | 825.4 | 804.1 | 879.2 | 810.7 | 754.7 | 760.9 | 720.2 | 780 | 730 | 820.2 | 678.6 | 689.4 | 758.9 | 656 | 609.7 | 807.5 | 795.4 | 800 | 801 | 800 | 801 | 870.2 | 868.9 | 758.2 | 766.8 | 699.9 | 693.7 | 697 | 718.7 | 706.2 | 724.2 | 703.9 | 689.5 | 693.9 | 700.2 | 713.8 | 719.4 | 712.8 | 721.6 | 702.9 | 704 | 678.2 | 710 | 689.7 | 708 | 683.3 | 703.7 | 722.9 | 712.2 | 720.6 | 718.5 | 717.9 | 719.7 | 721.6 | 754.8 | 774.4 | 784.1 | 759.6 | 809.5 | 847.3 | 797.7 | 800.5 | 773.1 | 804.3 | 797.3 | 771.9 | 839.6 | 820.6 | 731.9 | 836.6 | 823.9 | 624.1 | 616.4 | 803.4 | 664.9 | 766.6 | 716.1 | 712.8 | 709.5 | 713.4 | 693.1 | 696.5 | 713.6 | 702.3 | 697.5 | 723.9 | 788.3 | 720 | 722.9 | 691.4 | 674.6 | 672.4 | 705 | 714.1 | 710.5 | 710.5 | 717 | 784.3 | 706.9 | 705.7 | 719 | 711.8 | 652.4 | 715.6 | 731.8 | 692.2 | 683.4 | 701.4 | 779.1 | 697.6 | 723.1 | 705.5 | 720.8 | 684.3 | 643.6 | 719.3 | 760.3 | 680.3 | 685.6 | 734.9 | 727.2 | 714.8 | 728 | 720.4 | 716.3 | 771.2 | 684.6 | 695.8 | 665.6 | 714.4 | 713 | 701.4 | 717.6 | 734.8 | 730.7 | 711.6 | 725 | 734.6 | 729.9 | 734.1 | 739.7 | 726.2 | 696.9 | 700 | 739 | 1233.7 | 696 | 707.7 | 764.1 | 731.2 | 732.8 | 699.4 | 769.8 | 732.7 | 773.9 | 689.4 | 734.3 | 691 | 696.9 | 667.7 | 711.5 | 710.6 | 707.5 | 0 | 33.35 | 0 | 0 | 3.44 | 3.26 | 0 | 0 | 87067120 | 257915 | 88423930 | 301551 | 72336500 | 152361 | 86693980 | 130851 | 822640 | 10040 | 104390 | 570 | 60780 | 202 | 62220 | 283 | 60200 | 183 | 60240 | 198 | 120000 | 2000 | 120000 | 0 | 243440 | 240000 | 11.8667 | 3.44 | 3.26 |  | 33.35 | 0 | 248854.6
2025-05-09 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:55 | 17:16 | 534 | 518.1 | 566 | 564.4 | 557.2 | 540.1 | 573.4 | 546.5 | 566.3 | 567.2 | 571.8 | 567.3 | 564.4 | 567.5 | 570.8 | 570.5 | 536.8 | 540.5 | 565.6 | 572.2 | 590.8 | 582.6 | 586.9 | 583.8 | 584.1 | 580.9 | 585.5 | 580.8 | 590.4 | 589.6 | 580.7 | 582 | 555.1 | 523.2 | 528 | 529.4 | 537.1 | 538.4 | 558.2 | 533.9 | 549.8 | 596.8 | 629.3 | 589.7 | 592.7 | 611 | 659.7 | 651.5 | 707.1 | 622.8 | 595.1 | 586.4 | 581.7 | 609.7 | 605.3 | 609.7 | 631.6 | 577.9 | 510 | 583.1 | 564 | 527.3 | 577.1 | 1354.4 | 1331.6 | 1320.9 | 1351.3 | 1374.2 | 1345.6 | 1329.5 | 1355.3 | 1373.4 | 1334.5 | 1324.2 | 1333 | 1288.2 | 1268.9 | 1312.3 | 1331.3 | 1327.3 | 1319.6 | 1391.3 | 1328.4 | 1289 | 1348.4 | 1290.2 | 1283.9 | 1323.4 | 1330.7 | 1281.5 | 1331 | 1362.7 | 1384.6 | 1387.3 | 1386.4 | 1393.1 | 1500 | 1378.1 | 1371.9 | 1315.2 | 1305.4 | 1365.3 | 1325.8 | 1378.1 | 1440.2 | 1383.3 | 1394.6 | 1377.9 | 1372.9 | 1399.9 | 1383.1 | 1398.3 | 1250.3 | 1289.5 | 1339.8 | 1356.9 | 1350 | 1354.5 | 1345.9 | 1341.2 | 1340.9 | 1350.4 | 1278.3 | 1289 | 1351.7 | 1339.7 | 1321.6 | 1346.2 | 1334.5 | 1335.4 | 1332.3 | 1226.2 | 1342.1 | 1363.9 | 1333.6 | 1336.4 | 1241.6 | 1358.1 | 1445.8 | 1329.7 | 1322 | 1342.8 | 1351.3 | 1340 | 1334.8 | 1358.8 | 1352 | 1299.2 | 1409.9 | 1241.8 | 1186 | 1349 | 1254.6 | 1332.6 | 1343.8 | 1341.4 | 1291.5 | 1327.2 | 1321.1 | 1342.4 | 1341.6 | 1345.5 | 1320.1 | 1406.1 | 1365.7 | 1242.9 | 1221.4 | 1218.9 | 1232.8 | 1230.1 | 1228.5 | 1231.1 | 1234.5 | 1246.8 | 1250.8 | 1241.6 | 1240.8 | 1240.9 | 1252.2 | 1171.2 | 1069.4 | 1277.3 | 1249.1 | 1245.6 | 1251.2 | 1244.7 | 1236.6 | 1247 | 1234.9 | 1249.1 | 1222.9 | 1248.8 | 1221 | 1235.1 | 1180.3 | 1175 | 1185.7 | 1328.1 | 1294.5 | 1172 | 1347.8 | 1352.8 | 1361.2 | 1408.4 | 1370.4 | 1497.8 | 1375.1 | 1281.4 | 1299.9 | 1230.3 | 1342.1 | 1252 | 1405.2 | 1171.7 | 1187.1 | 1309.1 | 1126.4 | 1057.4 | 1383.5 | 1374.1 | 1386.3 | 1373.1 | 1373 | 1345.1 | 1485.8 | 1448.2 | 1302.3 | 1316.7 | 1197.2 | 1197.3 | 1189.8 | 1239.6 | 1207.8 | 1237 | 1208 | 1192.5 | 1194.1 | 1194.8 | 1228.7 | 1230.1 | 1222 | 1230.2 | 1211.2 | 1212 | 1170.8 | 1246.3 | 1190.2 | 1223.3 | 1178 | 1225.6 | 1243.1 | 1230.2 | 1237.7 | 1248 | 1229.9 | 1233.7 | 1242.9 | 1271.2 | 1309.6 | 1335.6 | 1275.2 | 1344.7 | 1407.9 | 1339 | 1342.6 | 1300.5 | 1356.6 | 1343.9 | 1297.9 | 1404.8 | 1346.9 | 1257.2 | 1373.8 | 1396 | 1058.7 | 1043.8 | 1347.9 | 1122.2 | 1288.9 | 1208.5 | 1198.2 | 1197.5 | 1205.5 | 1173.7 | 1185.5 | 1199.1 | 1181.7 | 1178.6 | 1221.1 | 1304 | 1215.1 | 1213.6 | 1164.5 | 1140.8 | 1140.9 | 1192.9 | 1207.4 | 1200.1 | 1199 | 1207.8 | 1315.2 | 1192.2 | 1189.6 | 1216.8 | 1200.9 | 1098.3 | 1207.9 | 1226.9 | 1166.1 | 1154.6 | 1167.6 | 1315.4 | 1169.2 | 1214.8 | 1187 | 1209.3 | 1149.5 | 1080.5 | 1184.7 | 1260.2 | 1148.5 | 1154.4 | 1226.6 | 1208.7 | 1201.8 | 1205.4 | 1202.3 | 1198.6 | 1280.8 | 1147.7 | 1167.3 | 1168.2 | 1190.5 | 1196 | 1178.1 | 1218.4 | 1232.7 | 1233 | 1189.5 | 1220.8 | 1237.2 | 1215.2 | 1235.5 | 1238.8 | 1220.1 | 1175 | 1173 | 1230.9 | 1096.4 | 1166 | 1178.5 | 1283.6 | 1216.4 | 1216.7 | 1179.9 | 1275.3 | 1228.1 | 1283.3 | 1153.5 | 1224.7 | 1153.6 | 1159.5 | 1113 | 1172 | 1179.9 | 1177.7 | 0 | 41.19 | 0 | 0 | 5.83 | 5.56 | 0 | 0 | 87170200 | 258096 | 88528970 | 301803 | 72439240 | 152424 | 86795420 | 130943 | 823680 | 10040 | 105400 | 580 | 103080 | 181 | 105040 | 252 | 102740 | 63 | 101440 | 92 | 208000 | 0 | 202000 | 2000 | 412300 | 410000 | 12.35 | 5.83 | 5.56 |  | 41.19 | 0 | 421144.6
2025-05-10 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:54 | 17:22 | 550.1 | 535.2 | 584.3 | 583.6 | 577.6 | 559.6 | 592.8 | 565.3 | 587.3 | 590.1 | 590.7 | 587.3 | 589.8 | 590.5 | 596.9 | 594.9 | 557.4 | 560.1 | 583.7 | 592.1 | 609 | 602.3 | 607.9 | 607 | 600.5 | 599.9 | 606.6 | 603.5 | 607.5 | 608 | 601 | 603.5 | 577 | 544.3 | 549.2 | 551.5 | 561.7 | 563.3 | 582.6 | 557.9 | 574.2 | 622.6 | 656.8 | 615.2 | 618.8 | 638.2 | 688.3 | 680.4 | 740.1 | 651.5 | 622.1 | 612.7 | 607.7 | 637.8 | 631.4 | 636.4 | 657.9 | 603.2 | 531.4 | 608 | 587.3 | 549.2 | 603.2 | 1394.6 | 1368.7 | 1345.5 | 1384.2 | 1404.2 | 1376.4 | 1368.2 | 1396 | 1408.1 | 1377.3 | 1359 | 1377 | 1325.7 | 1309.4 | 1360.6 | 1397.7 | 1385 | 1374.5 | 1452 | 1399.6 | 1307 | 1403 | 1349.1 | 1335.7 | 1381.5 | 1385.6 | 1336.3 | 1381.5 | 1383.9 | 1408.2 | 1407.3 | 1414.1 | 1423.5 | 1528.7 | 1410.3 | 1411 | 1344.1 | 1335.8 | 1408.4 | 1367.9 | 1411.7 | 1478.2 | 1417.4 | 1427 | 1406.1 | 1400.7 | 1432 | 1421.6 | 1390.9 | 1294.1 | 1333.7 | 1388.3 | 1411.8 | 1401.4 | 1413.5 | 1407.1 | 1402.7 | 1396.1 | 1410.2 | 1338.2 | 1348.9 | 1413.3 | 1402 | 1383.4 | 1408.9 | 1399.3 | 1399.1 | 1394.2 | 1279.4 | 1404.2 | 1423.7 | 1394.5 | 1396.5 | 1300.6 | 1414.1 | 1502.8 | 1377.8 | 1371.1 | 1402.4 | 1404.8 | 1390.4 | 1387.4 | 1409.3 | 1377.4 | 1349.9 | 1465 | 1319 | 1211.9 | 1404.5 | 1308.6 | 1393.1 | 1405 | 1396.9 | 1346.4 | 1391.8 | 1381.7 | 1389.9 | 1393.9 | 1391.4 | 1366.9 | 1473.4 | 1427.8 | 1323.7 | 1243.4 | 1227 | 1264.3 | 1265 | 1272.5 | 1276.1 | 1281.9 | 1295.9 | 1302.9 | 1290.5 | 1276.3 | 1277.5 | 1297.5 | 1209.1 | 1108.8 | 1327.1 | 1298.4 | 1297.2 | 1305.5 | 1299.4 | 1292.8 | 1302.6 | 1288.4 | 1305.9 | 1275.2 | 1304.7 | 1270.1 | 1285.2 | 1229.9 | 1223.4 | 1232.9 | 1378 | 1341.8 | 1214.9 | 1392.6 | 1396.5 | 1399.1 | 1459.9 | 1416.3 | 1534.8 | 1386.5 | 1307 | 1320.5 | 1249.7 | 1360.9 | 1299 | 1461.1 | 1219.1 | 1229.1 | 1358.8 | 1167.2 | 1096.9 | 1418.9 | 1406.5 | 1428.3 | 1413.9 | 1415.6 | 1415.5 | 1544.3 | 1508.8 | 1342.4 | 1358.1 | 1230.9 | 1232.1 | 1223.4 | 1273.2 | 1241.2 | 1267.6 | 1249.6 | 1234.9 | 1233 | 1222 | 1256.4 | 1273.4 | 1255.8 | 1271.6 | 1253.3 | 1211 | 1211.1 | 1295.2 | 1236.6 | 1267.8 | 1222.5 | 1270 | 1288.2 | 1279.2 | 1277.2 | 1281.8 | 1273.9 | 1284.4 | 1287.4 | 1338.6 | 1386.8 | 1410.8 | 1341.8 | 1416.4 | 1479.7 | 1408.1 | 1413.6 | 1370.9 | 1425.6 | 1411.3 | 1361.2 | 1470.7 | 1428.6 | 1288.4 | 1436 | 1455.7 | 1100.2 | 1088.9 | 1369 | 1169.9 | 1351.7 | 1281.7 | 1272.6 | 1274 | 1279 | 1224.1 | 1258.4 | 1274.2 | 1257.6 | 1254.4 | 1295.5 | 1398.8 | 1290.2 | 1285.6 | 1234.2 | 1209.8 | 1210.5 | 1263.2 | 1277.9 | 1269.9 | 1271.6 | 1275.4 | 1403 | 1261 | 1261.1 | 1278.2 | 1267.2 | 1165.2 | 1278.5 | 1294.5 | 1229.9 | 1216.3 | 1229.5 | 1382.3 | 1236.5 | 1287.5 | 1238.9 | 1283.9 | 1220 | 1147.1 | 1264.4 | 1330.5 | 1220.4 | 1225.8 | 1297.5 | 1275.8 | 1279.2 | 1278.5 | 1278.9 | 1267.4 | 1361.5 | 1220.7 | 1230.6 | 1229.4 | 1247.9 | 1245 | 1241.8 | 1279.6 | 1294.9 | 1302.3 | 1251.6 | 1295.4 | 1302.5 | 1288.5 | 1304.1 | 1314.4 | 1290.5 | 1246.2 | 1245 | 1309.7 | 1170.9 | 1241.3 | 1256.2 | 1360.3 | 1285.7 | 1287.8 | 1253 | 1356.6 | 1306.2 | 1362.7 | 1225.8 | 1306.2 | 1232.4 | 1232 | 1185.9 | 1252.6 | 1260.1 | 1256.2 | 0 | 42.15 | 0 | 0 | 6.12 | 5.75 | 0 | 0 | 87276680 | 258267 | 88638320 | 302006 | 72545820 | 152571 | 86902920 | 131027 | 824750 | 10050 | 106470 | 580 | 106480 | 171 | 109350 | 203 | 106580 | 147 | 107500 | 84 | 214000 | 2000 | 214000 | 0 | 429910 | 428000 | 12.4667 | 6.12 | 5.75 |  | 42.15 | 0 | 438872.6
2025-05-11 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 5:28 | 17:34 | 328.2 | 319.9 | 349.3 | 349.1 | 343.6 | 328.8 | 354.9 | 336.2 | 348.7 | 351.3 | 353.1 | 349.8 | 351.1 | 350.8 | 354.5 | 354.5 | 331.8 | 336 | 351.5 | 355.3 | 365.9 | 361.8 | 364.7 | 363.2 | 362.6 | 358.6 | 366.1 | 364.3 | 369.1 | 367.6 | 362.6 | 363.8 | 344.8 | 323.1 | 326.5 | 328.5 | 334.3 | 333.7 | 345.5 | 332.6 | 343 | 373.2 | 391.9 | 369.5 | 371.8 | 384.7 | 415 | 410.2 | 443.8 | 391.6 | 373.7 | 365.8 | 361.1 | 381.9 | 378.5 | 381.8 | 398.4 | 365.1 | 322.3 | 367.1 | 351.2 | 330.7 | 360.3 | 840.2 | 825.8 | 828.8 | 832.3 | 846.4 | 825.7 | 820 | 836.4 | 845.3 | 821.7 | 809.1 | 820.5 | 789.5 | 778 | 828.5 | 838.7 | 834.6 | 824.3 | 879.3 | 846 | 805.9 | 855.2 | 812.5 | 809 | 835.9 | 838.7 | 830.7 | 831.4 | 820.5 | 838.7 | 840.9 | 849.3 | 856 | 928.6 | 848.6 | 847.1 | 802.6 | 796.5 | 850.6 | 824.8 | 855.6 | 886.9 | 846.2 | 858.8 | 844.7 | 840.2 | 864 | 858.1 | 865.9 | 778 | 810.4 | 829.6 | 851.5 | 842.9 | 844.7 | 840 | 837.5 | 833.8 | 838.2 | 794.7 | 802 | 842.2 | 835.5 | 822.6 | 838.6 | 830.6 | 830 | 824.6 | 791.6 | 834.4 | 844 | 825.5 | 828.9 | 774.8 | 851.9 | 911.2 | 822.9 | 822.9 | 839 | 840.3 | 833.4 | 829.8 | 838 | 842.4 | 803.7 | 873.8 | 786 | 725.2 | 843.5 | 781.7 | 836.6 | 839.9 | 833.3 | 802.2 | 838.1 | 841.5 | 827.2 | 831.3 | 831.1 | 819.5 | 886.1 | 858.9 | 791.2 | 751.6 | 765.6 | 757.3 | 754.5 | 757.9 | 758.4 | 761.7 | 768 | 774.6 | 766.1 | 765.7 | 773 | 775.4 | 723.5 | 661.4 | 791.4 | 774.4 | 771.8 | 776.7 | 771.8 | 767.1 | 774.6 | 766.4 | 774 | 755.7 | 774.7 | 754.9 | 765.6 | 730.8 | 726.5 | 733.6 | 820.2 | 803.7 | 728.5 | 837.4 | 842 | 843.5 | 878.5 | 854.6 | 934.8 | 860.3 | 799.8 | 805.3 | 767.3 | 834.3 | 804 | 880.4 | 730.2 | 736.9 | 812.6 | 698.6 | 656.8 | 867.2 | 840.8 | 867.4 | 854.5 | 845.3 | 838.6 | 941.1 | 927.4 | 800.6 | 811 | 737.7 | 733.8 | 736.1 | 757.9 | 740 | 760.8 | 745.8 | 734.3 | 734.9 | 729.3 | 723.1 | 759.5 | 714.4 | 759.4 | 749.1 | 748 | 720.4 | 761.9 | 735.5 | 756.8 | 727.7 | 754.1 | 765.5 | 757.1 | 741.5 | 759 | 749 | 762.4 | 765.2 | 794.2 | 817.7 | 836.8 | 798.4 | 850.6 | 890.7 | 840 | 841.3 | 813.4 | 846.4 | 838.6 | 810.2 | 882.4 | 864.9 | 770.5 | 877.5 | 869.3 | 656.6 | 648.9 | 843.2 | 699 | 803.5 | 756.1 | 751.3 | 749.7 | 752.9 | 721.4 | 740.9 | 751.6 | 736.9 | 737.1 | 763.7 | 828.5 | 758.1 | 760.1 | 728.7 | 712 | 712.4 | 744.8 | 754.9 | 753.2 | 751.4 | 756.9 | 828 | 746.9 | 745.7 | 755.9 | 750 | 688.4 | 754.8 | 771.4 | 727.6 | 718.8 | 667.4 | 734 | 737.8 | 760.7 | 759.6 | 758.1 | 720.9 | 675.7 | 669.2 | 770.1 | 716.6 | 715.8 | 769.9 | 723.9 | 755.8 | 744.5 | 743 | 648.7 | 810.2 | 722.3 | 724.8 | 530.3 | 708.6 | 720 | 571 | 752.8 | 764.9 | 765.4 | 741.4 | 759 | 767.8 | 761.8 | 768.1 | 774.3 | 759.8 | 731.2 | 734 | 772.5 | 686.3 | 728.1 | 738.8 | 797.6 | 755.9 | 762.2 | 731.5 | 801.5 | 764.6 | 807.1 | 720.4 | 765.9 | 722.5 | 728.3 | 695.4 | 741.9 | 741.9 | 738.5 | 0 | 33.11 | 0 | 0 | 3.46 | 3.28 | 0 | 0 | 87340980 | 258464 | 88703760 | 302276 | 72609500 | 152733 | 86965160 | 131244 | 825390 | 10050 | 107090 | 580 | 64300 | 197 | 65440 | 270 | 63680 | 162 | 62240 | 217 | 128000 | 0 | 124000 | 0 | 255660 | 252000 | 12.1 | 3.46 | 3.28 |  | 33.11 | 0 | 261207.5
2025-05-12 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:55 | 17:24 | 500.9 | 488.2 | 533.7 | 533.1 | 523.1 | 504.5 | 541.6 | 515.9 | 533 | 535.7 | 539.3 | 535.8 | 532.7 | 537.2 | 540 | 540.9 | 508.4 | 511.5 | 531.5 | 540.9 | 556.3 | 548.9 | 552.3 | 552.2 | 550.1 | 545.1 | 553.9 | 547.4 | 556.7 | 555.7 | 548 | 549.9 | 519.4 | 489.4 | 495.4 | 497.3 | 506.9 | 509.2 | 523 | 503 | 517.5 | 558 | 583.7 | 548.8 | 553.7 | 569.1 | 611 | 604.5 | 651.6 | 586.1 | 556.2 | 546.6 | 541.6 | 573.1 | 570.7 | 567.2 | 596.4 | 547.5 | 483.6 | 549.1 | 534.3 | 497.6 | 538.4 | 1247.8 | 1228.9 | 1250.4 | 1247.7 | 1242.2 | 1239.7 | 1220.9 | 1263 | 1244.2 | 1226.5 | 1198.6 | 1224.6 | 1191.7 | 1181.5 | 1174 | 1247.8 | 1263.8 | 1221.5 | 1291.7 | 1271 | 1201.7 | 1276 | 1214.3 | 1190.2 | 1223.7 | 1262 | 1239 | 1241.9 | 1206.9 | 1232.3 | 1249.4 | 1262.5 | 1246 | 1339.8 | 1260.8 | 1245.4 | 1190.2 | 1192.2 | 1254.5 | 1236.5 | 1249 | 1302.9 | 1244.4 | 1269.3 | 1236.3 | 1236.1 | 1273.2 | 1267.8 | 1250.6 | 1138.4 | 1182.5 | 1239.1 | 1246.3 | 1187.1 | 1258.1 | 1227 | 1265.8 | 1247.7 | 1221 | 1189.3 | 1208.8 | 1270.9 | 1249.8 | 1242.8 | 1262.2 | 1241.9 | 1236.8 | 1221.1 | 1183.2 | 1220.6 | 1233.7 | 1213.1 | 1182.2 | 1140.6 | 1183.1 | 1262.9 | 1165.5 | 1175.5 | 1170.5 | 1183.2 | 1196.5 | 1181.3 | 1197.9 | 1190 | 1156.3 | 1248.6 | 1109.3 | 1047.2 | 1192.5 | 1109.3 | 1182.3 | 1197.4 | 1178.1 | 1171.7 | 1196.3 | 1210.6 | 1175.7 | 1193.6 | 1192.3 | 1182.8 | 1264.3 | 1224 | 1141.3 | 1033 | 1048.2 | 1039.7 | 1036.8 | 1037.2 | 1040.2 | 1050.4 | 1060.9 | 1072.5 | 1059.5 | 1053 | 1058.9 | 1064.4 | 1002.2 | 922.8 | 1091 | 1066.3 | 1068 | 1075 | 1074.9 | 1066.4 | 1080.1 | 1065.8 | 1081.3 | 1059.7 | 1083.5 | 1063.3 | 1075.9 | 1031.6 | 1027.5 | 1030.4 | 1158.1 | 1139.7 | 1029.7 | 1162.4 | 1170.8 | 1187.9 | 1209.3 | 1179.7 | 1303.4 | 1164.6 | 1105.6 | 1122.1 | 1077.5 | 1167.3 | 1122 | 1234.8 | 1037.1 | 1053.4 | 1103.2 | 999.3 | 933.5 | 1198.7 | 1198.3 | 1223.3 | 1196.2 | 1185.3 | 1200 | 1297.3 | 1278.5 | 1136.2 | 1141.3 | 1054.1 | 1037.2 | 1039.4 | 1080.2 | 1048 | 1071 | 1059.6 | 1040.8 | 1043.7 | 1023.8 | 1053.7 | 1067.6 | 1055.1 | 1066.7 | 1064 | 1068 | 1025.1 | 1085.2 | 1044.7 | 1070.1 | 1039.5 | 1074.7 | 1072.9 | 1067 | 1064 | 1077.9 | 1065.6 | 1072.8 | 1065.3 | 1189.1 | 1162 | 1247.8 | 1186.4 | 1220 | 1303.9 | 1206.8 | 1225.6 | 1218.1 | 1274 | 1245.8 | 1205.1 | 1289.1 | 1257.3 | 1153 | 1255.1 | 1275.5 | 965.3 | 957.4 | 1224.4 | 1032.2 | 1196.3 | 1105.4 | 1103.3 | 1104.1 | 1107.1 | 1071.8 | 1087.2 | 1105.9 | 1091.2 | 1085.8 | 1123 | 1199.8 | 1119 | 1121.1 | 1079.1 | 1058.5 | 1061.9 | 1104.1 | 1115.8 | 1110.7 | 1112.8 | 1117.6 | 1185.9 | 1105.1 | 1100 | 1120.6 | 1108.2 | 1025.6 | 1116.7 | 1124.7 | 1085.5 | 1074.6 | 1059 | 1155.4 | 1070 | 1107.2 | 1111.6 | 1111.3 | 1064.1 | 1004.7 | 1069.5 | 1141.4 | 1053.8 | 1055.1 | 1112.1 | 1093.1 | 1090.6 | 1099.2 | 1092.6 | 1069.3 | 1164.9 | 1056.2 | 1051.8 | 994.5 | 1080 | 1073 | 1011.4 | 1093.9 | 1109.1 | 1107 | 1080.5 | 1101.6 | 1114.1 | 1105 | 1112.1 | 1118 | 1104.3 | 1072.5 | 1078 | 1121.8 | 1015.8 | 1062.9 | 1075.8 | 1144.3 | 1101.5 | 1101.2 | 1070 | 1147.4 | 1108.7 | 1150.9 | 1047.4 | 1111.9 | 1050 | 1056.5 | 1023.3 | 1068.9 | 1076.1 | 1077.2 | 0 | 38.47 | 0 | 0 | 5.38 | 5.12 | 0 | 0 | 87436450 | 258655 | 88797440 | 302554 | 72700650 | 152835 | 87058690 | 131386 | 826330 | 10050 | 108010 | 590 | 95470 | 191 | 93680 | 278 | 91150 | 102 | 93530 | 142 | 188000 | 0 | 184000 | 2000 | 373830 | 372000 | 12.4833 | 5.38 | 5.12 |  | 38.47 | 0 | 379993.1
2025-05-13 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 5:00 | 17:33 | 322.8 | 314.9 | 343.2 | 342.5 | 337.4 | 323.7 | 349.2 | 331 | 343.1 | 343.3 | 348.9 | 344.7 | 343.6 | 343.3 | 347.4 | 347.4 | 325.2 | 330 | 346.6 | 349 | 362 | 356.5 | 357.2 | 354.7 | 357.5 | 355.2 | 359.9 | 357.3 | 364.4 | 361.6 | 357.2 | 355.7 | 336.9 | 315.8 | 318.8 | 320.7 | 326.9 | 326.4 | 338.1 | 326 | 324.2 | 364 | 381.9 | 359.3 | 361.1 | 373.4 | 401.8 | 396.4 | 425 | 379.7 | 361.6 | 355.2 | 352.3 | 371 | 369.6 | 370.7 | 386.9 | 354 | 314.3 | 357 | 346.1 | 323.8 | 349.7 | 829.2 | 816.8 | 822.5 | 826.5 | 832.7 | 817 | 811.3 | 829 | 831.4 | 809.1 | 797.2 | 805.5 | 778.3 | 766.7 | 795.3 | 824.4 | 825.1 | 812.3 | 859.6 | 831.9 | 794 | 829 | 797.3 | 792.9 | 817.1 | 830 | 822.2 | 822.7 | 809.3 | 823.2 | 827.6 | 835 | 832.2 | 898.7 | 831.1 | 826.5 | 790.1 | 783.7 | 831.7 | 807.5 | 836.9 | 836.6 | 831.2 | 845.8 | 829.3 | 826.5 | 850.3 | 844.4 | 846.8 | 751 | 793.3 | 817.6 | 830.5 | 824.3 | 830.2 | 736.2 | 825.9 | 819.6 | 822.4 | 782.8 | 792.1 | 827.3 | 799.1 | 811 | 824.4 | 794.9 | 814 | 805.9 | 728.5 | 810.6 | 820.3 | 804 | 804.7 | 756.5 | 810.3 | 864.5 | 789.7 | 793.2 | 798.5 | 803.1 | 802.5 | 799 | 809.2 | 807.2 | 776 | 841.5 | 725.5 | 703 | 808.8 | 755.9 | 803.7 | 809.6 | 778.5 | 769.3 | 811.5 | 813.8 | 799.3 | 804.7 | 799.9 | 792.1 | 851.9 | 826.4 | 718.6 | 697.1 | 704.5 | 699.2 | 698.6 | 699.8 | 701.7 | 707.4 | 715.6 | 723 | 713.1 | 706.5 | 715.3 | 715.5 | 674 | 617.3 | 733.4 | 713.3 | 717 | 724.2 | 721.6 | 715.4 | 723.3 | 715.2 | 723.5 | 707.6 | 722.6 | 711.3 | 717.8 | 683.9 | 682 | 690.2 | 781.5 | 765.2 | 694.6 | 788.1 | 792.2 | 796.3 | 826.8 | 803.3 | 878.5 | 766.6 | 750.8 | 763 | 728.8 | 789.5 | 738 | 829.1 | 707 | 702.7 | 768.7 | 666.8 | 625.2 | 790 | 782.5 | 816.3 | 820 | 791.6 | 789.3 | 874.5 | 858.7 | 747.7 | 753.8 | 692.4 | 687.7 | 691.7 | 710.8 | 703.8 | 716.7 | 696.6 | 684.8 | 688.3 | 692.8 | 714.1 | 706.8 | 710.3 | 709.7 | 699.1 | 701 | 676 | 710.3 | 684.4 | 700.9 | 681.2 | 704.1 | 712.6 | 708.7 | 721.7 | 723.9 | 711.2 | 714.4 | 718.5 | 763.4 | 789.5 | 823.2 | 784.9 | 814 | 869.2 | 765.2 | 796.5 | 800.5 | 834 | 823.5 | 793.4 | 856.5 | 839.1 | 755.4 | 844.7 | 845.5 | 641.7 | 634.7 | 817.5 | 682.9 | 786.6 | 720.7 | 718 | 717.5 | 715.7 | 700.8 | 707.9 | 719.5 | 707.8 | 705 | 732.3 | 781.9 | 729.3 | 732.7 | 701 | 685.4 | 682.8 | 716.5 | 729.3 | 725.8 | 724.9 | 730.5 | 786 | 724.8 | 716.6 | 733.6 | 724.9 | 662.7 | 728.3 | 739.4 | 703.7 | 696.5 | 693.8 | 757.6 | 693.5 | 720.8 | 719.5 | 717.7 | 689.7 | 646 | 697.1 | 753.3 | 678 | 684.8 | 727.7 | 719.4 | 711.4 | 717.9 | 721.2 | 718.1 | 765.3 | 680.6 | 682.8 | 690.8 | 709.5 | 717 | 697.6 | 711.8 | 719.4 | 712.1 | 701.8 | 714.5 | 727.5 | 720.5 | 727 | 732.9 | 720.2 | 693.9 | 699 | 734.4 | 656.3 | 691.6 | 701.3 | 749.3 | 715.8 | 714.6 | 691.9 | 750.4 | 719.4 | 756.1 | 679.3 | 722.1 | 680.6 | 687.3 | 659.7 | 698.8 | 701.6 | 700.6 | 0 | 33.39 | 0 | 0 | 3.4 | 3.23 | 0 | 0 | 87499260 | 258865 | 88859810 | 302880 | 72761340 | 153004 | 87119550 | 131675 | 826950 | 10060 | 108610 | 590 | 62810 | 210 | 62370 | 326 | 60690 | 169 | 60860 | 289 | 124000 | 2000 | 120000 | 0 | 246730 | 244000 | 12.55 | 3.4 | 3.23 |  | 33.39 | 0 | 251049.7
2025-05-14 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:57 | 17:21 | 444.8 | 433.6 | 472.5 | 472.8 | 463.5 | 445.4 | 479 | 454.8 | 470.8 | 473 | 476.6 | 472.4 | 471.1 | 473.5 | 476.8 | 476.3 | 447.4 | 452.3 | 472.8 | 478.5 | 491.5 | 485.9 | 488.7 | 488.1 | 486.7 | 482 | 487.7 | 486.1 | 493.9 | 491.8 | 483.1 | 483.3 | 459.1 | 433 | 438.2 | 440.8 | 449.3 | 450.9 | 461.9 | 446.3 | 435.9 | 496.6 | 520.6 | 491.8 | 494.5 | 509.5 | 548.7 | 543.1 | 585 | 519.7 | 495.2 | 485.4 | 478.8 | 506.7 | 504.9 | 508.8 | 530.1 | 487.4 | 430.3 | 490.5 | 472 | 443.1 | 479.6 | 1128.8 | 1113.7 | 1124.3 | 1134.1 | 1141.8 | 1120.2 | 1102.4 | 1129.6 | 1137.3 | 1108.1 | 1095.8 | 1107.6 | 1074.2 | 1055.9 | 1081 | 1119.6 | 1115.2 | 1081.5 | 1171.1 | 1135.6 | 1079 | 1138.8 | 1095.5 | 1081.2 | 1123.8 | 1132.9 | 1116.1 | 1117.3 | 1119.6 | 1147.5 | 1156.6 | 1165 | 1166.5 | 1259.9 | 1157.4 | 1156.2 | 1095.3 | 1092 | 1158.6 | 1127.9 | 1158 | 1212.3 | 1149.3 | 1168.8 | 1141.1 | 1142.5 | 1171.5 | 1164.2 | 1141.4 | 1063.2 | 1090.2 | 1069 | 1117.9 | 1111 | 1115.3 | 1120.7 | 1108.2 | 1112.5 | 1056.4 | 1053.6 | 1062.7 | 1116.6 | 1108.2 | 1094.7 | 1113.8 | 1081 | 1106.5 | 1096.6 | 1046.7 | 1099.1 | 1115.2 | 1086.6 | 1089.8 | 1037.4 | 1121.4 | 1189.7 | 1084.3 | 1115 | 1103.5 | 1102.8 | 1098.1 | 1094.6 | 1113 | 1107.8 | 1063.6 | 1190 | 1034.8 | 959.3 | 1105.8 | 1032.5 | 1095 | 1101.7 | 1100.6 | 1053.4 | 1108.1 | 1093 | 1067.1 | 1098.6 | 1099.7 | 1086.8 | 1151.3 | 1121.9 | 1020.5 | 976.9 | 994.7 | 989.6 | 988.6 | 989.4 | 990.4 | 994.9 | 1004.2 | 1009.4 | 993.8 | 994.9 | 1002 | 1005.1 | 946.8 | 861.1 | 1021.9 | 1003.1 | 999.2 | 1007.9 | 1005.2 | 996.1 | 1006.3 | 994.3 | 1006.2 | 985.7 | 1005.9 | 986.4 | 995.6 | 953.1 | 947.7 | 952.8 | 1083.4 | 1063 | 957.7 | 1098.2 | 1105.3 | 1110.1 | 1148.7 | 1095.7 | 1227.6 | 1059.1 | 1043.1 | 1032.1 | 1004.8 | 1082.4 | 1045 | 1147.9 | 955.5 | 973.1 | 1068.6 | 923.7 | 864.6 | 1099.2 | 1083.1 | 1133.1 | 1113.9 | 1101.1 | 1093.4 | 1213.7 | 1190.5 | 1037.9 | 1046.2 | 964.2 | 957.2 | 961.4 | 992.3 | 972.1 | 996.5 | 966.5 | 950.4 | 955 | 957.4 | 970 | 985.2 | 966.2 | 987 | 962.7 | 967 | 927.3 | 981.5 | 946.5 | 976 | 937.5 | 976.7 | 990.6 | 980.9 | 979.1 | 993.7 | 982.6 | 992.1 | 996 | 1068.3 | 1097.8 | 1124.8 | 1072.7 | 1100.7 | 1187.2 | 1123 | 1100.3 | 1092.6 | 1138.4 | 1121 | 1089.3 | 1172.1 | 1121.3 | 1029.5 | 1155.4 | 1154.1 | 876.7 | 868.1 | 1123.5 | 934.1 | 1081.8 | 994.4 | 990.8 | 991.1 | 995.1 | 965.1 | 973.4 | 993.7 | 973 | 974.6 | 1004.9 | 1081.6 | 1001.5 | 999.6 | 957.8 | 941.3 | 943.1 | 983.4 | 993.1 | 989.5 | 988.4 | 989.3 | 1059 | 978.8 | 977.8 | 996.1 | 982.4 | 908 | 992.9 | 1012.6 | 961.9 | 953.9 | 948.1 | 1060.7 | 956.5 | 992.7 | 994 | 985.5 | 946.4 | 891.5 | 986.9 | 1035.8 | 938.5 | 939.5 | 998.1 | 983.6 | 975.7 | 990.4 | 983.3 | 972.7 | 1052.5 | 939.9 | 962.3 | 935.3 | 976.4 | 970 | 945.7 | 989.7 | 1004.1 | 1003.1 | 974.8 | 997.3 | 1006.8 | 999.1 | 1008.7 | 1010.6 | 997 | 959.8 | 962 | 1009.6 | 907.2 | 956.9 | 968.1 | 1048.6 | 1004.5 | 1004.6 | 967.4 | 1047.8 | 1008.9 | 1059.9 | 954.5 | 1007.7 | 956.2 | 954.9 | 917.9 | 971.7 | 973.8 | 973.1 | 0 | 35.24 | 0 | 0 | 4.74 | 4.52 | 0 | 0 | 87585600 | 259043 | 88945800 | 303136 | 72845200 | 153139 | 87203640 | 131777 | 827810 | 10060 | 109450 | 600 | 86340 | 178 | 85990 | 256 | 83860 | 135 | 84090 | 102 | 172000 | 0 | 168000 | 2000 | 340280 | 340000 | 12.4 | 4.74 | 4.52 |  | 35.24 | 0 | 345926.8
2025-05-15 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 5:29 | 17:29 | 232.4 | 225.1 | 247.3 | 247.3 | 243.6 | 232.4 | 251.6 | 237.9 | 248.2 | 248.1 | 249.2 | 247.7 | 249.6 | 248.4 | 252 | 250.9 | 233.6 | 240 | 249.7 | 251.8 | 259.4 | 257.3 | 256.8 | 256.5 | 254 | 254.5 | 260.2 | 259 | 262.1 | 258.9 | 257.3 | 253.2 | 246.4 | 230 | 230.5 | 233.8 | 237 | 235.1 | 245 | 237 | 232.1 | 266.7 | 279.8 | 264.1 | 266.3 | 276.2 | 297.5 | 295 | 314.9 | 278.6 | 265.7 | 260 | 258.4 | 272.1 | 268.9 | 272 | 284.5 | 260.5 | 229.4 | 262.2 | 247.5 | 235.4 | 256.9 | 587.8 | 578.9 | 582.2 | 583.9 | 593.5 | 580.2 | 566.8 | 590.2 | 595.2 | 580.7 | 572.5 | 579.1 | 556.4 | 549.7 | 579.1 | 587.9 | 587.5 | 580.1 | 615.4 | 591.3 | 564.4 | 596.5 | 565.9 | 564.7 | 586 | 588.5 | 582.6 | 583.4 | 568.5 | 580.3 | 583.1 | 588.3 | 593.5 | 642.9 | 588.2 | 586.3 | 553.2 | 551.4 | 589.1 | 570.2 | 594 | 615.2 | 588.7 | 597.6 | 589.1 | 582.8 | 602.7 | 598.1 | 602.6 | 542.2 | 563.9 | 584.2 | 600.8 | 593.3 | 594.6 | 591.4 | 588 | 591.7 | 594.1 | 561.9 | 566.7 | 598.3 | 596.9 | 583.7 | 598 | 588 | 588.9 | 586.2 | 568.2 | 594.4 | 601.3 | 587.8 | 589.9 | 580.4 | 608.8 | 651.8 | 588.7 | 589.2 | 598.3 | 599.9 | 596.6 | 593 | 603.9 | 602.2 | 574.7 | 622.9 | 561.4 | 517.2 | 601.5 | 557.6 | 595.8 | 597.3 | 593.9 | 571.7 | 597.3 | 598.7 | 588.9 | 592.4 | 592.8 | 585.6 | 631 | 613 | 563.7 | 531 | 544.3 | 532.4 | 533.9 | 535.5 | 536.7 | 539.2 | 543.9 | 551.2 | 542.4 | 541.3 | 550.1 | 553.4 | 514.6 | 471.6 | 564.5 | 550 | 550.5 | 552.3 | 545.9 | 543.7 | 548.7 | 545.4 | 547.6 | 535.4 | 545.1 | 537.7 | 542.7 | 514.4 | 512.3 | 524.4 | 582.6 | 571.4 | 519 | 598.3 | 603.3 | 601.3 | 624.9 | 609.3 | 667.2 | 611.7 | 571.2 | 570.4 | 545.4 | 593.5 | 565 | 627.3 | 522 | 525 | 579 | 498.6 | 469.7 | 614.3 | 605.1 | 616.1 | 607.1 | 598.7 | 592.7 | 666.2 | 656.2 | 564.5 | 574.4 | 523.5 | 516.8 | 513 | 530.8 | 520.2 | 535.2 | 530.2 | 519.5 | 521.3 | 506.7 | 488.4 | 533.6 | 485.7 | 536.1 | 535.8 | 539 | 513.1 | 543.2 | 523.6 | 533.5 | 518.7 | 535.3 | 545.3 | 538.2 | 511.9 | 534.5 | 519.9 | 543.1 | 540.1 | 561.8 | 578.2 | 592.1 | 565.6 | 602.1 | 631.2 | 594.9 | 596.7 | 575.3 | 599.8 | 594 | 574.3 | 625.4 | 612.5 | 555.4 | 624.5 | 615.7 | 466.5 | 460.6 | 597.9 | 496.5 | 571.2 | 528.7 | 524.7 | 518.1 | 519.3 | 510.5 | 516.7 | 524.4 | 512.8 | 512.1 | 534.9 | 581 | 530.2 | 533.5 | 513.5 | 501.3 | 492.6 | 515.1 | 530.2 | 522.8 | 521.7 | 529.6 | 528.1 | 525.4 | 517.5 | 532.6 | 528.6 | 476.8 | 526.8 | 540.5 | 509.5 | 505 | 497.2 | 545.4 | 512.1 | 532.1 | 528.6 | 527 | 507.2 | 469.5 | 502.4 | 556.4 | 494.3 | 500.7 | 540.5 | 520.2 | 532.7 | 533.1 | 528.4 | 488 | 570 | 503.8 | 509.3 | 423.1 | 506.5 | 505 | 434 | 524.1 | 527.5 | 538.1 | 515.8 | 523.8 | 534.5 | 527.5 | 532.1 | 539.5 | 524.5 | 506 | 510 | 539.8 | 476.1 | 503.8 | 517.8 | 558.5 | 524.9 | 525.3 | 509.6 | 555.9 | 535.1 | 563.3 | 500.4 | 532.3 | 499.9 | 506.8 | 483.5 | 518.9 | 520.5 | 510.7 | 0 | 27.646 | 0 | 0 | 2.412 | 2.2107 | 0 | 0 | 87630820 | 259240 | 88992320 | 303409 | 72890230 | 153293 | 87247120 | 131938 | 828260 | 10070 | 109890 | 600 | 45220 | 197 | 46520 | 273 | 45030 | 154 | 43480 | 161 | 90000 | 2000 | 88000 | 0 | 180250 | 178000 | 12 | 2.412 | 2.2107 |  | 27.646 | 0 | 184356.7
2025-05-16 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 5:02 | 17:22 | 358.4 | 347.9 | 382.2 | 380.7 | 372.6 | 356.8 | 388 | 366.1 | 379.8 | 381.7 | 384.7 | 380.9 | 379.6 | 381 | 383.8 | 382.6 | 360.4 | 366.1 | 385.3 | 387.9 | 399.8 | 394.4 | 397 | 394.5 | 396.1 | 392.2 | 397.1 | 393.9 | 402.7 | 400.7 | 393.7 | 393.2 | 373.1 | 350.4 | 353 | 356.5 | 361.4 | 361.1 | 373.6 | 359.5 | 364.9 | 401.9 | 422.8 | 397.7 | 401.2 | 414.6 | 446.6 | 442 | 476.9 | 421.1 | 402.5 | 393.3 | 389.1 | 410.7 | 407.2 | 413.2 | 430.4 | 393.7 | 347.9 | 397.1 | 379.3 | 357.1 | 388.1 | 912.7 | 898.9 | 909.8 | 914.6 | 931.9 | 911.5 | 897.9 | 914.9 | 927.3 | 900.8 | 893.8 | 900 | 873.9 | 855.4 | 866.8 | 897.4 | 899.5 | 891.3 | 999 | 909.3 | 872.4 | 919.8 | 881.4 | 880 | 912.3 | 917 | 901.5 | 906.6 | 921.6 | 937.1 | 940.7 | 943.4 | 947.2 | 1028.7 | 936.8 | 932.6 | 885 | 877.7 | 930.8 | 902.5 | 942.4 | 976.6 | 936.8 | 947 | 933.7 | 927.8 | 949.1 | 941.8 | 952.4 | 837.9 | 882.8 | 892.8 | 915.1 | 902.2 | 902.5 | 899.6 | 892.9 | 902.1 | 883.5 | 852.8 | 861.5 | 907.8 | 901.6 | 888.2 | 907.5 | 895.2 | 897.7 | 888.3 | 842.6 | 897.8 | 906.3 | 887.3 | 885.2 | 871.5 | 910.1 | 970.3 | 877.6 | 882 | 893 | 897.5 | 892.6 | 890.1 | 900.6 | 895.1 | 857.2 | 932.4 | 842.2 | 777 | 897.8 | 838.6 | 892.2 | 894.2 | 891.5 | 838 | 895.7 | 897.6 | 880.4 | 885.4 | 890.5 | 878.4 | 942.5 | 915.2 | 846.7 | 795.4 | 807.6 | 798.9 | 793 | 789.4 | 788.3 | 790.8 | 799.1 | 803.6 | 794.5 | 811.3 | 813.3 | 805 | 761.4 | 687.6 | 814.1 | 804.9 | 799.1 | 806.7 | 801.2 | 794.6 | 802.6 | 792.9 | 805.4 | 785.7 | 802.2 | 786.2 | 791.7 | 756.5 | 751.6 | 756.7 | 879.7 | 862.3 | 779.8 | 908.1 | 919.5 | 923.3 | 939.6 | 910.6 | 1016.9 | 938.9 | 874 | 843.1 | 839.6 | 920.1 | 840 | 944.3 | 790 | 791.5 | 870 | 753.9 | 713.8 | 937.1 | 902.3 | 939.8 | 929.9 | 923.8 | 914 | 1015 | 1002.6 | 830.4 | 838.7 | 761.8 | 762.6 | 752.9 | 788.5 | 771 | 789 | 772.7 | 761.8 | 761.1 | 761.7 | 796.7 | 787.5 | 788.3 | 788.8 | 773.7 | 770 | 749 | 793.9 | 759.7 | 784.8 | 751 | 783.7 | 793.5 | 787.5 | 803.7 | 802.2 | 790 | 793.1 | 799.1 | 839 | 864.4 | 887.4 | 845.8 | 900.3 | 949.6 | 897.6 | 872.9 | 866.9 | 907.6 | 900.9 | 870.7 | 942.8 | 914.4 | 828.3 | 937.6 | 925.2 | 695 | 694 | 902.9 | 745.8 | 861.2 | 773.3 | 767.6 | 767.8 | 773.9 | 753.3 | 766.3 | 768 | 769.3 | 763.5 | 782 | 853.5 | 781 | 780.5 | 743 | 728.3 | 729.9 | 765.2 | 777.2 | 771.6 | 775.2 | 780.1 | 860 | 774.7 | 761.6 | 790.5 | 774.9 | 704.3 | 780.9 | 791.6 | 751.4 | 745.8 | 740.1 | 850.2 | 733.5 | 768 | 761.5 | 759.6 | 720.1 | 697.4 | 778 | 799.8 | 727.8 | 744.1 | 772.8 | 770.7 | 764.7 | 763.1 | 773.6 | 784.5 | 813.4 | 735.3 | 736.2 | 749.7 | 753.5 | 760 | 757.9 | 789.5 | 797 | 803.9 | 792 | 793.3 | 800.8 | 794.5 | 799.4 | 796.6 | 786.3 | 752.5 | 760 | 799.9 | 716.2 | 757.6 | 770.3 | 846.1 | 801.9 | 799.3 | 775.3 | 826.5 | 813.8 | 853.2 | 760 | 809.2 | 760.1 | 763.1 | 732.4 | 774.7 | 773.6 | 773.5 | 0 | 32 | 0 | 0 | 3.76 | 3.53 | 0 | 0 | 87701020 | 259428 | 89062350 | 303668 | 72958860 | 153506 | 87314100 | 132160 | 828960 | 10070 | 110560 | 610 | 70200 | 188 | 70030 | 259 | 68630 | 213 | 66980 | 222 | 140000 | 0 | 134000 | 2000 | 275840 | 274000 | 12.3333 | 3.76 | 3.53 |  | 32 | 0 | 278251.9
2025-05-17 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 5:05 | 17:30 | 306 | 298 | 325.6 | 326 | 321.1 | 307.8 | 331.3 | 313.8 | 327.8 | 328.9 | 329.3 | 327.5 | 328.6 | 329.4 | 333.7 | 333 | 310.4 | 316.7 | 330.4 | 333.7 | 343.8 | 340.3 | 343.5 | 341.5 | 340.4 | 339.1 | 343.9 | 342.7 | 348.2 | 345.7 | 341.7 | 340.7 | 320.3 | 301.4 | 304.7 | 307.9 | 313.9 | 313.9 | 321.9 | 312.9 | 320.4 | 346.8 | 362.9 | 342.2 | 347.3 | 357.6 | 387 | 384.7 | 414.3 | 369.3 | 352.1 | 346.2 | 342.9 | 360.7 | 356.9 | 361 | 374.2 | 343.4 | 303.9 | 346.2 | 329.5 | 312.4 | 340.2 | 783.3 | 768.3 | 772.5 | 773.7 | 784.5 | 766.8 | 768 | 781.8 | 786.7 | 766.5 | 755.5 | 763 | 733.5 | 723.7 | 781.1 | 790.3 | 788 | 773.7 | 823.3 | 797 | 755.4 | 799.1 | 760.1 | 754.9 | 781 | 781.5 | 778.2 | 777.3 | 758.6 | 773.4 | 776.6 | 783 | 792.1 | 854.7 | 786.2 | 784.8 | 736.1 | 736.3 | 785.9 | 763.3 | 788.4 | 818.3 | 781.1 | 791.8 | 778.9 | 770.2 | 798.5 | 793.6 | 775.2 | 724.7 | 751.1 | 778.6 | 797.4 | 791 | 791.7 | 794.7 | 783 | 786.5 | 789.7 | 749 | 756.1 | 795.9 | 793.5 | 778.3 | 794.8 | 782.6 | 783.9 | 779.1 | 767 | 787 | 795.5 | 778.7 | 779.1 | 747.7 | 785.4 | 838.5 | 760.8 | 760.1 | 775.5 | 776.8 | 773.4 | 767.5 | 782 | 779.4 | 748.2 | 840 | 732.9 | 676.2 | 779 | 728 | 778.6 | 781.6 | 775.7 | 678.2 | 788.1 | 770.5 | 775.2 | 780.6 | 757.9 | 765.9 | 826 | 800.6 | 739.8 | 675.7 | 690.1 | 681.7 | 679.9 | 679.7 | 678.8 | 683.3 | 690.3 | 696.5 | 689.9 | 692.6 | 697.6 | 699.2 | 657 | 600.1 | 714.9 | 698.5 | 698.3 | 701.4 | 695.9 | 692 | 697.2 | 693.2 | 699.9 | 685.4 | 699 | 686.2 | 689.8 | 659.5 | 655.8 | 661.9 | 770.2 | 751.7 | 657.1 | 780.7 | 788.4 | 789.9 | 813.1 | 793.9 | 868.4 | 799.7 | 745.8 | 726.8 | 711.2 | 775.9 | 749 | 820.5 | 690.2 | 693 | 766.2 | 660.8 | 618.8 | 775.5 | 788.4 | 804.1 | 793.6 | 785 | 774.5 | 869 | 856 | 724.5 | 731.9 | 669.9 | 666.6 | 667.6 | 685.8 | 679.4 | 694.4 | 676.4 | 664.5 | 667 | 670 | 688.1 | 683.6 | 684.7 | 687.8 | 681.7 | 684 | 660.4 | 696.7 | 667.5 | 678.9 | 661.3 | 688 | 692.4 | 687.7 | 702.8 | 703.6 | 688 | 690.5 | 697.3 | 759.9 | 781 | 798.1 | 758.9 | 805.5 | 842.9 | 770 | 796.2 | 767.5 | 799.7 | 790.9 | 765.2 | 813 | 810.4 | 728.4 | 825.4 | 818 | 620.7 | 614 | 793.5 | 659.9 | 760.2 | 701.2 | 695.4 | 691.4 | 694.8 | 681 | 683.1 | 695.2 | 680.3 | 680.1 | 704.9 | 758.2 | 701.7 | 701 | 674.5 | 662.9 | 657.6 | 686.3 | 697.8 | 690.5 | 689.9 | 693.1 | 760 | 688.3 | 683.9 | 696.7 | 687.9 | 632.4 | 694.2 | 707.3 | 667.7 | 661.2 | 669.8 | 750 | 670.8 | 699.7 | 693.4 | 693.2 | 660.7 | 619.4 | 680.2 | 728.8 | 659.4 | 666 | 706.3 | 700.5 | 687.5 | 696.3 | 695.5 | 699.6 | 741.3 | 655.6 | 672.1 | 661.8 | 688.1 | 687 | 688 | 706.8 | 713 | 722.8 | 694 | 711.2 | 719 | 710.2 | 716.5 | 720.4 | 704.8 | 679.3 | 674 | 720 | 642.5 | 680.3 | 692.5 | 750 | 714.3 | 711.5 | 693 | 717.1 | 726 | 754.7 | 676.1 | 720.6 | 677.3 | 685.3 | 656.3 | 693.5 | 694.3 | 689.9 | 0 | 30.13 | 0 | 0 | 3.22 | 3 | 0 | 0 | 87760930 | 259609 | 89123080 | 303912 | 73018460 | 153622 | 87373640 | 132283 | 829560 | 10080 | 111150 | 610 | 59910 | 181 | 60730 | 244 | 59600 | 116 | 59540 | 123 | 120000 | 2000 | 118000 | 0 | 239780 | 238000 | 12.4167 | 3.22 | 3 |  | 30.13 | 0 | 242923.9
2025-05-18 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 5:12 | 17:20 | 189 | 183.3 | 201.3 | 201.4 | 198.4 | 189.7 | 205 | 193.5 | 202.2 | 203.2 | 203 | 202 | 203.3 | 203.1 | 205.8 | 204.8 | 191.1 | 196.1 | 205.1 | 206.5 | 213.1 | 211.1 | 212.9 | 212 | 210.3 | 209.2 | 213.5 | 212.4 | 215.6 | 214.1 | 211.4 | 208.7 | 200.3 | 187.2 | 187.9 | 190.3 | 193.1 | 192.7 | 200 | 193.4 | 198.3 | 217.7 | 228.2 | 214.8 | 218.3 | 225.6 | 244.1 | 241.9 | 257.9 | 229.7 | 219.8 | 214.4 | 211.5 | 222.7 | 220.4 | 221.9 | 233.8 | 213.9 | 188.2 | 213.3 | 202.5 | 193 | 211 | 483.8 | 475.2 | 479 | 479 | 487.4 | 476.5 | 476.5 | 486.3 | 490 | 477.9 | 471.2 | 476.4 | 457.7 | 450.9 | 474.8 | 483.5 | 483.4 | 477 | 505.3 | 486.4 | 463.3 | 490.3 | 464.6 | 464.4 | 481.3 | 483.9 | 479.2 | 480.2 | 467.5 | 476.1 | 477.9 | 482.1 | 486.4 | 527.3 | 482 | 480.3 | 452.2 | 450.8 | 483 | 467.3 | 487.3 | 503.6 | 483.4 | 490.4 | 483.4 | 475.7 | 495.3 | 491.5 | 495.2 | 446 | 463.5 | 480 | 495.4 | 487.9 | 488.3 | 486.3 | 480 | 487.2 | 489.8 | 462.3 | 465.9 | 494.1 | 492.6 | 481.6 | 493.5 | 483.2 | 484.7 | 482.8 | 488.8 | 488.7 | 495.8 | 484.5 | 485.3 | 479.4 | 497 | 533.5 | 482.5 | 483.3 | 490.4 | 492.8 | 490.9 | 487.3 | 496 | 494.9 | 473.8 | 513.1 | 463.2 | 432 | 495.2 | 460.2 | 492.7 | 492 | 489.8 | 481.6 | 485.2 | 494.1 | 487.7 | 489.1 | 489.9 | 484.1 | 518.9 | 504.9 | 466.4 | 406.4 | 415.6 | 410.3 | 409.2 | 410.5 | 409.7 | 414.5 | 421.2 | 425.7 | 419.8 | 418.9 | 422.3 | 423.7 | 397.5 | 361.2 | 431.7 | 424.7 | 423.7 | 428.6 | 425.7 | 421.3 | 426.2 | 420.9 | 428.8 | 416.8 | 426 | 422.4 | 422.6 | 401.3 | 401.2 | 404 | 482.8 | 470.5 | 422.8 | 487.5 | 492.6 | 492.4 | 508.8 | 496.8 | 544.1 | 499.4 | 466.6 | 466.3 | 441.6 | 483.2 | 481 | 511.8 | 431.3 | 432.3 | 478.6 | 411.6 | 400 | 498.7 | 491.5 | 500.8 | 493.4 | 487.7 | 480.2 | 543.8 | 535.9 | 441.4 | 447.2 | 407.3 | 405.3 | 400.2 | 414.3 | 412.8 | 423.4 | 412.2 | 404.5 | 406 | 406.7 | 424.5 | 417.9 | 421.2 | 420.5 | 417.4 | 412 | 393.2 | 422.3 | 404.1 | 394.4 | 398.9 | 414.6 | 420.9 | 418.3 | 432.3 | 424.1 | 419.8 | 422.2 | 424.9 | 458.1 | 471 | 482.8 | 460.4 | 490.9 | 515.9 | 487 | 486.8 | 471 | 492.2 | 487.4 | 471.3 | 511.7 | 499.5 | 454.7 | 510 | 505.4 | 388 | 383.1 | 378.2 | 490 | 468 | 407.1 | 404.6 | 402.9 | 403.9 | 396.6 | 396.6 | 404.8 | 392.9 | 394.7 | 411.4 | 451.5 | 410.2 | 410.6 | 391.4 | 384.6 | 381.3 | 401.8 | 400.9 | 404.8 | 405.3 | 408.8 | 451 | 408.2 | 400.7 | 416.2 | 407.7 | 368.2 | 410.6 | 416.8 | 395 | 392 | 379.4 | 435.2 | 376.7 | 397.5 | 393.7 | 393.6 | 372.7 | 346.9 | 400.6 | 416.8 | 372.4 | 374.9 | 400.6 | 395.6 | 387.8 | 392.1 | 399.1 | 405.6 | 425.1 | 366.1 | 377.7 | 385.3 | 387.5 | 390 | 391 | 406.5 | 410 | 416.9 | 398.9 | 409.2 | 415.5 | 410.4 | 413.8 | 416 | 407.4 | 389.2 | 392 | 417.6 | 369.5 | 390.4 | 398.1 | 434.6 | 412.3 | 412.2 | 398.8 | 413.9 | 419.3 | 438.5 | 388.2 | 416.6 | 387.4 | 396.4 | 375.8 | 397.8 | 397.2 | 397.7 | 0 | 27.2893 | 0 | 0 | 1.96 | 1.79 | 0 | 0 | 87798120 | 259803 | 89161120 | 304187 | 73055550 | 153776 | 87408740 | 132447 | 829930 | 10080 | 111510 | 610 | 37190 | 194 | 38040 | 275 | 37090 | 154 | 35100 | 164 | 74000 | 0 | 72000 | 0 | 147420 | 146000 | 12.1333 | 1.96 | 1.79 |  | 27.2893 | 0 | 147793.8
2025-05-19 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 6:45 | 17:23 | 372.9 | 366.1 | 397.1 | 398 | 391 | 377.5 | 404.3 | 381.9 | 396.9 | 400.1 | 401.6 | 398.3 | 400.2 | 400.2 | 400.2 | 404.3 | 403.9 | 378.1 | 382.8 | 399.7 | 404.7 | 415.2 | 411 | 414.9 | 414 | 410.5 | 407.5 | 414.8 | 412.6 | 417.8 | 416.7 | 411.8 | 410.7 | 393 | 370.3 | 370.3 | 373.2 | 377.2 | 382.7 | 382.7 | 394.2 | 380.8 | 394.1 | 425.2 | 445.1 | 421.7 | 424.7 | 436.7 | 471.6 | 466.2 | 500.2 | 444.1 | 425 | 416.4 | 412.1 | 433.6 | 429.4 | 433.5 | 450 | 413.7 | 365.8 | 417.5 | 417.5 | 939.4 | 925.3 | 932.6 | 934.9 | 942.5 | 926.5 | 923.8 | 945.4 | 944.7 | 927.1 | 891 | 923.8 | 888.1 | 878.5 | 925.6 | 938.6 | 939.3 | 924.7 | 977.5 | 946.7 | 900.2 | 947 | 904.7 | 901.1 | 928.1 | 939.8 | 930 | 935.2 | 907.1 | 926.6 | 928.1 | 937.8 | 939.8 | 1013.4 | 937 | 910.1 | 883.8 | 875.1 | 939.9 | 911.3 | 941.4 | 976.7 | 933.4 | 951 | 937.6 | 929.1 | 960.4 | 954.6 | 925.7 | 858.7 | 895.9 | 931.3 | 953.6 | 940.4 | 947.3 | 944 | 936.1 | 947.1 | 951.1 | 903 | 908.4 | 960.9 | 957.4 | 943.1 | 961.9 | 947.5 | 947.9 | 940.7 | 950.2 | 945.1 | 956.9 | 937.8 | 936.1 | 924.8 | 970.6 | 1031.8 | 943.5 | 944.4 | 955.2 | 959.4 | 957.6 | 950.1 | 964.5 | 957.8 | 919.8 | 988.9 | 895.1 | 826.9 | 956.9 | 886.3 | 940.1 | 943.4 | 941.8 | 896.3 | 948.1 | 933.9 | 896.3 | 941.5 | 898 | 930.8 | 991.4 | 965.3 | 878.2 | 847.5 | 860.4 | 852.8 | 848.3 | 850 | 850.1 | 858.3 | 865.4 | 873.2 | 864.3 | 864.3 | 866.8 | 872.2 | 820.6 | 751.4 | 886.7 | 873.5 | 870.5 | 877.2 | 872.7 | 864.6 | 872.2 | 863.4 | 871.9 | 851.7 | 868.5 | 849.7 | 862.8 | 823.3 | 816 | 829.1 | 943.5 | 923.9 | 834.3 | 956.5 | 965.2 | 969.2 | 994.7 | 972.3 | 1066.1 | 980.5 | 914 | 869.9 | 851 | 957.4 | 889 | 993.3 | 836.8 | 849 | 932.6 | 809.3 | 760 | 970 | 967.3 | 981.5 | 967 | 960.4 | 949.3 | 1055 | 1034.5 | 890.1 | 896.2 | 820.7 | 816.7 | 815.5 | 839.2 | 829.7 | 848 | 831.4 | 820 | 818.2 | 822.2 | 854.6 | 846.1 | 848.9 | 851.3 | 831.8 | 830 | 810.7 | 848.6 | 819.8 | 829.9 | 816.2 | 848.1 | 856 | 848.3 | 868.6 | 870.4 | 853.3 | 857 | 863.6 | 878.5 | 901.9 | 938.5 | 892.5 | 945.2 | 991.9 | 906.4 | 942.1 | 918.8 | 963.5 | 950.9 | 919.7 | 986.4 | 942.5 | 882.6 | 975.2 | 977.6 | 745.9 | 746.8 | 947.6 | 789 | 910.3 | 838.5 | 832.7 | 831.1 | 838.6 | 813.6 | 818.5 | 828.7 | 811.2 | 815.6 | 839 | 905.4 | 840.5 | 836.9 | 800.8 | 795.4 | 794.5 | 828.6 | 829.4 | 835.8 | 833.8 | 841.8 | 907 | 834.7 | 830.3 | 850.7 | 836.6 | 766.1 | 841.6 | 848.3 | 806.6 | 803.8 | 819.8 | 912.1 | 808.1 | 837.7 | 830.3 | 831.5 | 790.6 | 740.9 | 830.9 | 872.4 | 791.9 | 792.3 | 844.7 | 837.4 | 823.9 | 838 | 840.4 | 846.7 | 883.3 | 792.7 | 804.5 | 813.2 | 820.7 | 827 | 823.1 | 828.8 | 835.9 | 846.3 | 817.7 | 836.7 | 844.8 | 836.8 | 844.1 | 850 | 836.5 | 790.5 | 793 | 851.1 | 765 | 804 | 817.8 | 884.5 | 844.3 | 845.3 | 814.2 | 849.2 | 853.6 | 890.9 | 800.5 | 851.6 | 803.2 | 811.5 | 776.2 | 822.2 | 820.2 | 818 | 0 | 34.79 | 0 | 0 | 3.97 | 3.63 | 0 | 0 | 87870000 | 260005 | 89235280 | 304474 | 73127670 | 153970 | 87479510 | 132624 | 830650 | 10090 | 112220 | 620 | 71880 | 202 | 74160 | 287 | 72120 | 194 | 70770 | 177 | 144000 | 2000 | 142000 | 2000 | 288930 | 286000 | 10.6333 | 3.97 | 3.63 |  | 34.79 | 0 | 293791.3
2025-05-20 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:50 | 17:34 | 222.7 | 216.3 | 237.1 | 237.6 | 233.6 | 223.9 | 241.3 | 226.8 | 238.6 | 239.7 | 238.9 | 237.5 | 239.4 | 239.8 | 242.5 | 240.7 | 225.7 | 229.6 | 240.7 | 242.8 | 250.1 | 247.2 | 249.5 | 247.1 | 248.2 | 245.6 | 250.4 | 248.5 | 252.8 | 251.2 | 247.2 | 247.6 | 236.4 | 221.5 | 222 | 225.6 | 228.2 | 227 | 236.1 | 227.9 | 234 | 255.2 | 269.1 | 252 | 255.7 | 265.2 | 286.1 | 284.1 | 301.8 | 268.9 | 256.4 | 251 | 247 | 260.3 | 257.7 | 260.4 | 273.9 | 249.7 | 220.2 | 249.7 | 249.7 | 236.7 | 225.5 | 567.9 | 556.7 | 562.9 | 562.9 | 572.6 | 560.8 | 558.7 | 570.4 | 576.1 | 560.9 | 553.9 | 560.4 | 538.6 | 530.5 | 554 | 563.7 | 562.6 | 556.1 | 590.9 | 569.7 | 541.1 | 574.7 | 547.1 | 545 | 565.2 | 568.1 | 561.2 | 561.6 | 556.9 | 563.3 | 567.4 | 569.6 | 576.5 | 625.2 | 572.3 | 558.9 | 533.3 | 533.7 | 569.5 | 551.1 | 574.5 | 594.8 | 572.4 | 577.6 | 569.1 | 558.6 | 581.5 | 577.8 | 584.2 | 525.6 | 545.9 | 558.7 | 575.1 | 567.9 | 566.5 | 565 | 555.5 | 565.4 | 569.7 | 537.7 | 541.3 | 574.7 | 572.3 | 559.5 | 573.2 | 561.9 | 564 | 562.6 | 568.7 | 569.7 | 577.6 | 565.3 | 565.7 | 558.2 | 586 | 628.5 | 567.3 | 566.9 | 578.5 | 580.2 | 575.2 | 571.6 | 580.6 | 580.7 | 565 | 600.3 | 542.5 | 509 | 579.4 | 538.7 | 576 | 574.2 | 570.2 | 573.9 | 574.5 | 577.8 | 569.7 | 570.6 | 571.8 | 563.5 | 605.3 | 588.5 | 544.8 | 514.4 | 524.9 | 516.9 | 515.9 | 519.8 | 516.7 | 520.6 | 526.9 | 532.5 | 527.4 | 526.8 | 530.4 | 533.9 | 497.5 | 455.9 | 548.2 | 533.4 | 533.3 | 535.1 | 530.6 | 527.3 | 532.7 | 528.4 | 532 | 519.6 | 529.4 | 520.7 | 526.1 | 500.4 | 496.5 | 508.7 | 570.5 | 554.3 | 499.9 | 578.2 | 585 | 585.6 | 602 | 589.1 | 645.9 | 594.4 | 556.2 | 557 | 529.4 | 580.9 | 545 | 604.9 | 509.1 | 508.9 | 565.9 | 485.6 | 455.7 | 598 | 590.8 | 600.6 | 592.4 | 581 | 579 | 647.5 | 638.2 | 546 | 556.2 | 504.7 | 502.5 | 502.1 | 514 | 508.9 | 522.4 | 512.3 | 505.2 | 504.9 | 506.4 | 517.9 | 516.7 | 518.6 | 521.8 | 521.2 | 520 | 505.3 | 528.9 | 507 | 514.8 | 502.4 | 520.2 | 530.3 | 522.3 | 540.2 | 532.5 | 522.8 | 525.7 | 530.5 | 536.3 | 553.3 | 564.3 | 538.9 | 571.9 | 601 | 569.4 | 568.8 | 548.5 | 573 | 566.3 | 547.9 | 599.1 | 584.6 | 533.8 | 595.6 | 593.3 | 545 | 447.7 | 570 | 470 | 474.6 | 504.6 | 499.5 | 495.8 | 498.5 | 488.5 | 492.3 | 498.4 | 491.6 | 492.6 | 511.6 | 549.6 | 507.6 | 507.2 | 490 | 479.3 | 471.7 | 493.1 | 505.6 | 500.2 | 500.4 | 508.1 | 540 | 500.5 | 496.6 | 508.7 | 504.8 | 456.5 | 505.4 | 515.9 | 486.1 | 482.3 | 500.1 | 560.9 | 489.5 | 506.6 | 503 | 504.4 | 484.3 | 449.4 | 523.9 | 541.7 | 476.4 | 484.7 | 524.6 | 519.2 | 514.3 | 516.8 | 517.8 | 517.6 | 546.3 | 488.1 | 496.2 | 490.3 | 511.4 | 509 | 513 | 508.1 | 507 | 521.4 | 495.6 | 509.8 | 517.6 | 505.1 | 516.1 | 522 | 507.7 | 469.5 | 477 | 518.6 | 459.6 | 487.2 | 498 | 543.4 | 508.9 | 508.8 | 494.7 | 512.4 | 519.6 | 540 | 483.4 | 513 | 483.6 | 497.1 | 466.9 | 495 | 499.4 | 492.4 | 0 | 28.83 | 0 | 0 | 2.26 | 2.06 | 0 | 0 | 87913740 | 260187 | 89280190 | 304714 | 73171380 | 154119 | 87521380 | 132730 | 831090 | 10090 | 112650 | 620 | 43740 | 182 | 44910 | 240 | 43710 | 149 | 41870 | 106 | 88000 | 0 | 86000 | 0 | 174230 | 174000 | 12.7333 | 2.26 | 2.06 |  | 28.83 | 0 | 178420.3
2025-05-21 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:59 | 5:30 | 154.7 | 149.9 | 165.2 | 165 | 161.8 | 154.8 | 168.4 | 157.4 | 165.8 | 163 | 166.6 | 165.1 | 166.1 | 164.6 | 168.2 | 167.5 | 155.1 | 160 | 167.5 | 168.9 | 174.3 | 172.2 | 171.4 | 170.8 | 170.1 | 169.6 | 174.8 | 173.8 | 176.9 | 174.1 | 172.9 | 168.5 | 163.1 | 151.9 | 152.8 | 155.2 | 157.7 | 154.6 | 161.6 | 158.3 | 161.9 | 177.8 | 186.8 | 174.2 | 174.2 | 176 | 183.5 | 198.1 | 195.9 | 208.5 | 186.1 | 176.5 | 173 | 172.8 | 180.3 | 177.4 | 178.5 | 190.4 | 172.4 | 176 | 173.6 | 165.4 | 170 | 396.4 | 389.2 | 394.6 | 393.4 | 400.4 | 390.8 | 390.6 | 399.2 | 402.3 | 392.4 | 386.4 | 391.3 | 375.3 | 370.1 | 384.5 | 395.7 | 395.7 | 390 | 414.2 | 398.7 | 378.6 | 402 | 381.2 | 380.9 | 394.1 | 397.6 | 393.1 | 392.9 | 385.7 | 391.9 | 394.6 | 397.5 | 401.8 | 435.6 | 399.2 | 396.7 | 371.3 | 370.3 | 397.5 | 382.3 | 401.7 | 415.3 | 396.8 | 403.7 | 396.7 | 390.3 | 406.9 | 404.1 | 407.2 | 366.6 | 380.9 | 392.3 | 404.3 | 399.2 | 399 | 397.1 | 391.2 | 397.3 | 399.6 | 377.5 | 380.3 | 403 | 402.6 | 392.9 | 402.7 | 394.5 | 394.7 | 393.4 | 399.3 | 399.4 | 403.9 | 394.5 | 400.4 | 390.1 | 407.2 | 436 | 393.5 | 394.8 | 400.9 | 402.7 | 400.6 | 397.1 | 403.5 | 403.2 | 385.4 | 416.5 | 376.2 | 347.1 | 403 | 372.7 | 400 | 402.2 | 397.2 | 402.3 | 401.6 | 390.8 | 395.5 | 397.7 | 394.5 | 392.5 | 424.1 | 412.1 | 372.9 | 353 | 362.2 | 354.3 | 355.9 | 359.1 | 357.8 | 357.4 | 362.6 | 368.3 | 362.7 | 361.2 | 367 | 370.2 | 342.8 | 313.8 | 378.2 | 367.1 | 367.4 | 368.7 | 364.3 | 362.3 | 366 | 364 | 364.7 | 356.6 | 363.5 | 359.2 | 362.2 | 343.8 | 341.1 | 351.5 | 393.9 | 383 | 346.8 | 399.6 | 403.3 | 402.5 | 417.6 | 407.6 | 447 | 409.9 | 384.2 | 384.7 | 365.8 | 400.1 | 388 | 409 | 351.7 | 352 | 389.5 | 335 | 313 | 408.2 | 406.9 | 416 | 407 | 397.9 | 398.1 | 444.5 | 438.1 | 376.5 | 384.3 | 350.2 | 346.3 | 346.4 | 351.4 | 353.4 | 362.1 | 354.4 | 347.5 | 348.8 | 352.5 | 358.5 | 355.4 | 359.5 | 358.8 | 362.6 | 364 | 349.9 | 361.5 | 349.4 | 353.8 | 346.5 | 357.1 | 365.5 | 358.5 | 378.7 | 367.2 | 358.1 | 362.1 | 364.5 | 376.5 | 386.4 | 396.3 | 377.5 | 402.2 | 422.3 | 393.2 | 398.8 | 385 | 401.8 | 398.1 | 384.7 | 420.5 | 408.7 | 373.1 | 416.7 | 413.2 | 383.4 | 311.6 | 400 | 331 | 383 | 353.6 | 350.6 | 345.7 | 345.6 | 342.1 | 344.6 | 348.4 | 342.7 | 341.8 | 357 | 383.3 | 353.9 | 354.4 | 342.1 | 336 | 326.5 | 343.6 | 354.1 | 350.2 | 348.9 | 356.3 | 377 | 350.6 | 345.7 | 355.7 | 353.2 | 318.9 | 351.9 | 360.9 | 338.7 | 336.7 | 355.7 | 387.4 | 343.7 | 355 | 351.4 | 351.7 | 338 | 311.5 | 367.4 | 379.7 | 328.7 | 339 | 370.7 | 366.9 | 362.5 | 364.1 | 366.1 | 367.9 | 385.6 | 342.9 | 348.3 | 349.6 | 359 | 360 | 361.3 | 349.7 | 349.6 | 361.7 | 343.6 | 349.4 | 357.7 | 355 | 356.9 | 363.5 | 350.7 | 340.6 | 351 | 362.8 | 320.5 | 336.9 | 347.6 | 376.6 | 352.4 | 353.4 | 340.2 | 369.8 | 358.8 | 377.8 | 335.6 | 355 | 335.1 | 346.3 | 323.6 | 347.7 | 349.8 | 341.2 | 0 | 27.83 | 0 | 0 | 1.65 | 1.51 | 0 | 0 | 87944130 | 260366 | 89311240 | 304935 | 73201460 | 154202 | 87550360 | 132861 | 831400 | 10090 | 112940 | 630 | 30390 | 179 | 31050 | 221 | 30080 | 83 | 28980 | 131 | 62000 | 0 | 58000 | 2000 | 120500 | 120000 | 0.51667 | 1.65 | 1.51 |  | 27.83 | 0 | 124193.2
2025-05-22 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:54 | 17:13 | 346.7 | 341.4 | 370.6 | 371.6 | 367.3 | 352.9 | 376.7 | 355.8 | 372.7 | 378 | 373.2 | 370.8 | 379.8 | 377.2 | 383.7 | 381.2 | 354.3 | 358.4 | 372 | 378 | 387.7 | 383.2 | 386 | 388.9 | 383.4 | 379.4 | 386.7 | 385.3 | 390.9 | 389.4 | 383.3 | 383.6 | 375.6 | 351.8 | 354.1 | 357.8 | 363.5 | 361.3 | 375.7 | 362.3 | 373.5 | 406.5 | 429 | 404.3 | 405.5 | 417.4 | 450.5 | 445.8 | 476.2 | 418.2 | 403.5 | 398.4 | 396.1 | 407.8 | 401.9 | 408.7 | 425.5 | 391.5 | 342.8 | 392.3 | 373.3 | 350.7 | 392.9 | 691.2 | 676.7 | 864.2 | 864.2 | 680 | 682.2 | 677.3 | 700 | 701.7 | 677.2 | 669 | 678.7 | 651.2 | 643 | 679.7 | 693.4 | 876.8 | 678.7 | 724 | 698.5 | 663.1 | 702.3 | 664.3 | 666.5 | 687.4 | 873.2 | 689.2 | 687.3 | 670.3 | 687.3 | 691.4 | 702.1 | 705.1 | 764.6 | 881.6 | 695.7 | 653.5 | 648.3 | 701 | 664 | 705.9 | 730.2 | 695 | 706.2 | 692 | 861.5 | 714.5 | 708.2 | 713.5 | 782.2 | 666.1 | 685.8 | 702.2 | 694.4 | 693.9 | 883.5 | 680.6 | 691.6 | 695.2 | 657 | 660.1 | 896.8 | 901.8 | 877.3 | 900.6 | 882.4 | 885.8 | 680.2 | 895.6 | 690.9 | 698.8 | 685.6 | 699.7 | 878.7 | 931 | 767.8 | 694.6 | 898.1 | 707.6 | 710.5 | 913.7 | 703.1 | 710.9 | 708.5 | 677.4 | 731.7 | 858.1 | 606.6 | 709.9 | 655.3 | 693.7 | 701.6 | 693 | 909.5 | 695.3 | 695.2 | 687 | 691.3 | 688.1 | 890 | 740 | 925.7 | 659.9 | 830.5 | 844 | 833.2 | 833.2 | 834.3 | 830.5 | 832 | 841 | 848.3 | 840.3 | 846.5 | 850.3 | 851.6 | 798.3 | 729 | 867.2 | 850.6 | 845.3 | 851.3 | 846.3 | 837.4 | 848.1 | 838 | 845.4 | 826.2 | 843.8 | 822.2 | 841.1 | 797.6 | 788.2 | 807.4 | 693.9 | 676.5 | 796.2 | 717.5 | 717.7 | 716.2 | 748 | 724.2 | 1033.1 | 953 | 887.2 | 889.8 | 846.7 | 924 | 890 | 958.6 | 805.7 | 623.5 | 693.3 | 594.1 | 554.5 | 699 | 721.7 | 964.3 | 726 | 709.9 | 930.9 | 790.4 | 792 | 871.8 | 880.3 | 800.7 | 802.2 | 792.1 | 815.2 | 807.2 | 827.1 | 818.5 | 807.7 | 803.9 | 805.6 | 831.5 | 824.1 | 823.6 | 825.8 | 820.3 | 824 | 790.7 | 833.5 | 807.3 | 826.6 | 799.9 | 828.4 | 835.4 | 829.9 | 855.4 | 850.6 | 829.8 | 833.1 | 842.4 | 645.4 | 661 | 683.2 | 616 | 692.1 | 729.8 | 692.2 | 903.9 | 666.5 | 693.4 | 692.1 | 665.3 | 951.4 | 706.5 | 648.2 | 724.2 | 713.9 | 541.8 | 547.7 | 693.6 | 573.5 | 663.7 | 800.9 | 797.6 | 798 | 803.2 | 784.2 | 789.8 | 794.4 | 783 | 785.6 | 810.6 | 881.2 | 809.7 | 808.1 | 773.8 | 763 | 758.3 | 785.8 | 800 | 794.4 | 794.2 | 803.3 | 870.3 | 792.1 | 791.6 | 807.9 | 797.8 | 732.1 | 804.3 | 820 | 774.7 | 770.6 | 791.8 | 877.1 | 776.8 | 805.7 | 798.5 | 803 | 762.9 | 717.6 | 816.2 | 852.7 | 762.5 | 768.1 | 822.1 | 813.6 | 803.9 | 817.3 | 813.3 | 821.3 | 861.1 | 772.9 | 784.2 | 799.1 | 802.1 | 806 | 804.6 | 805.7 | 806 | 819.1 | 786.1 | 808.5 | 817.7 | 803.9 | 817.9 | 826.3 | 812.3 | 781.5 | 788 | 825.8 | 739.4 | 777.4 | 790 | 859.9 | 815 | 815.6 | 786.1 | 851.4 | 824.6 | 859 | 773.3 | 819.1 | 773.6 | 782.1 | 744.5 | 790.8 | 792.9 | 791.6 | 0 | 35.66 | 0 | 0 | 3.91 | 3.5 | 0 | 0 | 88003760 | 260538 | 89375220 | 305161 | 73263700 | 154281 | 87617920 | 132967 | 832010 | 10100 | 113580 | 630 | 59630 | 172 | 63980 | 226 | 62240 | 79 | 67560 | 106 | 122000 | 2000 | 128000 | 0 | 253410 | 250000 | 12.3167 | 3.91 | 3.5 |  | 35.66 | 0 | 258606.3
2025-05-23 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:38 | 17:34 | 570.4 | 554.7 | 609.5 | 605 | 590.4 | 577 | 618.4 | 584 | 604.1 | 607.3 | 614.6 | 612 | 603.7 | 608.9 | 615.6 | 617.7 | 579.1 | 585.6 | 609.8 | 620.5 | 641.5 | 631 | 637 | 636.6 | 632.8 | 625.2 | 634.2 | 628.6 | 644.3 | 641.4 | 631.7 | 629.5 | 591.8 | 560.6 | 564.4 | 567.7 | 577.9 | 583.1 | 595.1 | 574.7 | 594 | 638.1 | 672.1 | 633.3 | 636.1 | 656.3 | 707 | 703.1 | 752.1 | 679.4 | 646.2 | 640.4 | 639.8 | 663.4 | 654.2 | 650.9 | 685.1 | 624.4 | 555.4 | 633.2 | 617.6 | 572.6 | 625.9 | 1444.2 | 1415.9 | 1451.1 | 1455.3 | 1436.2 | 1423.8 | 1397.7 | 1449 | 1434.3 | 1399 | 1368.8 | 1399.5 | 1368.9 | 1357.9 | 1445.2 | 1446.2 | 1458.7 | 1407 | 1496.8 | 1486.8 | 1388.5 | 1445.8 | 1415.2 | 1382.9 | 1414.8 | 1428.4 | 1446.8 | 1427.9 | 1409.5 | 1439.8 | 1463.5 | 1478.7 | 1438.7 | 1535 | 1456.5 | 1434.2 | 1386.1 | 1377.2 | 1440.9 | 1398.6 | 1436.6 | 1496.9 | 1442.7 | 1477.8 | 1430 | 1436.7 | 1476.5 | 1469 | 1465.9 | 1358.2 | 1356.8 | 1423.9 | 1431.1 | 1430.9 | 1448.2 | 1461.9 | 1446.3 | 1443.1 | 1422.9 | 1383.7 | 1400.2 | 1438.4 | 1467.5 | 1447.7 | 1473.4 | 1452.9 | 1439.8 | 1429.2 | 1454.2 | 1428.3 | 1453.9 | 1424.5 | 1441.8 | 1418.4 | 1433.3 | 1506.3 | 1399.7 | 1413.3 | 1421.8 | 1423 | 1440.3 | 1416 | 1412.1 | 1401.9 | 1406.6 | 1502.2 | 1374.7 | 1257.8 | 1414.2 | 1330 | 1396.5 | 1417.6 | 1388.1 | 1455.3 | 1387.8 | 1421.3 | 1404.7 | 1410.9 | 1386.4 | 1431.2 | 1480.1 | 1438.2 | 1368.4 | 1292.4 | 1314.6 | 1310.2 | 1316.4 | 1310.7 | 1324.5 | 1316.7 | 1321.6 | 1328.4 | 1330.6 | 1325 | 1327.8 | 1345 | 1270.2 | 1164.8 | 1362.5 | 1344.3 | 1340.5 | 1343.6 | 1332.1 | 1330.1 | 1338.5 | 1332.1 | 1357.5 | 1325.4 | 1363.1 | 1319.5 | 1329.3 | 1291 | 1280.1 | 1270.5 | 1450 | 1432.2 | 1291.5 | 1458.1 | 1465.9 | 1488.6 | 1510.1 | 1468.4 | 1623 | 1458.4 | 1357.7 | 1334.8 | 1313.3 | 1445.3 | 1356 | 1533.7 | 1308.2 | 1329.7 | 1454.7 | 1264.2 | 1179.8 | 1466.5 | 1476.2 | 1536.2 | 1481.2 | 1450.3 | 1474.2 | 1597.7 | 1561.5 | 1404.9 | 1400.6 | 1293.6 | 1306.7 | 1258.9 | 1309 | 1281.4 | 1320.3 | 1329.6 | 1313.9 | 1303.2 | 1293 | 1326.4 | 1336.4 | 1321.4 | 1335.2 | 1338.7 | 1336 | 1304 | 1364.9 | 1316.8 | 1342.6 | 1302.7 | 1352.1 | 1356.7 | 1340.6 | 1349.3 | 1374.4 | 1342.5 | 1353.9 | 1346.8 | 1397.3 | 1415.8 | 1458.8 | 1373.5 | 1445.2 | 1514.8 | 1443.4 | 1462.6 | 1422.9 | 1497.1 | 1464.3 | 1409.5 | 1504 | 1453.9 | 1373 | 1450.6 | 1487.2 | 1130.4 | 1146.7 | 1434.7 | 1214.4 | 1398.5 | 1317.5 | 1313.4 | 1313.3 | 1325 | 1279.2 | 1287.8 | 1296.2 | 1273.3 | 1280.7 | 1318.5 | 1396.6 | 1324.9 | 1320.7 | 1266.9 | 1224.4 | 1258.6 | 1300.6 | 1316.2 | 1307.2 | 1303.4 | 1314.5 | 1400 | 1315.6 | 1315.3 | 1327.8 | 1321 | 1209.3 | 1329 | 1314.6 | 1283.8 | 1270.5 | 1285.9 | 1413 | 1270.7 | 1315.4 | 1300.9 | 1305.1 | 1247.2 | 1168.9 | 1315.3 | 1353.5 | 1255.3 | 1267.9 | 1318.4 | 1319.8 | 1301.8 | 1310 | 1321.8 | 1321 | 1365.9 | 1248.2 | 1247 | 1262 | 1265.1 | 1269 | 1278.5 | 1269.7 | 1296.6 | 1302.3 | 1263.5 | 1300.1 | 1301.9 | 1296.7 | 1301.2 | 1312.7 | 1281.1 | 1251.9 | 1260 | 1324.2 | 1203.2 | 1251.8 | 1278.4 | 1367.8 | 1302.9 | 1311.2 | 1282.5 | 1368 | 1340.7 | 1381.6 | 1275.6 | 1336.9 | 1279.7 | 1263.3 | 1217.3 | 1273.4 | 1293.6 | 1265.8 | 0 | 42.2 | 0 | 0 | 6.56 | 6.05 | 0 | 0 | 88113380 | 260707 | 89487920 | 305386 | 73374960 | 154352 | 87728700 | 133078 | 833120 | 10100 | 114690 | 640 | 109620 | 169 | 112700 | 225 | 111260 | 71 | 110780 | 111 | 222000 | 0 | 222000 | 2000 | 444360 | 444000 | 12.9333 | 6.56 | 6.05 |  | 42.2 | 0 | 453488.8
2025-05-24 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 5:09 | 17:44 | 465.9 | 460.8 | 497.2 | 499.1 | 488.3 | 475.1 | 505.2 | 475.8 | 493.4 | 499.6 | 501.4 | 496.6 | 499.1 | 497.7 | 504.2 | 504.9 | 472.5 | 476.4 | 495.8 | 503.5 | 518 | 511.6 | 515.8 | 515 | 509.8 | 505 | 514.3 | 510.2 | 521.4 | 518 | 510.6 | 513.6 | 491.1 | 462.5 | 466.5 | 469.7 | 477.5 | 479 | 491.6 | 474.9 | 493.7 | 531.1 | 556.7 | 530.3 | 528.4 | 545.8 | 582.2 | 575.1 | 614.4 | 549.5 | 525.7 | 518.3 | 516.9 | 535.2 | 529.1 | 532.6 | 555.6 | 512.6 | 425.7 | 517.1 | 500.4 | 465.9 | 510.5 | 1165.5 | 1148.6 | 1167.9 | 1168.4 | 1166.8 | 1158 | 1140.2 | 1178.5 | 1164.7 | 1146.3 | 1113.8 | 1146.1 | 1107.1 | 1101.2 | 1118.2 | 1160.1 | 1175.6 | 1142.5 | 1202.9 | 1182.9 | 1117.6 | 1168 | 1126.2 | 1114.4 | 1145.5 | 1177 | 1167.5 | 1162.8 | 1125.4 | 1156.1 | 1168.5 | 1184.9 | 1166.1 | 1256.1 | 1169.3 | 1161.8 | 1109.8 | 1098.6 | 1173.9 | 1149.7 | 1170.5 | 1225.2 | 1152.6 | 1188.5 | 1157.9 | 1160.7 | 1195.1 | 1189.2 | 1187.7 | 1070.6 | 1107.7 | 1150.9 | 1149.2 | 1159.1 | 1169 | 1143.3 | 1157 | 1166.3 | 1144 | 1110.3 | 1120.9 | 1185.5 | 1186.9 | 1162.3 | 1188.8 | 1098.3 | 1160.8 | 1155 | 1146.2 | 1159.7 | 1177.9 | 1153.4 | 1171.8 | 1100.8 | 1177.2 | 1247 | 1150.9 | 1162.2 | 1156.9 | 1165.5 | 1176.2 | 1166.1 | 1157.8 | 1167.5 | 1137 | 1228.9 | 1083.9 | 1028.4 | 1169.1 | 1091.5 | 1150.5 | 1165.4 | 1163 | 1185.5 | 1169.5 | 1133.8 | 1131.5 | 1161.2 | 1131.9 | 1154.3 | 1217.4 | 1184 | 1072.7 | 1036.2 | 1054 | 1044.4 | 1043.7 | 1037.6 | 1050 | 1052.8 | 1061 | 1069.6 | 1055.9 | 1054.8 | 1062.1 | 1068.9 | 1008.2 | 922.7 | 1079.1 | 1066.6 | 1060.5 | 1072.1 | 1066.5 | 1055.3 | 1068.6 | 1053.4 | 1065.2 | 1041.8 | 1065.4 | 1048.6 | 1062.5 | 1012 | 1008.3 | 1016.4 | 1153.2 | 1133.3 | 1029.5 | 1169.2 | 1175.3 | 1186.2 | 1216.2 | 1180.7 | 1303 | 1182.6 | 1098.7 | 1090.8 | 1070.6 | 1155.2 | 1102 | 1211.3 | 1024.5 | 1047.4 | 1097.6 | 995.5 | 934.9 | 1192 | 1183.8 | 1219.9 | 1186.5 | 1174.5 | 1176.5 | 1282.5 | 1257.9 | 1098.2 | 1098.1 | 1019.3 | 993.2 | 1015.8 | 1035.8 | 1031.2 | 1052.7 | 1030.8 | 1013.7 | 1016.5 | 1024.7 | 1059.1 | 1048.8 | 1048.2 | 1051.6 | 1026.9 | 1008 | 993.5 | 1038.1 | 1010.6 | 1042.8 | 1006.7 | 1042.4 | 1054.9 | 1043.8 | 1067.5 | 1070.5 | 1050.4 | 1054.1 | 1059.8 | 1084.2 | 1125.1 | 1167.8 | 1108.3 | 1168.4 | 1220.9 | 1125.1 | 1141.5 | 1138.5 | 1191.8 | 1172.5 | 1135.3 | 1220.3 | 1180 | 1109.1 | 1198 | 1213.5 | 931.9 | 938.5 | 1168.7 | 995.4 | 1129 | 1029.7 | 1031.4 | 1030.7 | 1036.9 | 983.7 | 1014.5 | 1024.2 | 1005.3 | 1008.3 | 1037.6 | 1099.9 | 1042 | 1045.5 | 995.9 | 990.2 | 988.9 | 1021.7 | 1036.8 | 1027.9 | 1025.8 | 1041.6 | 1098 | 1035.3 | 1032.4 | 1049.6 | 1041.4 | 953.1 | 1045 | 1011.4 | 1012.5 | 1001.8 | 1011.6 | 1119.5 | 999.7 | 1041 | 1026.6 | 1031.2 | 981.9 | 923.9 | 1040.3 | 1078 | 984.6 | 991.4 | 1046.7 | 1040.2 | 1026.3 | 1042.5 | 1044.2 | 1054.3 | 1094.9 | 988.7 | 997.2 | 1020.8 | 1021.5 | 1032 | 1026.3 | 1038.3 | 1067.9 | 1053.9 | 1036.3 | 1046.7 | 1059.3 | 1061.8 | 1058.8 | 1041.4 | 1024.4 | 1010.9 | 1013 | 1065.9 | 960.2 | 1009.8 | 1025.1 | 1095 | 1060.5 | 1063.6 | 1015.9 | 1106.9 | 1061.4 | 1107.2 | 1003.7 | 1060.6 | 1003.8 | 1010.7 | 974.1 | 1020.8 | 1023.5 | 1021.4 | 0 | 38.97 | 0 | 0 | 5.33 | 4.87 | 0 | 0 | 88202570 | 260852 | 89578770 | 305572 | 73463780 | 154430 | 87816680 | 133207 | 834010 | 10100 | 115570 | 640 | 89190 | 145 | 90850 | 186 | 88820 | 78 | 87980 | 129 | 178000 | 0 | 176000 | 0 | 356840 | 354000 | 12.5833 | 5.33 | 4.87 |  | 38.97 | 0 | 363339.9
2025-05-25 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:50 | 17:26 | 402.8 | 396.2 | 431.2 | 431.9 | 423.1 | 406.7 | 439.6 | 413 | 431 | 433.8 | 437.3 | 432.7 | 434.5 | 435.7 | 441.1 | 440.6 | 411.9 | 418.2 | 436 | 442.7 | 455.8 | 449.8 | 452.4 | 453.9 | 450.4 | 444.9 | 453.3 | 450.7 | 459.4 | 458.4 | 449 | 450.9 | 426 | 402.1 | 405.2 | 408.1 | 415.2 | 416.4 | 427.2 | 414.1 | 426.4 | 462.8 | 487 | 458.3 | 461.8 | 477.3 | 513.6 | 508.1 | 548.3 | 485.2 | 463 | 457.6 | 455.6 | 472.5 | 467 | 472.8 | 492.4 | 451.1 | 398.9 | 456.1 | 436.6 | 409.4 | 448.1 | 1036.9 | 1017.6 | 1023.2 | 1026.1 | 1040.2 | 1014.8 | 1015.7 | 1037.5 | 1042.6 | 1016.9 | 1000.8 | 960.6 | 970.2 | 959.5 | 1014.6 | 1034.2 | 1033.7 | 1003.6 | 1076.3 | 1042.6 | 991.9 | 1049.1 | 993.5 | 998.5 | 1029.4 | 1032.7 | 1031.7 | 1030.4 | 992.1 | 1020.5 | 1021.7 | 1036.2 | 1045.3 | 1130.5 | 1027.1 | 1037.2 | 972.1 | 965 | 1043 | 1009.6 | 1046.7 | 1066.7 | 1031.2 | 1052.4 | 1029 | 1021.9 | 1059.9 | 1055.4 | 1045.5 | 962.2 | 992.4 | 1024.2 | 1051.6 | 1040.5 | 1040.9 | 1029.6 | 1018.3 | 1034.2 | 1040.4 | 986.5 | 991.7 | 1042.8 | 1044.6 | 1023 | 1046 | 1031.1 | 1032.2 | 1028 | 1035.5 | 1040.8 | 1048.9 | 1027.3 | 1044.7 | 1008.6 | 1018 | 1120.1 | 1016.9 | 1018.7 | 1033 | 1037.4 | 1030.6 | 1028.2 | 1043.2 | 1009.9 | 996 | 1086.7 | 974.8 | 901.4 | 1042.1 | 969.6 | 1036.9 | 1044.2 | 1034.2 | 1034.9 | 1045.5 | 1044.2 | 1029.7 | 1035.3 | 1034.8 | 1013.8 | 1098.8 | 1062.3 | 984.5 | 907.1 | 923.3 | 918.3 | 918.4 | 918.2 | 920 | 922.5 | 933.9 | 937.6 | 927.6 | 928.5 | 933.4 | 937 | 880.2 | 799.4 | 949.9 | 935.4 | 929.1 | 940.2 | 935.4 | 925.5 | 936.8 | 922.6 | 937.6 | 913.5 | 938 | 921.1 | 930.6 | 886.5 | 882.2 | 885.9 | 1021.1 | 994.8 | 897.5 | 1037.6 | 1042.2 | 1041.8 | 1083.6 | 1037.1 | 1148.4 | 1060.5 | 986 | 993.1 | 943.8 | 1032.2 | 990 | 1079.3 | 906.2 | 915.5 | 982.5 | 869.9 | 815.5 | 1050.9 | 1021.6 | 1073.1 | 1058.3 | 1039.3 | 1038.3 | 1153.5 | 1138.9 | 978.6 | 984 | 899.5 | 898.6 | 896.8 | 919.2 | 909.3 | 932.5 | 909.6 | 897 | 898.5 | 901.8 | 925.1 | 924.3 | 913.2 | 924.7 | 909.2 | 908 | 879.8 | 928 | 892.4 | 917.3 | 884.4 | 916.4 | 931.2 | 919.7 | 930 | 934.2 | 922.5 | 927.3 | 932.7 | 1000.9 | 1015.5 | 1045.8 | 994.7 | 1042.2 | 1109.5 | 1020.3 | 1053.2 | 1012.9 | 1054.8 | 1052.2 | 1008.6 | 1105 | 1071.5 | 980.7 | 1092.2 | 1080.5 | 819.1 | 824.9 | 1049.1 | 876.4 | 1002.9 | 913.2 | 911.3 | 914.5 | 919.5 | 898.2 | 904.6 | 909.5 | 894.2 | 896.6 | 924.3 | 1025.5 | 927.1 | 927.5 | 883.9 | 870 | 870.4 | 901.3 | 915.4 | 906.7 | 908.8 | 918.4 | 1028 | 913.6 | 912.7 | 928.4 | 918.6 | 836.5 | 926.4 | 938.3 | 892.6 | 880.8 | 886.2 | 1002.2 | 886.9 | 934 | 922.6 | 916 | 870.2 | 821.5 | 919.3 | 969.3 | 875.9 | 876.9 | 940 | 923.2 | 912.7 | 920.9 | 917.4 | 910.5 | 986.9 | 871.3 | 886.3 | 870.5 | 903.5 | 900 | 895.2 | 910.8 | 935.7 | 925.7 | 898.2 | 921.3 | 928.1 | 927.8 | 929.7 | 939.9 | 926.1 | 890.5 | 890 | 941.6 | 839.3 | 887.6 | 897.6 | 962.9 | 920.9 | 922 | 886.2 | 974.4 | 932.7 | 964.4 | 868.9 | 928.6 | 871.9 | 881.4 | 844.8 | 892.4 | 892.8 | 899.5 | 0 | 38.5 | 0 | 0 | 4.58 | 4.13 | 0 | 0 | 88281500 | 260995 | 89659790 | 305755 | 73543070 | 154531 | 87895180 | 133405 | 834800 | 10110 | 116350 | 640 | 78930 | 143 | 81020 | 183 | 79290 | 101 | 78500 | 198 | 158000 | 2000 | 156000 | 0 | 317740 | 314000 | 12.6 | 4.58 | 4.13 |  | 38.5 | 0 | 321675.4
2025-05-26 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 6:01 | 17:24 | 259.2 | 254.7 | 277.7 | 277.9 | 273.1 | 261.4 | 283.6 | 265.5 | 279.1 | 278.8 | 281.1 | 278.7 | 279.9 | 279.9 | 284.4 | 283.2 | 264.3 | 270.2 | 282 | 284.7 | 293.7 | 289.5 | 292.9 | 292.5 | 289.7 | 286.1 | 292.8 | 289.6 | 296.8 | 295.1 | 289.1 | 287.6 | 274.8 | 258.9 | 260.5 | 263.2 | 266.8 | 266.9 | 274.4 | 267.4 | 275.6 | 299.2 | 315.3 | 295.9 | 300.4 | 310.9 | 334.9 | 332.4 | 355.6 | 315.5 | 300.9 | 297.1 | 294.9 | 305.4 | 302.8 | 305.6 | 321.5 | 293.4 | 259.2 | 295.5 | 279.6 | 266 | 291.5 | 664 | 651.7 | 657.2 | 657.3 | 668.2 | 652.6 | 651.4 | 667.8 | 671.9 | 656.3 | 646.2 | 655.9 | 625.9 | 619.1 | 650.6 | 663.7 | 664.5 | 641.5 | 692.9 | 668.2 | 633 | 673.4 | 637.8 | 638.3 | 659 | 663.7 | 659.4 | 659.2 | 640.8 | 649.4 | 656 | 661.4 | 666.1 | 722.5 | 663.5 | 660.7 | 615.4 | 612.2 | 660.4 | 639.4 | 667.3 | 689 | 658.8 | 673.4 | 659.8 | 649.3 | 678.3 | 675.3 | 677.1 | 613.5 | 637.3 | 656.3 | 675.3 | 669 | 667.1 | 662.2 | 649.2 | 663.1 | 670.8 | 633.7 | 636.7 | 673.6 | 674.4 | 658.7 | 674.3 | 661.8 | 663.2 | 661.2 | 668 | 671.5 | 678.1 | 662.6 | 672.3 | 653.5 | 666 | 730.4 | 662 | 663.5 | 672.9 | 678 | 671.7 | 668.1 | 679.1 | 675.9 | 646.4 | 701.5 | 631.4 | 582.1 | 676.8 | 628.7 | 672.1 | 675.6 | 667.6 | 673.8 | 675 | 674.6 | 664 | 667.2 | 668.6 | 656.2 | 711.9 | 689.1 | 636 | 597.3 | 611.1 | 603.7 | 606 | 609.9 | 608.3 | 608.3 | 616.6 | 622.5 | 614.7 | 613.7 | 618.9 | 623 | 581.3 | 530.7 | 632.6 | 621.3 | 617.8 | 623 | 617.8 | 612.3 | 620.3 | 612.5 | 618.3 | 600.8 | 616.3 | 607.4 | 614.9 | 583.3 | 579.4 | 590.5 | 659.9 | 643.3 | 582.7 | 672.5 | 676.2 | 676.8 | 703.5 | 681.2 | 749.7 | 689.8 | 641.2 | 644.3 | 612.8 | 672.4 | 660 | 697 | 586.7 | 589.8 | 653.9 | 562.2 | 592 | 693.2 | 685.7 | 698.8 | 687 | 672.3 | 672.7 | 748 | 737.3 | 635.6 | 644.1 | 587.9 | 585.8 | 586.1 | 596.3 | 595.4 | 610.4 | 594.6 | 587.9 | 587.8 | 592.3 | 611.8 | 604.3 | 609.3 | 607.1 | 598.2 | 600 | 577.7 | 608.3 | 586.1 | 596.1 | 581 | 599.5 | 615.2 | 605.3 | 625.6 | 615.8 | 608.4 | 612 | 615.5 | 636.7 | 646.7 | 664.6 | 633.3 | 674.5 | 708.4 | 667.9 | 672.9 | 644.8 | 672.7 | 671.8 | 646.2 | 708 | 685.1 | 625.6 | 697.6 | 689.3 | 524 | 527.8 | 672 | 561.4 | 643.6 | 596.3 | 591.9 | 591.2 | 596.3 | 586.9 | 593.1 | 589.6 | 581.2 | 585.8 | 602.8 | 667.8 | 601.8 | 600.9 | 578.2 | 572.6 | 519 | 585.4 | 598.2 | 594.6 | 593.7 | 601.8 | 640.7 | 596.1 | 595.4 | 604.5 | 602.2 | 544.6 | 602.7 | 613.1 | 580.5 | 573.4 | 592.7 | 665 | 582.8 | 610.1 | 601.9 | 596.9 | 568.6 | 536.1 | 609.8 | 637.8 | 568.1 | 575.3 | 622.4 | 613.4 | 606.3 | 605.1 | 607.4 | 610.5 | 647.4 | 573 | 583.8 | 583.1 | 597.6 | 600 | 593.8 | 597.3 | 609.9 | 609.8 | 585.7 | 602.8 | 606.3 | 603.7 | 606.4 | 614 | 599.9 | 580.3 | 588 | 611.2 | 542.6 | 577.7 | 586.9 | 634.4 | 600.6 | 603.3 | 578.9 | 635.6 | 609.9 | 635.5 | 568.9 | 604.5 | 572.4 | 581.1 | 549.5 | 584.8 | 586.9 | 582.8 | 0 | 31.05 | 0 | 0 | 2.71 | 2.48 | 0 | 0 | 88332470 | 261131 | 89712330 | 305874 | 73594130 | 154687 | 87945180 | 133543 | 835320 | 10110 | 116850 | 650 | 50970 | 136 | 52540 | 119 | 51060 | 156 | 50000 | 138 | 104000 | 0 | 100000 | 2000 | 204570 | 204000 | 11.3833 | 2.71 | 2.48 |  | 31.05 | 0 | 209033.7
2025-05-27 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:45 | 17:39 | 548.3 | 542.6 | 586.2 | 588.6 | 579.8 | 562.5 | 596.4 | 564.3 | 584.4 | 592.7 | 594.2 | 587.9 | 591.8 | 591.4 | 598.3 | 597.7 | 561 | 563.1 | 586.6 | 595.6 | 608.9 | 600.4 | 605.6 | 607.8 | 602.2 | 592.3 | 602.1 | 587.3 | 614.8 | 610.2 | 596.4 | 599.8 | 584.3 | 549.8 | 554 | 559.1 | 568.2 | 569.6 | 586.5 | 566.2 | 589.9 | 631.3 | 657.4 | 634.1 | 632.7 | 648.6 | 684.1 | 677.3 | 704.6 | 641.6 | 623.1 | 614.8 | 607.2 | 626 | 617.4 | 618.3 | 645.7 | 603.9 | 522.8 | 603.4 | 582.6 | 543.1 | 610.1 | 1339.8 | 1329 | 1383.6 | 1364.5 | 1343.4 | 1358.4 | 1309.6 | 1375 | 1340.7 | 1324.2 | 1292 | 1319.4 | 1292.1 | 1283.1 | 1340.3 | 1345.3 | 1386.3 | 1306.4 | 1379.9 | 1378.9 | 1282.9 | 1331.5 | 1298.3 | 1275.7 | 1309.8 | 1386.1 | 1347 | 1341.6 | 1303.9 | 1333.8 | 1369.7 | 1377.8 | 1356 | 1421.5 | 1345.4 | 1354.9 | 1277.2 | 1283.6 | 1353.2 | 1342 | 1339.5 | 1336.3 | 1325.2 | 1373.4 | 1334.5 | 1335.2 | 1378.6 | 1375.4 | 1338.4 | 1260.3 | 1267.1 | 1319.3 | 1316.2 | 1321.1 | 1341.5 | 1347.5 | 1346.9 | 1332.2 | 1314.9 | 1274.1 | 1296.6 | 1373.7 | 1379.5 | 1354.2 | 1384.6 | 1309 | 1326.4 | 1318.9 | 1377.7 | 1314.7 | 1359.8 | 1322.9 | 1308.3 | 1295.9 | 1419.1 | 1480.4 | 1385.3 | 1412.4 | 1391.4 | 1400 | 1440.1 | 1385.9 | 1415.1 | 1317.4 | 1384.8 | 1457.4 | 1337.1 | 1232.4 | 1372.2 | 1264 | 1334.5 | 1349.9 | 1369.6 | 1396.2 | 1315.2 | 1302.7 | 1315.5 | 1359.8 | 1350.7 | 1391.6 | 1389.9 | 1369.8 | 1302.8 | 1326.9 | 1340.8 | 1325.3 | 1318.1 | 1217.3 | 1308.9 | 1307.9 | 1309.8 | 1313.4 | 1305.3 | 1336.4 | 1336.8 | 1326.4 | 1277.1 | 1162.3 | 1319 | 1314.6 | 1301.9 | 1311.9 | 1303.4 | 1291.7 | 1301.9 | 1292 | 1299 | 1276.8 | 1296.1 | 1267.8 | 1283.9 | 1241.4 | 1235.6 | 1249.8 | 1396.9 | 1397 | 1289.7 | 1442.5 | 1464.4 | 1410.6 | 1472.1 | 1329.1 | 1555.4 | 1478.1 | 1385.4 | 1372.6 | 1358.4 | 1481 | 1400 | 1473.4 | 1277.7 | 1295.5 | 1422.9 | 1246.7 | 1109.6 | 1478.4 | 1501.8 | 1565.4 | 1491 | 1466.7 | 1509.3 | 1575.1 | 1531.6 | 1291.8 | 1297.9 | 1225 | 1225.4 | 1203.7 | 1237.3 | 1232.2 | 1260.5 | 1244.3 | 1230.2 | 1227.9 | 1234.6 | 1261.2 | 1241.1 | 1254.3 | 1266.8 | 1244 | 1245 | 1217.1 | 1269.8 | 1234.9 | 1281.2 | 1242.6 | 1304 | 1274.4 | 1271.9 | 1302.5 | 1339.6 | 1275.7 | 1283.7 | 1292.3 | 1305.8 | 1332.6 | 1376.2 | 1298.1 | 1332 | 1405.4 | 1318.4 | 1323.7 | 1325.1 | 1388 | 1351.3 | 1308.4 | 1388.8 | 1364.3 | 1293.5 | 1376.5 | 1407.4 | 1098 | 1103.5 | 1334.2 | 1174.5 | 1303.3 | 1242.9 | 1237.7 | 1233.1 | 1242 | 1205.8 | 1070.6 | 1225.4 | 1206.1 | 1208 | 1231.6 | 1307.9 | 1232.4 | 1228.7 | 1194.3 | 1186.5 | 1182.7 | 1211.6 | 1215.9 | 1210.7 | 1206.1 | 1215.8 | 1309 | 1211.9 | 1212.5 | 1222.7 | 1217 | 1141.1 | 1223.6 | 1124.3 | 1192.1 | 1181 | 1227.2 | 1340.1 | 1188.9 | 1257.9 | 1246.1 | 1235.3 | 1186.3 | 1132.1 | 1242.3 | 1279.2 | 1203.5 | 1213.8 | 1260.1 | 1256.4 | 1234.9 | 1246 | 1253.4 | 1269.4 | 1296.7 | 1194.8 | 1197.7 | 1218.9 | 1222.3 | 1231 | 1230.1 | 1266.4 | 1281 | 1283.3 | 1252 | 1273.5 | 1271.3 | 1277.5 | 1276.6 | 1246.4 | 1241.8 | 1226 | 1225 | 1276.4 | 1174.5 | 1229.5 | 1244 | 1325.5 | 1293.3 | 1291.5 | 1249.2 | 1333.5 | 1293.8 | 1332.4 | 1237.7 | 1295.5 | 1240.5 | 1235.4 | 1146.2 | 1158.8 | 1248.4 | 1156.5 | 0 | 39.98 | 0 | 0 | 6.52 | 5.9 | 0 | 0 | 88436260 | 261286 | 89820620 | 306059 | 73701280 | 154761 | 88050560 | 133657 | 836370 | 10120 | 117910 | 650 | 103790 | 155 | 108290 | 185 | 107150 | 74 | 105380 | 114 | 210000 | 2000 | 212000 | 0 | 424610 | 422000 | 12.9 | 6.52 | 5.9 |  | 39.98 | 0 | 432604.2
2025-05-28 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:47 | 17:37 | 602.1 | 591.3 | 642.3 | 640.8 | 636.6 | 615.2 | 651.7 | 619.9 | 639.5 | 646.2 | 647.9 | 641.9 | 640.5 | 644.3 | 650.5 | 648.9 | 610.6 | 616.8 | 642.1 | 650.7 | 669.1 | 659.6 | 669.3 | 667.6 | 661 | 653.1 | 663 | 648.4 | 671.7 | 669.5 | 657.4 | 658.7 | 627.8 | 597.3 | 602.5 | 603.5 | 612.2 | 616.6 | 631 | 608.8 | 629.5 | 668.7 | 709.5 | 672.9 | 673.3 | 695.8 | 741.6 | 733.8 | 783.7 | 701.2 | 669.7 | 663.2 | 660.7 | 683.9 | 675.1 | 677.4 | 712 | 653.1 | 581.4 | 658.8 | 639.8 | 597 | 652.6 | 1502.3 | 1480.5 | 1511.9 | 1508.4 | 1512.2 | 1503.4 | 1471 | 1524.1 | 1510.5 | 1484.3 | 1449.8 | 1488 | 1439.9 | 1428.7 | 1469.2 | 1485.5 | 1516.7 | 1469.4 | 1542.8 | 1523.1 | 1437.6 | 1502.5 | 1454.1 | 1436.2 | 1474.5 | 1521.2 | 1502 | 1495.3 | 1463 | 1504.9 | 1518.9 | 1533.9 | 1516.1 | 1627.4 | 1525 | 1509.4 | 1434.8 | 1431 | 1514.6 | 1491 | 1512.4 | 1533.6 | 1532.1 | 1545.7 | 1502.4 | 1500.6 | 1547.3 | 1536.6 | 1540.6 | 1386 | 1425 | 1475.5 | 1482.7 | 1481.7 | 1488.4 | 1496.2 | 1467.6 | 1488.8 | 1487.5 | 1416.1 | 1430.3 | 1512.5 | 1514.6 | 1485.7 | 1518.7 | 1480 | 1481.6 | 1474.6 | 1502.6 | 1476.7 | 1500.8 | 1470.2 | 1412.9 | 1424.9 | 1482.5 | 1570.1 | 1455.4 | 1467 | 1465.8 | 1478 | 1496.9 | 1473.7 | 1493.6 | 1479.6 | 1451.2 | 1566.2 | 1415.9 | 1307.5 | 1479.4 | 1391.2 | 1463.8 | 1478.1 | 1430.9 | 1499.2 | 1494.8 | 1478.6 | 1448.3 | 1483.8 | 1484.5 | 1474.2 | 1536.5 | 1494.1 | 1393 | 1318.1 | 1338.1 | 1332.1 | 1334.2 | 1334.3 | 1338.4 | 1343.7 | 1359.4 | 1361.6 | 1347.3 | 1343.8 | 1345 | 1352.1 | 1276.1 | 1168.6 | 1372.9 | 1348.9 | 1343.3 | 1355.8 | 1357.6 | 1336.6 | 1358 | 1335 | 1352.8 | 1327.7 | 1354.7 | 1338.8 | 1355.8 | 1288.8 | 1283.7 | 1301 | 1460.4 | 1421.8 | 1268.9 | 1470.7 | 1484.1 | 1503.3 | 1530.4 | 1486.5 | 1646.4 | 1493.9 | 1393 | 1423.6 | 1357.5 | 1468.7 | 1450 | 1527.8 | 1303 | 1322.3 | 1450.7 | 1261.4 | 1205.7 | 1503.9 | 1494.8 | 1546.7 | 1503 | 1495 | 1485.5 | 1621.5 | 1615.2 | 1404.5 | 1406.1 | 1307.8 | 1305.3 | 1301 | 1334.5 | 1319.5 | 1351.8 | 1315 | 1306.1 | 1309.6 | 1315.3 | 1352 | 1340.2 | 1335.6 | 1337.9 | 1313.9 | 1323 | 1276.4 | 1345.5 | 1293.4 | 1329.1 | 1290.9 | 1338.8 | 1354.7 | 1340.2 | 1355.4 | 1366.3 | 1341.1 | 1347.1 | 1356.3 | 1443.1 | 1438.5 | 1506.7 | 1428.9 | 1501.7 | 1570 | 1488.1 | 1437.2 | 1458.7 | 1524.1 | 1496.5 | 1444.9 | 1559.8 | 1506 | 1418.1 | 1517.8 | 1542.8 | 1190.2 | 1202.7 | 1488.3 | 1271 | 1441.2 | 1347.3 | 1343.6 | 1342.8 | 1346.6 | 1308.2 | 1327.9 | 1335.8 | 1324.7 | 1314.2 | 1357.6 | 1449.6 | 1354 | 1360 | 1299.2 | 1281.9 | 1286 | 1320.8 | 1338.9 | 1323.8 | 1320.7 | 1340.5 | 1459.8 | 1336.2 | 1338.2 | 1351.7 | 1343.1 | 1235.4 | 1351.8 | 1366.4 | 1307.4 | 1291.6 | 1312.1 | 1436.6 | 1303.5 | 1365 | 1356.9 | 1349 | 1284 | 1209.3 | 1327.8 | 1405.3 | 1292.4 | 1295 | 1372.9 | 1356.7 | 1345.9 | 1350.1 | 1350 | 1354.8 | 1422.3 | 1291.7 | 1299.2 | 1304.8 | 1320.4 | 1323 | 1322.5 | 1333.3 | 1365.7 | 1362 | 1321.9 | 1357.8 | 1361.2 | 1363 | 1366.5 | 1375.9 | 1347.5 | 1309 | 1312 | 1372.7 | 1243.3 | 1305.6 | 1323.3 | 1411.7 | 1355.9 | 1361.5 | 1315 | 1424.9 | 1375.8 | 1417.1 | 1298.1 | 1372.2 | 1301.7 | 1306 | 1257 | 1309.2 | 1322.7 | 1303.7 | 0 | 42.69 | 0 | 0 | 6.92 | 6.37 | 0 | 0 | 88551240 | 261422 | 89936360 | 306198 | 73814540 | 154858 | 88164830 | 133810 | 837510 | 10120 | 119040 | 660 | 114980 | 136 | 115740 | 139 | 113260 | 97 | 114270 | 153 | 228000 | 0 | 226000 | 2000 | 458250 | 454000 | 12.8333 | 6.92 | 6.37 |  | 42.69 | 0 | 466944.9997
2025-05-29 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 5:01 | 17:00 | 205.1 | 201.7 | 219.2 | 219 | 219.8 | 208.1 | 223.2 | 211.7 | 221.7 | 221.5 | 220.8 | 219.5 | 223.3 | 220.7 | 226.5 | 224.9 | 207.5 | 212.6 | 220.9 | 224.1 | 229.7 | 225.7 | 231.1 | 229.8 | 228.9 | 225.7 | 230.8 | 229.7 | 232.5 | 231.6 | 226.9 | 226.2 | 221.6 | 208.4 | 208.7 | 210.6 | 213.1 | 211.8 | 220.6 | 214.3 | 220.8 | 240.3 | 254.1 | 238.5 | 241.5 | 250.9 | 269.4 | 268.2 | 282.8 | 251.8 | 239.9 | 237.7 | 235.2 | 243.4 | 240.5 | 243.1 | 255.5 | 233.7 | 205.5 | 234 | 220.3 | 210.5 | 234 | 517.7 | 508.2 | 512.9 | 511.1 | 518.9 | 509.4 | 509.9 | 523.2 | 525.1 | 516 | 505.4 | 516.3 | 491.2 | 488.7 | 507.9 | 517.6 | 519.1 | 508 | 540.4 | 521.1 | 492.8 | 506 | 497.2 | 497.8 | 512.8 | 504 | 514.6 | 514.4 | 501.5 | 506.3 | 514.5 | 513.8 | 524.7 | 568.8 | 523.2 | 517.1 | 475.3 | 477.9 | 515.8 | 500.4 | 518.8 | 536.8 | 511.3 | 520.5 | 510 | 498.6 | 524.1 | 523.5 | 528.2 | 476.7 | 497.6 | 512.3 | 530.9 | 523.1 | 522.8 | 516.4 | 507.2 | 520.4 | 529.3 | 499 | 499.6 | 533 | 535.9 | 520.6 | 535.4 | 521.5 | 525.9 | 525.8 | 532.5 | 534.5 | 541.5 | 529.2 | 541.3 | 523.5 | 549.5 | 590.5 | 533.6 | 530 | 541 | 544 | 541.2 | 528 | 546.4 | 545.4 | 523.3 | 569.2 | 510.1 | 469.4 | 545.3 | 507.4 | 542.6 | 543.6 | 536.1 | 541.2 | 541 | 541.3 | 535.6 | 536.3 | 539 | 528.8 | 572.3 | 555.7 | 512.5 | 474.7 | 486 | 478.7 | 484.1 | 487.1 | 486.6 | 486.9 | 494.8 | 499.8 | 494.3 | 489.5 | 493.7 | 498.9 | 464 | 426.3 | 511.2 | 498.2 | 498.1 | 500.7 | 496.5 | 493.6 | 499.6 | 494.1 | 497.8 | 484.6 | 495.7 | 490.3 | 496.2 | 469.5 | 466.2 | 478.3 | 535.5 | 518.3 | 470.1 | 539.8 | 542.7 | 541.6 | 566.3 | 547.9 | 598 | 548.3 | 512.4 | 512.1 | 483.9 | 490 | 523 | 562.9 | 473.8 | 475.6 | 525.8 | 452.3 | 423.8 | 554.8 | 547.7 | 559 | 549.5 | 547 | 537.3 | 600.1 | 591.7 | 510.2 | 519.7 | 472.7 | 471.5 | 467.5 | 481.6 | 471.8 | 487.5 | 480.5 | 475 | 473.1 | 464.1 | 444.1 | 483.7 | 444.8 | 487.4 | 489.2 | 483 | 471.9 | 496.2 | 475.3 | 481.9 | 471.5 | 485.5 | 498.2 | 490 | 471 | 489 | 480.7 | 494.7 | 498 | 503.3 | 519.7 | 527.5 | 502.8 | 532.9 | 559.3 | 533.1 | 532.7 | 510.7 | 533.6 | 531.8 | 511.1 | 563.3 | 550 | 500.2 | 560 | 554.1 | 421.4 | 421.9 | 533.3 | 449.1 | 510.1 | 476.1 | 470.7 | 464.5 | 466.9 | 458 | 466.5 | 473.5 | 467.6 | 461.4 | 481 | 522.8 | 471.8 | 476.3 | 457.9 | 450 | 443 | 456.5 | 467.9 | 463.5 | 461.9 | 471.3 | 505 | 468.2 | 466.6 | 475.5 | 473.9 | 426.4 | 471.4 | 479.9 | 454.5 | 450.7 | 429.6 | 489.1 | 460.8 | 482.3 | 478.3 | 474.8 | 453.7 | 425.6 | 444.5 | 499.7 | 447.6 | 458.8 | 497.5 | 486.4 | 488.9 | 482.1 | 484.8 | 415.8 | 513 | 458.5 | 451.4 | 420 | 474.1 | 470 | 419 | 476.7 | 484 | 486.9 | 462.9 | 479.4 | 479.8 | 476.2 | 477.5 | 486.6 | 472.3 | 459.3 | 463 | 482.9 | 429.5 | 456 | 465.4 | 508.4 | 477.2 | 477.9 | 461.5 | 502.9 | 485.7 | 508 | 456.4 | 482.1 | 458.2 | 466.3 | 436.2 | 466.7 | 468 | 460.4 | 0 | 20.38 | 0 | 0 | 2.1 | 1.88 | 0 | 0 | 88591290 | 261551 | 89978300 | 306302 | 73854950 | 154954 | 88203680 | 133944 | 837920 | 10130 | 119430 | 660 | 40050 | 129 | 41940 | 104 | 40410 | 96 | 38850 | 134 | 82000 | 2000 | 78000 | 0 | 161250 | 160000 | 11.9833 | 2.1 | 1.88 |  | 20.38 | 0 | 165598.3
2025-05-30 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 4:55 | 17:00 | 116.6 | 112.5 | 124.1 | 123.5 | 124.5 | 118.3 | 126.7 | 119.2 | 125.8 | 123.6 | 124.8 | 124.4 | 126.7 | 123.9 | 128.7 | 127.4 | 115.8 | 120.2 | 125 | 126.5 | 130 | 127.9 | 130.2 | 127.7 | 127.3 | 127.5 | 131.5 | 129.6 | 132.3 | 129.9 | 129.2 | 125.5 | 126.1 | 117.6 | 116.8 | 118.9 | 120.5 | 119.1 | 124.7 | 122 | 125.1 | 137 | 144.5 | 135.5 | 136.4 | 143 | 153.7 | 152.4 | 158.2 | 143.1 | 136.5 | 132.4 | 132.2 | 137.5 | 135 | 136.1 | 145 | 131.5 | 115.7 | 131.5 | 124.7 | 119 | 130.8 | 292.5 | 287.7 | 292 | 292 | 294.3 | 288.8 | 289.5 | 297.2 | 298.1 | 293.2 | 286.9 | 293.2 | 279.3 | 277.7 | 286.2 | 291.8 | 294.7 | 286.8 | 304.8 | 293.6 | 277.9 | 296.2 | 280.3 | 280.8 | 289 | 294.2 | 290.8 | 291 | 280.8 | 284 | 287.9 | 288.5 | 293.3 | 318 | 293.2 | 289.6 | 266.9 | 267.4 | 290.3 | 280.8 | 292.7 | 301.1 | 288.1 | 293.9 | 288.8 | 281.4 | 296.6 | 296.1 | 298.1 | 267.1 | 280.6 | 289.6 | 301.4 | 295.5 | 295.5 | 293.2 | 285.9 | 295 | 300.1 | 282.3 | 282.7 | 303.8 | 305.9 | 296 | 304.9 | 295.4 | 298.1 | 298 | 304 | 303.5 | 308 | 300.9 | 308.2 | 299.2 | 301 | 339 | 305.5 | 307.7 | 310.1 | 311.4 | 310.8 | 308.3 | 313 | 311.5 | 298.8 | 325 | 290.5 | 267.5 | 311.3 | 289.6 | 309.4 | 310 | 305.1 | 309.6 | 307.8 | 307.7 | 305.1 | 305.4 | 307.2 | 302.1 | 326.6 | 318.6 | 291.9 | 271.9 | 279.8 | 272.2 | 275.6 | 277 | 277.6 | 275.9 | 279.7 | 284.9 | 281.6 | 278.9 | 283.8 | 286.8 | 264.7 | 244.4 | 293.9 | 283.8 | 285.4 | 285.1 | 281.4 | 279.5 | 282.4 | 282.4 | 279.9 | 275.1 | 277.7 | 277.6 | 279.6 | 262 | 262.1 | 273.7 | 306.9 | 296.8 | 272.2 | 310.9 | 313.5 | 313.1 | 326.5 | 316.2 | 347.6 | 316.8 | 298.4 | 297.6 | 283.5 | 277.8 | 297 | 330.2 | 274.7 | 272.5 | 302 | 259.5 | 243.9 | 321.5 | 317.7 | 325.1 | 318.3 | 311.2 | 310.5 | 344.9 | 342.2 | 287.7 | 295.5 | 268.8 | 263.1 | 257.1 | 273.3 | 261.9 | 268.6 | 274.3 | 267.8 | 267.7 | 241.5 | 193.2 | 271 | 196 | 271.6 | 276.3 | 267 | 274.4 | 285.4 | 272.6 | 278.1 | 271.3 | 280.5 | 283.4 | 278.1 | 236 | 264.2 | 252.2 | 279.7 | 277.6 | 282.7 | 292 | 296.7 | 282.7 | 299.3 | 315 | 301.4 | 300.3 | 287.7 | 301.2 | 300.4 | 289.4 | 318.4 | 311.1 | 282.9 | 317.5 | 314.4 | 238 | 238.6 | 301.1 | 254.7 | 288.8 | 264.6 | 260.8 | 254.5 | 254.3 | 251.6 | 258 | 262.6 | 258 | 252.5 | 267.2 | 289.3 | 259.9 | 264.6 | 256.1 | 251.2 | 241.1 | 251.7 | 260.5 | 257.1 | 255.7 | 263.7 | 292 | 262.2 | 256.3 | 265 | 265.7 | 234.6 | 260.4 | 266.5 | 252.1 | 250.3 | 211.4 | 257.8 | 255.7 | 267 | 264.5 | 261.8 | 253.6 | 233.5 | 220.6 | 278.9 | 242.4 | 253.1 | 282.4 | 265.2 | 278.7 | 272.4 | 260.8 | 200.8 | 290 | 258 | 253.6 | 149 | 264.8 | 268 | 216.7 | 258.7 | 260.6 | 268.3 | 262.6 | 257.3 | 260.9 | 258.1 | 259.1 | 267.5 | 256.6 | 252 | 251 | 267.4 | 233.4 | 247.1 | 255.2 | 275.4 | 265.6 | 265.4 | 247.7 | 269.9 | 260.9 | 276.2 | 245.7 | 265 | 247.2 | 256.5 | 235.5 | 255.4 | 257.2 | 248 | 0 | 26.06 | 0 | 0 | 1.2 | 1.08 | 0 | 0 | 88613860 | 261717 | 90002000 | 306521 | 73877520 | 155081 | 88224250 | 134079 | 838150 | 10130 | 119650 | 670 | 22570 | 166 | 23700 | 219 | 22570 | 127 | 20570 | 135 | 46000 | 0 | 44000 | 2000 | 89410 | 90000 | 12.0833 | 1.2 | 1.08 |  | 26.06 | 0 | 92993.4
2025-05-31 | 2026 | 2025 |  |  | May-25 | 31 | 91870 | 5:09 | 17:06 | 399.4 | 388.7 | 423.5 | 422.8 | 422.8 | 404.5 | 430.1 | 410.2 | 427.5 | 426 | 427.9 | 424.5 | 428.1 | 427.4 | 433.6 | 430.6 | 405.1 | 409.9 | 425.1 | 430.6 | 442.1 | 435.6 | 441 | 439.7 | 437.6 | 433.6 | 439.8 | 433.8 | 444.6 | 441.6 | 437.5 | 437.4 | 421.9 | 397.8 | 400.8 | 404.5 | 409.4 | 407.9 | 423.3 | 408.8 | 419.5 | 451.7 | 474.1 | 448.4 | 451.6 | 464.2 | 496.3 | 492 | 522.1 | 470.1 | 463 | 445.7 | 443.2 | 458.2 | 452 | 457.3 | 474.8 | 437.6 | 387.2 | 438.9 | 423.2 | 399.8 | 438.3 | 995 | 974.3 | 989.2 | 984.1 | 990.3 | 983.9 | 972.8 | 1000.3 | 996.1 | 980.5 | 962.1 | 978.9 | 944.4 | 937.8 | 959 | 987.3 | 1001.1 | 971.4 | 1026.9 | 1002.8 | 951.1 | 994.6 | 954.9 | 948.3 | 977.3 | 970 | 989.8 | 987 | 967.9 | 979 | 990.9 | 994.9 | 997.2 | 1072.4 | 1003.9 | 991.4 | 930.4 | 936.2 | 988 | 967.9 | 988.9 | 997.4 | 988.5 | 1000.1 | 983.3 | 970.4 | 1006.1 | 1003 | 980.2 | 876.7 | 942.4 | 977.8 | 968.7 | 989.3 | 994.1 | 1000.4 | 980.8 | 992.2 | 997.1 | 945.5 | 957 | 1012.2 | 1010.9 | 987.4 | 1010.1 | 967.9 | 988.8 | 984.1 | 1001.4 | 993.1 | 1006.9 | 987.1 | 1003.1 | 955.3 | 961 | 1041.3 | 990.9 | 997.3 | 999 | 1005.3 | 1012.6 | 999.8 | 1012.3 | 931.1 | 976.5 | 1055.3 | 952.7 | 830 | 1004.2 | 942.9 | 994.7 | 1001.3 | 981.3 | 991.1 | 982.9 | 982.4 | 943.7 | 996 | 983 | 994 | 1045.2 | 1017.2 | 923.5 | 884.6 | 898.7 | 893.4 | 895.1 | 895.8 | 896 | 895.9 | 907.9 | 912.7 | 903.5 | 902.2 | 907.7 | 909.7 | 863.2 | 792 | 921.8 | 908.3 | 905.2 | 910.4 | 907.1 | 899 | 907.1 | 897.5 | 908.1 | 889.6 | 904.8 | 892.6 | 900.5 | 860.4 | 856.6 | 870.7 | 988 | 968.4 | 887.5 | 1003 | 1008.7 | 1019.2 | 1045.3 | 1016.4 | 1116.4 | 1020.3 | 954.4 | 939.6 | 904.2 | 851.2 | 944 | 1048 | 854.7 | 872 | 921.7 | 815 | 777 | 984.5 | 997.3 | 1050.8 | 1021.8 | 997.5 | 1010.1 | 1103.7 | 1081.6 | 922.3 | 932.1 | 862.4 | 862.5 | 850.2 | 894 | 855.7 | 885.3 | 870.3 | 864.2 | 863.5 | 842.1 | 808.5 | 886.7 | 793.6 | 890.9 | 875.4 | 870 | 863 | 896.7 | 860.9 | 881.8 | 865.1 | 905 | 893.3 | 890.5 | 822.6 | 901.3 | 866.1 | 893.1 | 880.7 | 939.4 | 960.2 | 994.4 | 944.5 | 951.6 | 1045.6 | 1000.6 | 1003.9 | 969.7 | 1014.8 | 1004.2 | 967.4 | 1025 | 992.9 | 943.2 | 1031 | 1037.3 | 801.2 | 802.2 | 996.8 | 848.3 | 960.4 | 883.2 | 875.3 | 869.1 | 871.7 | 855.6 | 868 | 878.3 | 862.7 | 857.5 | 879.4 | 951.2 | 878.1 | 883.4 | 842.4 | 840 | 832.5 | 863.5 | 876.7 | 872.4 | 870 | 878.5 | 946.9 | 876.6 | 870.3 | 873.8 | 878.9 | 799.2 | 880.2 | 888.4 | 852.7 | 836.9 | 809.4 | 898.2 | 847.1 | 887.6 | 878.8 | 873.9 | 835.1 | 789.7 | 830.1 | 897.5 | 837.6 | 839.5 | 892.8 | 857.8 | 877 | 866.8 | 875 | 832.1 | 925.9 | 833 | 840.1 | 759.4 | 836.1 | 840 | 742.2 | 870 | 901.3 | 897.1 | 867.9 | 891.9 | 897.3 | 889.6 | 894.3 | 900.4 | 882.3 | 856.9 | 860 | 895.3 | 811 | 853.4 | 864.8 | 926.8 | 863.9 | 866.9 | 862.8 | 918.7 | 900.9 | 926.4 | 842.3 | 893.7 | 846.3 | 850.6 | 820.3 | 856.5 | 864.2 | 856.9 | 0 | 32.64 | 0 | 0 | 4.41 | 3.98 | 0 | 0 | 88689870 | 261905 | 90079850 | 306792 | 73952700 | 155249 | 88298580 | 134245 | 838910 | 10130 | 120390 | 670 | 76010 | 188 | 77850 | 271 | 75180 | 168 | 74330 | 166 | 152000 | 0 | 148000 | 0 | 303370 | 300000 | 11.95 | 4.41 | 3.98 |  | 32.64 | 0 | 308085.8
2025-06-01 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 5:04 | 17:29 | 341.2 | 334.5 | 364.2 | 364.2 | 361.2 | 343.1 | 371.8 | 351.7 | 365.3 | 368.4 | 369.1 | 365 | 367.3 | 368.6 | 372.5 | 372 | 347.1 | 354.3 | 367.3 | 373.2 | 383.8 | 378 | 382.1 | 383 | 380.8 | 375.9 | 383.2 | 381.4 | 387.2 | 385.5 | 380.3 | 380.4 | 360.8 | 340.1 | 343.5 | 346.7 | 351.6 | 351.2 | 362.1 | 350.6 | 362.5 | 392.5 | 412.9 | 387.8 | 391.8 | 405.4 | 435.4 | 431.3 | 463.1 | 409.6 | 390.2 | 387 | 385.4 | 398.1 | 393.5 | 399.5 | 417.4 | 382.8 | 336.7 | 382.9 | 367.6 | 346.6 | 378.7 | 873.1 | 856.3 | 860.2 | 863.5 | 875.7 | 860.2 | 854.8 | 875.1 | 878.2 | 860.4 | 843.6 | 859.1 | 819.9 | 811 | 854.6 | 869.8 | 868.3 | 860.6 | 908.3 | 877.8 | 833.9 | 884.2 | 838.2 | 838.9 | 866.3 | 868.3 | 866.9 | 865.7 | 842 | 858.1 | 863.3 | 872.5 | 880.4 | 953.4 | 872.5 | 872.3 | 814.6 | 810.6 | 874.8 | 848.9 | 879.3 | 909.6 | 867.4 | 884 | 865.9 | 855.2 | 889.2 | 886.3 | 892 | 808 | 838.9 | 858.8 | 851 | 875.1 | 881.4 | 866.7 | 876.9 | 868.7 | 878.8 | 830.4 | 837.2 | 884 | 881.8 | 861.3 | 882.7 | 870.6 | 871.4 | 865.4 | 872.4 | 877.3 | 883.9 | 867.9 | 882.9 | 851.2 | 888.7 | 880 | 901 | 865.2 | 875.2 | 880.3 | 873.5 | 873.6 | 884.1 | 829 | 844.7 | 919.4 | 825.8 | 762.1 | 883.6 | 821.1 | 877.1 | 881.3 | 872 | 881 | 855.9 | 879.8 | 868.4 | 873.3 | 873.8 | 858.3 | 926.8 | 897.9 | 834.2 | 775.9 | 790.8 | 785.5 | 786.7 | 788.4 | 787.8 | 788.7 | 798.3 | 802.5 | 794.6 | 796.4 | 800.1 | 804 | 754.2 | 685.7 | 813.6 | 802.3 | 795.8 | 804.4 | 799.7 | 791.9 | 800.7 | 790.2 | 799.6 | 779.6 | 800.5 | 785.9 | 795.1 | 756.6 | 752.1 | 759.2 | 864.9 | 842.6 | 761.5 | 881.6 | 885.3 | 885.6 | 919.9 | 893.9 | 977.1 | 900.5 | 838.7 | 842.4 | 767.1 | 736 | 840 | 923.7 | 769.9 | 773.1 | 856.8 | 735.9 | 691.6 | 910.8 | 878.1 | 913.3 | 899.3 | 885 | 883.7 | 979 | 965.5 | 831.3 | 835.4 | 763.4 | 762 | 733.5 | 796.7 | 768.7 | 787.9 | 771.6 | 761.2 | 762.1 | 756.8 | 783.2 | 787.1 | 776.7 | 786.5 | 773.1 | 771 | 754.1 | 791.6 | 760.1 | 788.6 | 755.3 | 789.1 | 792.6 | 784.1 | 792.7 | 791.4 | 780.1 | 788.2 | 788.8 | 838.3 | 860.9 | 879.1 | 834.5 | 888.4 | 930.6 | 873.6 | 884.2 | 849.9 | 886.3 | 885 | 849.9 | 928.5 | 907 | 827.7 | 922 | 911.5 | 691.5 | 692.2 | 880.7 | 736.5 | 843.9 | 783.6 | 780.1 | 778.2 | 781.9 | 763.5 | 771 | 784.7 | 774.8 | 766.3 | 794.1 | 865.6 | 785 | 791 | 752.7 | 742.9 | 740.2 | 775.7 | 780.5 | 780.7 | 781.4 | 780.7 | 877 | 775.7 | 774.7 | 786.1 | 779.1 | 709.2 | 784.1 | 794.3 | 755.1 | 745.8 | 743.4 | 854.1 | 753.3 | 790.3 | 786.3 | 782.6 | 742.5 | 701.3 | 769.3 | 819.1 | 740.1 | 745.8 | 795.6 | 780 | 778.7 | 782.3 | 780.2 | 771.1 | 835.3 | 740.3 | 747.1 | 733.7 | 765.8 | 761 | 750.5 | 784.3 | 801.3 | 795.9 | 768.7 | 790.7 | 794.3 | 793.8 | 794 | 802.9 | 786.9 | 757.9 | 755 | 801.3 | 713.4 | 756.6 | 764.6 | 834.5 | 794.3 | 796.4 | 761.8 | 838.4 | 801.4 | 837 | 751.3 | 796.8 | 751.6 | 759.5 | 721.1 | 765.6 | 764.5 | 765.6 | 0 | 36.9 | 0 | 0 | 3.7 | 3.35 | 0 | 0 | 88756720 | 262025 | 90148240 | 306873 | 74019550 | 155528 | 88364810 | 134605 | 839580 | 10140 | 121050 | 670 | 66850 | 120 | 68390 | 81 | 66850 | 279 | 66230 | 360 | 134000 | 2000 | 132000 | 0 | 268320 | 266000 | 12.4167 | 3.7 | 3.35 |  | 36.9 | 0 | 272689.4
2025-06-02 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:39 | 17:35 | 317.3 | 309.4 | 338.4 | 337.7 | 336.9 | 320.1 | 345.5 | 327.4 | 341.1 | 342.8 | 343 | 340.2 | 341.7 | 342.8 | 346.5 | 344.5 | 322.5 | 330.1 | 343 | 347.7 | 358.5 | 352.1 | 358 | 356.7 | 356 | 350.1 | 356.1 | 351.8 | 361 | 356.3 | 353.4 | 354.5 | 335.3 | 316.5 | 319.1 | 322.1 | 326.4 | 324.4 | 336.9 | 324.3 | 333.3 | 362.9 | 383.3 | 358.3 | 362.4 | 374.8 | 402.4 | 399.9 | 429.6 | 380.3 | 362.1 | 357.6 | 355.8 | 368.1 | 363.7 | 369.2 | 387.3 | 353.5 | 312.1 | 355.7 | 338.9 | 321.8 | 350.6 | 813.9 | 796.1 | 803.2 | 803.9 | 816 | 802.5 | 795.8 | 814.3 | 819.4 | 804.3 | 790.7 | 793.5 | 765.5 | 749.8 | 778.3 | 806.7 | 802 | 799.2 | 839.7 | 816.3 | 774 | 822.9 | 776.7 | 777 | 803.8 | 809.7 | 801.7 | 804.6 | 794.9 | 808 | 812.6 | 817.7 | 828.1 | 895.3 | 818.1 | 816.3 | 762.5 | 759.2 | 813.4 | 792.8 | 822.9 | 847.2 | 814.6 | 825.9 | 810.5 | 798.1 | 828.6 | 825.7 | 833.6 | 754.2 | 776.6 | 794.6 | 821.2 | 811 | 815.5 | 805.1 | 808.1 | 801.4 | 808.6 | 765.3 | 772.2 | 816.5 | 812.6 | 794.2 | 812.1 | 800.6 | 800.8 | 794.2 | 801.2 | 803.5 | 812.8 | 796.9 | 811.8 | 780.7 | 821.1 | 878.9 | 797.9 | 800.4 | 806.8 | 812.4 | 807.8 | 806.1 | 814.6 | 811 | 775.6 | 843.1 | 756.1 | 694.9 | 815.4 | 755.2 | 805.9 | 810.7 | 797.3 | 808.1 | 804.2 | 806.9 | 792.5 | 796.9 | 796.7 | 784.6 | 850.1 | 823.4 | 759.9 | 700 | 713.6 | 709.1 | 711.5 | 713.6 | 714 | 715.3 | 728.5 | 731.3 | 721.5 | 717.2 | 722 | 725.8 | 679.5 | 615.6 | 728.8 | 724.2 | 718.4 | 729.9 | 727.9 | 716.1 | 727.5 | 709.9 | 723.9 | 699.4 | 719.7 | 712.2 | 720.3 | 681.4 | 678.3 | 691.7 | 781.7 | 761.3 | 687.8 | 797.3 | 801.8 | 804.2 | 836.7 | 813.4 | 889.3 | 821.7 | 764.2 | 767.6 | 610 | 560 | 760 | 833.3 | 697.3 | 698.1 | 764.1 | 665.5 | 625.4 | 823.7 | 811 | 826.9 | 813.2 | 794.4 | 800.1 | 886.2 | 874.2 | 738.1 | 742.7 | 679.1 | 681.5 | 662.7 | 711.4 | 692.6 | 709.2 | 685.7 | 679.3 | 679.5 | 681.4 | 703.7 | 703.3 | 697.1 | 708.2 | 689.4 | 696 | 679.4 | 709.2 | 676.6 | 700 | 672.5 | 705.8 | 711.3 | 701.9 | 711.5 | 710.5 | 708.9 | 709.1 | 712.9 | 761.5 | 785.8 | 798.6 | 757.9 | 808.6 | 846.4 | 801.8 | 805.9 | 772.6 | 809.3 | 809.2 | 773.4 | 847.9 | 826.5 | 749.9 | 839.8 | 827.2 | 629.8 | 631.1 | 801.4 | 670.9 | 770.5 | 713.9 | 707.3 | 704.7 | 708.8 | 693.6 | 704.3 | 710.1 | 698 | 692.3 | 718 | 768.2 | 710.3 | 712.4 | 677.5 | 677.8 | 671.5 | 708.1 | 712 | 707 | 714.7 | 712.1 | 770 | 706.9 | 702.1 | 714.1 | 707 | 639.7 | 708.8 | 716 | 681.4 | 673.5 | 683 | 762.6 | 677.3 | 713.5 | 706.5 | 701.2 | 663.1 | 625.6 | 600 | 731.4 | 668.9 | 676.4 | 722.2 | 714.5 | 705 | 700.7 | 704.8 | 703.9 | 750 | 663 | 674.9 | 650.8 | 688.6 | 692 | 672.9 | 719.2 | 732.6 | 730.7 | 698.9 | 721.7 | 722.8 | 718.7 | 719.7 | 726.5 | 709.7 | 684.2 | 680 | 721.8 | 644.8 | 683.5 | 694 | 763 | 722.9 | 720.8 | 700.1 | 759.6 | 733.6 | 759.9 | 683.8 | 726.2 | 683.2 | 690.7 | 656.3 | 693.4 | 694.7 | 692.4 | 0 | 34.45 | 0 | 0 | 3.49 | 3.16 | 0 | 0 | 88818970 | 262156 | 90211190 | 307003 | 74080010 | 155614 | 88425110 | 134736 | 840200 | 10140 | 121650 | 680 | 62250 | 131 | 62950 | 130 | 60460 | 86 | 60300 | 131 | 124000 | 0 | 120000 | 2000 | 245960 | 244000 | 12.9333 | 3.49 | 3.16 |  | 34.45 | 0 | 248944.7
2025-06-03 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:33 | 17:33 | 261.8 | 255 | 279.8 | 279.1 | 278.9 | 265.6 | 284.7 | 274.6 | 283.8 | 284.7 | 282.8 | 281.4 | 283.6 | 283.3 | 286.7 | 284.2 | 267 | 272.8 | 283.5 | 287.3 | 296.7 | 290.8 | 296 | 295.6 | 296 | 290 | 295 | 292.5 | 299.5 | 297.9 | 293 | 294.3 | 278.2 | 261.7 | 263.4 | 266.5 | 270.3 | 268.1 | 279.9 | 268.3 | 275.3 | 300 | 316.9 | 295.8 | 299.7 | 310.1 | 333.6 | 332.6 | 351.1 | 316.1 | 299.9 | 297.9 | 296.5 | 304.3 | 300.9 | 306 | 321.1 | 292.7 | 258.3 | 292.4 | 279.3 | 266.5 | 291.2 | 673.6 | 656.5 | 663.6 | 663 | 676 | 665.4 | 658.8 | 674 | 679.4 | 664.2 | 655.6 | 663.6 | 636.1 | 625.6 | 654.4 | 667.4 | 661 | 661.3 | 696.7 | 673.2 | 638.5 | 679.6 | 644.4 | 644.6 | 665.9 | 669.1 | 665.9 | 665.3 | 652.7 | 660.6 | 665.2 | 667.6 | 680.1 | 735.6 | 675 | 670.4 | 621.6 | 621.4 | 669.3 | 650.6 | 675.1 | 698.1 | 671.1 | 679.1 | 671 | 658.1 | 684.5 | 680.8 | 688.1 | 621.6 | 644.1 | 660.7 | 682.4 | 673.8 | 675.9 | 666 | 670.6 | 665.1 | 675.6 | 636.8 | 642.7 | 679.8 | 676.9 | 661.2 | 677.6 | 666.6 | 667.9 | 664.8 | 669.9 | 675.2 | 680.7 | 667.7 | 679.6 | 655.5 | 681.1 | 732.8 | 663.1 | 660 | 672.5 | 676.3 | 671.7 | 669.3 | 668 | 675.2 | 646.9 | 704.9 | 631 | 580.5 | 678.5 | 631.3 | 675.9 | 677.3 | 667.1 | 675.7 | 676.1 | 678.3 | 666.7 | 669.3 | 669.4 | 656.4 | 700.2 | 691.8 | 637.8 | 598.2 | 610.8 | 606.9 | 609.5 | 612.5 | 610.7 | 610 | 619.1 | 620.9 | 616.4 | 615.3 | 617.8 | 622.3 | 580.2 | 529.3 | 630.3 | 620.7 | 615.8 | 620.7 | 618.4 | 611.5 | 619.4 | 609.7 | 618 | 600.7 | 617 | 606.6 | 613.8 | 584.3 | 579.2 | 591.2 | 658.9 | 641.1 | 579.6 | 670.8 | 675.3 | 677.6 | 703.5 | 683.2 | 746.3 | 688.5 | 643.6 | 646.2 | 610 | 664.5 | 644 | 704.8 | 589.2 | 587.3 | 653.7 | 561.1 | 590 | 693.5 | 684.9 | 694.8 | 685.6 | 675.5 | 685 | 746.5 | 737.5 | 637.9 | 644 | 587.5 | 590 | 592.5 | 616.5 | 596.4 | 612.5 | 593 | 588.8 | 588.3 | 591.4 | 598.6 | 605.8 | 596.7 | 606.9 | 601 | 616 | 593 | 615.8 | 586.8 | 602.7 | 583.7 | 610.2 | 615.2 | 605 | 615 | 614.3 | 607.9 | 608.8 | 614.6 | 634.8 | 656.3 | 666.7 | 633.2 | 675.5 | 711.7 | 675.3 | 675.2 | 649.5 | 678.5 | 677 | 649.3 | 712.5 | 693.1 | 619.5 | 703.6 | 694.6 | 529.5 | 530.2 | 672.9 | 563.6 | 645.3 | 604.8 | 597.7 | 595.7 | 598.8 | 586.7 | 595.9 | 601.8 | 596.7 | 588.4 | 613.8 | 650.4 | 605.1 | 608.7 | 581.8 | 574.2 | 569.8 | 597.2 | 603.7 | 601.6 | 606.1 | 605.1 | 650 | 599.1 | 598.4 | 606.1 | 604.1 | 546 | 605.8 | 614.6 | 582 | 576 | 584.7 | 671.9 | 584.2 | 611.2 | 607.1 | 603.6 | 575.2 | 541.7 | 607 | 633.7 | 573.2 | 580.9 | 627.4 | 618.1 | 614.7 | 607.3 | 610.7 | 595.4 | 647 | 577.9 | 581.9 | 548 | 598 | 600 | 585.8 | 602.2 | 611.5 | 614.1 | 583 | 607.9 | 606.3 | 600 | 605.1 | 612.3 | 596.8 | 580.4 | 595 | 608.8 | 543.5 | 577.6 | 586.1 | 645 | 602.3 | 602.9 | 587.3 | 636.7 | 617.1 | 637.9 | 576.9 | 609.3 | 577.5 | 586.2 | 551.9 | 584.8 | 589.2 | 583.9 | 0 | 32.94 | 0 | 0 | 2.78 | 2.49 | 0 | 0 | 88870550 | 262265 | 90263860 | 307132 | 74131110 | 155630 | 88475100 | 134772 | 840720 | 10150 | 122150 | 680 | 51580 | 109 | 52670 | 129 | 51100 | 16 | 49990 | 36 | 104000 | 2000 | 100000 | 0 | 205340 | 204000 | 13 | 2.78 | 2.49 |  | 32.94 | 0 | 210051.5
2025-06-04 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 5:02 | 17:19 | 438.7 | 427.4 | 468.9 | 467.6 | 460.9 | 441 | 477.2 | 459 | 468.4 | 469.5 | 474.5 | 470.9 | 468 | 467.8 | 473.6 | 473.8 | 444.2 | 451.2 | 468.6 | 475.4 | 492.1 | 480.1 | 487.2 | 488.1 | 488.8 | 478.9 | 485.4 | 481.8 | 497.4 | 490.9 | 484.1 | 486.7 | 453.6 | 427.8 | 434.4 | 437.5 | 447.7 | 446.5 | 459.5 | 442.8 | 456.6 | 490.7 | 513.9 | 481.8 | 489.6 | 503.6 | 544.7 | 542 | 580.8 | 519.7 | 491.6 | 489.2 | 489.4 | 503 | 497.3 | 506.3 | 529.4 | 483.4 | 427.8 | 486.6 | 470.6 | 441.7 | 478.9 | 1132.3 | 1137 | 1138 | 1140 | 1138.9 | 1124 | 1100.4 | 1124.7 | 1133.6 | 1108.8 | 1095.8 | 1105 | 1064.6 | 1041 | 1106.3 | 1119 | 1122.9 | 1107.2 | 1179.8 | 1141.2 | 1081.1 | 1150.5 | 1096.6 | 1100 | 1132.5 | 1132.3 | 1122.8 | 1119.5 | 1126.7 | 1149 | 1155 | 1160.6 | 1173.8 | 1263.9 | 1163.9 | 1162.1 | 1096.8 | 1095.2 | 1154.6 | 1116.4 | 1157.6 | 1213.8 | 1154.8 | 1162.3 | 1139.9 | 1148.2 | 1164.2 | 1159.5 | 1143.1 | 1060.1 | 1093.8 | 1101.8 | 1129.3 | 1121.4 | 1131.5 | 1112.6 | 1127.2 | 1108.3 | 1123.4 | 1065.9 | 1076.3 | 1123.5 | 1115 | 1101 | 1122.3 | 1116.8 | 1114.5 | 1103.1 | 1107.3 | 1112.1 | 1122.2 | 1099.5 | 1117.9 | 1073.2 | 1064.8 | 1134.8 | 1040.4 | 1041.2 | 1054.5 | 1061 | 1066 | 1058.4 | 1071 | 1074.8 | 1050 | 1132.2 | 1014.6 | 941.6 | 1079 | 1016.6 | 1090.7 | 1102.2 | 1092.7 | 1105.7 | 1109.1 | 1110.6 | 1088.6 | 1098.5 | 1064.5 | 1062.1 | 1160.7 | 1121.9 | 1039.4 | 960 | 958.6 | 958 | 956 | 961 | 960 | 965 | 966 | 966.2 | 960 | 967.6 | 970.3 | 968.1 | 914.4 | 832.2 | 1010 | 972.1 | 966 | 974 | 967.6 | 958 | 971.2 | 961.5 | 973.9 | 968 | 976.6 | 962.2 | 967.1 | 922.2 | 918.5 | 919.7 | 1065.2 | 1034.4 | 926.6 | 1073.1 | 1080.4 | 1080.7 | 1114.6 | 1084.7 | 1184.4 | 1086.2 | 1026 | 1019.8 | 969 | 1067 | 1049 | 1138.6 | 960 | 955 | 1053.6 | 905.3 | 848.5 | 1110 | 1104 | 1112.1 | 1108 | 1108 | 1121 | 1188.7 | 1195 | 1035.7 | 1036.4 | 950.3 | 952.3 | 958.2 | 996.4 | 968.2 | 989.3 | 956.7 | 944.2 | 946.6 | 951.8 | 973.5 | 971.7 | 958.1 | 967.1 | 956.7 | 988 | 941.9 | 984.2 | 943 | 977.9 | 936.4 | 980.7 | 981 | 967.4 | 978.5 | 982.9 | 966.2 | 969.8 | 972.7 | 1073.1 | 1082.6 | 1128.3 | 1070.3 | 1116.3 | 1193.3 | 1127.6 | 1137.3 | 1095.3 | 1142.8 | 1137.2 | 1088.9 | 1180.3 | 1151.2 | 1042.4 | 1157.2 | 1155.5 | 875 | 879 | 1122.1 | 935.3 | 1077.6 | 1022.8 | 1014.6 | 1011.9 | 1017.5 | 989.5 | 1004.5 | 1019.5 | 1001.3 | 994 | 1025.8 | 1091.8 | 1014.3 | 1020.2 | 969.3 | 965.2 | 960.8 | 1009.5 | 1013.9 | 1012.2 | 1016.6 | 1009.1 | 1095 | 1006.5 | 1004.4 | 1020.1 | 1011.4 | 916.3 | 1017.2 | 1026.7 | 976.6 | 966 | 982.8 | 1089.8 | 983 | 1028.2 | 1022.8 | 1014.4 | 957 | 902.3 | 987.4 | 1052 | 964.7 | 973.7 | 1030.6 | 1017 | 1008.5 | 1006.7 | 1012.8 | 997.1 | 1072.4 | 955 | 954.4 | 942.2 | 970.3 | 972 | 954.4 | 999.3 | 1019.5 | 1018.9 | 977.9 | 1009.1 | 1007.6 | 1010.3 | 1007.1 | 1018.3 | 997.6 | 963.1 | 960 | 1019.2 | 914.3 | 965.5 | 981.4 | 1076.2 | 1019.2 | 1020.1 | 986.2 | 1070.4 | 1035.4 | 1088.8 | 978.8 | 1033.8 | 981.1 | 972.9 | 930.7 | 994 | 989.3 | 983 | 0 | 37.12 | 0 | 0 | 4.79 | 4.51 | 0 | 0 | 88956830 | 262415 | 90348660 | 307316 | 74214330 | 155684 | 88560610 | 134861 | 841570 | 10150 | 122990 | 690 | 86280 | 150 | 84800 | 184 | 83220 | 54 | 85510 | 89 | 170000 | 0 | 168000 | 2000 | 339810 | 338000 | 12.2833 | 4.79 | 4.51 |  | 37.12 | 0 | 346019.6
2025-06-05 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:58 | 17:38 | 397.3 | 385.3 | 422.7 | 421.9 | 411.8 | 394.1 | 427.9 | 412.5 | 419.5 | 419.8 | 425.7 | 422.3 | 414.6 | 420.3 | 420.2 | 422.8 | 398.8 | 404.6 | 423 | 428.2 | 441.4 | 435.9 | 438.3 | 436.9 | 438.6 | 435.5 | 436.1 | 434.2 | 445.6 | 443.1 | 436.7 | 437.7 | 401.7 | 378.9 | 384.5 | 387.2 | 396.5 | 397.3 | 404.5 | 391 | 403.5 | 434.4 | 455.6 | 430.5 | 433.9 | 446.8 | 481.1 | 478.8 | 514.3 | 460.4 | 432.9 | 430.3 | 432.4 | 448.1 | 443.1 | 450.7 | 471.5 | 431.9 | 383.9 | 437.1 | 420.7 | 393.8 | 422.8 | 1004.4 | 992.7 | 997.5 | 1000.4 | 1004 | 995.7 | 980 | 1002.8 | 1003.2 | 986.2 | 971.2 | 985.5 | 952.4 | 936.6 | 980.8 | 997.8 | 1003 | 978.3 | 1042.1 | 989 | 967.1 | 1013.3 | 966.1 | 962.9 | 994.5 | 1005.5 | 998.7 | 999.9 | 966.1 | 989.5 | 994.3 | 1000.5 | 1004.1 | 1086.9 | 999.3 | 995.7 | 947.8 | 946.5 | 1001.9 | 971.1 | 1003.3 | 1020.7 | 996.9 | 1013.1 | 1000.8 | 1003.5 | 1022.1 | 1017.9 | 993.7 | 927 | 957.6 | 979.7 | 974.9 | 994.8 | 1003 | 992.5 | 1003.7 | 992.6 | 990.3 | 940.8 | 951.5 | 996.2 | 986.8 | 974.2 | 990.9 | 981.9 | 965.4 | 964 | 970 | 974.6 | 978.3 | 961.1 | 976.2 | 940.9 | 988.5 | 1047.1 | 953.1 | 950.6 | 973.5 | 971.7 | 966.2 | 960 | 972.5 | 961.2 | 926.6 | 1000.6 | 901.9 | 830.8 | 963.7 | 895.9 | 957.1 | 965.5 | 956.5 | 958.4 | 950 | 935.6 | 951.3 | 958.7 | 955.4 | 937 | 1017.6 | 985.1 | 910.6 | 903.8 | 915.3 | 901.4 | 894.7 | 886.1 | 882.5 | 878.1 | 883.5 | 889.7 | 885.7 | 910.2 | 915.7 | 903.1 | 859.7 | 774.6 | 899.3 | 898.4 | 888.3 | 896.2 | 886.8 | 878 | 881.3 | 876.1 | 882.2 | 866 | 882.1 | 855.2 | 814.1 | 830.2 | 819.1 | 832 | 969.6 | 953.4 | 865.2 | 1008.1 | 1014.2 | 1024.5 | 1051.2 | 1027.5 | 1132.6 | 1046.9 | 982 | 986.7 | 882.3 | 975.9 | 969 | 1037.8 | 866.8 | 874.9 | 971.1 | 836.2 | 790.4 | 1033.8 | 1047.8 | 1057.7 | 1047.7 | 1027.4 | 1034.2 | 1119.8 | 1102.1 | 901.3 | 900.8 | 832.4 | 831.6 | 828.2 | 862.3 | 841 | 863.4 | 843.5 | 832.2 | 829.8 | 834.3 | 861.7 | 855.3 | 853.4 | 855.9 | 843.2 | 850 | 830.7 | 865.1 | 836.5 | 873.2 | 834.4 | 876.1 | 867.5 | 863 | 887.5 | 887.6 | 863.1 | 871.9 | 876.7 | 878.9 | 962.1 | 982.8 | 933.9 | 967.9 | 879 | 958.2 | 985.5 | 953.2 | 997.1 | 990.4 | 951.4 | 1024.4 | 1000.5 | 919.1 | 1008.9 | 999.9 | 761.4 | 762.1 | 972.9 | 811.4 | 943.7 | 896.9 | 891.5 | 881.5 | 897.6 | 861.2 | 885.3 | 886.4 | 864.4 | 857.3 | 882 | 954.5 | 874 | 875.3 | 835.5 | 849.3 | 834.1 | 876.5 | 879.8 | 879.3 | 884 | 880.5 | 948.1 | 873.9 | 867.9 | 880.2 | 873.2 | 795.9 | 873.7 | 878.2 | 839.5 | 832.1 | 865.1 | 964.4 | 854.7 | 889 | 882.6 | 872.6 | 826.6 | 779.8 | 869 | 907.4 | 829.3 | 841.1 | 886.2 | 880.2 | 859.8 | 866.4 | 868.2 | 874.5 | 927 | 822.7 | 825.7 | 838.8 | 839.1 | 840 | 843.1 | 854.1 | 876.4 | 872.7 | 843 | 865.3 | 861 | 871.3 | 858.4 | 872.6 | 853.3 | 823.1 | 826 | 876.6 | 786.6 | 829.9 | 844.4 | 926.1 | 882.2 | 882.5 | 850.7 | 924 | 890.5 | 940.5 | 852.4 | 892.2 | 827 | 818 | 803.1 | 862.2 | 851.6 | 845.3 | 0 | 35.24 | 0 | 0 | 4.34 | 4.02 | 0 | 0 | 89033060 | 262587 | 90424920 | 307549 | 74289230 | 155786 | 88634960 | 135059 | 842330 | 10150 | 123730 | 690 | 76230 | 172 | 76260 | 233 | 74900 | 102 | 74350 | 198 | 152000 | 0 | 148000 | 0 | 301740 | 300000 | 12.6667 | 4.34 | 4.02 |  | 35.24 | 0 | 306002.7
2025-06-06 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 5:26 | 17:31 | 405.4 | 396.3 | 433.4 | 433.3 | 426.6 | 409.5 | 440.2 | 423.9 | 432.4 | 433.8 | 439.6 | 435.3 | 433.9 | 434.9 | 437.6 | 438.2 | 412.3 | 417 | 439.2 | 442.2 | 456.8 | 450.3 | 450.3 | 449 | 453.3 | 452.3 | 453.2 | 447.4 | 460.5 | 456.3 | 451.8 | 449.5 | 423.6 | 398 | 402.7 | 406.7 | 415.4 | 412.1 | 427.1 | 410.2 | 423.8 | 456.8 | 478.4 | 451.5 | 453.6 | 468.2 | 499.8 | 496.2 | 526.5 | 474.4 | 451 | 448.3 | 448.8 | 462.2 | 454 | 462.3 | 483.8 | 444 | 393.1 | 445.3 | 431.1 | 402.7 | 440.2 | 1036.8 | 1026.1 | 1040.5 | 1039 | 1023.7 | 1017.5 | 1010.1 | 1038.4 | 1022.7 | 1006.5 | 983.6 | 1000 | 966.1 | 953.2 | 964.6 | 1034.8 | 1047 | 1008.8 | 1077.5 | 1058.8 | 999.6 | 1039 | 1005.8 | 988.7 | 1024 | 1048.7 | 1035.1 | 1031.8 | 1019.7 | 1036.2 | 1060.5 | 1061 | 1053.8 | 1132.8 | 1061.6 | 1049.8 | 991.5 | 1003.3 | 1049.4 | 1028.2 | 1042.7 | 1071.4 | 1031.6 | 1052.5 | 1015.6 | 1028.2 | 1051.2 | 1057.3 | 1059.9 | 966.4 | 985.4 | 1011.8 | 1012.7 | 1019.6 | 1024.7 | 1041.3 | 1033.6 | 1018.4 | 1011.3 | 962.2 | 974.3 | 1025.4 | 1024 | 1003.3 | 1025.2 | 1008.5 | 1004.2 | 997.5 | 1017.6 | 1002.4 | 1022.9 | 999.7 | 1013.7 | 969 | 1007.3 | 1061 | 1008 | 999.5 | 983.4 | 1004 | 1011.2 | 1002.9 | 1007 | 967.5 | 983.7 | 1062.5 | 961.4 | 893.5 | 1006.8 | 950.3 | 997.2 | 1001.7 | 979.5 | 1024.5 | 1018.6 | 1008.7 | 950.8 | 1015.1 | 954.2 | 1001.4 | 1046.1 | 1017.7 | 978.8 | 857.2 | 873.9 | 870.7 | 878.4 | 882.5 | 888.3 | 897.9 | 914.1 | 908.2 | 892.1 | 877.5 | 885 | 895 | 843.1 | 770.5 | 895.8 | 891.1 | 883.8 | 895.8 | 897.2 | 881.3 | 901 | 879.3 | 896.8 | 871.4 | 899.8 | 906.6 | 905.1 | 861.8 | 864.9 | 866.6 | 965.1 | 948.3 | 857.3 | 975.7 | 977.4 | 981.6 | 1017.2 | 987 | 1083.6 | 988.3 | 923.6 | 937.3 | 899.5 | 967.7 | 948 | 1015.1 | 847.9 | 867.9 | 954.9 | 829.5 | 776.6 | 999.7 | 1002.3 | 1013.2 | 1004.9 | 1000.7 | 1000 | 1066.8 | 1057.6 | 932.1 | 930.7 | 869.7 | 869.7 | 883.7 | 908.2 | 890.3 | 907.1 | 869.7 | 862.3 | 870.4 | 871.4 | 900 | 897 | 888.2 | 898.1 | 856.7 | 878 | 859.7 | 879.6 | 845.1 | 893.5 | 852 | 894.7 | 900 | 882.4 | 884.7 | 883.5 | 893.2 | 891.8 | 897.3 | 949.9 | 1003.5 | 1044.8 | 981.3 | 1003.3 | 1030 | 1007.7 | 1021.8 | 988.7 | 1033.2 | 1018.6 | 984.9 | 1054.4 | 1024.1 | 963.4 | 1035.4 | 1059.6 | 815.7 | 816.7 | 1008.6 | 864.4 | 977 | 925.8 | 923.9 | 917.8 | 916.2 | 899.4 | 909.1 | 935.2 | 923.5 | 907.8 | 936.4 | 979.9 | 924.8 | 929.7 | 898.9 | 880.4 | 872 | 911.8 | 910.7 | 916.8 | 918.3 | 902.9 | 960.6 | 903.2 | 903.7 | 909.6 | 907.1 | 837.5 | 913.3 | 928.5 | 884.4 | 870.8 | 906.9 | 973.2 | 899.5 | 942.2 | 940.7 | 936.1 | 896.6 | 849.4 | 946.4 | 977.1 | 890.4 | 889 | 954 | 936.9 | 931.9 | 941.8 | 939.9 | 947.4 | 987.7 | 898 | 918.1 | 923.1 | 938.7 | 937 | 934.3 | 914 | 933.8 | 933.5 | 909 | 932.9 | 929.4 | 945.8 | 938.1 | 956.4 | 942.9 | 899.8 | 902 | 962.4 | 871.6 | 915 | 925.2 | 969.6 | 936.1 | 938.7 | 904.1 | 980.5 | 945.5 | 969.8 | 884.9 | 940.7 | 889.2 | 909.5 | 874.8 | 906.9 | 915.2 | 908.3 | 0 | 37.01 | 0 | 0 | 4.52 | 4.25 | 0 | 0 | 89111900 | 262719 | 90502940 | 307727.6 | 74364550 | 155799.8 | 88713680 | 135099.4 | 843100 | 10160 | 124500 | 700 | 78840 | 132 | 78020 | 178.6 | 75320 | 13.8 | 78720 | 40.4 | 154000 | 2000 | 154000 | 2000 | 310900 | 308000 | 12.0833 | 4.52 | 4.25 |  | 37.01 | 0 | 316890.6
2025-06-07 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:55 | 17:24 | 492.3 | 481.7 | 525.2 | 524.8 | 525.4 | 508.8 | 535 | 517.1 | 530 | 534.1 | 534.3 | 530.5 | 534.4 | 533 | 536.8 | 535.5 | 503.1 | 505.3 | 530.3 | 534.7 | 552 | 545.2 | 549.4 | 548.8 | 546.9 | 548.9 | 549.3 | 542 | 550.1 | 550.4 | 546.5 | 546.3 | 526.5 | 494.7 | 499.3 | 501.5 | 510 | 505.8 | 527.8 | 503.3 | 521.4 | 566 | 597.8 | 565.9 | 563.5 | 583.3 | 620.7 | 615.6 | 653.8 | 586.4 | 561.6 | 554.8 | 552.4 | 573.3 | 562.7 | 566 | 590.1 | 543.5 | 478.5 | 545.8 | 526 | 493.4 | 546.7 | 1231 | 1215.5 | 1227.5 | 1228.5 | 1224.4 | 1219.3 | 1210.4 | 1247.7 | 1229.5 | 1216.6 | 1185.1 | 1211.6 | 1168.1 | 1156.9 | 1174.3 | 1204.9 | 1233.9 | 1180 | 1259 | 1232 | 1178.2 | 1215.5 | 1184 | 1166 | 1200.8 | 1234.7 | 1223.2 | 1229.1 | 1172.4 | 1206.4 | 1215 | 1227 | 1218 | 1307.3 | 1219.9 | 1216 | 1163.8 | 1168.1 | 1222.6 | 1197.1 | 1218.8 | 1258.8 | 1218.1 | 1237.9 | 1217.2 | 1220.9 | 1248 | 1244.1 | 1228.5 | 1137 | 1153.2 | 1212.2 | 1229.3 | 1214.9 | 1233.5 | 1246.7 | 1241.1 | 1234.8 | 1232.7 | 1171.6 | 1186.7 | 1261.2 | 1259.1 | 1232.2 | 1261.8 | 1228 | 1228.5 | 1218.3 | 1252.8 | 1230.1 | 1255.7 | 1227.9 | 1248.2 | 1221.2 | 1227.9 | 1301.6 | 1204.5 | 1222.8 | 1205.5 | 1215.2 | 1235.6 | 1224.9 | 1231.1 | 1187.6 | 1191.5 | 1295 | 1169.8 | 1082.9 | 1232.7 | 1163.1 | 1224.5 | 1235.4 | 1213.7 | 1264.5 | 1221.9 | 1236.2 | 1226.2 | 1235.1 | 1227.4 | 1221.5 | 1291 | 1257.5 | 1169.3 | 1075.2 | 1095.8 | 1096.6 | 1100.7 | 1099.9 | 1101.9 | 1104.7 | 1117.2 | 1119.7 | 1109.8 | 1103.6 | 1109.7 | 1116.2 | 1053.8 | 961 | 1126 | 1115 | 1106.9 | 1118.6 | 1116.5 | 1098.8 | 1113.5 | 1095.5 | 1111.3 | 1086.6 | 1111.7 | 1103.7 | 965.8 | 1055.2 | 1054.2 | 1063 | 1198.5 | 1184.2 | 1066.3 | 1215.4 | 1221.6 | 1232.7 | 1265.2 | 1228.8 | 1349.3 | 1222.1 | 1134.1 | 1144.3 | 939.9 | 1178.8 | 1176 | 1276.7 | 1080 | 1087.5 | 1196.8 | 1038.2 | 974.6 | 1207.4 | 1202.3 | 1269.9 | 1226.2 | 1202 | 1215.7 | 1330.5 | 1301 | 1159 | 1156.9 | 1075.8 | 1080 | 1090.8 | 1129.8 | 1101.1 | 1122.8 | 1084.1 | 1073.2 | 1076.2 | 1080.5 | 1121 | 1108.9 | 1103 | 1104.4 | 1083.1 | 1112 | 1067.3 | 1109.8 | 1066.1 | 1104.2 | 1064.8 | 1113.6 | 1109.3 | 1090.6 | 1105.4 | 1117.1 | 1099.5 | 1099.6 | 1084 | 1146.3 | 1192.6 | 1249.6 | 1186.4 | 1221.8 | 1296.6 | 1236.6 | 1245.6 | 1201.5 | 1258.4 | 1240.8 | 1200.7 | 1304.9 | 1263.8 | 1184.8 | 1277.8 | 1304.3 | 1001.7 | 1002.2 | 1240.6 | 1048 | 1193.9 | 1112.9 | 1105.5 | 1104.3 | 1103.8 | 1067.7 | 1087.8 | 1114.8 | 1103.2 | 1088.3 | 1126.2 | 1181.2 | 1107.7 | 1126.4 | 1079.6 | 1049.5 | 1054.6 | 1097.3 | 1103.2 | 1097.1 | 1098.9 | 1099.9 | 1180 | 1101.1 | 1100.7 | 1114.9 | 1106.6 | 1012.9 | 1111.9 | 1124.8 | 1073.5 | 1063.8 | 1075.2 | 1180.6 | 1070.2 | 1116.6 | 1115.8 | 1113.8 | 1069.5 | 1007.4 | 1110 | 1159.9 | 1059.9 | 1071.2 | 1128.5 | 1120.6 | 1110.4 | 1109.2 | 1111.3 | 1109.9 | 1171.6 | 1060.7 | 1075 | 1071.1 | 1098.1 | 1100 | 1086.6 | 1124.1 | 1147.7 | 1138.1 | 1109 | 1135.3 | 1145.1 | 1138.3 | 1142.7 | 1147.4 | 1095.4 | 1091.1 | 1093 | 1138.1 | 1022 | 1084.9 | 1094.8 | 1168.9 | 1122.4 | 1128.6 | 1089.4 | 1184.3 | 1141.1 | 1166.9 | 1077 | 1134.3 | 1075.6 | 1090 | 1038.8 | 1061.8 | 1088.9 | 1078.7 | 0 | 40.89 | 0 | 0 | 5.87 | 5.14 | 0 | 0 | 89206090 | 262857 | 90598880 | 307910 | 74458040 | 155917 | 88808240 | 135284 | 844050 | 10160 | 125440 | 700 | 94190 | 138 | 95940 | 182.4 | 93490 | 117.2 | 94560 | 184.6 | 190000 | 0 | 188000 | 0 | 378180 | 378000 | 12.4833 | 5.87 | 5.14 |  | 40.89 | 0 | 384478.2
2025-06-08 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:43 | 17:37 | 590 | 577 | 627 | 623.5 | 624.5 | 608.7 | 637 | 614.8 | 631 | 631.4 | 637.6 | 632.9 | 628.9 | 630.4 | 633.5 | 632.8 | 599.3 | 602.1 | 634.8 | 640 | 660.1 | 650.8 | 656.8 | 651.4 | 653.4 | 655 | 654.7 | 647.5 | 659.8 | 657.8 | 652.8 | 653.8 | 617.8 | 584.8 | 590.2 | 590.5 | 601 | 600.1 | 622.9 | 595.1 | 617.4 | 667.7 | 702.2 | 659.9 | 660 | 681.2 | 734.5 | 725.5 | 781.2 | 695.7 | 661.9 | 655.7 | 654.2 | 681.7 | 673.5 | 674.2 | 697.6 | 645.1 | 568.7 | 649.4 | 629.4 | 588.1 | 641.2 | 1498.6 | 1476 | 1471.1 | 1482.3 | 1480.5 | 1468.7 | 1463 | 1497.2 | 1488.3 | 1462.4 | 1427.6 | 1462.2 | 1415.9 | 1395.6 | 1501.6 | 1504.8 | 1505.5 | 1471.2 | 1565.6 | 1523.3 | 1446.3 | 1503.4 | 1444.1 | 1429.5 | 1467.5 | 1487.2 | 1490 | 1493.7 | 1418 | 1441.7 | 1446.2 | 1465.7 | 1464.3 | 1557 | 1461.4 | 1467.2 | 1403.6 | 1397.7 | 1479.6 | 1435.3 | 1479.1 | 1515.3 | 1471.8 | 1501.1 | 1472.5 | 1482.9 | 1511.6 | 1505.3 | 1500.8 | 1377.1 | 1406.9 | 1484 | 1486.8 | 1491.7 | 1500.8 | 1523.1 | 1509.3 | 1469.4 | 1481 | 1407.8 | 1431.8 | 1495.8 | 1495.8 | 1464.2 | 1501.2 | 1465.4 | 1482.4 | 1469.9 | 1476.9 | 1474.3 | 1493 | 1467.5 | 1485.9 | 1417.4 | 1440.7 | 1529.4 | 1416.2 | 1421.1 | 1423.4 | 1441.3 | 1455.9 | 1450.2 | 1460.5 | 1461.4 | 1414.2 | 1554.4 | 1390.4 | 1290.4 | 1470.2 | 1381.3 | 1457.7 | 1475.5 | 1458.9 | 1493.1 | 1427.5 | 1473.7 | 1446.8 | 1462.1 | 1470.2 | 1440 | 1531 | 1486.7 | 1402.8 | 1272.3 | 1274 | 1278.9 | 1279.6 | 1280 | 1285.2 | 1293.3 | 1310.2 | 1312.7 | 1307.2 | 1280.1 | 1288.3 | 1308.2 | 1225.6 | 1122.2 | 1337.7 | 1314.9 | 1306.1 | 1321.8 | 1319.8 | 1306.1 | 1327 | 1298 | 1328.7 | 1292.4 | 1335.1 | 1322.7 | 1278 | 1264.3 | 1264.3 | 1264.5 | 1427.2 | 1386.7 | 1237.5 | 1420.6 | 1433.8 | 1441.8 | 1478 | 1432.3 | 1564.8 | 1422.3 | 1355.5 | 1348.7 | 1290.8 | 1420.8 | 1405 | 1468 | 1263.1 | 1288.4 | 1404 | 1210.4 | 1134.1 | 1464.7 | 1463.3 | 1496.6 | 1469.1 | 1463.8 | 1459.8 | 1579.4 | 1587.3 | 1419.1 | 1413.1 | 1303.7 | 1307.5 | 1304.7 | 1359.4 | 1316.7 | 1351.3 | 1316.7 | 1297.8 | 1300.7 | 1306.4 | 1345.2 | 1340.2 | 1321.9 | 1333 | 1317.4 | 1328 | 1264.8 | 1337.7 | 1292.6 | 1334.9 | 1283.4 | 1335.3 | 1348.5 | 1315.2 | 1325.5 | 1323.2 | 1333.3 | 1328.1 | 1293.3 | 1476.1 | 1507.6 | 1535.2 | 1456.5 | 1497.5 | 1589.3 | 1493.7 | 1520 | 1461.3 | 1521.9 | 1508 | 1444.6 | 1556.4 | 1524 | 1414.5 | 1520 | 1543.9 | 1174.5 | 1174 | 1478.3 | 1244.4 | 1429.1 | 1374.2 | 1366.5 | 1362.7 | 1368.3 | 1316.5 | 1348.5 | 1368.9 | 1347.7 | 1330.5 | 1375.3 | 1417.9 | 1362.9 | 1375.6 | 1313.2 | 1296.6 | 1289.8 | 1355 | 1350 | 1352.6 | 1356.1 | 1344.9 | 1433.7 | 1344 | 1340.9 | 1357.7 | 1348.4 | 1229 | 1356 | 1374.4 | 1307.6 | 1292.3 | 1316.7 | 1478.1 | 1325 | 1392 | 1380.3 | 1375.5 | 1307.8 | 1228 | 1361.2 | 1431.8 | 1316 | 1324.1 | 1399.4 | 1385.4 | 1376.6 | 1373.9 | 1375.3 | 1377.6 | 1454.9 | 1311.7 | 1325.9 | 1327.3 | 1341.3 | 1344 | 1338.3 | 1362.9 | 1396.7 | 1393.9 | 1350 | 1391.6 | 1394.5 | 1395.9 | 1399.9 | 1411.3 | 1383.4 | 1335 | 1335 | 1402.6 | 1261.7 | 1335 | 1347.4 | 1453 | 1385.6 | 1395.1 | 1345.2 | 1462.9 | 1408.7 | 1449.8 | 1320.8 | 1401.3 | 1324.9 | 1330.1 | 1272 | 1342.4 | 1347.5 | 1338.4 | 0 | 43.91 | 0 | 0 | 6.97 | 6.27 | 0 | 0 | 89319280 | 262986 | 90712660 | 308026 | 74569790 | 156029 | 88924300 | 135446 | 845170 | 10160 | 126570 | 700 | 113190 | 129 | 113780 | 116 | 111750 | 112 | 116060 | 162 | 224000 | 0 | 226000 | 0 | 454780 | 450000 | 12.9 | 6.97 | 6.27 |  | 43.91 | 0 | 463613.8
2025-06-09 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:51 | 17:37 | 561.3 | 547.9 | 595 | 592.4 | 592.5 | 576.2 | 600.3 | 580.2 | 596 | 601.4 | 598.5 | 594.4 | 603.8 | 601.7 | 608.5 | 607.5 | 566.7 | 569.8 | 596.1 | 601.8 | 623.3 | 615.5 | 624.5 | 622.3 | 621.2 | 622.9 | 624.4 | 619.5 | 630 | 628.4 | 624.1 | 626.8 | 592.3 | 558.1 | 563.7 | 566.7 | 579 | 577.1 | 600.2 | 572.6 | 593.8 | 641.9 | 675.2 | 640.8 | 638.5 | 661.1 | 709.3 | 700.6 | 755.9 | 673.1 | 638.9 | 631.4 | 628.8 | 660.1 | 653.8 | 650.6 | 671.8 | 622 | 546.6 | 626.9 | 604 | 567 | 619.5 | 1419.3 | 1397.3 | 1391.4 | 1404.8 | 1407.7 | 1400.4 | 1386.2 | 1416 | 1409.7 | 1388.7 | 1356.6 | 1390.4 | 1347.1 | 1330.1 | 1433.3 | 1437.8 | 1436 | 1407.7 | 1498 | 1451 | 1455 | 1432.6 | 1381.4 | 1359.1 | 1397.6 | 1409.9 | 1419.5 | 1415.3 | 1373 | 1410 | 1419.6 | 1429.7 | 1430.3 | 1532.1 | 1430 | 1427.8 | 1350.8 | 1356.6 | 1415 | 1387.7 | 1405.5 | 1490.4 | 1404.1 | 1423.3 | 1405.6 | 1409.4 | 1432.6 | 1423.9 | 1429.6 | 1310.4 | 1344.6 | 1424.7 | 1444.9 | 1433.1 | 1449.6 | 1456.6 | 1460.8 | 1397.5 | 1439.7 | 1369.8 | 1392.6 | 1453.2 | 1440.4 | 1416.7 | 1441.5 | 1366.5 | 1421.4 | 1403.3 | 1400.3 | 1409.7 | 1409.9 | 1398.3 | 1419.8 | 1356.8 | 1372 | 1451.3 | 1335.5 | 1348 | 1343.7 | 1354.6 | 1357.3 | 1356.3 | 1358.5 | 1344.8 | 1310.3 | 1430.2 | 1277.9 | 1186.7 | 1363.2 | 1279.5 | 1361.3 | 1379.2 | 1359.8 | 1395.1 | 1380.8 | 1351 | 1343.8 | 1355.8 | 1306 | 1319.6 | 1462.9 | 1401.9 | 1292.4 | 1245 | 1259.3 | 1250.7 | 1244.4 | 1241.5 | 1244.4 | 1240.4 | 1254.4 | 1250.4 | 1248.3 | 1257.9 | 1261.3 | 1260.7 | 1071.5 | 1077.9 | 1256.7 | 1254.9 | 1242.4 | 1256.2 | 1224.8 | 1229.8 | 1243.8 | 1220.9 | 1240.5 | 1205.5 | 1237.8 | 1217.1 | 1228.9 | 1172.1 | 1164.7 | 1181.9 | 1338.4 | 1313.8 | 1188.4 | 1369.5 | 1377.7 | 1390.4 | 1429.8 | 1392.2 | 1533 | 1405.3 | 1315.9 | 1342.9 | 1004.8 | 1377.4 | 1348 | 1436.6 | 1201.8 | 1210 | 1339.8 | 1148.9 | 1083.3 | 1416.4 | 1371.2 | 1426.4 | 1398.2 | 1392 | 1395 | 1502.7 | 1469.7 | 1292.2 | 1289.9 | 1186.6 | 1200.3 | 1184.6 | 1236.1 | 1193.9 | 1224.4 | 1214.3 | 1196.7 | 1190.3 | 1180.5 | 1212.7 | 1213.5 | 1197 | 1217.3 | 1213.4 | 1222 | 1195.7 | 1247.4 | 1195.5 | 1244.6 | 1186.8 | 1244.1 | 1229.3 | 1212.3 | 1227.6 | 1240.8 | 1215.4 | 1226.1 | 1203.8 | 1347.4 | 1414.7 | 1435.3 | 1358.1 | 1427.4 | 1493.4 | 1406.9 | 1422.6 | 1378.2 | 1443.5 | 1433.9 | 1367.4 | 1467.5 | 1424 | 1314.4 | 1423.6 | 1430.5 | 1078.1 | 1087.6 | 1391.3 | 1159.7 | 1351.4 | 1311.5 | 1304 | 1296.2 | 1312.2 | 1251.5 | 1288.8 | 1290.7 | 1265.8 | 1244.2 | 1295 | 1382.8 | 1289.4 | 1292.4 | 1229.9 | 1233.7 | 1230.5 | 1293.7 | 1295.3 | 1293.6 | 1299.1 | 1294.2 | 1333.7 | 1285.9 | 1286.3 | 1292.8 | 1284.7 | 1170.6 | 1291.9 | 1294.9 | 1235.5 | 1225.5 | 1254.1 | 1375.2 | 1243.8 | 1297.6 | 1288.5 | 1280.5 | 1224 | 1152.9 | 1228.5 | 1348.5 | 1224.8 | 1234.9 | 1300.2 | 1292.1 | 1277.7 | 1278.7 | 1282.2 | 1287.8 | 1359.8 | 1220.4 | 1247.6 | 1245.3 | 1265.2 | 1269 | 1263.6 | 1353.8 | 1379.1 | 1370.2 | 1318.3 | 1353.9 | 1352.5 | 1346.4 | 1340.4 | 1345.6 | 1315.5 | 1264.8 | 1270 | 1324.9 | 1188.7 | 1266.6 | 1280.3 | 1423.6 | 1367 | 1365.8 | 1312.2 | 1421.4 | 1373.3 | 1414.6 | 1288 | 1362.9 | 1287.2 | 1287.9 | 1224.8 | 1295.6 | 1290.7 | 1272.8 | 0 | 43.69 | 0 | 0 | 6.68 | 5.96 | 0 | 0 | 89427640 | 263114 | 90820480 | 308130 | 74674200 | 156151 | 89034700 | 135570 | 846250 | 10170 | 127640 | 710 | 108360 | 128 | 107820 | 104 | 104410 | 122 | 110400 | 124 | 216000 | 2000 | 214000 | 2000 | 430990 | 430000 | 12.7667 | 6.68 | 5.96 |  | 43.69 | 0 | 439500.2
2025-06-10 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:55 | 17:09 | 574.8 | 559.4 | 614.6 | 610.9 | 608.6 | 588.9 | 625.9 | 603.3 | 615.8 | 621 | 624.3 | 618.6 | 619.8 | 621.3 | 626.2 | 623.4 | 586.9 | 589.3 | 619.9 | 623.2 | 645.6 | 634.6 | 640.4 | 637.9 | 640.1 | 639.2 | 638 | 626.9 | 645.9 | 642.6 | 636.4 | 635.8 | 606 | 570.1 | 575.9 | 579.5 | 591.3 | 588.8 | 612.1 | 582.9 | 604.2 | 655.7 | 692.5 | 653.4 | 650.2 | 675 | 721.5 | 712.9 | 766.5 | 678.5 | 650.3 | 643.1 | 640.4 | 667.3 | 657.2 | 652.3 | 684.3 | 629.1 | 555.5 | 632.6 | 613.4 | 573.2 | 630.1 | 1474.6 | 1458.9 | 1460.1 | 1474.4 | 1463.7 | 1459.5 | 1439.6 | 1480.9 | 1469.5 | 1447.6 | 1409 | 1444.2 | 1393.9 | 1373.4 | 1463.3 | 1464.2 | 1473.2 | 1436.5 | 1523.6 | 1491 | 1421.6 | 1467.8 | 1433.2 | 1402.9 | 1446.5 | 1444 | 1470.1 | 1467.2 | 1421.2 | 1456.8 | 1468 | 1484.5 | 1472.4 | 1566.8 | 1478.8 | 1473.3 | 1412.6 | 1415.7 | 1473.5 | 1438.4 | 1458.6 | 1516.5 | 1469.7 | 1489.4 | 1453.5 | 1467 | 1492.6 | 1489.3 | 1493.5 | 1370 | 1389.4 | 1450.3 | 1448 | 1453.2 | 1453.1 | 1483.2 | 1477.9 | 1451.5 | 1453.1 | 1383.4 | 1405.8 | 1469.1 | 1465.5 | 1436.5 | 1467.6 | 1431.2 | 1439.6 | 1430.7 | 1437.2 | 1435 | 1448.8 | 1430.3 | 1456.2 | 1400.4 | 1429.5 | 1518.1 | 1409.7 | 1424.1 | 1427 | 1421.9 | 1433 | 1430.1 | 1438.4 | 1401.1 | 1395.3 | 1516.7 | 1360.1 | 1252.7 | 1430.6 | 1338.1 | 1408.2 | 1421.9 | 1414.2 | 1443.9 | 1430.4 | 1399.1 | 1421.8 | 1417.7 | 1425.4 | 1400.3 | 1494.1 | 1442.4 | 1347.1 | 1268.8 | 1291.5 | 1283.7 | 1279.6 | 1279 | 1281.4 | 1286.9 | 1306.6 | 1304.1 | 1296.2 | 1295.4 | 1297.9 | 1303.5 | 1226 | 1115.6 | 1309.2 | 1300.9 | 1286.8 | 1302.7 | 1303.2 | 1282.6 | 1306.4 | 1278.1 | 1297.6 | 1270.3 | 1301.1 | 1291.3 | 1303.7 | 1234.6 | 1227.7 | 1243.8 | 1398.1 | 1367.1 | 1232.8 | 1425.2 | 1436.1 | 1448.6 | 1480.7 | 1443.1 | 1578.7 | 1436.6 | 1336.9 | 1360.1 | 1027 | 1400.6 | 1368 | 1469 | 1234.2 | 1246.9 | 1372.4 | 1193.5 | 1131 | 1455.1 | 1417.1 | 1481 | 1447.7 | 1421.7 | 1434.3 | 1566.4 | 1534 | 1324.6 | 1330 | 1232.2 | 1249.3 | 1239.6 | 1296.8 | 1259.1 | 1293.3 | 1253.9 | 1249 | 1249.8 | 1247 | 1300.4 | 1291.3 | 1286.1 | 1288.3 | 1249.8 | 1290 | 1228.8 | 1279.3 | 1228.2 | 1269.7 | 1228.6 | 1275 | 1306.4 | 1280 | 1284.9 | 1277.7 | 1292 | 1292.6 | 1261.3 | 1360.8 | 1428.4 | 1457.8 | 1375.4 | 1446.9 | 1513.5 | 1408.8 | 1422.9 | 1416.6 | 1481.1 | 1460.2 | 1402.8 | 1499.8 | 1457.4 | 1350.8 | 1450.5 | 1480.7 | 1129 | 1136.1 | 1429.6 | 1204.8 | 1392.1 | 1334.1 | 1327.4 | 1328.4 | 1333.2 | 1285.7 | 1316.1 | 1332.8 | 1308.7 | 1302.5 | 1341 | 1410.7 | 1335.1 | 1331.6 | 1264.6 | 1264.8 | 1262.2 | 1326.6 | 1322.5 | 1323.1 | 1312.9 | 1315.6 | 1410 | 1313.4 | 1317.4 | 1320.7 | 1316.2 | 1202.9 | 1328.3 | 1330.2 | 1268.1 | 1256.8 | 1220 | 1416.9 | 1279.8 | 1342.5 | 1336.6 | 1326.1 | 1251.6 | 1174.3 | 1314.2 | 1364.9 | 1265.9 | 1264.5 | 1350.5 | 1337.2 | 1323.8 | 1310.9 | 1321.8 | 1315 | 1393.1 | 1249 | 1241.9 | 1247.7 | 1259.3 | 1260 | 1260.7 | 1297.6 | 1327.5 | 1331.7 | 1270.2 | 1320.2 | 1301.4 | 1311.4 | 1297.4 | 1323.2 | 1231 | 1253.8 | 1260 | 1331.2 | 1193.1 | 1257.9 | 1274.5 | 1395.1 | 1328.2 | 1334 | 1288.6 | 1399.2 | 1351.5 | 1383.7 | 1251.9 | 1336.6 | 1259.4 | 1265.5 | 1206.5 | 1268.7 | 1272.2 | 1259.2 | 0 | 45.65 | 0 | 0 | 6.81 | 6.17 | 0 | 0 | 89539340 | 263229 | 90932290 | 308185 | 74782560 | 156308 | 89145700 | 135786 | 847360 | 10170 | 128730 | 710 | 111700 | 115 | 111810 | 55 | 108360 | 157 | 111000 | 216 | 222000 | 0 | 218000 | 0 | 442870 | 440000 | 12.2333 | 6.81 | 6.17 |  | 45.65 | 0 | 451487
2025-06-11 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:54 | 17:38 | 628 | 615.6 | 667.9 | 666.4 | 667.1 | 652.1 | 677 | 654.3 | 669.7 | 676.2 | 676.1 | 672.3 | 676.5 | 675.5 | 681.6 | 678.5 | 638.3 | 639.6 | 671.2 | 677.5 | 698.6 | 689.4 | 694.7 | 693.3 | 692.6 | 694.4 | 693.5 | 692.9 | 698.9 | 696.8 | 691.3 | 694.3 | 662 | 625.8 | 632.5 | 634 | 646.7 | 644.3 | 668.4 | 636.7 | 660.6 | 715 | 752.4 | 714.1 | 708.7 | 734 | 788.6 | 778.8 | 835.2 | 740.8 | 708.2 | 699.2 | 696.2 | 727.3 | 717.2 | 725.4 | 741.7 | 686.4 | 604 | 691.3 | 669.2 | 624.4 | 687.7 | 1577.9 | 1561.2 | 1568 | 1582 | 1566.8 | 1576.6 | 1542.1 | 1595.6 | 1565.1 | 1541.2 | 1501.5 | 1545.2 | 1509.1 | 1489.2 | 1574.5 | 1570.8 | 1584.9 | 1537.8 | 1626.3 | 1600.4 | 1521.8 | 1557.8 | 1526.5 | 1496.2 | 1537.7 | 1582.8 | 1582.4 | 1579.5 | 1515.9 | 1556.4 | 1572.8 | 1588.7 | 1562.6 | 1659.1 | 1580.6 | 1566.9 | 1509.1 | 1513.5 | 1572.8 | 1541.2 | 1553.3 | 1616.7 | 1562 | 1599.6 | 1560.4 | 1578.4 | 1603.9 | 1598.7 | 1596.7 | 1472.8 | 1596.7 | 1562.2 | 1554.4 | 1557.4 | 1582.1 | 1603.2 | 1602.3 | 1582 | 1573 | 1498.6 | 1525.2 | 1600.5 | 1597.6 | 1566 | 1600.4 | 1577.8 | 1571.9 | 1560.9 | 1580.3 | 1552.1 | 1580.7 | 1554.8 | 1578 | 1535.7 | 1568.8 | 1654.8 | 1554.9 | 1572.8 | 1547.9 | 1560.8 | 1585 | 1571.9 | 1594.1 | 1569 | 1536.7 | 1663.8 | 1497.1 | 1382.6 | 1565.1 | 1466.9 | 1531.3 | 1551.9 | 1558.9 | 1592.9 | 1570.2 | 1549.4 | 1564.6 | 1556.1 | 1505.6 | 1541.7 | 1611 | 1565.3 | 1503.7 | 1430.6 | 1449.9 | 1445.4 | 1443.3 | 1439.2 | 1445.3 | 1448.8 | 1462.9 | 1464.2 | 1454.3 | 1450.5 | 1454.2 | 1462.8 | 1374.2 | 1247.9 | 1461.8 | 1460.7 | 1446.3 | 1464.5 | 1461.4 | 1446.2 | 1459.6 | 1426.2 | 1448.4 | 1412.8 | 1447.1 | 1425.6 | 1445.4 | 1369.3 | 1362.7 | 1386.5 | 1549.3 | 1529 | 1373.1 | 1567.6 | 1581.8 | 1609 | 1628.2 | 1586.2 | 1759 | 1582.6 | 1474.7 | 1525.3 | 1105.9 | 1566 | 1520.3 | 1630.5 | 1381.4 | 1402.1 | 1499.4 | 1333.2 | 1256.1 | 1532.6 | 1604 | 1643.8 | 1598 | 1568.7 | 1602 | 1705.3 | 1656.1 | 1502.6 | 1477 | 1382.5 | 1388.1 | 1382.1 | 1451.7 | 1391.7 | 1434.7 | 1397.3 | 1381.2 | 1386.4 | 1363.3 | 1428.3 | 1428.3 | 1408.7 | 1426.1 | 1396 | 1410.2 | 1374.4 | 1441 | 1374.4 | 1438.1 | 1370.6 | 1436.9 | 1439.6 | 1419 | 1429.8 | 1435.2 | 1420.5 | 1435.4 | 1358 | 1489.7 | 1564.6 | 1599.3 | 1516.4 | 1576.6 | 1640.2 | 1562.3 | 1584.2 | 1541 | 1616.8 | 1582.5 | 1533.3 | 1629.7 | 1581.9 | 1494.5 | 1574.1 | 1638.8 | 1253.5 | 1256.5 | 1560 | 1330.6 | 1521.9 | 1438.3 | 1434.3 | 1432.3 | 1435.5 | 1383.8 | 1410.1 | 1441.6 | 1419.5 | 1402.1 | 1452.3 | 1509.3 | 1442.1 | 1452.5 | 1378.1 | 1357.7 | 1362.2 | 1430.4 | 1434.3 | 1427.6 | 1427.9 | 1432.5 | 1506.2 | 1430.4 | 1428 | 1443.4 | 1434.1 | 1299 | 1441.1 | 1451.5 | 1381.1 | 1368.8 | 1386.4 | 1536.7 | 1379.6 | 1455.9 | 1448.9 | 1443.5 | 1367.8 | 1285.1 | 1439.3 | 1496.7 | 1371.3 | 1366.9 | 1463.6 | 1437.3 | 1433.7 | 1429.4 | 1434.5 | 1422.9 | 1520.6 | 1370.3 | 1372.1 | 1372.4 | 1392.2 | 1389 | 1374.7 | 1421.3 | 1466.9 | 1455.8 | 1413 | 1450.6 | 1457.8 | 1456.8 | 1456.9 | 1467.8 | 1421.1 | 1388.9 | 1390 | 1464.2 | 1309.8 | 1386.9 | 1400.7 | 1511.7 | 1450.2 | 1457.8 | 1397 | 1528.2 | 1469.8 | 1510.7 | 1370.5 | 1462.2 | 1375.9 | 1386.1 | 1325 | 1385.5 | 1395.6 | 1371.1 | 0 | 44.68 | 0 | 0 | 7.41 | 6.62 | 0 | 0 | 89659450 | 263365 | 91055370 | 308287 | 74902160 | 156553 | 89267160 | 136044 | 848570 | 10180 | 129930 | 720 | 120110 | 136 | 123080 | 102 | 119600 | 245 | 121460 | 258 | 242000 | 2000 | 240000 | 2000 | 484250 | 482000 | 12.7333 | 7.41 | 6.62 |  | 44.68 | 0 | 493931.8
2025-06-12 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:41 | 17:33 | 588.4 | 575 | 629.7 | 624.3 | 624.7 | 608.3 | 641.7 | 618.1 | 631.1 | 636.2 | 642.2 | 636.3 | 635.5 | 637 | 642.8 | 642.4 | 602.9 | 605.3 | 640 | 643.2 | 669.6 | 657.3 | 662.6 | 658.7 | 664.5 | 664.4 | 661.4 | 659.2 | 671.5 | 667.4 | 660.3 | 660.2 | 617.5 | 585.8 | 592.3 | 593.6 | 607.2 | 607.4 | 625.1 | 598.1 | 617.8 | 668.5 | 703.8 | 665.9 | 659.6 | 684.4 | 734.1 | 726.6 | 788.7 | 701.3 | 665.9 | 657.3 | 653.3 | 686.6 | 680.6 | 689.2 | 706.5 | 652.2 | 575.7 | 656.4 | 639.4 | 594.7 | 644.4 | 1514.8 | 1489.4 | 1485.1 | 1497.3 | 1495.4 | 1489.4 | 1483.9 | 1519.3 | 1501.3 | 1483.7 | 1443.1 | 1481.9 | 1431.3 | 1409.7 | 1531.1 | 1530.2 | 1530.9 | 1489.4 | 1582.5 | 1545.4 | 1468 | 1518.1 | 1463 | 1445.8 | 1476.1 | 1502.3 | 1518.7 | 1516.2 | 1460.9 | 1504 | 1512.4 | 1532.4 | 1518.6 | 1622.3 | 1521.5 | 1471.5 | 1455.8 | 1460.4 | 1507.1 | 1476.9 | 1498.9 | 1558.9 | 1509.7 | 1527 | 1495.3 | 1508 | 1527.6 | 1519.5 | 1528.1 | 1398.8 | 1422 | 1508.2 | 1515 | 1518.1 | 1535.3 | 1530.8 | 1551.5 | 1521.8 | 1502.3 | 1434.7 | 1468.3 | 1513.1 | 1496.2 | 1479.5 | 1502 | 1494.7 | 1479.2 | 1461 | 1471.7 | 1463 | 1475.3 | 1453.5 | 1478.7 | 1391.6 | 1468.5 | 1565.5 | 1455.3 | 1466.1 | 1453.1 | 1470.5 | 1489.2 | 1475 | 1497.3 | 1470 | 1444.9 | 1564 | 1404.8 | 1296.3 | 1483.6 | 1377.6 | 1448.6 | 1453.3 | 1409.1 | 1475.8 | 1450.4 | 1421.5 | 1459.7 | 1456.9 | 1469.1 | 1445.6 | 1520.2 | 1469.8 | 1409.1 | 1322.4 | 1336.5 | 1328.2 | 1318.9 | 1309.8 | 1312.5 | 1319.3 | 1339.6 | 1342.1 | 1331.3 | 1337.3 | 1338.6 | 1339 | 1264.8 | 1154.3 | 1364.7 | 1343.7 | 1349.2 | 1348.1 | 1345.5 | 1350.4 | 1355.8 | 1329.9 | 1351.5 | 1318.7 | 1352.7 | 1337.6 | 1353.9 | 1283.7 | 1278.7 | 1295.5 | 1450.9 | 1418.5 | 1271.2 | 1461.4 | 1442.2 | 1483.8 | 1518.7 | 1481.6 | 1625.5 | 1479.2 | 1380.4 | 1411.5 | 985.3 | 1420.1 | 1415 | 1533.4 | 1282.9 | 1307.3 | 1434.6 | 1237.5 | 1161.1 | 1498.5 | 1490.9 | 1515.4 | 1485.1 | 1447.9 | 1445.5 | 1592.4 | 1548.9 | 1399.4 | 1389.5 | 1290.4 | 1299.3 | 1299.6 | 1359.2 | 1312.7 | 1344.6 | 1306.7 | 1296.8 | 1300.5 | 1239.6 | 1347.2 | 1331.3 | 1332.4 | 1338.5 | 1303.1 | 1300 | 1280.7 | 1334.9 | 1284.9 | 1332.4 | 1287.4 | 1346.5 | 1344.7 | 1323.3 | 1352.7 | 1351.1 | 1342.2 | 1338.5 | 1309.9 | 1470.2 | 1503.8 | 1535.2 | 1453 | 1516.7 | 1580.4 | 1457 | 1488.6 | 1459.6 | 1524.6 | 1505 | 1442.6 | 1551.5 | 1520.9 | 1421.8 | 1509.1 | 1544.4 | 1168.5 | 1171.1 | 1471.8 | 1244.7 | 1430.1 | 1389.7 | 1384 | 1382.5 | 1385.7 | 1329.9 | 1364.3 | 1386.5 | 1361.2 | 1351.9 | 1394 | 1468.4 | 1384.8 | 1389.2 | 1323.9 | 1316.4 | 1317 | 1384.5 | 1388.8 | 1388.9 | 1390.3 | 1385.1 | 1427.2 | 1376.4 | 1378.5 | 1372.3 | 1368 | 1255.8 | 1379.4 | 1385.7 | 1318.6 | 1301.2 | 1342.4 | 1487.8 | 1330.8 | 1393 | 1387.9 | 1381.2 | 1312.6 | 1230.5 | 1379.5 | 1438.3 | 1314.5 | 1320.8 | 1405.4 | 1390.6 | 1381.4 | 1379.8 | 1385.6 | 1326.4 | 1455.5 | 1315.2 | 1331.6 | 1346 | 1363.4 | 1365 | 1363 | 1394.7 | 1432.9 | 1423.1 | 1383 | 1426.1 | 1426.1 | 1422.5 | 1421.3 | 1435.1 | 1399.3 | 1351.7 | 1355 | 1426.5 | 1278.1 | 1355.2 | 1369.6 | 1476 | 1415.8 | 1424.6 | 1369.2 | 1492.9 | 1438.4 | 1471.8 | 1345.2 | 1430.1 | 1350.4 | 1359.9 | 1297.6 | 1356.1 | 1365.7 | 1342.6 | 0 | 46.25 | 0 | 0 | 7.12 | 6.41 | 0 | 0 | 89774240 | 263470.7 | 91170620 | 308339 | 75014250 | 156742 | 89384590 | 136229 | 849710 | 10180 | 131070 | 720 | 114790 | 105.7 | 115250 | 52 | 112090 | 189 | 117430 | 185 | 228000 | 0 | 228000 | 0 | 459560 | 456000 | 12.8667 | 7.12 | 6.41 |  | 46.25 | 0 | 468705.6
2025-06-13 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:43 | 17:44 | 542.9 | 532 | 579.4 | 577.4 | 580 | 565.1 | 589.8 | 570.8 | 586.1 | 590.1 | 588.6 | 585.6 | 585.8 | 591.4 | 593.4 | 595.5 | 557.4 | 563.1 | 587.6 | 593.9 | 611.4 | 602.7 | 611 | 609.8 | 601.6 | 602 | 605 | 605.8 | 603.8 | 600.2 | 597.4 | 602 | 571.5 | 542.9 | 548.9 | 546.8 | 558 | 559.9 | 576.8 | 551.9 | 573 | 621.5 | 656.5 | 617.2 | 617.7 | 636.8 | 687.7 | 678.3 | 732.4 | 651.9 | 601.6 | 611.2 | 608.9 | 635.9 | 627.7 | 638.5 | 655.5 | 604.4 | 530.5 | 606.4 | 581.5 | 545.9 | 597.8 | 1385.4 | 1364.6 | 1357.9 | 1371.4 | 1376 | 1367.7 | 1360.9 | 1388.1 | 1372.1 | 1355.7 | 1322.7 | 1352 | 1315.8 | 1295.9 | 1353.2 | 1374 | 1367.1 | 1332.9 | 1421 | 1386.5 | 1319.6 | 1371.5 | 1329.2 | 1311.7 | 1345.8 | 1371.3 | 1370.3 | 1377.9 | 1318.1 | 1340.6 | 1356.8 | 1361.5 | 1385 | 1472.2 | 1374.1 | 1368.6 | 1291.8 | 1313.9 | 1363.6 | 1338.5 | 1349.9 | 1446.6 | 1349.7 | 1372.3 | 1374.4 | 1360.9 | 1399.7 | 1383.5 | 1329 | 1262.4 | 1294.8 | 1348.9 | 1369.3 | 1362.1 | 1377.7 | 1382.3 | 1382.1 | 1374.3 | 1377.9 | 1311.2 | 1327.2 | 1401.5 | 1397.8 | 1339.4 | 1407.4 | 1378.1 | 1378.8 | 1378.8 | 1382.7 | 1388.1 | 1392.9 | 1367.2 | 1372.8 | 1325.6 | 1371.5 | 1451.5 | 1353.3 | 1357.9 | 1356 | 1370.7 | 1380.7 | 1364 | 1385.3 | 1376 | 1351.1 | 1459.4 | 1321.6 | 1213.7 | 1369 | 1289.4 | 1356.7 | 1355.9 | 1360.5 | 1374.2 | 1363.5 | 1323.7 | 1373.2 | 1363.6 | 1383.3 | 1360.9 | 1406.6 | 1365.3 | 1325.1 | 1154.5 | 1183.1 | 1202.9 | 1214.5 | 1216.2 | 1225.5 | 1235.4 | 1257.2 | 1265.2 | 1244.9 | 1175.7 | 1195.8 | 1234.2 | 1137.7 | 1037.7 | 1226.1 | 1226.7 | 1214.6 | 1229.6 | 1273.3 | 1251.3 | 1278.2 | 1202.9 | 1249.3 | 1199.1 | 1244.7 | 1254.8 | 1270 | 1193.2 | 1194 | 1219 | 1330.4 | 1282.6 | 1141.5 | 1296.9 | 1302.7 | 1314.1 | 1352.9 | 1305.7 | 1428.5 | 1297.6 | 1211.2 | 1232.1 | 1176.4 | 1281.2 | 1278 | 1396.9 | 1179.9 | 1182.5 | 1292.5 | 1117.7 | 1041.4 | 1262.8 | 1317.3 | 1361.3 | 1328.3 | 1312.1 | 1260.9 | 1444.4 | 1440 | 1339.8 | 1337.9 | 1236.9 | 1247 | 1225 | 1289.7 | 1237.5 | 1276.8 | 1238.4 | 1225.3 | 1234.3 | 1216.8 | 1278 | 1268.7 | 1264.5 | 1257.3 | 1226.4 | 1228 | 1204.9 | 1253.9 | 1202.4 | 1245.2 | 1199.3 | 1245.7 | 1264.7 | 1231.9 | 1252 | 1227.9 | 1251.6 | 1237.1 | 1198.5 | 1295.3 | 1364 | 1393.8 | 1316.4 | 1385.5 | 1450.2 | 1378.1 | 1383.7 | 1349 | 1420.7 | 1403.1 | 1350.7 | 1442.2 | 1402.8 | 1312.8 | 1408 | 1435.6 | 1094.8 | 1093.2 | 1364.4 | 1158.9 | 1332.7 | 1266 | 1264 | 1260.3 | 1275.3 | 1220.4 | 1258.1 | 1260.1 | 1238 | 1231.7 | 1269.7 | 1341.4 | 1259.2 | 1263 | 1204.6 | 1210.1 | 1201.7 | 1265.8 | 1261.1 | 1260.8 | 1259.8 | 1254 | 1367.2 | 1259.3 | 1255 | 1266.2 | 1258.3 | 1137.7 | 1261.3 | 1263.1 | 1206.7 | 1198.1 | 1210.2 | 1356.9 | 1201.8 | 1263 | 1255 | 1249.5 | 1188.3 | 1112.8 | 1251.5 | 1296.5 | 1199 | 1207.5 | 1280.1 | 1270.2 | 1252.5 | 1248 | 1254.2 | 1205 | 1322 | 1193.2 | 1197.6 | 1208.1 | 1227.3 | 1230 | 1232.1 | 1305 | 1339.4 | 1333.5 | 1287.7 | 1324.2 | 1324.7 | 1313.4 | 1309.8 | 1313.1 | 1276 | 1236 | 1240 | 1295.8 | 1164.7 | 1238.5 | 1252.8 | 1383.6 | 1324.2 | 1326.2 | 1274.9 | 1382.8 | 1331.5 | 1371.7 | 1248.2 | 1318.7 | 1249.4 | 1254.9 | 1194.7 | 1254.1 | 1255.8 | 1230.9 | 0 | 45.83 | 0 | 0 | 6.56 | 5.85 | 0 | 0 | 89879010 | 263571 | 91277290 | 308381 | 75117720 | 156954 | 89492100 | 136473 | 850760 | 10180 | 132120 | 730 | 104770 | 100.3 | 106670 | 42 | 103470 | 212 | 107510 | 244 | 210000 | 0 | 210000 | 2000 | 422420 | 420000 | 13.0167 | 6.56 | 5.85 |  | 45.83 | 0 | 430540.7999
2025-06-14 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 5:31 | 17:47 | 436.1 | 428.4 | 464.2 | 464.9 | 461.6 | 446.2 | 471.2 | 455.7 | 466.1 | 468.3 | 469.4 | 466 | 467.6 | 467.1 | 470.7 | 469.4 | 441.3 | 445.7 | 467.5 | 471.4 | 484.7 | 480.2 | 481.3 | 481.3 | 481.5 | 482 | 482.5 | 481.9 | 486.4 | 485.3 | 481.1 | 482.9 | 457.5 | 431.5 | 436 | 438.8 | 446.6 | 445.4 | 461.6 | 441.8 | 458.7 | 495.5 | 520.8 | 492.2 | 492.4 | 510.1 | 547.9 | 541.7 | 580.6 | 516.3 | 473.8 | 484.7 | 482.9 | 505.5 | 497.9 | 504.4 | 521.5 | 480.4 | 422.9 | 481.2 | 463.4 | 434.9 | 477.3 | 1100.3 | 1090.7 | 1092.3 | 1098.2 | 1103.2 | 1098.9 | 1081.3 | 1031.6 | 1102.9 | 1087.8 | 1065.6 | 1086.7 | 1047.7 | 1031.6 | 1089.8 | 1094.8 | 1099 | 1081 | 1144.3 | 1108 | 1058.1 | 1103.4 | 1058.8 | 1048.3 | 1087.6 | 1100.3 | 1096.4 | 1100.1 | 1067.6 | 1094.2 | 1095.9 | 1106.1 | 1105.4 | 1193.3 | 1097.6 | 1099.3 | 1048.1 | 1049.9 | 1103.7 | 1071.7 | 1105.1 | 1157.7 | 1100.4 | 1116.4 | 1098.9 | 1105.1 | 1122.8 | 1116.5 | 1122.5 | 1021.8 | 1047 | 1087.7 | 1102.2 | 1096.6 | 1104.5 | 1111.1 | 1107.5 | 1100.1 | 1095.6 | 1037.7 | 1053.6 | 1106 | 1104.6 | 1078.9 | 1103.2 | 1087.1 | 1087.1 | 1078.3 | 1086.3 | 1087.1 | 1097.3 | 1081.6 | 1099.2 | 1060.8 | 1095 | 1167.3 | 1076 | 1082.9 | 1077.5 | 1084.5 | 1090.6 | 1086.1 | 1101.4 | 1060 | 1052.3 | 1143.1 | 1091 | 951.9 | 1091 | 1016.2 | 1080.4 | 1088.6 | 1091.2 | 1097.3 | 1061.4 | 1084.3 | 1037.7 | 1082.5 | 1085.8 | 1086.3 | 1142.7 | 1105.9 | 1042.5 | 959.3 | 977.8 | 971.6 | 936 | 973.9 | 976.4 | 976.6 | 986.6 | 992.2 | 981.1 | 979.3 | 985 | 992.4 | 933.3 | 846.5 | 996.6 | 990.2 | 987.6 | 973.6 | 987.2 | 985.9 | 987.4 | 970.4 | 979.2 | 959 | 977.1 | 973 | 983.2 | 930.5 | 927.5 | 941.1 | 1065.8 | 1043.3 | 935.5 | 1080 | 1086.6 | 1092.8 | 1127.5 | 1094.8 | 1202.2 | 1099 | 1023.8 | 1038.7 | 986.9 | 1064.3 | 1045 | 1130.6 | 945.4 | 956.1 | 1055.3 | 909.1 | 853.8 | 1109.8 | 1100.4 | 1122.8 | 1099.8 | 1084.6 | 1087.5 | 1190.1 | 1166.7 | 1016.6 | 1014.5 | 940.2 | 941.7 | 943.2 | 982.5 | 953.1 | 976.4 | 946.9 | 936.6 | 939.2 | 938.6 | 954.2 | 979.4 | 949.6 | 975.7 | 944.3 | 951 | 931.4 | 972.4 | 933.8 | 974.1 | 930.5 | 974.1 | 974.1 | 959.2 | 962 | 971 | 964.7 | 972.1 | 963.2 | 1045.5 | 1068.6 | 1091.2 | 1036 | 1094 | 1144.6 | 1084.2 | 1092.9 | 1056.8 | 1106.8 | 1096.5 | 1054.6 | 1141.2 | 1109.4 | 1022.8 | 1117.8 | 1124 | 857.7 | 857.8 | 1084.4 | 910.8 | 1047.4 | 978 | 976.1 | 973.2 | 977.2 | 954.2 | 964.9 | 978.5 | 964.7 | 955.3 | 985.5 | 1061.9 | 976.2 | 981.8 | 935.6 | 929.9 | 929 | 974.6 | 978.3 | 979.3 | 982.5 | 978 | 1062.5 | 976 | 971.8 | 984.3 | 976.9 | 885.3 | 979.1 | 983.4 | 938.7 | 930.9 | 863.6 | 962.7 | 937.8 | 983.5 | 978 | 974.2 | 924.7 | 870.8 | 817.3 | 992 | 923.5 | 907 | 979.3 | 923.6 | 967.3 | 949.8 | 959.7 | 869.6 | 1032.8 | 922.7 | 913.2 | 816.9 | 880.4 | 880 | 826.6 | 963.1 | 985.6 | 979.8 | 951.3 | 974.4 | 979.3 | 980 | 979 | 988 | 969 | 936.1 | 933 | 987.9 | 883 | 935.7 | 947 | 1019.2 | 979.2 | 983.3 | 939.4 | 1032.4 | 987.6 | 1024.3 | 927.5 | 984.9 | 931.6 | 939 | 893.9 | 945.2 | 945.6 | 939.6 | 0 | 38.19 | 0 | 0 | 4.84 | 4.42 | 0 | 0 | 89963230 | 263679 | 91362160 | 308467 | 75200140 | 157174 | 89573680 | 136700.9 | 851600 | 10190 | 132940 | 730 | 84220 | 108 | 84870 | 86 | 82420 | 220 | 81580 | 227.9 | 168000 | 2000 | 164000 | 0 | 333090 | 332000 | 12.2667 | 4.84 | 4.42 |  | 38.19 | 0 | 338811.8
2025-06-15 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:44 | 17:30 | 509.8 | 500.8 | 544.2 | 543 | 538.6 | 518.9 | 552.5 | 532.2 | 541.8 | 547.6 | 551.4 | 545.3 | 548.5 | 545.6 | 551.4 | 549.8 | 516.7 | 521.3 | 549 | 552.5 | 570.8 | 564.1 | 564.6 | 564.4 | 566.7 | 567.5 | 567.7 | 566.5 | 572.1 | 570.6 | 566 | 564.8 | 535.3 | 505.2 | 511.3 | 514.6 | 525 | 520.7 | 540.9 | 517.6 | 538 | 581.3 | 608.5 | 574.3 | 576 | 595.5 | 638.4 | 580.6 | 683.6 | 606.5 | 577.8 | 570.2 | 567.9 | 593.4 | 586.3 | 594.1 | 609 | 564.3 | 496.3 | 565.9 | 546.2 | 511.3 | 557.9 | 1294.4 | 1284.9 | 1281.7 | 1293.8 | 1296.7 | 1289.3 | 1274.5 | 1302.8 | 1295.6 | 1276.4 | 1244.7 | 1274.9 | 1230.6 | 1209.8 | 1278.7 | 1288.1 | 1294.4 | 1271.6 | 1340.5 | 1295.2 | 1244.8 | 1287.7 | 1236.2 | 1230.1 | 1271.6 | 1289.8 | 1286.8 | 1294.1 | 1237.5 | 1276.4 | 1279.8 | 1296 | 1289.7 | 1380.1 | 1279.6 | 1287.8 | 1233.1 | 1224.9 | 1295.4 | 1250.7 | 1292.3 | 1357.5 | 1290 | 1313 | 1289.5 | 1301.4 | 1318.7 | 1313.9 | 1316.4 | 1198.4 | 1225.8 | 1280.9 | 1290.8 | 1287.8 | 1301.1 | 1303.4 | 1307.1 | 1293.3 | 1286.9 | 1218.2 | 1239.9 | 1299.3 | 1296.8 | 1268.2 | 1296.9 | 1278.2 | 1276 | 1265.8 | 1274.8 | 1271.4 | 1287.6 | 1268.1 | 1288.7 | 1242.2 | 1255.4 | 1334.5 | 1212.6 | 1251.4 | 1235.6 | 1246.5 | 1256.3 | 1253 | 1266 | 1234.1 | 1212.5 | 1330.2 | 1191.2 | 1110 | 1263.6 | 1187.6 | 1255.9 | 1270.1 | 1272.9 | 1267.8 | 1271.5 | 1265.5 | 1175.1 | 1260.9 | 1186.8 | 1262.3 | 1328.6 | 1286.2 | 1211.6 | 1125.3 | 1147.6 | 1138.9 | 1083.2 | 1126.6 | 1129.8 | 1130.2 | 1138.8 | 1145.6 | 1131.6 | 1148 | 1151.3 | 1145.4 | 1083.5 | 977.2 | 1142.6 | 1138 | 1131.7 | 1140.8 | 1138 | 1134.4 | 1138.1 | 1114.1 | 1125.4 | 1099.5 | 1125 | 1124.5 | 1134.9 | 1071.4 | 1069.9 | 1084.1 | 1218.3 | 1198.1 | 1078.6 | 1248.2 | 1256.2 | 1267 | 1296.7 | 1270.9 | 1401 | 1275.2 | 1187.1 | 1208.4 | 1153 | 1188.1 | 1168 | 1295.7 | 1087.5 | 1098.5 | 1213.7 | 1046 | 984.4 | 1284.2 | 1278.1 | 1296.7 | 1266.5 | 1236.8 | 1253.8 | 1362.6 | 1331.9 | 1177.4 | 1168.1 | 1082.6 | 1080.3 | 1096 | 1138.2 | 1107.3 | 1132.6 | 1083.4 | 1071.6 | 1077.4 | 1083.5 | 1123.8 | 1125.8 | 1114.9 | 1095.8 | 1080.1 | 1078 | 1069.1 | 1109.9 | 1066.7 | 1114.3 | 1063.8 | 1112.2 | 1113.9 | 1093.5 | 1113.9 | 1115.3 | 1105.7 | 1112.8 | 1106.7 | 1223.6 | 1253.6 | 1285.3 | 1216.7 | 1281.3 | 1331 | 1265 | 1274.8 | 1235.9 | 1297 | 1287.2 | 1239.5 | 1324.1 | 1266.7 | 1188.8 | 1290.1 | 1305.1 | 1002.6 | 1003.5 | 1263.6 | 1065.4 | 1226.2 | 1159.3 | 1160.7 | 1158.6 | 1159.2 | 1119.4 | 1138.8 | 1164.7 | 1142.5 | 1133.1 | 1166.4 | 1228.7 | 1156.9 | 1159.2 | 1104.2 | 1097.6 | 1099.2 | 1153.2 | 1153.3 | 1156.5 | 1161.6 | 1155.3 | 1233.7 | 1148.5 | 1146.8 | 1158.2 | 1148.6 | 1047.3 | 1152.2 | 1156.9 | 1101.6 | 1093.6 | 1115.8 | 1214.1 | 1113.9 | 1166.3 | 1163.1 | 1156.3 | 1092.9 | 1028.8 | 1030.9 | 1186.9 | 1095.9 | 1102 | 1171.8 | 1154.1 | 1141.3 | 1148.4 | 1144.8 | 1122.2 | 1222.7 | 1092.2 | 1092.6 | 1023.4 | 1109.9 | 1108.1 | 1040.8 | 1108.7 | 1142.3 | 1138.5 | 1105 | 1135.2 | 1132.9 | 1138 | 1133.1 | 1149.1 | 1128.8 | 1090.3 | 1094 | 1153.8 | 1034.2 | 1089.2 | 1100.9 | 1190.9 | 1153 | 1152 | 1100.4 | 1216 | 1156.7 | 1201.2 | 1090 | 1093 | 1096.3 | 1094.9 | 1045 | 1111.6 | 1103.5 | 1097 | 0 | 42.6 | 0 | 0 | 5.92 | 5.32 | 0 | 0 | 90061940 | 263801 | 91460700 | 308516 | 75295380 | 157370 | 89670180 | 136922 | 852580 | 10200 | 133890 | 730 | 98710 | 122 | 98540 | 49 | 95240 | 196 | 96500 | 221.1 | 196000 | 2000 | 190000 | 0 | 388990 | 386000 | 12.7667 | 5.92 | 5.32 |  | 42.6 | 0 | 395786
2025-06-16 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 5:16 | 17:25 | 189.1 | 182.2 | 201.9 | 199.8 | 199.8 | 190.2 | 205.6 | 197.2 | 203.5 | 202.8 | 204.5 | 202.9 | 203.5 | 202.6 | 205.6 | 204 | 191.1 | 196.5 | 206.8 | 207 | 214.7 | 212.5 | 212 | 210.6 | 214.2 | 213.8 | 215 | 213.9 | 216.8 | 215.9 | 213.7 | 211.2 | 200 | 187.1 | 188.3 | 190.4 | 193.6 | 191.1 | 200.1 | 192.8 | 197.9 | 216.9 | 228.2 | 213.3 | 215.8 | 224.2 | 242 | 239 | 256.1 | 228.1 | 218 | 213.3 | 213.3 | 223 | 220.9 | 220.9 | 231.7 | 211.4 | 187 | 211.6 | 201.6 | 193.1 | 208.6 | 486.8 | 480 | 482.4 | 481.3 | 488.9 | 482.6 | 479.1 | 487.6 | 491.4 | 480.8 | 475.5 | 480.8 | 460.8 | 451.5 | 479.2 | 483 | 484.2 | 478.8 | 507.5 | 485.9 | 465.4 | 490.1 | 465.2 | 464.1 | 482.5 | 486.3 | 480.8 | 483.3 | 463.8 | 473.4 | 476.7 | 479.7 | 486.2 | 526.2 | 483.6 | 482.4 | 453.1 | 458.6 | 483.8 | 468.8 | 488.8 | 506.8 | 487 | 490.2 | 485.9 | 480 | 494.4 | 492 | 496.7 | 447.6 | 464.8 | 479.7 | 492.5 | 487.7 | 487 | 491 | 485.2 | 484.7 | 485.9 | 457.8 | 463.4 | 490.2 | 489.2 | 476.5 | 489.1 | 479.9 | 481.2 | 477.9 | 481.8 | 485.3 | 488.6 | 480.2 | 487.6 | 471.2 | 490.3 | 527.3 | 464.9 | 479.7 | 486.2 | 487.2 | 484.8 | 481.6 | 490.7 | 487.8 | 468.2 | 509 | 459.2 | 421.5 | 487 | 452.5 | 486.1 | 485.5 | 485 | 486.3 | 486.6 | 486.6 | 467.1 | 482.4 | 484.5 | 486.4 | 513.1 | 495.9 | 463.2 | 423.1 | 435.5 | 425.8 | 409.4 | 430.5 | 429.7 | 430.1 | 438 | 444.4 | 438.9 | 436.1 | 440.8 | 446 | 415.1 | 380.4 | 451.5 | 443.3 | 445.1 | 445.2 | 439.6 | 443.5 | 442.5 | 437 | 438.6 | 428.6 | 434.2 | 437.9 | 439.7 | 413.1 | 413.1 | 425.2 | 475.2 | 462.9 | 418.7 | 482.7 | 486 | 486.2 | 507.2 | 491.4 | 537.3 | 492.4 | 461.7 | 462.1 | 439.7 | 476.5 | 488 | 510.1 | 425.5 | 423 | 471.3 | 404.4 | 378 | 499.5 | 492.1 | 501.8 | 491.9 | 480.6 | 479.4 | 540.7 | 540.1 | 452.5 | 457.1 | 421.4 | 418.8 | 420.8 | 432.8 | 424.8 | 438.8 | 424.3 | 419.2 | 419.6 | 419.7 | 397.2 | 432.8 | 403.3 | 414.2 | 433 | 439 | 427.2 | 440.4 | 420.6 | 432.4 | 418.6 | 436.5 | 439.1 | 430 | 415.2 | 440.3 | 429.1 | 435.4 | 436.6 | 463.7 | 478.6 | 486 | 460.7 | 490.9 | 515.3 | 487.1 | 488.3 | 469.2 | 490.5 | 487.7 | 468.8 | 513.7 | 502 | 454.5 | 507.4 | 499.8 | 380.9 | 390 | 484.1 | 406.2 | 466.3 | 437.6 | 434.1 | 425.6 | 426.1 | 420.4 | 429.6 | 435.2 | 427.9 | 422.4 | 441.3 | 479.7 | 431.4 | 437.5 | 421.9 | 415.5 | 405.3 | 426.6 | 432.3 | 430.9 | 433 | 433.4 | 477.3 | 432.8 | 428.2 | 434.1 | 435.6 | 388.7 | 431.7 | 438 | 416 | 391.2 | 420.9 | 471.5 | 421.7 | 441.5 | 436.4 | 433.4 | 416.1 | 388.9 | 397 | 463.4 | 406.9 | 419.3 | 456.1 | 447.5 | 447.5 | 438.7 | 442.9 | 430.3 | 472.2 | 417.8 | 420.9 | 356.9 | 430 | 433 | 391.6 | 424.9 | 432.1 | 438.4 | 416.2 | 427.7 | 432.6 | 428.2 | 429.2 | 438.5 | 423.6 | 413 | 416 | 438.3 | 387.5 | 409.5 | 420.8 | 452.2 | 415.8 | 424.7 | 410.9 | 452.1 | 427 | 451.4 | 406.8 | 406 | 407 | 417.9 | 391 | 418.1 | 421.3 | 410 | 0 | 30.98 | 0 | 0 | 1.96 | 1.79 | 0 | 0 | 90099140 | 263894 | 91498400 | 308591 | 75331820 | 157449 | 89705580 | 136999 | 852950 | 10200 | 134250 | 740 | 37200 | 93 | 37700 | 75 | 36440 | 79 | 35400 | 77 | 74000 | 0 | 72000 | 2000 | 146740 | 146000 | 12.15 | 1.96 | 1.79 |  | 30.98 | 0 | 150699.8
2025-06-17 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 5:13 | 17:52 | 188.2 | 183.3 | 201.7 | 199.6 | 197.9 | 188 | 205.5 | 196.5 | 201.9 | 200.6 | 204.1 | 201.8 | 201.1 | 199.8 | 203 | 202.5 | 189.7 | 195.3 | 206.1 | 206.1 | 214 | 211.9 | 209.1 | 209.3 | 212.2 | 212.6 | 214.2 | 212.9 | 216.6 | 214.4 | 213 | 210 | 196.2 | 183.6 | 186.1 | 187.6 | 191.2 | 188.6 | 196.5 | 190.7 | 195.9 | 214.3 | 224.6 | 209.8 | 212.1 | 220.2 | 238.2 | 234.4 | 251.9 | 225.7 | 213.7 | 209.4 | 209.1 | 220.6 | 218.3 | 218.6 | 230.6 | 210.3 | 186.1 | 210.7 | 201 | 190.2 | 204.5 | 488.6 | 483.9 | 486.4 | 486.1 | 476.7 | 484.2 | 480.4 | 489.4 | 492.2 | 481.5 | 475.5 | 480.4 | 460.2 | 451 | 480.9 | 484.2 | 485.1 | 479.2 | 510.3 | 488.2 | 467 | 493.1 | 493.1 | 468.7 | 447.6 | 487.3 | 490.6 | 482.8 | 476.9 | 485.9 | 491.2 | 493.4 | 499.6 | 541.5 | 495.8 | 494.6 | 463.1 | 468.1 | 493.9 | 478.6 | 497.9 | 518.7 | 492.5 | 498.1 | 488.5 | 488.1 | 500.2 | 498.3 | 503.1 | 454.1 | 471.9 | 479.1 | 492.3 | 487.1 | 487.5 | 490.4 | 486.1 | 483.9 | 482.4 | 454.6 | 461.7 | 484.7 | 482.5 | 471.3 | 482.4 | 475.1 | 474.5 | 469.1 | 472.4 | 476.3 | 477.6 | 471.1 | 478.8 | 461.3 | 473.3 | 509.2 | 462.9 | 466.2 | 466.6 | 469 | 469.2 | 468.2 | 474.4 | 472.9 | 451.3 | 492.4 | 443.1 | 409.2 | 473.8 | 439.8 | 471.8 | 474 | 472.3 | 475.5 | 473.9 | 473.7 | 465.4 | 468.4 | 467.8 | 470 | 503.3 | 485.3 | 449.1 | 404.3 | 417.8 | 408.7 | 408.1 | 412.6 | 413.2 | 413.7 | 420.8 | 426.8 | 418.8 | 417.2 | 423 | 428.5 | 398.1 | 364.3 | 440.6 | 425.9 | 426.5 | 427.4 | 422.4 | 425.2 | 424 | 423.7 | 421.9 | 416.7 | 421.2 | 421.8 | 423.6 | 397.3 | 397.1 | 407.7 | 456.9 | 443.5 | 404.9 | 463.7 | 465.3 | 464.8 | 485.5 | 470.8 | 515.7 | 472.2 | 442.2 | 442.3 | 421.5 | 455.6 | 451 | 487.9 | 406.6 | 405.5 | 438.4 | 386.6 | 380.1 | 479.7 | 478 | 487.3 | 478.5 | 465.9 | 467 | 521.2 | 522.7 | 439.8 | 443.5 | 408.4 | 404.5 | 407.1 | 420.4 | 410.2 | 424.4 | 410.9 | 404.2 | 405.6 | 403.4 | 402.3 | 419.2 | 408.5 | 402.3 | 416.8 | 416 | 409.4 | 421.4 | 405.7 | 416.8 | 403.6 | 418 | 423.5 | 415.2 | 423.7 | 416.1 | 410.2 | 418.8 | 421.7 | 455.5 | 468.8 | 477.4 | 452.1 | 482.5 | 505.6 | 476.1 | 478.8 | 459.1 | 481.3 | 481.7 | 460.3 | 501.1 | 491.5 | 444.6 | 495.7 | 487.1 | 369.1 | 369.3 | 472.8 | 395 | 456.9 | 435.1 | 434.9 | 425.4 | 428.5 | 420.2 | 428.9 | 432.4 | 425.5 | 420.7 | 436 | 474.2 | 427.6 | 431.1 | 415.6 | 415.7 | 404.8 | 426.4 | 432 | 432.9 | 434 | 432.5 | 458 | 429.2 | 425.5 | 430.5 | 431.3 | 386.7 | 426.6 | 431.7 | 409.5 | 385.9 | 398.9 | 455.8 | 419.7 | 437.7 | 433.6 | 430.5 | 410.2 | 382.1 | 413.8 | 452.6 | 403.7 | 414.9 | 450.5 | 431.3 | 439.7 | 436 | 429.3 | 413.1 | 468.2 | 412.2 | 406.5 | 376.2 | 419 | 418 | 398.5 | 418.9 | 425.8 | 431.4 | 411.6 | 421.3 | 425.5 | 425 | 424.5 | 433.6 | 418.7 | 409.1 | 408 | 433.8 | 383.9 | 407.3 | 415.7 | 444 | 421.5 | 424.3 | 403.9 | 448.8 | 428.2 | 447.4 | 402.5 | 424.7 | 404.8 | 415.9 | 386.8 | 416.3 | 416.6 | 410.6 | 0 | 31.31 | 0 | 0 | 1.94 | 1.83 | 0 | 0 | 90136520 | 264036 | 91535070 | 308660 | 75367060 | 157666 | 89740620 | 137197 | 853310 | 10200 | 134600 | 740 | 37380 | 142 | 36670 | 69 | 35240 | 217 | 35040 | 198 | 72000 | 0 | 70000 | 0 | 144330 | 142000 | 12.65 | 1.94 | 1.83 |  | 31.31 | 0 | 148282.2
2025-06-18 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 5:06 | 17:06 | 479.3 | 472.8 | 515.4 | 515.1 | 515.5 | 495.1 | 528.1 | 509.8 | 519.4 | 525.7 | 529.7 | 524.6 | 525.2 | 525.6 | 530.8 | 530.7 | 498.7 | 506.4 | 530.7 | 534.3 | 552.6 | 546.2 | 547.7 | 547.7 | 550.9 | 550.6 | 550.6 | 550.3 | 563.5 | 559.6 | 554.5 | 554.4 | 508.1 | 482.1 | 489.8 | 491.7 | 503 | 502.7 | 512.9 | 496.5 | 511.4 | 547.2 | 571.1 | 543.9 | 546.2 | 560.3 | 601.1 | 593.6 | 638.9 | 581 | 551.3 | 548.7 | 549.1 | 575.5 | 567.1 | 571.1 | 585.1 | 541.7 | 473 | 545.7 | 536.6 | 501.8 | 532.9 | 1248.1 | 1228.1 | 1244.2 | 1213.6 | 1195.5 | 1190.9 | 1206.2 | 1228.9 | 1201.9 | 1192.3 | 1198.5 | 1180.9 | 1146.6 | 1155.8 | 1282.2 | 1278 | 1294 | 1231.4 | 1314.5 | 1281.2 | 1217.2 | 1258.3 | 1207 | 1194.6 | 1227.2 | 1262.6 | 1256.4 | 1242.2 | 1185 | 1213.6 | 1239.6 | 1250.9 | 1237.2 | 1325.8 | 1260.7 | 1237.4 | 1170 | 1189.2 | 1233.4 | 1215 | 1225.9 | 1302.7 | 1215.9 | 1235.1 | 1188.9 | 1207 | 1230.2 | 1238 | 1230.1 | 1163.6 | 1180.1 | 1243 | 1259.1 | 1259.7 | 1281.3 | 1321 | 1305.5 | 1251.5 | 1241.9 | 1200.5 | 1230.6 | 1272.2 | 1263.6 | 1263.2 | 1285.1 | 1263.6 | 1256.4 | 1238.3 | 1263.1 | 1237.4 | 1242.5 | 1212.8 | 1215.2 | 1163.9 | 1213.3 | 1280.08 | 1185.3 | 1200 | 1203.1 | 1201 | 1224.3 | 1196.8 | 1230 | 1186 | 1199.9 | 1278.3 | 1176 | 1084.9 | 1202.3 | 1126.4 | 1204.4 | 1205.5 | 1240.2 | 1222.3 | 1190.6 | 1198.4 | 1233.7 | 1237.9 | 1236.8 | 1256.4 | 1256.6 | 1218.3 | 1171.9 | 1067.1 | 1086.1 | 1084 | 1079.7 | 1095.4 | 1095.8 | 1094.5 | 1100.5 | 1108.1 | 1103.5 | 1092.1 | 1101 | 1115.9 | 1059 | 968.5 | 1149.4 | 1115.8 | 1113.3 | 1120.7 | 1113.4 | 1117.4 | 1120 | 1116.6 | 1123.7 | 1113.3 | 1127.4 | 1081.4 | 1120.4 | 1071.5 | 1069.7 | 1064.5 | 1211.9 | 1184.5 | 1084.4 | 1209.7 | 1207.3 | 1217.4 | 1265.6 | 1220.9 | 1335.2 | 1213.8 | 1129.6 | 1119.8 | 1099.3 | 1194.9 | 1130 | 1262.2 | 1065.6 | 1084.3 | 1185.2 | 1034.9 | 973.1 | 1231.2 | 1223.4 | 1289.6 | 1247.4 | 1221.9 | 1240.3 | 1299 | 1279.1 | 1151.4 | 1147.2 | 1078.7 | 1072.2 | 1083 | 1127.6 | 1093.3 | 1119.6 | 1068.8 | 1066 | 1074.6 | 1082.9 | 1122.6 | 1117.2 | 1115.5 | 1069.8 | 1158 | 1156 | 1043.2 | 1080.7 | 1046.7 | 1086.9 | 1086 | 1100 | 1114.3 | 1108.8 | 1114.8 | 1118.9 | 1114.1 | 1113.3 | 1120.8 | 1182.4 | 1211 | 1269.6 | 1196.3 | 1207.6 | 1314.1 | 1253.1 | 1241.2 | 1238.9 | 1312.2 | 1285.1 | 1243.2 | 1305.5 | 1269.8 | 1185.4 | 1269.7 | 1287.1 | 996.9 | 998.7 | 1251.8 | 1062.4 | 1231.3 | 1157.1 | 1156.5 | 1155.3 | 1165.6 | 1139 | 1156.5 | 1153.6 | 1136.2 | 1129.9 | 1154 | 1230.7 | 1146.8 | 1145.7 | 1102 | 1126.8 | 1124.7 | 1175.2 | 1175.7 | 1178.7 | 1176.1 | 1169.9 | 1111.1 | 1164.6 | 1159 | 1160.1 | 1160.3 | 1062.9 | 1162.5 | 1150.2 | 1112.6 | 1091.2 | 1114 | 1226.1 | 1108.6 | 1142.5 | 1147.9 | 1141 | 1086.8 | 1026.7 | 1131 | 1169.9 | 1085 | 1092.9 | 1149.6 | 1142.4 | 1127.5 | 1138.1 | 1143 | 1127.6 | 1191.7 | 1084.1 | 1076.2 | 1056.2 | 1087.8 | 1100 | 1092.5 | 1131.9 | 1152.5 | 1145.8 | 1114.2 | 1134.2 | 1138.9 | 1136.6 | 1135 | 1138.6 | 1111.9 | 1082 | 1084 | 1137.9 | 1041.8 | 1085.7 | 1096.4 | 1190.4 | 1151.2 | 1151.2 | 1153 | 1187.9 | 1141.8 | 1186.3 | 1092.7 | 1137.5 | 1092.8 | 1089.7 | 1042.2 | 1091.6 | 1099 | 1082.3 | 0 | 41.15 | 0 | 0 | 5.56 | 5 | 0 | 0 | 90230960 | 264171 | 91631210 | 308796 | 75459620 | 157795 | 89837250 | 137355 | 854260 | 10210 | 135540 | 750 | 94440 | 135 | 96140 | 136 | 92560 | 129 | 96630 | 158 | 190000 | 2000 | 188000 | 2000 | 379770 | 378000 | 12 | 5.56 | 5 |  | 41.15 | 0 | 387842.28
2025-06-19 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 5:23 | 17:38 | 406.2 | 399.5 | 433.9 | 433.1 | 429.3 | 411.5 | 439.9 | 424.4 | 433.8 | 435.4 | 437.8 | 433.2 | 436 | 432.9 | 438.2 | 436.9 | 410.7 | 414.5 | 435.5 | 438.7 | 452.9 | 447.5 | 447.9 | 447.9 | 448.4 | 449.8 | 450.1 | 448.7 | 454 | 452.6 | 449 | 448.2 | 428.5 | 403.2 | 406.9 | 410.1 | 417.3 | 414.3 | 432.2 | 414.1 | 431.3 | 465.2 | 489.3 | 464.1 | 462.5 | 480 | 512 | 503.5 | 538.9 | 480 | 459.5 | 452.7 | 450.3 | 470.4 | 463.4 | 469.3 | 484.9 | 447.5 | 372.4 | 446.8 | 431.8 | 404.1 | 444 | 1024.2 | 1016.6 | 1021.5 | 1026.9 | 1029.3 | 1028 | 1007.4 | 1033.6 | 1027.5 | 1012.5 | 992.9 | 1013 | 977.1 | 964.4 | 989.5 | 1018.3 | 1023.2 | 1004.9 | 1065 | 1031.7 | 983.2 | 1024.9 | 985 | 975.9 | 1012.9 | 1027.5 | 1004.4 | 1022.3 | 1003.5 | 1024 | 1033.7 | 1041 | 1036.3 | 1119.7 | 1036 | 1031.9 | 980.5 | 986.1 | 1033.2 | 1008.1 | 1036.2 | 1067.9 | 1030.1 | 1046.1 | 1026.4 | 1032.7 | 1049.6 | 1043.7 | 1020.6 | 958.5 | 981.3 | 1009 | 1025.5 | 1016.3 | 1027.1 | 1034.9 | 1031.5 | 1020.9 | 1017.4 | 964.3 | 979.5 | 1029.2 | 1030.9 | 1004 | 1030 | 1010.7 | 1011.4 | 1003 | 1015 | 1014.2 | 1025.4 | 1010 | 1027.3 | 993.6 | 1045.8 | 1112.9 | 1025.2 | 1034.1 | 1028.6 | 1035.9 | 1041.5 | 1033.9 | 1046.9 | 1036.7 | 1003.6 | 1084.2 | 982.6 | 906.3 | 1037 | 961.8 | 1019.3 | 1023 | 1027.5 | 1030.8 | 1020.3 | 1014.4 | 1016 | 1016.4 | 1023.6 | 1037.9 | 1058.3 | 1039.5 | 985.7 | 922.1 | 938.8 | 933.7 | 935 | 932.4 | 935.3 | 936.8 | 945.2 | 950.5 | 940.4 | 942.8 | 945.7 | 950 | 900.2 | 818.7 | 974.5 | 948.1 | 945.1 | 950.3 | 945.3 | 943.5 | 943.2 | 941.9 | 944.2 | 935.9 | 944.3 | 932.6 | 939.2 | 894.6 | 890.6 | 897.9 | 1023.2 | 1002.7 | 919 | 1040.8 | 1045.4 | 1056.4 | 1080.9 | 1051.6 | 1159.5 | 1055.1 | 984.3 | 997.6 | 955.2 | 1033.2 | 1006 | 1085.4 | 916.5 | 921.3 | 1016.3 | 879.3 | 831 | 1073.7 | 1066.2 | 1111.8 | 1083.2 | 1057.2 | 1073.6 | 745.1 | 90.3 | 957.2 | 956.2 | 886.9 | 891 | 884.7 | 920.3 | 896 | 919.9 | 898.4 | 890.1 | 890.5 | 882.7 | 899.9 | 930.9 | 900.1 | 889.5 | 898.4 | 886 | 888.1 | 925.2 | 889.1 | 932.2 | 889 | 934.4 | 931.2 | 930.2 | 918.7 | 940.9 | 922.8 | 932.9 | 941.4 | 983.3 | 1003 | 1023.9 | 970.6 | 1022.9 | 1070.7 | 1015.9 | 996.6 | 986.5 | 1034.3 | 1026.5 | 985.9 | 1065.1 | 1041.3 | 959.5 | 1046 | 1050.4 | 803.6 | 802.9 | 1012.8 | 853.6 | 978.3 | 921.2 | 920.9 | 914.2 | 916.8 | 897.3 | 904.8 | 919.6 | 906.1 | 898.1 | 923.2 | 993.1 | 914 | 918.4 | 878.8 | 875.2 | 872.2 | 914.3 | 917.3 | 925.4 | 922.1 | 913.4 | 1035 | 910.5 | 906.6 | 918.5 | 910.4 | 830 | 912 | 920.2 | 878.4 | 870.3 | 859.8 | 959.5 | 883.5 | 921.5 | 915.6 | 911.5 | 867.1 | 818.7 | 872.1 | 951.4 | 867.7 | 877.2 | 927.8 | 913.6 | 907.8 | 913 | 912.2 | 871.9 | 968.4 | 867.9 | 877.6 | 788.8 | 873 | 880 | 811 | 913.9 | 933.4 | 932.2 | 899.6 | 924 | 922 | 925.7 | 919.6 | 929.1 | 911.6 | 880 | 886 | 925.9 | 834 | 882 | 891.6 | 964.5 | 930.6 | 934.6 | 889.3 | 979.8 | 934.2 | 969.9 | 881.2 | 930.7 | 885.1 | 893.1 | 845.5 | 894.9 | 892.2 | 888 | 0 | 39.56 | 0 | 0 | 4.54 | 4.15 | 0 | 0 | 90309610 | 264292 | 91711770 | 308850.7 | 75536680 | 157954.8 | 89914460 | 137503.8 | 855050 | 10210 | 136300 | 750 | 78650 | 121 | 80560 | 54.7 | 77060 | 159.8 | 77210 | 148.8 | 158000 | 0 | 152000 | 0 | 313480 | 310000 | 12.25 | 4.54 | 4.15 |  | 39.56 | 0 | 318890.5
2025-06-20 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:47 | 17:29 | 423 | 416.2 | 448.2 | 450.9 | 444.3 | 427 | 453.7 | 440.9 | 448 | 453.1 | 451.8 | 448.7 | 450.3 | 448.7 | 452.1 | 449.1 | 428.6 | 430.4 | 450.3 | 454.2 | 465.2 | 460.7 | 463 | 460.7 | 462.9 | 462.8 | 464.4 | 465.1 | 468.8 | 467.7 | 464 | 465 | 430.8 | 410.4 | 419.6 | 421.5 | 430.8 | 427.5 | 437.5 | 424.3 | 434.4 | 465.1 | 483.3 | 457 | 461.5 | 471.8 | 508.1 | 500.1 | 538.1 | 485.7 | 463.8 | 456.8 | 456.1 | 479.3 | 475 | 478.1 | 493.3 | 458.7 | 403.8 | 462 | 448.8 | 422.9 | 447.8 | 1052.1 | 1036.1 | 1053.5 | 1043.1 | 1034.7 | 1033.8 | 1021.2 | 1049 | 1033.4 | 1025.5 | 997 | 1025.6 | 985.7 | 979.8 | 966.4 | 1012.5 | 1057.8 | 1025.5 | 1092.6 | 1063.6 | 1008.9 | 1057.7 | 1016.4 | 1006.4 | 1044.3 | 1069.2 | 1048.9 | 1048.5 | 1005.6 | 1038.3 | 1051.1 | 1060.4 | 1061.2 | 1141.7 | 1063.6 | 1059.2 | 1002.3 | 1003.6 | 1059 | 1033.7 | 1055.1 | 1090 | 1044.6 | 1062.8 | 1033.1 | 1047.2 | 1064.3 | 1064.8 | 1068.3 | 952 | 1007.6 | 1031.7 | 1024.4 | 1041.9 | 1057.2 | 1066.2 | 1065.2 | 1045.6 | 1038.7 | 994.3 | 1010.9 | 1056.9 | 1046.6 | 1040.1 | 1054.2 | 1043.6 | 1037.1 | 1017.4 | 1032.3 | 1018.1 | 1018.5 | 1003.7 | 1014 | 937.4 | 974.8 | 1040.9 | 964.1 | 985.4 | 954.1 | 964 | 988.5 | 986.4 | 985.7 | 986.7 | 947.9 | 1032 | 929.8 | 867.6 | 989.9 | 924.3 | 977.5 | 994.9 | 995.1 | 982.2 | 993.1 | 998.7 | 962 | 987.3 | 979.6 | 991.1 | 1048.8 | 1013.7 | 903 | 843.6 | 856.9 | 851.2 | 857.1 | 858.4 | 861.9 | 864.1 | 870.1 | 874.6 | 863 | 856.7 | 863.1 | 872.5 | 821.8 | 744 | 886.7 | 867.2 | 858.1 | 870.5 | 867.9 | 864.3 | 867.3 | 857.6 | 864.8 | 853.1 | 865.7 | 872.9 | 870.2 | 825.2 | 828.6 | 828.6 | 940.2 | 918.9 | 838.4 | 955.8 | 960.1 | 967.5 | 996.6 | 969 | 1063.2 | 975.2 | 915.1 | 910.1 | 886.9 | 963 | 969 | 1003.6 | 841.8 | 843 | 931.4 | 802.7 | 789 | 962.6 | 988.4 | 1021.5 | 1005 | 975.5 | 990.2 | 1071.9 | 1106.9 | 916.5 | 911.5 | 850.7 | 832 | 863.1 | 887.2 | 864.7 | 869.3 | 840 | 828.4 | 839.1 | 826.3 | 841.8 | 871.8 | 834.6 | 859 | 834.7 | 831.2 | 807.3 | 853.9 | 825.4 | 861.9 | 825.4 | 860.4 | 862.2 | 857.3 | 840.4 | 848.9 | 839.3 | 853.2 | 849.3 | 1013.9 | 1017.6 | 1057.9 | 997.2 | 1054.2 | 1095.8 | 1011.8 | 1030 | 1006.3 | 1059.5 | 1050.6 | 1008.6 | 1077.7 | 1051.9 | 971.5 | 1058.5 | 1056.4 | 811.7 | 815.2 | 1024.1 | 868.2 | 998.9 | 946.6 | 948.3 | 940.3 | 940.4 | 917 | 921.8 | 945.8 | 932.7 | 920.6 | 948.6 | 1016.2 | 938.2 | 942.2 | 908.7 | 893 | 896.4 | 936.2 | 940.2 | 946.6 | 944.6 | 936 | 984.3 | 934 | 932.7 | 943.2 | 934.2 | 859.8 | 933.6 | 941.1 | 899.1 | 889.6 | 861.2 | 966.5 | 915.6 | 957.2 | 946.8 | 944.1 | 900.7 | 856.5 | 885.1 | 968.5 | 906.1 | 897.1 | 964 | 921.3 | 944.9 | 949.7 | 929.6 | 901.3 | 1007.9 | 913.2 | 898.4 | 836.1 | 901.8 | 913 | 855.1 | 934.9 | 962.6 | 958.4 | 930.3 | 952.1 | 946.3 | 959.5 | 944.8 | 962 | 937.8 | 914.3 | 917 | 970.3 | 881.7 | 923.6 | 937.4 | 995.1 | 970.1 | 971.6 | 926.5 | 1013.3 | 968.8 | 1005.6 | 922.5 | 970.5 | 927.4 | 930.1 | 889.8 | 940.9 | 935.1 | 928.3 | 31.6 | 37.42 | 0 | 0 | 4.56 | 4.28 | 0 | 0 | 90389900 | 264419 | 91789090 | 308943 | 75611580 | 158163 | 89994330 | 137669 | 855830 | 10210 | 137070 | 760 | 80290 | 127 | 77320 | 92.3 | 74900 | 208.2 | 79870 | 165.2 | 156000 | 0 | 154000 | 2000 | 312380 | 310000 | 12.7 | 4.56 | 4.28 |  | 37.42 | 0 | 317374.3
2025-06-21 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:58 | 17:40 | 443.5 | 435.6 | 466.5 | 469.2 | 468.6 | 450.2 | 471.7 | 458.7 | 469.5 | 475.4 | 468.4 | 466.6 | 475 | 474.1 | 476.5 | 473.6 | 446.7 | 447.5 | 465.9 | 471 | 482.1 | 479.1 | 483.4 | 482.6 | 478.6 | 481.1 | 482.5 | 483.3 | 488.1 | 485.4 | 482.6 | 482.7 | 461.2 | 435.9 | 442.7 | 445.6 | 453.1 | 448.4 | 466.6 | 448 | 465.8 | 499.4 | 520.3 | 498.7 | 499 | 511.4 | 551.9 | 543.4 | 579.5 | 518.9 | 497.7 | 490.9 | 487.8 | 510.2 | 499.6 | 506.2 | 519.5 | 482.6 | 425.9 | 482.7 | 467.6 | 439.5 | 482.1 | 1086.3 | 1072.3 | 1082.6 | 1077.1 | 1073.1 | 1066.2 | 1062.4 | 1090.6 | 1080.1 | 1075.3 | 1038 | 1076 | 1026.4 | 1035.8 | 1104.8 | 1104.3 | 1112.2 | 1075.4 | 1146.2 | 1112.4 | 1055.3 | 1096.5 | 1050.2 | 1041.7 | 1072.8 | 1096.6 | 1090.8 | 1085.4 | 1009.5 | 1037.4 | 1054 | 1062.2 | 1071.1 | 1150.8 | 1081.1 | 1079.2 | 1004.2 | 1012.8 | 1072.7 | 1053.7 | 1064.8 | 1115.1 | 1046.8 | 1073.1 | 1055.6 | 1054.5 | 1083.6 | 1089.5 | 1087.9 | 958.1 | 1033.6 | 1083 | 1072.9 | 1100 | 1112.4 | 1128.8 | 1127.6 | 1099.1 | 1099.5 | 1048.4 | 1065.5 | 1114.2 | 1111.9 | 1095.8 | 1113.2 | 1089.7 | 1104.5 | 1085.9 | 1098 | 1092.4 | 1101.3 | 1085.1 | 1106.5 | 1058.4 | 1115.6 | 1189 | 1109 | 1103.1 | 1101.1 | 1102.1 | 1116.9 | 1106.4 | 1118 | 1108.6 | 1070.4 | 1157.1 | 1049 | 965.5 | 1106.5 | 1023.4 | 1080.3 | 1091 | 1066.2 | 1066.1 | 1087.7 | 1082.4 | 1086.4 | 1085.6 | 1092.1 | 1108.5 | 1153 | 1114.9 | 1024.1 | 989.3 | 1002.8 | 992.2 | 988.3 | 988.6 | 989.2 | 992.3 | 998.3 | 1010.5 | 1006.6 | 1005 | 1005.5 | 1016.2 | 960.1 | 883.6 | 1051.3 | 1017.3 | 1019.9 | 1019 | 1009.8 | 1015.1 | 1011.9 | 1019.8 | 1016.1 | 1010.1 | 1019.3 | 995.8 | 1002 | 963.1 | 953.8 | 961.3 | 1104.7 | 1089.4 | 995.2 | 1125.2 | 1129.5 | 1139.7 | 1142.3 | 1131.1 | 1245.9 | 1127.7 | 1048.6 | 1065.1 | 1008.6 | 1110.7 | 1086.2 | 1171.3 | 988.8 | 996.9 | 1101.6 | 956.9 | 905.7 | 1084.8 | 1141.6 | 1203.1 | 1164.7 | 1142.4 | 1158.2 | 1245.1 | 1300.4 | 1054.5 | 1047.3 | 978.7 | 971.9 | 971.5 | 1015.3 | 976.4 | 1003.6 | 982.3 | 965.3 | 967.5 | 968.5 | 963.8 | 995.7 | 968.4 | 997 | 983.3 | 987.2 | 979.7 | 1018.2 | 976.3 | 1027.9 | 975.8 | 1025.8 | 997.1 | 997.6 | 993.3 | 1014.4 | 989.6 | 1002.1 | 1009.3 | 1036.2 | 1075.7 | 1133.3 | 1070.9 | 1107.3 | 1178 | 1110.2 | 1125.2 | 1083.5 | 1134.7 | 1123.5 | 1082.2 | 1162.7 | 1133.9 | 1048.5 | 1140.4 | 1154.1 | 886 | 883.4 | 1107 | 938.4 | 1074.9 | 1028.9 | 1030.1 | 1019.9 | 1024.2 | 996.5 | 1005 | 1029.8 | 1008 | 1001.1 | 1026.8 | 1093.1 | 1017.8 | 1015.8 | 977.6 | 970.6 | 975.6 | 1012.2 | 1019.6 | 1016.3 | 1010.4 | 1009.4 | 1063.7 | 1005.1 | 1007.5 | 1005.6 | 1001.7 | 928.8 | 1006.2 | 1012.3 | 966.6 | 955.3 | 973.7 | 1070.6 | 993.7 | 1034.8 | 1027.9 | 1020 | 969 | 917.3 | 972.4 | 1053.9 | 983.2 | 996.9 | 1037.3 | 1031.1 | 1015.1 | 1018.5 | 1022.3 | 984.6 | 1074.7 | 971.2 | 969.7 | 930.7 | 976 | 985 | 948.5 | 1005.6 | 1026.3 | 1027.1 | 987.8 | 1010.6 | 1011.8 | 1017.9 | 1012.1 | 1025.2 | 1007.8 | 979.8 | 982 | 1028.9 | 933.9 | 978.4 | 992 | 1072.9 | 1041 | 1041.4 | 993 | 1080.7 | 1034.4 | 1087.1 | 993.3 | 1039 | 999.4 | 989.1 | 947.3 | 1005.5 | 983.4 | 985.1 | 30.6 | 38.75 | 0 | 0 | 5.02 | 4.54 | 0 | 0 | 90473130 | 264535 | 91875310 | 308984 | 75696850 | 158291 | 90080270 | 137756 | 856680 | 10220 | 137930 | 760 | 83230 | 116 | 86220 | 41 | 85270 | 128 | 85940 | 87 | 170000 | 2000 | 172000 | 0 | 340660 | 342000 | 12.7 | 5.02 | 4.54 |  | 38.75 | 0 | 346720.2
2025-06-22 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 5:29 | 17:45 | 522.3 | 512.4 | 552.4 | 553.4 | 554.1 | 537.1 | 564.3 | 545.1 | 555.1 | 565.3 | 564.4 | 561.6 | 569.2 | 567.4 | 574.8 | 575.8 | 533.3 | 538.3 | 560.9 | 567.7 | 582.7 | 578.5 | 586.4 | 586.2 | 575.9 | 579.9 | 582.4 | 585.7 | 584.1 | 583.8 | 580.6 | 584.7 | 557.9 | 524.1 | 530 | 534.4 | 547.2 | 546.2 | 563 | 542 | 563.1 | 604.6 | 631.6 | 601 | 602 | 620.4 | 669 | 659.2 | 706.4 | 636.7 | 606.7 | 599 | 599 | 627 | 613.8 | 621.8 | 633.2 | 589.3 | 516.4 | 589.1 | 570.5 | 534.8 | 586.3 | 1299.3 | 1285.6 | 1298.3 | 1296.1 | 1280.9 | 1281.6 | 1276.5 | 1315.6 | 1285.8 | 1283.4 | 1267.5 | 1276.6 | 1232.4 | 1235.3 | 1287.3 | 1318.8 | 1327.8 | 1283.2 | 1365.4 | 1339.2 | 1262 | 1307.7 | 1258.8 | 1244.9 | 1281.9 | 1311.1 | 1305 | 1303.3 | 1189 | 1233.6 | 1244.2 | 1268.9 | 1262.3 | 1346.8 | 1274.5 | 1277.7 | 1212.9 | 1209.3 | 1289 | 1254.7 | 1278.7 | 1313.1 | 1269.7 | 1299.9 | 1268.4 | 1282.3 | 1308.6 | 1311.7 | 1309.6 | 1211 | 1229.6 | 1296.4 | 1317.1 | 1303 | 1330.5 | 1348.1 | 1352.4 | 1329.9 | 1331.1 | 1267.8 | 1283.4 | 1364 | 1357.9 | 1335 | 1377 | 1338.2 | 1342.2 | 1337.6 | 1368.9 | 1338.2 | 1363.4 | 1336.7 | 1347.1 | 1325.7 | 1338.8 | 1414.7 | 1321 | 1342.4 | 1321.2 | 1307 | 1363.2 | 1342.7 | 1366.4 | 1350.2 | 1329.4 | 1435.6 | 1308.3 | 1209.2 | 1345.4 | 1262.1 | 1325.2 | 1335.7 | 1363.2 | 1380.7 | 1359.1 | 1342.5 | 1326.7 | 1352.4 | 1338.4 | 1392.6 | 1383.9 | 1346.9 | 1318.7 | 1201.9 | 1217.8 | 1212.4 | 1217.9 | 1212.6 | 1218.4 | 1219.5 | 1223.1 | 1230.9 | 1226.8 | 1214.4 | 1223.3 | 1238.5 | 1177 | 1076.7 | 1280.8 | 1239.8 | 1239.1 | 1240.2 | 1228.9 | 1235.8 | 1233.3 | 1241.9 | 1242.9 | 1242 | 1251 | 1238.3 | 1236.4 | 1185.2 | 1184.6 | 1178.6 | 1354.2 | 1333.7 | 1210.1 | 1343.3 | 1350.3 | 1367 | 1393.9 | 1349.9 | 1495.9 | 1345.6 | 1257.7 | 1239 | 1246.7 | 1355.1 | 1280 | 1418.3 | 1202.7 | 1231.6 | 1309.8 | 1167.5 | 1088.5 | 1358.4 | 1379.6 | 1438.9 | 1400 | 1355.2 | 1400.3 | 1479.4 | 1489 | 1294.5 | 1279.5 | 1203.5 | 1207.3 | 1199.5 | 1248.6 | 1213.7 | 1246.1 | 1218 | 1205.8 | 1206.4 | 1209.4 | 1248.2 | 1250 | 1242.9 | 1244.8 | 1201.7 | 1212 | 1178.2 | 1222.9 | 1193.2 | 1240.7 | 1200.4 | 1251.6 | 1248.5 | 1244.9 | 1258.9 | 1268.4 | 1239.5 | 1243.3 | 1254 | 1284.7 | 1290.6 | 1385.6 | 1315.2 | 1366.7 | 1420.9 | 1356.1 | 1371.3 | 1327.8 | 1392.5 | 1357.7 | 1326.1 | 1417.7 | 1368.4 | 1308.7 | 1380.8 | 1435 | 1097.8 | 1101.2 | 1354.9 | 1169.3 | 1317.1 | 1222.2 | 1227.7 | 1221.3 | 1220 | 1189.5 | 1200.5 | 1236 | 1217.5 | 1200.6 | 1235.9 | 1300 | 1227.4 | 1242.7 | 1187.7 | 1161.8 | 1161.9 | 1212.2 | 1215.2 | 1217.3 | 1207.4 | 1214.1 | 1296.2 | 1212.8 | 1209.9 | 1222.9 | 1217.1 | 1113.8 | 1220.4 | 1238.7 | 1181.1 | 1171.2 | 1188.7 | 1297 | 1180.1 | 1233.7 | 1216.5 | 1232.9 | 1178.3 | 1111.6 | 1242.9 | 1289.9 | 1167.8 | 1167.4 | 1247.2 | 1230.6 | 1219.3 | 1229.9 | 1235 | 1232.6 | 1301.6 | 1176 | 1180.5 | 1209 | 1206.8 | 1215 | 1211.5 | 1222.6 | 1260.3 | 1249.5 | 1222.2 | 1243.4 | 1249.6 | 1259 | 1247.5 | 1261.4 | 1231 | 1194 | 1198 | 1256.1 | 1129.8 | 1192.2 | 1203.5 | 1279.4 | 1254.6 | 1262.7 | 1190.4 | 1315.1 | 1248.1 | 1289.5 | 1175.2 | 1246.9 | 1160.9 | 1198.3 | 1139.6 | 1196.1 | 1197.5 | 1180.2 | 31.4 | 41.12 | 0 | 0 | 6.29 | 5.51 | 0 | 0 | 90572750 | 264651 | 91980680 | 309053 | 75800990 | 158477 | 90184340 | 138013 | 857690 | 10220 | 138960 | 760 | 99620 | 116 | 105370 | 69 | 104140 | 186 | 104070 | 257 | 202000 | 0 | 206000 | 0 | 413200 | 408000 | 12.2667 | 6.29 | 5.51 |  | 41.12 | 0 | 420997
2025-06-23 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 5:52 | 17:34 | 139.9 | 134.9 | 147.6 | 146.3 | 145.6 | 139.1 | 150.7 | 143.6 | 147.4 | 145.7 | 149.8 | 147.9 | 148.2 | 146.6 | 149 | 148.6 | 137.4 | 143.1 | 149.9 | 149.1 | 155.5 | 154.3 | 152.4 | 150.3 | 151.3 | 153.5 | 155.5 | 155.1 | 157.6 | 153.2 | 155 | 149.3 | 145.3 | 134.4 | 136.3 | 137.2 | 141.6 | 136.6 | 143.5 | 140.5 | 143.3 | 157.7 | 164.4 | 156 | 154.8 | 161.9 | 174.8 | 171.5 | 182.9 | 164.5 | 154 | 150.9 | 152.1 | 160.4 | 159.3 | 158 | 166.8 | 152.1 | 135.3 | 153.3 | 148 | 139.7 | 148.3 | 350.8 | 347.4 | 353 | 349.2 | 355.2 | 347.9 | 345.7 | 352.3 | 352.9 | 347.3 | 340.3 | 345.8 | 331.4 | 330.3 | 348.3 | 350.9 | 355.2 | 346.2 | 368.8 | 353.3 | 340 | 356.3 | 337.2 | 335.8 | 349.9 | 356 | 348.9 | 350.2 | 337.6 | 350.7 | 350.2 | 352.6 | 354.3 | 384.8 | 355.4 | 351.5 | 134.5 | 263 | 354.7 | 343.5 | 355.7 | 369.9 | 351 | 356.9 | 350 | 356.2 | 359.2 | 356.6 | 359.2 | 328.2 | 339.3 | 348 | 356.5 | 352.7 | 354.4 | 359.3 | 356.1 | 350.3 | 350.5 | 331.9 | 337.6 | 356.1 | 356 | 347.4 | 356.1 | 350.7 | 350.6 | 345.3 | 350.5 | 348.5 | 351.6 | 345.9 | 350.5 | 340.7 | 347.6 | 370.6 | 339 | 343 | 340.7 | 342.5 | 345.8 | 343.2 | 348.9 | 346.7 | 329.4 | 362.3 | 327.8 | 299.3 | 347 | 321.5 | 343.7 | 345.7 | 347.4 | 352.5 | 348.7 | 346.3 | 342.5 | 344.9 | 343.1 | 349.4 | 366.6 | 355 | 330.4 | 292.6 | 306.1 | 293.8 | 298.9 | 298.7 | 301.2 | 299.6 | 303.3 | 311.5 | 307.1 | 302.7 | 309.8 | 315.1 | 289.9 | 267.2 | 328.8 | 309.6 | 313.8 | 312 | 304.7 | 308.8 | 308.8 | 313 | 308.8 | 307.7 | 307.4 | 310.4 | 309.8 | 287.8 | 289.1 | 299.1 | 340 | 328.4 | 300.9 | 340.7 | 340.3 | 342.6 | 354.6 | 344 | 381.1 | 346.7 | 324.7 | 325.3 | 310.8 | 335.7 | 320 | 360 | 302.3 | 301.7 | 327.2 | 290 | 266.7 | 351.3 | 347.8 | 363.7 | 354 | 350.6 | 349.8 | 383.5 | 394.5 | 326 | 329.3 | 304.9 | 299.8 | 301.5 | 306.3 | 306.5 | 316 | 307.2 | 298 | 300.4 | 307.5 | 297.4 | 306.8 | 302.5 | 308.4 | 314 | 310 | 310.2 | 310.8 | 301.2 | 310.1 | 299.7 | 309.9 | 313.4 | 309.8 | 322.5 | 315.2 | 305.7 | 310.6 | 313.6 | 337.8 | 345.1 | 352.9 | 334.8 | 356.3 | 372.9 | 349.3 | 355.6 | 337.2 | 352.7 | 353.1 | 337.3 | 371.3 | 361.7 | 331.1 | 365.9 | 358.2 | 273.6 | 272.9 | 346.9 | 291.7 | 335 | 321 | 321.3 | 310.1 | 309.1 | 304.9 | 313.8 | 319.6 | 312.9 | 306.1 | 320.6 | 349.9 | 313.2 | 319.1 | 308 | 305.8 | 294 | 309.6 | 318.7 | 317.4 | 314.9 | 320.8 | 347.4 | 317.4 | 310.7 | 315.4 | 318.8 | 282.6 | 311 | 316.1 | 300.3 | 297.8 | 312 | 342.6 | 310.8 | 323.6 | 303.7 | 315.9 | 305.3 | 280.5 | 315.9 | 345.6 | 293 | 307.4 | 339.9 | 336.6 | 331.9 | 325.6 | 332.2 | 313.7 | 349.6 | 306.8 | 292.4 | 313.8 | 320.7 | 319 | 326.7 | 314.5 | 320.5 | 324.9 | 313.4 | 312.6 | 322 | 319.8 | 318.2 | 326.6 | 313.4 | 305 | 308 | 328 | 286.4 | 301.3 | 313.1 | 320.9 | 318.8 | 319 | 299.1 | 335.2 | 318.6 | 337.3 | 299.9 | 316 | 301.6 | 310.7 | 289.1 | 314.4 | 314.3 | 302.6 | 27.27 | 29.59 | 0 | 0 | 1.52 | 1.39 | 0 | 0 | 90599300 | 264797 | 92007310 | 309150 | 75826870 | 158649 | 90210060 | 138282 | 857960 | 10230 | 139220 | 770 | 26550 | 146 | 26630 | 97 | 25880 | 172 | 25720 | 269 | 54000 | 2000 | 52000 | 2000 | 104780 | 106000 | 11.7 | 1.52 | 1.39 |  | 29.59 | 0 | 108742.2
2025-06-24 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:58 | 17:18 | 283.5 | 272.2 | 301 | 297.3 | 297.8 | 283.4 | 309.1 | 295.1 | 303 | 303.4 | 309.9 | 305.9 | 302.9 | 305.9 | 307.7 | 307.7 | 288.4 | 296.8 | 312.9 | 311.9 | 326.1 | 321 | 322.1 | 320.4 | 324.8 | 324.8 | 325.4 | 324.4 | 330.9 | 327.5 | 326.4 | 322.9 | 298.6 | 277.6 | 280.4 | 283 | 289.7 | 288.2 | 299.7 | 290.1 | 299.7 | 323 | 338.2 | 320.1 | 324.2 | 333.4 | 359.7 | 356.2 | 383.5 | 344.6 | 326.1 | 322 | 321.3 | 339.4 | 336.2 | 335.6 | 346.8 | 317 | 284.3 | 321.1 | 311.8 | 292.6 | 315.6 | 743.3 | 731.7 | 736.5 | 734.7 | 734.2 | 721.9 | 726.6 | 735.6 | 733.2 | 718.4 | 718.4 | 711.1 | 680.1 | 677.1 | 742.1 | 745.5 | 748.1 | 731.4 | 779.3 | 748.2 | 715.4 | 747.1 | 714.9 | 708.5 | 736.9 | 742.8 | 739.3 | 739.1 | 725.3 | 732.7 | 745 | 742.2 | 742.2 | 806.4 | 747.7 | 740.6 | 696.5 | 707.4 | 740.6 | 720.9 | 742.6 | 778.2 | 740 | 747.1 | 731.9 | 733.2 | 749.4 | 747.4 | 755.4 | 662 | 709.9 | 733.2 | 747 | 744.7 | 746.8 | 759.8 | 746.6 | 741.2 | 739.5 | 701.5 | 712.2 | 745.8 | 739.9 | 728.5 | 743.2 | 733.2 | 733.6 | 725.8 | 733.2 | 730.6 | 735 | 720.3 | 729.1 | 709.5 | 737.6 | 785.9 | 719.2 | 724.5 | 727.6 | 726.5 | 728.5 | 693.4 | 730.8 | 722.2 | 699.7 | 754.7 | 686.3 | 630 | 721.8 | 672.6 | 718.9 | 721.3 | 723.7 | 694.1 | 728 | 727.4 | 716.2 | 719.7 | 707.3 | 726.5 | 761 | 735.8 | 689.9 | 636.9 | 651.5 | 646 | 650.2 | 646.8 | 650.5 | 652.4 | 659.3 | 664.3 | 656.7 | 654.6 | 657.6 | 659.6 | 621.9 | 566.2 | 674.8 | 657.4 | 656.9 | 662.4 | 656.7 | 656.1 | 654.9 | 653.5 | 656.9 | 650.8 | 653 | 643 | 645.7 | 617.5 | 612.8 | 625.8 | 718.3 | 695.2 | 639.9 | 726.8 | 731.3 | 740.4 | 759.5 | 739.7 | 813.4 | 745 | 697.8 | 705.6 | 672.9 | 735.7 | 689 | 755.4 | 638.8 | 637 | 681 | 593.4 | 575.8 | 759.1 | 755.3 | 781.3 | 767.9 | 746 | 756.8 | 821.1 | 843.5 | 671.4 | 669.5 | 622.1 | 621.5 | 622.1 | 644.9 | 628.6 | 645.4 | 630 | 623.6 | 622.3 | 621 | 633.9 | 642.1 | 633 | 641.1 | 632.6 | 625 | 624.1 | 626.6 | 622.2 | 611.1 | 106.9 | 386.9 | 649.1 | 650.2 | 650.6 | 652.7 | 641.6 | 649.2 | 655.9 | 678.5 | 728.5 | 741.2 | 704 | 694.9 | 775.8 | 703.9 | 725.2 | 712.9 | 748.9 | 744.3 | 715.1 | 771.9 | 754.7 | 691.6 | 755.3 | 756.2 | 576 | 575.9 | 729.4 | 614.1 | 709.7 | 652.6 | 651.3 | 647.7 | 647 | 639.3 | 644.7 | 655.3 | 644.7 | 639.6 | 660.4 | 706.9 | 651.1 | 653.9 | 629.5 | 627.4 | 623.5 | 652.5 | 662.1 | 664.3 | 665.2 | 662.1 | 708 | 657 | 650.1 | 656.6 | 654.7 | 591.9 | 653.1 | 655.5 | 625.3 | 621.1 | 615.7 | 687.6 | 620.4 | 654.2 | 618.3 | 646.5 | 618.5 | 581.8 | 650 | 675.6 | 613.4 | 624 | 665 | 650.8 | 652.9 | 646.6 | 652.6 | 643.4 | 692.5 | 615.2 | 615.4 | 638.8 | 637.7 | 640 | 646.2 | 660.4 | 669.6 | 675.5 | 644.4 | 664.4 | 664 | 660.8 | 662.7 | 668.5 | 668 | 634.5 | 630 | 667 | 595.3 | 631.5 | 641.9 | 693.5 | 663.1 | 662.7 | 637.7 | 698.1 | 670 | 695.7 | 630.8 | 665.2 | 630.4 | 640.9 | 605.7 | 637.6 | 641.6 | 649 | 28.25 | 33.03 | 0 | 0 | 3.11 | 2.97 | 0 | 0 | 90655560 | 264955 | 92064040 | 309289 | 75881460 | 158872 | 90265490 | 138616 | 858510 | 10240 | 139760 | 770 | 56260 | 158 | 56730 | 139 | 54590 | 223 | 55430 | 334 | 110000 | 2000 | 108000 | 0 | 223010 | 218000 | 12.3333 | 3.11 | 2.97 |  | 33.03 | 0 | 226808.3
2025-06-25 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 5:23 | 17:39 | 442.6 | 432.2 | 471.8 | 471.7 | 464.3 | 446 | 482.3 | 464.2 | 468.4 | 473.6 | 482.2 | 477.2 | 474.1 | 474.9 | 477.2 | 477.7 | 450.7 | 457.8 | 480.6 | 485.2 | 498.1 | 495.3 | 494.6 | 493.8 | 493.7 | 496.3 | 496.7 | 495.8 | 502.2 | 499.3 | 495.7 | 497 | 464.8 | 436.3 | 440.9 | 445.6 | 455.7 | 453.9 | 465.2 | 450.7 | 466.9 | 501 | 524 | 499.6 | 500.7 | 515.2 | 552.6 | 543.5 | 586.4 | 528.1 | 498.4 | 493.6 | 491.9 | 517.7 | 510.7 | 517.2 | 531 | 492.5 | 436.8 | 497.3 | 478.9 | 448 | 482.9 | 1120.3 | 1108.4 | 1123.4 | 1090.6 | 1108.6 | 1095.9 | 1097.4 | 1117.9 | 1111.4 | 1090.7 | 1066.1 | 1091.8 | 1044.6 | 1039.4 | 1112.4 | 1114.4 | 1128.5 | 1103.1 | 1162.6 | 1123.3 | 1081.3 | 1123.1 | 1072.7 | 1071.3 | 1110.1 | 1130.1 | 1120.2 | 1119.6 | 1053.7 | 1093.6 | 1098.8 | 1118.8 | 1105 | 1163.5 | 1098.8 | 1104.1 | 902.9 | 1051.4 | 1119.9 | 1080.8 | 1120.4 | 1141.5 | 1105.9 | 1131.4 | 1096.2 | 1117.1 | 1134.4 | 1138.9 | 1112.3 | 1044 | 1068.1 | 1093.7 | 1082.2 | 1114.6 | 1124.3 | 1136.6 | 1128.1 | 1116 | 1104 | 1043.4 | 1063 | 1129.5 | 1126.5 | 1103.7 | 1131.7 | 1078.7 | 1111.2 | 1098.5 | 1114.2 | 1101.6 | 1106.5 | 1083.1 | 1091.7 | 1074.7 | 1136.6 | 1189.6 | 1097.6 | 1113.6 | 1113.1 | 1112.5 | 1128.4 | 1044.8 | 1134.2 | 1060.1 | 1052.8 | 1147.8 | 1060.4 | 967.8 | 1101.8 | 1017.6 | 1078.7 | 1083.8 | 1071.1 | 1089.6 | 1081.7 | 1080.5 | 1087.6 | 1101.3 | 1046.3 | 1123.1 | 1130.7 | 1100.4 | 1059 | 1029 | 1041.6 | 0 | 1028.7 | 1022 | 1024.4 | 1023.5 | 1030.7 | 1038.2 | 1023.8 | 1039.6 | 1041.7 | 1040.4 | 989.6 | 896.4 | 1062.2 | 1036.5 | 1029.6 | 1038.1 | 1034.8 | 1033.6 | 1032.9 | 1030.7 | 1032 | 1024.6 | 1036.6 | 1012.7 | 1001.1 | 979.4 | 969.7 | 981 | 1113.8 | 1091.2 | 944.8 | 1136.1 | 1141 | 1159.3 | 1175 | 1152.3 | 1280 | 1163.8 | 1082.6 | 1092.8 | 1051.7 | 1146.6 | 1060 | 1189 | 1001.7 | 1004.9 | 1099.4 | 938.3 | 912 | 1178.8 | 1173.6 | 1229.7 | 1189.9 | 1168.7 | 1184.7 | 1273.1 | 1323.7 | 1057.8 | 1051 | 977.8 | 970.7 | 965.5 | 1011.9 | 971.9 | 1006.6 | 988 | 962.2 | 976.3 | 958.4 | 975.5 | 1018.7 | 963.8 | 1012.5 | 986.1 | 987 | 977.9 | 905.4 | 964 | 865.4 | 0 | 0 | 1020.8 | 1022.9 | 1010.8 | 1035.2 | 1006.3 | 1023.3 | 1030.4 | 1053.8 | 1071.5 | 1099.1 | 1046.2 | 1102.3 | 1151.7 | 1083 | 1112.3 | 1069.3 | 1118.4 | 1106.2 | 1079.4 | 1166 | 1111 | 1055.8 | 1140.7 | 1150 | 882.2 | 882.7 | 1110.5 | 942 | 1070.5 | 985.7 | 993 | 990.4 | 995.5 | 967.3 | 963.5 | 991.8 | 972.2 | 967.8 | 993.6 | 1081.4 | 988 | 996.9 | 945.4 | 950.7 | 949.1 | 997.2 | 1000.3 | 1007.6 | 1007.6 | 1006.7 | 1091 | 994.5 | 989 | 998.7 | 992.5 | 903.5 | 992.6 | 1002.4 | 953.9 | 943.8 | 933.9 | 1038.1 | 946.9 | 981.5 | 939.8 | 978.6 | 930.4 | 875.9 | 943.6 | 1019.3 | 925 | 933.2 | 986.3 | 963 | 967.8 | 974.4 | 970.1 | 951 | 1039.5 | 926.6 | 898.1 | 954.6 | 945.3 | 968 | 959.1 | 967.4 | 997.8 | 989.4 | 964.1 | 985.8 | 987.5 | 997.2 | 989.3 | 1000.7 | 983.8 | 943.3 | 947 | 995.2 | 893.9 | 951.4 | 958.9 | 1028.5 | 998.5 | 1003.4 | 948.9 | 1047 | 992 | 1038.6 | 941.8 | 992.2 | 939.4 | 953.9 | 905.4 | 956 | 951.4 | 955.8 | 28.71 | 37.2 | 0 | 0 | 5.03 | 4.93 | 0 | 0 | 90740820 | 265097 | 92150060 | 309475 | 75965050 | 158991 | 90348620 | 138734 | 859370 | 10240 | 140590 | 780 | 85260 | 142 | 86020 | 186 | 83590 | 119 | 83130 | 118 | 172000 | 0 | 166000 | 2000 | 338000 | 338000 | 12.2667 | 5.03 | 4.93 |  | 37.2 | 0 | 343933.3
2025-06-26 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:58 | 17:46 | 560.4 | 512.4 | 591.3 | 590.3 | 591.5 | 562.7 | 600 | 582.3 | 597.2 | 600.3 | 599 | 598.5 | 601.6 | 604.2 | 609.1 | 609.4 | 571.2 | 569.3 | 595.5 | 602 | 621.8 | 583.6 | 624.7 | 624.1 | 615.1 | 618.2 | 621.3 | 619.3 | 622.2 | 622.7 | 618.9 | 619.1 | 589.6 | 554.5 | 560.8 | 560.8 | 574.9 | 576 | 593.8 | 566.5 | 582.4 | 630.3 | 665.3 | 633.5 | 622.8 | 645.4 | 662.1 | 675.6 | 722.1 | 651.4 | 618.4 | 608.6 | 603 | 633.2 | 633.4 | 647.5 | 664.5 | 614.5 | 542.1 | 616.2 | 596 | 554.4 | 581.5 | 1368.1 | 1364.8 | 1397.7 | 1402.1 | 1381.5 | 1391 | 1350.8 | 1403.8 | 1377.6 | 1357.7 | 1315.8 | 1352.8 | 1327.9 | 1326.5 | 1390.8 | 1385.4 | 1424 | 1354.7 | 1433.9 | 1413 | 1331.2 | 1349.9 | 1289 | 1288 | 1326.9 | 1396.6 | 1377.9 | 1377.2 | 1332.4 | 1371.9 | 1396.2 | 1416 | 1375.5 | 1460.3 | 1404.4 | 1372.2 | 1056.9 | 1341.2 | 1364.8 | 1348.1 | 1376.2 | 1467.9 | 1389.4 | 1418.7 | 1375.3 | 1395.2 | 1390.6 | 1403.4 | 1388.3 | 1280.4 | 1272.3 | 1372.2 | 1347.6 | 1359.3 | 1374.2 | 1412.2 | 1387.7 | 1378.9 | 1355.6 | 1284.4 | 1307.2 | 1388.8 | 1384.2 | 1351.6 | 1386.2 | 1340.5 | 1340.1 | 1342.3 | 1377.9 | 1334.6 | 1365.6 | 1337.1 | 1348.5 | 1333.1 | 1319.4 | 1424.4 | 1315.1 | 1344.7 | 1326 | 1331.9 | 1373.6 | 1290.1 | 1363 | 1303.5 | 1345.1 | 1437.4 | 1316.3 | 1208.6 | 1348 | 1267.1 | 1315.8 | 1329.7 | 1350.4 | 1374.9 | 1342.8 | 1333 | 1357.9 | 1347.1 | 1368.4 | 1403.7 | 1384.9 | 1352.1 | 1286.1 | 1243.3 | 1254.8 | 0 | 1253.1 | 1247.8 | 1246 | 1240.5 | 1237.7 | 1250.3 | 1256.4 | 1250.2 | 1252.8 | 1272.8 | 1207.4 | 1098.9 | 1268.4 | 1266 | 1254.2 | 1264.6 | 1259.3 | 1257 | 1267.5 | 1239.2 | 1261 | 1227.5 | 1260.5 | 1267.2 | 1269.7 | 1218.7 | 1220.6 | 1218.7 | 1298.2 | 1285.5 | 1199.9 | 1343.2 | 1349.3 | 1376 | 1395.4 | 1366.5 | 1521.5 | 1365.8 | 1284.9 | 1320.6 | 1224.9 | 1370.1 | 1240 | 1351.8 | 1152.8 | 1171.4 | 1287.6 | 1130.6 | 1071.9 | 1345.6 | 1381.8 | 1429.4 | 1380.6 | 1335.5 | 1386.8 | 1445.3 | 1522.3 | 1243.8 | 1237.7 | 1178.9 | 1165.8 | 1199.6 | 1232.7 | 1199.1 | 1231.1 | 1153.3 | 1153.6 | 1186.2 | 1199.3 | 1223.6 | 1249 | 1230.1 | 1265.3 | 1150.3 | 1161 | 1150.2 | 1112.4 | 1125.7 | 1100.7 | 0 | 0 | 1242.1 | 1223.2 | 1199.9 | 1222.1 | 1251.6 | 1240.3 | 1235.5 | 1335.5 | 1311.4 | 1369.3 | 1300.8 | 1343.5 | 1397.7 | 1308.9 | 1357.3 | 1324.4 | 1400.3 | 1365.1 | 1327.5 | 1397.4 | 1356.7 | 1282.3 | 1287 | 1384.8 | 1074.7 | 1080.6 | 1339.9 | 1154.5 | 1315 | 1246.6 | 1242.9 | 1233.5 | 1244.9 | 1199.3 | 1232.2 | 1247.5 | 1230.4 | 1214.8 | 1253.6 | 1328.2 | 1243.2 | 1250.8 | 1207.1 | 1201.5 | 1188.7 | 1244.5 | 1245.4 | 1251.3 | 1255.9 | 1250.8 | 1308.2 | 1235.8 | 1235.3 | 1244.8 | 1248.4 | 1135.8 | 1249 | 1247 | 1203.8 | 1203.2 | 1230.8 | 1331.1 | 1197.9 | 1282 | 1255.6 | 1256.4 | 1198.2 | 1135.5 | 1282 | 1316 | 1240 | 1255.1 | 1316.4 | 1315.8 | 1313 | 1303.4 | 1324.3 | 1330.9 | 1333.1 | 1240.4 | 1075.5 | 1255.6 | 1255.4 | 1283 | 1281 | 1306.9 | 1323.5 | 1319.7 | 1280.4 | 1303 | 1307.5 | 1305.1 | 1300.8 | 1316.1 | 1290.4 | 1264 | 1270 | 1326.3 | 1220.4 | 1274.9 | 1289.7 | 1386.5 | 1326.3 | 1326.8 | 1299.5 | 1371.6 | 1345.9 | 1408.6 | 1312.6 | 1354.6 | 1309.9 | 1282.4 | 1231.6 | 1306.2 | 1298.1 | 1283.2 | 32.74 | 43.94 | 0 | 0 | 6.98 | 6.55 | 0.36 | 0.3635 | 90846480 | 265187 | 92255100 | 309481 | 76064900 | 159123 | 90456050 | 138876 | 860410 | 10250 | 141620 | 780 | 105660 | 90 | 105040 | 6 | 99850 | 132 | 107430 | 142 | 208000 | 2000 | 206000 | 0 | 417980 | 414000 | 12.8 | 6.62 | 6.1865 |  | 43.94 | 0 | 427586.6
2025-06-27 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 6:09 | 17:45 | 367.1 | 340.4 | 387.9 | 389.3 | 383.9 | 369.1 | 393.4 | 379.1 | 384.5 | 389.6 | 391.6 | 387.3 | 392 | 388.6 | 392.6 | 393.4 | 367.9 | 371.3 | 388.5 | 392.4 | 403.5 | 400.5 | 401.5 | 401.3 | 398.3 | 400.8 | 403.6 | 404.4 | 405.8 | 403.7 | 401.9 | 401 | 384.7 | 360 | 365 | 366.3 | 374.7 | 371.3 | 384.6 | 370.5 | 385.9 | 418.6 | 437.6 | 416.2 | 413.4 | 429 | 456.9 | 452 | 488.2 | 430.6 | 410.7 | 405 | 402.3 | 420.4 | 416.4 | 421.7 | 435.8 | 403.8 | 355 | 405.1 | 390.2 | 364.5 | 376.8 | 916.2 | 913.6 | 911 | 920.8 | 923.3 | 916.2 | 902.5 | 925.1 | 920.1 | 909.4 | 882.2 | 910.2 | 871.8 | 874.4 | 907.5 | 912.3 | 912.9 | 902.2 | 951.3 | 918.8 | 880.1 | 917.5 | 872.4 | 874.3 | 903.4 | 915.8 | 916.4 | 919.7 | 868 | 898.5 | 898.5 | 918.5 | 910.7 | 986.4 | 900.5 | 911.6 | 852.5 | 857 | 918.6 | 887.8 | 920.1 | 937.2 | 904.6 | 931.1 | 916.7 | 925.3 | 936.7 | 934.5 | 933.1 | 849.7 | 874.5 | 906.1 | 927.2 | 913.2 | 925.8 | 898.1 | 926.5 | 922.4 | 916.8 | 868.6 | 877.3 | 923.3 | 926 | 901.3 | 925.9 | 913.7 | 913.2 | 903.2 | 912.7 | 888.6 | 923.3 | 912 | 925.2 | 893.1 | 937.7 | 994.4 | 924 | 920.2 | 919 | 924.3 | 925.2 | 921.3 | 935.8 | 920 | 891.5 | 966.2 | 876.2 | 807.6 | 925.8 | 852.8 | 910 | 918.8 | 902.1 | 927.2 | 919.4 | 913.2 | 891.3 | 913.8 | 918.5 | 926.9 | 965.4 | 931.6 | 861.1 | 820.2 | 835.3 | 140 | 781.8 | 824.7 | 831.4 | 834.3 | 839.7 | 847.9 | 839.5 | 830.6 | 839.4 | 850.3 | 798.4 | 724 | 875.2 | 847.5 | 844.4 | 851.5 | 844.4 | 844.7 | 844.4 | 844.2 | 843.5 | 838.3 | 848.5 | 836.5 | 842.2 | 798.4 | 795.9 | 800.1 | 919.7 | 896.6 | 814.1 | 927.7 | 927 | 928.3 | 966 | 936.2 | 1023.6 | 936.4 | 868.6 | 880 | 841.5 | 906.1 | 859 | 974.2 | 811.4 | 822.9 | 902.6 | 777.8 | 729.8 | 952.8 | 941.7 | 982.8 | 959.8 | 939.6 | 946.2 | 1032.7 | 1066.2 | 873 | 862.3 | 802.2 | 802.6 | 796.7 | 828.2 | 810.1 | 833.9 | 815.6 | 799.6 | 803.1 | 806.7 | 838.2 | 837.8 | 833.6 | 835.4 | 812 | 815 | 802.6 | 778 | 798.1 | 792.2 | 349.8 | 346.6 | 836.5 | 833 | 853.8 | 846.5 | 834.8 | 838.3 | 845.8 | 878.2 | 892.4 | 919.1 | 873 | 924.6 | 965.1 | 912 | 922.9 | 886.5 | 929 | 925.1 | 887.7 | 957.2 | 940.3 | 866.1 | 948.2 | 944.9 | 722.5 | 720.5 | 914.9 | 767.7 | 878.7 | 813.8 | 820.4 | 812.4 | 814.1 | 789.9 | 798.4 | 821.9 | 804.6 | 794.3 | 820.1 | 891 | 815 | 825.9 | 782.5 | 773.1 | 772.7 | 813.5 | 821.9 | 824.5 | 820.7 | 826.4 | 887.6 | 820.5 | 814.7 | 827.4 | 821.6 | 742.4 | 821.3 | 825.5 | 789.1 | 781.4 | 794.5 | 879.3 | 782.5 | 819.8 | 815.9 | 811.8 | 771.6 | 740.9 | 793.8 | 857.2 | 767.3 | 780.1 | 829 | 824.5 | 804.7 | 815.7 | 821.9 | 824.3 | 869.6 | 770.8 | 777.7 | 791.7 | 791.7 | 794 | 794.8 | 800.9 | 825.9 | 817.6 | 800.4 | 810.8 | 818 | 825.3 | 816.9 | 826.4 | 808.5 | 776.1 | 779 | 826.9 | 739.3 | 791 | 789.5 | 849.2 | 828.9 | 834.1 | 780.2 | 871.4 | 822.6 | 862.4 | 780.9 | 825 | 784 | 786.7 | 746.6 | 801 | 792.9 | 783.3 | 31.82 | 39.19 | 0 | 0 | 4.18 | 4.13 | 0 | 0 | 90916480 | 265297 | 92326290 | 309554 | 76134240 | 159375 | 90524820 | 139255 | 861110 | 10250 | 142310 | 790 | 70000 | 110 | 71190 | 73 | 69340 | 252 | 68770 | 379 | 140000 | 0 | 138000 | 2000 | 279300 | 278000 | 11.6 | 4.18 | 4.13 |  | 39.19 | 0 | 284710.2
2025-06-28 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:41 | 17:36 | 517.1 | 476.1 | 543.6 | 543.2 | 540.6 | 522.3 | 550.3 | 533.8 | 545.4 | 550.8 | 548.9 | 545.9 | 550.1 | 550.3 | 553.9 | 551.8 | 520.6 | 523.9 | 547.9 | 552.7 | 568.8 | 562.9 | 567.4 | 567.6 | 565.1 | 565.4 | 566.7 | 567.1 | 571.8 | 569.7 | 565.8 | 568.7 | 540.2 | 508.8 | 514.1 | 517.5 | 526.8 | 523.4 | 542.8 | 519.3 | 537.9 | 579.2 | 608 | 577.4 | 577 | 595.1 | 638 | 629.2 | 675.3 | 605.6 | 580 | 573.3 | 568.3 | 595.1 | 586 | 592.6 | 606.3 | 562.4 | 497.7 | 565.1 | 547 | 513.9 | 557.2 | 1279 | 1266.8 | 1278.5 | 1279.7 | 1276.3 | 1278 | 1251.5 | 1284.3 | 1274.8 | 1253 | 1225.6 | 1253.7 | 1214.6 | 1216.7 | 1244.3 | 1277.3 | 1290.8 | 1254.1 | 1326.7 | 1295.9 | 1229.7 | 1274.4 | 1226 | 1215.8 | 1249.3 | 1284.2 | 1278.8 | 1278.5 | 1203.9 | 1236.7 | 1257.6 | 1266.7 | 1259.2 | 1349 | 1274.1 | 1263.1 | 1166.3 | 1209.1 | 1265.1 | 1241 | 1258.6 | 1309 | 1258.2 | 1283.5 | 1270.1 | 1262.1 | 1298.5 | 1291.4 | 1289.8 | 1188.1 | 1203.1 | 1265.3 | 1281.8 | 1272.2 | 1289.7 | 1288 | 1297.8 | 1285.4 | 1279.7 | 1217.1 | 1235.3 | 1303.9 | 1301.1 | 1275 | 1304.9 | 1277.3 | 1278.5 | 1268 | 1283.9 | 1273.1 | 1287.8 | 1267.6 | 1283.7 | 1244.9 | 1303.6 | 1388.9 | 1289 | 1294.1 | 1289.2 | 1295.4 | 1305.4 | 1290.4 | 1307.9 | 1295 | 1255.9 | 1361.1 | 1232.7 | 1137 | 1291.6 | 1202 | 1277.4 | 1279.3 | 1237.3 | 1293.5 | 1288.2 | 1237.7 | 1263.6 | 1283.9 | 1219.7 | 1302.8 | 1331 | 1296 | 1243.4 | 1146.9 | 1159.9 | 1156.2 | 1158.9 | 1158.4 | 1163.2 | 1168.2 | 1182.3 | 1188.6 | 1178.5 | 1161.2 | 1165.6 | 1185.4 | 1116.8 | 1024.5 | 1224.5 | 1186.1 | 1184.1 | 1190.8 | 1184.6 | 1187.4 | 1185.8 | 1185.2 | 1190.8 | 1181.3 | 1192.3 | 1170.5 | 1176.1 | 1123.1 | 1115.4 | 1129.3 | 1286.6 | 1253.9 | 1148.1 | 1288.9 | 1291.3 | 1302.4 | 1342.6 | 1300.7 | 1426.3 | 1303.3 | 1214.7 | 1237.6 | 1175.9 | 1269.4 | 1189 | 1354.9 | 1140.6 | 1151.7 | 1250.1 | 1101.6 | 1037.9 | 1317.4 | 1306.2 | 1366.1 | 1334.7 | 1297.8 | 1305.9 | 1438.7 | 1479.6 | 1224.8 | 1215.6 | 1132 | 1133.2 | 1133.2 | 1181.3 | 1145 | 1175.9 | 1136.3 | 1128.1 | 1134 | 1135 | 1179.3 | 1176.1 | 1175.3 | 1171.5 | 1134.7 | 1134 | 1126.4 | 1106.3 | 1118.1 | 1100.1 | 1116 | 1140.4 | 1174.9 | 1172.4 | 1186.1 | 1192.7 | 1173.5 | 1175.5 | 1188.5 | 1181.8 | 1220 | 1296.7 | 1236.1 | 1291.9 | 1350.8 | 1291.7 | 1296.1 | 1251.5 | 1312.5 | 1298.1 | 1248.9 | 1354.4 | 1320.5 | 1227.6 | 1323.4 | 1338.8 | 1033.2 | 1029.5 | 1286.2 | 1093 | 1239.9 | 1152.3 | 1154.1 | 1153.4 | 1153.2 | 1122.4 | 1136.5 | 1159.1 | 1138.3 | 1131.5 | 1162.9 | 1241.8 | 1154.1 | 1160.2 | 1107.8 | 1102.3 | 1105.9 | 1155.4 | 1162.4 | 1165.3 | 1164.2 | 1163.1 | 1237.6 | 1155.3 | 1150.9 | 1166.4 | 1158.2 | 1055.2 | 1158.3 | 1162.9 | 1113.1 | 1107.1 | 1118.5 | 1240.6 | 1108.9 | 1157.2 | 1152.9 | 1147 | 1096 | 1034.4 | 1156.4 | 1205 | 1096.7 | 1104.6 | 1172.8 | 1159.7 | 1147.1 | 1150.7 | 1157.4 | 1164.1 | 1219.5 | 1099.3 | 1116.3 | 1133.7 | 1131.9 | 1132 | 1133.5 | 1142.5 | 1173.7 | 1176 | 1134.8 | 1168.9 | 1167.9 | 1172.1 | 1166.9 | 1180.4 | 1160.1 | 1121.5 | 1124 | 1174.8 | 1061.2 | 1120.1 | 1130.3 | 1217.4 | 1176.6 | 1182.5 | 1128 | 1236.2 | 1183.1 | 1211.1 | 1111.4 | 1175 | 1169 | 1170 | 1071.8 | 1123.9 | 1127.8 | 1117.6 | 32.33 | 41.77 | 0 | 0 | 6.04 | 5.69 | 0 | 0 | 91013890 | 265407 | 92427080 | 309600 | 76232940 | 159548 | 90622780 | 139459 | 862090 | 10250 | 143290 | 790 | 97410 | 110 | 100790 | 46 | 98700 | 173 | 97960 | 204 | 196000 | 0 | 196000 | 0 | 394860 | 392000 | 12.9167 | 6.04 | 5.69 |  | 41.77 | 0 | 402152.8
2025-06-29 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:37 | 17:55 | 478.3 | 441.9 | 505.1 | 506 | 503.2 | 483 | 513.3 | 496.5 | 507.8 | 512.6 | 511.9 | 508.3 | 512 | 511.9 | 515.7 | 514.1 | 483.4 | 488.1 | 510.8 | 515.2 | 530.6 | 525.5 | 531.8 | 529.6 | 527.6 | 528.3 | 530.4 | 528.4 | 533.1 | 532.5 | 529.1 | 531 | 504.8 | 472.9 | 477.7 | 481.1 | 489 | 486.6 | 506.1 | 483.8 | 502.8 | 541.6 | 571.1 | 538.4 | 539.8 | 558.6 | 601.2 | 592.9 | 640.4 | 567.8 | 542.8 | 534.7 | 529.8 | 558.1 | 548.8 | 555.2 | 573.2 | 526.6 | 465.5 | 530.9 | 510 | 478.5 | 524 | 1203.7 | 1189.1 | 1183.7 | 1191.5 | 1199.2 | 1185.7 | 1184.8 | 1206.2 | 1204.6 | 1188.3 | 1158.6 | 1187 | 1134 | 1134.8 | 1195.5 | 1201.9 | 1196.8 | 1189.6 | 1255 | 1204.8 | 1157.1 | 1209.7 | 1149.3 | 1149.6 | 1187.6 | 1193.4 | 1199.7 | 1202.2 | 1133.4 | 1168.7 | 1172.8 | 1185.5 | 1191.8 | 1286.6 | 1177.9 | 1189.6 | 1128.8 | 1128.9 | 1196.9 | 1158.1 | 1201.5 | 1251.4 | 1193.7 | 1206.7 | 1191.5 | 1188 | 1214.7 | 1212.7 | 1221.7 | 1108.3 | 1147.1 | 1194.4 | 1222.3 | 1206.6 | 1217.9 | 1214.6 | 1214 | 1212.6 | 1210.9 | 1147 | 1159.3 | 1217.3 | 1214.6 | 1188.7 | 1217.9 | 1179.4 | 1204.4 | 1194.2 | 1201.7 | 1206.9 | 1216.6 | 1197.5 | 1212.5 | 1169.3 | 1241 | 1324 | 1212.2 | 1216.4 | 1223.7 | 1226.3 | 1221.6 | 1217.7 | 1235.9 | 1224 | 1181.4 | 1278.8 | 1135 | 1063.5 | 1222.1 | 1131.1 | 1208 | 1209.1 | 1217.7 | 1214.4 | 1214.3 | 1209.1 | 1210.4 | 1209.5 | 1220.6 | 1224.1 | 1268.4 | 1227 | 1165.6 | 1110 | 1125 | 1116.5 | 1117.6 | 1112 | 1112.9 | 1110.4 | 1120.3 | 1125.9 | 1118.3 | 1128.6 | 1128.9 | 1131.5 | 1073.1 | 972.4 | 1172.4 | 1130.6 | 1126.6 | 1129 | 1121.4 | 1125.2 | 1121.6 | 1128.2 | 1129.6 | 1123.8 | 1132.1 | 1108.9 | 1113.4 | 1065 | 1057.6 | 1063.9 | 1234.4 | 1202.6 | 1091.6 | 1251.2 | 1258.9 | 1269.8 | 1298.4 | 1265.6 | 1389.2 | 1273.7 | 1187.5 | 1199.9 | 1146.7 | 1244.2 | 1167 | 1311.9 | 1104.5 | 1105.4 | 1223.6 | 1050.4 | 990 | 1303.1 | 1292.7 | 1340.5 | 1318.1 | 1280.2 | 1293.5 | 1414 | 1452.6 | 1167.7 | 1156.2 | 1070.4 | 1079.2 | 1067.2 | 1113.6 | 1079.8 | 1111.3 | 1090.9 | 1081.5 | 1078.8 | 1074.2 | 1116.4 | 1116.7 | 1111.5 | 1113.1 | 1091 | 1100 | 1083.2 | 1064.2 | 1077.4 | 1057.6 | 1070.1 | 1093.3 | 1121.4 | 1123.4 | 1141.4 | 1144.5 | 1117.7 | 1120.7 | 1135 | 1174.7 | 1201.9 | 1224.5 | 1164.6 | 1229.6 | 1287.9 | 1218.6 | 1226.4 | 1179.6 | 1232.6 | 1224.2 | 1174.7 | 1279.9 | 1255.5 | 1147 | 1257.9 | 1257.8 | 962.2 | 955.3 | 1211.9 | 1018.8 | 1166.6 | 1089.4 | 1089.4 | 1088.4 | 1088.2 | 1058.8 | 1070.2 | 1095.5 | 1079.1 | 1070.3 | 1103 | 1157.4 | 1091.5 | 1099.6 | 1048.6 | 1032.1 | 1034.7 | 1084.4 | 1091.7 | 1094 | 1094.3 | 1092.2 | 1159 | 1086.1 | 1084.7 | 1095 | 1088.5 | 987.7 | 1092.7 | 1101.5 | 1048.7 | 1039.4 | 1053.1 | 1179.6 | 1045.2 | 1095 | 1090 | 1087.6 | 1033.4 | 973.6 | 1096.4 | 1142 | 1033.2 | 1041.7 | 1108.1 | 1097.9 | 1083.7 | 1088.3 | 1094.3 | 1095.7 | 1156.5 | 1032 | 1051.7 | 1072 | 1068.9 | 1069 | 1070.3 | 1093.7 | 1118.1 | 1113.5 | 1076 | 1108 | 1111.2 | 1108.6 | 1109.1 | 1115.9 | 1096.3 | 1056.1 | 1060 | 1109.4 | 994.6 | 1054.8 | 1062.1 | 1150.9 | 1109.1 | 1112 | 1057.8 | 1168.9 | 1111.2 | 1146.5 | 1041.7 | 1105.6 | 1046 | 1060.2 | 1002.4 | 1056.9 | 1057.5 | 1057.8 | 31.18 | 39.68 | 0 | 0 | 5.3 | 5.1 | 0 | 0 | 91105740 | 265498 | 92522720 | 309645 | 76327670 | 159733 | 90715290 | 139679 | 863030 | 10260 | 144220 | 790 | 91850 | 91 | 95640 | 45 | 94730 | 185 | 92510 | 220 | 188000 | 2000 | 186000 | 0 | 374730 | 374000 | 13.3 | 5.3 | 5.1 |  | 39.68 | 0 | 380887.6
2025-06-30 | 2026 | 2025 |  |  | Jun-25 | 30 | 91870 | 4:47 | 17:49 | 506 | 490.8 | 540.5 | 539.6 | 533.6 | 515.8 | 552.8 | 531.7 | 539.7 | 543.3 | 555.6 | 548.3 | 543.4 | 546 | 548.1 | 548.7 | 516.1 | 522.1 | 556 | 556.1 | 582.3 | 572.5 | 571.9 | 567.8 | 578 | 579.3 | 578 | 572.9 | 591 | 586.2 | 580.7 | 578.4 | 531.5 | 498.8 | 506.1 | 510.5 | 519 | 516.7 | 536.2 | 511.4 | 530.9 | 573 | 598.8 | 568.8 | 569.9 | 586.3 | 627.6 | 621 | 664.1 | 609.6 | 575.2 | 570.8 | 569.7 | 600.8 | 592.6 | 596.5 | 608.6 | 560.5 | 500.4 | 565.6 | 557 | 517.7 | 554.4 | 1310.8 | 1302.9 | 1336.7 | 1311.7 | 1283 | 1291.4 | 1264.2 | 1308 | 1278.8 | 1255.5 | 1224.9 | 1241.2 | 1204.6 | 1199 | 1238.1 | 1336.3 | 1364.3 | 1349 | 1377.8 | 1374.2 | 1274.4 | 1316.3 | 1285.2 | 1252.3 | 1290.3 | 1352.3 | 1315.2 | 1296.5 | 1238 | 1272.1 | 1317.6 | 1329.2 | 1306.4 | 1391.1 | 1346.1 | 1258.8 | 1171.6 | 1203.2 | 1317.6 | 1312.4 | 1298.2 | 1386.5 | 1280 | 1264.1 | 1268.9 | 1276.6 | 1319.7 | 1320.8 | 1324.9 | 1145.1 | 1242.3 | 1294.9 | 1290.8 | 1296.3 | 1317.2 | 1371.6 | 1347.9 | 1302.2 | 1289.5 | 1238.2 | 1269.8 | 1324.7 | 1315.2 | 1302.3 | 1325.1 | 1263.1 | 1285.5 | 1268.3 | 1295.6 | 1267.5 | 1288.9 | 1260.3 | 1260.9 | 1252 | 1333.8 | 1390.1 | 1289.7 | 1269 | 1302.7 | 1297.9 | 1319.4 | 1285.4 | 1311.8 | 1234.5 | 1260.6 | 1336.3 | 1224.5 | 1123.3 | 1277.3 | 1186.9 | 1248.7 | 1254.7 | 1281.2 | 1301.7 | 1235.6 | 1238.2 | 1234.5 | 1274 | 1255.8 | 1293.5 | 1291.2 | 1263 | 1193.4 | 1237.2 | 1271.1 | 1261.5 | 1259.8 | 1254.8 | 1251.7 | 1249.3 | 1246.5 | 1244.7 | 1251.3 | 1265.9 | 1264.9 | 1276.6 | 1207.8 | 1103.8 | 1277.5 | 1268.5 | 1252.6 | 1246.3 | 1226.3 | 1226.5 | 1212.4 | 1229.5 | 1215.5 | 1210.7 | 1211.9 | 1170.4 | 1185.8 | 1137.3 | 1120.5 | 1149.9 | 1316.8 | 1321 | 1223.2 | 1374.4 | 1394.4 | 1438.1 | 1413.3 | 1387.2 | 1564.1 | 1396.5 | 1317.1 | 1362.9 | 1317.6 | 1433.7 | 1321 | 1396.7 | 1211.7 | 1199.6 | 1342.3 | 1159.2 | 1113.3 | 1433.1 | 1437.3 | 1510 | 1449.4 | 1422.7 | 1461.2 | 1530.4 | 1629.3 | 1189.6 | 1176.5 | 1118.6 | 1112.3 | 1128.6 | 1171.7 | 1136.7 | 1170.1 | 1126.5 | 1117.6 | 1118.6 | 1127.5 | 1170.1 | 1167.3 | 1162.5 | 1165.6 | 1127.3 | 1143 | 1131.1 | 1114.5 | 1113.2 | 1129.8 | 1113.3 | 1158.6 | 1166.3 | 1177.7 | 1200.8 | 1227.6 | 1173.6 | 1156.6 | 1205.4 | 1298.2 | 1339.1 | 1369.7 | 1295 | 1348.5 | 1393.9 | 1243.6 | 1293.7 | 1274.7 | 1340 | 1321.6 | 1254.8 | 1341.8 | 1322.6 | 1258.2 | 1309.3 | 1357.1 | 1031 | 1032.1 | 1274.1 | 1101.4 | 1245.6 | 1281.2 | 1272.7 | 1261.1 | 1271.8 | 1221.4 | 1244.6 | 1267.7 | 1240.3 | 1237.1 | 1252.8 | 1280.9 | 1240.3 | 1231.4 | 1194.3 | 1191.7 | 1189.2 | 1231.2 | 1227 | 1228.9 | 1221.5 | 1215.9 | 1324.8 | 1209.9 | 1211.1 | 1200.6 | 1202.8 | 1125.3 | 1211.4 | 1218.6 | 1162.1 | 1152.4 | 1246.9 | 1338.9 | 1248.5 | 1289 | 1271.1 | 1259.6 | 1187.1 | 1125.2 | 1178.3 | 1277.8 | 1233.9 | 1253.3 | 1285.6 | 1300.3 | 1271.2 | 1258.2 | 1274.5 | 1246.4 | 1308.3 | 1196.8 | 1150 | 1197.4 | 1187.8 | 1212 | 1210 | 1218.9 | 1245.9 | 1256.9 | 1206.1 | 1241.3 | 1227.8 | 1236.4 | 1225 | 1237.2 | 1208.8 | 1183.8 | 1187 | 1247.4 | 1149.2 | 1185.7 | 1210.5 | 1314.4 | 1270.3 | 1275.2 | 1234.6 | 1312.2 | 1275.8 | 1324.9 | 1237.6 | 1273.6 | 1235 | 1208.7 | 1158.8 | 1218.5 | 1220.7 | 1193.4 | 33.35 | 43.29 | 0 | 0 | 6.01 | 5.73 | 0 | 0 | 91204510 | 265604 | 92624860 | 309698 | 76429540 | 159918 | 90820500 | 139861 | 864030 | 10260 | 145250 | 800 | 98770 | 106 | 102140 | 53 | 101870 | 185 | 105210 | 182 | 200000 | 0 | 206000 | 2000 | 407990 | 406000 | 13.0333 | 6.01 | 5.73 |  | 43.29 | 0 | 416348.1
2025-07-01 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | 4:49 | 17:43 | 504.9 | 492.8 | 533.8 | 533.8 | 527.9 | 509.7 | 542.3 | 523.9 | 531.1 | 536.9 | 541.7 | 537.4 | 536.6 | 537.7 | 540.1 | 539.2 | 508.3 | 514.4 | 540.4 | 544.7 | 561.7 | 555.7 | 556.5 | 555.2 | 559.2 | 558 | 557.5 | 555.2 | 567.2 | 563.7 | 557.7 | 557.6 | 523.1 | 492.7 | 500.1 | 501.8 | 511.2 | 510.2 | 524.2 | 504.6 | 522.3 | 563.2 | 591.4 | 562 | 558.8 | 576.6 | 622.1 | 611.7 | 668.5 | 590.8 | 560.9 | 551.9 | 547.8 | 580.8 | 572.9 | 580.6 | 599 | 552.1 | 488.3 | 556.8 | 535.4 | 501.1 | 541.8 | 1279.8 | 1270.2 | 1273.7 | 1283.6 | 1287.5 | 1268.5 | 1257.7 | 1277.9 | 1284.4 | 1260.4 | 1231.2 | 1259.6 | 1205.1 | 1203.5 | 1283 | 1279.5 | 1277.1 | 1264.3 | 1333.3 | 1279.1 | 1229.4 | 1285.4 | 1221 | 1223.4 | 1269.3 | 1284 | 1276.3 | 1280.1 | 1219.1 | 1256.1 | 1251.6 | 1268.1 | 1261.5 | 1365.7 | 1245.8 | 1258.8 | 1196.2 | 1201 | 1276.4 | 1226.2 | 1285.1 | 1270.7 | 1273.7 | 1297 | 1280.6 | 1287.3 | 1309.6 | 1304.5 | 1306.7 | 1160.8 | 1225.6 | 1264.5 | 1264.3 | 1281.4 | 1284.6 | 1286.6 | 1279.7 | 1270.9 | 1261.2 | 1192.9 | 1213.5 | 1262.8 | 1256.5 | 1232.8 | 1259.1 | 1246.4 | 1251.1 | 1229.7 | 1230 | 1249.7 | 1249.2 | 1235 | 1252.5 | 1197.3 | 1244.6 | 1332.3 | 1213.1 | 1221.8 | 1222.4 | 1227 | 1224.8 | 1221.1 | 1238.8 | 1197.2 | 1177.7 | 1279.4 | 1159.6 | 1061.7 | 1225.9 | 1125.4 | 1213.2 | 1224.3 | 1201.3 | 1232.2 | 1225.1 | 1227.3 | 1207.7 | 1217.9 | 1214 | 1223.6 | 1311.1 | 1252.2 | 1159 | 1088.6 | 1109 | 1099.4 | 1103.5 | 1106.4 | 1113.6 | 1118.9 | 1129.4 | 1136.1 | 1123.7 | 1102.7 | 1107.4 | 1130.1 | 1055.8 | 966.8 | 1169.9 | 1132.2 | 1129.9 | 1136.6 | 1129.7 | 1129.8 | 1129 | 1130.5 | 1128.2 | 1123.3 | 1130.7 | 1115.5 | 1124 | 1066.6 | 1060.4 | 1074.2 | 1210.1 | 1174.4 | 1066.6 | 1205.9 | 1209.5 | 1218 | 1261.9 | 1222.3 | 1342.3 | 1235.4 | 1149.4 | 1154.4 | 1108.8 | 1198.8 | 1151 | 1271.4 | 1056.6 | 1075.9 | 1175.6 | 1020.2 | 952.4 | 1262 | 1231.3 | 1273.6 | 1252.6 | 1219.3 | 1227.3 | 1348 | 1370.1 | 1161.4 | 1151.1 | 1071 | 1063.8 | 1070.6 | 1114.1 | 1075.4 | 1107.8 | 1077.7 | 1066.7 | 1070.6 | 1060 | 1084.4 | 1115.6 | 1081.9 | 1110.4 | 1072.4 | 1078 | 1056.2 | 1072.8 | 1062.2 | 1078.9 | 1062.6 | 1096.1 | 1116.1 | 1114.6 | 1102 | 1114.5 | 1099.2 | 1105.1 | 1126.6 | 1181.3 | 1213.2 | 1260.4 | 1193.1 | 1259.4 | 1308.3 | 1235 | 1248 | 1192.7 | 1255.3 | 1262.3 | 1202.1 | 1301.5 | 1274.3 | 1155.2 | 1285.8 | 1267.4 | 962.4 | 958.9 | 1235.1 | 1027.4 | 1189.4 | 1151.6 | 1152.7 | 1146.1 | 1150.8 | 1116.6 | 1128.6 | 1153.8 | 1130 | 1123.4 | 1150.9 | 1252 | 1140.5 | 1148 | 1096.6 | 1094.2 | 1095 | 1148.3 | 1156.6 | 1162.8 | 1164.8 | 1159.4 | 1253.7 | 1140.5 | 1140.3 | 1143.3 | 1137.7 | 1039.4 | 1138.8 | 1148.6 | 1086.8 | 1077.7 | 1103.4 | 1229.9 | 1115.1 | 1157.5 | 1152.3 | 1145.3 | 1088.2 | 1023.2 | 1083.7 | 1197.5 | 1089.7 | 1102 | 1164.2 | 1138 | 1138.8 | 1142.2 | 1147.2 | 1114.1 | 1216 | 1090.3 | 1058.2 | 1116.7 | 1095.1 | 1109 | 1120.7 | 1119.4 | 1153.7 | 1144.8 | 1120.3 | 1144.5 | 1153.3 | 1156 | 1154.8 | 1161.8 | 1144.4 | 1102.8 | 1105 | 1160.3 | 1037.9 | 1100.3 | 1109.8 | 1186.1 | 1146.9 | 1156.7 | 1092.5 | 1219.3 | 1146.7 | 1195.5 | 1084.5 | 1147.9 | 1094.5 | 1104.5 | 1047.2 | 1112.6 | 1109.1 | 1108.2 | 30.82 | 39.25 | 0 | 0 | 5.45 | 5.29 | 0 | 0 | 91301490 | 265718 | 92721420 | 309816 | 76522710 | 160003 | 90916340 | 139983 | 864990 | 10270 | 146190 | 800 | 96980 | 114 | 96560 | 118 | 93170 | 85 | 95840 | 122 | 192000 | 2000 | 188000 | 0 | 382550 | 380000 | 12.9 | 5.45 | 5.29 |  | 39.25 | 0 | 390721.7
2025-07-02 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | 4:47 | 17:53 | 422.7 | 410.3 | 448.4 | 446.5 | 436.3 | 418.1 | 458.1 | 439.3 | 440.3 | 447.8 | 458.7 | 451.7 | 449.1 | 451.4 | 454.9 | 459.8 | 427.9 | 437.5 | 460.6 | 462.3 | 480.7 | 476.7 | 476.4 | 477.1 | 478.8 | 480.9 | 482 | 479.9 | 489.5 | 488.4 | 481.9 | 479.4 | 439.8 | 410 | 415.7 | 421.4 | 433.3 | 433 | 442.5 | 429.4 | 444.8 | 479.5 | 500.5 | 480.2 | 481.2 | 495.2 | 536.1 | 529.3 | 575.8 | 513.8 | 489.1 | 484 | 482.6 | 507.1 | 497.8 | 502.5 | 513.8 | 476.9 | 422 | 480.2 | 463.5 | 434.6 | 470.5 | 1082.3 | 1071.6 | 1067 | 1071.4 | 1078.6 | 1063.9 | 1065.1 | 1080.7 | 1074.7 | 1060.1 | 1028.6 | 1055.6 | 1010 | 1006.5 | 1101.6 | 1108.9 | 1110.1 | 1084.5 | 1147.6 | 1102.5 | 1053.5 | 1098.3 | 1015.4 | 1039.6 | 1075 | 1079.5 | 1090.9 | 1088.8 | 1045 | 1077.5 | 1098.2 | 1105.2 | 1118 | 1205.5 | 1110.2 | 1115.3 | 1001.3 | 1045.9 | 1103.2 | 1077.1 | 1106.7 | 1165.9 | 1082.6 | 1101.8 | 1071.7 | 1085.7 | 1102.5 | 1094.3 | 1106.8 | 1006.9 | 1038.8 | 1087.8 | 1111.8 | 1107.4 | 1113.9 | 1123.4 | 1117.1 | 1097.4 | 1095.7 | 1042.7 | 1056.7 | 1115.5 | 1115.7 | 1097.2 | 1130 | 1103.1 | 1107.8 | 1092.4 | 1098 | 1109.6 | 1114 | 1094.1 | 1101.8 | 1071.2 | 1103 | 1177.4 | 1081.9 | 1087.3 | 1091.1 | 1098.5 | 1108 | 1096.5 | 1122.9 | 1115.5 | 1074.6 | 1157.7 | 1053.8 | 968.4 | 1108 | 1024.8 | 1094.4 | 1103.5 | 1107.2 | 1111 | 1109.1 | 1101.1 | 1113.1 | 1108 | 1088.9 | 1121.7 | 1154.4 | 1119.2 | 1061.5 | 983.4 | 995.7 | 983.9 | 983 | 981.7 | 986.6 | 989.1 | 992.5 | 1008.7 | 1000.5 | 992.5 | 998 | 1009.1 | 949.9 | 863.4 | 1035.3 | 1010.9 | 1004.2 | 1015.4 | 1007.8 | 1010.3 | 1013.2 | 1005.6 | 1012.6 | 1000.1 | 1021.9 | 1015.9 | 1016.1 | 969.1 | 967.1 | 964.5 | 1080.4 | 1045.4 | 932.5 | 1090.5 | 1093.4 | 1095.6 | 1136.4 | 1106.9 | 1213.9 | 1112.5 | 1037.6 | 1019 | 1006.3 | 1056.9 | 1016 | 1140.5 | 946.6 | 963.4 | 1040.1 | 911.8 | 857.9 | 1133.8 | 1121.1 | 1159.4 | 1140 | 1107.5 | 1120.2 | 1213.8 | 1250.3 | 1072.3 | 1060 | 986.6 | 985.6 | 997 | 1025.5 | 1004 | 1025.3 | 994.7 | 981.2 | 985.8 | 987.7 | 1012.4 | 1021.7 | 1009 | 1019.3 | 980.1 | 979 | 954.7 | 962 | 970 | 968.7 | 974.7 | 986.3 | 1018.9 | 1007.8 | 1007.6 | 1003.4 | 1009.3 | 1007.1 | 1010.5 | 1120.7 | 1135.9 | 1155.3 | 1102.2 | 1155.3 | 1198.9 | 1127.5 | 1139.3 | 1090.8 | 1131.7 | 1123.9 | 1080.8 | 1181.7 | 1163.9 | 1065.5 | 1170.6 | 1162.8 | 893.6 | 882.4 | 1122.1 | 945.7 | 1077 | 1032.3 | 1030.2 | 1021.3 | 1025.8 | 995.2 | 1007.2 | 1029.5 | 1013.3 | 997.3 | 1029.2 | 1110.9 | 1015.9 | 1029.5 | 988.6 | 974.7 | 974.7 | 1023.7 | 1029.8 | 1036.3 | 1030.4 | 1032.9 | 1107.8 | 1007.5 | 1007.4 | 1009.1 | 1007.8 | 921.6 | 1010.5 | 1028 | 976.5 | 967.2 | 993.1 | 1112.4 | 1011.9 | 1050.5 | 1032.6 | 1032 | 990.5 | 943.8 | 1030.6 | 1110.6 | 996.4 | 1015.8 | 1065.4 | 1055.5 | 1046.8 | 1062.8 | 1059.9 | 1043.3 | 1121.8 | 1009.7 | 988.4 | 1047.3 | 1045.2 | 1046 | 1049.4 | 1083.7 | 1110.7 | 1100.2 | 1072 | 1092.2 | 1094.3 | 1101.5 | 1093.2 | 1102.8 | 1084.2 | 1037.8 | 1034 | 1088.4 | 979.5 | 1041.8 | 1050.5 | 1143.2 | 1110.1 | 1114.9 | 1051.7 | 1160.7 | 1103.1 | 1144.4 | 1047 | 1104.1 | 1050 | 1056.6 | 1000.6 | 1067.8 | 1053 | 1046.5 | 30.75 | 38.79 | 0 | 0 | 4.99 | 4.91 | 0 | 0 | 91384580 | 265843 | 92807700 | 309846 | 76607460 | 160158 | 91004550 | 140146 | 865830 | 10270 | 147050 | 810 | 83090 | 125 | 86280 | 30 | 84750 | 155 | 88210 | 163 | 168000 | 0 | 172000 | 2000 | 342330 | 340000 | 13.1 | 4.99 | 4.91 |  | 38.79 | 0 | 349612.5
2025-07-03 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | 5:23 | 17:48 | 539.8 | 526.3 | 568.8 | 567.3 | 562.7 | 544.7 | 572.7 | 554.3 | 564.5 | 571.1 | 569.3 | 564.6 | 572.8 | 568.1 | 574.5 | 569.6 | 537.1 | 536.1 | 562.4 | 567 | 583.5 | 576.7 | 580.4 | 578.9 | 577.1 | 578.3 | 580.2 | 577.8 | 583.3 | 581.7 | 578.6 | 578.7 | 567.4 | 530.9 | 534.1 | 537.7 | 548.9 | 543.9 | 567.9 | 543.9 | 567.2 | 609.4 | 637.8 | 606.5 | 607.3 | 625.6 | 665.1 | 653 | 687.5 | 616.4 | 599.2 | 589.1 | 579.4 | 600.8 | 592 | 602.4 | 619.1 | 577.3 | 506.9 | 571.3 | 557.5 | 520.1 | 582.5 | 1256.1 | 1250.9 | 1309 | 1260.7 | 1252.8 | 1263.5 | 1235.1 | 1280.9 | 1250 | 1246.6 | 1212.3 | 1220.2 | 1212 | 1187.1 | 1233.4 | 1258.6 | 1314 | 1236.8 | 1299.5 | 1284.9 | 1213.6 | 1258.4 | 1198.7 | 1195.2 | 1236.3 | 1314.2 | 1260.8 | 1260.8 | 1209.1 | 1258.1 | 1269.2 | 1295.8 | 1262.4 | 1355.2 | 1309.4 | 1264.9 | 1213.1 | 1223.2 | 1260.5 | 1234.3 | 1255.8 | 1328.6 | 1255.6 | 1271.5 | 1248 | 1295.9 | 1275 | 1273.4 | 1269 | 1200.9 | 1184.4 | 1252 | 1252.2 | 1251.1 | 1264 | 1314.2 | 1284.1 | 1259.1 | 1247.2 | 1184.8 | 1211.4 | 1279.6 | 1309.3 | 1267 | 1298.9 | 1224.8 | 1263.2 | 1228.9 | 1285.3 | 1242.3 | 1268.3 | 1239 | 1252.6 | 1245.2 | 1336.1 | 1371 | 1270.5 | 1348.1 | 1265.8 | 1283.6 | 1351.7 | 1266.6 | 1350.9 | 1283.5 | 1237.8 | 1322.2 | 1262.8 | 1100.8 | 1276.7 | 1162.1 | 1224.7 | 1225.8 | 1242.1 | 1284 | 1243.8 | 1240.7 | 1224.3 | 1221.8 | 1232.1 | 1328.6 | 1291.9 | 1247.9 | 1191.8 | 1223.8 | 1221.2 | 1207.1 | 1207.3 | 1199.4 | 1207.8 | 1212.9 | 1221.1 | 1217.9 | 1205.3 | 1218.8 | 1222.5 | 1221.9 | 1165.7 | 1053.6 | 1250.8 | 1216.5 | 1206.5 | 1212.4 | 1206.5 | 1205.2 | 1210.4 | 1208.8 | 1213.5 | 1206.2 | 1215.6 | 1199.9 | 1212.9 | 1152.2 | 1145.4 | 1158.3 | 1265.3 | 1233.2 | 1113.2 | 1276.9 | 1282.8 | 1304 | 1330.1 | 1299.6 | 1503.6 | 1375.5 | 1253.3 | 1281.4 | 1182.7 | 1385.1 | 1216 | 1331.3 | 1120.3 | 1134 | 1221.4 | 1078 | 1011.5 | 1360.3 | 1376.8 | 1450.4 | 1393.2 | 1367.8 | 1410.2 | 1455.7 | 1561.9 | 1233.7 | 1218.7 | 1141.5 | 1140.3 | 1119.4 | 1174.8 | 1137.5 | 1175.6 | 1157.5 | 1142.1 | 1145.2 | 1126 | 1155.5 | 1196.7 | 1162.6 | 1192 | 1153.1 | 1159 | 1138.3 | 1170.1 | 1144.2 | 1175.8 | 1141.7 | 1188.7 | 1194.1 | 1191.7 | 1171.9 | 1212.5 | 1182.5 | 1198.2 | 1202 | 1197.3 | 1249.5 | 1253.6 | 1188 | 1258.9 | 1316.2 | 1225.4 | 1219.5 | 1222.1 | 1277.9 | 1259.6 | 1213.1 | 1327.4 | 1276.9 | 1183.1 | 1281.3 | 1297.3 | 987.3 | 984.6 | 1244.8 | 1056.5 | 1209.4 | 1150 | 1151.2 | 1147.4 | 1155.3 | 1121.4 | 1138 | 1152.3 | 1137 | 1123.5 | 1155.1 | 1228.9 | 1144.7 | 1152.3 | 1104.7 | 1102.6 | 1095.5 | 1146.3 | 1147.8 | 1155.1 | 1156.8 | 1150.3 | 1233 | 1139.3 | 1137.2 | 1146.3 | 1141.7 | 1045.8 | 1142.3 | 1153.1 | 1103.5 | 1097.6 | 1092.4 | 1252.7 | 1111.2 | 1154.7 | 1148.8 | 1147.9 | 1092.4 | 1032.1 | 1142.5 | 1190.5 | 1097.8 | 1114.3 | 1166.8 | 1150.3 | 1144.9 | 1148.1 | 1155.9 | 1136.7 | 1218.4 | 1096.7 | 1093.6 | 1115.6 | 1098.3 | 1123 | 1120.2 | 1188.9 | 1210.5 | 1124.3 | 1161.1 | 1181.8 | 1185.2 | 1182.3 | 1176.2 | 1180 | 1151.5 | 1109.4 | 1112 | 1170.1 | 1058.9 | 1116.7 | 1133.7 | 1246 | 1210.8 | 1205.6 | 1146.7 | 1249.1 | 1193.2 | 1245.3 | 1148.2 | 1193 | 1146.2 | 1132.9 | 1080.3 | 1146.6 | 1143.2 | 1123.5 | 30.98 | 41.52 | 0 | 0 | 6.14 | 5.95 | 0 | 0 | 91482990 | 265854 | 92908720 | 309943 | 76706350 | 160295 | 91102490 | 140312 | 866820 | 10270 | 148030 | 810 | 98410 | 11 | 101020 | 97 | 98890 | 137 | 97940 | 166 | 198000 | 0 | 196000 | 0 | 396260 | 394000 | 12.4167 | 6.14 | 5.95 |  | 41.52 | 0 | 403457.4
2025-07-04 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | 5:26 | 17:47 | 407.7 | 399.6 | 428.7 | 431 | 430.5 | 416 | 435.2 | 421.9 | 433.8 | 437.7 | 434.5 | 432.2 | 439.5 | 437.8 | 442.3 | 440.3 | 412.4 | 415.9 | 434 | 437.2 | 450 | 446.6 | 449.6 | 452.2 | 448 | 448.5 | 450 | 449.4 | 453.5 | 452.5 | 449.4 | 448.8 | 440.4 | 411.2 | 412.3 | 418.4 | 423.8 | 420.2 | 441.6 | 422.4 | 442.5 | 474 | 493.8 | 471.5 | 473.8 | 485.6 | 522.7 | 515.7 | 546.7 | 489.1 | 472.1 | 464.4 | 460.5 | 481.2 | 471.7 | 477.6 | 487.2 | 454 | 397.3 | 453.9 | 434.1 | 411.1 | 458.3 | 1014.4 | 1009.5 | 1019.9 | 1013.5 | 1013.8 | 1006.8 | 995.7 | 1021.1 | 1012.5 | 1000.7 | 975.9 | 969.9 | 960 | 946 | 1013.1 | 1013.5 | 1021.9 | 998.2 | 1053.3 | 1023.9 | 976.1 | 1014.7 | 971.5 | 963.7 | 1000.5 | 1025.6 | 1011.9 | 1015.8 | 967.2 | 995 | 1005.5 | 1017 | 1005.9 | 1072.8 | 1013.4 | 1003.2 | 955.7 | 967.6 | 1009.7 | 986.6 | 1011.8 | 1061 | 1004.3 | 1027.3 | 1009 | 1013.2 | 1035 | 1032.3 | 977.4 | 948.4 | 960.1 | 1003.1 | 1025.7 | 1012.4 | 1023.3 | 1035.9 | 1028.7 | 1022.4 | 1025.9 | 970.6 | 981.5 | 1050.3 | 1057.8 | 1026.4 | 1057.6 | 1006 | 1034.5 | 1029.5 | 1048.1 | 1037.2 | 1055.1 | 1035.5 | 1046.1 | 1000.1 | 1028.5 | 1090 | 1029 | 1027.5 | 1017.5 | 1024 | 1041.7 | 1032.9 | 1047.2 | 1021.4 | 1006 | 1097 | 1005 | 922.3 | 1041 | 973.6 | 1033.2 | 1041.5 | 1029.3 | 1055.7 | 1026.3 | 991.2 | 1045.3 | 1049.5 | 1049.7 | 1062.1 | 1089.2 | 1052.2 | 1006.6 | 908.5 | 923.1 | 915.2 | 917.2 | 915.9 | 919.1 | 918.6 | 923.5 | 931.2 | 926.7 | 921.2 | 926.3 | 936.6 | 884 | 808.2 | 964.7 | 936.8 | 934.7 | 938.6 | 931.4 | 934.1 | 934.9 | 933.2 | 936.1 | 929.6 | 939.1 | 940.3 | 937.4 | 893 | 894.7 | 892.9 | 1019.3 | 990.1 | 901.9 | 1023.1 | 1023.8 | 1033.6 | 1063.1 | 1034.4 | 1135.8 | 1041.2 | 970.2 | 953.9 | 942 | 1025.7 | 965 | 1072.2 | 891.8 | 908.7 | 970 | 865.1 | 816.7 | 1038.9 | 1056.2 | 1089.8 | 1070 | 1051.4 | 1058 | 1144.8 | 1178.9 | 973.4 | 965.7 | 907.4 | 902.8 | 915.3 | 943.2 | 924.6 | 946 | 908.3 | 900.9 | 905.1 | 898.6 | 940.7 | 942.2 | 936.7 | 940.8 | 904.2 | 899 | 895.3 | 918 | 894.7 | 915.8 | 899 | 909.1 | 936.6 | 931 | 937 | 942.1 | 932.4 | 931.3 | 938.7 | 983.2 | 994.3 | 1027.3 | 975.1 | 1024 | 1079.3 | 1007.1 | 1034.3 | 998.6 | 1051.3 | 1039.4 | 1003.8 | 1084.5 | 1054.7 | 983 | 1067.5 | 1081.6 | 841.2 | 831.4 | 1033 | 886.7 | 997.9 | 922.7 | 922.9 | 917 | 919.1 | 902.7 | 906.3 | 924 | 911.9 | 902.5 | 927.4 | 994 | 917.8 | 922.8 | 887.6 | 878.3 | 876 | 915.4 | 924.9 | 924.6 | 924.2 | 925.2 | 996 | 917.4 | 912.7 | 929.1 | 920.8 | 837.5 | 919 | 924.4 | 883 | 879.6 | 882.5 | 988.3 | 885.4 | 923.9 | 916.9 | 915 | 874.5 | 828.2 | 904.9 | 959.4 | 875.8 | 882.2 | 935.7 | 924.1 | 912.6 | 921 | 924.4 | 913.2 | 971.9 | 875.3 | 863.1 | 899.1 | 898.2 | 908 | 905.5 | 907.9 | 927.6 | 895.2 | 899.8 | 920.6 | 922.7 | 927.3 | 924.8 | 934.7 | 920.7 | 891.4 | 897 | 935.2 | 842.9 | 889.9 | 900 | 962.3 | 930.6 | 932 | 888.4 | 973.5 | 928.2 | 964.5 | 878.5 | 927.3 | 883.2 | 894.6 | 851.6 | 893.4 | 896 | 893.4 | 29.6 | 36.49 | 0 | 0 | 4.53 | 4.39 | 0 | 0 | 91560980 | 266085 | 92989390 | 310077 | 76785100 | 160427 | 91180220 | 140527 | 867610 | 10280 | 148810 | 820 | 77990 | 231 | 80670 | 134 | 78750 | 132 | 77730 | 215 | 158000 | 2000 | 156000 | 2000 | 315140 | 314000 | 12.35 | 4.53 | 4.39 |  | 36.49 | 0 | 320777.3
2025-07-05 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | 6:18 | 17:44 | 341.1 | 330.3 | 361.6 | 360.7 | 354.9 | 338.4 | 370.6 | 355.2 | 361.9 | 361.7 | 371.2 | 368.2 | 360.1 | 363.8 | 365.3 | 366.5 | 346 | 353.4 | 371.8 | 375 | 384.2 | 382.1 | 383.6 | 380.2 | 381.8 | 383.1 | 387 | 384.3 | 386.8 | 386.8 | 386.2 | 386.3 | 349.7 | 326.7 | 333 | 337.1 | 345.5 | 345.8 | 353.4 | 343.5 | 355.1 | 377.1 | 392.4 | 371.8 | 377.4 | 385.9 | 418.3 | 413.1 | 448.8 | 407.1 | 384.9 | 381.8 | 380.3 | 403.1 | 399.1 | 398.5 | 410.2 | 377.4 | 338.6 | 384.2 | 372.8 | 352 | 370.1 | 851.5 | 842.8 | 854.7 | 850.4 | 846.2 | 850.1 | 841.7 | 864.3 | 849.4 | 843.7 | 822.1 | 840.7 | 808.8 | 808.3 | 859.3 | 862.5 | 878.2 | 847.3 | 895.3 | 867.3 | 828.3 | 855.2 | 818.4 | 814.7 | 840.8 | 718.1 | 855.7 | 854.6 | 803.2 | 814.6 | 832.6 | 834 | 831 | 893.5 | 846.6 | 832.4 | 791 | 794.9 | 838.1 | 821 | 834 | 874.6 | 834.7 | 849.4 | 839.7 | 832.1 | 858.8 | 856.2 | 855.4 | 790.1 | 804.9 | 855.9 | 872.8 | 862.5 | 878.7 | 892.4 | 884.8 | 875.1 | 873.2 | 831.3 | 845.7 | 888.7 | 880.6 | 872.8 | 892.4 | 870 | 875.1 | 862.9 | 880.4 | 860.7 | 868.1 | 849.4 | 851.6 | 815.6 | 827.4 | 879.8 | 810.9 | 818.5 | 821.1 | 825.7 | 843.9 | 827.9 | 848 | 823.5 | 826 | 894.6 | 821.8 | 757.9 | 838.6 | 791.5 | 837.5 | 841.6 | 817.7 | 821.8 | 853.1 | 825.7 | 821.5 | 845.2 | 852.9 | 876.3 | 877.8 | 852.8 | 822.4 | 759.2 | 763 | 750.7 | 748.2 | 736 | 734.2 | 732.3 | 739.4 | 747.4 | 742.6 | 763.2 | 762.9 | 753.1 | 725.6 | 661.3 | 781.4 | 752.8 | 750.6 | 751.9 | 749 | 749.8 | 753.9 | 750.4 | 753.6 | 745.2 | 753.6 | 761.6 | 754.5 | 719.5 | 722.8 | 722.5 | 827.1 | 814.7 | 729.2 | 847.8 | 856.3 | 881 | 871.3 | 856.9 | 963.5 | 873.6 | 820.1 | 808.5 | 805.7 | 877.5 | 813 | 900 | 755.8 | 750 | 829.6 | 720.2 | 688.4 | 872.1 | 897.2 | 936.2 | 913 | 886.4 | 903.3 | 958.8 | 1000.1 | 780.3 | 775.7 | 729.6 | 728.6 | 733.4 | 752.5 | 742.4 | 755.3 | 731.9 | 726.5 | 728.3 | 732.1 | 756.5 | 754.5 | 761.6 | 759.3 | 731 | 723 | 721.9 | 740 | 718 | 739.1 | 727.3 | 754.2 | 755.8 | 750.1 | 755 | 771.7 | 745.8 | 748.7 | 751.8 | 859.8 | 878.2 | 896.1 | 847.9 | 884.6 | 923.9 | 873.9 | 798.6 | 856.5 | 896.7 | 883 | 852 | 909.4 | 861.3 | 822.8 | 881 | 890.9 | 686.6 | 683 | 859.8 | 734.7 | 848.1 | 779.1 | 782.7 | 754.4 | 776.4 | 772.7 | 769.8 | 789.5 | 786.7 | 776.5 | 803.4 | 851.3 | 796.1 | 797.2 | 770.3 | 752.6 | 753.2 | 785.9 | 791.6 | 792.1 | 788.7 | 791.5 | 839 | 785.7 | 784.5 | 788.2 | 785 | 726.8 | 787.9 | 797.6 | 760.1 | 749.7 | 755.5 | 828.3 | 750 | 783 | 780.5 | 781.9 | 755.9 | 714.5 | 793.5 | 818.6 | 740.2 | 746.7 | 796.1 | 786.3 | 777.8 | 782.2 | 779.1 | 771.6 | 827.8 | 747.8 | 743.7 | 763.5 | 763.9 | 751 | 764.7 | 751 | 768.7 | 769.2 | 751.6 | 769.6 | 768.6 | 772.8 | 775.4 | 780.4 | 773 | 751.3 | 748 | 782.1 | 706.5 | 742.3 | 748.9 | 790.8 | 765.9 | 772.1 | 737.5 | 807.7 | 773.1 | 799.4 | 730.1 | 772.9 | 733.1 | 747.6 | 708.4 | 743.9 | 745.8 | 741.3 | 29.27 | 35.81 | 0 | 0 | 3.71 | 3.58 | 0 | 0 | 91626040 | 266208 | 93055520 | 310153 | 76850360 | 160600 | 91246020 | 140725 | 868260 | 10280 | 149460 | 820 | 65060 | 123 | 66130 | 76 | 65260 | 173 | 65800 | 198 | 130000 | 0 | 130000 | 0 | 262250 | 260000 | 11.4333 | 3.71 | 3.58 |  | 35.81 | 0 | 266861.6
2025-07-06 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | 6:35 | 17:10 | 317.6 | 308.5 | 335.3 | 334.3 | 332.8 | 319.8 | 341.3 | 327.8 | 337.8 | 338.5 | 340.4 | 338.4 | 339 | 339.4 | 342.4 | 341.3 | 319.9 | 325.8 | 340.6 | 342.9 | 351.7 | 349.9 | 350.5 | 350.8 | 347.8 | 349.9 | 352.6 | 351.9 | 352.5 | 352 | 350.8 | 349.8 | 334.4 | 312.3 | 315 | 318.4 | 324.1 | 322.6 | 335 | 323.5 | 335.2 | 359.4 | 376.5 | 357.7 | 361 | 371 | 400.1 | 395.5 | 424.5 | 378.8 | 363 | 357.9 | 354.5 | 372.9 | 367.3 | 369.2 | 381.6 | 351.4 | 311 | 353.9 | 339.2 | 321.4 | 350.7 | 787.6 | 782.9 | 780.5 | 784.6 | 792.4 | 786.7 | 783.4 | 799.6 | 795.8 | 787.8 | 770.2 | 786 | 750.6 | 752.2 | 748.5 | 756.9 | 787.4 | 748.2 | 819.3 | 784.1 | 755.2 | 785.7 | 744.6 | 748.5 | 774.8 | 783 | 784.3 | 789.7 | 736.2 | 754 | 752.3 | 762.6 | 763.8 | 825.7 | 757.3 | 761 | 398.4 | 727.6 | 772.1 | 744.5 | 779.8 | 776.5 | 776.4 | 787.6 | 785.3 | 776.9 | 797.9 | 792.8 | 794.6 | 719.8 | 745.9 | 783.1 | 805 | 792 | 799.6 | 798.3 | 794.8 | 802.1 | 803.4 | 758.7 | 764.8 | 813.9 | 813 | 794.2 | 815.6 | 775.7 | 803.4 | 796.6 | 805.4 | 803.8 | 811.6 | 798.3 | 808.6 | 785.4 | 816.7 | 873.4 | 798.5 | 801.3 | 806.6 | 809 | 809.9 | 805 | 817.6 | 810.6 | 784.5 | 847.5 | 771.7 | 709.5 | 808.2 | 752.9 | 804.4 | 804.5 | 812 | 787.2 | 787.4 | 805.5 | 805.8 | 806.1 | 811.5 | 817.7 | 844.5 | 818.2 | 777.2 | 721.5 | 734.4 | 725.3 | 727.7 | 723.3 | 723.7 | 723 | 730 | 736.1 | 729.4 | 735.3 | 738.3 | 739.6 | 700.5 | 635.5 | 765.2 | 737.3 | 736.5 | 738.2 | 730.9 | 735 | 732.4 | 736.6 | 736.5 | 732 | 736 | 728.1 | 728.8 | 694.1 | 691 | 698.7 | 806.9 | 785.8 | 718.1 | 817.5 | 822.9 | 831.7 | 849.3 | 829.9 | 912.9 | 834.5 | 779.6 | 790.2 | 754.9 | 818.9 | 756 | 857.2 | 720.6 | 720.6 | 763.2 | 688 | 649.1 | 848.1 | 841.9 | 875 | 858.4 | 840.2 | 842.4 | 922.4 | 945.9 | 758 | 753.9 | 704.2 | 703.1 | 701.3 | 726.3 | 711.9 | 731.5 | 709.3 | 703.4 | 704.4 | 706.6 | 710.4 | 726.8 | 709.6 | 726.8 | 712.3 | 715 | 705.2 | 729.6 | 702.7 | 722 | 702.2 | 731.8 | 730.4 | 730.3 | 729.8 | 742.7 | 727 | 728.8 | 738.9 | 763.6 | 780.1 | 795.1 | 759.2 | 799.9 | 840.3 | 803.7 | 802.1 | 778 | 816.9 | 808.9 | 782.4 | 847.1 | 824.4 | 758.5 | 834.5 | 835.5 | 644 | 636.7 | 805.4 | 682.5 | 777.8 | 693.1 | 694.6 | 657.3 | 658.6 | 682.9 | 682.4 | 699.4 | 691.9 | 684.6 | 708.7 | 769 | 699.2 | 706.8 | 676.5 | 662.7 | 661.5 | 693.4 | 697.7 | 703.1 | 705.1 | 707.3 | 744.1 | 705.5 | 698.1 | 717.8 | 710.9 | 634.2 | 706 | 709.4 | 679.5 | 678.7 | 661.7 | 746.8 | 660.7 | 694.1 | 691.5 | 691.3 | 661.7 | 623 | 709.8 | 729.5 | 649.5 | 655.1 | 707.9 | 695 | 686.5 | 689 | 692.6 | 675.5 | 741.5 | 656.2 | 653.3 | 674.6 | 677.2 | 673 | 676.7 | 684.8 | 695.4 | 698.7 | 670.3 | 690.8 | 660.5 | 690.9 | 692 | 698.9 | 686.1 | 662.2 | 674 | 694.1 | 620.9 | 658.9 | 666.6 | 719.8 | 692.8 | 694.9 | 660.9 | 729.7 | 693.4 | 722.6 | 650.1 | 691.2 | 654 | 665.1 | 627.2 | 663.3 | 663.3 | 662 | 28.82 | 34.42 | 0 | 0 | 3.35 | 3.26 | 0 | 0 | 91685980 | 266314 | 93118580 | 310186 | 76912300 | 160737 | 91304460 | 140937 | 868870 | 10290 | 150060 | 830 | 59940 | 106 | 63060 | 33 | 61940 | 137 | 58440 | 212 | 122000 | 2000 | 120000 | 2000 | 243380 | 242000 | 10.5833 | 3.35 | 3.26 |  | 34.42 | 0 | 247589.6
2025-07-07 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-08 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-09 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-10 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-11 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-12 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-13 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-14 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-15 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-16 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-17 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-18 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-19 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-20 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-21 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-22 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-23 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-24 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-25 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-26 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-27 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-28 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-29 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-30 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-07-31 | 2026 | 2025 |  |  | Jul-25 | 31 | 91870 | [388 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Formulas:
Days = DAY(EOMONTH([Date],0))

## Basic Data (hidden)
Equipment | Affected DC Capacity | Plant Equivalent Weightage | Fault Category Plant BD sheet | IS Number | LT Number | String Type | Equipment | Inverter Number | Status | Plant capacity | LT Number
BLK1INV1 | 132 | 0.1437% | Module | BLK1 | ACCB1 | Str_Typ1(330*40) | Tx | INV1 | Open | 91870 | LT1
BLK1INV2 | 132 | 0.1437% | Cables | BLK2 | ACCB2 | Str_Typ2 (310*40) | MVP | INV2 | Close |  | LT2
BLK1INV3 | 132 | 0.1437% | String Fuses | BLK3 | ACCB3 | Str_Typ3(315*40) | Aux_Tx | INV3
BLK1INV4 | 132 | 0.1437% | ACCB | BLK4 | ACCB4 | Str_Typ4(450*56) | MCR_MVP_IC_1 | INV4
BLK1INV5 | 132 | 0.1437% | Inverter | BLK5 | ACCB5 | Str_Typ4(455*56) | MCR_MVP_IC_2 | INV5
BLK1INV6 | 132 | 0.1437% | IDT | BLK6 | ACCB6 | Str_Typ1(330*20) | MCR_MVP_IC_3 | INV6
BLK1INV7 | 132 | 0.1437% | PTR | BLK7 | ACCB7 | Str_Typ2 (310*20) | MCR_MVP_IC_4 | INV7
BLK1INV8 | 132 | 0.1437% | MV Panel | BLK8 | ACCB8 | Str_Typ3(315*20) | MCR_MVP_OG1 | INV8
BLK1INV9 | 132 | 0.1437% | Metering System Plant | BLK9 |  | Str_Typ4(450*26) | MCR_MVP_OG2 | INV9
BLK1INV10 | 132 | 0.1437% | Grid System | BLK10 |  | Str_Typ4(455*26) | PWR_TX1 | INV10
BLK1INV11 | 130.68 | 0.1422% | Metering System Grid | BLK11 |  |  | PWR_TX2 | INV11
BLK1INV12 | 132 | 0.1437% | WMS | BLK12 |  |  | 220KV_Line | INV12
BLK1INV13 | 132 | 0.1437% | MMS |  |  |  |  | INV13
BLK1INV14 | 125.4 | 0.1365% | Battery Charger_MCR |  |  |  | Line_Bay1 | INV14
BLK1INV15 | 132 | 0.1437% | IC_UPS |  |  |  | Line_Bay2 | INV15
BLK1INV16 | 132 | 0.1437% | IC_Auxiliary Tranformer |  |  |  |  | INV16
BLK1INV17 | 132 | 0.1437% | IC_Auxiliary DB |  |  |  |  | INV17
BLK1INV18 | 132 | 0.1437% | IC_SCADA Panel |  |  |  |  | INV18
BLK1INV19 | 132 | 0.1437% | Connectors |  |  |  |  | INV19
BLK1INV20 | 125.4 | 0.1365% | LT Panel |  |  |  |  | INV20
BLK1INV21 | 132 | 0.1437% | SS |  |  |  |  | INV21
BLK1INV22 | 132 | 0.1437% | Force Majeure |  |  |  |  | INV22
BLK1INV23 | 132 | 0.1437% | [5 empty] | INV23
BLK1INV24 | 132 | 0.1437% | [5 empty] | INV24
BLK1INV25 | 132 | 0.1437% | [5 empty] | INV25
BLK1INV26 | 131.67 | 0.1433% | [5 empty] | INV26
BLK1INV27 | 125.4 | 0.1365% | [5 empty] | INV27
BLK1INV28 | 132 | 0.1437% | [5 empty] | INV28
BLK1INV29 | 132 | 0.1437% | [5 empty] | INV29
BLK1INV30 | 132 | 0.1437% | [5 empty] | INV30
BLK1INV31 | 125.4 | 0.1365% | [5 empty] | INV31
BLK1INV32 | 132 | 0.1437%
BLK1INV33 | 138.16 | 0.1504%
BLK1INV34 | 144.24 | 0.157%
BLK1INV35 | 149.2 | 0.1624%
BLK1INV36 | 136.4 | 0.1485%
BLK1INV37 | 136.8 | 0.1489%
BLK1INV38 | 143.3 | 0.156%
BLK1INV39 | 140.16 | 0.1526%
BLK1INV40 | 136.8 | 0.1489%
BLK1INV41 | 125.4 | 0.1365%
BLK1INV42 | 137.9 | 0.1501%
BLK1INV43 | 125.4 | 0.1365%
BLK1INV44 | 125.4 | 0.1365%
BLK1INV45 | 142.9 | 0.1555%
BLK1INV46 | 132 | 0.1437%
BLK1INV47 | 125.4 | 0.1365%
BLK1INV48 | 144.9 | 0.1577%
BLK1INV49 | 132 | 0.1437%
BLK1INV50 | 138.6 | 0.1509%
BLK1INV51 | 125.4 | 0.1365%
BLK1INV52 | 125.4 | 0.1365%
BLK1INV53 | 132 | 0.1437%
BLK1INV54 | 125.6 | 0.1367%
BLK1INV55 | 148.8 | 0.162%
BLK1INV56 | 163.6 | 0.1781%
BLK1INV57 | 136.4 | 0.1485%
BLK1INV58 | 144.8 | 0.1576%
BLK1INV59 | 132 | 0.1437%
BLK1INV60 | 142.6 | 0.1552%
BLK1INV61 | 125.2 | 0.1363%
BLK1INV62 | 143.8 | 0.1565%
BLK1INV63 | 148.8 | 0.162%
BLK2INV1 | 289.8 | 0.3154%
BLK2INV2 | 289.8 | 0.3154%
BLK2INV3 | 288.9 | 0.3145%
BLK2INV4 | 289.8 | 0.3154%
BLK2INV5 | 289.8 | 0.3154%
BLK2INV6 | 289.35 | 0.315%
BLK2INV7 | 289.8 | 0.3154%
BLK2INV8 | 289.8 | 0.3154%
BLK2INV9 | 289.8 | 0.3154%
BLK2INV10 | 289.8 | 0.3154%
BLK2INV11 | 287.55 | 0.313%
BLK2INV12 | 289.8 | 0.3154%
BLK2INV13 | 277.2 | 0.3017%
BLK2INV14 | 277.2 | 0.3017%
BLK2INV15 | 289.8 | 0.3154%
BLK2INV16 | 289.8 | 0.3154%
BLK2INV17 | 289.8 | 0.3154%
BLK2INV18 | 289.8 | 0.3154%
BLK2INV19 | 302.4 | 0.3292%
BLK2INV20 | 289.8 | 0.3154%
BLK2INV21 | 277.2 | 0.3017%
BLK2INV22 | 289.8 | 0.3154%
BLK2INV23 | 277.2 | 0.3017%
BLK2INV24 | 277.2 | 0.3017%
BLK2INV25 | 289.35 | 0.315%
BLK2INV26 | 289.8 | 0.3154%
BLK2INV27 | 289.8 | 0.3154%
BLK2INV28 | 289.8 | 0.3154%
BLK3INV1 | 289.8 | 0.3154%
BLK3INV2 | 289.8 | 0.3154%
BLK3INV3 | 289.8 | 0.3154%
BLK3INV4 | 289.8 | 0.3154%
BLK3INV5 | 289.8 | 0.3154%
BLK3INV6 | 315 | 0.3429%
BLK3INV7 | 289.8 | 0.3154%
BLK3INV8 | 289.8 | 0.3154%
BLK3INV9 | 277.2 | 0.3017%
BLK3INV10 | 277.2 | 0.3017%
BLK3INV11 | 289.8 | 0.3154%
BLK3INV12 | 288.45 | 0.314%
BLK3INV13 | 289.8 | 0.3154%
BLK3INV14 | 289.8 | 0.3154%
BLK3INV15 | 289.8 | 0.3154%
BLK3INV16 | 289.8 | 0.3154%
BLK3INV17 | 289.8 | 0.3154%
BLK3INV18 | 289.8 | 0.3154%
BLK3INV19 | 289.8 | 0.3154%
BLK3INV20 | 289.8 | 0.3154%
BLK3INV21 | 289.8 | 0.3154%
BLK3INV22 | 264.6 | 0.288%
BLK3INV23 | 277.2 | 0.3017%
BLK4INV1 | 289.8 | 0.3154%
BLK4INV2 | 289.8 | 0.3154%
BLK4INV3 | 289.8 | 0.3154%
BLK4INV4 | 289.8 | 0.3154%
BLK4INV5 | 289.8 | 0.3154%
BLK4INV6 | 289.8 | 0.3154%
BLK4INV7 | 289.8 | 0.3154%
BLK4INV8 | 289.8 | 0.3154%
BLK4INV9 | 277.2 | 0.3017%
BLK4INV10 | 277.2 | 0.3017%
BLK4INV11 | 289.8 | 0.3154%
BLK4INV12 | 289.8 | 0.3154%
BLK4INV13 | 289.8 | 0.3154%
BLK4INV14 | 289.8 | 0.3154%
BLK4INV15 | 289.8 | 0.3154%
BLK4INV16 | 289.8 | 0.3154%
BLK4INV17 | 289.8 | 0.3154%
BLK4INV18 | 289.8 | 0.3154%
BLK4INV19 | 289.8 | 0.3154%
BLK4INV20 | 289.8 | 0.3154%
BLK4INV21 | 289.8 | 0.3154%
BLK4INV22 | 289.8 | 0.3154%
BLK4INV23 | 277.2 | 0.3017%
BLK5INV1 | 289.8 | 0.3154%
BLK5INV2 | 315 | 0.3429%
BLK5INV3 | 289.8 | 0.3154%
BLK5INV4 | 289.8 | 0.3154%
BLK5INV5 | 289.8 | 0.3154%
BLK5INV6 | 289.8 | 0.3154%
BLK5INV7 | 289.8 | 0.3154%
BLK5INV8 | 289.8 | 0.3154%
BLK5INV9 | 289.8 | 0.3154%
BLK5INV10 | 289.8 | 0.3154%
BLK5INV11 | 277.2 | 0.3017%
BLK5INV12 | 302.4 | 0.3292%
BLK5INV13 | 277.2 | 0.3017%
BLK5INV14 | 252 | 0.2743%
BLK5INV15 | 289.8 | 0.3154%
BLK5INV16 | 264.6 | 0.288%
BLK5INV17 | 289.8 | 0.3154%
BLK5INV18 | 289.8 | 0.3154%
BLK5INV19 | 289.8 | 0.3154%
BLK5INV20 | 289.8 | 0.3154%
BLK5INV21 | 289.8 | 0.3154%
BLK5INV22 | 289.8 | 0.3154%
BLK5INV23 | 289.8 | 0.3154%
BLK5INV24 | 289.8 | 0.3154%
BLK5INV25 | 289.8 | 0.3154%
BLK5INV26 | 289.8 | 0.3154%
BLK5INV27 | 302.4 | 0.3292%
BLK5INV28 | 289.8 | 0.3154%
BLK5INV29 | 277.2 | 0.3017%
BLK6INV1 | 264.6 | 0.288%
BLK6INV2 | 264.6 | 0.288%
BLK6INV3 | 264.6 | 0.288%
BLK6INV4 | 264.6 | 0.288%
BLK6INV5 | 264.6 | 0.288%
BLK6INV6 | 264.6 | 0.288%
BLK6INV7 | 264.6 | 0.288%
BLK6INV8 | 264.6 | 0.288%
BLK6INV9 | 264.6 | 0.288%
BLK6INV10 | 264.6 | 0.288%
BLK6INV11 | 264.6 | 0.288%
BLK6INV12 | 264.6 | 0.288%
BLK6INV13 | 264.6 | 0.288%
BLK6INV14 | 252 | 0.2743%
BLK6INV15 | 226.8 | 0.2469%
BLK6INV16 | 277.2 | 0.3017%
BLK6INV17 | 264.6 | 0.288%
BLK6INV18 | 264.6 | 0.288%
BLK6INV19 | 264.6 | 0.288%
BLK6INV20 | 264.6 | 0.288%
BLK6INV21 | 264.6 | 0.288%
BLK6INV22 | 264.6 | 0.288%
BLK6INV23 | 264.6 | 0.288%
BLK6INV24 | 264.6 | 0.288%
BLK6INV25 | 264.6 | 0.288%
BLK6INV26 | 264.6 | 0.288%
BLK6INV27 | 264.6 | 0.288%
BLK6INV28 | 264.6 | 0.288%
BLK6INV29 | 252 | 0.2743%
BLK6INV30 | 252 | 0.2743%
BLK6INV31 | 252 | 0.2743%
BLK7INV1 | 293.02 | 0.319%
BLK7INV2 | 278.04 | 0.3026%
BLK7INV3 | 254.8 | 0.2773%
BLK7INV4 | 292.74 | 0.3186%
BLK7INV5 | 293.02 | 0.319%
BLK7INV6 | 290.5 | 0.3162%
BLK7INV7 | 305.76 | 0.3328%
BLK7INV8 | 293.02 | 0.319%
BLK7INV9 | 318.5 | 0.3467%
BLK7INV10 | 293.02 | 0.319%
BLK7INV11 | 280.28 | 0.3051%
BLK7INV12 | 280.28 | 0.3051%
BLK7INV13 | 267.54 | 0.2912%
BLK7INV14 | 293.02 | 0.319%
BLK7INV15 | 329.7 | 0.3589%
BLK7INV16 | 305.76 | 0.3328%
BLK7INV17 | 203.84 | 0.2219%
BLK7INV18 | 254.8 | 0.2773%
BLK7INV19 | 279.72 | 0.3045%
BLK7INV20 | 216.58 | 0.2357%
BLK7INV21 | 254.8 | 0.2773%
BLK7INV22 | 305.76 | 0.3328%
BLK7INV23 | 304.36 | 0.3313%
BLK7INV24 | 304.36 | 0.3313%
BLK7INV25 | 304.92 | 0.3319%
BLK7INV26 | 305.48 | 0.3325%
BLK7INV27 | 304.92 | 0.3319%
BLK7INV28 | 329.28 | 0.3584%
BLK7INV29 | 330.26 | 0.3595%
BLK8INV1 | 280.28 | 0.3051%
BLK8INV2 | 280.28 | 0.3051%
BLK8INV3 | 254.8 | 0.2773%
BLK8INV4 | 254.8 | 0.2773%
BLK8INV5 | 254.8 | 0.2773%
BLK8INV6 | 267.54 | 0.2912%
BLK8INV7 | 254.8 | 0.2773%
BLK8INV8 | 267.54 | 0.2912%
BLK8INV9 | 254.8 | 0.2773%
BLK8INV10 | 254.8 | 0.2773%
BLK8INV11 | 254.8 | 0.2773%
BLK8INV12 | 254.8 | 0.2773%
BLK8INV13 | 267.54 | 0.2912%
BLK8INV14 | 267.54 | 0.2912%
BLK8INV15 | 267.54 | 0.2912%
BLK8INV16 | 267.54 | 0.2912%
BLK8INV17 | 254.8 | 0.2773%
BLK8INV18 | 254.8 | 0.2773%
BLK8INV19 | 254.8 | 0.2773%
BLK8INV20 | 267.54 | 0.2912%
BLK8INV21 | 254.8 | 0.2773%
BLK8INV22 | 267.54 | 0.2912%
BLK8INV23 | 254.8 | 0.2773%
BLK8INV24 | 267.54 | 0.2912%
BLK8INV25 | 267.54 | 0.2912%
BLK8INV26 | 267.54 | 0.2912%
BLK8INV27 | 267.54 | 0.2912%
BLK8INV28 | 267.54 | 0.2912%
BLK8INV29 | 267.54 | 0.2912%
BLK8INV30 | 267.54 | 0.2912%
BLK8INV31 | 267.54 | 0.2912%
BLK9INV1 | 280.28 | 0.3051%
BLK9INV2 | 292.88 | 0.3188%
BLK9INV3 | 293.02 | 0.319%
BLK9INV4 | 279.72 | 0.3045%
BLK9INV5 | 292.88 | 0.3188%
BLK9INV6 | 331.24 | 0.3606%
BLK9INV7 | 279.86 | 0.3046%
BLK9INV8 | 280 | 0.3048%
BLK9INV9 | 280.28 | 0.3051%
BLK9INV10 | 293.02 | 0.319%
BLK9INV11 | 293.02 | 0.319%
BLK9INV12 | 280.28 | 0.3051%
BLK9INV13 | 304.64 | 0.3316%
BLK9INV14 | 305.48 | 0.3325%
BLK9INV15 | 278.6 | 0.3033%
BLK9INV16 | 305.48 | 0.3325%
BLK9INV17 | 305.76 | 0.3328%
BLK9INV18 | 229.32 | 0.2496%
BLK9INV19 | 229.32 | 0.2496%
BLK9INV20 | 293.02 | 0.319%
BLK9INV21 | 242.06 | 0.2635%
BLK9INV22 | 280.28 | 0.3051%
BLK10INV1 | 264.6 | 0.288%
BLK10INV2 | 264.6 | 0.288%
BLK10INV3 | 264.6 | 0.288%
BLK10INV4 | 264.6 | 0.288%
BLK10INV5 | 264.6 | 0.288%
BLK10INV6 | 264.6 | 0.288%
BLK10INV7 | 264.6 | 0.288%
BLK10INV8 | 264.6 | 0.288%
BLK10INV9 | 264.6 | 0.288%
BLK10INV10 | 264.6 | 0.288%
BLK10INV11 | 289.8 | 0.3154%
BLK10INV12 | 264.6 | 0.288%
BLK10INV13 | 264.6 | 0.288%
BLK10INV14 | 252 | 0.2743%
BLK10INV15 | 252 | 0.2743%
BLK10INV16 | 252 | 0.2743%
BLK10INV17 | 262.8 | 0.2861%
BLK10INV18 | 262.8 | 0.2861%
BLK10INV19 | 263.7 | 0.287%
BLK10INV20 | 263.7 | 0.287%
BLK10INV21 | 263.7 | 0.287%
BLK10INV22 | 288.9 | 0.3145%
BLK10INV23 | 263.7 | 0.287%
BLK10INV24 | 263.7 | 0.287%
BLK10INV25 | 263.7 | 0.287%
BLK10INV26 | 263.7 | 0.287%
BLK10INV27 | 238.5 | 0.2596%
BLK10INV28 | 263.7 | 0.287%
BLK10INV29 | 264.6 | 0.288%
BLK10INV30 | 252 | 0.2743%
BLK10INV31 | 252 | 0.2743%
BLK11INV1 | 254.8 | 0.2773%
BLK11INV2 | 293.02 | 0.319%
BLK11INV3 | 252 | 0.2743%
BLK11INV4 | 267.54 | 0.2912%
BLK11INV5 | 267.54 | 0.2912%
BLK11INV6 | 267.54 | 0.2912%
BLK11INV7 | 252 | 0.2743%
BLK11INV8 | 242.06 | 0.2635%
BLK11INV9 | 267.54 | 0.2912%
BLK11INV10 | 280.28 | 0.3051%
BLK11INV11 | 254.8 | 0.2773%
BLK11INV12 | 254.8 | 0.2773%
BLK11INV13 | 267.54 | 0.2912%
BLK11INV14 | 267.54 | 0.2912%
BLK11INV15 | 267.54 | 0.2912%
BLK11INV16 | 267.54 | 0.2912%
BLK11INV17 | 267.54 | 0.2912%
BLK11INV18 | 267.54 | 0.2912%
BLK11INV19 | 279.37 | 0.3041%
BLK11INV20 | 254.8 | 0.2773%
BLK11INV21 | 254.8 | 0.2773%
BLK11INV22 | 254.8 | 0.2773%
BLK11INV23 | 254.8 | 0.2773%
BLK11INV24 | 254.8 | 0.2773%
BLK11INV25 | 254.8 | 0.2773%
BLK12INV1 | 267.54 | 0.2912%
BLK12INV2 | 267.54 | 0.2912%
BLK12INV3 | 267.54 | 0.2912%
BLK12INV4 | 267.54 | 0.2912%
BLK12INV5 | 267.54 | 0.2912%
BLK12INV6 | 267.54 | 0.2912%
BLK12INV7 | 267.54 | 0.2912%
BLK12INV8 | 267.54 | 0.2912%
BLK12INV9 | 267.54 | 0.2912%
BLK12INV10 | 267.54 | 0.2912%
BLK12INV11 | 254.8 | 0.2773%
BLK12INV12 | 254.8 | 0.2773%
BLK12INV13 | 267.54 | 0.2912%
BLK12INV14 | 242.06 | 0.2635%
BLK12INV15 | 254.8 | 0.2773%
BLK12INV16 | 254.8 | 0.2773%
BLK12INV17 | 280.28 | 0.3051%
BLK12INV18 | 267.54 | 0.2912%
BLK12INV19 | 267.54 | 0.2912%
BLK12INV20 | 254.8 | 0.2773%
BLK12INV21 | 280.28 | 0.3051%
BLK12INV22 | 267.54 | 0.2912%
BLK12INV23 | 280.28 | 0.3051%
BLK12INV24 | 254.8 | 0.2773%
BLK12INV25 | 267.54 | 0.2912%
BLK12INV26 | 254.8 | 0.2773%
BLK12INV27 | 254.8 | 0.2773%
BLK12INV28 | 242.06 | 0.2635%
BLK12INV29 | 254.8 | 0.2773%
BLK12INV30 | 254.8 | 0.2773%
BLK12INV31 | 254.8 | 0.2773%
BLK1LT1 | 4196 | 4.567%
BLK1LT2 | 4249.4 | 4.625%
BLK2LT1 | 4028.4 | 4.385%
BLK2LT2 | 4031.6 | 4.388%
BLK3LT1 | 3476.3 | 3.784%
BLK3LT2 | 3150 | 3.429%
BLK4LT1 | 3452.4 | 3.758%
BLK4LT2 | 3174.2 | 3.455%
BLK5LT1 | 4032 | 4.389%
BLK5LT2 | 4321.8 | 4.704%
BLK6LT1 | 4195.8 | 4.567%
BLK6LT2 | 3931.2 | 4.279%
BLK7LT1 | 4363.2 | 4.749%
BLK7LT2 | 4004.8 | 4.359%
BLK8LT1 | 4204.2 | 4.576%
BLK8LT2 | 3949.4 | 4.299%
BLK9LT1 | 3476.5 | 3.784%
BLK9LT2 | 2774 | 3.019%
BLK10LT1 | 3969 | 4.32%
BLK10LT2 | 2912.4 | 3.17%
BLK11LT1 | 3153.9 | 3.433%
BLK11LT2 | 3413.4 | 3.715%
BLK12LT1 | 4204.2 | 4.576%
BLK12LT2 | 3936.7 | 4.285%
BLK1TX | 8445.3 | 9.193%
BLK2TX | 8060 | 8.773%
BLK3TX | 6626.3 | 7.213%
BLK4TX | 6627.6 | 7.214%
BLK5TX | 8353.8 | 9.093%
BLK6TX | 8127 | 8.846%
BLK7TX | 8368.1 | 9.109%
BLK8TX | 8153.6 | 8.875%
BLK9TX | 6250.4 | 6.804%
BLK10TX | 8152.2 | 8.874%
BLK11TX | 6567.3 | 7.148%
BLK12TX | 8140.9 | 8.861%
MCR_MVP_IC_1 | 23131.6 | 25.18%
MCR_MVP_IC_2 | 23108.4 | 25.15%
MCR_MVP_IC_3 | 22772.1 | 24.79%
MCR_MVP_IC_4 | 22860.4 | 24.88%
MCR_MVP_OG1 | 46240 | 50.33%
MCR_MVP_OG2 | 45632.5 | 49.67%
PWR_TX1 | 46240 | 50.33%
PWR_TX2 | 45632.5 | 49.67%
220KV_Line | 91872.5 | 100%
Line_Bay1 | 46240 | 50.33%
Line_Bay2 | 45632.5 | 49.67%
Str_Typ1(330*40) | 13.2 | 0.01437%
Str_Typ2 (310*40) | 12.4 | 0.0135%
Str_Typ3(315*40) | 12.6 | 0.01372%
Str_Typ4(450*56) | 25.2 | 0.02743%
Str_Typ4(455*56) | 25.48 | 0.02773%
Str_Typ1(330*20) | 6.4 | 0.006966%
Str_Typ2 (310*20) | 6.2 | 0.006749%
Str_Typ3(315*20) | 6.3 | 0.006858%
Str_Typ4(450*26) | 9 | 0.009796%
Str_Typ4(455*26) | 9.1 | 0.009905%
BLK1Aux_Tx | 8445.3 | 9.193%
BLK2Aux_Tx | 8060 | 8.773%
BLK3Aux_Tx | 6626.3 | 7.213%
BLK4Aux_Tx | 6627.6 | 7.214%
BLK5Aux_Tx | 8353.8 | 9.093%
BLK6Aux_Tx | 8127 | 8.846%
BLK7Aux_Tx | 8368.1 | 9.109%
BLK8Aux_Tx | 8153.6 | 8.875%
BLK9Aux_Tx | 6250.4 | 6.804%
BLK10Aux_Tx | 8152.2 | 8.874%
BLK11Aux_Tx | 6567.3 | 7.148%
BLK12Aux_Tx | 8140.9 | 8.861%
BLK1MVP | 8445.3 | 9.193%
BLK2MVP | 8060 | 8.773%
BLK3MVP | 6626.3 | 7.213%
BLK4MVP | 6627.6 | 7.214%
BLK5MVP | 8353.8 | 9.093%
BLK6MVP | 8127 | 8.846%
BLK7MVP | 8368.1 | 9.109%
BLK8MVP | 8153.6 | 8.875%
BLK9MVP | 6250.4 | 6.804%
BLK10MVP | 8152.2 | 8.874%
BLK11MVP | 6567.3 | 7.148%
BLK12MVP | 8140.9 | 8.861%

## Inv_SY_B
| 125.4 | 125.4 | 132 | 132 | 132 | 131.7 | 130.7 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 125.4 | 125.4 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 132 | 125.4 | 132 | 140.2 | 144.2 | 136.8 | 136.8 | 138.2 | 149.2 | 148.8 | 163.6 | 143.3 | 136.4 | 137.9 | 138.6 | 144.9 | 144.8 | 142.9 | 148.8 | 142.6 | 125.2 | 143.8 | 132 | 125.6 | 136.4 | 289.8 | 289.8 | 288.9 | 289.8 | 289.8 | 289.35 | 289.8 | 289.8 | 289.8 | 289.8 | 287.55 | 289.8 | 277.2 | 277.2 | 289.8 | 289.8 | 289.8 | 289.8 | 302.4 | 289.8 | 277.2 | 289.8 | 277.2 | 277.2 | 289.35 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 315 | 289.8 | 289.8 | 277.2 | 277.2 | 289.8 | 288.45 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 264.6 | 277.2 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 277.2 | 277.2 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 277.2 | 289.8 | 315 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 277.2 | 302.4 | 277.2 | 252 | 289.8 | 264.6 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 302.4 | 289.8 | 277.2 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 252 | 226.8 | 277.2 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 252 | 252 | 252 | 293.02 | 278.04 | 254.8 | 292.74 | 293.02 | 290.5 | 305.76 | 293.02 | 318.5 | 293.02 | 280.28 | 280.28 | 267.54 | 293.02 | 278.74 | 305.76 | 254.8 | 254.8 | 279.72 | 242.06 | 229.32 | 305.76 | 304.36 | 304.36 | 304.92 | 305.48 | 304.92 | 329.28 | 330.26 | 280.28 | 280.28 | 254.8 | 254.8 | 254.8 | 267.54 | 254.8 | 267.54 | 254.8 | 254.8 | 254.8 | 254.8 | 267.54 | 267.54 | 267.54 | 267.54 | 254.8 | 254.8 | 254.8 | 267.54 | 254.8 | 267.54 | 254.8 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 280.28 | 292.88 | 293.02 | 279.72 | 292.88 | 305.76 | 292.33 | 292.47 | 280.28 | 293.02 | 293.02 | 280.28 | 304.64 | 305.48 | 278.6 | 305.48 | 305.76 | 229.32 | 229.32 | 293.02 | 242.06 | 280.28 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 289.8 | 264.6 | 264.6 | 252 | 252 | 252 | 262.8 | 262.8 | 263.7 | 263.7 | 263.7 | 288.9 | 263.7 | 263.7 | 263.7 | 263.7 | 238.5 | 263.7 | 264.6 | 252 | 252 | 254.8 | 293.02 | 252 | 267.54 | 267.54 | 267.54 | 252 | 242.06 | 267.54 | 280.28 | 254.8 | 254.8 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 279.37 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 254.8 | 254.8 | 267.54 | 242.06 | 254.8 | 254.8 | 280.28 | 267.54 | 267.54 | 254.8 | 280.28 | 267.54 | 280.28 | 254.8 | 267.54 | 254.8 | 254.8 | 242.06 | 254.8 | 254.8 | 254.8 | 91872.42
| 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 | 237 | 238 | 239 | 240 | 241 | 242 | 243 | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273 | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304 | 305 | 306 | 307 | 308 | 309 | 310 | 311 | 312 | 313 | 314 | 315 | 316 | 317 | 318 | 319 | 320 | 321 | 322 | 323 | 324 | 325 | 326 | 327 | 328 | 329 | 330 | 331 | 332 | 333 | 334 | 335 | 336 | 337 | 338 | 339 | 340 | 341 | 342 | 343 | 344 | 345 | 346 | 347 | 348 | 349 | 350 | 351 | 352 | 353 | 354 | 355 | 356 | 357 | 358 | 359 | 360 | 361 | 362 | 363 | 364 | 365 | 366 | 367 | 368 | 369 | 370 | 371 | 372 | 373 | 374 | 375 | 376
Date | BLK1_INV1 | BLK1_INV2 | BLK1_INV3 | BLK1_INV4 | BLK1_INV5 | BLK1_INV6 | BLK1_INV7 | BLK1_INV8 | BLK1_INV9 | BLK1_INV10 | BLK1_INV11 | BLK1_INV12 | BLK1_INV13 | BLK1_INV14 | BLK1_INV15 | BLK1_INV16 | BLK1_INV17 | BLK1_INV18 | BLK1_INV19 | BLK1_INV20 | BLK1_INV21 | BLK1_INV22 | BLK1_INV23 | BLK1_INV24 | BLK1_INV25 | BLK1_INV26 | BLK1_INV27 | BLK1_INV28 | BLK1_INV29 | BLK1_INV30 | BLK1_INV31 | BLK1_INV32 | BLK1_INV33 | BLK1_INV34 | BLK1_INV35 | BLK1_INV36 | BLK1_INV37 | BLK1_INV38 | BLK1_INV39 | BLK1_INV40 | BLK1_INV41 | BLK1_INV42 | BLK1_INV43 | BLK1_INV44 | BLK1_INV45 | BLK1_INV46 | BLK1_INV47 | BLK1_INV48 | BLK1_INV49 | BLK1_INV50 | BLK1_INV51 | BLK1_INV52 | BLK1_INV53 | BLK1_INV54 | BLK1_INV55 | BLK1_INV56 | BLK1_INV57 | BLK1_INV58 | BLK1_INV59 | BLK1_INV60 | BLK1_INV61 | BLK1_INV62 | BLK1_INV63 | BLK2_INV1 | BLK2_INV2 | BLK2_INV3 | BLK2_INV4 | BLK2_INV5 | BLK2_INV6 | BLK2_INV7 | BLK2_INV8 | BLK2_INV9 | BLK2_INV10 | BLK2_INV11 | BLK2_INV12 | BLK2_INV13 | BLK2_INV14 | BLK2_INV15 | BLK2_INV16 | BLK2_INV17 | BLK2_INV18 | BLK2_INV19 | BLK2_INV20 | BLK2_INV21 | BLK2_INV22 | BLK2_INV23 | BLK2_INV24 | BLK2_INV25 | BLK2_INV26 | BLK2_INV27 | BLK2_INV28 | BLK3_INV1 | BLK3_INV2 | BLK3_INV3 | BLK3_INV4 | BLK3_INV5 | BLK3_INV6 | BLK3_INV7 | BLK3_INV8 | BLK3_INV9 | BLK3_INV10 | BLK3_INV11 | BLK3_INV12 | BLK3_INV13 | BLK3_INV14 | BLK3_INV15 | BLK3_INV16 | BLK3_INV17 | BLK3_INV18 | BLK3_INV19 | BLK3_INV20 | BLK3_INV21 | BLK3_INV22 | BLK3_INV23 | BLK4_INV1 | BLK4_INV2 | BLK4_INV3 | BLK4_INV4 | BLK4_INV5 | BLK4_INV6 | BLK4_INV7 | BLK4_INV8 | BLK4_INV9 | BLK4_INV10 | BLK4_INV11 | BLK4_INV12 | BLK4_INV13 | BLK4_INV14 | BLK4_INV15 | BLK4_INV16 | BLK4_INV17 | BLK4_INV18 | BLK4_INV19 | BLK4_INV20 | BLK4_INV21 | BLK4_INV22 | BLK4_INV23 | BLK5_INV1 | BLK5_INV2 | BLK5_INV3 | BLK5_INV4 | BLK5_INV5 | BLK5_INV6 | BLK5_INV7 | BLK5_INV8 | BLK5_INV9 | BLK5_INV10 | BLK5_INV11 | BLK5_INV12 | BLK5_INV13 | BLK5_INV14 | BLK5_INV15 | BLK5_INV16 | BLK5_INV17 | BLK5_INV18 | BLK5_INV19 | BLK5_INV20 | BLK5_INV21 | BLK5_INV22 | BLK5_INV23 | BLK5_INV24 | BLK5_INV25 | BLK5_INV26 | BLK5_INV27 | BLK5_INV28 | BLK5_INV29 | BLK6_INV1 | BLK6_INV2 | BLK6_INV3 | BLK6_INV4 | BLK6_INV5 | BLK6_INV6 | BLK6_INV7 | BLK6_INV8 | BLK6_INV9 | BLK6_INV10 | BLK6_INV11 | BLK6_INV12 | BLK6_INV13 | BLK6_INV14 | BLK6_INV15 | BLK6_INV16 | BLK6_INV17 | BLK6_INV18 | BLK6_INV19 | BLK6_INV20 | BLK6_INV21 | BLK6_INV22 | BLK6_INV23 | BLK6_INV24 | BLK6_INV25 | BLK6_INV26 | BLK6_INV27 | BLK6_INV28 | BLK6_INV29 | BLK6_INV30 | BLK6_INV31 | BLK7_INV1 | BLK7_INV2 | BLK7_INV3 | BLK7_INV4 | BLK7_INV5 | BLK7_INV6 | BLK7_INV7 | BLK7_INV8 | BLK7_INV9 | BLK7_INV10 | BLK7_INV11 | BLK7_INV12 | BLK7_INV13 | BLK7_INV14 | BLK7_INV15 | BLK7_INV16 | BLK7_INV17 | BLK7_INV18 | BLK7_INV19 | BLK7_INV20 | BLK7_INV21 | BLK7_INV22 | BLK7_INV23 | BLK7_INV24 | BLK7_INV25 | BLK7_INV26 | BLK7_INV27 | BLK7_INV28 | BLK7_INV29 | BLK8_INV1 | BLK8_INV2 | BLK8_INV3 | BLK8_INV4 | BLK8_INV5 | BLK8_INV6 | BLK8_INV7 | BLK8_INV8 | BLK8_INV9 | BLK8_INV10 | BLK8_INV11 | BLK8_INV12 | BLK8_INV13 | BLK8_INV14 | BLK8_INV15 | BLK8_INV16 | BLK8_INV17 | BLK8_INV18 | BLK8_INV19 | BLK8_INV20 | BLK8_INV21 | BLK8_INV22 | BLK8_INV23 | BLK8_INV24 | BLK8_INV25 | BLK8_INV26 | BLK8_INV27 | BLK8_INV28 | BLK8_INV29 | BLK8_INV30 | BLK8_INV31 | BLK9_INV1 | BLK9_INV2 | BLK9_INV3 | BLK9_INV4 | BLK9_INV5 | BLK9_INV6 | BLK9_INV7 | BLK9_INV8 | BLK9_INV9 | BLK9_INV10 | BLK9_INV11 | BLK9_INV12 | BLK9_INV13 | BLK9_INV14 | BLK9_INV15 | BLK9_INV16 | BLK9_INV17 | BLK9_INV18 | BLK9_INV19 | BLK9_INV20 | BLK9_INV21 | BLK9_INV22 | BLK10_INV1 | BLK10_INV2 | BLK10_INV3 | BLK10_INV4 | BLK10_INV5 | BLK10_INV6 | BLK10_INV7 | BLK10_INV8 | BLK10_INV9 | BLK10_INV10 | BLK10_INV11 | BLK10_INV12 | BLK10_INV13 | BLK10_INV14 | BLK10_INV15 | BLK10_INV16 | BLK10_INV17 | BLK10_INV18 | BLK10_INV19 | BLK10_INV20 | BLK10_INV21 | BLK10_INV22 | BLK10_INV23 | BLK10_INV24 | BLK10_INV25 | BLK10_INV26 | BLK10_INV27 | BLK10_INV28 | BLK10_INV29 | BLK10_INV30 | BLK10_INV31 | BLK11_INV1 | BLK11_INV2 | BLK11_INV3 | BLK11_INV4 | BLK11_INV5 | BLK11_INV6 | BLK11_INV7 | BLK11_INV8 | BLK11_INV9 | BLK11_INV10 | BLK11_INV11 | BLK11_INV12 | BLK11_INV13 | BLK11_INV14 | BLK11_INV15 | BLK11_INV16 | BLK11_INV17 | BLK11_INV18 | BLK11_INV19 | BLK11_INV20 | BLK11_INV21 | BLK11_INV22 | BLK11_INV23 | BLK11_INV24 | BLK11_INV25 | BLK12_INV1 | BLK12_INV2 | BLK12_INV3 | BLK12_INV4 | BLK12_INV5 | BLK12_INV6 | BLK12_INV7 | BLK12_INV8 | BLK12_INV9 | BLK12_INV10 | BLK12_INV11 | BLK12_INV12 | BLK12_INV13 | BLK12_INV14 | BLK12_INV15 | BLK12_INV16 | BLK12_INV17 | BLK12_INV18 | BLK12_INV19 | BLK12_INV20 | BLK12_INV21 | BLK12_INV22 | BLK12_INV23 | BLK12_INV24 | BLK12_INV25 | BLK12_INV26 | BLK12_INV27 | BLK12_INV28 | BLK12_INV29 | BLK12_INV30 | BLK12_INV31 | Plant
2025-03-29 | 1.5183 | 1.4673 | 1.5636 | 1.5667 | 1.5606 | 1.4715 | 1.6098 | 1.5318 | 1.5886 | 1.5955 | 1.5894 | 1.5864 | 1.5939 | 1.5955 | 1.6167 | 1.6061 | 1.5774 | 1.6029 | 1.5947 | 1.6114 | 1.6598 | 1.6485 | 1.6553 | 1.6447 | 1.6629 | 1.6614 | 1.6697 | 1.6591 | 1.6712 | 1.6773 | 1.6576 | 1.6591 | 1.5629 | 1.5319 | 1.5486 | 1.5766 | 1.6013 | 1.5949 | 1.5735 | 1.5869 | 1.5379 | 1.6084 | 1.6394 | 1.6345 | 1.644 | 1.6823 | 1.6857 | 1.6781 | 1.6351 | 1.6657 | 1.6679 | 1.6229 | 1.6039 | 1.6149 | 1.5877 | 1.6326 | 1.6243 | 1.5519 | 1.5471 | 1.5396 | 1.5894 | 1.5995 | 1.5968 | 1.764 | 1.7692 | 1.7304 | 1.7402 | 1.7692 | 1.7363 | 1.7036 | 1.7388 | 1.774 | 1.7008 | 1.7173 | 1.6939 | 1.7096 | 1.6688 | 1.7478 | 1.7588 | 1.7612 | 1.7384 | 1.7745 | 1.7502 | 1.7789 | 1.7767 | 1.7583 | 1.7576 | 1.7512 | 1.7581 | 1.7267 | 1.7333 | 1.6142 | 1.6874 | 1.6977 | 1.7274 | 1.7467 | 1.7321 | 1.7453 | 1.7322 | 1.7121 | 1.7157 | 1.7284 | 1.6928 | 1.7553 | 1.7388 | 1.6874 | 1.7636 | 1.7243 | 1.7191 | 1.7702 | 1.7736 | 1.7864 | 1.7491 | 1.7608 | 1.7453 | 1.8068 | 1.764 | 1.7761 | 1.7833 | 1.7781 | 1.7761 | 1.7774 | 1.7727 | 1.7792 | 1.7937 | 1.7836 | 1.7847 | 1.7761 | 1.7619 | 1.7443 | 1.7464 | 1.7878 | 1.7533 | 1.7778 | 1.7336 | 1.7826 | 1.7929 | 1.8171 | 1.7883 | 1.746 | 1.744 | 1.7933 | 1.7964 | 1.7743 | 1.7933 | 1.8109 | 1.7602 | 1.7803 | 1.7487 | 1.7359 | 1.7536 | 1.7512 | 1.8042 | 1.7671 | 1.8043 | 1.7605 | 1.7871 | 1.7795 | 1.7892 | 1.7536 | 1.7585 | 1.7571 | 1.7471 | 1.8191 | 1.8554 | 1.7532 | 1.7048 | 1.7381 | 1.6867 | 1.689 | 1.7067 | 1.7071 | 1.7098 | 1.7596 | 1.7664 | 1.7222 | 1.7313 | 1.7434 | 1.7653 | 1.6722 | 1.7152 | 1.7027 | 1.7441 | 1.7105 | 1.7404 | 1.7706 | 1.7298 | 1.7668 | 1.7294 | 1.7434 | 1.7256 | 1.7608 | 1.7234 | 1.7339 | 1.7381 | 1.7282 | 1.7508 | 1.7159 | 1.7616 | 1.7575 | 1.748 | 1.7538 | 1.7656 | 1.7304 | 1.7791 | 1.7991 | 1.8002 | 2.0444 | 1.7814 | 1.7298 | 1.7425 | 2.0557 | 1.7779 | 2.2488 | 1.7681 | 1.7625 | 1.7797 | 1.7447 | 1.7206 | 1.7036 | 1.7486 | 1.7139 | 1.6826 | 1.6742 | 1.7314 | 1.7062 | 1.6637 | 1.7144 | 1.7159 | 1.7115 | 1.7005 | 1.6887 | 1.7327 | 1.7022 | 1.6974 | 1.7217 | 1.7155 | 1.7198 | 1.7067 | 1.6973 | 1.6958 | 1.7018 | 1.7441 | 1.7433 | 1.7182 | 1.7126 | 1.7088 | 1.6947 | 1.7147 | 1.7082 | 1.7082 | 1.7055 | 1.7508 | 1.7283 | 1.7078 | 1.713 | 1.7197 | 1.7236 | 1.7232 | 1.763 | 1.7632 | 1.7806 | 1.7867 | 1.7815 | 1.7804 | 1.7864 | 1.7692 | 1.7518 | 1.7697 | 1.8057 | 1.7121 | 1.7408 | 1.7877 | 1.7674 | 1.7875 | 1.7936 | 1.7767 | 1.8058 | 1.7704 | 1.7101 | 1.6954 | 1.6867 | 1.6742 | 1.7169 | 1.6689 | 1.7075 | 1.6667 | 1.6863 | 1.7124 | 1.6991 | 1.6893 | 1.7026 | 1.7234 | 1.6821 | 1.6679 | 1.68 | 1.7123 | 1.694 | 1.6955 | 1.7008 | 4.2703 | 1.6932 | 1.6777 | 1.7133 | 1.6989 | 1.6776 | 1.6997 | 1.7063 | 1.7123 | 1.7131 | 1.7582 | 1.7193 | 1.7337 | 1.7186 | 1.7111 | 1.6951 | 1.7107 | 1.6698 | 1.7063 | 1.704 | 1.6794 | 1.6868 | 1.7448 | 1.7212 | 1.7085 | 1.7089 | 1.7123 | 1.7186 | 1.7482 | 1.6896 | 1.6852 | 1.7484 | 1.7571 | 1.6852 | 1.772 | 1.6981 | 1.7519 | 1.7325 | 1.7418 | 1.7519 | 1.7377 | 1.7153 | 1.7358 | 1.7594 | 1.7171 | 1.7414 | 1.8395 | 1.7388 | 1.6913 | 1.719 | 1.8395 | 1.7379 | 1.6951 | 1.7003 | 1.7547 | 1.7094 | 1.7481 | 1.75 | 1.7013 | 1.7291 | 1.6958 | 1.7276 | 1.7467 | 1.6958 | 1.7602 | 1.75 | 1.7245
2025-03-30 | 3.6061 | 3.4753 | 3.6977 | 3.7045 | 3.6947 | 3.4738 | 3.7758 | 3.6235 | 3.7402 | 3.747 | 3.7583 | 3.75 | 3.7447 | 3.7523 | 3.7962 | 3.7871 | 3.7193 | 3.7464 | 3.6985 | 3.7644 | 3.8652 | 3.8288 | 3.872 | 3.8621 | 3.853 | 3.8523 | 3.8553 | 3.8348 | 3.8606 | 3.8765 | 3.8364 | 3.8462 | 3.6591 | 3.614 | 3.6579 | 3.7081 | 3.7656 | 3.7799 | 3.7227 | 3.7344 | 3.6447 | 3.7603 | 3.837 | 3.8136 | 3.8348 | 3.9255 | 3.9142 | 3.8763 | 3.8203 | 3.8535 | 3.857 | 3.7694 | 3.7403 | 3.7474 | 3.6837 | 3.767 | 3.7641 | 3.6003 | 3.5935 | 3.5793 | 3.7462 | 3.6982 | 3.7339 | 4.1063 | 4.021 | 4.0114 | 4.0614 | 4.1232 | 4.0563 | 3.9707 | 4.0542 | 4.1349 | 3.9783 | 4.0031 | 3.9672 | 4.004 | 3.9174 | 4.0545 | 4.0725 | 4.0732 | 3.9296 | 4.1141 | 4.0614 | 4.1331 | 4.1277 | 4.0942 | 4.0866 | 4.0695 | 4.0718 | 4.0224 | 4.038 | 3.8768 | 3.9703 | 3.9893 | 4.0549 | 4.0821 | 4.0594 | 4.0552 | 4.06 | 4.0206 | 4.0267 | 4.0345 | 3.948 | 4.0997 | 4.0766 | 3.9196 | 4.119 | 4.0469 | 4.038 | 4.1277 | 4.1353 | 4.1749 | 4.0801 | 4.0967 | 4.0949 | 4.2098 | 4.1322 | 4.1511 | 4.1856 | 4.1667 | 4.1222 | 4.1218 | 4.118 | 4.1335 | 4.1411 | 4.1211 | 4.011 | 4.1042 | 4.097 | 4.0483 | 4.0507 | 4.1373 | 4.0666 | 4.1173 | 4.028 | 4.137 | 4.1367 | 4.2022 | 4.1438 | 4.0556 | 4.038 | 4.148 | 4.158 | 4.0973 | 4.0538 | 4.1877 | 4.089 | 4.1291 | 4.0658 | 4.039 | 4.079 | 4.0669 | 4.1859 | 4.1084 | 4.1787 | 4.0894 | 4.1473 | 4.128 | 4.1529 | 4.0697 | 4.079 | 4.079 | 4.0418 | 4.2103 | 4.2778 | 4.0754 | 4.0208 | 4.0794 | 3.9845 | 3.9924 | 4.034 | 4.0321 | 4.051 | 4.1504 | 4.1546 | 4.0359 | 4.079 | 4.0892 | 4.1308 | 3.9508 | 4.0556 | 4.0234 | 4.1243 | 4.0858 | 4.0801 | 4.1463 | 4.0737 | 4.1572 | 4.0745 | 4.1179 | 4.0601 | 4.0816 | 4.0571 | 4.0945 | 4.1306 | 4.1056 | 4.1155 | 3.9833 | 4.0753 | 4.0589 | 4.05 | 4.0577 | 4.0833 | 4.0251 | 4.11 | 4.1268 | 4.1564 | 4.0285 | 4.108 | 3.9852 | 4.0011 | 4.1307 | 4.0803 | 4.0714 | 4.0911 | 4.0691 | 4.1048 | 4.0507 | 4.0139 | 3.9595 | 3.9598 | 3.9732 | 3.906 | 3.8905 | 4.0081 | 3.8497 | 3.9293 | 4.0331 | 4.0283 | 4.0322 | 4 | 3.9919 | 4.0863 | 4.0087 | 4.0691 | 4.0628 | 4.0487 | 4.0636 | 4.0386 | 4.0188 | 4.0114 | 4.0185 | 4.0338 | 4.0498 | 3.9925 | 4.039 | 4.0298 | 4.0069 | 4.0487 | 4.0226 | 4.0357 | 4.0274 | 4.0689 | 4.0588 | 4.0484 | 4.0401 | 4.0648 | 4.0039 | 3.9992 | 4.0857 | 4.088 | 4.1389 | 4.1418 | 4.1275 | 4.1293 | 4.1462 | 4.1113 | 4.0697 | 4.1095 | 4.179 | 4.0323 | 4.0147 | 4.1276 | 4.0803 | 4.1344 | 4.1527 | 4.1212 | 4.1721 | 4.0984 | 4.0302 | 4.0147 | 4.0113 | 3.9834 | 3.8825 | 3.9441 | 4.0438 | 3.9611 | 3.9082 | 4.0548 | 4.0252 | 4.0057 | 4.034 | 4.0742 | 3.9885 | 3.9889 | 3.9985 | 4.0411 | 4.0209 | 4.0303 | 4.0322 | 4.2703 | 4.003 | 3.9894 | 4.0516 | 4.0178 | 4.0021 | 4.0129 | 4.0321 | 4.0425 | 4.0516 | 4.1056 | 4.0253 | 4.1016 | 4.0562 | 4.0491 | 4.0162 | 4.0456 | 3.9709 | 4.0013 | 3.9585 | 3.9851 | 3.9851 | 4.0543 | 4.0031 | 3.9803 | 3.9732 | 3.9773 | 3.9856 | 4.0674 | 3.9529 | 3.9192 | 4.0655 | 4.0632 | 4.0632 | 4.1005 | 3.9673 | 4.1003 | 4.0401 | 4.0779 | 4.0521 | 4.0678 | 4.0304 | 4.0757 | 4.1235 | 4.045 | 4.0954 | 4.2473 | 4.0775 | 3.9788 | 4.0561 | 4.1185 | 4.0663 | 3.9867 | 4.005 | 4.117 | 4.011 | 4.0936 | 4.0938 | 4.0012 | 4.0633 | 4.009 | 4.0279 | 4.111 | 4.0981 | 4.1374 | 4.1201 | 4.0075
2025-03-31 | 3.5526 | 3.4155 | 3.6356 | 3.6417 | 3.6386 | 3.4267 | 3.7077 | 3.5606 | 3.6811 | 3.6856 | 3.6917 | 3.6879 | 3.6848 | 3.6902 | 3.7333 | 3.7227 | 3.6555 | 3.681 | 3.6447 | 3.6992 | 3.7909 | 3.7598 | 3.8053 | 3.778 | 3.7856 | 3.7864 | 3.7856 | 3.7659 | 3.7902 | 3.8045 | 3.7652 | 3.7742 | 3.6008 | 3.5598 | 3.5989 | 3.6499 | 3.7026 | 3.7201 | 3.6705 | 3.673 | 3.5811 | 3.6997 | 3.7809 | 3.7544 | 3.7719 | 3.8625 | 3.8485 | 3.8125 | 3.7683 | 3.7837 | 3.7859 | 3.702 | 3.671 | 3.6798 | 3.614 | 3.7173 | 3.6956 | 3.5316 | 3.5248 | 3.5104 | 3.6727 | 3.6425 | 3.6701 | 4.0431 | 3.9562 | 3.9495 | 3.9945 | 4.0576 | 3.9934 | 3.9092 | 3.9893 | 3.9945 | 3.6936 | 4.0184 | 3.9086 | 3.943 | 3.8615 | 3.9838 | 4.0003 | 4.0035 | 3.9841 | 4.0437 | 3.9969 | 4.0635 | 4.0604 | 4.0346 | 4.0195 | 4.0041 | 4.0062 | 3.9569 | 3.972 | 3.8468 | 3.9061 | 3.9244 | 3.9824 | 4.0121 | 3.9927 | 3.989 | 3.9852 | 3.9531 | 3.9625 | 3.9679 | 3.8863 | 4.03 | 3.9103 | 4.0252 | 4.0518 | 3.9859 | 3.9689 | 4.06 | 4.069 | 4.108 | 4.0151 | 4.0368 | 4.0255 | 4.1325 | 4.0621 | 4.0766 | 4.1132 | 4.0873 | 4.05 | 4.0511 | 4.0447 | 4.0595 | 4.0718 | 4.0493 | 4.059 | 4.0286 | 4.0228 | 3.9765 | 3.9821 | 4.0607 | 3.9959 | 4.0438 | 3.9589 | 4.0663 | 4.0649 | 4.1636 | 4.1032 | 4.0117 | 3.9917 | 4.1104 | 4.2274 | 4.0455 | 4.0021 | 4.1301 | 4.0342 | 4.0743 | 4.0126 | 3.982 | 4.0151 | 4.0128 | 4.127 | 4.0504 | 4.1087 | 4.0242 | 4.0797 | 4.0576 | 4.0804 | 4.0059 | 4.0128 | 4.0145 | 3.9779 | 4.1392 | 4.206 | 4.0119 | 4.0026 | 4.0597 | 3.9667 | 3.9769 | 4.0132 | 4.0147 | 4.0257 | 4.1224 | 4.1232 | 4.0227 | 4.0578 | 4.0669 | 4.1028 | 3.9266 | 4.0397 | 3.9885 | 4.0926 | 4.0548 | 4.0593 | 4.124 | 4.0412 | 4.1179 | 4.0355 | 4.0816 | 4.0197 | 4.0378 | 4.0008 | 4.0427 | 4.0825 | 4.0516 | 4.073 | 4.0281 | 4.0433 | 4.5016 | 4.024 | 4.0335 | 4.063 | 4.0015 | 4.085 | 4.1024 | 4.0281 | 4.0306 | 4.0306 | 3.9702 | 3.9895 | 4.0529 | 4.0421 | 4.0369 | 4.0495 | 4.0387 | 4.0684 | 4.0263 | 3.9858 | 3.9401 | 3.9979 | 3.9505 | 3.8782 | 3.8656 | 3.9802 | 3.9278 | 3.8586 | 3.9657 | 3.9588 | 3.98 | 3.9482 | 3.9288 | 4.0153 | 3.9426 | 4.0047 | 4.0055 | 3.9847 | 3.9937 | 3.9732 | 3.9545 | 3.9523 | 3.9598 | 3.9765 | 3.9953 | 3.9458 | 3.9957 | 3.9733 | 3.9545 | 3.9945 | 3.9785 | 3.9785 | 3.9792 | 4.0218 | 4.0319 | 3.9979 | 3.9923 | 4.0203 | 3.9218 | 3.9228 | 4.0052 | 4.0072 | 4.0539 | 4.0594 | 4.0519 | 4.0449 | 4.0659 | 4.0342 | 3.9936 | 4.032 | 4.1045 | 3.9636 | 3.9451 | 4.0494 | 4.0044 | 4.0607 | 4.0747 | 4.0403 | 4.0944 | 4.021 | 3.952 | 3.9233 | 3.9271 | 3.8991 | 3.955 | 3.8738 | 3.9543 | 3.8753 | 3.8273 | 3.9754 | 3.9448 | 3.9286 | 3.952 | 3.9933 | 3.9083 | 3.9131 | 3.9239 | 3.9772 | 3.9454 | 3.9545 | 3.9579 | 3.829 | 3.9261 | 3.9139 | 3.9625 | 3.9389 | 3.9199 | 3.9443 | 3.9577 | 3.971 | 3.9702 | 4.0078 | 3.9363 | 4.0016 | 3.9587 | 3.9545 | 3.9246 | 3.9599 | 3.8821 | 3.8843 | 3.8672 | 3.8878 | 3.8893 | 3.959 | 3.9067 | 3.8888 | 3.8835 | 3.8734 | 3.882 | 3.9714 | 3.8619 | 3.8265 | 3.9655 | 3.96 | 3.9655 | 3.9992 | 3.8499 | 3.9841 | 3.9463 | 3.9602 | 3.9482 | 3.9534 | 3.9164 | 3.9617 | 4.011 | 3.9359 | 3.9874 | 4.1597 | 3.9702 | 3.8829 | 3.9474 | 4.0082 | 3.9643 | 3.869 | 3.894 | 4.0141 | 3.9072 | 4.0005 | 3.971 | 3.8976 | 3.9564 | 4.1597 | 3.9172 | 4.0007 | 3.9933 | 4.0267 | 4.0055 | 3.944
2025-04-01 | 3.567 | 3.4338 | 3.6545 | 3.6606 | 3.653 | 3.4434 | 3.7292 | 3.5788 | 3.6977 | 3.7023 | 3.7106 | 3.7061 | 3.7038 | 3.7061 | 3.7538 | 3.7409 | 3.6746 | 3.701 | 3.6659 | 3.7197 | 3.8098 | 3.778 | 3.8038 | 3.8129 | 3.8008 | 3.8008 | 3.8068 | 3.7871 | 3.8061 | 3.8235 | 3.7848 | 3.7962 | 3.6129 | 3.5734 | 3.614 | 3.6699 | 3.7241 | 3.7352 | 3.6833 | 3.6938 | 3.6068 | 3.7247 | 3.8044 | 3.7749 | 3.7939 | 3.8857 | 3.8733 | 3.8353 | 3.7751 | 3.8067 | 3.8013 | 3.7259 | 3.6955 | 3.7039 | 3.6409 | 3.7411 | 3.7204 | 3.5568 | 3.5527 | 3.5369 | 3.6962 | 3.6624 | 3.7082 | 4.0587 | 3.9762 | 3.9637 | 4.0159 | 4.079 | 4.0145 | 3.9313 | 4.0148 | 4.0939 | 3.9406 | 3.9631 | 3.931 | 3.9646 | 3.8824 | 3.9969 | 4.0186 | 4.0238 | 4.0055 | 4.0602 | 4.0066 | 4.0819 | 4.0728 | 4.0408 | 4.0339 | 4.0173 | 4.0204 | 4.0204 | 3.9044 | 3.7402 | 3.9068 | 3.9303 | 3.9945 | 4.0193 | 3.9981 | 3.9938 | 3.9955 | 3.9614 | 3.9686 | 3.9776 | 3.8884 | 4.0414 | 4.087 | 4.0324 | 4.0642 | 4.0003 | 3.9817 | 4.0773 | 4.0839 | 4.1184 | 4.0253 | 4.0473 | 4.0449 | 4.1618 | 4.0801 | 4.1025 | 4.1315 | 4.1118 | 4.0787 | 4.0804 | 4.074 | 4.0841 | 4.1011 | 4.0807 | 4.0921 | 4.0625 | 4.0542 | 4.0079 | 4.0131 | 4.0925 | 4.0283 | 4.0769 | 3.9886 | 4.0939 | 4.0963 | 4.0079 | 3.773 | 4.0221 | 4.0066 | 4.0625 | 4.1239 | 4.0611 | 4.0204 | 4.1473 | 4.0549 | 4.0924 | 4.0324 | 4.0018 | 4.0409 | 4.0338 | 4.1523 | 4.0759 | 4.1408 | 4.0573 | 4.1135 | 4.0918 | 4.1146 | 4.0314 | 4.0449 | 4.0383 | 3.9993 | 4.1696 | 4.2367 | 4.0379 | 3.9713 | 4.0302 | 3.9426 | 3.9539 | 3.9906 | 3.9924 | 4.0068 | 4.1051 | 4.1047 | 4.0026 | 4.0314 | 4.0435 | 4.0828 | 3.9099 | 4.0176 | 3.9704 | 4.0737 | 4.0355 | 4.0442 | 4.1062 | 4.0242 | 4.1036 | 4.0197 | 4.0695 | 4.0072 | 4.0272 | 3.9985 | 4.0333 | 4.0722 | 4.0452 | 4.0567 | 3.9533 | 4.0437 | 4.0326 | 4.0271 | 4.0376 | 4.064 | 4.0051 | 4.0881 | 4.1024 | 4.1298 | 4.0014 | 4.0791 | 3.9583 | 3.9721 | 4.3435 | 4.0509 | 4.0416 | 4.0585 | 4.0415 | 4.0738 | 4.0267 | 3.9878 | 4.0061 | 3.9578 | 3.9945 | 3.9433 | 3.8872 | 3.5766 | 3.972 | 3.8615 | 3.9667 | 3.9588 | 3.9792 | 3.9466 | 3.9303 | 4.0228 | 3.9463 | 4.0027 | 3.9988 | 3.9827 | 3.9929 | 3.9759 | 3.9523 | 3.9512 | 3.9605 | 3.9678 | 3.9902 | 3.9294 | 3.9818 | 3.9662 | 3.9486 | 3.987 | 3.9676 | 3.9736 | 3.9721 | 4.0102 | 4.0155 | 3.9908 | 3.9841 | 4.0121 | 3.9368 | 3.9385 | 4.0216 | 4.024 | 4.0747 | 4.0771 | 4.0776 | 4.0664 | 4.0898 | 4.0629 | 4.0233 | 4.0631 | 4.1311 | 3.9881 | 3.967 | 4.0792 | 4.0352 | 4.0629 | 4.0773 | 3.2138 | 4.9364 | 3.5668 | 3.9494 | 3.9233 | 3.9203 | 3.898 | 3.7007 | 3.8636 | 3.9573 | 3.8715 | 3.8205 | 3.9645 | 3.94 | 3.9191 | 3.9429 | 3.9837 | 3.8877 | 3.8933 | 3.9148 | 3.9684 | 3.9367 | 3.9473 | 3.9526 | 4.2703 | 3.9276 | 3.9056 | 3.9803 | 3.9393 | 3.904 | 3.9427 | 3.9524 | 3.9694 | 3.9734 | 3.9898 | 3.9158 | 3.9897 | 3.9557 | 3.9463 | 3.9138 | 3.9448 | 3.8664 | 3.8847 | 3.8536 | 3.8823 | 3.8748 | 3.9127 | 3.891 | 3.8723 | 3.8749 | 3.8667 | 3.8772 | 3.965 | 3.8438 | 3.803 | 3.9525 | 3.9356 | 3.96 | 3.9847 | 3.7949 | 3.9661 | 3.9239 | 3.9433 | 3.9362 | 3.9265 | 3.9164 | 3.9437 | 4.0073 | 3.9265 | 3.9823 | 4.1122 | 3.9732 | 3.8883 | 3.947 | 4.0118 | 3.9396 | 3.8555 | 3.8903 | 4.0059 | 3.9107 | 3.9987 | 3.9839 | 3.8936 | 3.9583 | 3.9023 | 3.9199 | 4.0048 | 4 | 4.0279 | 4.0145 | 3.9467
2025-04-02 | 2.8915 | 2.7863 | 2.9144 | 2.9129 | 2.9053 | 2.7768 | 2.9763 | 2.8515 | 2.9447 | 2.9492 | 2.9477 | 2.9386 | 2.9394 | 2.95 | 2.9773 | 2.9667 | 2.9219 | 2.9545 | 2.9379 | 2.9674 | 3.0409 | 3.0189 | 3.0379 | 3.0326 | 3.0462 | 3.0409 | 3.0523 | 3.0371 | 3.0576 | 3.0644 | 3.0356 | 3.0379 | 2.8985 | 2.8589 | 2.878 | 2.9147 | 2.9545 | 2.9553 | 2.9182 | 2.9266 | 2.8121 | 2.9401 | 3.0111 | 2.9832 | 3.0124 | 3.0825 | 3.0737 | 3.0524 | 2.9976 | 3.0244 | 3.0381 | 2.9616 | 2.9372 | 2.9476 | 2.8985 | 2.9643 | 2.9583 | 2.8296 | 2.8283 | 2.8136 | 2.925 | 2.9084 | 2.9333 | 3.216 | 3.147 | 3.1533 | 3.1743 | 3.2284 | 3.1875 | 3.1204 | 3.1825 | 3.246 | 3.127 | 3.1563 | 3.1232 | 3.1706 | 3.1061 | 3.1746 | 3.2008 | 3.1953 | 2.766 | 3.2183 | 3.1815 | 3.2316 | 3.2298 | 3.2042 | 3.2009 | 3.1889 | 3.1932 | 3.1549 | 3.1653 | 3.0963 | 3.1429 | 3.1139 | 3.1898 | 3.2153 | 3.2057 | 3.196 | 3.1746 | 3.1522 | 3.1656 | 3.1556 | 3.0941 | 3.2167 | 3.3326 | 3.2164 | 3.2288 | 3.1957 | 3.1736 | 3.2388 | 3.2353 | 3.2709 | 3.1995 | 3.2107 | 3.1929 | 3.2792 | 3.2329 | 3.234 | 3.2612 | 3.2322 | 3.2257 | 3.1687 | 3.1962 | 3.2226 | 3.2398 | 3.2236 | 3.226 | 3.2208 | 3.1843 | 3.1812 | 3.1715 | 3.2305 | 3.1925 | 3.2312 | 3.1667 | 3.2378 | 3.2745 | 3.2771 | 3.2387 | 3.2091 | 3.1653 | 3.2453 | 3.2553 | 3.2091 | 3.1732 | 3.266 | 3.1994 | 3.2233 | 3.1782 | 3.1526 | 3.1786 | 3.186 | 3.2721 | 3.2208 | 3.2671 | 3.1963 | 3.236 | 3.2384 | 3.2571 | 3.1846 | 3.1963 | 3.1936 | 3.1542 | 3.2986 | 3.3499 | 3.1807 | 3.1478 | 3.2143 | 3.133 | 3.1323 | 3.1799 | 3.1686 | 3.1924 | 3.2676 | 3.2766 | 3.1927 | 3.2188 | 3.2358 | 3.2426 | 3.1179 | 3.1958 | 3.1818 | 3.2494 | 3.2313 | 3.232 | 3.2604 | 3.2192 | 3.2702 | 3.2101 | 3.2313 | 3.1882 | 3.2237 | 3.1799 | 3.2181 | 3.2429 | 3.2163 | 3.252 | 3.1056 | 3.2369 | 3.4537 | 3.18 | 3.1769 | 3.1962 | 3.1721 | 3.1465 | 3.097 | 3.2513 | 3.1583 | 3.0791 | 3.1304 | 3.1411 | 3.1929 | 3.1884 | 3.199 | 3.2053 | 3.2225 | 3.2281 | 3.1694 | 3.1302 | 3.0884 | 3.14 | 3.1028 | 3.0303 | 3.0274 | 3.1271 | 3.0797 | 3.0801 | 3.1679 | 3.1664 | 3.1707 | 3.166 | 3.1386 | 3.2115 | 3.1491 | 3.19 | 3.197 | 3.1856 | 3.1907 | 3.1734 | 3.1547 | 3.158 | 3.1558 | 3.1849 | 3.1856 | 3.1535 | 3.1778 | 3.1692 | 3.1278 | 0.035322 | 0.020184 | 3.1775 | 3.1648 | 3.2107 | 3.2021 | 3.1778 | 3.1689 | 3.1924 | 3.1351 | 3.1344 | 3.1882 | 3.1943 | 3.1767 | 3.2617 | 3.2326 | 3.2369 | 3.2521 | 3.2233 | 3.1957 | 3.2243 | 3.2658 | 3.155 | 3.1407 | 3.213 | 3.1822 | 3.9334 | 3.2152 | 2.5213 | 3.8895 | 2.8086 | 3.0839 | 3.1493 | 3.1485 | 3.1451 | 3.0816 | 3.1274 | 3.1795 | 3.1319 | 3.0964 | 3.2048 | 3.1791 | 3.161 | 3.1822 | 3.2187 | 3.1706 | 3.1567 | 3.1572 | 3.2002 | 3.171 | 3.1725 | 3.1854 | 4.2703 | 3.1551 | 3.1517 | 3.1907 | 3.1733 | 3.1727 | 3.1725 | 3.212 | 3.194 | 3.194 | 3.2331 | 3.193 | 3.2369 | 3.1965 | 3.1857 | 3.161 | 3.196 | 3.1385 | 3.0807 | 3.1436 | 3.1413 | 3.1527 | 3.2208 | 3.1767 | 3.1562 | 3.142 | 3.1405 | 3.1577 | 3.2169 | 3.1311 | 3.1413 | 3.1903 | 3.2433 | 3.23 | 3.2335 | 3.1606 | 3.2399 | 3.2208 | 3.2025 | 3.1988 | 3.2197 | 3.1633 | 3.2197 | 3.2406 | 3.1726 | 3.2276 | 3.3752 | 3.2066 | 3.1343 | 3.2021 | 3.2539 | 3.235 | 3.1521 | 3.1562 | 3.2524 | 3.1711 | 3.2451 | 3.2193 | 3.1566 | 3.2036 | 3.1613 | 3.1903 | 3.2385 | 3.2308 | 3.2684 | 3.2449 | 3.1531
2025-04-03 | 3.7057 | 3.5845 | 3.7348 | 3.7364 | 3.7174 | 3.5543 | 3.8041 | 3.6523 | 3.7561 | 3.7583 | 3.7735 | 3.7583 | 3.7545 | 3.7583 | 3.797 | 3.797 | 3.7337 | 3.7584 | 3.7333 | 3.778 | 3.8697 | 3.8364 | 3.8818 | 3.8545 | 3.8621 | 3.8621 | 3.8727 | 3.8568 | 3.8856 | 3.8939 | 3.8561 | 3.8667 | 3.6955 | 3.6435 | 3.6834 | 3.7217 | 3.7799 | 3.7855 | 3.7371 | 3.7448 | 3.6197 | 3.7575 | 3.8391 | 3.8246 | 3.8385 | 3.9327 | 3.9135 | 3.877 | 3.8227 | 3.8486 | 3.8607 | 3.765 | 3.7374 | 3.7481 | 3.6816 | 3.7719 | 3.756 | 3.5947 | 3.5895 | 3.5765 | 3.7455 | 3.707 | 3.7317 | 4.0973 | 4.021 | 4.018 | 4.0573 | 4.1211 | 4.0702 | 4.058 | 4.0638 | 4.0925 | 3.9952 | 4.0153 | 3.989 | 4.0465 | 3.9538 | 3.9786 | 4.0818 | 4.0707 | 3.9051 | 4.1002 | 4.0462 | 4.1183 | 4.1118 | 4.0754 | 4.079 | 4.0622 | 4.0628 | 4.0276 | 4.0421 | 3.951 | 4.0179 | 4.0424 | 4.0783 | 4.088 | 4.079 | 4.0449 | 4.0507 | 4.0368 | 4.0328 | 4.0304 | 3.9345 | 4.1025 | 4.2543 | 4.0908 | 4.1228 | 4.0832 | 4.0697 | 4.1353 | 4.1304 | 4.168 | 4.0824 | 4.0905 | 4.0704 | 4.1815 | 4.0159 | 4.1301 | 4.1446 | 4.1273 | 4.1115 | 4.1049 | 4.0758 | 4.1115 | 4.1235 | 4.1101 | 4.1149 | 4.1087 | 4.0683 | 4.0652 | 4.0573 | 4.1304 | 4.0811 | 4.127 | 4.0487 | 4.1353 | 4.1742 | 4.1798 | 4.1206 | 4.0528 | 4.0386 | 4.1308 | 4.0718 | 4.0887 | 4.0604 | 4.167 | 4.0876 | 4.118 | 4.0625 | 4.0292 | 4.0694 | 4.0738 | 4.1746 | 4.1108 | 4.1732 | 4.0849 | 4.1356 | 4.1435 | 4.1573 | 4.069 | 4.0825 | 4.078 | 4.028 | 4.203 | 4.2612 | 4.0664 | 3.9773 | 4.0465 | 3.955 | 3.9478 | 4.0015 | 3.997 | 4.0336 | 4.1213 | 4.1342 | 4.0249 | 4.0608 | 4.0745 | 4.076 | 3.9488 | 4.0335 | 4.0018 | 4.0945 | 4.0718 | 4.0865 | 4.1175 | 4.0658 | 4.1293 | 4.0522 | 4.0918 | 4.0351 | 4.0899 | 4.0276 | 4.0711 | 4.1028 | 4.0746 | 4.0925 | 3.8325 | 4.0789 | 4.0487 | 4.0623 | 4.054 | 4.0726 | 4.0486 | 4.1069 | 4.0471 | 4.1376 | 4.0121 | 3.996 | 3.9852 | 3.9888 | 4.0253 | 4.0705 | 4.1209 | 4.1016 | 4.1055 | 4.1134 | 4.045 | 3.9279 | 3.9417 | 4.0068 | 3.9591 | 3.8909 | 3.8722 | 3.993 | 3.9296 | 3.9104 | 3.9981 | 4.002 | 4.0102 | 3.9918 | 3.9732 | 4.0648 | 3.983 | 4.0267 | 4.0298 | 4.022 | 4.029 | 4.0229 | 3.9979 | 3.993 | 3.9919 | 3.9973 | 4.0141 | 3.9592 | 3.9987 | 3.991 | 3.9729 | 4.011 | 3.9859 | 4.0076 | 4.0001 | 4.0398 | 4.0435 | 4.0185 | 4.0099 | 4.0353 | 4.0203 | 4.0064 | 4.0789 | 4.0877 | 4.1454 | 4.1667 | 4.0547 | 4.0408 | 4.158 | 4.124 | 4.0868 | 4.1284 | 4.1698 | 4.0323 | 4.0047 | 4.1004 | 4.0623 | 5.0235 | 4.1074 | 3.2203 | 4.9864 | 3.5878 | 4.0272 | 3.9947 | 3.997 | 3.9917 | 3.8711 | 3.9486 | 4.0348 | 3.9694 | 3.9078 | 4.0461 | 4.0311 | 3.9974 | 4.0291 | 4.0619 | 3.9948 | 3.9909 | 3.9989 | 4.0381 | 4.0099 | 4.0083 | 4.0193 | 4.2703 | 3.9932 | 3.9845 | 4.0474 | 4.0091 | 4.0113 | 4.0155 | 4.059 | 4.0468 | 4.0444 | 4.0695 | 3.998 | 4.075 | 4.0323 | 4.0241 | 3.9938 | 4.025 | 3.9618 | 3.9904 | 3.9532 | 3.9682 | 3.9619 | 4.0323 | 3.9751 | 3.9437 | 3.9549 | 3.9497 | 3.9732 | 4.0573 | 3.9317 | 3.9392 | 4.0585 | 4.0632 | 4.011 | 4.0742 | 3.9893 | 4.1007 | 4.0529 | 4.0738 | 4.039 | 4.0734 | 4.0229 | 4.0801 | 4.0981 | 4.0338 | 4.0746 | 4.2268 | 4.0618 | 3.9738 | 4.0518 | 4.1071 | 4.0624 | 3.9972 | 4.0117 | 4.102 | 4.027 | 4.0966 | 4.0763 | 3.989 | 4.0353 | 3.9969 | 4.0235 | 4.0973 | 4.0914 | 4.1177 | 4.1068 | 4.003
2025-04-04 | 3.0678 | 2.9561 | 3.0856 | 3.0841 | 3.0826 | 2.9575 | 3.1477 | 3.022 | 3.122 | 3.122 | 3.1182 | 3.1114 | 3.1114 | 3.1144 | 3.1205 | 3.1515 | 3.3038 | 3.0917 | 2.9705 | 3.1083 | 3.1379 | 3.2174 | 3.1947 | 3.2167 | 3.2091 | 3.2174 | 3.2114 | 3.2212 | 3.2068 | 3.228 | 3.2333 | 3.2038 | 3.2061 | 3.2297 | 3.0303 | 3.0526 | 3.0877 | 3.1284 | 2.9705 | 3.2592 | 2.9462 | 2.806 | 3.0201 | 3.3523 | 3.1601 | 3.1534 | 2.9209 | 3.0289 | 2.9639 | 3.3538 | 3.7947 | 3.3256 | 3.1566 | 2.98 | 2.9717 | 3.161 | 2.9812 | 3.1438 | 3.7085 | 2.9562 | 2.8273 | 3.3861 | 2.9912 | 3.393 | 3.3192 | 3.3313 | 3.3454 | 3.4055 | 3.37 | 3.2957 | 3.3627 | 3.4251 | 3.3047 | 3.3372 | 3.3026 | 3.3532 | 3.2872 | 3.3423 | 3.3734 | 3.3709 | 3.3734 | 3.3896 | 3.352 | 3.4055 | 3.403 | 3.3791 | 3.3701 | 3.3648 | 3.3703 | 3.3257 | 3.3382 | 3.2888 | 3.3364 | 3.3571 | 2.9065 | 3.3961 | 3.3863 | 3.3813 | 3.3547 | 3.3402 | 3.3546 | 3.334 | 3.2626 | 3.2885 | 3.521 | 3.4079 | 3.4092 | 3.3796 | 3.3527 | 3.4168 | 3.4092 | 3.4517 | 3.3806 | 3.3856 | 3.3644 | 3.451 | 3.4106 | 3.4092 | 3.4375 | 3.403 | 3.401 | 3.4003 | 3.3709 | 3.4012 | 3.3316 | 3.4034 | 3.4103 | 3.3999 | 3.3613 | 3.3578 | 3.353 | 3.421 | 3.3768 | 3.4213 | 3.3458 | 3.4161 | 3.4607 | 3.4489 | 3.4079 | 3.3468 | 3.3375 | 3.4127 | 3.4244 | 3.3609 | 3.4231 | 3.4362 | 3.3989 | 3.403 | 3.3595 | 3.3279 | 3.8373 | 3.3606 | 3.4565 | 3.403 | 3.4448 | 3.3709 | 3.3989 | 3.4237 | 3.4372 | 3.3606 | 3.3713 | 3.3703 | 3.3282 | 3.4742 | 3.5235 | 3.3579 | 3.3178 | 3.3757 | 3.3042 | 3.3042 | 3.3454 | 3.3375 | 3.3575 | 3.4293 | 3.4365 | 3.3624 | 3.3878 | 3.3957 | 3.3998 | 3.2933 | 3.3629 | 3.324 | 3.4078 | 3.3912 | 3.3995 | 3.4184 | 3.3832 | 3.4274 | 3.3613 | 3.404 | 3.3462 | 3.398 | 3.3405 | 3.3741 | 3.4052 | 3.3794 | 3.4123 | 3.2762 | 3.3625 | 3.3477 | 3.3545 | 3.3578 | 3.3845 | 3.3497 | 3.4001 | 3.4078 | 3.4353 | 3.3431 | 3.3834 | 3.3199 | 3.3209 | 3.5122 | 3.2149 | 3.3689 | 3.3752 | 3.3955 | 3.3971 | 3.3451 | 3.2967 | 3.302 | 3.3125 | 3.273 | 3.2051 | 3.1999 | 3.2932 | 3.0219 | 3.2282 | 3.3149 | 3.3191 | 3.3195 | 3.2991 | 3.2881 | 3.272 | 3.3083 | 3.3403 | 3.3528 | 3.3442 | 3.2861 | 2.0068 | 3.3027 | 1.9496 | 3.3027 | 3.3328 | 3.3426 | 3.3046 | 3.3359 | 3.3163 | 3.2702 | 3.5283 | 3.3173 | 3.3217 | 3.3229 | 2.086 | 3.272 | 3.1663 | 3.3068 | 3.3008 | 3.3003 | 3.3003 | 3.3513 | 3.3601 | 3.4028 | 3.4301 | 3.4006 | 3.4038 | 3.4237 | 3.3964 | 3.3646 | 3.3959 | 3.4345 | 3.3154 | 3.2976 | 3.3711 | 3.3487 | 4.5046 | 4.4087 | 2.6551 | 4.1048 | 3.3888 | 3.3341 | 3.2959 | 3.3016 | 3.2937 | 3.237 | 3.2755 | 3.3246 | 3.2759 | 3.2419 | 3.3379 | 3.3254 | 3.3107 | 3.322 | 3.3571 | 3.3222 | 3.3087 | 3.3097 | 3.336 | 3.3144 | 3.3166 | 3.3257 | 4.2703 | 3.2988 | 3.3045 | 3.3318 | 3.3159 | 3.3195 | 3.3151 | 3.3602 | 3.3488 | 3.3389 | 2.7186 | 2.3336 | 3.1369 | 3.2885 | 3.2761 | 3.2485 | 3.2484 | 3.2442 | 2.2924 | 3.0566 | 3.2578 | 2.7606 | 3.3539 | 2.5577 | 3.309 | 2.8018 | 3.2227 | 2.1597 | 3.3629 | 3.283 | 2.894 | 1.7504 | 2.2194 | 3.8462 | 1.7159 | 3.29 | 3.3816 | 3.3546 | 3.349 | 3.3442 | 3.3539 | 3.3094 | 3.3681 | 3.3857 | 3.3251 | 3.3709 | 3.8932 | 3.3591 | 3.2893 | 3.3556 | 3.4038 | 3.3738 | 2.8919 | 3.2732 | 3.4007 | 3.3046 | 3.395 | 3.3591 | 3.3014 | 3.3516 | 3.3002 | 3.3254 | 3.3905 | 3.3744 | 3.4125 | 3.3936 | 3.2838
2025-04-05 | 3.953 | 3.8118 | 3.9811 | 3.9758 | 3.9697 | 3.8033 | 4.0413 | 3.8803 | 4.0091 | 4.0098 | 4.0189 | 4.0053 | 4.0068 | 4.0076 | 4.0515 | 4.0492 | 3.9801 | 4.0064 | 3.9773 | 4.0235 | 4.1295 | 4.0917 | 4.1455 | 4.1106 | 4.1174 | 4.1152 | 4.1242 | 4.1091 | 4.1341 | 4.1379 | 4.103 | 4.1129 | 3.9485 | 3.8971 | 3.9354 | 3.9713 | 4.0303 | 4.0351 | 3.9917 | 3.996 | 3.8758 | 4.0071 | 4.1026 | 4.0731 | 4.0885 | 4.1881 | 4.1729 | 4.1331 | 4.0697 | 4.0942 | 4.1122 | 4.0109 | 3.9805 | 3.9931 | 3.9247 | 4.0336 | 4.004 | 3.8177 | 3.8219 | 3.7962 | 3.9932 | 3.9307 | 3.9765 | 4.3723 | 4.2874 | 4.2849 | 4.3202 | 4.393 | 4.3394 | 4.2495 | 4.3368 | 4.4127 | 4.2636 | 4.2824 | 4.2647 | 4.3254 | 4.246 | 4.3178 | 4.3551 | 4.3416 | 4.3178 | 4.3724 | 4.3188 | 4.3929 | 4.3892 | 4.3535 | 4.3485 | 4.3273 | 4.334 | 4.295 | 4.3133 | 4.2219 | 4.2912 | 4.3192 | 3.6905 | 4.3703 | 4.3597 | 4.3402 | 4.3344 | 4.2157 | 4.3142 | 4.3026 | 4.209 | 4.3785 | 4.5445 | 4.3813 | 4.3996 | 4.3637 | 4.3368 | 4.4082 | 4.403 | 4.4496 | 4.3598 | 4.3669 | 4.3416 | 4.4586 | 4.3965 | 4.403 | 4.4237 | 4.3944 | 4.3837 | 4.3796 | 4.3485 | 4.3831 | 4.4023 | 4.383 | 4.391 | 4.3796 | 4.342 | 4.3333 | 4.3309 | 4.4148 | 4.3602 | 4.4099 | 4.3237 | 4.411 | 4.4545 | 4.461 | 4.4051 | 3.8006 | 4.3119 | 4.4099 | 4.4227 | 4.3623 | 4.3375 | 4.4403 | 4.3623 | 4.3986 | 4.3433 | 4.3063 | 4.3468 | 4.3471 | 4.4615 | 4.4006 | 4.4524 | 4.3575 | 4.4134 | 4.4237 | 4.3551 | 4.3468 | 4.3561 | 4.3578 | 4.3002 | 4.4881 | 4.5449 | 4.342 | 4.328 | 4.3964 | 4.3069 | 4.3039 | 4.3526 | 4.3473 | 4.3711 | 4.452 | 4.4645 | 4.3673 | 4.4085 | 4.418 | 4.421 | 4.2937 | 4.3814 | 4.3387 | 4.4324 | 4.4131 | 4.4206 | 4.4399 | 4.4029 | 4.458 | 4.3832 | 4.4286 | 4.3579 | 4.4274 | 4.3454 | 4.3942 | 4.4337 | 4.3984 | 4.427 | 4.2598 | 4.3623 | 4.3395 | 4.3523 | 4.3502 | 4.3773 | 4.3459 | 4.4069 | 4.4022 | 4.4437 | 4.3203 | 4.3685 | 4.2924 | 4.2942 | 4.5383 | 4.3515 | 4.3497 | 4.3858 | 4.3905 | 4.3985 | 4.3341 | 4.2916 | 4.2361 | 4.292 | 4.248 | 4.1643 | 4.1519 | 4.2775 | 4.2167 | 4.3346 | 4.3767 | 4.3254 | 4.3599 | 4.3779 | 4.316 | 4.429 | 4.3134 | 4.3987 | 4.3658 | 4.3509 | 4.3611 | 4.3287 | 4.316 | 4.3048 | 4.3171 | 4.3929 | 4.4435 | 4.332 | 4.3571 | 4.3418 | 4.2947 | 4.5604 | 4.3235 | 4.3425 | 4.3294 | 4.3679 | 4.3795 | 4.3474 | 4.3351 | 4.3676 | 4.3075 | 4.2758 | 4.3516 | 4.359 | 4.4196 | 4.446 | 4.407 | 4.3215 | 4.4331 | 4.3932 | 4.355 | 4.3956 | 4.4518 | 4.3132 | 4.2854 | 4.3784 | 4.3335 | 5.3489 | 4.3764 | 3.4322 | 5.3243 | 3.8244 | 4.3485 | 4.3095 | 4.3103 | 4.3027 | 4.1882 | 4.2695 | 4.3462 | 4.2819 | 4.2128 | 4.3673 | 4.3378 | 4.3152 | 4.3439 | 4.3893 | 4.3175 | 4.3052 | 4.3109 | 4.3562 | 4.3276 | 4.3208 | 4.3398 | 4.0768 | 4.3041 | 4.3015 | 4.3523 | 4.3276 | 4.3283 | 4.3276 | 4.3791 | 4.3623 | 4.3563 | 4.4141 | 4.3465 | 4.421 | 4.3612 | 4.3496 | 4.3175 | 4.3619 | 4.2803 | 4.3096 | 4.2707 | 4.3042 | 4.3159 | 4.3814 | 4.3336 | 4.3022 | 4.2909 | 4.2853 | 4.2973 | 4.3834 | 4.2818 | 4.2908 | 4.3607 | 4.4333 | 4.427 | 4.4243 | 4.2681 | 4.4008 | 4.3646 | 4.3799 | 4.3537 | 4.3836 | 4.3257 | 4.3926 | 4.4244 | 4.3496 | 4.4172 | 4.5604 | 4.3844 | 4.2981 | 4.3352 | 4.4301 | 4.3731 | 4.4778 | 4.3096 | 4.4152 | 4.3278 | 4.4087 | 4.3706 | 4.2975 | 4.362 | 4.3128 | 4.3418 | 4.4142 | 4.3093 | 4.447 | 4.4227 | 4.2957
2025-04-06 | 3.4545 | 3.3405 | 3.4773 | 3.4773 | 3.4758 | 3.3341 | 3.5455 | 3.4068 | 3.5144 | 3.525 | 3.5182 | 3.5121 | 3.5152 | 3.5311 | 3.5614 | 3.5538 | 3.4936 | 3.5311 | 3.503 | 3.5455 | 3.6364 | 3.6106 | 3.6583 | 3.6583 | 3.6379 | 3.6333 | 3.6447 | 3.6295 | 3.6485 | 3.6636 | 3.6258 | 3.6439 | 3.4644 | 3.4211 | 3.4474 | 3.4872 | 3.5375 | 3.551 | 3.503 | 3.5072 | 3.4008 | 3.5193 | 3.6012 | 3.598 | 3.6104 | 3.6954 | 3.683 | 3.6593 | 3.6112 | 3.6336 | 3.6481 | 3.5722 | 3.531 | 3.5397 | 3.4758 | 3.5696 | 3.5376 | 3.3864 | 3.3826 | 3.3686 | 3.4939 | 3.4976 | 3.5411 | 3.8537 | 3.7723 | 3.766 | 3.7909 | 3.8499 | 3.7992 | 3.7405 | 3.8119 | 3.8744 | 3.745 | 3.7635 | 3.7415 | 3.7904 | 3.7208 | 3.814 | 3.9821 | 3.8375 | 4.0097 | 3.8575 | 3.8161 | 3.9322 | 3.8727 | 3.8442 | 3.8384 | 3.8172 | 3.8188 | 3.8095 | 3.7971 | 3.676 | 3.7616 | 3.7678 | 3.8292 | 3.862 | 3.8419 | 3.8175 | 3.7857 | 3.6385 | 3.7821 | 3.7736 | 3.6921 | 3.8344 | 3.8789 | 3.8316 | 3.8475 | 3.813 | 3.7809 | 3.8613 | 3.8599 | 3.8989 | 3.8201 | 3.8427 | 3.7867 | 3.8906 | 3.8364 | 3.8395 | 3.8644 | 3.8371 | 3.8316 | 3.8323 | 3.8012 | 3.8297 | 3.8554 | 3.8368 | 3.8423 | 3.834 | 3.7926 | 3.7926 | 3.7909 | 3.8685 | 3.8175 | 3.8696 | 3.7819 | 3.852 | 3.9073 | 3.8371 | 3.8844 | 3.568 | 3.8647 | 3.8986 | 3.9055 | 3.8489 | 3.8102 | 3.9206 | 3.8716 | 3.8799 | 3.8257 | 3.8009 | 3.8306 | 3.8226 | 3.9297 | 3.8734 | 3.9165 | 3.8437 | 3.8851 | 3.8968 | 3.9113 | 3.8361 | 3.8427 | 3.8499 | 3.7957 | 3.9428 | 3.9976 | 3.8286 | 3.8503 | 3.918 | 3.836 | 3.8299 | 3.8779 | 3.8636 | 3.8878 | 3.9569 | 3.9758 | 3.8934 | 3.941 | 3.9418 | 3.9422 | 3.827 | 3.9056 | 3.8698 | 3.9588 | 3.9376 | 3.9433 | 3.9626 | 3.9301 | 3.9777 | 3.9093 | 3.9528 | 3.8893 | 3.9478 | 3.8696 | 3.9123 | 3.9556 | 3.9194 | 3.9429 | 3.797 | 3.8984 | 3.8689 | 3.8915 | 3.8946 | 3.9243 | 3.8838 | 3.9434 | 3.9488 | 3.9775 | 3.8672 | 3.9054 | 3.8432 | 3.8444 | 4.0504 | 3.8955 | 3.905 | 3.9215 | 3.9343 | 3.9399 | 3.8771 | 3.8265 | 3.7893 | 3.8464 | 3.8207 | 3.7328 | 3.7223 | 3.7779 | 3.7516 | 3.7951 | 3.849 | 3.8662 | 3.8854 | 3.8277 | 3.8177 | 3.8768 | 3.7875 | 3.8999 | 3.8387 | 3.8363 | 3.8528 | 3.7815 | 3.7916 | 3.7422 | 3.7849 | 3.8513 | 3.898 | 3.7995 | 3.8312 | 3.8426 | 3.7763 | 3.956 | 3.8065 | 3.814 | 3.8043 | 3.8256 | 3.8529 | 3.8174 | 3.8065 | 3.8376 | 3.7916 | 3.7667 | 3.8308 | 3.8424 | 3.8941 | 3.925 | 3.8963 | 3.8937 | 3.9214 | 3.8905 | 3.8574 | 3.8986 | 3.9401 | 3.8032 | 3.7846 | 3.8768 | 3.8377 | 4.7466 | 3.8924 | 3.0442 | 4.7178 | 3.3955 | 3.822 | 3.7891 | 3.7989 | 3.7952 | 3.7075 | 3.7634 | 3.8254 | 3.7668 | 3.7226 | 3.8469 | 3.8261 | 3.8042 | 3.8303 | 3.8639 | 3.8063 | 3.8087 | 3.8086 | 3.8497 | 3.8214 | 3.8187 | 3.8377 | 3.5029 | 4.6784 | 3.8028 | 3.8039 | 3.8578 | 4.2335 | 3.4577 | 3.8122 | 4.0599 | 3.8532 | 3.8622 | 3.8264 | 3.8841 | 3.8372 | 3.8275 | 3.8032 | 3.8393 | 3.7796 | 3.7987 | 3.7709 | 3.7845 | 3.7841 | 3.8619 | 3.8024 | 3.7856 | 3.7796 | 3.7688 | 3.774 | 3.8637 | 3.7747 | 3.7951 | 3.8305 | 3.9172 | 3.8854 | 3.8756 | 3.7497 | 3.866 | 3.8342 | 3.8409 | 3.8361 | 3.8503 | 3.8013 | 3.8619 | 3.888 | 3.8234 | 3.8901 | 3.9286 | 3.8566 | 3.7772 | 3.8536 | 3.8976 | 3.8404 | 3.7561 | 3.7834 | 3.8807 | 3.8037 | 3.8787 | 3.8376 | 3.7712 | 3.8368 | 3.7885 | 3.823 | 3.88 | 3.8622 | 3.9058 | 3.8936 | 3.7952
2025-04-07 | 3.4601 | 3.3716 | 3.4992 | 3.5008 | 3.4758 | 3.3295 | 3.5624 | 3.4129 | 3.5076 | 3.5212 | 3.5356 | 3.5167 | 3.5205 | 3.5265 | 3.5561 | 3.5606 | 3.4984 | 3.5311 | 3.5098 | 3.5492 | 3.6477 | 3.6159 | 3.6561 | 3.6333 | 3.6242 | 3.6364 | 3.6205 | 3.6371 | 3.6614 | 3.6697 | 3.6318 | 3.6447 | 3.4598 | 3.4083 | 3.4514 | 3.4841 | 3.5447 | 3.5463 | 3.4894 | 3.5064 | 3.4076 | 3.5292 | 3.6006 | 3.5928 | 3.6016 | 3.6918 | 3.6763 | 3.6398 | 3.6082 | 3.6267 | 3.6283 | 3.5402 | 3.5115 | 3.5259 | 3.4675 | 3.5549 | 3.5437 | 3.3997 | 3.3946 | 3.3762 | 3.525 | 3.4841 | 3.5029 | 3.8554 | 3.785 | 3.7795 | 3.8244 | 3.8789 | 3.8258 | 3.7612 | 3.823 | 3.8803 | 3.7533 | 3.7538 | 3.7457 | 3.7897 | 3.7186 | 3.8126 | 3.8458 | 3.8337 | 3.8071 | 3.8614 | 3.8133 | 3.8784 | 3.8768 | 3.8398 | 3.8362 | 3.8248 | 3.8282 | 3.7895 | 3.8054 | 3.6946 | 3.7954 | 3.7992 | 3.8765 | 3.8885 | 3.874 | 3.8244 | 3.8161 | 3.8084 | 3.7976 | 3.8033 | 3.7168 | 3.864 | 4.0041 | 3.8409 | 3.883 | 3.8351 | 3.8316 | 3.8961 | 3.8913 | 3.9206 | 3.8439 | 3.8528 | 3.8278 | 3.9382 | 3.8772 | 3.8906 | 3.8989 | 3.8879 | 3.8706 | 3.8575 | 3.8304 | 3.8589 | 3.8751 | 3.8599 | 3.8658 | 3.8599 | 3.824 | 3.8137 | 3.8106 | 3.8882 | 3.8378 | 3.8806 | 3.7978 | 3.8727 | 3.9221 | 3.9055 | 3.8502 | 3.6339 | 3.7654 | 3.852 | 3.8651 | 3.8188 | 3.6632 | 3.8937 | 3.8171 | 3.824 | 3.7976 | 3.7698 | 3.8143 | 3.8019 | 3.9033 | 3.8502 | 3.9144 | 3.8316 | 3.882 | 3.8854 | 3.901 | 3.8092 | 3.824 | 3.8192 | 3.7685 | 3.9484 | 3.9965 | 3.8063 | 3.7513 | 3.8216 | 3.74 | 3.7373 | 3.7804 | 3.7842 | 3.8129 | 3.8764 | 3.8964 | 3.8057 | 3.8258 | 3.8424 | 3.8613 | 3.7325 | 3.8144 | 3.7803 | 3.8692 | 3.8473 | 3.8617 | 3.8866 | 3.8439 | 3.9017 | 3.825 | 3.8662 | 3.8039 | 3.8719 | 3.8035 | 3.8515 | 3.8798 | 3.8508 | 3.8639 | 3.7131 | 3.8088 | 3.781 | 3.7921 | 3.7864 | 3.8021 | 3.7847 | 3.8366 | 3.8358 | 3.8659 | 3.7484 | 3.7873 | 3.7322 | 3.7195 | 3.914 | 3.8079 | 3.7947 | 3.8395 | 3.8288 | 3.8441 | 3.7642 | 3.7193 | 3.6667 | 3.7344 | 3.6862 | 3.6336 | 3.6006 | 3.7211 | 3.6726 | 3.8315 | 3.8679 | 3.8744 | 3.8858 | 3.8536 | 3.8301 | 3.8881 | 3.789 | 3.9156 | 3.8199 | 3.8285 | 3.8626 | 3.7759 | 3.7871 | 3.7482 | 3.7807 | 3.8689 | 3.9019 | 3.7971 | 3.792 | 3.8379 | 3.771 | 3.9639 | 3.7725 | 3.7972 | 3.777 | 3.8084 | 3.8196 | 3.7935 | 3.7886 | 3.8077 | 3.7958 | 3.7558 | 3.838 | 3.8417 | 3.9016 | 3.9155 | 3.8713 | 3.877 | 3.8982 | 3.8622 | 3.8284 | 3.8715 | 3.9135 | 3.796 | 3.79 | 3.87 | 3.8239 | 3.8479 | 3.8457 | 3.8724 | 3.8974 | 3.8487 | 3.8284 | 3.7993 | 3.7993 | 3.7974 | 3.6927 | 3.7543 | 3.8345 | 3.7721 | 3.7113 | 3.836 | 3.8133 | 3.794 | 3.8296 | 3.8615 | 3.794 | 3.7865 | 3.7915 | 3.8303 | 3.8051 | 3.7941 | 3.8206 | 3.5666 | 3.7816 | 3.7831 | 3.8328 | 3.8047 | 3.8059 | 3.8002 | 3.8519 | 3.8349 | 3.8321 | 3.9215 | 3.8335 | 3.9131 | 3.8488 | 3.8405 | 3.8136 | 3.8472 | 3.7813 | 3.6686 | 3.7948 | 3.7943 | 3.8046 | 3.8708 | 3.8334 | 3.7886 | 3.8129 | 3.7957 | 3.8185 | 3.883 | 3.7908 | 3.7892 | 3.9184 | 3.9392 | 3.9168 | 3.9513 | 3.7699 | 3.9052 | 3.8488 | 3.8955 | 3.8533 | 3.8809 | 3.8495 | 3.8899 | 3.928 | 3.8622 | 3.9062 | 3.9246 | 3.8959 | 3.8086 | 3.8724 | 3.9305 | 3.8604 | 3.8148 | 3.8383 | 3.9007 | 3.8483 | 3.9004 | 3.8968 | 3.8124 | 3.8704 | 3.8226 | 3.8513 | 3.9147 | 3.9301 | 3.9435 | 3.9254 | 3.7794
2025-04-08 | 4.2161 | 4.0885 | 4.2568 | 4.2515 | 4.2439 | 4.0714 | 4.3236 | 4.1462 | 4.2856 | 4.2894 | 4.2985 | 4.2833 | 4.2879 | 4.2894 | 4.3326 | 4.3326 | 4.26 | 4.2703 | 4.2371 | 4.2917 | 4.4091 | 4.3591 | 4.4068 | 4.3932 | 4.3765 | 4.3909 | 4.4015 | 4.3841 | 4.4045 | 4.4114 | 4.3765 | 4.3886 | 4.2197 | 4.1683 | 4.2121 | 4.2456 | 4.3126 | 4.3182 | 4.2727 | 4.2711 | 4.1523 | 4.286 | 4.387 | 4.3692 | 4.356 | 4.4682 | 4.4444 | 4.3945 | 4.3423 | 4.3699 | 4.3783 | 4.2785 | 4.2439 | 4.2429 | 4.183 | 4.282 | 4.1714 | 4.0722 | 4.0631 | 4.0466 | 4.25 | 4.1911 | 4.2346 | 4.6705 | 4.5794 | 4.5701 | 4.6128 | 4.6888 | 4.6325 | 4.5397 | 4.6325 | 4.7108 | 4.559 | 4.5703 | 4.5604 | 4.618 | 4.5368 | 4.6077 | 4.5604 | 4.6318 | 4.6111 | 4.6667 | 4.6142 | 4.6901 | 4.5618 | 4.654 | 4.6429 | 4.5965 | 4.6242 | 4.5849 | 4.6052 | 4.5269 | 4.6329 | 4.6232 | 4.6805 | 4.7091 | 4.6765 | 4.6456 | 4.6201 | 4.7009 | 4.627 | 4.5942 | 4.4964 | 4.6698 | 4.8937 | 4.6939 | 4.695 | 4.656 | 4.6315 | 4.7039 | 4.6984 | 4.7453 | 2.4875 | 4.6595 | 4.6211 | 4.7509 | 4.6877 | 4.6988 | 4.7157 | 4.6884 | 4.6801 | 4.6749 | 4.6403 | 4.6739 | 4.6991 | 4.676 | 4.6853 | 4.6767 | 4.636 | 4.6259 | 4.6273 | 4.7136 | 4.6567 | 4.7032 | 4.6163 | 4.7026 | 4.75 | 4.766 | 4.6651 | 4.0573 | 4.5549 | 4.7126 | 4.7243 | 4.6615 | 4.6108 | 4.7467 | 4.7112 | 4.7172 | 4.7341 | 4.6035 | 4.669 | 4.7374 | 4.8583 | 4.6929 | 4.7526 | 4.6563 | 4.7143 | 4.7212 | 4.7398 | 4.6456 | 4.6542 | 4.6498 | 4.5887 | 4.756 | 4.8302 | 4.6418 | 4.6304 | 4.7003 | 4.6126 | 4.6077 | 4.6546 | 4.655 | 4.6833 | 4.7627 | 4.7797 | 4.6757 | 4.7109 | 4.72 | 4.7298 | 4.5937 | 4.6847 | 4.6313 | 4.7332 | 4.7154 | 4.7294 | 4.7555 | 4.7079 | 4.7687 | 4.6841 | 4.7373 | 4.6572 | 4.7317 | 4.6429 | 4.6965 | 4.7373 | 4.7004 | 4.7278 | 4.5526 | 4.6587 | 4.6401 | 4.6509 | 4.6475 | 4.675 | 4.6487 | 4.7116 | 4.6995 | 4.7492 | 4.6097 | 4.6636 | 4.5907 | 4.5813 | 4.8217 | 4.6455 | 4.6374 | 4.6911 | 4.6865 | 4.6968 | 4.6263 | 4.5774 | 4.5219 | 4.5778 | 4.5314 | 4.452 | 4.4297 | 4.5606 | 4.4813 | 4.6646 | 4.7121 | 4.7162 | 4.7418 | 4.6935 | 4.6718 | 4.7351 | 4.6135 | 4.7645 | 4.6637 | 4.6684 | 4.6998 | 4.6352 | 4.6102 | 4.6053 | 4.6068 | 4.7088 | 4.761 | 4.633 | 4.655 | 4.6821 | 4.5911 | 4.8077 | 4.615 | 4.6348 | 4.6217 | 4.6737 | 4.6823 | 4.6419 | 4.6303 | 4.6666 | 4.595 | 4.5551 | 4.6454 | 4.6482 | 4.7118 | 4.7272 | 4.7019 | 4.7003 | 4.726 | 4.683 | 4.6427 | 4.6896 | 4.74 | 4.5928 | 4.589 | 4.6409 | 4.6409 | 4.6782 | 4.6786 | 4.6935 | 4.7298 | 4.6596 | 4.6281 | 4.5922 | 4.5922 | 4.5847 | 4.4448 | 4.5416 | 4.6323 | 4.5605 | 4.4883 | 4.65 | 4.618 | 4.5975 | 4.6364 | 4.679 | 4.5917 | 4.5901 | 4.5921 | 4.6435 | 4.6113 | 4.6049 | 4.6295 | 4.5112 | 4.5897 | 4.5851 | 4.6485 | 4.6128 | 4.6092 | 4.6083 | 4.6629 | 4.6492 | 4.646 | 4.7068 | 4.6287 | 4.7115 | 4.6401 | 4.6326 | 4.6027 | 4.648 | 4.5613 | 4.6266 | 4.5529 | 4.5777 | 4.5942 | 4.6629 | 4.6135 | 4.5788 | 4.5735 | 4.5653 | 4.5915 | 4.6705 | 4.5667 | 4.5816 | 4.6723 | 4.7178 | 4.6703 | 4.7469 | 4.5305 | 4.6789 | 4.6412 | 4.6558 | 4.6341 | 4.6487 | 4.6094 | 4.6576 | 4.7144 | 4.6311 | 4.7009 | 4.6821 | 4.68 | 4.5861 | 4.6546 | 4.7186 | 4.655 | 4.5574 | 4.492 | 4.708 | 4.6129 | 4.7006 | 4.666 | 4.5863 | 4.6539 | 4.5985 | 4.6232 | 4.7038 | 4.7002 | 4.7378 | 4.7135 | 4.5816
2025-04-09 | 2.177 | 2.1204 | 2.1962 | 2.1932 | 2.1811 | 2.0949 | 2.2379 | 2.1356 | 2.1985 | 2.2015 | 2.2136 | 2.1955 | 2.2129 | 2.1977 | 2.222 | 2.2326 | 2.1834 | 2.2057 | 2.1909 | 2.2144 | 2.2818 | 2.2583 | 2.2841 | 2.2833 | 2.275 | 2.2735 | 2.2902 | 2.2811 | 2.297 | 2.2902 | 2.2758 | 2.2758 | 2.1848 | 2.1308 | 2.1643 | 2.189 | 2.2249 | 2.2129 | 2.1894 | 2.2065 | 2.1432 | 2.2418 | 2.2836 | 2.2961 | 2.2778 | 2.3423 | 2.3231 | 2.2937 | 2.2408 | 2.2736 | 2.2749 | 2.2067 | 2.1926 | 2.2057 | 2.1747 | 2.2197 | 2.1868 | 2.1276 | 2.127 | 2.1203 | 2.2136 | 2.1871 | 2.1848 | 2.4124 | 2.3751 | 2.3759 | 2.4017 | 2.4296 | 2.3923 | 2.3451 | 2.3958 | 2.4262 | 2.353 | 2.3478 | 2.3502 | 2.3788 | 2.3395 | 2.3954 | 2.4196 | 2.412 | 2.3844 | 2.4236 | 2.3916 | 2.4278 | 2.4282 | 2.3968 | 2.4019 | 2.3929 | 2.4023 | 2.3789 | 2.3872 | 2.3199 | 2.3723 | 2.3713 | 2.4206 | 2.4099 | 2.4098 | 2.3685 | 2.4072 | 2.4123 | 2.3658 | 2.4023 | 2.3782 | 2.4137 | 2.5324 | 2.3885 | 2.4341 | 2.4469 | 2.4607 | 2.4669 | 2.442 | 2.4517 | 2.4044 | 2.4116 | 2.4017 | 2.4748 | 2.4337 | 2.4496 | 2.4489 | 2.4503 | 2.4306 | 2.422 | 2.4037 | 2.4232 | 2.4393 | 2.4334 | 2.431 | 2.4351 | 2.4072 | 2.3999 | 2.3709 | 2.4555 | 2.4244 | 2.4565 | 2.3992 | 2.4389 | 2.4859 | 2.5131 | 2.4676 | 2.4193 | 2.412 | 2.4707 | 2.4748 | 2.4465 | 2.4227 | 2.4931 | 2.4589 | 2.4614 | 2.4587 | 2.403 | 2.4397 | 2.4672 | 2.5102 | 2.4431 | 2.479 | 2.4334 | 2.461 | 2.4569 | 2.4624 | 2.4237 | 2.4289 | 2.4344 | 2.4079 | 2.4934 | 2.5276 | 2.4232 | 2.4165 | 2.472 | 2.3995 | 2.3961 | 2.3624 | 2.4146 | 2.4358 | 2.4656 | 2.5008 | 2.4441 | 2.458 | 2.4879 | 2.4958 | 2.4111 | 2.4665 | 2.4398 | 2.4822 | 2.4807 | 2.4845 | 2.4762 | 2.463 | 2.4841 | 2.458 | 2.4633 | 2.4335 | 2.4735 | 2.4233 | 2.4569 | 2.4635 | 2.4413 | 2.4675 | 2.394 | 2.3558 | 2.4494 | 2.3359 | 2.4579 | 2.464 | 2.4532 | 2.4886 | 2.4942 | 2.507 | 2.4336 | 2.4468 | 2.4232 | 2.4022 | 2.4718 | 2.464 | 2.4482 | 2.4808 | 2.4739 | 2.4767 | 2.4355 | 2.4199 | 2.3804 | 2.4363 | 2.3937 | 2.3691 | 2.3393 | 2.3688 | 2.3863 | 2.4383 | 2.4657 | 2.4772 | 2.4698 | 2.4419 | 2.4067 | 2.4745 | 2.418 | 2.511 | 2.436 | 2.4462 | 2.4698 | 2.4157 | 2.4041 | 2.4026 | 2.4146 | 2.4953 | 2.5098 | 2.4435 | 2.4183 | 2.4623 | 2.4266 | 2.551 | 2.418 | 2.4262 | 2.4153 | 2.4867 | 2.4602 | 2.4101 | 2.4262 | 2.4393 | 2.4058 | 2.3706 | 2.4346 | 2.4335 | 2.4764 | 2.4938 | 2.4466 | 2.4652 | 2.4611 | 2.434 | 2.4145 | 2.3548 | 2.4685 | 2.4087 | 2.4049 | 2.4538 | 2.4248 | 2.4381 | 2.4276 | 2.4483 | 2.4643 | 2.4311 | 2.4033 | 2.3957 | 2.3655 | 2.3579 | 2.3057 | 2.3443 | 2.4089 | 2.3583 | 2.3076 | 2.4063 | 2.4669 | 2.401 | 2.4392 | 2.4361 | 2.3829 | 2.3484 | 2.3573 | 2.3957 | 2.3792 | 2.3629 | 2.3864 | 1.9495 | 2.3716 | 2.3606 | 2.3986 | 2.386 | 2.4226 | 2.4039 | 2.4864 | 2.4694 | 2.4036 | 2.4863 | 2.3899 | 2.4746 | 2.4303 | 2.4131 | 2.3937 | 2.4294 | 2.3676 | 2.4191 | 2.4179 | 2.3642 | 2.3936 | 2.4538 | 2.4337 | 2.3974 | 2.4172 | 2.4116 | 2.4288 | 2.4749 | 2.3905 | 2.4015 | 2.4812 | 2.5 | 2.5118 | 2.5126 | 2.3899 | 2.4665 | 2.434 | 2.4677 | 2.3981 | 2.4546 | 2.4669 | 2.4516 | 2.4864 | 2.431 | 2.4596 | 2.4725 | 2.4684 | 2.399 | 2.4294 | 2.4816 | 2.4265 | 2.4082 | 2.2995 | 2.438 | 2.4187 | 2.4344 | 2.4657 | 2.3905 | 2.418 | 2.3897 | 2.4188 | 2.4539 | 2.4839 | 2.4847 | 2.4568 | 2.3915
2025-04-10 | 3.5502 | 3.4593 | 3.5826 | 3.5833 | 3.5765 | 3.429 | 3.6519 | 3.4992 | 3.6159 | 3.6227 | 3.622 | 3.6091 | 3.6205 | 3.6227 | 3.6591 | 3.6538 | 3.5933 | 3.614 | 3.5879 | 3.6326 | 3.7295 | 3.6924 | 3.7341 | 3.7167 | 3.7189 | 3.7174 | 3.7288 | 3.7144 | 3.7333 | 3.7424 | 3.7091 | 3.7235 | 3.5644 | 3.5183 | 3.5518 | 3.5853 | 3.6419 | 3.6411 | 3.5977 | 3.6069 | 3.5 | 3.6234 | 3.7087 | 3.6842 | 3.6952 | 3.788 | 3.7694 | 3.7332 | 3.6748 | 3.7076 | 3.7214 | 3.6309 | 3.5952 | 3.6004 | 3.5435 | 3.6291 | 3.6156 | 3.4565 | 3.4521 | 3.4242 | 3.6045 | 3.5518 | 3.5938 | 3.9413 | 3.8634 | 3.8584 | 3.8989 | 3.9558 | 3.9088 | 3.8292 | 3.9048 | 3.9676 | 3.8395 | 3.8498 | 3.8337 | 3.8889 | 3.8142 | 3.8858 | 3.9248 | 3.9137 | 3.8896 | 3.9398 | 3.8941 | 3.9592 | 3.9558 | 3.9242 | 3.9199 | 3.9057 | 3.9037 | 3.8685 | 3.8865 | 3.8123 | 3.8851 | 3.8896 | 3.9382 | 3.9651 | 3.9425 | 3.9434 | 3.961 | 3.9246 | 3.8914 | 3.9762 | 3.8932 | 3.9545 | 4.1404 | 3.9341 | 4.0183 | 4.0017 | 3.991 | 4.0204 | 3.9693 | 4.05 | 3.9558 | 3.9369 | 3.913 | 4.0166 | 3.9593 | 3.9731 | 3.9824 | 3.9596 | 3.9551 | 3.9513 | 3.9214 | 3.9481 | 3.9724 | 3.95 | 3.9593 | 3.9524 | 3.9137 | 3.9055 | 3.9075 | 3.9959 | 3.9365 | 3.9914 | 3.8989 | 3.9696 | 4.0256 | 4.048 | 3.9778 | 3.9196 | 3.8954 | 3.9962 | 4.0079 | 3.9538 | 4.0079 | 3.9962 | 3.9876 | 3.9931 | 3.9927 | 3.8911 | 3.9425 | 3.9962 | 4.0915 | 3.9724 | 4.0204 | 3.9358 | 3.9886 | 3.9893 | 4.0076 | 3.9258 | 3.932 | 3.9313 | 3.8796 | 4.0331 | 4.0914 | 3.9185 | 3.8881 | 3.9494 | 3.8753 | 3.8707 | 3.9055 | 3.9044 | 3.9282 | 3.9974 | 4.0128 | 3.9274 | 3.9656 | 3.9705 | 3.9758 | 3.8675 | 3.9347 | 3.881 | 3.972 | 3.9626 | 3.9766 | 3.9958 | 3.9512 | 4.0011 | 3.8348 | 3.9777 | 3.9036 | 3.9649 | 3.8896 | 3.938 | 3.9655 | 3.9353 | 3.9611 | 3.8502 | 3.953 | 4.4278 | 3.7545 | 3.956 | 3.9855 | 3.9488 | 3.925 | 4.005 | 4.0393 | 3.9261 | 3.9667 | 3.9075 | 3.9008 | 4.2021 | 3.9358 | 3.9368 | 3.9733 | 3.9865 | 3.9891 | 4.1252 | 3.8893 | 3.8484 | 3.9006 | 3.86 | 3.7953 | 3.7731 | 3.8739 | 3.8091 | 3.8843 | 3.9221 | 3.9164 | 3.9454 | 3.9082 | 3.8858 | 3.9533 | 3.8503 | 3.9627 | 3.8893 | 3.8936 | 3.9101 | 3.885 | 3.8592 | 3.8536 | 3.8577 | 3.9231 | 3.9666 | 3.8591 | 3.8809 | 3.8889 | 3.8316 | 4.0267 | 3.8469 | 3.8719 | 3.8592 | 3.9048 | 3.8974 | 3.8858 | 3.8753 | 3.9026 | 3.8615 | 3.8251 | 3.9066 | 3.9089 | 3.9665 | 4.0015 | 3.9582 | 3.9751 | 3.981 | 3.9458 | 3.91 | 3.9564 | 3.9952 | 3.8651 | 3.864 | 3.9178 | 3.9178 | 3.9521 | 3.9399 | 3.9595 | 3.9907 | 3.9382 | 3.8466 | 3.8133 | 3.8156 | 3.8061 | 3.6633 | 3.7744 | 3.8454 | 3.7872 | 3.7392 | 3.8813 | 3.96 | 3.887 | 3.9074 | 3.8825 | 3.8175 | 3.8123 | 3.8238 | 3.8642 | 3.8426 | 3.8312 | 3.8464 | 3.8467 | 3.818 | 3.8089 | 3.8745 | 3.8339 | 3.9031 | 3.8843 | 3.9773 | 3.9687 | 3.8683 | 3.8952 | 3.8366 | 3.896 | 3.8447 | 3.8368 | 3.7916 | 3.8381 | 3.7689 | 3.8234 | 3.7623 | 3.7947 | 3.8006 | 3.8562 | 3.8103 | 3.7766 | 3.7815 | 3.7856 | 3.7991 | 3.8666 | 3.7606 | 3.7818 | 3.823 | 3.9046 | 3.8854 | 3.8944 | 3.7845 | 3.8985 | 3.8581 | 3.8794 | 3.854 | 3.8734 | 3.8346 | 3.8723 | 3.9168 | 3.8447 | 3.8964 | 3.905 | 3.8876 | 3.8115 | 3.867 | 3.9215 | 3.8711 | 3.7957 | 3.6791 | 3.9129 | 3.818 | 3.9104 | 3.874 | 3.8108 | 3.8757 | 3.8179 | 3.8418 | 3.9127 | 3.9113 | 3.9337 | 3.9215 | 3.8616
2025-04-11 | 1.949 | 1.8844 | 1.9621 | 1.9636 | 1.9606 | 1.8641 | 2.0122 | 1.9189 | 1.9902 | 1.9939 | 1.9848 | 1.978 | 1.9909 | 1.9962 | 2.0159 | 2.003 | 1.9705 | 2 | 1.9932 | 2.0091 | 2.0674 | 2.0492 | 2.0682 | 2.0545 | 2.0712 | 2.0644 | 2.0773 | 2.0674 | 2.0803 | 2.0848 | 2.0614 | 2.0652 | 1.9705 | 1.9378 | 1.9402 | 1.9729 | 2 | 1.9936 | 1.975 | 1.9817 | 1.9144 | 1.9957 | 2.0423 | 2.0249 | 2.0431 | 2.0933 | 2.0851 | 2.0766 | 2.0214 | 2.0579 | 2.0748 | 2.0247 | 1.9928 | 2 | 1.9675 | 2.0119 | 2.002 | 1.9165 | 1.9161 | 1.9068 | 1.8432 | 1.9801 | 1.9905 | 2.1843 | 2.1394 | 2.134 | 2.1411 | 2.1729 | 2.1555 | 2.1087 | 2.1563 | 2.1815 | 2.1108 | 2.1276 | 2.108 | 2.1439 | 2.0992 | 2.1387 | 2.157 | 2.1394 | 2.1429 | 2.1587 | 2.1698 | 2.1724 | 2.1867 | 2.1948 | 2.1677 | 2.1476 | 2.1594 | 1.96 | 2.1356 | 2.0945 | 2.127 | 2.1429 | 2.1577 | 2.1763 | 2.1606 | 2.1725 | 2.1636 | 2.1429 | 2.1421 | 2.1663 | 2.1307 | 2.166 | 2.2657 | 2.1698 | 2.1939 | 2.1839 | 2.1732 | 2.197 | 2.1684 | 2.2088 | 2.1697 | 2.1457 | 2.1491 | 2.2063 | 2.1784 | 2.1843 | 2.2108 | 2.1863 | 2.1818 | 2.1836 | 2.1587 | 2.1847 | 2.2088 | 2.1981 | 2.1449 | 2.1929 | 2.1553 | 2.1532 | 2.1553 | 2.2122 | 2.1787 | 2.2188 | 2.1549 | 2.1957 | 2.2424 | 2.2298 | 2.1921 | 2.1639 | 2.1587 | 2.2088 | 2.2143 | 2.1998 | 2.1912 | 2.2015 | 2.1877 | 2.2114 | 2.2034 | 2.1508 | 2.1778 | 2.2022 | 2.2619 | 2.1867 | 2.2143 | 2.1712 | 2.1991 | 2.1643 | 2.1753 | 2.1646 | 2.1708 | 2.1729 | 2.1598 | 2.2259 | 2.266 | 2.1692 | 2.0779 | 2.1202 | 2.0941 | 2.1039 | 2.1209 | 2.1077 | 2.1206 | 2.1655 | 2.1776 | 2.1383 | 2.1508 | 2.1523 | 2.1633 | 2.1151 | 2.1526 | 2.1043 | 2.1576 | 2.1561 | 2.1674 | 2.1689 | 2.1557 | 2.1697 | 2.13 | 2.167 | 2.1198 | 2.1595 | 2.1088 | 2.1304 | 2.1496 | 2.1306 | 2.1575 | 2.1282 | 2.1954 | 2.1919 | 2.1859 | 2.19 | 2.2169 | 2.0977 | 2.2159 | 2.2333 | 2.2347 | 2.1871 | 2.2078 | 2.187 | 2.176 | 2.296 | 2.19 | 2.206 | 2.2053 | 2.2258 | 2.2234 | 2.1869 | 2.1412 | 2.1238 | 2.1632 | 2.1274 | 2.078 | 2.0802 | 2.1341 | 2.0996 | 2.0836 | 2.1161 | 2.1189 | 2.1319 | 2.1126 | 2.0958 | 2.1444 | 2.0872 | 2.1456 | 2.1075 | 2.1083 | 2.1142 | 2.0797 | 2.0763 | 2.07 | 2.0842 | 2.1523 | 2.1715 | 2.1134 | 2.1077 | 2.1107 | 2.064 | 2.1389 | 2.0898 | 2.0946 | 2.0924 | 2.1253 | 2.1264 | 2.0965 | 2.0976 | 2.1107 | 2.1243 | 2.107 | 2.1463 | 2.1486 | 2.1695 | 2.1945 | 2.1739 | 2.1807 | 2.1882 | 2.1695 | 2.1483 | 2.1771 | 2.195 | 2.116 | 2.1317 | 2.156 | 2.1481 | 2.1886 | 2.1856 | 2.1719 | 2.2102 | 2.1728 | 2.0726 | 2.051 | 2.0442 | 2.042 | 1.9894 | 2.0295 | 2.0646 | 2.0295 | 2.0091 | 2.0797 | 2.1066 | 2.0771 | 2.0873 | 2.0897 | 2.0619 | 2.0425 | 2.0521 | 2.0811 | 2.0633 | 2.0641 | 2.0709 | 1.9685 | 2.0573 | 2.044 | 2.0849 | 2.0641 | 2.091 | 2.0857 | 2.1259 | 2.2321 | 2.1246 | 2.075 | 2.0401 | 2.0663 | 2.0505 | 2.0382 | 2.0218 | 2.0421 | 2.0057 | 2.0446 | 2.0144 | 2.0149 | 2.0247 | 2.0655 | 2.0367 | 2.0165 | 2.0072 | 2.0199 | 2.0419 | 2.0639 | 1.9969 | 2.0369 | 2.0926 | 2.0969 | 2.0997 | 2.1048 | 2.0449 | 2.0961 | 2.1156 | 2.0819 | 2.0696 | 2.0902 | 2.0554 | 2.0875 | 2.0988 | 2.0606 | 2.0965 | 2.1193 | 2.086 | 2.0429 | 2.0754 | 2.1111 | 2.0876 | 2.0404 | 2.0367 | 2.1091 | 2.0476 | 2.1032 | 2.0804 | 2.0459 | 2.0763 | 2.0389 | 2.0765 | 2.1032 | 2.0887 | 2.1103 | 2.1036 | 2.1085
2025-04-12 | 3.512 | 3.4187 | 3.5348 | 3.5379 | 3.5144 | 3.3713 | 3.6136 | 3.4561 | 3.5515 | 3.5629 | 3.5758 | 3.5568 | 3.5538 | 3.5674 | 3.5932 | 3.5932 | 3.5359 | 3.5702 | 3.6364 | 3.5864 | 3.6864 | 3.6523 | 3.6856 | 3.6652 | 3.6697 | 3.675 | 3.6833 | 3.6735 | 3.6939 | 3.7015 | 3.6652 | 3.6811 | 3.4962 | 3.4482 | 3.4817 | 3.5175 | 3.5734 | 3.5781 | 3.5212 | 3.5367 | 3.4356 | 3.5421 | 3.6172 | 3.6104 | 3.6257 | 3.7149 | 3.6863 | 3.6579 | 3.5905 | 3.6518 | 3.6408 | 3.5606 | 3.5332 | 3.548 | 3.4938 | 3.5843 | 3.5524 | 3.4144 | 3.4097 | 3.3873 | 3.1932 | 3.5104 | 3.5323 | 3.8458 | 3.7843 | 3.8003 | 3.8254 | 3.8606 | 3.8324 | 3.7467 | 3.8382 | 3.8599 | 3.7578 | 3.75 | 3.7467 | 3.8117 | 3.7493 | 3.6781 | 3.824 | 3.8268 | 3.8095 | 3.6706 | 3.8682 | 3.8582 | 3.8696 | 3.8972 | 3.847 | 3.8116 | 3.8392 | 3.7612 | 3.8092 | 3.7467 | 3.8137 | 3.8361 | 3.8775 | 3.8703 | 3.847 | 3.8489 | 3.8499 | 3.8496 | 3.8276 | 3.8699 | 3.8062 | 3.8644 | 4.048 | 3.8571 | 3.9193 | 3.8841 | 3.8885 | 3.9262 | 3.8823 | 3.8247 | 3.7132 | 3.8164 | 3.8081 | 3.8927 | 3.843 | 3.8696 | 3.6522 | 3.8703 | 3.8692 | 3.5573 | 3.8214 | 3.8611 | 3.8965 | 3.8768 | 3.793 | 3.8706 | 3.813 | 3.8054 | 3.8043 | 3.8961 | 3.8385 | 3.9055 | 3.7985 | 3.7457 | 3.8496 | 3.8854 | 3.8206 | 3.7867 | 3.7761 | 3.8385 | 3.8589 | 3.8647 | 3.8682 | 3.8268 | 3.8475 | 3.8705 | 3.8595 | 3.7734 | 3.8317 | 3.8613 | 3.9592 | 3.8309 | 3.8844 | 3.7588 | 3.8171 | 3.7726 | 3.766 | 3.6084 | 3.8254 | 3.6153 | 3.7792 | 3.8988 | 3.9614 | 3.8117 | 3.675 | 3.7411 | 3.7014 | 3.7113 | 3.732 | 3.7362 | 3.7653 | 3.8216 | 3.8409 | 3.768 | 3.7766 | 3.7906 | 3.8046 | 3.7294 | 3.7923 | 3.7063 | 3.8061 | 3.8008 | 3.8292 | 3.8314 | 3.8069 | 3.8413 | 3.7634 | 3.8288 | 3.7457 | 3.8296 | 3.7509 | 3.791 | 3.823 | 3.7988 | 3.8155 | 3.7032 | 3.8066 | 3.7928 | 3.7764 | 3.781 | 3.82 | 3.7739 | 3.6759 | 3.8433 | 3.6666 | 3.7477 | 3.748 | 3.7579 | 3.725 | 3.9105 | 3.784 | 3.8462 | 3.8344 | 3.8378 | 3.8395 | 3.7781 | 3.6349 | 3.6076 | 3.647 | 3.6639 | 3.5937 | 3.5908 | 3.6768 | 3.6123 | 3.7348 | 3.773 | 3.8026 | 3.8057 | 3.8006 | 3.7632 | 3.8458 | 3.7344 | 3.8265 | 3.7555 | 3.7673 | 3.79 | 3.7348 | 3.7221 | 3.7105 | 3.7206 | 3.7524 | 2.398 | 3.7108 | 3.7187 | 3.7594 | 3.6817 | 3.8854 | 3.7049 | 3.7258 | 3.7138 | 3.749 | 3.7624 | 3.7366 | 3.7213 | 3.7441 | 3.7627 | 3.709 | 3.7861 | 3.787 | 3.7176 | 3.8481 | 3.8097 | 3.8336 | 3.8615 | 3.8383 | 3.7895 | 3.8522 | 3.8393 | 3.7079 | 3.7459 | 3.7744 | 3.7742 | 3.8601 | 3.8379 | 3.8264 | 3.8875 | 3.8319 | 3.7385 | 3.7105 | 3.7071 | 3.7147 | 3.6232 | 3.6716 | 3.7362 | 3.6704 | 3.6334 | 3.7536 | 3.7536 | 3.7423 | 3.7619 | 3.7643 | 3.7179 | 3.7099 | 3.7074 | 3.7496 | 3.7201 | 3.7277 | 3.7349 | 3.6085 | 3.7035 | 3.6936 | 3.7535 | 3.7156 | 3.7849 | 3.7474 | 3.8065 | 3.8206 | 3.7512 | 3.794 | 3.6728 | 3.796 | 3.743 | 3.7254 | 3.7004 | 3.731 | 3.6817 | 3.7082 | 3.6517 | 3.6927 | 3.7002 | 3.7441 | 3.7041 | 3.6533 | 3.6772 | 3.6768 | 3.7142 | 3.7413 | 3.6546 | 3.717 | 3.7936 | 3.814 | 3.8069 | 3.8203 | 3.6996 | 3.7923 | 3.7546 | 3.7707 | 3.734 | 3.7748 | 3.7351 | 3.7792 | 3.7953 | 3.7355 | 3.792 | 3.8069 | 3.7766 | 3.7259 | 3.7751 | 3.8246 | 3.7548 | 3.7217 | 3.7236 | 3.812 | 3.7216 | 3.7908 | 3.7716 | 3.7186 | 3.7662 | 3.7182 | 3.7512 | 3.8214 | 3.8077 | 3.8273 | 3.8242 | 3.7387
2025-04-13 | 4.2297 | 4.0893 | 4.253 | 4.2409 | 4.2439 | 4.1002 | 4.3382 | 4.1477 | 4.2879 | 4.2924 | 4.2985 | 4.2841 | 4.2886 | 4.2977 | 4.3356 | 4.3235 | 4.2504 | 4.2759 | 4.2462 | 4.2985 | 4.4152 | 4.3636 | 4.4129 | 4.3924 | 4.3932 | 4.3947 | 4.3992 | 4.3871 | 4.4159 | 4.4205 | 4.3773 | 4.397 | 4.2311 | 4.1858 | 4.2145 | 4.2496 | 4.3939 | 4.3174 | 4.2689 | 4.2687 | 4.1447 | 4.2639 | 4.3689 | 4.3516 | 4.3589 | 4.4682 | 4.4343 | 4.4052 | 4.305 | 4.4941 | 4.2522 | 4.2785 | 4.2388 | 4.2374 | 4.1768 | 4.2624 | 4.2419 | 4.0568 | 6.0104 | 4.0362 | 3.8242 | 4.1839 | 4.2463 | 4.6135 | 4.5262 | 4.5396 | 4.5649 | 4.589 | 4.5931 | 4.4776 | 4.6042 | 4.6084 | 4.4962 | 4.4876 | 4.4986 | 4.5905 | 4.5216 | 4.5745 | 4.5935 | 4.6046 | 4.5228 | 4.5665 | 4.648 | 4.6335 | 4.6077 | 4.6923 | 4.597 | 4.5346 | 4.5925 | 4.5569 | 4.5618 | 4.4796 | 4.5697 | 4.599 | 4.6456 | 4.6218 | 4.5467 | 4.6028 | 4.6156 | 4.6266 | 4.6089 | 4.6208 | 4.5665 | 4.5987 | 4.8692 | 4.8689 | 4.6967 | 4.6253 | 4.636 | 4.6888 | 4.6881 | 4.7019 | 5.0828 | 4.5202 | 4.578 | 4.6166 | 4.5935 | 4.6394 | 4.6946 | 4.6653 | 4.6318 | 4.627 | 4.5902 | 4.6551 | 4.6694 | 4.6398 | 4.5528 | 4.6304 | 4.5928 | 4.57 | 4.5652 | 4.6484 | 4.5638 | 4.6739 | 4.5573 | 4.628 | 4.7219 | 4.6297 | 4.5041 | 4.5562 | 4.5549 | 4.5894 | 4.6253 | 4.6225 | 4.5832 | 4.6725 | 4.5007 | 4.6811 | 4.6763 | 4.5649 | 4.6246 | 4.619 | 4.7748 | 4.5428 | 4.6315 | 4.5956 | 4.6511 | 4.6432 | 4.6097 | 4.3613 | 4.5845 | 4.4814 | 4.5597 | 4.5976 | 4.6863 | 4.6071 | 4.5378 | 4.6119 | 4.3292 | 4.5605 | 4.5563 | 4.5816 | 4.6047 | 4.6727 | 4.6829 | 4.6085 | 4.6357 | 4.641 | 4.6451 | 4.5591 | 4.6239 | 4.5148 | 4.6395 | 4.6353 | 4.658 | 4.6602 | 4.6334 | 4.6644 | 4.582 | 4.661 | 4.5601 | 4.6489 | 4.5503 | 4.5945 | 4.6373 | 4.6032 | 4.5833 | 4.4744 | 4.6202 | 4.9305 | 4.5576 | 4.5905 | 4.6733 | 4.549 | 4.6065 | 4.6769 | 4.6461 | 4.5262 | 4.6104 | 4.5653 | 4.5222 | 4.7715 | 4.5474 | 4.5965 | 4.6444 | 4.5807 | 4.6579 | 5.6524 | 4.4574 | 4.2361 | 4.539 | 4.4536 | 4.3554 | 4.3949 | 4.4324 | 4.3078 | 4.5062 | 4.5483 | 4.5914 | 4.6126 | 4.5369 | 4.5586 | 4.4737 | 4.5201 | 4.6291 | 4.5612 | 4.5683 | 4.5443 | 3.9273 | 4.51 | 4.2749 | 4.5085 | 4.5934 | 4.6495 | 4.5126 | 4.5582 | 4.5585 | 4.4767 | 4.7096 | 4.5096 | 4.5298 | 4.5234 | 3.9972 | 4.4939 | 4.2495 | 4.5264 | 4.3978 | 4.5394 | 4.4817 | 4.5731 | 4.5621 | 4.5725 | 4.5732 | 4.5767 | 4.5581 | 4.6646 | 4.64 | 4.5604 | 4.6314 | 4.5811 | 4.4173 | 4.5179 | 4.4517 | 4.5598 | 4.6402 | 4.6232 | 4.5666 | 4.6802 | 4.6061 | 4.4981 | 4.4932 | 4.4989 | 4.4985 | 4.3602 | 4.4531 | 4.5253 | 4.4271 | 4.4025 | 4.542 | 4.5352 | 4.5563 | 4.5752 | 4.5425 | 4.5099 | 4.5056 | 4.5118 | 4.5632 | 4.5142 | 4.5089 | 4.5351 | 4.4341 | 4.5009 | 4.4945 | 4.5286 | 4.5123 | 4.5795 | 4.559 | 4.5945 | 4.6365 | 4.527 | 4.5404 | 4.3977 | 4.5742 | 4.5275 | 4.5092 | 4.4827 | 4.5147 | 4.441 | 4.458 | 4.3981 | 4.46 | 4.4623 | 4.5283 | 4.4524 | 4.4386 | 4.424 | 4.4023 | 4.4121 | 4.5109 | 4.425 | 4.4741 | 4.3395 | 4.5322 | 4.0816 | 4.071 | 4.3784 | 4.5518 | 4.5219 | 4.5418 | 4.5208 | 4.5511 | 4.47 | 4.5533 | 4.5731 | 4.504 | 4.5761 | 4.5918 | 4.5522 | 4.4819 | 4.5443 | 4.602 | 4.5219 | 4.0842 | 4.3164 | 4.6099 | 4.3646 | 4.5896 | 4.5073 | 4.4537 | 4.5455 | 4.4568 | 4.4886 | 4.5947 | 4.5447 | 4.6119 | 4.6009 | 4.5152
2025-04-14 | 3.9585 | 3.8437 | 3.9841 | 3.9811 | 3.9705 | 3.8337 | 4.0673 | 3.8947 | 4.0152 | 4.022 | 4.0341 | 4.0152 | 4.0136 | 4.028 | 4.0583 | 4.053 | 3.9904 | 4.0223 | 3.9939 | 4.0409 | 4.153 | 4.1121 | 4.1492 | 4.1386 | 4.1311 | 4.1371 | 4.1439 | 4.1318 | 4.1568 | 4.1621 | 4.1227 | 4.1394 | 3.9553 | 3.9139 | 3.9378 | 3.9745 | 4.0335 | 4.0415 | 3.9864 | 3.9912 | 3.8818 | 4.0043 | 4.1006 | 4.0775 | 4.0899 | 4.191 | 4.1709 | 4.1344 | 4.0685 | 4.1082 | 4.1136 | 4.0189 | 3.9841 | 3.9931 | 3.9344 | 4.0196 | 4.0047 | 3.8254 | 3.8259 | 3.8088 | 3.5977 | 3.9506 | 3.9817 | 4.2512 | 4.2547 | 4.2842 | 4.3226 | 4.381 | 4.3325 | 4.2491 | 4.3395 | 4.3954 | 4.2657 | 4.2706 | 4.2626 | 4.3178 | 4.2446 | 4.324 | 4.362 | 4.343 | 4.3133 | 4.3618 | 4.3844 | 4.3932 | 4.4237 | 4.4383 | 4.382 | 4.3328 | 4.3313 | 4.295 | 4.3119 | 4.2522 | 4.3371 | 4.3357 | 4.3778 | 4.4068 | 4.3822 | 4.3689 | 4.3834 | 4.3723 | 4.3355 | 4.3941 | 4.311 | 4.393 | 4.6032 | 4.3989 | 4.4441 | 4.4244 | 4.4106 | 4.4486 | 4.3992 | 4.4738 | 4.3832 | 4.3438 | 4.3427 | 4.4351 | 4.3923 | 4.4096 | 4.4327 | 4.3054 | 4.3837 | 4.3861 | 4.3467 | 4.3957 | 4.4065 | 4.3785 | 4.2954 | 4.373 | 4.3447 | 4.3323 | 4.3302 | 4.4248 | 4.3627 | 4.4279 | 4.3147 | 4.3164 | 4.447 | 4.4303 | 4.3556 | 4.3095 | 4.2847 | 4.3844 | 4.401 | 4.3527 | 4.3257 | 4.4289 | 4.3133 | 4.4026 | 4.4094 | 4.2929 | 4.3476 | 4.393 | 4.5106 | 4.3713 | 4.4137 | 4.3447 | 4.3982 | 4.4082 | 4.4141 | 4.1511 | 4.3485 | 4.344 | 4.2871 | 4.4296 | 4.4965 | 4.3312 | 4.2634 | 4.3375 | 4.2797 | 4.2782 | 4.2959 | 4.2997 | 4.3216 | 4.3949 | 4.4082 | 4.3311 | 4.3579 | 4.3643 | 4.3726 | 4.2778 | 4.3452 | 4.2688 | 4.367 | 4.3647 | 4.3889 | 4.3923 | 4.3617 | 4.3983 | 4.3197 | 4.3953 | 4.3987 | 4.3874 | 4.2834 | 4.333 | 4.3655 | 4.3325 | 4.3583 | 4.2465 | 4.3497 | 4.3367 | 4.3352 | 4.3448 | 4.3862 | 4.3358 | 4.3908 | 4.4019 | 4.4243 | 4.3078 | 4.3553 | 4.3052 | 4.2837 | 4.4127 | 4.3318 | 4.3297 | 4.3772 | 4.1885 | 4.3832 | 4.3315 | 4.2484 | 4.2118 | 4.2683 | 4.2218 | 4.1302 | 4.1214 | 4.2371 | 4.1691 | 4.2893 | 4.3367 | 4.3379 | 4.3568 | 4.3379 | 4.3074 | 4.3846 | 4.2693 | 4.3748 | 4.3006 | 4.3065 | 4.3203 | 4.2498 | 4.2532 | 4.2218 | 4.2513 | 4.343 | 4.3866 | 4.2622 | 4.3014 | 4.3042 | 4.2296 | 4.4623 | 4.2483 | 4.2693 | 4.2659 | 4.2723 | 4.304 | 4.276 | 4.2689 | 4.3029 | 4.2971 | 4.2564 | 4.3413 | 4.3426 | 4.3922 | 4.4221 | 4.3735 | 4.3967 | 4.4199 | 4.3772 | 4.3345 | 4.3856 | 4.4144 | 4.2674 | 4.2882 | 4.3257 | 4.3223 | 4.3799 | 4.3524 | 4.3693 | 4.4196 | 4.3678 | 4.2766 | 4.0676 | 4.2464 | 4.243 | 4.1364 | 4.2063 | 4.2774 | 4.2071 | 4.1606 | 4.3216 | 4.3582 | 4.3061 | 4.3296 | 4.3179 | 4.2544 | 4.246 | 4.253 | 4.3037 | 4.2677 | 4.2711 | 4.2802 | 4.2703 | 4.1361 | 4.2378 | 4.3015 | 4.2601 | 4.3233 | 4.3057 | 4.3745 | 4.3813 | 4.2948 | 4.3151 | 4.2516 | 4.3266 | 4.2827 | 4.2674 | 4.2401 | 4.2687 | 4.1944 | 4.1953 | 4.1983 | 4.2135 | 4.2233 | 4.2883 | 4.2382 | 4.1994 | 4.1953 | 4.1897 | 4.2158 | 4.2954 | 4.1805 | 4.1805 | 4.2425 | 4.25 | 4.354 | 4.3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2676
2025-04-15 | 3.7735 | 3.681 | 3.803 | 3.803 | 3.7795 | 3.6439 | 3.8845 | 3.7189 | 3.8205 | 3.8288 | 3.8462 | 3.8265 | 3.8235 | 3.8348 | 3.8659 | 3.8712 | 3.803 | 3.8317 | 3.8068 | 3.85 | 3.9621 | 3.9197 | 3.9636 | 3.9462 | 3.9348 | 3.9447 | 3.9515 | 3.9432 | 3.9659 | 3.9705 | 3.9288 | 3.9515 | 3.7712 | 3.7161 | 3.752 | 3.7863 | 3.8469 | 3.8596 | 3.7992 | 3.8166 | 3.7121 | 3.8203 | 3.9036 | 3.9137 | 3.9042 | 4.0014 | 3.9672 | 3.9315 | 3.8539 | 3.9218 | 3.9311 | 3.839 | 3.6818 | 3.8095 | 3.7583 | 3.8411 | 3.8192 | 3.6606 | 3.655 | 3.6453 | 3.4386 | 3.7739 | 3.8021 | 4.1446 | 4.0714 | 4.0796 | 4.1135 | 4.1429 | 4.1182 | 4.03 | 4.1318 | 4.148 | 4.0407 | 4.0341 | 4.0328 | 4.1032 | 4.0437 | 3.9393 | 4.0362 | 4.1353 | 4.0797 | 4.1118 | 4.1553 | 4.1627 | 4.1663 | 4.1973 | 4.1418 | 4.0926 | 4.1215 | 4.0718 | 4.1018 | 4.0197 | 4.0949 | 4.1163 | 4.1587 | 4.1415 | 4.1098 | 4.1329 | 4.1325 | 4.1346 | 4.1071 | 4.1463 | 4.0773 | 4.1401 | 4.2471 | 4.1387 | 4.2039 | 4.1601 | 4.1674 | 4.2126 | 4.1684 | 4.0355 | 4.0726 | 4.105 | 3.8423 | 4.1925 | 4.0756 | 4.1829 | 3.8213 | 4.019 | 4.167 | 4.1615 | 4.1331 | 4.1811 | 4.2036 | 4.185 | 4.1021 | 4.1805 | 4.0369 | 4.1156 | 4.1115 | 4.1967 | 4.1322 | 4.206 | 4.0983 | 4.1691 | 4.1443 | 4.2008 | 4.1111 | 4.0959 | 4.0918 | 4.1201 | 4.1674 | 4.1304 | 4.1063 | 4.2091 | 4.1629 | 4.2027 | 4.1852 | 4.0967 | 4.1599 | 4.1618 | 4.2823 | 4.1266 | 4.186 | 4.0324 | 4.1843 | 4.0952 | 3.9921 | 3.8823 | 4.1277 | 2.6501 | 4.0997 | 4.1875 | 4.2519 | 4.136 | 4.0658 | 4.1308 | 4.0763 | 4.0775 | 4.0816 | 4.0941 | 4.116 | 4.172 | 4.1848 | 4.1179 | 4.1429 | 4.1527 | 4.1568 | 4.0913 | 4.1631 | 4.0404 | 4.1527 | 4.1455 | 4.1693 | 4.1689 | 4.1413 | 4.1746 | 4.1043 | 4.1678 | 4.0828 | 4.1629 | 4.068 | 4.1134 | 4.156 | 4.1266 | 4.1476 | 4.0332 | 4.1598 | 4.1507 | 4.1183 | 4.1332 | 4.1948 | 4.1117 | 4.0919 | 4.2091 | 3.826 | 4.0923 | 4.0841 | 4.1269 | 4.0871 | 4.2871 | 3.8919 | 4.1315 | 4.1872 | 3.8578 | 4.1957 | 4.1392 | 3.8648 | 3.9187 | 3.9361 | 4.0119 | 3.9282 | 3.9597 | 4.0027 | 3.926 | 4.0502 | 4.0877 | 4.1248 | 4.1362 | 4.1189 | 4.0768 | 4.1538 | 4.0454 | 4.1633 | 4.0867 | 4.0926 | 4.0863 | 3.9717 | 4.0383 | 3.9486 | 4.0349 | 4.1252 | 4.1692 | 4.044 | 4.0674 | 4.0993 | 4.0222 | 4.2268 | 4.0502 | 4.0469 | 4.0386 | 4.0117 | 4.0914 | 4.0286 | 4.0446 | 4.0663 | 3.9896 | 3.9337 | 4.1137 | 4.1102 | 3.9511 | 4.1598 | 4.004 | 4.0558 | 4.1926 | 4.168 | 4.1086 | 4.1687 | 4.1633 | 4.0228 | 4.0747 | 4.0831 | 4.116 | 4.1824 | 4.1527 | 4.139 | 4.2167 | 4.148 | 4.0359 | 3.8337 | 4.0144 | 4.011 | 3.9252 | 3.9728 | 4.0442 | 3.9856 | 3.9422 | 4.0779 | 4.0828 | 4.0676 | 4.0926 | 4.0937 | 4.0286 | 4.0183 | 4.0198 | 4.0658 | 4.0375 | 4.0383 | 4.0501 | 4.2703 | 3.8369 | 4.0019 | 4.0796 | 4.0338 | 4.1006 | 4.0732 | 4.1293 | 4.1516 | 4.0817 | 4.0667 | 3.968 | 4.1028 | 4.0401 | 4.0323 | 4.0073 | 4.0528 | 3.9936 | 3.8891 | 3.9625 | 3.9937 | 4.002 | 4.0428 | 4.0016 | 3.9661 | 3.9781 | 3.9706 | 3.9676 | 4.047 | 3.9666 | 4.02 | 3.9847 | 4.137 | 4.2229 | 4.0895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0364
2025-04-16 | 3.1483 | 3.0869 | 3.1689 | 3.1705 | 3.172 | 3.06 | 3.2433 | 3.0924 | 3.1947 | 3.2121 | 3.2121 | 3.1902 | 3.2152 | 3.2227 | 3.2508 | 3.2553 | 3.1762 | 3.2169 | 3.1992 | 3.2318 | 3.3341 | 3.2909 | 3.3364 | 3.3182 | 3.3205 | 3.3182 | 3.3326 | 3.3326 | 3.3545 | 3.3523 | 3.3152 | 3.3409 | 3.1886 | 3.1467 | 3.1619 | 3.193 | 3.2424 | 3.252 | 3.2061 | 3.2209 | 3.1258 | 3.2275 | 3.3135 | 3.3194 | 3.3063 | 3.3965 | 3.3653 | 3.3353 | 3.2897 | 3.3364 | 3.3226 | 3.2422 | 2.9517 | 3.2457 | 3.1913 | 3.254 | 3.2345 | 3.0954 | 3.0998 | 2.6989 | 3.3598 | 3.0525 | 2.9443 | 3.5266 | 3.4527 | 3.4697 | 3.4807 | 3.5266 | 3.4685 | 3.4096 | 3.4669 | 3.5124 | 3.4079 | 3.4203 | 3.4006 | 3.4325 | 3.3701 | 3.3126 | 3.5735 | 3.5414 | 3.4824 | 3.5605 | 3.5718 | 3.5653 | 3.6149 | 3.6097 | 3.5581 | 3.5279 | 3.5248 | 3.4724 | 3.4665 | 3.5038 | 3.5552 | 3.5749 | 3.5908 | 3.6204 | 3.6152 | 3.5997 | 3.5939 | 3.5548 | 3.5386 | 3.5849 | 3.515 | 3.5866 | 3.7788 | 3.5645 | 3.6021 | 3.5497 | 3.5801 | 3.5887 | 3.5573 | 3.6246 | 3.5733 | 3.5505 | 3.5052 | 3.6011 | 3.5842 | 3.5935 | 3.6308 | 3.4351 | 3.5414 | 3.5435 | 3.5408 | 3.575 | 3.5721 | 3.5355 | 3.5072 | 3.558 | 3.5745 | 3.5514 | 3.5259 | 3.5932 | 3.5397 | 3.578 | 3.4758 | 3.5214 | 3.5162 | 3.6798 | 3.5756 | 3.5483 | 3.4375 | 3.6377 | 3.6318 | 3.5921 | 3.5366 | 3.6649 | 3.6087 | 3.6418 | 3.6108 | 3.5541 | 3.5762 | 3.5983 | 3.6633 | 3.5611 | 3.5849 | 3.5556 | 3.559 | 3.6052 | 3.5918 | 3.4124 | 3.5721 | 3.5231 | 3.5462 | 3.5718 | 3.6253 | 3.5552 | 3.5771 | 3.644 | 3.5975 | 3.5918 | 3.5899 | 3.6036 | 3.5979 | 3.6523 | 3.6584 | 3.6175 | 3.6712 | 3.6625 | 3.6757 | 3.5937 | 3.6711 | 3.5866 | 3.6829 | 3.6618 | 3.6757 | 3.6481 | 3.6636 | 3.6701 | 3.6126 | 3.6829 | 3.5922 | 3.6474 | 3.5374 | 3.5918 | 3.6365 | 3.6103 | 3.6056 | 3.5489 | 3.661 | 3.6515 | 3.6421 | 3.6346 | 3.6623 | 3.6499 | 3.6936 | 3.698 | 3.6281 | 3.6232 | 3.6735 | 3.6338 | 3.6233 | 3.8028 | 3.6218 | 3.6248 | 3.6688 | 3.5053 | 3.6867 | 3.6299 | 3.574 | 3.4913 | 3.5635 | 3.5442 | 3.4906 | 3.4947 | 3.5241 | 3.4633 | 3.5143 | 3.5607 | 3.5534 | 3.5534 | 3.5675 | 3.3431 | 3.6833 | 3.3838 | 3.6805 | 3.6091 | 3.5644 | 3.5349 | 3.3333 | 3.4503 | 3.5202 | 3.438 | 3.7068 | 3.5926 | 3.6366 | 3.3692 | 3.7527 | 3.4141 | 3.71 | 3.5509 | 3.5423 | 3.5337 | 3.5408 | 3.5008 | 3.5909 | 3.4948 | 3.5505 | 3.5372 | 3.4987 | 3.5564 | 3.55 | 3.5984 | 3.6153 | 3.572 | 3.5905 | 3.5889 | 3.5585 | 3.5346 | 3.5704 | 3.6207 | 3.4824 | 3.4777 | 3.5155 | 3.4998 | 3.5592 | 3.5239 | 3.5745 | 3.5859 | 3.5572 | 3.4165 | 3.2305 | 3.3915 | 3.4017 | 3.3201 | 3.3621 | 3.4244 | 3.3492 | 3.3243 | 3.4191 | 3.4503 | 3.4165 | 3.3394 | 3.4524 | 3.3952 | 3.3821 | 3.3954 | 3.4053 | 3.3887 | 3.3853 | 3.3929 | 4.2703 | 3.1949 | 3.3667 | 3.416 | 3.3656 | 3.4226 | 3.4054 | 3.4936 | 3.4671 | 3.3988 | 3.3987 | 3.3458 | 3.4944 | 3.4395 | 3.4193 | 3.3999 | 3.3921 | 3.3702 | 3.3113 | 3.4105 | 3.3964 | 3.3968 | 3.4866 | 3.4268 | 3.4178 | 3.4286 | 3.4286 | 3.3072 | 3.4936 | 3.4078 | 3.4568 | 3.3363 | 3.5479 | 3.6028 | 3.4274 | 3.1879 | 3.3012 | 3.1947 | 3.2829 | 3.2717 | 3.2631 | 3.2563 | 3.275 | 3.3206 | 3.269 | 3.3289 | 3.3359 | 3.3131 | 3.2161 | 3.3002 | 3.3387 | 3.2828 | 3.167 | 3.1838 | 3.3042 | 3.2193 | 3.324 | 3.3053 | 3.2449 | 3.2997 | 3.2178 | 3.2139 | 3.3141 | 3.2963 | 3.3328 | 3.3261 | 3.4606
2025-04-17 | 3.7313 | 3.638 | 3.7689 | 3.7758 | 3.7545 | 3.5953 | 3.8814 | 3.7061 | 3.8053 | 3.8242 | 3.8606 | 3.8288 | 3.8182 | 3.8379 | 3.8614 | 3.8652 | 3.811 | 3.8389 | 3.825 | 3.8667 | 3.9871 | 3.9326 | 3.9765 | 3.9386 | 3.9598 | 3.9689 | 3.978 | 3.9576 | 3.997 | 4 | 3.953 | 3.9644 | 3.7303 | 3.6898 | 3.7321 | 3.7624 | 3.8278 | 3.8413 | 3.7606 | 3.7871 | 3.6598 | 3.7618 | 3.8329 | 3.8041 | 3.8472 | 3.9233 | 3.9088 | 3.8898 | 3.7683 | 3.9114 | 3.8996 | 3.8151 | 3.4719 | 3.7999 | 3.75 | 3.8174 | 3.8085 | 3.6515 | 3.655 | 3.6307 | 3.4455 | 3.7643 | 3.7735 | 4.1066 | 4.048 | 4.081 | 4.0839 | 4.0469 | 4.0892 | 4.0718 | 4.089 | 4.0473 | 3.9707 | 3.9315 | 3.9479 | 4.0552 | 3.9848 | 4.0511 | 4.0756 | 4.1529 | 4.021 | 4.0483 | 4.1408 | 4.1273 | 4.0745 | 4.1605 | 4.0779 | 4.0159 | 4.0286 | 4.1046 | 4.1235 | 3.9017 | 3.9776 | 4.0262 | 4.0804 | 4.0311 | 3.9765 | 4.0635 | 4.0404 | 4.0332 | 4.0234 | 4.0749 | 4.0305 | 4.0445 | 4.265 | 4.0297 | 4.1315 | 4.0421 | 4.06 | 4.1363 | 4.1235 | 3.9569 | 4.1497 | 4.0144 | 4.0535 | 4.0732 | 4.0483 | 4.1118 | 4.1988 | 4.0317 | 4.1177 | 4.0876 | 4.061 | 4.1328 | 4.1919 | 4.1684 | 4.0835 | 4.1708 | 4.0776 | 4.0487 | 4.0269 | 4.098 | 4.0093 | 4.1201 | 4.0204 | 4.0652 | 4.1508 | 4.0362 | 3.9146 | 3.9862 | 4.0421 | 3.9986 | 4.0438 | 4.1225 | 4.0362 | 4.1039 | 4.0549 | 4.1771 | 4.1313 | 4.0794 | 4.1623 | 4.0618 | 4.2332 | 3.9883 | 4.0759 | 4.0821 | 4.1208 | 3.9869 | 4.0638 | 3.9517 | 4.0621 | 3.8406 | 3.9731 | 4.0331 | 4.1225 | 4.123 | 3.9921 | 4.0219 | 3.9554 | 3.9531 | 3.9135 | 3.9592 | 3.9747 | 4.0423 | 4.0711 | 3.9936 | 4.0408 | 4.0423 | 4.0249 | 4.0083 | 4.1111 | 3.9343 | 4.0321 | 4.0578 | 4.0733 | 4.0488 | 4.0401 | 4.0616 | 4.0302 | 4.0752 | 3.9898 | 4.0695 | 4.0079 | 4.0344 | 4.1071 | 4.0853 | 4.0925 | 3.9042 | 4.0642 | 4.0542 | 3.9906 | 3.9042 | 4.1284 | 3.9603 | 4.0223 | 4.1429 | 4.0687 | 3.9828 | 4.0245 | 4.1097 | 4.0195 | 4.2226 | 4.0084 | 4.0887 | 4.1582 | 3.9686 | 4.1605 | 4.0991 | 3.9047 | 3.7827 | 3.9535 | 3.9004 | 3.8317 | 3.8971 | 3.8812 | 3.7822 | 3.9275 | 3.9732 | 4.0612 | 4.0534 | 4.0816 | 3.977 | 4.1299 | 3.9871 | 4.0973 | 4.0259 | 4.0334 | 4.0526 | 3.9714 | 3.9512 | 3.9542 | 3.9721 | 4.0934 | 4.1201 | 3.9984 | 3.9702 | 4.0577 | 3.9482 | 4.1994 | 4.0188 | 3.977 | 3.9676 | 4.0203 | 4.0734 | 3.98 | 3.9759 | 3.9949 | 4.0149 | 3.9272 | 4.0308 | 4.0011 | 3.9361 | 4.0185 | 4.0427 | 4.0804 | 4.1476 | 4.1611 | 4.0502 | 4.128 | 4.0254 | 3.7908 | 4.0535 | 4.0265 | 4.0457 | 4.1776 | 4.1422 | 4.0106 | 4.2085 | 4.0909 | 3.9331 | 3.7929 | 3.9146 | 3.9475 | 3.8405 | 3.8976 | 3.9588 | 3.8828 | 3.8662 | 3.9701 | 3.9365 | 3.963 | 3.8832 | 3.9913 | 3.9845 | 3.9631 | 3.9368 | 3.9734 | 3.9579 | 3.9587 | 3.9666 | 2.73 | 3.8483 | 3.9488 | 4.0224 | 3.9742 | 4.0608 | 3.9985 | 4.0291 | 4.1087 | 4.0508 | 3.9631 | 3.7881 | 4.0028 | 3.925 | 3.916 | 3.9116 | 3.9548 | 3.9032 | 3.8439 | 3.8404 | 3.9125 | 3.9109 | 3.9504 | 3.8873 | 3.8719 | 3.8817 | 3.8607 | 3.8327 | 3.9281 | 3.8815 | 3.9388 | 3.8956 | 4.0243 | 3.9678 | 3.9356 | 3.9755 | 4.0357 | 4.0162 | 4.0166 | 3.9751 | 3.9833 | 3.9306 | 3.965 | 3.9762 | 3.916 | 4.0004 | 4.0031 | 3.9433 | 3.9139 | 3.9462 | 4.0063 | 3.9842 | 3.9732 | 3.9564 | 4.0498 | 3.9286 | 3.9994 | 3.956 | 3.9246 | 3.9594 | 3.938 | 3.971 | 4.0197 | 4.0082 | 4.0145 | 4.0078 | 3.9778
2025-04-18 | 4.4593 | 4.3357 | 4.4985 | 4.4879 | 4.478 | 4.3326 | 4.6106 | 4.3864 | 4.528 | 4.5348 | 4.578 | 4.5439 | 4.5318 | 4.5455 | 4.5833 | 4.5848 | 4.5136 | 4.5271 | 4.5121 | 4.5621 | 4.7068 | 4.6432 | 4.7053 | 4.6576 | 4.6705 | 4.6909 | 4.6871 | 4.647 | 4.7 | 4.7106 | 4.6697 | 4.6902 | 4.4864 | 4.4314 | 4.4561 | 4.4928 | 4.563 | 4.5718 | 4.5182 | 4.5231 | 4.4091 | 4.5128 | 4.6214 | 4.6118 | 4.6067 | 4.7171 | 4.6327 | 4.5948 | 4.4383 | 4.6106 | 4.629 | 4.5294 | 4.1082 | 4.4776 | 4.4206 | 4.4591 | 4.4785 | 4.2896 | 4.3035 | 4.2698 | 4.0939 | 4.4538 | 4.4751 | 4.8088 | 4.7291 | 4.812 | 4.7957 | 4.7591 | 4.8246 | 4.6836 | 4.8689 | 4.7792 | 4.6957 | 4.6482 | 4.6925 | 4.8182 | 4.7579 | 4.7619 | 4.8161 | 4.9237 | 4.7198 | 4.7536 | 4.913 | 4.8467 | 4.7778 | 4.904 | 4.7799 | 4.6909 | 4.8558 | 4.793 | 4.7823 | 4.5349 | 4.648 | 4.7257 | 4.7798 | 4.7208 | 4.6359 | 4.8368 | 4.7464 | 4.7251 | 4.7493 | 4.7785 | 4.7665 | 4.7112 | 4.8927 | 4.726 | 4.8361 | 4.7705 | 4.7509 | 4.8578 | 4.7139 | 4.8471 | 4.9051 | 4.6991 | 4.717 | 4.8116 | 4.7805 | 4.8644 | 4.7667 | 4.9406 | 4.873 | 4.7585 | 4.8099 | 4.9116 | 4.9555 | 4.9265 | 4.8357 | 4.922 | 4.805 | 4.7767 | 4.7526 | 4.8288 | 4.7322 | 4.8561 | 4.7433 | 4.7885 | 4.7652 | 4.5997 | 4.7187 | 4.7985 | 4.8623 | 4.7947 | 4.8389 | 4.9503 | 4.8112 | 4.9034 | 4.8064 | 4.9784 | 4.8591 | 4.7991 | 4.873 | 4.7971 | 4.9641 | 4.6943 | 4.7771 | 4.7836 | 4.8357 | 4.8043 | 4.7774 | 4.7792 | 4.7712 | 4.7788 | 4.8099 | 4.7232 | 4.8392 | 4.8351 | 4.7706 | 4.8209 | 4.7751 | 4.7819 | 4.7464 | 4.8167 | 4.8496 | 4.9237 | 4.9244 | 4.8235 | 4.8137 | 4.8299 | 4.839 | 4.7988 | 4.9008 | 4.6659 | 4.8239 | 4.8212 | 4.8636 | 4.8893 | 4.8356 | 4.8779 | 4.7748 | 4.8564 | 4.7528 | 4.8409 | 4.7513 | 4.8193 | 4.8821 | 4.8397 | 4.8972 | 4.6441 | 4.8324 | 4.8685 | 4.7062 | 4.7355 | 4.8716 | 4.6949 | 4.7669 | 4.8841 | 4.8045 | 4.6982 | 4.8002 | 4.8445 | 4.7434 | 4.9509 | 4.705 | 4.8057 | 4.8823 | 4.7658 | 4.9104 | 5.0584 | 4.5824 | 4.5942 | 4.6327 | 4.5871 | 4.4818 | 4.5691 | 4.5281 | 4.4208 | 4.685 | 4.7124 | 4.8293 | 4.7822 | 4.8014 | 4.7421 | 4.8442 | 4.6894 | 4.8501 | 4.7892 | 4.7959 | 4.7586 | 4.6064 | 4.6916 | 4.5952 | 4.6756 | 4.8124 | 4.8497 | 4.6927 | 4.735 | 4.77 | 4.6587 | 4.9058 | 4.7417 | 4.7002 | 4.7047 | 4.652 | 4.7899 | 4.6655 | 4.7129 | 4.7178 | 4.7167 | 4.6917 | 4.7976 | 4.7687 | 4.7477 | 4.7619 | 4.7877 | 4.8446 | 4.9162 | 4.9167 | 4.7744 | 4.8673 | 4.7755 | 4.452 | 4.8119 | 4.6193 | 4.7956 | 4.935 | 4.9028 | 4.7328 | 4.9707 | 4.8377 | 4.7808 | 4.7498 | 4.7517 | 4.7317 | 4.6289 | 4.6965 | 4.791 | 4.6999 | 4.6841 | 4.7929 | 4.697 | 4.7971 | 4.8005 | 4.829 | 4.7937 | 4.7984 | 4.7732 | 4.8246 | 4.7835 | 4.7797 | 4.799 | 4.2703 | 4.7619 | 4.7596 | 4.7971 | 4.7603 | 4.8964 | 4.802 | 4.7861 | 4.9107 | 4.8456 | 4.7806 | 4.5574 | 4.9004 | 4.8064 | 4.7769 | 4.7462 | 4.7929 | 4.7385 | 4.5545 | 4.6222 | 4.7991 | 4.7916 | 4.8139 | 4.7118 | 4.7399 | 4.7275 | 4.6924 | 4.686 | 4.7564 | 4.7669 | 4.7606 | 4.7889 | 4.8595 | 4.7881 | 4.8077 | 4.7641 | 4.8475 | 4.8015 | 4.8269 | 4.7847 | 4.8494 | 4.7754 | 4.8449 | 4.8527 | 4.8015 | 4.8968 | 4.9058 | 4.8266 | 4.8129 | 4.8305 | 4.8501 | 4.7595 | 4.7529 | 4.7455 | 4.907 | 4.7042 | 4.8344 | 4.742 | 4.7786 | 4.7873 | 4.7775 | 4.7998 | 4.9029 | 4.8615 | 4.9038 | 4.8827 | 4.7378
2025-04-19 | 4.1603 | 4.0686 | 4.203 | 4.2083 | 4.1758 | 4.038 | 4.3007 | 4.0924 | 4.2098 | 4.2288 | 4.2606 | 4.2288 | 4.2333 | 4.2348 | 4.2705 | 4.2811 | 4.2065 | 4.2265 | 4.1947 | 4.2492 | 4.3788 | 4.3235 | 4.378 | 4.3477 | 4.3371 | 4.3523 | 4.3621 | 4.3523 | 4.375 | 4.3765 | 4.3273 | 4.3583 | 4.1652 | 4.1108 | 4.1515 | 4.1802 | 4.2552 | 4.2648 | 4.1917 | 4.2089 | 4.122 | 4.229 | 4.3239 | 4.3143 | 4.2997 | 4.4153 | 4.382 | 4.3327 | 4.2573 | 4.3168 | 4.3087 | 4.2067 | 3.8167 | 4.1801 | 4.1264 | 4.1707 | 4.213 | 4.0344 | 4.0304 | 4.0146 | 3.8053 | 4.1521 | 4.173 | 4.5721 | 4.5214 | 4.5168 | 4.5756 | 4.5493 | 4.4482 | 4.4531 | 4.5821 | 4.5449 | 4.4627 | 4.4041 | 4.4462 | 4.5368 | 4.474 | 4.2547 | 4.2098 | 4.5607 | 4.4645 | 4.4977 | 4.5952 | 4.5963 | 4.5469 | 4.6566 | 4.5574 | 4.4845 | 4.5631 | 4.539 | 4.5476 | 4.4199 | 4.5176 | 4.548 | 4.6142 | 4.5635 | 4.4822 | 4.56 | 4.5714 | 4.5952 | 4.5462 | 4.5932 | 4.5325 | 4.5556 | 4.8454 | 4.5362 | 4.6705 | 4.5521 | 4.597 | 4.6622 | 4.6332 | 4.6584 | 4.6236 | 4.491 | 4.5293 | 4.5556 | 4.3627 | 4.5939 | 4.6277 | 4.6184 | 4.6008 | 4.5856 | 4.5487 | 4.6053 | 4.6149 | 4.5945 | 4.501 | 4.5894 | 4.5487 | 4.5224 | 4.5107 | 4.5914 | 4.4986 | 4.6104 | 4.4972 | 4.5604 | 4.3474 | 4.6046 | 4.4619 | 4.5262 | 4.5259 | 4.5404 | 4.5618 | 4.5876 | 4.5569 | 4.6453 | 4.5669 | 4.6356 | 4.6197 | 4.5213 | 4.5909 | 4.5676 | 4.7147 | 4.4714 | 4.5545 | 4.548 | 4.5911 | 4.5787 | 4.4458 | 4.4727 | 4.5304 | 4.5483 | 4.511 | 4.5188 | 4.6073 | 4.5602 | 4.5393 | 4.6081 | 4.5427 | 4.5378 | 4.5019 | 4.5665 | 4.5945 | 4.6406 | 4.6425 | 4.562 | 4.6077 | 4.6198 | 4.6345 | 4.5444 | 4.5811 | 4.4805 | 4.6168 | 4.5956 | 4.6338 | 4.6368 | 4.5941 | 4.6368 | 4.5556 | 4.6262 | 4.5242 | 4.6236 | 4.5159 | 4.5729 | 4.6016 | 4.5694 | 4.5889 | 4.4345 | 4.5903 | 4.5703 | 4.5245 | 4.5366 | 4.6224 | 4.5058 | 4.5796 | 4.6556 | 4.6028 | 4.4869 | 4.6058 | 4.5649 | 4.5147 | 5.0334 | 4.5039 | 5.4046 | 4.5392 | 4.1999 | 5.328 | 4.86 | 3.4118 | 4.4329 | 4.425 | 4.4953 | 4.3878 | 4.3257 | 4.0412 | 4.3432 | 4.5012 | 4.5041 | 4.5616 | 4.5671 | 4.553 | 4.5096 | 4.6005 | 4.4767 | 4.6075 | 4.5063 | 4.5153 | 4.5369 | 4.4771 | 4.476 | 4.4408 | 4.4782 | 4.5612 | 4.6056 | 4.4623 | 4.4887 | 4.5188 | 4.4636 | 4.6703 | 4.4479 | 4.4786 | 4.461 | 4.4864 | 4.5208 | 4.4831 | 4.4909 | 4.5066 | 4.5087 | 4.4148 | 4.5325 | 4.5142 | 4.5076 | 4.5078 | 4.5158 | 4.5574 | 4.6207 | 4.5932 | 4.5072 | 4.5904 | 4.5191 | 4.3662 | 4.5126 | 4.3993 | 4.5441 | 4.5888 | 4.5504 | 4.5028 | 4.6311 | 4.5644 | 4.3485 | 4.4369 | 4.4233 | 4.4206 | 4.2585 | 4.359 | 4.4641 | 4.3836 | 4.325 | 4.4872 | 4.4555 | 4.4826 | 4.5272 | 4.5063 | 4.4155 | 4.4198 | 4.4365 | 4.4901 | 4.3773 | 4.4592 | 4.4736 | 3.7629 | 4.4418 | 4.4297 | 4.5135 | 4.4558 | 4.5119 | 4.4983 | 4.506 | 4.5857 | 4.5056 | 4.4435 | 4.297 | 4.5286 | 4.4644 | 4.4528 | 4.4289 | 4.4683 | 4.3787 | 4.3612 | 4.3988 | 4.4015 | 4.4113 | 4.4715 | 4.4068 | 4.3844 | 4.4184 | 4.3885 | 4.3336 | 4.474 | 4.3881 | 4.4443 | 4.4027 | 4.5573 | 4.5133 | 4.4356 | 4.4999 | 4.6221 | 4.5526 | 4.5885 | 4.5204 | 4.5657 | 4.5178 | 4.5623 | 4.5855 | 4.5178 | 4.551 | 4.5526 | 4.5429 | 4.4551 | 4.5149 | 4.5726 | 4.5455 | 4.4292 | 4.532 | 4.6068 | 4.5169 | 4.5832 | 4.564 | 4.3619 | 4.5485 | 4.4827 | 4.4996 | 4.577 | 4.6001 | 4.5965 | 4.575 | 4.4702
2025-04-20 | 2.8652 | 2.8062 | 2.8894 | 2.8902 | 2.8561 | 2.7737 | 2.9587 | 2.7992 | 2.872 | 2.8864 | 2.9227 | 2.9 | 2.8886 | 2.8902 | 2.9076 | 2.9318 | 2.8796 | 2.9083 | 2.8902 | 2.922 | 3.0091 | 2.9765 | 3.003 | 2.9727 | 2.9894 | 2.9939 | 2.997 | 2.9939 | 3.025 | 3.025 | 2.9765 | 2.9864 | 2.8492 | 2.8014 | 2.8301 | 2.8596 | 2.9123 | 2.9131 | 2.8561 | 2.886 | 2.8303 | 2.9016 | 2.9473 | 2.9693 | 2.9605 | 3.0355 | 3.0027 | 2.9731 | 2.8875 | 2.9616 | 2.9648 | 2.8716 | 2.6227 | 2.8765 | 2.8391 | 2.909 | 2.8891 | 2.7805 | 2.7819 | 2.767 | 2.6076 | 2.8694 | 2.8622 | 3.1329 | 3.1008 | 3.1184 | 3.1384 | 3.1291 | 3.1087 | 3.0538 | 3.0193 | 3.009 | 3.0366 | 3.0092 | 3.0497 | 3.0999 | 3.0595 | 3.0983 | 3.1177 | 3.1401 | 3.0604 | 3.0982 | 3.1473 | 3.1447 | 3.1273 | 3.1692 | 3.1176 | 3.0817 | 3.1432 | 3.1084 | 3.1218 | 3.0435 | 3.109 | 3.1273 | 3.1705 | 3.1315 | 3.0994 | 3.1411 | 3.1339 | 3.1443 | 3.1079 | 3.1494 | 3.1056 | 3.1277 | 3.3019 | 3.1066 | 3.1915 | 3.1211 | 3.156 | 3.2043 | 3.1829 | 3.1815 | 3.1735 | 3.0851 | 3.0921 | 3.1259 | 2.9859 | 3.1435 | 2.9486 | 3.1605 | 3.1377 | 3.1273 | 3.0985 | 3.1425 | 3.1749 | 3.1601 | 3.098 | 3.1608 | 3.1025 | 3.1039 | 3.0887 | 3.1425 | 3.0939 | 3.1546 | 3.0769 | 3.1156 | 2.9769 | 3.1401 | 3.0311 | 3.0538 | 3.0707 | 3.0687 | 3.0918 | 3.1184 | 3.0956 | 3.1529 | 3.1118 | 3.1818 | 3.13 | 3.0768 | 3.1329 | 3.1111 | 3.1992 | 3.0614 | 3.1208 | 3.1021 | 3.1335 | 3.1239 | 3.099 | 3.0914 | 3.0997 | 3.107 | 3.0835 | 3.1128 | 3.1787 | 3.1032 | 2.9996 | 3.0506 | 2.9955 | 2.9947 | 2.9936 | 3.006 | 3.0265 | 3.0514 | 3.0816 | 3.0351 | 3.0529 | 3.0688 | 3.0707 | 3.0329 | 3.0957 | 2.9888 | 3.0665 | 3.0673 | 3.0892 | 3.0794 | 3.0642 | 3.0843 | 3.0457 | 3.0707 | 3.0261 | 3.0824 | 3.0317 | 3.0529 | 3.0786 | 3.0683 | 3.077 | 3.0206 | 3.1222 | 3.3752 | 3.0334 | 3.1022 | 3.1429 | 3.0544 | 3.1052 | 3.1623 | 3.1182 | 3.0462 | 3.0976 | 3.0971 | 3.0517 | 3.3687 | 3.0884 | 3.6617 | 3.1523 | 3.1428 | 3.1513 | 3.1162 | 3.0063 | 3.0001 | 3.0789 | 3.0008 | 2.8997 | 2.9634 | 2.9801 | 2.9153 | 2.9934 | 3.0027 | 3.0765 | 3.0691 | 3.0597 | 3.007 | 3.1044 | 3.0276 | 3.1056 | 3.0341 | 3.0538 | 3.0734 | 2.9566 | 3.0022 | 2.9211 | 3.0104 | 3.0703 | 3.1001 | 3.0075 | 2.9891 | 3.0495 | 3.0081 | 3.1476 | 3.01 | 3.0096 | 2.9969 | 3.0141 | 3.0556 | 2.9906 | 3.013 | 3.019 | 3.0766 | 2.9326 | 3.0936 | 3.0917 | 2.9954 | 3.1047 | 2.9713 | 3.1104 | 3.1447 | 3.1356 | 3.0762 | 3.1426 | 3.0961 | 3.0009 | 3.0747 | 3.0303 | 3.0674 | 3.1367 | 3.1397 | 3.0814 | 3.1583 | 3.1201 | 2.898 | 3.0355 | 3.0144 | 3.0163 | 2.9263 | 2.9868 | 3.0423 | 2.9735 | 2.9467 | 3.0518 | 3.0052 | 2.9021 | 3.0559 | 3.0603 | 3.0329 | 3.0012 | 3.0088 | 3.0365 | 2.8889 | 3.0148 | 3.0235 | 2.9488 | 2.9996 | 2.9841 | 3.0421 | 3.0049 | 3.0629 | 3.0163 | 3.0416 | 3.0845 | 3.0302 | 3.0828 | 2.9425 | 3.0897 | 3.0283 | 3.0182 | 2.9969 | 3.0317 | 2.9703 | 2.9992 | 2.9756 | 2.9765 | 2.9859 | 3.0272 | 2.9977 | 2.9487 | 2.9887 | 2.9842 | 3.0037 | 3.0325 | 2.9678 | 3.0016 | 3.0706 | 3.0875 | 3.0612 | 3.0914 | 2.9506 | 3.0437 | 3.0044 | 3.0508 | 2.9794 | 3.0291 | 3.0313 | 3.0407 | 3.0687 | 3.0238 | 3.0447 | 3.0338 | 3.0537 | 3.0088 | 3.0428 | 3.0911 | 2.9677 | 2.8654 | 3.0055 | 3.0353 | 3.0041 | 3.0272 | 3.0206 | 2.8312 | 3.025 | 2.9796 | 3.033 | 3.0798 | 3.0887 | 3.084 | 3.0738 | 3.0374
2025-04-21 | 3.8477 | 3.7648 | 3.878 | 3.8856 | 3.85 | 3.7092 | 3.9656 | 3.775 | 3.8765 | 3.9008 | 3.9129 | 3.8909 | 3.9015 | 3.9015 | 3.9288 | 3.9364 | 3.8716 | 3.8963 | 3.8667 | 3.9136 | 4.0189 | 3.9803 | 4.0197 | 3.9985 | 3.9871 | 3.9947 | 4.0083 | 4.0083 | 4.025 | 4.0318 | 3.9795 | 4.0091 | 3.8485 | 3.7927 | 3.8238 | 3.8628 | 3.9274 | 3.929 | 3.8636 | 3.8868 | 3.8023 | 3.9009 | 3.982 | 3.9832 | 3.9846 | 4.0847 | 4.0483 | 4.0034 | 3.9364 | 3.977 | 3.9861 | 3.8782 | 3.5346 | 3.864 | 3.8032 | 3.8985 | 3.8804 | 3.7307 | 3.7276 | 3.7031 | 3.5068 | 3.8209 | 3.8578 | 4.1994 | 4.1404 | 4.136 | 4.1877 | 4.225 | 4.0529 | 4.0994 | 4.2005 | 4.2195 | 4.1194 | 4.0233 | 4.1094 | 4.2641 | 4.11 | 4.1342 | 4.1777 | 4.1736 | 4.137 | 4.1756 | 4.2008 | 4.2143 | 4.2329 | 4.2294 | 4.1995 | 4.1528 | 4.1715 | 4.1467 | 4.1546 | 4.0718 | 4.1625 | 4.168 | 4.2243 | 4.2119 | 4.186 | 4.1608 | 4.1877 | 4.1962 | 4.1439 | 4.2167 | 4.1144 | 4.2177 | 4.4117 | 4.197 | 4.2781 | 4.2374 | 4.2384 | 4.303 | 4.2588 | 4.2912 | 4.2234 | 4.1685 | 4.1643 | 4.2526 | 4.2015 | 4.2395 | 4.2381 | 4.235 | 4.225 | 4.2115 | 4.1714 | 4.2193 | 4.2429 | 4.2277 | 4.1401 | 4.2191 | 4.1718 | 4.1611 | 4.1546 | 4.2433 | 4.186 | 4.2533 | 4.1477 | 4.2008 | 4.1017 | 4.284 | 4.1927 | 4.1667 | 4.1553 | 4.2167 | 4.2029 | 4.2184 | 4.1856 | 4.2712 | 4.2329 | 4.2554 | 4.2378 | 4.2208 | 4.2155 | 4.235 | 4.4067 | 4.1822 | 4.1836 | 4.1829 | 4.2319 | 4.2246 | 4.2226 | 4.1636 | 4.1746 | 4.1818 | 4.1453 | 4.25 | 4.2988 | 4.18 | 4.1376 | 4.206 | 4.1497 | 4.147 | 4.1455 | 4.1614 | 4.1912 | 4.2309 | 4.2551 | 4.1859 | 4.2147 | 4.223 | 4.2332 | 4.1647 | 4.231 | 4.1126 | 4.2313 | 4.2203 | 4.2498 | 4.2389 | 4.2116 | 4.2468 | 4.1776 | 4.2347 | 4.1425 | 4.2347 | 4.1376 | 4.1878 | 4.2198 | 4.1925 | 4.2087 | 4.0926 | 4.2213 | 4.1982 | 4.1849 | 4.199 | 4.2465 | 4.1833 | 4.2424 | 4.276 | 4.2512 | 4.1401 | 4.2133 | 4.1796 | 4.1325 | 4.5419 | 4.1712 | 4.1821 | 4.2437 | 4.2582 | 4.2473 | 4.4305 | 4.0555 | 4.0695 | 4.1727 | 4.0762 | 4.0219 | 4.0437 | 3.7567 | 4.0126 | 4.112 | 4.1391 | 4.175 | 4.1809 | 4.1558 | 4.1127 | 4.206 | 4.1041 | 4.2166 | 4.1366 | 4.1476 | 4.1515 | 4.0301 | 4.1052 | 4.0106 | 4.1067 | 4.1617 | 4.2057 | 4.0738 | 4.0988 | 4.1527 | 4.0973 | 4.3053 | 4.0925 | 4.1142 | 4.094 | 4.0757 | 4.1482 | 4.0936 | 4.116 | 4.134 | 4.1284 | 4.0505 | 4.1577 | 4.1645 | 4.2154 | 4.2301 | 4.1778 | 4.2062 | 4.2372 | 4.2076 | 4.1567 | 4.2044 | 4.2066 | 4.0693 | 4.098 | 4.1289 | 4.1395 | 4.2077 | 4.1588 | 4.1895 | 4.2436 | 4.1937 | 3.9962 | 4.065 | 4.0612 | 4.065 | 3.9611 | 4.0098 | 4.0979 | 4.0246 | 3.9906 | 4.1398 | 4.1484 | 4.0363 | 4.164 | 4.1429 | 4.0679 | 4.0683 | 4.0772 | 4.1267 | 3.9989 | 4.0971 | 4.1115 | 4.0575 | 4.0804 | 4.0702 | 4.135 | 4.0929 | 4.156 | 4.1263 | 4.2014 | 4.206 | 4.129 | 4.0914 | 3.9711 | 4.146 | 4.0809 | 4.0712 | 4.0532 | 4.0909 | 4.0209 | 4.0151 | 4.0306 | 4.0208 | 4.0228 | 4.0831 | 4.0263 | 3.9826 | 4.0297 | 4.0099 | 3.9631 | 4.1175 | 4.0055 | 4.0714 | 4.0283 | 4.1809 | 4.1837 | 4.0039 | 4.036 | 4.1433 | 4.0869 | 4.1078 | 4.07 | 4.1242 | 4.0947 | 4.0966 | 4.1508 | 4.0966 | 4.1291 | 4.1248 | 4.1269 | 4.0527 | 4.1115 | 4.1613 | 4.092 | 3.962 | 4.088 | 4.1837 | 4.0913 | 4.1276 | 4.1316 | 3.8968 | 4.1123 | 4.0561 | 4.0832 | 4.1494 | 4.1656 | 4.1668 | 4.1617 | 4.1091
2025-04-22 | 0.81499 | 0.7799 | 0.82197 | 0.81818 | 0.81591 | 0.78208 | 0.84545 | 0.79394 | 0.83182 | 0.82348 | 0.83182 | 0.82727 | 0.8303 | 0.82576 | 0.83939 | 0.83636 | 0.81738 | 0.83971 | 0.84091 | 0.84167 | 0.87727 | 0.86742 | 0.87955 | 0.87121 | 0.87955 | 0.87424 | 0.88409 | 0.8803 | 0.89167 | 0.87879 | 0.87652 | 0.87197 | 0.82121 | 0.79745 | 0.79665 | 0.81419 | 0.82855 | 0.81738 | 0.81212 | 0.83014 | 0.7947 | 0.83809 | 0.85645 | 0.84503 | 0.85599 | 0.87699 | 0.87936 | 0.8797 | 0.84535 | 0.8723 | 0.87023 | 0.82741 | 0.82828 | 0.84334 | 0.83425 | 0.83905 | 0.84812 | 0.79663 | 0.80911 | 0.79972 | 0.8303 | 0.83838 | 0.81232 | 0.92271 | 0.90338 | 0.91277 | 0.90718 | 0.92236 | 0.90548 | 0.89924 | 0.91477 | 0.92719 | 0.89752 | 0.90071 | 0.89476 | 0.90584 | 0.88997 | 0.91684 | 0.92616 | 0.92995 | 0.91097 | 0.92956 | 0.9303 | 0.92785 | 0.93961 | 0.9329 | 0.92496 | 0.9193 | 0.91097 | 0.90683 | 0.90994 | 0.87888 | 0.89372 | 0.89821 | 0.90511 | 0.91753 | 0.91302 | 0.9196 | 0.90994 | 0.89899 | 0.89683 | 0.91546 | 0.89478 | 0.92202 | 0.93685 | 0.91994 | 0.92823 | 0.92063 | 0.90959 | 0.93099 | 0.92788 | 0.93892 | 0.92328 | 0.921 | 0.91891 | 0.94617 | 0.9372 | 0.93789 | 0.94859 | 0.93616 | 0.92961 | 0.93306 | 0.92316 | 0.93506 | 0.94513 | 0.93754 | 0.9196 | 0.93823 | 0.9234 | 0.92133 | 0.9196 | 0.94237 | 0.93168 | 0.94237 | 0.91511 | 0.92409 | 0.90765 | 0.94203 | 0.89206 | 0.93513 | 0.91097 | 0.93168 | 0.93237 | 0.92926 | 0.91442 | 0.93823 | 0.9303 | 0.93182 | 0.92989 | 0.90584 | 0.91667 | 0.92995 | 0.95087 | 0.92616 | 0.93513 | 0.91787 | 0.92892 | 0.93478 | 0.93927 | 0.91787 | 0.92133 | 0.92133 | 0.91339 | 0.94312 | 0.95928 | 0.91595 | 0.88246 | 0.91081 | 0.87831 | 0.88209 | 0.88624 | 0.87415 | 0.89078 | 0.90816 | 0.92744 | 0.91081 | 0.8972 | 0.91799 | 0.93046 | 0.89008 | 0.92196 | 0.91558 | 0.92063 | 0.92933 | 0.9263 | 0.91383 | 0.91988 | 0.91988 | 0.91686 | 0.9093 | 0.90136 | 0.90854 | 0.90023 | 0.90438 | 0.90159 | 0.89603 | 0.93175 | 0.89755 | 0.91929 | 0.92268 | 0.91207 | 0.91768 | 0.92496 | 0.91804 | 0.92997 | 0.93972 | 0.93372 | 0.91765 | 0.92336 | 0.915 | 0.9112 | 0.90048 | 0.92851 | 0.92818 | 0.92268 | 0.93343 | 0.92622 | 0.90529 | 0.89449 | 0.89368 | 0.90551 | 0.88482 | 0.87862 | 0.88482 | 0.89316 | 0.87991 | 0.89161 | 0.91551 | 0.91954 | 0.91052 | 0.89796 | 0.88062 | 0.91484 | 0.89893 | 0.92857 | 0.90188 | 0.90777 | 0.90934 | 0.87501 | 0.87389 | 0.87277 | 0.88996 | 0.95958 | 0.31436 | 0.93838 | 0.90902 | 0.91484 | 0.88099 | 0.90659 | 0.89295 | 0.90529 | 0.89445 | 0.93967 | 0.90566 | 0.87239 | 0.89706 | 0.8993 | 0.91979 | 0.9089 | 0.92724 | 0.92843 | 0.94339 | 0.94976 | 0.93388 | 0.93685 | 0.93835 | 0.93134 | 0.91905 | 0.92943 | 0.94242 | 0.91561 | 0.91385 | 0.92936 | 0.92295 | 0.92796 | 0.9175 | 0.92826 | 0.94068 | 0.93121 | 0.91005 | 0.90023 | 0.87566 | 0.87264 | 0.87453 | 0.88851 | 0.89872 | 0.88587 | 0.87226 | 0.91686 | 0.90787 | 0.9006 | 0.91232 | 0.92698 | 0.90714 | 0.91032 | 0.87443 | 0.90639 | 0.89154 | 0.88661 | 0.9105 | 0.90862 | 0.89837 | 0.87789 | 0.89609 | 0.90557 | 0.89099 | 0.89344 | 0.93008 | 0.91548 | 0.89841 | 0.93799 | 0.90199 | 0.92897 | 0.91201 | 0.90043 | 0.8937 | 0.91627 | 0.87582 | 0.88286 | 0.92693 | 0.87127 | 0.90306 | 0.95799 | 0.94416 | 0.93967 | 0.91986 | 0.9307 | 0.91612 | 0.94642 | 0.90895 | 0.92739 | 0.86538 | 0.9427 | 0.94702 | 0.96036 | 0.8993 | 0.91463 | 0.9251 | 0.91201 | 0.88473 | 0.91014 | 0.89146 | 0.90267 | 0.92584 | 0.88585 | 0.91366 | 0.92582 | 0.92024 | 0.88119 | 0.89011 | 0.93053 | 0.90624 | 0.88062 | 0.87949 | 0.91013 | 0.8859 | 0.90566 | 0.90873 | 0.8803 | 0.88847 | 0.87716 | 0.92151 | 0.90763 | 0.92033 | 0.93407 | 0.89835 | 0.89897
2025-04-23 | 2.6037 | 2.5191 | 2.622 | 2.6235 | 2.6098 | 2.5072 | 2.6848 | 2.5568 | 2.6447 | 2.6364 | 2.6523 | 2.6356 | 2.6462 | 2.6402 | 2.6735 | 2.6689 | 2.6196 | 2.6459 | 2.6288 | 2.6553 | 2.7326 | 2.6992 | 2.728 | 2.7015 | 2.7015 | 2.7061 | 2.728 | 2.7182 | 2.7348 | 2.7288 | 2.7068 | 2.7091 | 2.622 | 2.5718 | 2.5893 | 2.6156 | 2.6555 | 2.6411 | 2.6235 | 2.6435 | 2.5735 | 2.6491 | 2.7205 | 2.6952 | 2.7069 | 2.7764 | 2.7627 | 2.7386 | 2.6394 | 2.7055 | 2.7155 | 2.6345 | 2.6169 | 2.6329 | 2.5843 | 2.6291 | 2.6411 | 2.5182 | 2.5248 | 2.5014 | 2.6295 | 2.5924 | 2.6158 | 2.8499 | 2.8012 | 2.8037 | 2.8257 | 2.8575 | 2.835 | 2.7902 | 2.8527 | 2.8644 | 2.8054 | 2.7999 | 2.7999 | 2.8413 | 2.7933 | 2.7726 | 2.8489 | 2.8364 | 2.7364 | 2.8356 | 2.863 | 2.8615 | 2.8644 | 2.8766 | 2.8503 | 2.8177 | 2.8268 | 2.8133 | 2.8219 | 2.7792 | 2.8188 | 2.8357 | 2.8516 | 2.864 | 2.8022 | 2.8551 | 2.8551 | 2.8272 | 2.8182 | 2.8568 | 2.7981 | 2.8582 | 2.9772 | 2.8561 | 2.8941 | 2.8599 | 2.8471 | 2.9113 | 2.8868 | 2.9089 | 2.8753 | 2.8258 | 2.7685 | 2.8754 | 2.7146 | 2.8806 | 2.8847 | 2.8747 | 2.8685 | 2.7378 | 2.8478 | 2.8745 | 2.8913 | 2.8789 | 2.8233 | 2.8792 | 2.7271 | 2.8451 | 2.8399 | 2.8989 | 2.8533 | 2.9127 | 2.8427 | 2.8668 | 2.7998 | 2.9268 | 2.8511 | 2.9341 | 2.853 | 2.9224 | 2.9048 | 2.891 | 2.8789 | 2.9344 | 2.7892 | 2.9199 | 2.9616 | 2.7947 | 2.8865 | 2.9027 | 2.8598 | 2.8533 | 2.8948 | 2.8671 | 2.8043 | 2.7878 | 2.7743 | 2.8585 | 2.8685 | 2.8571 | 2.8385 | 2.881 | 2.9355 | 2.8019 | 2.8273 | 2.8662 | 2.8197 | 2.8186 | 2.8163 | 2.8186 | 2.8125 | 2.8689 | 2.893 | 2.8522 | 2.87 | 2.8794 | 2.8825 | 2.8365 | 2.8792 | 2.8016 | 2.873 | 2.8772 | 2.8885 | 2.8715 | 2.8605 | 2.8726 | 2.8443 | 2.8753 | 2.8209 | 2.8655 | 2.8114 | 2.8137 | 2.8484 | 2.8139 | 2.8671 | 2.8217 | 2.9046 | 2.8885 | 2.8814 | 2.8974 | 2.936 | 2.8715 | 2.8029 | 2.9538 | 2.939 | 2.8764 | 2.9196 | 2.8949 | 2.8797 | 2.8747 | 2.8797 | 2.8893 | 2.9109 | 2.9376 | 2.9191 | 2.8833 | 2.8238 | 2.6994 | 2.8663 | 2.823 | 2.776 | 2.7742 | 2.8016 | 2.7409 | 2.769 | 2.8018 | 2.8301 | 2.7955 | 2.8167 | 2.7689 | 2.8681 | 2.7917 | 2.8654 | 2.814 | 2.8175 | 2.8297 | 2.773 | 2.7693 | 2.7697 | 2.7861 | 2.8513 | 2.6138 | 2.7967 | 2.8119 | 2.8277 | 2.7667 | 2.8383 | 2.7906 | 2.8037 | 2.7914 | 2.8328 | 2.8418 | 2.7895 | 2.8022 | 2.8205 | 2.8329 | 2.7943 | 2.851 | 2.8511 | 2.7479 | 2.8666 | 2.7394 | 2.8769 | 2.8978 | 2.8783 | 2.8309 | 2.8843 | 2.8663 | 2.7344 | 2.8083 | 2.7933 | 2.8434 | 2.882 | 2.8484 | 2.8486 | 2.9042 | 2.8693 | 2.7763 | 2.7525 | 2.7264 | 2.7252 | 2.7018 | 2.7139 | 2.7748 | 2.7207 | 2.7075 | 2.8122 | 2.7581 | 2.7838 | 2.8057 | 2.8175 | 2.7603 | 2.7238 | 2.7477 | 2.7873 | 2.7607 | 2.7565 | 2.7664 | 2.6968 | 2.7581 | 2.7171 | 2.7929 | 2.7664 | 2.7656 | 2.7782 | 2.8288 | 2.8329 | 2.7825 | 2.7755 | 2.6933 | 2.8032 | 2.7697 | 2.7461 | 2.7282 | 2.7671 | 2.7055 | 2.6725 | 2.7176 | 2.7151 | 2.7422 | 2.7902 | 2.7495 | 2.7304 | 2.7252 | 2.7431 | 2.7245 | 2.7816 | 2.7064 | 2.7779 | 2.69 | 2.8167 | 2.7614 | 2.7414 | 2.7734 | 2.8246 | 2.8149 | 2.816 | 2.7708 | 2.8183 | 2.7667 | 2.8104 | 2.8168 | 2.7757 | 2.8195 | 2.823 | 2.822 | 2.7679 | 2.7955 | 2.8516 | 2.7722 | 2.7573 | 2.7573 | 2.8273 | 2.7544 | 2.8134 | 2.7794 | 2.7406 | 2.7887 | 2.7469 | 2.783 | 2.8257 | 2.8257 | 2.8493 | 2.8293 | 2.792
2025-04-24 | 3.0463 | 2.9545 | 3.078 | 3.0682 | 3.0409 | 2.9218 | 3.1691 | 2.9909 | 3.0788 | 3.0848 | 3.1348 | 3.0909 | 3.0833 | 3.0758 | 3.1129 | 3.0955 | 3.0574 | 3.1077 | 3.1273 | 3.1333 | 3.253 | 3.2045 | 3.2205 | 3.1856 | 3.2424 | 3.2129 | 3.222 | 3.1962 | 3.2742 | 3.2674 | 3.2 | 3.2068 | 3.0242 | 2.9912 | 3.0144 | 3.051 | 3.0941 | 3.0853 | 3.0341 | 3.0598 | 2.9705 | 3.0578 | 3.1262 | 3.076 | 3.1148 | 3.1823 | 3.1796 | 3.1431 | 3.1204 | 3.1438 | 3.1173 | 3.0399 | 3.0216 | 3.0524 | 3.0104 | 3.0798 | 3.0766 | 2.9453 | 2.9577 | 2.9353 | 3.0682 | 3.0263 | 3.0117 | 3.4158 | 3.3585 | 3.3673 | 3.3941 | 3.4365 | 3.3662 | 3.3223 | 3.3944 | 3.4476 | 3.3333 | 3.3347 | 3.3123 | 3.3553 | 3.2825 | 3.3658 | 3.401 | 3.3778 | 3.3395 | 3.4157 | 3.4386 | 3.4174 | 3.4776 | 3.4643 | 3.4325 | 3.4066 | 3.3999 | 3.3523 | 3.3692 | 3.4786 | 3.519 | 3.5473 | 3.5411 | 3.5783 | 3.5756 | 3.5576 | 3.53 | 3.4784 | 3.4776 | 3.5017 | 3.4377 | 3.5093 | 3.5059 | 3.4896 | 3.4986 | 3.4517 | 3.4362 | 3.5062 | 3.4783 | 3.5383 | 3.4819 | 3.4351 | 3.3516 | 3.4068 | 3.3116 | 3.4017 | 3.4344 | 3.3958 | 3.3509 | 3.274 | 3.3268 | 3.3784 | 3.3413 | 3.3026 | 3.2719 | 3.3123 | 3.3154 | 3.2916 | 3.2726 | 3.3499 | 3.3019 | 3.3568 | 3.2433 | 3.2553 | 3.1934 | 3.2968 | 3.2333 | 3.1856 | 3.1729 | 3.2505 | 3.2516 | 3.2239 | 3.2057 | 3.2774 | 3.2957 | 3.1926 | 3.2675 | 3.2013 | 3.2476 | 3.2633 | 3.2789 | 3.2667 | 3.3026 | 3.2743 | 3.2464 | 3.3309 | 3.1598 | 3.2781 | 3.295 | 3.2491 | 3.2219 | 3.3297 | 3.3665 | 3.2536 | 3.1954 | 3.2506 | 3.2037 | 3.2234 | 3.2351 | 3.2328 | 3.2449 | 3.2751 | 3.3005 | 3.2615 | 3.2502 | 3.2634 | 3.2982 | 3.2163 | 3.2725 | 3.1995 | 3.2971 | 3.2846 | 3.3005 | 3.28 | 3.2691 | 3.2925 | 3.2464 | 3.2967 | 3.2237 | 3.2986 | 3.2279 | 3.2475 | 3.2821 | 3.2591 | 3.2698 | 3.1523 | 3.2287 | 3.2041 | 3.2008 | 3.211 | 3.2399 | 3.2185 | 3.2042 | 3.2782 | 3.1346 | 3.2218 | 3.2596 | 3.2249 | 3.196 | 3.1929 | 3.2012 | 3.2339 | 3.2367 | 3.185 | 3.2405 | 3.1777 | 3.2028 | 3.1427 | 3.2163 | 3.1746 | 3.1485 | 3.1467 | 3.1393 | 3.1469 | 3.26 | 3.2985 | 3.3383 | 3.3085 | 3.3316 | 3.2989 | 3.3701 | 3.278 | 3.3053 | 3.2567 | 3.29 | 3.3128 | 3.2036 | 3.2298 | 3.1749 | 3.2175 | 3.0773 | 2.7378 | 3.2304 | 3.1771 | 3.2304 | 3.1707 | 3.239 | 3.1663 | 3.2462 | 3.2119 | 3.176 | 3.2197 | 3.2111 | 3.2193 | 3.2343 | 3.3174 | 3.271 | 3.3435 | 3.3487 | 3.4004 | 3.4128 | 3.3031 | 3.3812 | 3.3937 | 3.3646 | 3.3206 | 3.3563 | 3.3824 | 3.2709 | 3.2606 | 3.3151 | 3.2964 | 3.3312 | 3.2897 | 3.3421 | 3.362 | 3.3449 | 3.3621 | 3.3269 | 3.3137 | 3.3432 | 3.2536 | 3.311 | 3.3348 | 3.2642 | 3.2498 | 3.3689 | 3.3357 | 3.3466 | 3.3647 | 3.3675 | 3.3556 | 3.3202 | 3.3421 | 3.376 | 3.3549 | 3.3493 | 3.3496 | 3.3309 | 3.3144 | 3.311 | 3.3185 | 3.3227 | 3.3719 | 3.3455 | 3.4135 | 3.3956 | 3.3373 | 3.3485 | 3.2493 | 3.4063 | 3.3367 | 3.3165 | 3.2889 | 3.3353 | 3.2781 | 3.2623 | 3.2653 | 3.2877 | 3.3148 | 3.3558 | 3.3001 | 3.2911 | 3.2952 | 3.2642 | 3.2145 | 3.3558 | 3.2826 | 3.356 | 3.2202 | 3.3293 | 3.332 | 3.2166 | 3.315 | 3.3804 | 3.349 | 3.3595 | 3.3281 | 3.367 | 3.3124 | 3.3703 | 3.3782 | 3.3214 | 3.3681 | 3.3795 | 3.3554 | 3.2868 | 3.3399 | 3.3846 | 3.3367 | 3.2937 | 3.2978 | 3.3595 | 3.3013 | 3.3438 | 3.3559 | 3.3018 | 3.3195 | 3.3065 | 3.3175 | 3.3533 | 3.3713 | 3.3885 | 3.3701 | 3.2729
2025-04-25 | 4.366 | 4.2584 | 4.3985 | 4.4038 | 4.3659 | 4.2225 | 4.4958 | 4.2765 | 4.4023 | 4.4227 | 4.4409 | 4.4136 | 4.4311 | 4.4182 | 4.4689 | 4.4727 | 4.3979 | 4.4187 | 4.3818 | 4.4356 | 4.5629 | 4.503 | 4.5621 | 4.5402 | 4.5205 | 4.5174 | 4.5477 | 4.5402 | 4.5712 | 4.5712 | 4.5205 | 4.553 | 4.3667 | 4.303 | 4.3413 | 4.3844 | 4.4506 | 4.453 | 4.3886 | 4.4123 | 4.3227 | 4.4237 | 4.5229 | 4.5146 | 4.5066 | 4.6281 | 4.5898 | 4.422 | 4.4352 | 4.5136 | 4.5323 | 4.4126 | 4.3759 | 4.392 | 4.3177 | 4.4269 | 4.3952 | 4.2125 | 4.222 | 4.2051 | 4.4197 | 4.3384 | 4.3776 | 4.7557 | 4.685 | 4.6923 | 4.7409 | 4.755 | 4.7334 | 4.6366 | 4.7553 | 4.7409 | 4.6591 | 4.6051 | 4.6515 | 4.7302 | 4.6656 | 4.7329 | 4.7612 | 4.7484 | 4.6729 | 4.7421 | 4.8078 | 4.7955 | 4.7788 | 4.7316 | 4.7558 | 4.6947 | 4.7395 | 4.7198 | 4.7267 | 4.6242 | 4.7222 | 4.7519 | 4.8047 | 4.7681 | 4.6962 | 4.7516 | 4.7695 | 4.7709 | 4.7276 | 4.7909 | 4.6857 | 4.7678 | 4.9082 | 4.7585 | 4.8644 | 4.766 | 4.7895 | 4.8768 | 4.8464 | 4.8634 | 4.8356 | 4.6955 | 4.7246 | 4.7678 | 4.7429 | 4.8054 | 4.6032 | 4.8126 | 4.7881 | 4.7785 | 4.7464 | 4.7955 | 4.8133 | 4.7988 | 4.705 | 4.7926 | 4.6432 | 4.7326 | 4.7215 | 4.8157 | 4.7284 | 4.8437 | 4.7215 | 4.6539 | 4.6591 | 4.7912 | 4.646 | 4.7091 | 4.6366 | 4.7219 | 4.7602 | 4.7757 | 4.7581 | 4.8347 | 4.5086 | 4.8398 | 4.8297 | 4.7208 | 4.7984 | 4.7816 | 4.9203 | 4.5928 | 4.7778 | 4.6539 | 4.7447 | 4.8123 | 4.6791 | 4.7395 | 4.7609 | 4.7516 | 4.7057 | 4.7526 | 4.8485 | 4.7633 | 4.7018 | 4.709 | 4.7177 | 4.709 | 4.568 | 4.7071 | 4.7271 | 4.7615 | 4.7963 | 4.7305 | 4.7525 | 4.7751 | 4.7838 | 4.7294 | 4.7963 | 4.6494 | 4.7808 | 4.7736 | 4.7982 | 4.7789 | 4.76 | 4.7838 | 4.7328 | 4.7929 | 4.7007 | 4.7993 | 4.7022 | 4.7389 | 4.7746 | 4.752 | 4.7587 | 4.6628 | 4.8069 | 4.7606 | 4.7264 | 4.7546 | 4.8213 | 4.7043 | 4.5939 | 4.8377 | 4.8058 | 4.6657 | 4.7799 | 4.7313 | 4.6754 | 4.5885 | 4.74 | 4.7543 | 4.8312 | 4.7229 | 4.8199 | 4.7536 | 4.6085 | 4.5962 | 4.7112 | 4.611 | 4.5473 | 4.5471 | 4.5961 | 4.4843 | 4.6589 | 4.6842 | 4.7378 | 4.7586 | 4.7206 | 4.6681 | 4.779 | 4.6651 | 4.7834 | 4.708 | 4.7174 | 4.7225 | 4.6191 | 4.6408 | 4.5847 | 4.6449 | 4.7998 | 4.7378 | 4.6472 | 4.6849 | 4.73 | 4.6625 | 4.7292 | 4.6643 | 4.6741 | 4.6543 | 4.6614 | 4.7193 | 4.664 | 4.6756 | 4.6995 | 4.6682 | 4.4913 | 4.7219 | 4.7169 | 4.7272 | 4.7299 | 4.7409 | 4.7639 | 4.8245 | 4.8 | 4.7133 | 4.7981 | 4.7545 | 4.5767 | 4.6525 | 4.6199 | 4.7164 | 4.8007 | 4.7453 | 4.7498 | 4.8438 | 4.7724 | 4.6527 | 4.6334 | 4.6251 | 4.6478 | 4.4989 | 4.585 | 4.6614 | 4.5733 | 4.531 | 4.7033 | 4.5883 | 4.6833 | 4.7041 | 4.7008 | 4.6472 | 4.6365 | 4.6507 | 4.7013 | 4.678 | 4.6678 | 4.6621 | 4.6165 | 4.6424 | 4.628 | 4.6841 | 4.6314 | 4.7203 | 4.6826 | 4.7271 | 4.7341 | 4.6913 | 4.6362 | 4.485 | 4.7274 | 4.6412 | 4.6262 | 4.6094 | 4.6516 | 4.5708 | 4.5548 | 4.549 | 4.5977 | 4.6036 | 4.6457 | 4.5791 | 4.5414 | 4.5731 | 4.5638 | 4.5249 | 4.6415 | 4.5565 | 4.6429 | 4.5648 | 4.7402 | 4.737 | 4.5922 | 4.6173 | 4.7339 | 4.6845 | 4.7167 | 4.6632 | 4.6924 | 4.6786 | 4.7174 | 4.7402 | 4.6756 | 4.7166 | 4.737 | 4.7111 | 4.6468 | 4.6986 | 4.7582 | 4.6357 | 4.6475 | 4.6614 | 4.7512 | 4.6528 | 4.729 | 4.6803 | 4.6232 | 4.6901 | 4.637 | 4.6731 | 4.7521 | 4.7559 | 4.7602 | 4.759 | 4.6599
2025-04-26 | 4.5048 | 4.3923 | 4.5326 | 4.5341 | 4.5129 | 4.3683 | 4.635 | 4.4068 | 4.55 | 4.5674 | 4.5773 | 4.5538 | 4.5674 | 4.5591 | 4.6106 | 4.6023 | 4.5359 | 4.559 | 4.5205 | 4.5758 | 4.7068 | 4.6447 | 4.7121 | 4.6795 | 4.6591 | 4.6523 | 4.6811 | 4.6682 | 4.7 | 4.7045 | 4.6485 | 4.6856 | 4.5068 | 4.4442 | 4.4801 | 4.5191 | 4.5797 | 4.5837 | 4.5303 | 4.5399 | 4.4477 | 4.5556 | 4.6741 | 4.6513 | 4.644 | 4.7699 | 4.7252 | 4.5329 | 4.5978 | 4.6518 | 4.6672 | 4.5388 | 4.5014 | 4.5259 | 4.4427 | 4.5654 | 4.5262 | 4.3282 | 4.3458 | 4.3129 | 4.5455 | 4.4538 | 4.5191 | 4.9168 | 4.8357 | 4.7937 | 4.8778 | 4.9327 | 4.8716 | 4.8088 | 4.9072 | 4.9372 | 4.8389 | 4.7974 | 4.833 | 4.8932 | 4.8222 | 4.8513 | 4.8689 | 4.8778 | 4.842 | 4.9011 | 4.9293 | 4.9405 | 4.941 | 4.8488 | 4.9196 | 4.8567 | 4.8361 | 4.8561 | 4.8782 | 4.8088 | 4.911 | 4.9041 | 4.9486 | 4.9548 | 4.8863 | 4.9006 | 4.9344 | 4.9372 | 4.8806 | 4.9396 | 4.8109 | 4.9389 | 5.0687 | 4.9493 | 5.0083 | 4.9517 | 4.951 | 5.0359 | 4.9917 | 5.03 | 4.7585 | 4.8593 | 4.8799 | 4.9462 | 4.921 | 4.961 | 4.9617 | 4.9438 | 4.9331 | 4.9379 | 4.8986 | 4.939 | 4.9589 | 4.9362 | 4.8461 | 4.8934 | 4.7802 | 4.8896 | 4.8778 | 4.972 | 4.8979 | 4.9917 | 4.8709 | 4.7899 | 4.7778 | 4.98 | 4.8378 | 4.8799 | 4.8565 | 4.9089 | 4.8965 | 4.8847 | 4.913 | 4.9862 | 4.8444 | 4.9672 | 5.0298 | 4.8467 | 4.9365 | 4.9517 | 5.0695 | 4.8682 | 4.9327 | 4.9041 | 4.9593 | 4.8492 | 4.9386 | 4.8741 | 4.8954 | 4.7988 | 4.7988 | 4.9243 | 5.0117 | 4.7994 | 4.8091 | 4.8938 | 4.8435 | 4.8416 | 4.8424 | 4.8639 | 4.8957 | 4.9509 | 4.9758 | 4.8949 | 4.9036 | 4.9006 | 4.9324 | 4.8484 | 4.9136 | 4.7947 | 4.9327 | 4.9233 | 4.9554 | 4.9482 | 4.9074 | 4.9516 | 4.8715 | 4.9505 | 4.8284 | 4.9426 | 4.8398 | 4.89 | 4.9103 | 4.8829 | 4.9167 | 4.7727 | 4.9018 | 4.8693 | 4.8627 | 4.8829 | 4.9377 | 4.8626 | 4.9225 | 4.9595 | 4.9468 | 4.8105 | 4.7809 | 4.8337 | 4.8034 | 4.7177 | 4.8639 | 4.8489 | 4.9172 | 4.9385 | 4.9161 | 4.85 | 4.758 | 4.7257 | 4.7979 | 4.7353 | 4.6907 | 4.6661 | 4.7212 | 4.6379 | 4.8084 | 4.8509 | 4.8591 | 4.8799 | 4.8426 | 4.7955 | 4.9188 | 4.7907 | 4.9066 | 4.8316 | 4.8438 | 4.845 | 4.7499 | 4.7881 | 4.7242 | 4.794 | 4.8976 | 4.8344 | 4.7265 | 4.7997 | 4.825 | 4.7514 | 4.8195 | 4.7518 | 4.8154 | 4.7817 | 4.7077 | 4.8303 | 4.7967 | 4.8101 | 4.8311 | 4.8687 | 4.7989 | 4.9092 | 4.907 | 4.9402 | 4.9392 | 4.9143 | 4.9506 | 4.9857 | 4.9512 | 4.885 | 4.9447 | 4.9199 | 4.7129 | 4.7193 | 4.7745 | 4.8496 | 4.9093 | 4.8565 | 4.9055 | 4.9579 | 4.9183 | 4.8413 | 4.8084 | 4.8054 | 4.8205 | 4.6841 | 4.7475 | 4.8462 | 4.7536 | 4.7154 | 4.9036 | 4.8395 | 4.8787 | 4.9044 | 4.8933 | 4.7921 | 4.8 | 4.8006 | 4.8718 | 4.8297 | 4.832 | 4.84 | 4.8494 | 4.807 | 4.7948 | 4.8673 | 4.8165 | 4.8872 | 4.862 | 4.9399 | 4.931 | 4.8563 | 4.8155 | 4.6891 | 4.9024 | 4.8269 | 4.8172 | 4.7959 | 4.8353 | 4.7418 | 4.6692 | 4.7445 | 4.7739 | 4.7751 | 4.8445 | 4.7417 | 4.7357 | 4.7567 | 4.7361 | 4.6965 | 4.8549 | 4.7449 | 4.8159 | 4.7622 | 4.9097 | 4.8469 | 4.8265 | 4.763 | 4.8845 | 4.8397 | 4.8617 | 4.8221 | 4.8707 | 4.8251 | 4.8789 | 4.9088 | 4.8333 | 4.8823 | 4.8705 | 4.8894 | 4.8058 | 4.8579 | 4.9231 | 4.8241 | 4.7926 | 4.8071 | 4.8976 | 4.823 | 4.8871 | 4.8466 | 4.7716 | 4.861 | 4.7904 | 4.8155 | 4.9004 | 4.8976 | 4.9223 | 4.9207 | 4.8109
2025-04-27 | 4.6244 | 4.4809 | 4.6576 | 4.6386 | 4.6106 | 4.4685 | 4.7751 | 4.5348 | 4.6598 | 4.6879 | 4.728 | 4.7114 | 4.6697 | 4.7045 | 4.7326 | 4.7409 | 4.681 | 4.7137 | 4.6833 | 4.7364 | 4.8758 | 4.8098 | 4.8485 | 4.8394 | 4.8167 | 4.8098 | 4.828 | 4.8242 | 4.8568 | 4.8515 | 4.7917 | 4.828 | 4.5735 | 4.5255 | 4.5598 | 4.6132 | 4.6938 | 4.7289 | 4.6295 | 4.6611 | 4.5379 | 4.6198 | 4.7025 | 4.6396 | 4.7091 | 4.7822 | 4.754 | 4.7278 | 4.5593 | 4.7606 | 4.7537 | 4.6302 | 4.6053 | 4.6453 | 4.5684 | 4.6438 | 4.6431 | 4.4467 | 4.476 | 4.4423 | 4.6992 | 4.6107 | 4.6129 | 5.0072 | 4.922 | 5.0177 | 5.0204 | 4.9683 | 5.0095 | 4.8775 | 5.0676 | 4.9669 | 4.883 | 4.8239 | 4.8751 | 5.0346 | 4.956 | 5.0276 | 5.0152 | 5.0801 | 4.6839 | 4.9702 | 5.136 | 5.0541 | 4.98 | 5.1302 | 4.974 | 4.91 | 5.0676 | 5.0007 | 4.9669 | 4.9496 | 5.0104 | 5.1542 | 5.1391 | 5.0573 | 4.9721 | 5.1567 | 5.0469 | 5.0051 | 5.0653 | 5.0197 | 4.9849 | 4.9707 | 5.1746 | 4.9714 | 5.0825 | 4.961 | 4.9693 | 5.0977 | 5.0942 | 4.9241 | 4.9369 | 4.912 | 4.6732 | 4.8285 | 4.9393 | 5.0121 | 4.8209 | 5.0776 | 5.0093 | 4.9741 | 4.9434 | 5.0451 | 5.0707 | 5.038 | 4.9472 | 5.0179 | 4.9258 | 4.8986 | 4.3061 | 1.4182 | 4.8461 | 4.9375 | 4.853 | 4.863 | 4.6595 | 4.7705 | 4.6387 | 4.7412 | 4.8064 | 4.6919 | 4.7402 | 4.8364 | 4.8068 | 4.8244 | 4.696 | 4.8965 | 4.8915 | 4.7929 | 4.8952 | 4.7957 | 5.0026 | 4.7419 | 4.823 | 4.6591 | 1.5304 | 4.7619 | 4.8188 | 4.6184 | 4.8357 | 4.7495 | 4.8064 | 4.8264 | 4.9248 | 4.8741 | 4.7615 | 4.8447 | 4.8243 | 4.8216 | 4.785 | 4.7823 | 4.7698 | 4.7797 | 4.7793 | 4.757 | 4.836 | 4.8553 | 4.8292 | 4.8742 | 4.9334 | 4.6414 | 4.8103 | 4.7891 | 4.7804 | 4.7525 | 4.7362 | 4.743 | 4.7354 | 4.7634 | 4.7207 | 4.7551 | 4.6723 | 4.6916 | 4.7821 | 4.7508 | 4.7718 | 4.7079 | 4.9061 | 4.8846 | 4.778 | 4.8137 | 4.9484 | 4.7541 | 4.6526 | 4.9328 | 4.6386 | 4.7417 | 4.7146 | 4.8849 | 4.8403 | 4.6997 | 4.8371 | 4.9031 | 4.894 | 4.8384 | 4.9777 | 4.9093 | 4.6965 | 4.7073 | 4.8377 | 4.7058 | 4.6651 | 4.6999 | 4.6547 | 4.6158 | 4.6925 | 4.7356 | 4.8717 | 4.8834 | 4.8677 | 4.7724 | 4.9133 | 4.7597 | 4.9199 | 4.8359 | 4.8324 | 4.8579 | 4.7185 | 4.6681 | 4.6561 | 4.6472 | 4.9282 | 4.8772 | 4.7889 | 4.7937 | 4.8717 | 4.7619 | 4.8548 | 4.8479 | 4.7073 | 4.7126 | 4.7727 | 4.9118 | 4.655 | 4.6786 | 4.7361 | 4.7667 | 4.7921 | 4.9041 | 4.8784 | 4.7412 | 4.8558 | 4.7761 | 4.8166 | 4.9925 | 4.9881 | 4.8454 | 4.9344 | 4.8336 | 4.6694 | 4.8141 | 4.6713 | 4.8204 | 4.9433 | 4.8801 | 4.8034 | 4.9674 | 4.9065 | 4.8862 | 4.8564 | 4.8692 | 4.8768 | 4.7453 | 4.828 | 4.8621 | 4.7759 | 4.7717 | 4.9017 | 4.716 | 4.8855 | 4.8647 | 4.9198 | 4.9111 | 4.9179 | 4.8942 | 4.895 | 4.8859 | 4.8927 | 4.8555 | 4.711 | 4.7948 | 4.8013 | 4.8419 | 4.7945 | 4.969 | 4.829 | 4.8689 | 4.9409 | 4.8659 | 4.9568 | 4.7007 | 4.9778 | 4.8531 | 4.8273 | 4.8083 | 4.8821 | 4.8013 | 4.6363 | 4.66 | 4.8615 | 4.8552 | 4.8434 | 4.8154 | 4.7556 | 4.7585 | 4.7668 | 4.7955 | 4.7636 | 4.7751 | 4.8528 | 4.94 | 4.9227 | 4.9333 | 4.9564 | 4.6984 | 4.6931 | 4.661 | 4.8034 | 4.8049 | 4.8 | 4.7959 | 4.8243 | 4.8553 | 4.8232 | 4.918 | 4.9019 | 4.8576 | 4.7934 | 4.8964 | 4.938 | 4.7552 | 4.6535 | 4.63 | 4.8819 | 4.6379 | 4.8924 | 4.8063 | 4.7892 | 4.8733 | 4.8014 | 4.8293 | 4.9661 | 4.9564 | 4.9714 | 4.8218 | 4.8014
2025-04-28 | 1.3868 | 1.3285 | 1.3962 | 1.3932 | 1.3932 | 1.3379 | 1.4338 | 1.3591 | 1.4189 | 1.4227 | 1.4106 | 1.4076 | 1.4167 | 1.4205 | 1.4356 | 1.4205 | 1.4043 | 1.4346 | 1.4326 | 1.4409 | 1.4924 | 1.475 | 1.4894 | 1.4735 | 1.4909 | 1.4795 | 1.4985 | 1.4871 | 1.503 | 1.5038 | 1.4818 | 1.4848 | 1.4023 | 1.378 | 1.3804 | 1.4019 | 1.4147 | 1.4099 | 1.3917 | 1.4019 | 1.3568 | 1.4123 | 1.4528 | 1.4276 | 1.4532 | 1.4841 | 1.4906 | 1.4899 | 1.4493 | 1.4752 | 1.4809 | 1.438 | 1.4127 | 1.4341 | 1.4075 | 1.4318 | 1.4368 | 1.3661 | 1.3722 | 1.3602 | 1.3992 | 1.414 | 1.4128 | 1.5514 | 1.5138 | 1.5296 | 1.5262 | 1.5566 | 1.5272 | 1.5117 | 1.5407 | 1.5666 | 1.5131 | 1.5236 | 1.5093 | 1.5328 | 1.4733 | 1.5286 | 1.5442 | 1.5459 | 1.5286 | 1.5536 | 1.5618 | 1.553 | 1.5745 | 1.5711 | 1.5534 | 1.5417 | 1.5483 | 1.519 | 1.5262 | 1.5179 | 1.539 | 1.5493 | 1.5466 | 1.5769 | 1.5667 | 1.5707 | 1.5535 | 1.5321 | 1.5418 | 1.5504 | 1.5202 | 1.5638 | 1.6263 | 1.5745 | 1.5721 | 1.5607 | 1.5349 | 1.5825 | 1.5683 | 1.5883 | 1.565 | 1.5483 | 1.4859 | 1.5756 | 1.5611 | 1.5569 | 1.5756 | 1.5473 | 1.5473 | 1.5597 | 1.5404 | 1.5556 | 1.5749 | 1.5597 | 1.5311 | 1.5576 | 1.5345 | 1.5324 | 1.4327 | 1.1881 | 1.5518 | 1.5738 | 1.5324 | 1.5445 | 1.5133 | 1.5663 | 1.5527 | 1.5242 | 1.5228 | 1.5538 | 1.5573 | 1.549 | 1.5321 | 1.5631 | 1.5594 | 1.5563 | 1.5572 | 1.5133 | 1.5298 | 1.5594 | 1.5971 | 1.5542 | 1.5618 | 1.2581 | 0 | 1.6674 | 1.6794 | 1.5304 | 1.5359 | 1.5338 | 1.5159 | 1.5628 | 1.5828 | 1.5278 | 1.4327 | 1.4274 | 1.4342 | 1.4358 | 1.4342 | 1.432 | 1.4278 | 1.4569 | 1.4626 | 1.4388 | 1.4369 | 1.4395 | 1.4452 | 1.4567 | 1.4281 | 1.4358 | 1.4426 | 1.4433 | 1.4584 | 1.4577 | 1.4437 | 1.4546 | 1.4259 | 1.4599 | 1.4191 | 1.452 | 1.4293 | 1.4324 | 1.4325 | 1.4302 | 1.4472 | 1.4903 | 1.5293 | 1.5228 | 1.5167 | 1.5241 | 1.5446 | 1.5264 | 1.5507 | 1.5601 | 1.5634 | 1.5281 | 1.5374 | 1.5168 | 1.5142 | 1.4386 | 1.5296 | 1.5365 | 1.5322 | 1.5508 | 1.5422 | 1.5101 | 1.4901 | 1.4703 | 1.5002 | 1.4784 | 1.425 | 1.4237 | 1.4887 | 1.4534 | 1.4211 | 1.4318 | 1.4258 | 1.4333 | 1.4403 | 1.4192 | 1.4509 | 1.4181 | 1.4356 | 1.4297 | 1.4376 | 1.4313 | 1.4245 | 1.4166 | 1.42 | 1.4174 | 1.4576 | 1.0204 | 1.4223 | 1.4233 | 1.4478 | 1.4166 | 1.4403 | 1.4495 | 1.4375 | 1.4398 | 1.4372 | 1.4331 | 1.417 | 1.417 | 1.4185 | 1.5064 | 1.504 | 1.5019 | 1.5269 | 1.5522 | 1.563 | 1.5469 | 1.5472 | 1.5513 | 1.5354 | 1.531 | 1.541 | 1.5602 | 1.5084 | 1.5007 | 1.5271 | 1.5113 | 1.5411 | 1.5241 | 1.5391 | 1.5583 | 1.541 | 1.4509 | 1.4346 | 1.4346 | 1.4358 | 1.4339 | 1.4312 | 1.4327 | 1.421 | 1.4286 | 1.4399 | 1.4369 | 1.4289 | 1.4225 | 1.4345 | 1.425 | 1.4238 | 1.43 | 1.425 | 1.4255 | 1.4122 | 1.4133 | 1.4296 | 1.4115 | 1.4247 | 1.4289 | 1.4297 | 1.4512 | 1.4228 | 1.4433 | 1.4437 | 1.4175 | 1.3544 | 1.377 | 1.3571 | 1.3669 | 1.349 | 1.3426 | 1.3444 | 1.3038 | 1.3142 | 1.3301 | 1.3387 | 1.3426 | 1.3755 | 1.3508 | 1.3291 | 1.3164 | 1.3478 | 1.3721 | 1.3813 | 1.2987 | 1.3465 | 1.3827 | 1.3791 | 1.3697 | 1.3968 | 1.3848 | 1.4256 | 1.4323 | 1.4088 | 1.4136 | 1.42 | 1.3983 | 1.4177 | 1.426 | 1.3964 | 1.4156 | 1.4089 | 1.4271 | 1.3831 | 1.4078 | 1.4345 | 1.4307 | 1.3871 | 1.3841 | 1.4505 | 1.3997 | 1.4439 | 1.4236 | 1.3932 | 1.4267 | 1.3838 | 1.4203 | 1.4269 | 1.4097 | 1.4199 | 1.3509 | 1.4664
2025-04-29 | 2.2982 | 2.2097 | 2.3121 | 2.3068 | 2.3053 | 2.2103 | 2.3749 | 2.2561 | 2.3462 | 2.347 | 2.3439 | 2.3326 | 2.3394 | 2.3455 | 2.3697 | 2.3515 | 2.3214 | 2.362 | 2.3485 | 2.3674 | 2.4455 | 2.4182 | 2.4515 | 2.4197 | 2.428 | 2.4098 | 2.447 | 2.4333 | 2.4568 | 2.4523 | 2.4227 | 2.4197 | 2.3045 | 2.2687 | 2.2831 | 2.3118 | 2.3381 | 2.3333 | 2.3083 | 2.3238 | 2.2432 | 2.3267 | 2.3897 | 2.3545 | 2.3896 | 2.4436 | 2.4424 | 2.4261 | 2.3643 | 2.3985 | 2.4164 | 2.3503 | 2.3225 | 2.3423 | 2.3059 | 2.3471 | 2.3495 | 2.2328 | 2.2564 | 2.2344 | 2.3265 | 2.3113 | 2.3226 | 2.5535 | 2.4945 | 2.5095 | 2.5121 | 2.5576 | 2.5156 | 2.4862 | 2.5324 | 2.5728 | 2.4896 | 2.5057 | 2.4872 | 2.5216 | 2.4708 | 2.5014 | 2.5259 | 2.5221 | 2.5083 | 2.5437 | 2.5583 | 2.5566 | 2.5901 | 2.5891 | 2.5653 | 2.5502 | 2.5421 | 2.5093 | 2.5138 | 2.4938 | 2.5324 | 2.5445 | 2.5476 | 2.5949 | 2.5803 | 2.5873 | 2.5663 | 2.5245 | 2.5332 | 2.5618 | 2.5117 | 2.5801 | 2.6832 | 2.588 | 2.5908 | 2.5714 | 2.5366 | 2.6049 | 2.5821 | 2.6242 | 2.5828 | 2.5592 | 2.5197 | 2.5794 | 2.5566 | 2.5531 | 2.5707 | 2.5421 | 2.5383 | 2.5542 | 2.5271 | 2.548 | 2.5707 | 2.5504 | 2.5045 | 2.5493 | 2.5245 | 2.521 | 2.5179 | 2.1097 | 2.5483 | 2.5839 | 2.5138 | 2.5314 | 2.4787 | 2.5621 | 2.5346 | 2.4879 | 2.4841 | 2.5407 | 2.5476 | 2.5252 | 2.5052 | 2.5573 | 2.5549 | 2.5512 | 2.5569 | 2.4964 | 2.5302 | 2.5542 | 2.6259 | 2.785 | 2.882 | 2.8703 | 0 | 2.8996 | 2.9175 | 2.528 | 2.5342 | 2.5373 | 2.5 | 2.5962 | 2.6304 | 2.5231 | 2.4751 | 2.5314 | 2.4913 | 2.4985 | 2.5064 | 2.4955 | 2.5042 | 2.5408 | 2.5642 | 2.5317 | 2.5348 | 2.5401 | 2.5616 | 2.4968 | 2.5472 | 2.5105 | 2.5503 | 2.5582 | 2.5601 | 2.5442 | 2.5382 | 2.5522 | 2.5317 | 2.5631 | 2.5076 | 2.5661 | 2.5091 | 2.5219 | 2.5381 | 2.5202 | 2.5591 | 2.4589 | 2.518 | 2.5016 | 2.5005 | 2.5094 | 2.5442 | 2.5108 | 2.5456 | 2.5648 | 2.5735 | 2.5093 | 2.5253 | 2.4953 | 2.4886 | 2.4324 | 2.5147 | 2.5208 | 2.5263 | 2.5529 | 2.5345 | 2.493 | 2.4588 | 2.4257 | 2.4708 | 2.438 | 2.4116 | 2.4023 | 2.4563 | 2.436 | 2.4996 | 2.5478 | 2.5424 | 2.5385 | 2.5353 | 2.4994 | 2.5616 | 2.4957 | 2.562 | 2.5298 | 2.5341 | 2.5114 | 2.452 | 2.4793 | 2.4512 | 2.4901 | 2.5962 | 2.5196 | 2.5118 | 2.5342 | 2.5341 | 2.4531 | 2.5157 | 2.489 | 2.5211 | 2.4953 | 2.4987 | 2.5095 | 2.4808 | 2.5039 | 2.5174 | 2.4929 | 2.4717 | 2.4667 | 2.5125 | 2.5567 | 2.5716 | 2.5543 | 2.5507 | 2.571 | 2.5565 | 2.5206 | 2.5592 | 2.5778 | 2.4568 | 2.4375 | 2.5213 | 2.5052 | 2.5501 | 2.5214 | 2.5524 | 2.5713 | 2.551 | 2.5215 | 2.4898 | 2.4717 | 2.4796 | 2.4214 | 2.4811 | 2.4947 | 2.4562 | 2.4433 | 2.5518 | 2.5262 | 2.5283 | 2.5325 | 2.5532 | 2.5171 | 2.4829 | 2.489 | 2.5342 | 2.5009 | 2.5006 | 2.5195 | 2.4669 | 2.4964 | 2.4862 | 2.507 | 2.5154 | 2.5354 | 2.5248 | 2.5665 | 2.5587 | 2.523 | 2.4423 | 2.4227 | 2.5544 | 2.514 | 2.4953 | 2.4822 | 2.5198 | 2.4581 | 2.4284 | 2.4636 | 2.4772 | 2.513 | 2.5637 | 2.4628 | 2.5189 | 2.4834 | 2.4845 | 2.4228 | 2.5454 | 2.4859 | 2.5141 | 2.2284 | 2.5632 | 2.5863 | 2.4651 | 2.5129 | 2.5518 | 2.5626 | 2.523 | 2.52 | 2.5465 | 2.4923 | 2.5342 | 2.5611 | 2.4942 | 2.5546 | 2.5863 | 2.5492 | 2.4952 | 2.5247 | 2.5781 | 2.5528 | 2.4972 | 2.455 | 2.5718 | 2.4943 | 2.5581 | 2.5321 | 2.4882 | 2.5222 | 2.4957 | 2.5216 | 2.5506 | 2.5506 | 2.5859 | 2.511 | 2.4966
2025-04-30 | 4.5534 | 4.4155 | 4.5742 | 4.5659 | 4.572 | 4.4381 | 4.6825 | 4.4576 | 4.6242 | 4.6402 | 4.6288 | 4.6174 | 4.6265 | 4.6379 | 4.6758 | 4.6561 | 4.5973 | 4.6284 | 4.5848 | 4.6455 | 4.7674 | 4.7205 | 4.7583 | 4.753 | 4.7227 | 4.6833 | 4.7424 | 4.7227 | 4.7583 | 4.7636 | 4.7045 | 4.7273 | 4.5621 | 4.5183 | 4.5295 | 4.5797 | 4.626 | 4.6507 | 4.5909 | 4.5877 | 4.4902 | 4.5927 | 4.7233 | 4.7032 | 4.7069 | 4.822 | 4.8003 | 4.7621 | 4.6779 | 4.6992 | 4.7295 | 4.6026 | 4.5519 | 4.5749 | 4.4972 | 4.5864 | 4.5692 | 4.3654 | 4.3786 | 4.3505 | 4.5795 | 4.504 | 4.5931 | 4.9817 | 4.8872 | 4.8868 | 4.9213 | 4.999 | 4.9069 | 4.8703 | 4.962 | 5.0252 | 4.8954 | 4.8788 | 4.8944 | 4.9426 | 4.8709 | 4.9179 | 4.9703 | 4.9365 | 4.9086 | 4.9907 | 5.019 | 5.0076 | 5.0521 | 4.982 | 4.9975 | 4.9449 | 4.9369 | 4.9034 | 4.9217 | 4.8872 | 4.9779 | 4.9745 | 4.9921 | 5.0414 | 5.0127 | 4.9921 | 4.9862 | 4.9773 | 4.9527 | 5.0069 | 4.8951 | 5.0273 | 5.2388 | 5.0452 | 5.0652 | 5.0238 | 4.9807 | 5.087 | 5.048 | 5.1215 | 5.0363 | 4.9737 | 4.9479 | 5.0362 | 5.0141 | 5.0145 | 5.0338 | 4.9893 | 4.971 | 5.0072 | 4.9618 | 5.0065 | 5.0283 | 4.989 | 4.9096 | 4.9838 | 4.9555 | 4.9541 | 4.9462 | 4.1249 | 4.9876 | 5.0638 | 4.9386 | 4.9651 | 4.846 | 5.0645 | 4.9832 | 4.9489 | 4.9231 | 5.0193 | 5.0373 | 4.9896 | 4.9741 | 5.0104 | 5.0455 | 5.0498 | 5.0486 | 4.9293 | 4.9841 | 5.0393 | 5.1565 | 5.2264 | 5.3827 | 5.5749 | 0 | 5.6001 | 5.5507 | 4.9727 | 4.9817 | 4.9869 | 4.9051 | 5.0519 | 5.1325 | 4.9567 | 4.8934 | 4.9751 | 4.9354 | 4.9312 | 4.9392 | 4.9358 | 4.9641 | 5.0317 | 5.0469 | 4.9785 | 4.983 | 4.9785 | 5.0113 | 4.9238 | 4.9938 | 4.895 | 5.0026 | 5.0128 | 5.0306 | 5.0253 | 4.9887 | 5.0378 | 4.9615 | 5.048 | 4.9206 | 5.0363 | 4.9244 | 4.972 | 4.9972 | 4.9663 | 5.0139 | 4.869 | 4.991 | 4.9498 | 4.9464 | 4.9614 | 5.0272 | 4.9621 | 5.0352 | 5.0477 | 4.8498 | 4.9354 | 4.9918 | 4.9297 | 4.9041 | 4.9616 | 4.9523 | 4.9572 | 4.9996 | 5.0365 | 5.0091 | 4.9616 | 4.7583 | 4.8052 | 4.8758 | 4.8314 | 4.746 | 4.7157 | 4.8658 | 4.8114 | 4.8865 | 4.9497 | 4.9482 | 4.9725 | 4.9349 | 4.9036 | 4.9953 | 4.8867 | 4.9894 | 4.938 | 4.9384 | 4.925 | 4.8632 | 4.8621 | 4.8423 | 4.8796 | 5.0071 | 5.0078 | 4.8481 | 4.9383 | 4.925 | 4.8251 | 4.9765 | 4.8621 | 4.9077 | 4.8864 | 4.8867 | 4.9406 | 4.9002 | 4.9047 | 4.9436 | 4.8976 | 4.8563 | 4.7382 | 4.9467 | 5.0014 | 5.0216 | 4.9779 | 4.9889 | 5.0289 | 4.9962 | 4.9389 | 4.9961 | 5.0204 | 4.8494 | 4.766 | 4.8874 | 4.9009 | 4.9904 | 4.9272 | 4.9782 | 5.0178 | 4.813 | 4.8859 | 4.8371 | 4.8432 | 4.8587 | 4.7184 | 4.7948 | 4.8624 | 4.7729 | 4.7547 | 4.9588 | 4.9048 | 4.9267 | 4.9218 | 4.9369 | 4.8401 | 4.8452 | 4.8588 | 4.9186 | 4.8627 | 4.8885 | 4.8862 | 4.936 | 4.8457 | 4.832 | 4.9105 | 4.8608 | 4.9258 | 4.9044 | 4.9803 | 4.971 | 4.8913 | 4.8481 | 4.8024 | 4.9163 | 4.8583 | 4.8408 | 4.8292 | 4.8639 | 4.7583 | 4.7754 | 4.7734 | 4.8081 | 4.8246 | 4.8886 | 4.7828 | 4.7862 | 4.7735 | 4.7784 | 4.7671 | 4.8792 | 4.77 | 4.8701 | 4.8344 | 4.9305 | 4.9372 | 4.8779 | 4.8333 | 4.9181 | 4.9163 | 4.8737 | 4.8815 | 4.9062 | 4.8374 | 4.9103 | 4.9372 | 4.8591 | 4.929 | 4.9333 | 4.9185 | 4.8368 | 4.8999 | 4.9553 | 4.924 | 4.8389 | 4.8378 | 4.9788 | 4.8537 | 4.9574 | 4.9058 | 4.8332 | 4.9185 | 4.8348 | 4.8544 | 4.9389 | 4.9031 | 4.9596 | 4.9513 | 4.8847
2025-05-01 | 1.5391 | 1.4888 | 1.5538 | 1.5523 | 1.5424 | 1.4814 | 1.5953 | 1.5114 | 1.5712 | 1.5758 | 1.5689 | 1.5606 | 1.5735 | 1.5742 | 1.5909 | 1.5803 | 1.5574 | 1.5877 | 1.5826 | 1.5939 | 1.6485 | 1.6326 | 1.6485 | 1.6341 | 1.6432 | 1.6205 | 1.6553 | 1.6455 | 1.6629 | 1.6614 | 1.6364 | 1.6386 | 1.5568 | 1.5303 | 1.5359 | 1.5566 | 1.5734 | 1.5678 | 1.5523 | 1.567 | 1.5174 | 1.5792 | 1.6193 | 1.598 | 1.6177 | 1.657 | 1.6555 | 1.6465 | 1.6027 | 1.6329 | 1.6378 | 1.591 | 1.5628 | 1.5811 | 1.5566 | 1.5885 | 1.5914 | 1.5203 | 1.52 | 1.5118 | 1.5606 | 1.5605 | 1.5645 | 1.7143 | 1.6787 | 1.6895 | 1.6925 | 1.7236 | 1.69 | 1.6749 | 1.7077 | 1.7305 | 1.6777 | 1.6842 | 1.6753 | 1.6937 | 1.6667 | 1.6936 | 1.7139 | 1.7098 | 1.6901 | 1.7196 | 1.7271 | 1.7219 | 1.7447 | 1.7341 | 1.7208 | 1.7087 | 1.7101 | 1.6863 | 1.6922 | 1.6708 | 1.697 | 1.7043 | 1.7136 | 1.7378 | 1.7302 | 1.7302 | 1.7157 | 1.6977 | 1.6955 | 1.7188 | 1.679 | 1.7319 | 1.7447 | 1.7315 | 1.7447 | 1.725 | 1.705 | 1.756 | 1.7402 | 1.7609 | 1.7317 | 1.7157 | 1.7019 | 1.7474 | 1.7302 | 1.7291 | 1.7409 | 1.7177 | 1.7153 | 1.7271 | 1.7042 | 1.7193 | 1.7402 | 1.7264 | 1.6905 | 1.7246 | 1.6263 | 1.6977 | 1.6929 | 1.4248 | 1.7184 | 1.7426 | 1.6984 | 1.707 | 1.6757 | 1.7529 | 1.7317 | 1.6988 | 1.6988 | 1.7312 | 1.735 | 1.7215 | 1.7081 | 1.7409 | 1.7329 | 1.7269 | 1.7259 | 1.6804 | 1.7012 | 1.7371 | 1.7714 | 1.8765 | 1.882 | 1.9265 | 0 | 1.9479 | 1.9617 | 1.6936 | 1.7001 | 1.6984 | 1.6784 | 1.7566 | 1.7798 | 1.6937 | 1.6784 | 1.7188 | 1.6969 | 1.6984 | 1.7086 | 1.7014 | 1.7094 | 1.7351 | 1.7449 | 1.7207 | 1.7158 | 1.7226 | 1.7445 | 1.6944 | 1.7284 | 1.6999 | 1.7354 | 1.7336 | 1.7381 | 1.7336 | 1.7237 | 1.7366 | 1.7132 | 1.7328 | 1.6905 | 1.7332 | 1.6897 | 1.7094 | 1.7175 | 1.702 | 1.7385 | 1.6589 | 1.7073 | 1.6982 | 1.6947 | 1.6968 | 1.7177 | 1.7062 | 1.732 | 1.7419 | 1.7453 | 1.7022 | 1.6698 | 1.6954 | 1.6862 | 1.7184 | 1.6971 | 1.6994 | 1.7037 | 1.7214 | 1.7145 | 1.6832 | 1.6572 | 1.626 | 1.6668 | 1.6394 | 1.6279 | 1.6237 | 1.656 | 1.6308 | 1.6698 | 1.7072 | 1.7017 | 1.6849 | 1.6224 | 1.6723 | 1.5585 | 1.6166 | 1.7202 | 1.6966 | 1.6982 | 1.3984 | 1.0286 | 1.6667 | 1.0215 | 1.682 | 1.7527 | 1.7622 | 1.6586 | 1.6846 | 1.6951 | 1.6431 | 1.7425 | 1.6622 | 1.6969 | 1.6775 | 1.266 | 1.5785 | 1.4947 | 1.6786 | 1.6764 | 1.6655 | 1.6485 | 1.6569 | 1.6828 | 1.7123 | 1.7236 | 1.6611 | 1.7048 | 1.7133 | 1.7053 | 1.6879 | 1.7072 | 1.723 | 1.6666 | 1.6289 | 1.695 | 1.6827 | 1.7016 | 1.6797 | 1.7033 | 1.7182 | 1.7012 | 1.6757 | 1.655 | 1.6515 | 1.6648 | 1.6243 | 1.6504 | 1.6595 | 1.6376 | 1.6319 | 1.7011 | 1.6774 | 1.6859 | 1.6841 | 1.7004 | 1.6722 | 1.6567 | 1.6617 | 1.6876 | 1.6739 | 1.6807 | 1.6841 | 1.6788 | 1.6621 | 1.6598 | 1.6689 | 1.6743 | 1.6868 | 1.6807 | 1.7196 | 1.7016 | 1.677 | 1.1935 | 1.3729 | 1.7052 | 1.6663 | 1.6652 | 1.6599 | 1.6829 | 1.643 | 1.2065 | 1.6191 | 1.6421 | 1.6664 | 1.7164 | 1.5572 | 1.6854 | 1.673 | 1.6113 | 0.98527 | 1.711 | 1.6766 | 1.6401 | 0.76413 | 1.6578 | 1.7582 | 1.0604 | 1.6416 | 1.6689 | 1.6723 | 1.6551 | 1.6547 | 1.6674 | 1.6371 | 1.667 | 1.6857 | 1.6439 | 1.6786 | 1.6837 | 1.6756 | 1.6335 | 1.6601 | 1.6919 | 1.669 | 1.6327 | 1.6356 | 1.6766 | 1.6455 | 1.6753 | 1.6619 | 1.6389 | 1.6569 | 1.6413 | 1.6825 | 1.6711 | 1.6774 | 1.6982 | 1.6805 | 1.6606
2025-05-02 | 4.0191 | 3.9171 | 4.0553 | 4.0591 | 4.0159 | 3.9096 | 4.1507 | 3.9371 | 4.0712 | 4.0795 | 4.0977 | 4.0773 | 4.0712 | 4.0765 | 4.1144 | 4.1015 | 4.0502 | 4.0702 | 4.0424 | 4.0962 | 4.1992 | 4.1553 | 4.2023 | 4.1667 | 4.1538 | 4.1242 | 4.1803 | 4.1242 | 4.1917 | 4.1962 | 4.1462 | 4.1689 | 3.9894 | 3.9506 | 3.9777 | 4.0144 | 4.0686 | 4.0949 | 4.0152 | 4.0439 | 3.9553 | 4.0128 | 4.0687 | 4.1199 | 4.1192 | 4.1939 | 4.0777 | 4.0591 | 3.8802 | 4.0921 | 4.1298 | 4.0283 | 3.9863 | 3.9876 | 3.9406 | 3.9209 | 3.9832 | 3.8471 | 3.8578 | 3.8234 | 4.05 | 3.9729 | 4.0037 | 4.1957 | 4.1587 | 4.3043 | 4.2308 | 4.1805 | 4.2692 | 4.1049 | 4.3009 | 4.1791 | 4.127 | 4.0852 | 4.1194 | 4.2511 | 4.2226 | 4.0759 | 4.0687 | 4.3371 | 4.0959 | 4.1346 | 4.313 | 4.2157 | 4.1518 | 4.2763 | 4.1616 | 4.1009 | 4.0959 | 4.2077 | 4.1919 | 4.0807 | 4.1391 | 4.2626 | 4.2888 | 4.1536 | 4.0775 | 4.3275 | 4.1601 | 4.1883 | 4.2201 | 4.1818 | 4.2156 | 4.1618 | 4.4262 | 4.1643 | 4.2781 | 4.1536 | 4.1732 | 4.285 | 4.2667 | 4.255 | 4.3621 | 4.0758 | 4.1636 | 4.1622 | 4.0311 | 4.2253 | 4.2098 | 4.3126 | 4.2346 | 4.2298 | 4.2125 | 4.2825 | 4.4144 | 4.3875 | 4.3157 | 4.3868 | 4.0977 | 4.1815 | 4.1663 | 3.6263 | 4.1315 | 4.2605 | 4.1605 | 4.1725 | 4.2475 | 4.2443 | 4.1044 | 4.1925 | 4.2916 | 4.1843 | 4.2029 | 4.4048 | 4.2015 | 4.196 | 4.2032 | 4.4012 | 4.2672 | 4.2716 | 4.3214 | 4.1846 | 4.3537 | 4.3264 | 4.3792 | 4.5431 | 0 | 4.4627 | 4.5017 | 4.1977 | 4.1784 | 4.2164 | 4.3106 | 4.1376 | 4.2398 | 4.1721 | 4.181 | 4.22 | 4.1852 | 4.1825 | 4.1557 | 4.1856 | 4.2041 | 4.2373 | 4.2475 | 4.2147 | 4.215 | 4.2203 | 4.24 | 4.269 | 4.4215 | 4.0761 | 4.2309 | 4.2245 | 4.2464 | 4.2328 | 4.2082 | 4.2279 | 4.1931 | 4.2332 | 4.1655 | 4.2256 | 4.1553 | 4.1814 | 4.2738 | 4.254 | 4.2738 | 4.1308 | 4.3479 | 4.4329 | 4.1822 | 4.1536 | 4.3959 | 4.1542 | 4.0601 | 4.405 | 4.2659 | 4.1744 | 4.2222 | 4.4102 | 4.2472 | 4.2584 | 4.1863 | 4.31 | 4.4093 | 4.1345 | 4.4762 | 4.4327 | 4.0195 | 4.0301 | 4.1333 | 4.1132 | 4.0533 | 4.1575 | 4.047 | 4.0259 | 4.0299 | 4.0649 | 4.2084 | 4.1641 | 4.1625 | 4.0783 | 4.2229 | 4.0947 | 4.2575 | 4.2104 | 4.208 | 4.1994 | 4.1112 | 4.0955 | 4.1022 | 4.1112 | 4.2586 | 4.2425 | 4.157 | 4.1171 | 4.2111 | 4.0925 | 1.0557 | 1.0402 | 4.1201 | 4.1044 | 4.1605 | 4.3044 | 4.1213 | 4.1257 | 4.1448 | 4.1954 | 3.9975 | 4.182 | 4.1624 | 4.0112 | 4.132 | 4.1446 | 4.1765 | 4.2647 | 4.3007 | 4.1472 | 4.2515 | 4.1377 | 4.0134 | 4.1522 | 4.0153 | 4.1758 | 4.3686 | 4.3097 | 4.1212 | 4.3873 | 4.2229 | 4.0711 | 4.0624 | 4.0639 | 4.0624 | 4.0034 | 3.9921 | 4.0797 | 4.011 | 4.0106 | 4.1187 | 4.0131 | 4.1111 | 4.1119 | 4.1782 | 4.1194 | 4.123 | 4.0845 | 4.1233 | 4.0823 | 4.0887 | 4.1031 | 4.0187 | 4.0929 | 4.0694 | 4.1217 | 4.0906 | 4.2524 | 4.1179 | 4.1085 | 4.2266 | 4.1817 | 4.1193 | 4.0267 | 4.1365 | 4.02 | 4.0155 | 4.0327 | 4.1032 | 4.0771 | 4.0226 | 3.9989 | 4.0471 | 4.0491 | 4.0278 | 3.9882 | 3.9841 | 3.9732 | 3.9729 | 4.005 | 3.9915 | 4.0196 | 4.093 | 4.1495 | 4.1515 | 4.1562 | 4.1538 | 3.9957 | 4.0652 | 4.0386 | 4.0573 | 4.0293 | 4.0697 | 4.0334 | 4.0629 | 4.0839 | 4.0517 | 4.1381 | 4.1562 | 4.0764 | 4.1358 | 4.1115 | 4.146 | 4.0224 | 4.0132 | 4.014 | 4.1327 | 3.9967 | 4.06 | 3.9828 | 4.0542 | 4.0484 | 4.0608 | 4.0836 | 4.1952 | 4.0973 | 4.1378 | 4.1472 | 4.1308
2025-05-03 | 4.6244 | 4.5199 | 4.6818 | 4.6977 | 4.6508 | 4.5171 | 4.8179 | 4.5636 | 4.7167 | 4.7492 | 4.7727 | 4.747 | 4.7705 | 4.7705 | 4.8227 | 4.8356 | 4.7376 | 4.7576 | 4.7098 | 4.778 | 4.9371 | 4.8682 | 4.9394 | 4.9068 | 4.878 | 4.8583 | 4.9212 | 4.8992 | 4.9477 | 4.9447 | 4.8902 | 4.922 | 4.7045 | 4.6356 | 4.6659 | 4.7145 | 4.799 | 4.8285 | 4.7485 | 4.7799 | 4.6955 | 4.7832 | 4.871 | 4.894 | 4.9013 | 1.7214 | 4.9276 | 4.8972 | 4.684 | 4.9002 | 4.9267 | 4.8107 | 4.759 | 4.7626 | 4.6961 | 4.6487 | 4.7285 | 4.5442 | 4.5407 | 4.5452 | 4.8129 | 4.7038 | 4.7735 | 5.0311 | 4.9455 | 5.0505 | 5.0255 | 4.9434 | 5.0009 | 4.8737 | 5.0876 | 4.9403 | 4.8647 | 4.7828 | 4.843 | 4.9636 | 4.9181 | 4.9769 | 5.0725 | 5.1957 | 4.9055 | 4.9871 | 5.2215 | 5.0942 | 4.9748 | 5.1631 | 5.1335 | 4.9062 | 5.1211 | 5.0604 | 5.0141 | 4.7974 | 4.8402 | 4.9393 | 5.0197 | 4.8896 | 4.8013 | 5.0411 | 4.9438 | 4.9462 | 4.9654 | 4.991 | 4.9981 | 4.9044 | 5.2484 | 4.8937 | 5.0573 | 4.8951 | 4.9161 | 5.0645 | 5.0725 | 5.0386 | 5.1803 | 4.8716 | 4.9289 | 4.979 | 4.9807 | 5.1073 | 5.293 | 5.2384 | 5.0928 | 4.9896 | 5.0869 | 5.18 | 5.2681 | 5.2388 | 5.1674 | 5.2484 | 5.1104 | 5.078 | 5.0362 | 4.3126 | 4.9686 | 5.1304 | 5.0262 | 4.9262 | 5.0844 | 4.9803 | 4.7813 | 4.9562 | 5.0928 | 4.9317 | 5.001 | 5.1912 | 5.0376 | 5.1235 | 4.9055 | 5.2644 | 5.1429 | 5.119 | 5.2036 | 5.0138 | 5.237 | 5.0445 | 5.1587 | 5.3306 | 0 | 5.3547 | 5.2498 | 5.0635 | 5.0169 | 4.9648 | 5.1311 | 4.9173 | 5.0345 | 5.1378 | 4.9921 | 5.048 | 5.0159 | 5.0147 | 4.9667 | 5.0287 | 5.0556 | 5.0911 | 5.1202 | 5.0767 | 5.0393 | 5.0695 | 5.1202 | 5.1119 | 5.2213 | 4.9329 | 5.1081 | 5.1119 | 5.1345 | 5.1236 | 5.1043 | 5.1368 | 5.0741 | 5.1327 | 5.0336 | 5.1228 | 5.0567 | 5.1047 | 5.1782 | 5.1579 | 5.181 | 4.8908 | 5.1475 | 5.1699 | 4.9334 | 4.9587 | 5.1401 | 4.9052 | 4.9669 | 5.151 | 4.8734 | 4.8719 | 4.9468 | 5.0901 | 4.956 | 4.9509 | 4.9205 | 5.2041 | 5.1935 | 5.1098 | 5.2156 | 5.1334 | 4.807 | 4.7802 | 4.8548 | 4.8026 | 4.8 | 4.8042 | 4.7971 | 4.7514 | 4.8937 | 4.9001 | 5.1291 | 4.9058 | 5.0879 | 5.0082 | 5.1786 | 5.0254 | 5.1609 | 5.1075 | 5.1338 | 5.1173 | 4.9712 | 5.0101 | 4.9376 | 5.0067 | 5.1197 | 5.1374 | 4.956 | 4.9282 | 5.0471 | 4.9028 | 1.0871 | 1.0705 | 5.0288 | 4.9806 | 4.9682 | 5.1088 | 4.9753 | 5.0105 | 5.0078 | 5.1199 | 4.886 | 5.0444 | 5.079 | 4.9119 | 5.0016 | 4.875 | 4.9903 | 5.188 | 5.229 | 5.043 | 5.1484 | 4.9662 | 4.8566 | 5.0384 | 4.7951 | 5.0343 | 5.2036 | 5.1443 | 4.9502 | 5.2437 | 5.1092 | 5.0865 | 5.0998 | 5.1172 | 5.0881 | 4.9796 | 4.9577 | 5.1172 | 5.0042 | 5.0431 | 5.1527 | 4.9752 | 5.1731 | 5.1576 | 5.1508 | 5.1409 | 5.1813 | 5.1298 | 5.1735 | 5.1126 | 5.0994 | 5.1323 | 4.9844 | 5.1047 | 5.1164 | 5.1214 | 5.1088 | 5.3019 | 5.1627 | 5.0949 | 5.275 | 5.1917 | 5.1586 | 4.841 | 5.2143 | 5.0677 | 5.0602 | 5.0355 | 5.1353 | 5.0207 | 4.886 | 4.9397 | 5.0742 | 5.0534 | 5.0807 | 4.9918 | 4.9742 | 5.0191 | 4.9914 | 4.9544 | 5.0091 | 5.0663 | 5.1193 | 5.0863 | 5.2033 | 5.1177 | 5.0942 | 5.0695 | 5.1633 | 5.117 | 5.1349 | 5.0766 | 5.1383 | 5.071 | 4.9495 | 5.1364 | 5.0893 | 5.1805 | 5.1727 | 5.1237 | 5.1264 | 5.1334 | 5.1994 | 4.9907 | 5.0953 | 5.0848 | 5.2123 | 4.9854 | 5.1035 | 5.0071 | 5.084 | 5.0897 | 5.0875 | 5.0973 | 5.2 | 5.1279 | 5.1994 | 5.2037 | 4.9714
2025-05-04 | 4.5008 | 4.4011 | 4.5515 | 4.5606 | 4.5197 | 4.3903 | 4.6702 | 4.4167 | 4.5583 | 4.5894 | 4.5977 | 4.5712 | 4.5879 | 4.572 | 4.6136 | 4.5917 | 4.5574 | 4.5574 | 4.5273 | 4.5856 | 4.7197 | 4.6553 | 4.7038 | 4.6583 | 4.6606 | 4.6409 | 4.6795 | 4.6492 | 4.7045 | 4.7015 | 4.6386 | 4.6644 | 4.5038 | 4.4609 | 4.4968 | 4.5191 | 4.5805 | 4.5734 | 4.5205 | 4.5303 | 4.4492 | 4.5556 | 4.6685 | 4.6557 | 4.625 | 4.7366 | 4.6997 | 4.6317 | 4.5226 | 4.5855 | 4.6012 | 4.4743 | 4.4177 | 4.4341 | 4.3874 | 4.45 | 4.4812 | 4.298 | 4.2987 | 4.2809 | 4.5136 | 4.4124 | 4.4545 | 4.9044 | 4.8375 | 4.8699 | 4.9262 | 4.9355 | 4.9027 | 4.7933 | 4.94 | 4.9289 | 4.833 | 4.7672 | 4.8237 | 4.8957 | 4.8366 | 4.8237 | 4.8592 | 4.8723 | 4.7833 | 4.8366 | 4.9275 | 4.9123 | 4.8858 | 4.9495 | 4.8885 | 4.8184 | 4.9082 | 4.8585 | 4.8751 | 4.7954 | 4.9182 | 4.9417 | 5.0024 | 4.9396 | 4.8644 | 4.9117 | 4.9127 | 4.9794 | 4.9196 | 4.952 | 4.8462 | 4.9444 | 5.088 | 4.9462 | 5.0535 | 4.9179 | 4.9607 | 5.0628 | 5.0248 | 5.0459 | 4.907 | 4.8258 | 4.8399 | 4.8582 | 4.7267 | 4.9023 | 4.7902 | 4.9203 | 4.8589 | 4.7629 | 4.8319 | 4.8947 | 4.892 | 4.8613 | 4.7878 | 4.8703 | 4.8337 | 4.7981 | 4.7788 | 4.0148 | 4.7792 | 4.8875 | 4.7705 | 4.7916 | 4.6075 | 4.9124 | 4.767 | 4.824 | 4.8482 | 4.8444 | 4.8751 | 4.8954 | 4.852 | 4.9293 | 4.7805 | 4.9405 | 4.9097 | 4.8164 | 4.881 | 4.8703 | 4.9913 | 4.6273 | 4.8268 | 4.7298 | 4.5583 | 4.8575 | 4.7136 | 4.8171 | 4.8078 | 4.7019 | 4.793 | 4.792 | 4.8844 | 4.8366 | 4.811 | 4.8673 | 4.8228 | 4.7986 | 4.7642 | 4.8212 | 4.8492 | 4.904 | 4.9153 | 4.8469 | 4.8469 | 4.85 | 4.8893 | 4.8183 | 4.8862 | 4.7291 | 4.8757 | 4.8673 | 4.904 | 4.8991 | 4.8503 | 4.8912 | 4.8235 | 4.8987 | 4.7838 | 4.8987 | 4.7842 | 4.8345 | 4.8611 | 4.8385 | 4.8595 | 4.7434 | 4.9115 | 4.876 | 4.8125 | 4.8341 | 4.9343 | 4.7953 | 4.8741 | 4.9695 | 4.9048 | 4.7834 | 4.9158 | 4.8796 | 4.8123 | 4.7069 | 4.8126 | 4.8344 | 4.9411 | 4.911 | 4.9252 | 4.8613 | 4.7099 | 4.5982 | 4.8137 | 4.7029 | 4.619 | 4.632 | 4.6772 | 4.6106 | 4.7167 | 4.7171 | 4.7818 | 4.7363 | 4.7535 | 4.6995 | 4.8328 | 4.7062 | 4.8497 | 4.7559 | 4.759 | 4.7794 | 4.7511 | 4.704 | 4.723 | 4.7294 | 4.8497 | 4.7135 | 4.6876 | 4.7264 | 4.6566 | 4.6027 | 2.9686 | 2.9827 | 4.7313 | 4.7107 | 4.7791 | 4.8161 | 4.7473 | 4.7589 | 4.7817 | 4.6771 | 4.566 | 4.6215 | 4.793 | 4.8064 | 4.7779 | 4.7648 | 4.8244 | 4.8798 | 4.8608 | 4.7751 | 4.8398 | 4.7617 | 4.6163 | 4.6554 | 4.6275 | 4.7783 | 4.8465 | 4.7837 | 4.7587 | 4.8699 | 4.7966 | 4.7003 | 4.6935 | 4.6927 | 4.6935 | 4.5397 | 4.5892 | 4.7139 | 4.5945 | 4.5858 | 4.7577 | 4.6749 | 4.7566 | 4.7736 | 4.7623 | 4.6508 | 4.6734 | 4.7036 | 4.7542 | 4.7099 | 4.7126 | 4.7459 | 4.6694 | 4.7084 | 4.675 | 4.7668 | 4.7069 | 4.7673 | 4.7455 | 4.7559 | 4.8103 | 4.7389 | 4.7575 | 4.5772 | 4.7536 | 4.6647 | 4.6715 | 4.6558 | 4.6865 | 4.5679 | 4.6393 | 4.6107 | 4.6228 | 4.6107 | 4.6759 | 4.6229 | 4.5597 | 4.6184 | 4.6131 | 4.6382 | 4.7002 | 4.5997 | 4.6778 | 4.7759 | 4.7747 | 4.7841 | 4.7869 | 4.5941 | 4.7148 | 4.667 | 4.7126 | 4.6569 | 4.7227 | 4.683 | 4.5085 | 4.76 | 4.7047 | 4.7284 | 4.7567 | 4.7432 | 4.6707 | 4.7013 | 4.7598 | 4.6425 | 4.6576 | 4.6688 | 4.7374 | 4.6589 | 4.7137 | 4.69 | 4.6366 | 4.7103 | 4.9215 | 4.6554 | 4.7501 | 4.7398 | 4.7582 | 4.7708 | 4.7351
2025-05-05 | 3.7408 | 3.685 | 3.8015 | 3.8129 | 3.7826 | 3.6614 | 3.8914 | 3.6977 | 3.8212 | 3.8447 | 3.8311 | 3.8189 | 3.847 | 3.8424 | 3.8773 | 3.8689 | 3.815 | 3.8349 | 3.7894 | 3.8462 | 3.9447 | 3.9061 | 3.9492 | 3.9409 | 3.8992 | 3.872 | 3.9394 | 3.9235 | 3.9455 | 3.9523 | 3.8985 | 3.9318 | 3.7947 | 3.7536 | 3.7719 | 3.8038 | 3.8541 | 3.8565 | 3.8061 | 3.8222 | 3.7485 | 3.8345 | 3.9182 | 3.9042 | 3.913 | 3.9949 | 3.9538 | 3.922 | 3.7781 | 3.8974 | 3.9282 | 3.826 | 3.7799 | 3.7785 | 3.7307 | 3.7649 | 3.7977 | 3.6522 | 3.6478 | 3.63 | 3.8053 | 3.7476 | 3.8057 | 4.0455 | 3.981 | 4.0464 | 4.0597 | 4.0321 | 4.0653 | 3.9496 | 4.0997 | 4.0359 | 3.9693 | 3.9322 | 3.9703 | 4.0703 | 3.9387 | 3.931 | 4.0531 | 4.098 | 3.9624 | 4.0198 | 4.1411 | 4.0754 | 4.0383 | 4.1162 | 4.031 | 3.9865 | 4.087 | 4.0386 | 4.0235 | 3.8803 | 3.9741 | 4.0255 | 4.0714 | 3.991 | 3.9337 | 4.0024 | 3.9952 | 4.0162 | 4.0159 | 4.0421 | 3.9972 | 4.0138 | 4.2412 | 4.0166 | 4.119 | 4.0121 | 4.0173 | 4.1301 | 4.1166 | 4.0324 | 4.0971 | 3.9766 | 3.9489 | 3.941 | 3.9527 | 4.0773 | 3.8647 | 4.1339 | 4.0652 | 3.9576 | 4.0667 | 4.1201 | 4.1718 | 4.146 | 4.0773 | 4.1491 | 3.8482 | 4.0587 | 4.0373 | 3.4268 | 4.0304 | 4.1398 | 4.0431 | 3.9979 | 3.9773 | 4.1059 | 3.9965 | 4.0497 | 4.0894 | 4.06 | 4.1056 | 4.0645 | 4.0901 | 4.1636 | 3.9986 | 4.202 | 4.1442 | 4.0931 | 4.156 | 4.107 | 4.2415 | 3.8613 | 4.0752 | 4.0852 | 3.8213 | 3.9714 | 3.9444 | 3.9406 | 4.0569 | 4.0797 | 4.0697 | 4.0625 | 4.1501 | 4.1061 | 4.0465 | 4.0967 | 4.0601 | 4.0529 | 4.0265 | 4.0601 | 4.0782 | 4.1145 | 4.1262 | 4.0877 | 4.0979 | 4.0899 | 4.1243 | 4.1024 | 4.1759 | 3.9654 | 4.1096 | 4.1024 | 4.1266 | 4.1255 | 4.0971 | 4.1289 | 4.0574 | 4.119 | 4.0144 | 4.1149 | 4.0435 | 4.0903 | 4.1282 | 4.1048 | 4.154 | 3.9629 | 4.1444 | 4.1252 | 4.0292 | 4.0635 | 4.1945 | 4.0146 | 4.082 | 4.2082 | 4.0533 | 4.0303 | 4.1476 | 4.0712 | 4.0557 | 3.9248 | 4.0408 | 4.1177 | 4.1091 | 4.1642 | 4.1808 | 4.1392 | 3.8919 | 3.8773 | 4.0899 | 3.9446 | 3.8602 | 3.9125 | 3.9234 | 3.8188 | 3.966 | 3.9956 | 4.075 | 4.0738 | 4.0573 | 3.9878 | 4.0942 | 3.983 | 4.1323 | 4.0522 | 4.0498 | 4.0389 | 3.9463 | 3.9822 | 3.9385 | 4.0001 | 4.137 | 4.0345 | 4.0204 | 4.0218 | 4.073 | 3.9897 | 2.5047 | 2.4871 | 3.996 | 3.959 | 3.9807 | 4.088 | 4.0028 | 4.0054 | 4.0069 | 3.9154 | 3.9549 | 3.9137 | 4.0226 | 3.9689 | 4.0195 | 4.0229 | 4.0616 | 4.1216 | 4.1373 | 4.0209 | 4.1063 | 4.0261 | 3.8618 | 3.9749 | 3.9286 | 4.0309 | 4.134 | 4.0747 | 4.0018 | 4.156 | 4.0713 | 3.9558 | 3.9494 | 3.9565 | 3.966 | 3.8912 | 3.898 | 3.969 | 3.9112 | 3.898 | 4.0291 | 3.9058 | 4.0185 | 4.0321 | 4.0611 | 3.9929 | 4.002 | 3.9947 | 4.032 | 3.9939 | 3.992 | 4.0118 | 3.9155 | 3.9829 | 3.9742 | 4.0387 | 4 | 4.0843 | 4.0265 | 4.0329 | 4.1 | 4.0484 | 3.9867 | 3.8629 | 4.0218 | 3.9351 | 3.9389 | 3.9374 | 4.0083 | 3.9313 | 3.9123 | 3.885 | 3.929 | 3.929 | 3.9673 | 3.9123 | 3.8891 | 3.9374 | 3.8981 | 3.8802 | 3.9553 | 3.9505 | 4.0188 | 3.9325 | 4.0777 | 4.0149 | 4.0118 | 3.9168 | 3.9983 | 3.9807 | 3.9904 | 3.8873 | 3.999 | 3.9542 | 3.8895 | 4.0147 | 3.9706 | 4.0357 | 4.0338 | 4.0099 | 3.9957 | 4.0157 | 4.062 | 3.8972 | 3.9527 | 3.9553 | 4.0322 | 3.9154 | 3.9893 | 3.9107 | 3.9509 | 3.9833 | 3.958 | 3.9867 | 4.0585 | 4.0239 | 4.0585 | 4.0624 | 3.9813
2025-05-06 | 2.8756 | 2.8054 | 2.9053 | 2.922 | 2.9 | 2.7882 | 2.9939 | 2.85 | 2.9515 | 2.9629 | 2.9644 | 2.9538 | 2.9553 | 2.9591 | 2.9871 | 2.9606 | 2.945 | 2.9761 | 2.9508 | 2.9917 | 3.0689 | 3.0439 | 3.0674 | 3.0348 | 3.0409 | 3.0189 | 3.0674 | 3.0394 | 3.075 | 3.0856 | 3.0379 | 3.0455 | 2.9136 | 2.8772 | 2.8868 | 2.9219 | 2.9569 | 2.9394 | 2.9152 | 2.9258 | 2.8561 | 2.9429 | 3.025 | 3.0044 | 3.0073 | 3.0839 | 3.0462 | 3.0235 | 2.9395 | 2.9846 | 2.9971 | 2.913 | 2.8766 | 2.8744 | 2.8508 | 2.9139 | 2.9261 | 2.7896 | 2.8107 | 2.7761 | 2.9197 | 2.8758 | 2.8959 | 3.1729 | 3.1208 | 3.1398 | 3.1453 | 3.1867 | 3.1322 | 3.1239 | 3.1912 | 3.2077 | 3.1146 | 3.0969 | 3.0921 | 3.1057 | 3.0689 | 3.1146 | 3.1829 | 3.1822 | 3.1263 | 3.1723 | 3.107 | 3.184 | 3.1939 | 3.2013 | 3.1685 | 3.1395 | 3.166 | 3.1404 | 3.1508 | 3.0849 | 3.1429 | 3.1542 | 3.1649 | 3.1863 | 3.1743 | 3.1922 | 3.1563 | 3.136 | 3.1245 | 3.177 | 3.1132 | 3.1781 | 3.3099 | 3.1808 | 3.2198 | 3.185 | 3.1625 | 3.2412 | 3.2139 | 3.2536 | 3.2218 | 3.1667 | 3.1511 | 3.1953 | 3.0656 | 3.1915 | 3.2212 | 3.1863 | 3.1598 | 3.1746 | 3.1486 | 3.1901 | 3.1874 | 3.1473 | 3.1115 | 3.1439 | 3.0397 | 3.0997 | 3.0756 | 2.5852 | 3.1077 | 3.1563 | 3.088 | 3.0618 | 3.0408 | 3.1974 | 3.1356 | 3.1101 | 3.1284 | 3.1553 | 3.167 | 3.1332 | 3.1315 | 3.1753 | 3.1518 | 3.1548 | 3.1366 | 3.0714 | 3.1075 | 3.1525 | 3.2169 | 3.1108 | 3.128 | 3.1056 | 2.9576 | 3.1363 | 3.1415 | 3.0835 | 3.1021 | 2.9879 | 3.0562 | 3.17 | 3.2077 | 3.0833 | 3.0873 | 3.1323 | 3.0937 | 3.0903 | 3.0945 | 3.0975 | 3.1088 | 3.1523 | 3.1565 | 3.1357 | 3.1413 | 3.1364 | 3.1648 | 3.1115 | 3.1601 | 3.0768 | 3.1542 | 3.1553 | 3.1754 | 3.1474 | 3.144 | 3.1489 | 3.1243 | 3.1561 | 3.0881 | 3.1338 | 3.0446 | 3.0892 | 3.1095 | 3.0782 | 3.1345 | 3.0902 | 3.1967 | 3.1664 | 3.1441 | 3.168 | 3.2324 | 3.1407 | 3.2025 | 3.2565 | 3.2319 | 3.1604 | 3.0666 | 3.1767 | 3.1564 | 3.0817 | 3.1688 | 3.188 | 3.2045 | 3.2329 | 3.2071 | 3.1781 | 3.1015 | 3.075 | 3.1561 | 3.0818 | 3.0251 | 3.0182 | 3.0977 | 3.034 | 3.0837 | 3.1147 | 3.1154 | 3.1268 | 3.1048 | 3.0556 | 3.0938 | 3.0388 | 3.1774 | 3.1154 | 3.0326 | 3.0389 | 2.9723 | 3.0059 | 2.9872 | 2.9992 | 3.1876 | 3.2104 | 3.0565 | 3.0986 | 3.126 | 2.9827 | 3.1036 | 3.0874 | 3.0358 | 3.0437 | 3.0358 | 3.1083 | 3.0351 | 3.0425 | 3.0713 | 3.0495 | 3.0869 | 3.0162 | 3.141 | 3.0961 | 3.1656 | 3.1187 | 3.1432 | 3.1647 | 3.1476 | 3.0998 | 3.1404 | 3.1572 | 3.0565 | 3.0284 | 3.0974 | 3.0979 | 3.131 | 3.0931 | 3.1138 | 3.1575 | 3.1272 | 3.0745 | 3.051 | 3.0522 | 3.0612 | 2.994 | 3.0265 | 3.0624 | 3.0015 | 2.9962 | 3.1051 | 3.0545 | 3.0918 | 3.085 | 3.1103 | 3.071 | 3.0579 | 3.0753 | 3.1088 | 3.083 | 3.0865 | 3.1013 | 3.0737 | 3.0485 | 3.0273 | 3.0686 | 3.0379 | 3.0943 | 3.069 | 3.1187 | 3.1127 | 3.0655 | 3.0341 | 3.0182 | 3.0976 | 3.0508 | 3.0302 | 3.0295 | 3.0651 | 3.0063 | 2.982 | 3.0412 | 3.0365 | 3.0377 | 3.0956 | 3.0175 | 3.0366 | 3.059 | 3.0276 | 3.0317 | 3.1034 | 3.0455 | 3.1429 | 3.0577 | 3.2029 | 3.1436 | 3.1334 | 3.1098 | 3.1438 | 3.1535 | 3.1278 | 3.0351 | 3.1502 | 3.1364 | 3.1307 | 3.1973 | 3.1386 | 3.1915 | 3.2064 | 3.1857 | 3.131 | 3.1766 | 3.2147 | 3.1551 | 3.1337 | 3.1307 | 3.2178 | 3.1308 | 3.182 | 3.1611 | 3.1283 | 3.1588 | 3.1009 | 3.1593 | 3.1901 | 3.1476 | 3.1805 | 3.2025 | 3.0887
2025-05-07 | 3.7337 | 3.6388 | 3.7773 | 3.7758 | 3.7152 | 3.5733 | 3.8806 | 3.6515 | 3.7644 | 3.7947 | 3.825 | 3.7917 | 3.7894 | 3.7932 | 3.8295 | 3.8371 | 3.7807 | 3.8198 | 3.7985 | 3.8409 | 3.9606 | 3.9144 | 3.9523 | 3.928 | 3.922 | 3.903 | 3.9538 | 3.928 | 3.9864 | 3.9811 | 3.925 | 3.9417 | 3.7083 | 3.6611 | 3.7097 | 3.7313 | 3.799 | 3.8094 | 3.7288 | 3.7743 | 3.6932 | 3.7767 | 3.8571 | 3.8392 | 3.856 | 3.9399 | 3.9424 | 3.9039 | 3.846 | 3.896 | 3.893 | 3.789 | 3.7424 | 3.7564 | 3.7224 | 3.8188 | 3.8011 | 3.6417 | 3.6518 | 3.6349 | 3.8114 | 3.7476 | 3.7581 | 4.1387 | 4.0631 | 4.0706 | 4.1084 | 4.1498 | 4.0729 | 4.0424 | 4.1173 | 4.1498 | 4.0449 | 4.0181 | 4.0362 | 4.0682 | 4.0047 | 4.0066 | 4.1636 | 4.1311 | 4.0863 | 4.1591 | 4.0059 | 4.1775 | 4.205 | 4.1822 | 4.1645 | 4.1144 | 4.1139 | 4.1032 | 4.107 | 3.999 | 4.1025 | 4.1118 | 4.1629 | 4.1746 | 4.1489 | 4.1135 | 4.1494 | 4.1295 | 4.0869 | 4.1722 | 4.0631 | 4.1739 | 4.2726 | 4.1387 | 4.2091 | 4.1394 | 4.1339 | 4.2405 | 4.2112 | 4.0794 | 4.192 | 4.1374 | 4.1187 | 4.206 | 4.049 | 4.1922 | 4.1794 | 4.1763 | 4.1235 | 4.146 | 4.1223 | 4.1652 | 4.1511 | 4.1225 | 4.0669 | 4.1384 | 4.1246 | 4.1084 | 4.0901 | 3.8261 | 4.1204 | 4.1763 | 4.0756 | 4.0759 | 3.9928 | 4.1549 | 4.08 | 4.0276 | 4.0162 | 4.0973 | 4.1063 | 4.0725 | 4.0642 | 4.1408 | 4.1294 | 4.1273 | 4.124 | 4.0382 | 4.1075 | 4.1366 | 4.2132 | 4.1039 | 4.1408 | 4.0028 | 3.8958 | 4.1456 | 4.1522 | 4.039 | 4.1014 | 4.1032 | 4.029 | 4.1653 | 4.2164 | 4.0833 | 3.9709 | 4.0367 | 3.994 | 3.9811 | 3.9879 | 3.9947 | 4.0272 | 4.0703 | 4.1062 | 4.0556 | 4.0461 | 4.0491 | 4.0926 | 4.0206 | 4.0904 | 3.9957 | 4.0967 | 4.0918 | 4.1202 | 4.0926 | 4.0627 | 4.1104 | 4.062 | 4.1183 | 4.0219 | 4.1311 | 4.0287 | 4.0616 | 4.0897 | 4.0702 | 4.0718 | 3.9929 | 4.1145 | 4.0565 | 4.0626 | 4.0666 | 4.1081 | 4.0617 | 4.0226 | 4.1366 | 4.1373 | 4.0263 | 4.0527 | 4.0304 | 3.9994 | 3.9822 | 4.0829 | 4.0671 | 4.1279 | 4.1348 | 4.1196 | 4.0594 | 3.9956 | 3.942 | 4.0183 | 3.962 | 3.9119 | 3.9791 | 4.0179 | 3.9502 | 4.0445 | 4.0802 | 4.0938 | 4.0918 | 4.071 | 4.0244 | 4.1232 | 4.0308 | 4.144 | 4.0655 | 4.044 | 4.06 | 3.9209 | 4.0132 | 3.8731 | 4.0087 | 4.1405 | 4.1444 | 3.9827 | 4.0252 | 4.0793 | 3.9329 | 4.0314 | 3.9897 | 4.0357 | 3.9983 | 3.9377 | 4.0289 | 3.9721 | 4.0222 | 4.0289 | 4.1187 | 4.0402 | 3.9772 | 4.1495 | 4.2082 | 4.2105 | 4.0328 | 4.1837 | 4.2172 | 4.1806 | 4.1298 | 4.1715 | 4.1803 | 4.0117 | 4.0083 | 4.1181 | 4.1045 | 4.1283 | 4.0799 | 4.1434 | 4.1676 | 4.1451 | 4.0465 | 4.0367 | 4.0408 | 4.0499 | 3.9444 | 3.9785 | 4.0533 | 3.9762 | 3.9705 | 4.1175 | 4.0866 | 4.1107 | 4.13 | 4.1329 | 4.0218 | 4.0421 | 4.0567 | 4.11 | 4.0637 | 4.0679 | 4.0933 | 4.0412 | 4.0561 | 4.0459 | 4.1149 | 4.0705 | 4.1354 | 4.1081 | 4.1731 | 4.1671 | 4.1071 | 4.0184 | 3.8956 | 4.1063 | 4.0256 | 3.9045 | 4.0226 | 4.069 | 3.9684 | 3.9217 | 4.0006 | 3.9973 | 4.0086 | 4.0536 | 3.9871 | 3.9534 | 4.0129 | 3.9904 | 3.8854 | 4.0842 | 3.9819 | 4.062 | 3.8768 | 4.1354 | 4.0149 | 3.9686 | 4.0196 | 4.1093 | 4.0831 | 4.1044 | 3.9871 | 4.1067 | 4.0719 | 4.1082 | 4.1276 | 4.073 | 4.1005 | 4.104 | 4.1171 | 4.0515 | 4.0859 | 4.1389 | 4.0424 | 4.0708 | 4.0857 | 4.115 | 4.0852 | 4.0652 | 4.0913 | 4.0338 | 4.1059 | 4.0455 | 4.0659 | 4.1304 | 4.1476 | 4.1507 | 4.148 | 4.0302
2025-05-08 | 2.4817 | 2.4258 | 2.5083 | 2.5098 | 2.4735 | 2.3751 | 2.5708 | 2.4174 | 2.5 | 2.5227 | 2.5265 | 2.5076 | 2.5265 | 2.5205 | 2.5447 | 2.5492 | 2.5016 | 2.5423 | 2.5182 | 2.5462 | 2.6212 | 2.6023 | 2.6227 | 2.6121 | 2.5917 | 2.5773 | 2.6318 | 2.6227 | 2.6417 | 2.6485 | 2.6045 | 2.6311 | 2.4894 | 2.4458 | 2.4729 | 2.492 | 2.5375 | 2.5295 | 2.4894 | 2.5239 | 2.478 | 2.5499 | 2.5992 | 2.5877 | 2.5994 | 2.6585 | 2.6542 | 2.6243 | 2.5874 | 2.6057 | 2.5982 | 2.525 | 2.4892 | 2.5052 | 2.4876 | 2.5458 | 2.545 | 2.4432 | 2.4425 | 2.4339 | 2.5258 | 2.5016 | 2.5117 | 2.7243 | 2.685 | 2.6944 | 2.7143 | 2.7557 | 2.6936 | 2.6705 | 2.7277 | 2.7488 | 2.6818 | 2.6604 | 2.6753 | 2.6912 | 2.6598 | 2.6977 | 2.7367 | 2.7243 | 2.6974 | 2.7368 | 2.6246 | 2.7446 | 2.6259 | 2.7543 | 2.7525 | 2.7251 | 2.7229 | 2.7012 | 2.7101 | 2.6542 | 2.7253 | 2.7312 | 2.765 | 2.7754 | 2.7737 | 2.7336 | 2.746 | 2.7316 | 2.7006 | 2.7612 | 2.6843 | 2.774 | 2.8844 | 2.7336 | 2.7881 | 2.7429 | 2.7415 | 2.8109 | 2.7867 | 2.8071 | 2.7664 | 2.7457 | 2.7205 | 2.8033 | 2.7605 | 2.7754 | 2.7464 | 2.7505 | 2.7447 | 2.7595 | 2.7294 | 2.7522 | 2.7667 | 2.7533 | 2.7015 | 2.7609 | 2.7302 | 2.7274 | 2.7129 | 2.5376 | 2.7498 | 2.7823 | 2.7177 | 2.7239 | 2.671 | 2.7964 | 2.7508 | 2.705 | 2.7053 | 2.7495 | 2.7553 | 2.7391 | 2.7308 | 2.7798 | 2.7726 | 2.7583 | 2.752 | 2.6937 | 2.7385 | 2.7771 | 2.8114 | 2.7447 | 2.7647 | 2.7374 | 2.6425 | 2.7533 | 2.7636 | 2.7091 | 2.7233 | 2.7226 | 2.6894 | 2.8029 | 2.7122 | 2.7085 | 2.6761 | 2.7362 | 2.7056 | 2.6833 | 2.7037 | 2.7135 | 2.7309 | 2.7521 | 2.7763 | 2.7366 | 2.723 | 2.7389 | 2.7725 | 2.7048 | 2.746 | 2.6793 | 2.7615 | 2.7528 | 2.7789 | 2.7657 | 2.7445 | 2.777 | 2.7294 | 2.763 | 2.6935 | 2.7717 | 2.7086 | 2.7502 | 2.7484 | 2.7333 | 2.7571 | 2.6316 | 2.7111 | 2.6852 | 2.6833 | 2.6872 | 2.7139 | 2.6995 | 2.7442 | 2.7604 | 2.7667 | 2.6927 | 2.7148 | 2.6919 | 2.6619 | 2.6189 | 2.6825 | 2.6633 | 2.7057 | 2.7131 | 2.7101 | 2.6587 | 2.641 | 2.6134 | 2.6285 | 2.6269 | 2.6188 | 2.6269 | 2.6427 | 2.631 | 2.7052 | 2.7358 | 2.7469 | 2.7225 | 2.7355 | 2.6863 | 2.7716 | 2.7069 | 2.7626 | 2.706 | 2.7233 | 2.748 | 2.668 | 2.6889 | 2.6643 | 2.6972 | 2.7586 | 2.763 | 2.6617 | 2.6538 | 2.7068 | 2.6463 | 2.6817 | 2.6303 | 2.702 | 2.662 | 2.6934 | 2.6856 | 2.6833 | 2.6901 | 2.6972 | 2.693 | 2.6441 | 2.6759 | 2.7156 | 2.7639 | 2.7711 | 2.7288 | 2.737 | 2.7583 | 2.7449 | 2.721 | 2.754 | 2.756 | 2.6863 | 2.6271 | 2.7386 | 2.6946 | 2.7215 | 2.6879 | 2.7418 | 2.7468 | 2.7351 | 2.7063 | 2.6939 | 2.6814 | 2.6961 | 2.6194 | 2.6323 | 2.6969 | 2.6542 | 2.6361 | 2.7358 | 2.7202 | 2.7211 | 2.732 | 2.7437 | 2.677 | 2.6683 | 2.6826 | 2.7173 | 2.6943 | 2.6943 | 2.719 | 2.7148 | 2.6807 | 2.6761 | 2.7266 | 2.6993 | 2.7354 | 2.7137 | 2.7657 | 2.7468 | 2.7119 | 2.7527 | 2.6589 | 2.7683 | 2.7028 | 2.637 | 2.6942 | 2.7155 | 2.6588 | 2.6886 | 2.7126 | 2.6699 | 2.6907 | 2.7469 | 2.7181 | 2.6718 | 2.7211 | 2.6927 | 2.6774 | 2.7605 | 2.6868 | 2.7308 | 2.6122 | 2.8038 | 2.7983 | 2.7527 | 2.6822 | 2.7465 | 2.7312 | 2.6598 | 2.7099 | 2.7458 | 2.7282 | 2.7439 | 2.7648 | 2.7144 | 2.7351 | 2.7473 | 2.7622 | 5.0967 | 2.7316 | 2.7775 | 2.7262 | 2.733 | 2.739 | 2.7449 | 2.7465 | 2.7387 | 2.7612 | 2.7057 | 2.7446 | 2.7119 | 2.7351 | 2.7584 | 2.7924 | 2.7889 | 2.7767 | 2.6945
2025-05-09 | 4.2584 | 4.1316 | 4.2879 | 4.2758 | 4.2212 | 4.101 | 4.3871 | 4.1402 | 4.2902 | 4.297 | 4.3318 | 4.2977 | 4.2758 | 4.2992 | 4.3242 | 4.322 | 4.2807 | 4.3102 | 4.2848 | 4.3348 | 4.4758 | 4.4136 | 4.4462 | 4.4227 | 4.425 | 4.4008 | 4.4356 | 4.4 | 4.4727 | 4.4667 | 4.3992 | 4.4091 | 4.2053 | 4.1722 | 4.2105 | 4.2217 | 4.2831 | 4.2935 | 4.2288 | 4.2576 | 4.1652 | 4.2568 | 4.3641 | 4.3107 | 4.3326 | 4.4211 | 4.4216 | 4.3784 | 4.3221 | 4.3461 | 4.3629 | 4.2524 | 4.197 | 4.2077 | 4.1802 | 4.2666 | 4.2446 | 4.0526 | 4.0735 | 4.0549 | 4.2727 | 4.1982 | 4.2309 | 4.6736 | 4.5949 | 4.5722 | 4.6629 | 4.7419 | 4.6504 | 4.5876 | 4.6767 | 4.7391 | 4.6049 | 4.6051 | 4.5997 | 4.6472 | 4.5776 | 4.5283 | 4.5939 | 4.5801 | 4.5535 | 4.6009 | 4.5839 | 4.6501 | 4.6529 | 4.6544 | 4.6317 | 4.5737 | 4.5918 | 4.422 | 4.5928 | 4.7022 | 4.7778 | 4.7871 | 4.784 | 4.8071 | 4.7619 | 4.7553 | 4.734 | 4.7446 | 4.7092 | 4.7112 | 4.5963 | 4.7553 | 4.9696 | 4.7733 | 4.8123 | 4.7547 | 4.7374 | 4.8306 | 4.7726 | 4.8251 | 4.7252 | 4.6519 | 4.6232 | 4.6822 | 4.6584 | 4.6739 | 4.6442 | 4.628 | 4.627 | 4.6598 | 4.6115 | 4.6501 | 4.6643 | 4.6228 | 4.5604 | 4.6453 | 4.6049 | 4.608 | 4.5973 | 4.2312 | 4.6311 | 4.7063 | 4.6018 | 4.6115 | 4.4791 | 4.6863 | 4.5898 | 4.5883 | 4.5618 | 4.6335 | 4.6629 | 4.6239 | 4.6059 | 4.6888 | 4.6653 | 4.6869 | 4.6624 | 4.4798 | 4.7063 | 4.6549 | 4.7415 | 4.5983 | 4.637 | 4.6287 | 4.4565 | 4.5797 | 4.5587 | 4.6322 | 4.6294 | 4.6429 | 4.5552 | 4.6498 | 4.7126 | 4.4838 | 4.616 | 4.6066 | 4.6591 | 4.6489 | 4.6429 | 4.6527 | 4.6655 | 4.712 | 4.7271 | 4.6924 | 4.6893 | 4.6897 | 4.7324 | 4.6476 | 4.7152 | 4.6079 | 4.7207 | 4.7075 | 4.7286 | 4.7041 | 4.6735 | 4.7128 | 4.667 | 4.7207 | 4.6217 | 4.7196 | 4.6145 | 4.6678 | 4.6837 | 4.6627 | 4.7052 | 4.5325 | 4.6558 | 4.5997 | 4.6041 | 4.6167 | 4.6857 | 4.6062 | 4.6768 | 4.7027 | 4.6929 | 4.5719 | 4.6379 | 4.5986 | 4.5802 | 4.4916 | 4.5958 | 4.5985 | 4.6589 | 4.68 | 4.6534 | 4.611 | 4.5248 | 4.5147 | 4.5548 | 4.5031 | 4.4946 | 4.4113 | 4.5123 | 4.385 | 4.6464 | 4.6978 | 4.6986 | 4.699 | 4.6695 | 4.6333 | 4.7402 | 4.6236 | 4.741 | 4.6801 | 4.6864 | 4.6892 | 4.5926 | 4.5978 | 4.5675 | 4.5982 | 4.7535 | 4.7567 | 4.595 | 4.6584 | 4.6711 | 4.5724 | 4.6232 | 4.581 | 4.6464 | 4.5982 | 4.6262 | 4.6647 | 4.5971 | 4.6113 | 4.6457 | 4.5355 | 4.4715 | 4.5581 | 4.5588 | 4.5913 | 4.6046 | 4.5804 | 4.5906 | 4.64 | 4.6297 | 4.5864 | 4.6307 | 4.6113 | 4.4091 | 4.5126 | 4.4972 | 4.5657 | 4.6167 | 4.5517 | 4.6 | 4.636 | 4.5986 | 4.5673 | 4.5283 | 4.5257 | 4.5559 | 4.4358 | 4.4803 | 4.5317 | 4.466 | 4.4543 | 4.6149 | 4.4997 | 4.5922 | 4.5865 | 4.621 | 4.527 | 4.5274 | 4.5392 | 4.5944 | 4.551 | 4.5468 | 4.5802 | 4.5524 | 4.521 | 4.5112 | 4.6143 | 4.554 | 4.605 | 4.5806 | 4.6368 | 4.6274 | 4.5817 | 4.5824 | 4.4891 | 4.6397 | 4.5406 | 4.4367 | 4.5201 | 4.5615 | 4.4638 | 4.4281 | 4.4962 | 4.5075 | 4.5306 | 4.5847 | 4.5178 | 4.492 | 4.5055 | 4.4939 | 4.4801 | 4.5846 | 4.5043 | 4.5812 | 4.5848 | 4.6723 | 4.6939 | 4.6236 | 4.5541 | 4.6075 | 4.6087 | 4.4461 | 4.5631 | 4.6244 | 4.5421 | 4.618 | 4.6303 | 4.5604 | 4.6115 | 4.6036 | 4.6008 | 4.5295 | 4.5761 | 4.6252 | 4.5797 | 4.5466 | 4.5477 | 4.6307 | 4.5501 | 4.5903 | 4.5786 | 4.5271 | 4.5776 | 4.5275 | 4.5506 | 4.598 | 4.5997 | 4.6307 | 4.6221 | 4.5583
2025-05-10 | 4.3868 | 4.2679 | 4.4265 | 4.4212 | 4.3758 | 4.2491 | 4.5356 | 4.2826 | 4.4492 | 4.4705 | 4.475 | 4.4492 | 4.4682 | 4.4735 | 4.522 | 4.5068 | 4.445 | 4.4665 | 4.422 | 4.4856 | 4.6136 | 4.5629 | 4.6053 | 4.5985 | 4.5492 | 4.5447 | 4.5955 | 4.572 | 4.6023 | 4.6061 | 4.553 | 4.572 | 4.3712 | 4.3405 | 4.3796 | 4.3979 | 4.4793 | 4.492 | 4.4136 | 4.449 | 4.35 | 4.4408 | 4.5548 | 4.4971 | 4.5234 | 4.6179 | 4.6133 | 4.5726 | 4.5238 | 4.5464 | 4.5609 | 4.4431 | 4.3846 | 4.4017 | 4.3605 | 4.4535 | 4.4214 | 4.23 | 4.2444 | 4.2281 | 4.4492 | 4.3726 | 4.4223 | 4.8123 | 4.7229 | 4.6573 | 4.7764 | 4.8454 | 4.7569 | 4.7212 | 4.8171 | 4.8589 | 4.7526 | 4.7261 | 4.7516 | 4.7825 | 4.7237 | 4.695 | 4.823 | 4.7792 | 4.7429 | 4.8016 | 4.8295 | 4.715 | 4.8413 | 4.8669 | 4.8185 | 4.7745 | 4.7812 | 4.6111 | 4.7671 | 4.7754 | 4.8592 | 4.8561 | 4.8796 | 4.912 | 4.853 | 4.8665 | 4.8689 | 4.8488 | 4.8189 | 4.8599 | 4.7422 | 4.8713 | 5.1008 | 4.891 | 4.9241 | 4.852 | 4.8333 | 4.9413 | 4.9055 | 4.7995 | 4.8908 | 4.8113 | 4.7905 | 4.8716 | 4.8357 | 4.8775 | 4.8554 | 4.8402 | 4.8175 | 4.8661 | 4.8276 | 4.8662 | 4.8768 | 4.8378 | 4.7736 | 4.8616 | 4.8285 | 4.8278 | 4.8109 | 4.4148 | 4.8454 | 4.9127 | 4.8119 | 4.8188 | 4.6919 | 4.8796 | 4.7708 | 4.7543 | 4.7312 | 4.8392 | 4.8475 | 4.7978 | 4.7874 | 4.863 | 4.7529 | 4.8698 | 4.8446 | 4.7583 | 4.8091 | 4.8464 | 4.9456 | 4.8071 | 4.8482 | 4.8202 | 4.646 | 4.8026 | 4.7678 | 4.7961 | 4.8099 | 4.8012 | 4.7167 | 4.8724 | 4.9268 | 4.7753 | 4.6992 | 4.6372 | 4.7782 | 4.7808 | 4.8091 | 4.8228 | 4.8447 | 4.8976 | 4.924 | 4.8772 | 4.8235 | 4.828 | 4.9036 | 4.798 | 4.8889 | 4.7875 | 4.907 | 4.9025 | 4.9339 | 4.9108 | 4.8859 | 4.9229 | 4.8692 | 4.9354 | 4.8193 | 4.9308 | 4.8001 | 4.8571 | 4.8806 | 4.8548 | 4.8925 | 4.7028 | 4.8259 | 4.7681 | 4.7571 | 4.7659 | 4.8162 | 4.7747 | 4.8335 | 4.8188 | 4.7318 | 4.6632 | 4.7114 | 4.6711 | 4.6444 | 4.6603 | 4.7786 | 4.7845 | 4.8238 | 4.8577 | 4.8219 | 4.7833 | 4.6406 | 4.6212 | 4.6928 | 4.637 | 4.634 | 4.6422 | 4.6899 | 4.5685 | 4.7895 | 4.8455 | 4.8308 | 4.8356 | 4.8014 | 4.7589 | 4.8713 | 4.738 | 4.9042 | 4.8465 | 4.8391 | 4.7959 | 4.6961 | 4.7597 | 4.6939 | 4.7529 | 4.9188 | 4.7527 | 4.7531 | 4.8411 | 4.8532 | 4.7387 | 4.7979 | 4.747 | 4.815 | 4.7813 | 4.7739 | 4.7911 | 4.7615 | 4.8008 | 4.812 | 4.7759 | 4.735 | 4.8147 | 4.7969 | 4.8361 | 4.8394 | 4.8168 | 4.8333 | 4.8912 | 4.8652 | 4.8164 | 4.8566 | 4.8277 | 4.6766 | 4.6246 | 4.7008 | 4.7609 | 4.7977 | 4.7484 | 4.672 | 4.8331 | 4.8227 | 4.8439 | 4.8095 | 4.8148 | 4.8337 | 4.6262 | 4.7559 | 4.8156 | 4.7528 | 4.7407 | 4.8961 | 4.8268 | 4.876 | 4.8587 | 4.8976 | 4.8008 | 4.8036 | 4.8067 | 4.8626 | 4.8157 | 4.8221 | 4.8366 | 4.8564 | 4.7819 | 4.7823 | 4.8472 | 4.8055 | 4.8855 | 4.8483 | 4.8923 | 4.8806 | 4.8266 | 4.8254 | 4.7174 | 4.9067 | 4.8124 | 4.6307 | 4.7989 | 4.8413 | 4.7389 | 4.726 | 4.747 | 4.7896 | 4.8108 | 4.8497 | 4.7686 | 4.7813 | 4.7787 | 4.7802 | 4.7372 | 4.8735 | 4.7908 | 4.8297 | 4.825 | 4.8976 | 4.8862 | 4.8736 | 4.7828 | 4.84 | 4.8677 | 4.6782 | 4.8419 | 4.8684 | 4.8161 | 4.8744 | 4.9129 | 4.8236 | 4.8909 | 4.8862 | 4.8953 | 4.8372 | 4.8717 | 4.9301 | 4.8534 | 4.8056 | 4.8135 | 4.9176 | 4.8402 | 4.8823 | 4.8619 | 4.8108 | 4.8823 | 4.8367 | 4.8352 | 4.8992 | 4.916 | 4.9454 | 4.9301 | 4.7502
2025-05-11 | 2.6172 | 2.551 | 2.6462 | 2.6447 | 2.603 | 2.4966 | 2.7154 | 2.547 | 2.6417 | 2.6614 | 2.675 | 2.65 | 2.6598 | 2.6576 | 2.6856 | 2.6856 | 2.6459 | 2.6794 | 2.6629 | 2.6917 | 2.772 | 2.7409 | 2.7629 | 2.7515 | 2.747 | 2.7167 | 2.7735 | 2.7598 | 2.7962 | 2.7848 | 2.747 | 2.7561 | 2.6121 | 2.5766 | 2.6037 | 2.6196 | 2.6659 | 2.6611 | 2.6174 | 2.6523 | 2.5985 | 2.6619 | 2.7178 | 2.701 | 2.7178 | 2.7836 | 2.7815 | 2.7567 | 2.7127 | 2.7327 | 2.7397 | 2.6526 | 2.6053 | 2.6356 | 2.614 | 2.6718 | 2.6774 | 2.5603 | 2.5743 | 2.5529 | 2.6606 | 2.633 | 2.6415 | 2.8992 | 2.8496 | 2.8688 | 2.872 | 2.9206 | 2.8536 | 2.8295 | 2.8861 | 2.9168 | 2.8354 | 2.8138 | 2.8313 | 2.8481 | 2.8066 | 2.8589 | 2.8941 | 2.8799 | 2.8444 | 2.9077 | 2.9193 | 2.9073 | 2.951 | 2.9311 | 2.9185 | 2.8889 | 2.8941 | 2.8665 | 2.8689 | 2.8313 | 2.8941 | 2.9017 | 2.9306 | 2.9538 | 2.9479 | 2.9282 | 2.9231 | 2.8954 | 2.8734 | 2.9351 | 2.8594 | 2.9524 | 3.0604 | 2.9199 | 2.9634 | 2.9148 | 2.8992 | 2.9814 | 2.961 | 2.9879 | 2.9403 | 2.9235 | 2.8627 | 2.9382 | 2.9086 | 2.9148 | 2.8986 | 2.8899 | 2.8772 | 2.8923 | 2.8669 | 2.8932 | 2.9061 | 2.883 | 2.8385 | 2.8937 | 2.8661 | 2.864 | 2.8454 | 2.7315 | 2.8792 | 2.9124 | 2.8485 | 2.8602 | 2.7951 | 2.9396 | 2.8927 | 2.8395 | 2.8395 | 2.8951 | 2.8996 | 2.8758 | 2.8634 | 2.8916 | 2.9068 | 2.8994 | 2.8896 | 2.8355 | 2.8778 | 2.9106 | 2.9543 | 2.8868 | 2.8982 | 2.8754 | 2.7681 | 2.892 | 2.9037 | 2.8544 | 2.8685 | 2.8678 | 2.8278 | 2.9302 | 2.9638 | 2.8543 | 2.8405 | 2.8934 | 2.8621 | 2.8515 | 2.8643 | 2.8662 | 2.8787 | 2.9025 | 2.9274 | 2.8953 | 2.8938 | 2.9214 | 2.9305 | 2.871 | 2.9162 | 2.855 | 2.9267 | 2.9169 | 2.9354 | 2.9169 | 2.8991 | 2.9274 | 2.8964 | 2.9252 | 2.856 | 2.9278 | 2.853 | 2.8934 | 2.9 | 2.8829 | 2.9111 | 2.7991 | 2.8906 | 2.8591 | 2.8606 | 2.8735 | 2.9036 | 2.8732 | 2.9165 | 2.935 | 2.936 | 2.8536 | 2.8732 | 2.868 | 2.8472 | 2.8844 | 2.8794 | 2.8658 | 2.8921 | 2.905 | 2.8861 | 2.8641 | 2.8362 | 2.7625 | 2.8499 | 2.8024 | 2.7671 | 2.7502 | 2.8581 | 2.8081 | 2.8564 | 2.8935 | 2.8952 | 2.8799 | 2.8889 | 2.8328 | 2.9042 | 2.8437 | 2.927 | 2.8819 | 2.8842 | 2.8622 | 2.7028 | 2.8388 | 2.6703 | 2.8385 | 2.94 | 2.9356 | 2.8273 | 2.8478 | 2.8866 | 2.8287 | 2.856 | 2.8186 | 2.8613 | 2.8299 | 2.7715 | 2.837 | 2.7996 | 2.8497 | 2.8601 | 2.8336 | 2.7919 | 2.8558 | 2.8543 | 2.9043 | 2.9131 | 2.8735 | 2.8765 | 2.9021 | 2.8885 | 2.8619 | 2.8907 | 2.8965 | 2.8313 | 2.7656 | 2.8725 | 2.8431 | 2.8632 | 2.8297 | 2.8776 | 2.8877 | 2.8668 | 2.8575 | 2.8394 | 2.8333 | 2.8454 | 2.7264 | 2.8001 | 2.8405 | 2.785 | 2.7857 | 2.8862 | 2.8589 | 2.8651 | 2.8726 | 2.8917 | 2.8254 | 2.827 | 2.8341 | 2.8725 | 2.8563 | 2.8495 | 2.8703 | 2.866 | 2.8324 | 2.8278 | 2.8665 | 2.8441 | 2.8864 | 2.8623 | 2.9153 | 2.8873 | 2.8524 | 2.6193 | 2.5049 | 2.9278 | 2.8433 | 2.8392 | 2.8336 | 2.8607 | 2.7915 | 2.5013 | 2.7476 | 2.8124 | 2.8093 | 2.8777 | 2.7058 | 2.825 | 2.7828 | 2.7772 | 2.4247 | 2.9001 | 2.8348 | 2.8446 | 2.0812 | 2.781 | 2.8257 | 2.241 | 2.8138 | 2.859 | 2.8609 | 2.7712 | 2.837 | 2.8699 | 2.8474 | 2.871 | 2.8941 | 2.8399 | 2.8697 | 2.8807 | 2.8874 | 2.8352 | 2.8575 | 2.8995 | 2.8457 | 2.8254 | 2.8489 | 2.8709 | 2.8596 | 2.8579 | 2.8796 | 2.8273 | 2.8627 | 2.8356 | 2.8583 | 2.8728 | 2.9117 | 2.9117 | 2.8984 | 2.8274
2025-05-12 | 3.9944 | 3.8931 | 4.0432 | 4.0386 | 3.9629 | 3.8307 | 4.1438 | 3.9083 | 4.0379 | 4.0583 | 4.0856 | 4.0591 | 4.0356 | 4.0697 | 4.0909 | 4.0977 | 4.0542 | 4.0789 | 4.0265 | 4.0977 | 4.2144 | 4.1583 | 4.1841 | 4.1833 | 4.1674 | 4.1295 | 4.1962 | 4.147 | 4.2174 | 4.2098 | 4.1515 | 4.1659 | 3.9348 | 3.9027 | 3.9506 | 3.9657 | 4.0423 | 4.0606 | 3.9621 | 4.0112 | 3.9205 | 3.98 | 4.0479 | 4.0117 | 4.0475 | 4.1179 | 4.0952 | 4.0625 | 3.9829 | 4.09 | 4.0777 | 3.9637 | 3.9076 | 3.9551 | 3.9413 | 3.9692 | 4.0081 | 3.8394 | 3.8626 | 3.8185 | 4.0477 | 3.9618 | 3.9472 | 4.3057 | 4.2405 | 4.3281 | 4.3054 | 4.2864 | 4.2844 | 4.2129 | 4.3582 | 4.2933 | 4.2322 | 4.1683 | 4.2257 | 4.2991 | 4.2623 | 4.0511 | 4.3057 | 4.3609 | 4.215 | 4.2715 | 4.3858 | 4.3351 | 4.403 | 4.3806 | 4.2937 | 4.2291 | 4.3547 | 4.2754 | 4.2854 | 4.1646 | 4.2522 | 4.3112 | 4.3565 | 4.2995 | 4.2533 | 4.3506 | 4.2974 | 4.2937 | 4.3009 | 4.3288 | 4.2867 | 4.3099 | 4.4959 | 4.294 | 4.3799 | 4.266 | 4.2654 | 4.3934 | 4.3747 | 4.3154 | 4.3023 | 4.2659 | 4.2757 | 4.3006 | 4.0963 | 4.3413 | 4.234 | 4.3678 | 4.3054 | 4.2133 | 4.2904 | 4.3608 | 4.3854 | 4.3126 | 4.2885 | 4.3554 | 4.2854 | 4.2678 | 4.2136 | 4.0828 | 4.2119 | 4.2571 | 4.186 | 4.0794 | 4.1147 | 4.0825 | 4.0092 | 4.0217 | 4.0562 | 4.039 | 4.0828 | 4.1287 | 4.0763 | 4.1335 | 4.1063 | 4.1714 | 4.129 | 4.0018 | 4.1556 | 4.1149 | 4.1924 | 4.0797 | 4.1318 | 4.0652 | 4.0431 | 4.128 | 4.1774 | 4.0569 | 4.1187 | 4.1142 | 4.0814 | 4.1809 | 4.2236 | 4.1172 | 3.904 | 3.9615 | 3.9293 | 3.9184 | 3.9199 | 3.9312 | 3.9698 | 4.0094 | 4.0533 | 4.0042 | 3.9796 | 4.0019 | 4.0227 | 3.977 | 4.0688 | 3.9358 | 4.0299 | 4.0363 | 4.0627 | 4.0624 | 4.0302 | 4.082 | 4.028 | 4.0865 | 4.0049 | 4.0949 | 4.0185 | 4.0661 | 4.0937 | 4.0774 | 4.0889 | 3.9523 | 4.0991 | 4.0412 | 3.9708 | 3.9956 | 4.0892 | 3.9551 | 4.026 | 4.0923 | 3.9745 | 3.9446 | 4.0035 | 4.0274 | 3.9837 | 4.0253 | 4.0385 | 4.0703 | 4.1342 | 3.9439 | 4.1283 | 4.0707 | 3.9204 | 3.9371 | 4.0193 | 3.923 | 3.8801 | 3.9355 | 3.9398 | 3.8712 | 4.0538 | 4.072 | 4.137 | 4.0706 | 4.0793 | 4.0375 | 4.113 | 4.0031 | 4.1586 | 4.0848 | 4.0962 | 4.0181 | 3.9385 | 3.9904 | 3.9437 | 3.9871 | 4.1758 | 4.1915 | 4.0232 | 4.0562 | 4.1001 | 3.9998 | 4.0797 | 4.017 | 4.0102 | 3.9882 | 3.977 | 4.0289 | 3.983 | 4.0099 | 3.9818 | 4.2425 | 3.9675 | 4.2584 | 4.2414 | 4.1655 | 4.2645 | 4.1282 | 4.1905 | 4.346 | 4.3478 | 4.2516 | 4.2996 | 4.2316 | 4.1158 | 4.1385 | 4.1086 | 4.1716 | 4.2094 | 4.175 | 4.1786 | 4.2642 | 4.2682 | 4.1776 | 4.1697 | 4.1727 | 4.1841 | 4.0506 | 4.1088 | 4.1795 | 4.124 | 4.1036 | 4.2441 | 4.1401 | 4.229 | 4.237 | 4.2821 | 4.2004 | 4.2139 | 4.2013 | 4.2458 | 4.212 | 4.2199 | 4.2381 | 4.1049 | 4.1907 | 4.1714 | 4.2495 | 4.2025 | 4.3002 | 4.2347 | 4.2506 | 4.3075 | 4.2643 | 4.1562 | 3.9431 | 4.246 | 4.1384 | 4.1549 | 4.1538 | 4.2226 | 4.1506 | 3.9975 | 4.0724 | 4.1358 | 4.1409 | 4.1568 | 4.0857 | 4.0764 | 4.1085 | 4.0839 | 3.9968 | 4.1697 | 4.1452 | 4.1279 | 3.9031 | 4.2386 | 4.2111 | 3.9694 | 4.0887 | 4.1455 | 4.1377 | 4.0386 | 4.1175 | 4.1642 | 4.1302 | 4.1568 | 4.1788 | 4.1276 | 4.2092 | 4.2308 | 4.193 | 4.1965 | 4.1715 | 4.2221 | 4.0827 | 4.1171 | 4.116 | 4.1994 | 4.0938 | 4.1441 | 4.1063 | 4.1107 | 4.156 | 4.1209 | 4.1464 | 4.2275 | 4.1951 | 4.2233 | 4.2276 | 4.1267
2025-05-13 | 2.5742 | 2.5112 | 2.6 | 2.5947 | 2.5561 | 2.4579 | 2.6718 | 2.5076 | 2.5992 | 2.6008 | 2.6432 | 2.6114 | 2.603 | 2.6008 | 2.6318 | 2.6318 | 2.5933 | 2.6316 | 2.6258 | 2.6439 | 2.7424 | 2.7008 | 2.7061 | 2.6871 | 2.7083 | 2.6909 | 2.7265 | 2.7068 | 2.7606 | 2.7394 | 2.7061 | 2.6947 | 2.5523 | 2.5183 | 2.5423 | 2.5574 | 2.6069 | 2.6029 | 2.5614 | 2.5997 | 2.4561 | 2.5963 | 2.6484 | 2.6265 | 2.6396 | 2.7019 | 2.693 | 2.664 | 2.5978 | 2.6497 | 2.651 | 2.5758 | 2.5418 | 2.5604 | 2.5525 | 2.5941 | 2.6001 | 2.4825 | 2.5104 | 2.4826 | 2.622 | 2.578 | 2.5638 | 2.8613 | 2.8185 | 2.847 | 2.852 | 2.8734 | 2.8236 | 2.7995 | 2.8606 | 2.8689 | 2.7919 | 2.7724 | 2.7795 | 2.8077 | 2.7659 | 2.7443 | 2.8447 | 2.8471 | 2.803 | 2.8426 | 2.8706 | 2.8644 | 2.8606 | 2.8763 | 2.8604 | 2.8239 | 2.864 | 2.8371 | 2.8389 | 2.7926 | 2.8406 | 2.8558 | 2.8813 | 2.8716 | 2.853 | 2.8678 | 2.852 | 2.8503 | 2.8272 | 2.8699 | 2.7994 | 2.8879 | 2.8868 | 2.8682 | 2.9186 | 2.8616 | 2.852 | 2.9341 | 2.9137 | 2.922 | 2.8382 | 2.8618 | 2.8213 | 2.8658 | 2.8444 | 2.8647 | 2.5404 | 2.8499 | 2.8282 | 2.8378 | 2.824 | 2.8575 | 2.8547 | 2.7574 | 2.7985 | 2.8447 | 2.7429 | 2.8088 | 2.7809 | 2.5138 | 2.7971 | 2.8306 | 2.7743 | 2.7767 | 2.7291 | 2.7961 | 2.7444 | 2.725 | 2.7371 | 2.7553 | 2.7712 | 2.7692 | 2.7571 | 2.7923 | 2.7854 | 2.7994 | 2.7827 | 2.6172 | 2.7897 | 2.7909 | 2.8568 | 2.7733 | 2.7937 | 2.6863 | 2.6546 | 2.8002 | 2.8081 | 2.7581 | 2.7767 | 2.7602 | 2.7333 | 2.8171 | 2.8516 | 2.5924 | 2.6345 | 2.6625 | 2.6425 | 2.6402 | 2.6447 | 2.6519 | 2.6735 | 2.7045 | 2.7324 | 2.695 | 2.6701 | 2.7033 | 2.7041 | 2.6746 | 2.7218 | 2.6457 | 2.6958 | 2.7098 | 2.737 | 2.7271 | 2.7037 | 2.7336 | 2.7029 | 2.7343 | 2.6742 | 2.7309 | 2.6882 | 2.7128 | 2.7139 | 2.7063 | 2.7389 | 2.6671 | 2.7521 | 2.7261 | 2.6922 | 2.7036 | 2.7411 | 2.7041 | 2.7415 | 2.7582 | 2.6162 | 2.6787 | 2.7223 | 2.7241 | 2.6944 | 2.6476 | 2.7116 | 2.7747 | 2.7578 | 2.7481 | 2.7547 | 2.7263 | 2.5837 | 2.571 | 2.682 | 2.6892 | 2.5913 | 2.5885 | 2.6558 | 2.6001 | 2.6677 | 2.6895 | 2.7174 | 2.699 | 2.7147 | 2.6568 | 2.7622 | 2.6789 | 2.7339 | 2.6876 | 2.7013 | 2.719 | 2.6691 | 2.6418 | 2.6549 | 2.6527 | 2.7437 | 2.7512 | 2.6531 | 2.6549 | 2.686 | 2.6198 | 2.6735 | 2.6318 | 2.6635 | 2.6489 | 2.6975 | 2.7058 | 2.6583 | 2.6703 | 2.6856 | 2.7237 | 2.6956 | 2.8094 | 2.806 | 2.7793 | 2.8428 | 2.6176 | 2.7234 | 2.8561 | 2.8462 | 2.8104 | 2.8307 | 2.8115 | 2.7468 | 2.7114 | 2.7652 | 2.7652 | 2.7983 | 2.7677 | 2.7899 | 2.8212 | 2.8065 | 2.7237 | 2.7135 | 2.7116 | 2.7048 | 2.6485 | 2.6754 | 2.7192 | 2.675 | 2.6644 | 2.7676 | 2.6981 | 2.7562 | 2.7691 | 2.7817 | 2.7198 | 2.7095 | 2.7264 | 2.7751 | 2.7524 | 2.749 | 2.7702 | 2.7207 | 2.7486 | 2.7175 | 2.7819 | 2.749 | 2.7786 | 2.7619 | 2.7944 | 2.7925 | 2.7639 | 2.7229 | 2.5855 | 2.752 | 2.6942 | 2.6893 | 2.6826 | 2.7369 | 2.6688 | 2.6056 | 2.6877 | 2.6609 | 2.6876 | 2.72 | 2.6889 | 2.659 | 2.6833 | 2.6957 | 2.6841 | 2.7394 | 2.6711 | 2.6797 | 2.7111 | 2.7845 | 2.814 | 2.7378 | 2.6605 | 2.6889 | 2.6617 | 2.6232 | 2.6706 | 2.7192 | 2.6931 | 2.7174 | 2.7394 | 2.6919 | 2.7233 | 2.7433 | 2.745 | 2.7113 | 2.7143 | 2.7524 | 2.6734 | 2.6755 | 2.671 | 2.7155 | 2.6773 | 2.6889 | 2.6977 | 2.666 | 2.699 | 2.6711 | 2.6974 | 2.7254 | 2.7425 | 2.7535 | 2.7496 | 2.7209
2025-05-14 | 3.547 | 3.4577 | 3.5795 | 3.5818 | 3.5114 | 3.3819 | 3.6649 | 3.4455 | 3.5667 | 3.5833 | 3.6106 | 3.5788 | 3.5689 | 3.5871 | 3.6121 | 3.6083 | 3.5678 | 3.6069 | 3.5818 | 3.625 | 3.7235 | 3.6811 | 3.7023 | 3.6977 | 3.6871 | 3.6515 | 3.6947 | 3.6826 | 3.7417 | 3.7258 | 3.6598 | 3.6614 | 3.478 | 3.453 | 3.4944 | 3.5152 | 3.5829 | 3.5957 | 3.4992 | 3.559 | 3.3023 | 3.5421 | 3.6103 | 3.595 | 3.6148 | 3.6867 | 3.6776 | 3.6499 | 3.5758 | 3.6267 | 3.6305 | 3.5199 | 3.4545 | 3.4969 | 3.4869 | 3.5605 | 3.5625 | 3.418 | 3.4369 | 3.411 | 3.5758 | 3.5279 | 3.5161 | 3.8951 | 3.843 | 3.8917 | 3.9134 | 3.94 | 3.8714 | 3.804 | 3.8979 | 3.9244 | 3.8237 | 3.8108 | 3.8219 | 3.8752 | 3.8092 | 3.7302 | 3.8634 | 3.8482 | 3.7319 | 3.8727 | 3.9186 | 3.8925 | 3.9296 | 3.952 | 3.9004 | 3.8839 | 3.9092 | 3.8513 | 3.8554 | 3.8634 | 3.9596 | 3.991 | 4.02 | 4.0252 | 3.9997 | 3.9938 | 3.9896 | 3.9513 | 3.9394 | 3.9979 | 3.9102 | 3.9959 | 4.1832 | 3.9658 | 4.0331 | 3.9375 | 3.9424 | 4.0424 | 4.0173 | 3.9386 | 4.0181 | 3.9329 | 3.6888 | 3.8575 | 3.8337 | 3.8485 | 3.8671 | 3.824 | 3.8389 | 3.6453 | 3.8009 | 3.8337 | 3.853 | 3.824 | 3.7774 | 3.8433 | 3.7302 | 3.8182 | 3.784 | 3.6118 | 3.7926 | 3.8482 | 3.7495 | 3.7605 | 3.7424 | 3.8696 | 3.7768 | 3.7415 | 3.8475 | 3.8078 | 3.8054 | 3.7892 | 3.7771 | 3.8406 | 3.8226 | 3.8369 | 3.9352 | 3.733 | 3.8067 | 3.8157 | 3.9021 | 3.7785 | 3.8016 | 3.7978 | 3.6349 | 3.8237 | 3.7716 | 3.6822 | 3.7909 | 3.7947 | 3.7502 | 3.8072 | 3.8713 | 3.6815 | 3.692 | 3.7593 | 3.74 | 3.7362 | 3.7392 | 3.743 | 3.76 | 3.7952 | 3.8148 | 3.7559 | 3.76 | 3.7868 | 3.7986 | 3.7571 | 3.7967 | 3.6865 | 3.791 | 3.7763 | 3.8091 | 3.7989 | 3.7646 | 3.8031 | 3.7577 | 3.8027 | 3.7252 | 3.8016 | 3.7279 | 3.7627 | 3.7821 | 3.7607 | 3.781 | 3.6974 | 3.8232 | 3.7586 | 3.7515 | 3.7721 | 3.8213 | 3.7569 | 3.7393 | 3.8543 | 3.6144 | 3.7216 | 3.6824 | 3.7557 | 3.6939 | 3.749 | 3.7543 | 3.75 | 3.8191 | 3.8202 | 3.816 | 3.7703 | 3.595 | 3.5586 | 3.7229 | 3.6531 | 3.6045 | 3.5859 | 3.6859 | 3.6047 | 3.7031 | 3.7327 | 3.7841 | 3.7567 | 3.7732 | 3.709 | 3.8151 | 3.7247 | 3.7932 | 3.73 | 3.748 | 3.7575 | 3.6256 | 3.6824 | 3.6114 | 3.6892 | 3.7783 | 3.7951 | 3.6393 | 3.6686 | 3.7147 | 3.6481 | 3.6794 | 3.6507 | 3.7026 | 3.6664 | 3.6596 | 3.7142 | 3.6727 | 3.7082 | 3.7228 | 3.8115 | 3.7483 | 3.8386 | 3.8349 | 3.7582 | 3.8828 | 3.8415 | 3.7621 | 3.8982 | 3.8851 | 3.8257 | 3.8865 | 3.8475 | 3.6706 | 3.6953 | 3.7822 | 3.7745 | 3.823 | 3.7855 | 3.8342 | 3.859 | 3.8597 | 3.7581 | 3.7445 | 3.7457 | 3.7608 | 3.6474 | 3.6788 | 3.7555 | 3.6772 | 3.6833 | 3.7978 | 3.7322 | 3.785 | 3.7778 | 3.8008 | 3.7353 | 3.7425 | 3.742 | 3.7789 | 3.7524 | 3.7482 | 3.7516 | 3.6656 | 3.7118 | 3.708 | 3.7774 | 3.7254 | 3.8071 | 3.7653 | 3.8269 | 3.8171 | 3.7853 | 3.721 | 3.6199 | 3.7956 | 3.7105 | 3.7153 | 3.6836 | 3.7556 | 3.683 | 3.6888 | 3.6956 | 3.6833 | 3.6872 | 3.7307 | 3.6765 | 3.6469 | 3.7019 | 3.6753 | 3.6357 | 3.7674 | 3.6888 | 3.7767 | 3.6707 | 3.832 | 3.8069 | 3.7115 | 3.6993 | 3.7531 | 3.7493 | 3.6436 | 3.7277 | 3.7632 | 3.7344 | 3.7703 | 3.7774 | 3.7265 | 3.7669 | 3.7755 | 3.7736 | 3.7478 | 3.7555 | 3.7995 | 3.7413 | 3.7546 | 3.755 | 3.7967 | 3.7384 | 3.771 | 3.7816 | 3.7461 | 3.7665 | 3.7527 | 3.7476 | 3.792 | 3.8136 | 3.8218 | 3.8191 | 3.7475
2025-05-15 | 1.8533 | 1.7951 | 1.8735 | 1.8735 | 1.8455 | 1.7646 | 1.925 | 1.8023 | 1.8803 | 1.8795 | 1.8879 | 1.8765 | 1.8909 | 1.8818 | 1.9091 | 1.9008 | 1.8628 | 1.9139 | 1.8917 | 1.9076 | 1.9652 | 1.9492 | 1.9455 | 1.9432 | 1.9242 | 1.928 | 1.9712 | 1.9621 | 1.9856 | 1.9614 | 1.9492 | 1.9182 | 1.8667 | 1.8341 | 1.8381 | 1.8644 | 1.89 | 1.8748 | 1.8561 | 1.89 | 1.7583 | 1.9023 | 1.9404 | 1.9306 | 1.9466 | 1.9986 | 1.994 | 1.9825 | 1.9248 | 1.9442 | 1.9479 | 1.8854 | 1.8644 | 1.8778 | 1.857 | 1.9034 | 1.912 | 1.8268 | 1.8323 | 1.8234 | 1.875 | 1.8742 | 1.8834 | 2.0283 | 1.9976 | 2.0152 | 2.0148 | 2.048 | 2.0052 | 1.9558 | 2.0366 | 2.0538 | 2.0038 | 1.991 | 1.9983 | 2.0072 | 1.983 | 1.9983 | 2.0286 | 2.0273 | 2.0017 | 2.0351 | 2.0404 | 2.0361 | 2.0583 | 2.0415 | 2.0372 | 2.0252 | 2.0307 | 2.0104 | 2.0131 | 1.9617 | 2.0024 | 2.0121 | 2.03 | 2.048 | 2.041 | 2.0297 | 2.0231 | 1.9957 | 1.9892 | 2.0328 | 1.9768 | 2.0497 | 2.1228 | 2.0314 | 2.0621 | 2.0328 | 2.011 | 2.0797 | 2.0638 | 2.0794 | 2.0491 | 2.0343 | 2.0159 | 2.0732 | 2.0473 | 2.0518 | 2.0407 | 2.029 | 2.0418 | 2.05 | 2.0271 | 2.0444 | 2.0645 | 2.0597 | 2.0141 | 2.0635 | 2.029 | 2.0321 | 2.0228 | 1.9607 | 2.0511 | 2.0749 | 2.0283 | 2.0355 | 2.0938 | 2.1008 | 2.0692 | 2.0314 | 2.0331 | 2.0645 | 2.07 | 2.0587 | 2.0462 | 2.0839 | 2.078 | 2.0732 | 2.0599 | 2.0253 | 2.0524 | 2.0756 | 2.1073 | 2.0559 | 2.0611 | 2.0493 | 1.9727 | 2.0611 | 2.0659 | 2.0321 | 2.0442 | 2.0455 | 2.0207 | 2.0866 | 2.1153 | 2.0335 | 2.0068 | 2.0571 | 2.0121 | 2.0178 | 2.0238 | 2.0283 | 2.0378 | 2.0556 | 2.0831 | 2.0499 | 2.0457 | 2.079 | 2.0915 | 2.0421 | 2.0794 | 2.0364 | 2.0786 | 2.0805 | 2.0873 | 2.0631 | 2.0548 | 2.0737 | 2.0612 | 2.0695 | 2.0234 | 2.0601 | 2.0321 | 2.051 | 2.0413 | 2.0329 | 2.081 | 1.9883 | 2.0551 | 2.0369 | 2.0438 | 2.0589 | 2.0699 | 2.0438 | 2.0794 | 2.0948 | 2.0876 | 2.038 | 2.0351 | 2.0386 | 2.0255 | 2.027 | 2.0516 | 2.0487 | 2.0604 | 2.0699 | 2.0598 | 2.0482 | 2.0091 | 1.9881 | 2.0242 | 1.991 | 1.9599 | 1.9438 | 2.0232 | 1.9869 | 2.0141 | 2.0494 | 2.0546 | 2.0283 | 2.0133 | 1.984 | 2.0416 | 2.0004 | 2.0808 | 2.0389 | 2.0459 | 1.9886 | 1.8255 | 1.9945 | 1.8154 | 2.0038 | 2.1028 | 2.1154 | 2.0137 | 2.0304 | 2.0549 | 1.9941 | 2.0357 | 2.0008 | 2.0382 | 2.0117 | 1.9134 | 1.9978 | 1.9433 | 2.03 | 2.0188 | 2.0044 | 1.9742 | 2.0207 | 2.022 | 2.0558 | 2.0644 | 2.035 | 2.0402 | 2.0526 | 2.047 | 2.0272 | 2.049 | 2.0529 | 2.005 | 1.9935 | 2.0443 | 2.0137 | 2.0343 | 2.0085 | 2.0405 | 2.0511 | 2.038 | 1.9981 | 1.983 | 1.958 | 1.9626 | 1.9293 | 1.9528 | 1.9819 | 1.938 | 1.9354 | 2.0215 | 2.0048 | 2.0038 | 2.0163 | 2.0377 | 1.9893 | 1.9548 | 1.96 | 2.0175 | 1.9826 | 1.9784 | 2.0083 | 1.828 | 1.9924 | 1.9625 | 2.0197 | 2.0046 | 1.9992 | 1.9977 | 2.0427 | 2.0218 | 2.004 | 1.9513 | 1.8613 | 2.0321 | 1.9889 | 1.9758 | 1.9698 | 2.0127 | 1.9396 | 1.8779 | 1.9852 | 1.94 | 1.9651 | 2.0203 | 1.9444 | 1.9911 | 1.9926 | 1.975 | 1.824 | 2.0403 | 1.9772 | 1.9988 | 1.6605 | 1.9878 | 1.9819 | 1.7033 | 1.959 | 1.9717 | 2.0113 | 1.9279 | 1.9578 | 1.9978 | 1.9717 | 1.9889 | 2.0165 | 1.9605 | 1.9859 | 2.0016 | 2.0176 | 1.9669 | 1.9772 | 2.0322 | 1.9927 | 1.9619 | 1.9634 | 2 | 1.9834 | 2.0001 | 2.0098 | 1.9639 | 1.9896 | 1.9619 | 1.989 | 1.9974 | 2.0365 | 2.0428 | 2.0043 | 1.9962
2025-05-16 | 2.8581 | 2.7743 | 2.8955 | 2.8841 | 2.8227 | 2.7092 | 2.9686 | 2.7735 | 2.8773 | 2.8917 | 2.9144 | 2.8856 | 2.8758 | 2.8864 | 2.9076 | 2.8985 | 2.874 | 2.9195 | 2.9189 | 2.9386 | 3.0288 | 2.9879 | 3.0076 | 2.9886 | 3.0008 | 2.9712 | 3.0083 | 2.9841 | 3.0508 | 3.0356 | 2.9826 | 2.9788 | 2.8265 | 2.7943 | 2.815 | 2.8429 | 2.882 | 2.8796 | 2.8303 | 2.8668 | 2.7644 | 2.8666 | 2.932 | 2.9072 | 2.9327 | 3 | 2.9933 | 2.9704 | 2.915 | 2.9386 | 2.9509 | 2.8521 | 2.8074 | 2.8344 | 2.8122 | 2.8915 | 2.8925 | 2.7609 | 2.7788 | 2.7615 | 2.8735 | 2.8432 | 2.8453 | 3.1494 | 3.1018 | 3.1492 | 3.156 | 3.2157 | 3.1502 | 3.0983 | 3.157 | 3.1998 | 3.1084 | 3.1083 | 3.1056 | 3.1526 | 3.0859 | 2.991 | 3.0966 | 3.1039 | 3.0756 | 3.3036 | 3.1377 | 3.1472 | 3.1739 | 3.1797 | 3.1746 | 3.1529 | 3.1643 | 3.1108 | 3.1284 | 3.1801 | 3.2336 | 3.246 | 3.2553 | 3.2685 | 3.2657 | 3.2326 | 3.2181 | 3.1926 | 3.1663 | 3.2119 | 3.1288 | 3.2519 | 3.3699 | 3.2326 | 3.2678 | 3.2219 | 3.2015 | 3.275 | 3.2498 | 3.2864 | 3.1667 | 3.1847 | 3.0807 | 3.1577 | 3.1132 | 3.1142 | 3.1042 | 3.0811 | 3.1128 | 3.0487 | 3.0765 | 3.1079 | 3.1325 | 3.1111 | 3.0649 | 3.1315 | 3.089 | 3.0977 | 3.0652 | 2.9075 | 3.098 | 3.1273 | 3.0618 | 3.0545 | 3.1439 | 3.1404 | 3.0803 | 3.0283 | 3.0435 | 3.0814 | 3.097 | 3.0801 | 3.0714 | 3.1077 | 3.0887 | 3.0924 | 3.0833 | 3.0382 | 3.0833 | 3.098 | 3.1693 | 3.0787 | 3.0856 | 3.0763 | 2.8916 | 3.0908 | 3.0973 | 3.038 | 3.0552 | 3.0728 | 3.0311 | 3.1167 | 3.158 | 3.0545 | 3.006 | 3.0522 | 3.0193 | 2.997 | 2.9834 | 2.9792 | 2.9887 | 3.02 | 3.037 | 3.0026 | 3.0661 | 3.0737 | 3.0423 | 3.0214 | 3.0317 | 2.9369 | 3.042 | 3.02 | 3.0488 | 3.028 | 3.003 | 3.0333 | 2.9966 | 3.0438 | 2.9694 | 3.0317 | 2.9713 | 2.9921 | 3.002 | 2.9825 | 3.0028 | 3.0022 | 3.1014 | 3.0604 | 3.1021 | 3.138 | 3.1783 | 3.073 | 3.1076 | 3.1928 | 3.2042 | 3.1183 | 3.0081 | 3.1382 | 3.1401 | 3.0136 | 3.0884 | 3.1005 | 3.1064 | 3.1103 | 3.1145 | 3.1127 | 3.0648 | 2.9646 | 3.0878 | 3.0497 | 3.0241 | 2.9975 | 3.0825 | 3.0358 | 2.9628 | 2.9924 | 2.9898 | 2.9929 | 2.9549 | 2.9472 | 3.0259 | 2.9491 | 3.0326 | 2.9898 | 2.987 | 2.9894 | 2.9779 | 2.9435 | 2.9465 | 2.9483 | 3.0365 | 3.022 | 2.9396 | 2.9674 | 2.9816 | 2.9334 | 2.9474 | 2.9293 | 2.9659 | 2.9435 | 3.004 | 2.9984 | 2.9528 | 2.9644 | 2.9868 | 2.9934 | 2.9514 | 3.0285 | 3.0237 | 3.074 | 3.1057 | 3.0705 | 2.9846 | 3.093 | 3.0974 | 3.0745 | 3.1065 | 3.0948 | 2.9933 | 2.9731 | 3.0693 | 3.0259 | 3.0307 | 3.0263 | 3.0814 | 3.0811 | 3.0726 | 2.9225 | 2.901 | 2.9017 | 2.9248 | 2.8469 | 2.8961 | 2.9025 | 2.9074 | 2.8855 | 2.9554 | 2.9451 | 2.9516 | 2.9497 | 2.9484 | 2.8901 | 2.8964 | 2.9117 | 2.9574 | 2.9261 | 2.9397 | 2.9583 | 2.9768 | 2.9378 | 2.8881 | 2.9977 | 2.9386 | 2.953 | 2.9613 | 2.9917 | 2.9817 | 2.9595 | 2.9046 | 2.9015 | 2.9107 | 2.8706 | 2.8463 | 2.8392 | 2.8575 | 2.8811 | 2.908 | 2.8536 | 2.8564 | 2.9203 | 2.8885 | 2.8807 | 2.8583 | 2.8523 | 2.8915 | 2.9323 | 2.9116 | 2.8858 | 2.8893 | 2.9423 | 2.9572 | 2.9827 | 2.9745 | 2.951 | 2.979 | 3.0048 | 2.9603 | 2.9652 | 2.9932 | 2.9696 | 2.988 | 2.9775 | 2.939 | 2.9533 | 2.9827 | 2.9898 | 2.9588 | 2.9733 | 3.0232 | 3.0188 | 2.9973 | 2.9876 | 3.0428 | 2.9488 | 3.0418 | 3.0441 | 2.9827 | 3.0246 | 2.9831 | 2.9949 | 3.0257 | 3.0404 | 3.0361 | 3.0357 | 3.0141
2025-05-17 | 2.4402 | 2.3764 | 2.4667 | 2.4697 | 2.4326 | 2.3371 | 2.5348 | 2.3773 | 2.4833 | 2.4917 | 2.4947 | 2.4811 | 2.4894 | 2.4955 | 2.528 | 2.5227 | 2.4753 | 2.5255 | 2.503 | 2.528 | 2.6045 | 2.578 | 2.6023 | 2.5871 | 2.5788 | 2.5689 | 2.6053 | 2.5962 | 2.6379 | 2.6189 | 2.5886 | 2.5811 | 2.4265 | 2.4035 | 2.4298 | 2.4553 | 2.5032 | 2.5032 | 2.4386 | 2.4952 | 2.4273 | 2.4736 | 2.5166 | 2.5015 | 2.5387 | 2.5876 | 2.5938 | 2.5853 | 2.5324 | 2.5771 | 2.5814 | 2.5105 | 2.474 | 2.4893 | 2.4648 | 2.5262 | 2.5148 | 2.4081 | 2.4273 | 2.4075 | 2.4962 | 2.4873 | 2.4941 | 2.7029 | 2.6511 | 2.6739 | 2.6698 | 2.707 | 2.6501 | 2.6501 | 2.6977 | 2.7146 | 2.6449 | 2.6274 | 2.6329 | 2.6461 | 2.6108 | 2.6953 | 2.7271 | 2.7191 | 2.6698 | 2.7226 | 2.7502 | 2.7251 | 2.7574 | 2.7421 | 2.7233 | 2.6992 | 2.6967 | 2.6853 | 2.6822 | 2.6177 | 2.6687 | 2.6798 | 2.7019 | 2.7333 | 2.7133 | 2.7129 | 2.7081 | 2.6555 | 2.6562 | 2.7119 | 2.6462 | 2.7205 | 2.8237 | 2.6953 | 2.7322 | 2.6877 | 2.6577 | 2.7553 | 2.7384 | 2.6749 | 2.7389 | 2.7096 | 2.6867 | 2.7516 | 2.7295 | 2.7319 | 2.7422 | 2.7019 | 2.7139 | 2.725 | 2.702 | 2.7276 | 2.7464 | 2.7381 | 2.6856 | 2.7426 | 2.7005 | 2.705 | 2.6884 | 2.6467 | 2.7157 | 2.745 | 2.687 | 2.6884 | 2.6973 | 2.7101 | 2.6619 | 2.6253 | 2.6228 | 2.676 | 2.6805 | 2.6687 | 2.6484 | 2.6984 | 2.6894 | 2.6991 | 2.7778 | 2.6439 | 2.6833 | 2.6881 | 2.7513 | 2.6867 | 2.697 | 2.6767 | 2.3402 | 2.7195 | 2.6587 | 2.6749 | 2.6936 | 2.6153 | 2.6429 | 2.7315 | 2.7626 | 2.6688 | 2.5537 | 2.6081 | 2.5763 | 2.5695 | 2.5688 | 2.5654 | 2.5824 | 2.6088 | 2.6323 | 2.6073 | 2.6175 | 2.6364 | 2.6425 | 2.6071 | 2.6459 | 2.579 | 2.6398 | 2.6391 | 2.6508 | 2.63 | 2.6153 | 2.6349 | 2.6198 | 2.6451 | 2.5903 | 2.6417 | 2.5933 | 2.607 | 2.6171 | 2.6024 | 2.6266 | 2.6285 | 2.7036 | 2.5789 | 2.6669 | 2.6906 | 2.7191 | 2.6593 | 2.7094 | 2.7265 | 2.7292 | 2.6609 | 2.5931 | 2.6583 | 2.6479 | 2.6871 | 2.6835 | 2.7088 | 2.7198 | 2.7392 | 2.7299 | 2.6984 | 2.5363 | 2.5904 | 2.6419 | 2.6026 | 2.5697 | 2.54 | 2.6391 | 2.5919 | 2.5849 | 2.6113 | 2.6291 | 2.6162 | 2.6201 | 2.5634 | 2.6664 | 2.5955 | 2.6546 | 2.6079 | 2.6177 | 2.6295 | 2.572 | 2.5551 | 2.5592 | 2.5708 | 2.6754 | 2.6845 | 2.5918 | 2.6041 | 2.6197 | 2.5376 | 2.5954 | 2.5716 | 2.588 | 2.5705 | 2.6269 | 2.6299 | 2.5716 | 2.5809 | 2.6063 | 2.7112 | 2.6666 | 2.7237 | 2.7131 | 2.7503 | 2.7567 | 2.634 | 2.7223 | 2.7383 | 2.7292 | 2.6991 | 2.7301 | 2.6687 | 2.6529 | 2.6145 | 2.702 | 2.6753 | 2.7067 | 2.6775 | 2.708 | 2.7262 | 2.7123 | 2.65 | 2.6281 | 2.613 | 2.6259 | 2.5737 | 2.5816 | 2.6274 | 2.5711 | 2.5703 | 2.664 | 2.6163 | 2.6519 | 2.6493 | 2.6766 | 2.6306 | 2.6095 | 2.6115 | 2.6553 | 2.6185 | 2.6162 | 2.6284 | 2.6307 | 2.6102 | 2.5935 | 2.642 | 2.6086 | 2.6516 | 2.6325 | 2.6731 | 2.6496 | 2.6238 | 2.6287 | 2.5596 | 2.6619 | 2.6153 | 2.5918 | 2.591 | 2.6218 | 2.5589 | 2.5424 | 2.6003 | 2.5879 | 2.6138 | 2.64 | 2.6183 | 2.5697 | 2.6026 | 2.5996 | 2.6149 | 2.6535 | 2.573 | 2.6378 | 2.5973 | 2.7005 | 2.6962 | 2.7002 | 2.6418 | 2.665 | 2.7017 | 2.594 | 2.6583 | 2.6874 | 2.6546 | 2.6781 | 2.6927 | 2.6344 | 2.666 | 2.6452 | 2.6912 | 2.6543 | 2.6699 | 2.7178 | 2.6759 | 2.6699 | 2.6594 | 2.7198 | 2.5585 | 2.7136 | 2.6927 | 2.6535 | 2.6934 | 2.6582 | 2.6896 | 2.7113 | 2.7217 | 2.7249 | 2.7076 | 2.6311
2025-05-18 | 1.5072 | 1.4617 | 1.525 | 1.5258 | 1.503 | 1.4404 | 1.5685 | 1.4659 | 1.5318 | 1.5394 | 1.5379 | 1.5303 | 1.5402 | 1.5386 | 1.5591 | 1.5515 | 1.5239 | 1.5638 | 1.5538 | 1.5644 | 1.6144 | 1.5992 | 1.6129 | 1.6061 | 1.5932 | 1.5848 | 1.6174 | 1.6091 | 1.6333 | 1.622 | 1.6015 | 1.5811 | 1.5174 | 1.4928 | 1.4984 | 1.5175 | 1.5399 | 1.5367 | 1.5152 | 1.5423 | 1.5023 | 1.5528 | 1.5825 | 1.5702 | 1.5958 | 1.6324 | 1.6361 | 1.6257 | 1.5764 | 1.6029 | 1.6114 | 1.5547 | 1.526 | 1.5369 | 1.5221 | 1.5528 | 1.5712 | 1.5 | 1.5032 | 1.4833 | 1.5341 | 1.5366 | 1.5469 | 1.6694 | 1.6398 | 1.658 | 1.6529 | 1.6818 | 1.6468 | 1.6442 | 1.6781 | 1.6908 | 1.6491 | 1.6387 | 1.6439 | 1.6512 | 1.6266 | 1.6384 | 1.6684 | 1.668 | 1.646 | 1.671 | 1.6784 | 1.6714 | 1.6919 | 1.676 | 1.6753 | 1.6634 | 1.6698 | 1.6536 | 1.657 | 1.6132 | 1.6429 | 1.6491 | 1.6636 | 1.6784 | 1.674 | 1.6632 | 1.6573 | 1.6313 | 1.6263 | 1.6667 | 1.62 | 1.6815 | 1.7378 | 1.668 | 1.6922 | 1.668 | 1.6415 | 1.7091 | 1.696 | 1.7088 | 1.6856 | 1.6721 | 1.6563 | 1.7095 | 1.6836 | 1.685 | 1.6781 | 1.6563 | 1.6812 | 1.6901 | 1.6677 | 1.6807 | 1.705 | 1.6998 | 1.6618 | 1.7029 | 1.6674 | 1.6725 | 1.666 | 1.6867 | 1.6863 | 1.7108 | 1.6718 | 1.6746 | 1.7294 | 1.715 | 1.6937 | 1.6649 | 1.6677 | 1.6922 | 1.7005 | 1.6939 | 1.6815 | 1.7115 | 1.7077 | 1.7092 | 1.6968 | 1.671 | 1.7143 | 1.7088 | 1.7392 | 1.7001 | 1.6977 | 1.6901 | 1.6618 | 1.6743 | 1.705 | 1.6829 | 1.6877 | 1.6905 | 1.6705 | 1.7159 | 1.7422 | 1.6825 | 1.5359 | 1.5707 | 1.5506 | 1.5465 | 1.5514 | 1.5484 | 1.5665 | 1.5918 | 1.6088 | 1.5865 | 1.5831 | 1.596 | 1.6013 | 1.5774 | 1.5926 | 1.5574 | 1.6051 | 1.6013 | 1.6198 | 1.6088 | 1.5922 | 1.6107 | 1.5907 | 1.6206 | 1.5752 | 1.61 | 1.5964 | 1.5971 | 1.5925 | 1.5921 | 1.6032 | 1.6477 | 1.6922 | 1.6593 | 1.6653 | 1.6811 | 1.695 | 1.6641 | 1.6954 | 1.7083 | 1.7043 | 1.6648 | 1.6637 | 1.6506 | 1.649 | 1.7256 | 1.6739 | 1.6927 | 1.6966 | 1.711 | 1.7004 | 1.7443 | 1.631 | 1.6149 | 1.6454 | 1.6181 | 1.5965 | 1.5748 | 1.6515 | 1.6227 | 1.5749 | 1.5955 | 1.5985 | 1.5907 | 1.5706 | 1.5486 | 1.6201 | 1.5826 | 1.6177 | 1.5875 | 1.5934 | 1.5962 | 1.5867 | 1.562 | 1.5743 | 1.5717 | 1.6381 | 1.617 | 1.5432 | 1.5785 | 1.5859 | 1.4742 | 1.5655 | 1.5497 | 1.5732 | 1.5635 | 1.6158 | 1.5852 | 1.5691 | 1.5781 | 1.5882 | 1.6344 | 1.6082 | 1.6477 | 1.6459 | 1.6761 | 1.6873 | 1.6659 | 1.6644 | 1.6805 | 1.6797 | 1.6634 | 1.6815 | 1.6797 | 1.6351 | 1.6321 | 1.6695 | 1.6529 | 1.692 | 1.6706 | 1.2907 | 2.0243 | 1.6698 | 1.5385 | 1.5291 | 1.5227 | 1.5265 | 1.4989 | 1.4989 | 1.5299 | 1.4849 | 1.4917 | 1.5548 | 1.558 | 1.5503 | 1.5518 | 1.5532 | 1.5262 | 1.5131 | 1.5289 | 1.5255 | 1.5351 | 1.537 | 1.5502 | 1.5611 | 1.548 | 1.5195 | 1.5783 | 1.5461 | 1.5438 | 1.5571 | 1.5752 | 1.5675 | 1.5556 | 1.489 | 1.4852 | 1.4948 | 1.4858 | 1.4716 | 1.4712 | 1.479 | 1.4331 | 1.4973 | 1.4871 | 1.4615 | 1.4714 | 1.4973 | 1.4787 | 1.4495 | 1.4656 | 1.4917 | 1.516 | 1.5216 | 1.4368 | 1.4823 | 1.5122 | 1.5208 | 1.5306 | 1.5345 | 1.5194 | 1.5325 | 1.5583 | 1.491 | 1.5295 | 1.553 | 1.534 | 1.5467 | 1.5549 | 1.5228 | 1.5275 | 1.5385 | 1.5609 | 1.5265 | 1.5322 | 1.5624 | 1.5506 | 1.5411 | 1.5407 | 1.5651 | 1.4767 | 1.5672 | 1.5645 | 1.5235 | 1.5572 | 1.5204 | 1.5557 | 1.5525 | 1.5612 | 1.5589 | 1.5608 | 1.6017
2025-05-19 | 2.9737 | 2.9195 | 3.0083 | 3.0152 | 2.9621 | 2.8664 | 3.0933 | 2.8932 | 3.0068 | 3.0311 | 3.0424 | 3.0174 | 3.0318 | 3.0318 | 3.0318 | 3.0629 | 3.2209 | 3.0152 | 2.9 | 3.028 | 3.0659 | 3.1455 | 3.1136 | 3.1432 | 3.1364 | 3.1098 | 3.0871 | 3.1424 | 3.1258 | 3.1652 | 3.1568 | 3.1197 | 3.1114 | 3.134 | 2.953 | 2.953 | 2.9761 | 3.008 | 2.8992 | 3.0518 | 2.9864 | 2.7161 | 2.733 | 3.1082 | 3.2537 | 3.0514 | 2.8465 | 2.9348 | 2.8826 | 3.2533 | 3.6672 | 3.2204 | 3.0664 | 2.8737 | 2.846 | 3.0343 | 2.8858 | 3.04 | 3.5942 | 2.8769 | 2.7712 | 3.324 | 3.0609 | 3.2415 | 3.1929 | 3.2281 | 3.226 | 3.2522 | 3.202 | 3.1877 | 3.2622 | 3.2598 | 3.1991 | 3.0986 | 3.1877 | 3.2038 | 3.1692 | 3.1939 | 3.2388 | 3.2412 | 3.1908 | 3.2325 | 3.2667 | 3.2475 | 3.2678 | 3.2637 | 3.2507 | 3.2075 | 3.2429 | 3.2091 | 3.2271 | 3.1301 | 3.1974 | 3.2026 | 3.236 | 3.2429 | 3.2171 | 3.2333 | 3.1404 | 3.1883 | 3.1569 | 3.2433 | 3.1593 | 3.2484 | 3.3703 | 3.2208 | 3.2816 | 3.2353 | 3.206 | 3.314 | 3.294 | 3.1943 | 3.2453 | 3.232 | 3.2136 | 3.2905 | 3.245 | 3.2688 | 3.2574 | 3.2302 | 3.2681 | 3.2819 | 3.2576 | 3.2771 | 3.3157 | 3.3037 | 3.2543 | 3.3192 | 3.2695 | 3.2709 | 3.246 | 3.2788 | 3.2612 | 3.3019 | 3.236 | 3.2302 | 3.3362 | 3.3492 | 3.2756 | 3.2557 | 3.2588 | 3.2961 | 3.3106 | 3.3043 | 3.2785 | 3.3282 | 3.305 | 3.3182 | 3.2702 | 3.2291 | 3.2813 | 3.3019 | 3.3496 | 3.244 | 3.2553 | 3.2498 | 3.0928 | 3.2716 | 3.2226 | 3.0928 | 3.2488 | 3.0987 | 3.2119 | 3.2784 | 3.3309 | 3.1681 | 3.2029 | 3.2517 | 3.223 | 3.206 | 3.2124 | 3.2128 | 3.2438 | 3.2706 | 3.3001 | 3.2664 | 3.2664 | 3.2759 | 3.2963 | 3.2563 | 3.3131 | 3.1988 | 3.3012 | 3.2899 | 3.3152 | 3.2982 | 3.2676 | 3.2963 | 3.263 | 3.2952 | 3.2188 | 3.2823 | 3.2113 | 3.2608 | 3.2671 | 3.2381 | 3.2901 | 3.2199 | 3.3229 | 3.2743 | 3.2674 | 3.294 | 3.3363 | 3.2532 | 3.3182 | 3.3473 | 3.3462 | 3.261 | 3.1037 | 3.1808 | 3.2674 | 3.1894 | 3.2486 | 3.2841 | 3.332 | 3.334 | 3.3434 | 3.3141 | 3.1724 | 3.1781 | 3.2248 | 3.1713 | 3.1439 | 3.1133 | 3.204 | 3.1324 | 3.1758 | 3.1975 | 3.221 | 3.2053 | 3.2005 | 3.1367 | 3.2563 | 3.1696 | 3.263 | 3.2182 | 3.2111 | 3.2268 | 3.1943 | 3.1625 | 3.173 | 3.182 | 3.2645 | 3.2575 | 3.1817 | 3.1719 | 3.2174 | 3.102 | 3.2033 | 3.17 | 3.1995 | 3.1707 | 3.2466 | 3.2533 | 3.1894 | 3.2033 | 3.2279 | 3.1344 | 3.0794 | 3.2029 | 3.1907 | 3.2273 | 3.244 | 3.1006 | 3.2212 | 3.2782 | 3.2882 | 3.2452 | 3.2814 | 3.2379 | 3.0853 | 3.168 | 3.1924 | 3.1973 | 3.2527 | 3.2566 | 3.2339 | 3.2595 | 3.2478 | 3.1689 | 3.147 | 3.141 | 3.1693 | 3.0748 | 3.0933 | 3.1319 | 3.0658 | 3.0824 | 3.1708 | 3.1242 | 3.1765 | 3.1629 | 3.1778 | 3.1563 | 3.1528 | 3.153 | 3.156 | 3.1695 | 3.1619 | 3.1923 | 3.1395 | 3.1653 | 3.1487 | 3.226 | 3.1725 | 3.2122 | 3.1915 | 3.206 | 3.2008 | 3.1897 | 3.2174 | 3.1128 | 3.2067 | 3.1311 | 3.1035 | 3.1079 | 3.1373 | 3.0608 | 3.1057 | 3.1126 | 3.1079 | 3.1095 | 3.1573 | 3.13 | 3.0795 | 3.1322 | 3.1412 | 3.1648 | 3.1618 | 3.1111 | 3.1574 | 3.1915 | 3.221 | 3.2457 | 3.2304 | 3.0979 | 3.1244 | 3.1633 | 3.0564 | 3.1274 | 3.1577 | 3.1278 | 3.155 | 3.1771 | 3.1266 | 3.1024 | 3.1122 | 3.1812 | 3.1604 | 3.1554 | 3.2096 | 3.1558 | 3.1558 | 3.1595 | 3.1954 | 3.0298 | 3.1906 | 3.1786 | 3.1417 | 3.1831 | 3.1523 | 3.1849 | 3.2066 | 3.2268 | 3.219 | 3.2104 | 3.184
2025-05-20 | 1.7759 | 1.7249 | 1.7962 | 1.8 | 1.7697 | 1.7001 | 1.8462 | 1.7182 | 1.8076 | 1.8159 | 1.8098 | 1.7992 | 1.8136 | 1.8167 | 1.8371 | 1.8235 | 1.7998 | 1.8309 | 1.8235 | 1.8394 | 1.8947 | 1.8727 | 1.8902 | 1.872 | 1.8803 | 1.8606 | 1.897 | 1.8826 | 1.9152 | 1.903 | 1.8727 | 1.8758 | 1.7909 | 1.7663 | 1.7703 | 1.799 | 1.8198 | 1.8102 | 1.7886 | 1.8174 | 1.7727 | 1.8203 | 1.8662 | 1.8421 | 1.8692 | 1.919 | 1.9176 | 1.9093 | 1.8447 | 1.8765 | 1.8798 | 1.8202 | 1.7821 | 1.7964 | 1.7797 | 1.8223 | 1.8407 | 1.7511 | 1.7588 | 1.7364 | 1.8917 | 1.8846 | 1.6532 | 1.9596 | 1.921 | 1.9484 | 1.9424 | 1.9758 | 1.9381 | 1.9279 | 1.9683 | 1.9879 | 1.9355 | 1.9263 | 1.9337 | 1.943 | 1.9138 | 1.9117 | 1.9451 | 1.9413 | 1.9189 | 1.954 | 1.9658 | 1.952 | 1.9831 | 1.9737 | 1.9661 | 1.9533 | 1.9603 | 1.9365 | 1.9379 | 1.9217 | 1.9438 | 1.9579 | 1.9655 | 1.9893 | 1.9848 | 1.9748 | 1.9286 | 1.9239 | 1.9253 | 1.9651 | 1.9106 | 1.9824 | 2.0524 | 1.9752 | 1.9931 | 1.9638 | 1.9275 | 2.0066 | 1.9938 | 2.0159 | 1.9864 | 1.9693 | 1.9279 | 1.9845 | 1.9596 | 1.9548 | 1.9496 | 1.9168 | 1.951 | 1.9658 | 1.9398 | 1.9527 | 1.9831 | 1.9748 | 1.9306 | 1.9779 | 1.9389 | 1.9462 | 1.9413 | 1.9624 | 1.9658 | 1.9931 | 1.9507 | 1.952 | 2.0137 | 2.0221 | 1.9952 | 1.9576 | 1.9562 | 1.9962 | 2.0021 | 1.9848 | 1.9724 | 2.0035 | 2.0038 | 2.0382 | 1.9851 | 1.9571 | 2.0198 | 1.9993 | 2.0359 | 1.9876 | 1.9814 | 1.9676 | 1.9803 | 1.9824 | 1.9938 | 1.9658 | 1.9689 | 1.9731 | 1.9444 | 2.0017 | 2.0307 | 1.9654 | 1.9441 | 1.9837 | 1.9535 | 1.9497 | 1.9645 | 1.9528 | 1.9675 | 1.9913 | 2.0125 | 1.9932 | 1.9909 | 2.0045 | 2.0178 | 1.9742 | 2.0101 | 1.9776 | 2.0159 | 2.0155 | 2.0223 | 2.0053 | 1.9928 | 2.0132 | 1.997 | 2.0106 | 1.9637 | 2.0008 | 1.9679 | 1.9883 | 1.9857 | 1.9702 | 2.0187 | 1.947 | 1.9936 | 1.9619 | 1.9751 | 1.9965 | 2.0158 | 1.9689 | 2.0104 | 2.0279 | 2.0285 | 1.9844 | 1.9873 | 1.9788 | 1.9825 | 1.9552 | 1.9783 | 1.998 | 1.9973 | 2.0231 | 2.0061 | 1.9872 | 1.9558 | 1.9411 | 1.9733 | 1.9428 | 1.9019 | 1.8989 | 1.9664 | 1.9324 | 1.9481 | 1.9844 | 1.9808 | 1.9721 | 1.9706 | 1.9212 | 1.9973 | 1.9526 | 2.0106 | 1.9827 | 1.9816 | 1.9874 | 1.9358 | 1.9313 | 1.9384 | 1.9504 | 2.0455 | 2.0408 | 1.9831 | 1.9769 | 1.9898 | 1.9242 | 1.9717 | 1.9444 | 1.9821 | 1.9522 | 2.0191 | 1.9904 | 1.9541 | 1.9649 | 1.9829 | 1.9134 | 1.8892 | 1.9258 | 1.9266 | 1.9527 | 1.9656 | 1.9478 | 1.9448 | 1.957 | 1.9555 | 1.9326 | 1.9548 | 1.9666 | 1.9137 | 1.916 | 1.9497 | 1.9404 | 2.3766 | 1.9523 | 1.9453 | 1.9417 | 1.6933 | 1.907 | 1.8878 | 1.8738 | 1.884 | 1.8462 | 1.8605 | 1.8836 | 1.8579 | 1.8617 | 1.9335 | 1.8965 | 1.9184 | 1.9169 | 1.9444 | 1.902 | 1.8718 | 1.8763 | 1.9239 | 1.8969 | 1.8976 | 1.9268 | 1.8692 | 1.898 | 1.8832 | 1.9291 | 1.9143 | 1.914 | 1.9166 | 1.9497 | 1.929 | 1.9139 | 1.9627 | 1.9142 | 1.9425 | 1.8935 | 1.8801 | 1.8853 | 1.9218 | 1.8566 | 1.9582 | 1.9327 | 1.8697 | 1.9023 | 1.9608 | 1.9406 | 1.9223 | 1.9317 | 1.9354 | 1.9347 | 1.9555 | 1.9156 | 1.9474 | 1.9243 | 2.0071 | 1.9976 | 2.0133 | 1.8992 | 1.895 | 1.9489 | 1.8524 | 1.9055 | 1.9347 | 1.8879 | 1.9291 | 1.9511 | 1.8977 | 1.8426 | 1.8721 | 1.9384 | 1.8987 | 1.9121 | 1.9545 | 1.9388 | 1.9021 | 1.9018 | 1.9415 | 1.8282 | 1.9421 | 1.9266 | 1.8972 | 1.9175 | 1.898 | 1.9509 | 1.9289 | 1.9427 | 1.96 | 1.9325 | 1.9316
2025-05-21 | 1.2337 | 1.1954 | 1.2515 | 1.25 | 1.2258 | 1.1754 | 1.2884 | 1.1924 | 1.2561 | 1.2348 | 1.2621 | 1.2508 | 1.2583 | 1.247 | 1.2742 | 1.2689 | 1.2368 | 1.2759 | 1.2689 | 1.2795 | 1.3205 | 1.3045 | 1.2985 | 1.2939 | 1.2886 | 1.2848 | 1.3242 | 1.3167 | 1.3402 | 1.3189 | 1.3098 | 1.2765 | 1.2356 | 1.2113 | 1.2185 | 1.2376 | 1.2576 | 1.2329 | 1.2242 | 1.2624 | 1.2265 | 1.2682 | 1.2954 | 1.2734 | 1.2734 | 1.2735 | 1.2299 | 1.3313 | 1.1974 | 1.455 | 1.3644 | 1.2799 | 1.2482 | 1.1925 | 1.2452 | 1.2414 | 1.1996 | 1.3352 | 1.377 | 1.2239 | 1.3152 | 1.3169 | 1.2463 | 1.3678 | 1.343 | 1.3659 | 1.3575 | 1.3816 | 1.3506 | 1.3478 | 1.3775 | 1.3882 | 1.354 | 1.3438 | 1.3502 | 1.3539 | 1.3351 | 1.3268 | 1.3654 | 1.3654 | 1.3458 | 1.3697 | 1.3758 | 1.3658 | 1.3872 | 1.3752 | 1.3741 | 1.362 | 1.372 | 1.3565 | 1.3558 | 1.3309 | 1.3523 | 1.3616 | 1.3716 | 1.3865 | 1.3829 | 1.3775 | 1.3689 | 1.3395 | 1.3359 | 1.3716 | 1.3254 | 1.3861 | 1.4331 | 1.3692 | 1.393 | 1.3689 | 1.3468 | 1.4041 | 1.3944 | 1.4051 | 1.3855 | 1.3741 | 1.3537 | 1.3951 | 1.3775 | 1.3768 | 1.3703 | 1.3499 | 1.3709 | 1.3789 | 1.3618 | 1.3719 | 1.3906 | 1.3892 | 1.3558 | 1.3896 | 1.3613 | 1.362 | 1.3575 | 1.3778 | 1.3782 | 1.3937 | 1.3613 | 1.3816 | 1.4073 | 1.4051 | 1.3841 | 1.3578 | 1.3623 | 1.3834 | 1.3896 | 1.3823 | 1.3703 | 1.3923 | 1.3913 | 1.3903 | 1.3773 | 1.3571 | 1.3774 | 1.3906 | 1.4085 | 1.3803 | 1.3879 | 1.3706 | 1.3882 | 1.3858 | 1.3485 | 1.3647 | 1.3723 | 1.3613 | 1.3544 | 1.4024 | 1.422 | 1.3452 | 1.3341 | 1.3689 | 1.339 | 1.345 | 1.3571 | 1.3522 | 1.3507 | 1.3704 | 1.3919 | 1.3707 | 1.3651 | 1.387 | 1.3991 | 1.3603 | 1.3836 | 1.3644 | 1.3874 | 1.3885 | 1.3934 | 1.3768 | 1.3692 | 1.3832 | 1.3757 | 1.3783 | 1.3477 | 1.3738 | 1.3575 | 1.3689 | 1.3643 | 1.3536 | 1.3948 | 1.3443 | 1.3775 | 1.3611 | 1.365 | 1.3764 | 1.3855 | 1.3658 | 1.391 | 1.4035 | 1.3989 | 1.3708 | 1.3726 | 1.3673 | 1.3654 | 1.392 | 1.3377 | 1.3803 | 1.3815 | 1.3925 | 1.384 | 1.3649 | 1.335 | 1.3369 | 1.3668 | 1.3348 | 1.3025 | 1.3056 | 1.3499 | 1.3265 | 1.3433 | 1.3711 | 1.3744 | 1.3591 | 1.3595 | 1.3134 | 1.387 | 1.3534 | 1.3909 | 1.3638 | 1.3689 | 1.3834 | 1.34 | 1.3284 | 1.3437 | 1.3411 | 1.4231 | 1.4286 | 1.3732 | 1.3512 | 1.3713 | 1.3224 | 1.3599 | 1.3348 | 1.3662 | 1.34 | 1.4155 | 1.3725 | 1.3385 | 1.3534 | 1.3624 | 1.3433 | 1.3193 | 1.3525 | 1.3496 | 1.3733 | 1.3811 | 1.3451 | 1.3636 | 1.3736 | 1.3712 | 1.3586 | 1.3726 | 1.3803 | 1.3379 | 1.3392 | 1.3641 | 1.3514 | 1.6719 | 1.3588 | 1.3651 | 1.3674 | 1.3665 | 1.3364 | 1.325 | 1.3065 | 1.3061 | 1.2929 | 1.3023 | 1.3167 | 1.2952 | 1.2918 | 1.3492 | 1.3226 | 1.3375 | 1.3394 | 1.3575 | 1.3333 | 1.2956 | 1.3075 | 1.3474 | 1.328 | 1.3231 | 1.3512 | 1.3049 | 1.3295 | 1.311 | 1.3489 | 1.3394 | 1.3371 | 1.3345 | 1.3639 | 1.344 | 1.3361 | 1.396 | 1.3221 | 1.3639 | 1.3269 | 1.3134 | 1.3146 | 1.3413 | 1.2869 | 1.3733 | 1.3547 | 1.29 | 1.3305 | 1.3856 | 1.3714 | 1.3549 | 1.3609 | 1.3684 | 1.3751 | 1.3802 | 1.3458 | 1.367 | 1.3721 | 1.4089 | 1.4129 | 1.418 | 1.3071 | 1.3067 | 1.3519 | 1.2843 | 1.306 | 1.337 | 1.3269 | 1.334 | 1.3587 | 1.3108 | 1.3367 | 1.3776 | 1.3561 | 1.3241 | 1.3222 | 1.3642 | 1.3437 | 1.3172 | 1.3209 | 1.3352 | 1.3194 | 1.3411 | 1.3479 | 1.3171 | 1.3269 | 1.3151 | 1.3591 | 1.3369 | 1.3646 | 1.3728 | 1.3391 | 1.3443
2025-05-22 | 2.7648 | 2.7225 | 2.8076 | 2.8152 | 2.7826 | 2.6796 | 2.8822 | 2.6955 | 2.8235 | 2.8636 | 2.8273 | 2.8091 | 2.8773 | 2.8576 | 2.9068 | 2.8879 | 2.8254 | 2.8581 | 2.8182 | 2.8636 | 2.9371 | 2.903 | 2.9242 | 2.9462 | 2.9045 | 2.8742 | 2.9295 | 2.9189 | 2.9614 | 2.95 | 2.9038 | 2.9061 | 2.8455 | 2.8054 | 2.8238 | 2.8533 | 2.8987 | 2.8812 | 2.8462 | 2.8892 | 2.8295 | 2.8994 | 2.975 | 2.9554 | 2.9642 | 3.0203 | 3.0194 | 2.996 | 2.9108 | 2.9184 | 2.9582 | 2.8891 | 2.8579 | 2.8144 | 2.7756 | 2.86 | 2.8595 | 2.7454 | 2.738 | 2.7281 | 2.828 | 2.7922 | 2.8805 | 2.3851 | 2.3351 | 2.9913 | 2.9821 | 2.3464 | 2.3577 | 2.3371 | 2.4155 | 2.4213 | 2.3368 | 2.3266 | 2.342 | 2.3492 | 2.3196 | 2.3454 | 2.3927 | 3.0255 | 2.342 | 2.3942 | 2.4103 | 2.3921 | 2.4234 | 2.3965 | 2.4044 | 2.3757 | 3.0131 | 2.3782 | 2.3716 | 2.313 | 2.3716 | 2.3858 | 2.4227 | 2.4331 | 2.4273 | 3.0421 | 2.4006 | 2.3575 | 2.3387 | 2.4189 | 2.302 | 2.4358 | 2.5197 | 2.3982 | 2.4369 | 2.3879 | 2.9727 | 2.4655 | 2.4438 | 2.462 | 2.9562 | 2.403 | 2.3665 | 2.4231 | 2.3961 | 2.3944 | 3.0487 | 2.3485 | 2.3865 | 2.3989 | 2.3701 | 2.3813 | 3.0945 | 3.1118 | 3.0273 | 3.1077 | 3.0449 | 3.0566 | 2.3471 | 3.0904 | 2.3841 | 2.4113 | 2.3658 | 2.4144 | 3.1699 | 3.2126 | 2.4375 | 2.3968 | 3.099 | 2.4417 | 2.4517 | 3.1529 | 2.4262 | 2.4531 | 2.4448 | 2.4437 | 2.4196 | 3.0956 | 2.4071 | 2.4496 | 2.4766 | 2.3937 | 2.421 | 2.3913 | 3.1384 | 2.3992 | 2.3989 | 2.3706 | 2.3854 | 2.3744 | 3.0711 | 2.4471 | 3.1943 | 2.3806 | 3.1387 | 3.1897 | 3.1489 | 3.1489 | 3.1531 | 3.1387 | 3.1444 | 3.1784 | 3.206 | 3.1757 | 3.1992 | 3.2135 | 3.2184 | 3.1679 | 3.2143 | 3.1284 | 3.2147 | 3.1946 | 3.2173 | 3.1984 | 3.1648 | 3.2052 | 3.167 | 3.195 | 3.1224 | 3.189 | 3.1073 | 3.1788 | 3.1651 | 3.1278 | 3.204 | 2.3681 | 2.4331 | 3.1248 | 2.451 | 2.4493 | 2.4654 | 2.4464 | 2.4715 | 3.2436 | 3.2523 | 3.1654 | 3.1747 | 3.1648 | 3.1534 | 3.1929 | 3.1351 | 3.1621 | 2.447 | 2.4785 | 2.4544 | 2.418 | 2.2861 | 2.3712 | 3.1683 | 2.381 | 2.3239 | 3.0529 | 2.4004 | 2.3981 | 3.1105 | 3.1408 | 3.1425 | 3.1484 | 3.1087 | 3.047 | 3.168 | 3.0915 | 3.2123 | 3.1699 | 3.155 | 3.1617 | 3.1079 | 3.0803 | 3.0784 | 3.0866 | 3.2194 | 3.2339 | 3.1032 | 3.1154 | 3.1684 | 3.0896 | 3.1393 | 3.0964 | 3.1225 | 3.102 | 3.1973 | 3.1793 | 3.1016 | 3.1139 | 3.1487 | 2.3027 | 2.2569 | 2.3316 | 2.2022 | 2.3631 | 2.3868 | 2.3679 | 3.0906 | 2.378 | 2.3664 | 2.362 | 2.3737 | 3.123 | 2.3128 | 2.3266 | 2.3707 | 2.3348 | 2.3626 | 2.3884 | 2.3671 | 2.3692 | 2.368 | 3.0268 | 3.0144 | 3.0159 | 3.0355 | 2.9637 | 2.9849 | 3.0023 | 2.9592 | 2.969 | 3.0635 | 3.0407 | 3.0601 | 3.054 | 3.0706 | 3.0278 | 3.0091 | 2.9901 | 3.0441 | 3.0125 | 3.0118 | 3.0463 | 3.0125 | 3.0038 | 3.0019 | 3.0637 | 3.0254 | 3.0696 | 3.0501 | 3.099 | 3.0742 | 3.0579 | 3.1075 | 2.9933 | 3.0825 | 3.0115 | 2.9846 | 3.0014 | 3.0274 | 2.9646 | 3.0508 | 3.0423 | 2.9925 | 3.0145 | 3.0728 | 3.041 | 3.0048 | 3.0549 | 3.0399 | 3.0698 | 3.0823 | 3.0334 | 3.0777 | 3.1362 | 3.148 | 3.1633 | 3.1578 | 3.0115 | 3.0126 | 3.0616 | 2.9383 | 3.022 | 3.0564 | 3.0048 | 3.0571 | 3.0885 | 3.0362 | 3.0671 | 3.0926 | 3.0866 | 3.0546 | 3.051 | 3.1005 | 3.068 | 3.0463 | 3.0485 | 3.0852 | 3.0377 | 3.0822 | 3.0648 | 3.0349 | 3.0616 | 3.0361 | 3.0695 | 3.0757 | 3.1036 | 3.1119 | 3.1068 | 2.8292
2025-05-23 | 4.5486 | 4.4234 | 4.6174 | 4.5833 | 4.4727 | 4.3812 | 4.7314 | 4.4242 | 4.5765 | 4.6008 | 4.6561 | 4.6364 | 4.5735 | 4.6129 | 4.6636 | 4.6795 | 4.618 | 4.6699 | 4.6197 | 4.7008 | 4.8598 | 4.7803 | 4.8258 | 4.8227 | 4.7939 | 4.7364 | 4.8045 | 4.7621 | 4.8811 | 4.8591 | 4.7856 | 4.7689 | 4.4833 | 4.4705 | 4.5008 | 4.5271 | 4.6085 | 4.6499 | 4.5083 | 4.5829 | 4.5 | 4.5514 | 4.6609 | 4.6294 | 4.6499 | 4.7489 | 4.7386 | 4.7251 | 4.5972 | 4.7411 | 4.7375 | 4.6439 | 4.6162 | 4.5783 | 4.518 | 4.5549 | 4.6042 | 4.3787 | 4.4361 | 4.4033 | 4.6788 | 4.5589 | 4.5887 | 4.9834 | 4.8858 | 5.0228 | 5.0217 | 4.9558 | 4.9207 | 4.823 | 5 | 4.9493 | 4.8275 | 4.7602 | 4.8292 | 4.9383 | 4.8986 | 4.9869 | 4.9903 | 5.0335 | 4.8551 | 4.9497 | 5.1304 | 5.009 | 4.989 | 5.1053 | 4.9888 | 4.8896 | 4.9289 | 4.9924 | 4.9272 | 4.8637 | 4.9683 | 5.05 | 5.1025 | 4.9645 | 4.873 | 5.0259 | 4.9489 | 5.0004 | 4.9683 | 4.972 | 4.8487 | 4.9572 | 5.1653 | 4.9783 | 5.0994 | 4.9344 | 4.9576 | 5.0949 | 5.069 | 5.0583 | 5.133 | 4.8947 | 4.9134 | 4.9382 | 4.9375 | 4.9972 | 5.0445 | 4.9907 | 4.9796 | 4.9099 | 4.9917 | 5.0512 | 4.9634 | 5.0638 | 4.9955 | 5.0842 | 5.0135 | 4.9683 | 4.9317 | 5.0179 | 4.9286 | 5.0169 | 4.9155 | 4.9752 | 5.1169 | 4.9458 | 4.7819 | 4.8299 | 4.8768 | 4.9061 | 4.9103 | 4.97 | 4.8861 | 4.8727 | 4.8375 | 5.0743 | 4.9676 | 4.9592 | 4.9913 | 4.8799 | 5.0265 | 4.8188 | 4.8916 | 4.7899 | 5.0217 | 4.7888 | 4.9044 | 4.8471 | 4.8685 | 4.784 | 4.9386 | 4.8945 | 4.9627 | 4.9365 | 4.8844 | 4.9683 | 4.9516 | 4.9751 | 4.9535 | 5.0057 | 4.9762 | 4.9947 | 5.0204 | 5.0287 | 5.0076 | 5.0181 | 5.0831 | 5.0405 | 5.1358 | 4.9152 | 5.0805 | 5.0661 | 5.0779 | 5.0344 | 5.0268 | 5.0586 | 5.0344 | 5.1304 | 5.0091 | 5.1515 | 4.9868 | 5.0238 | 5.123 | 5.0798 | 5.0417 | 4.9485 | 5.1511 | 5.0687 | 4.9809 | 5.0027 | 5.1243 | 4.9388 | 5.0113 | 5.0958 | 4.9771 | 4.8441 | 4.7624 | 4.9088 | 4.9324 | 4.8647 | 5.016 | 5.1342 | 5.2186 | 5.2006 | 5.2227 | 5.1448 | 4.7962 | 4.8502 | 5.0473 | 4.8577 | 4.7476 | 4.8347 | 4.8521 | 4.7281 | 5.0125 | 4.9971 | 5.0769 | 5.1283 | 4.9407 | 4.8927 | 5.029 | 4.935 | 5.2182 | 5.1566 | 5.1146 | 5.0746 | 4.9578 | 4.9951 | 4.9391 | 4.9907 | 5.2539 | 5.2433 | 5.1177 | 5.1017 | 5.168 | 5.0183 | 5.1126 | 5.0538 | 5.071 | 5.0108 | 5.0434 | 5.1372 | 5.0179 | 5.0606 | 5.034 | 4.9854 | 4.8341 | 4.9785 | 4.9103 | 4.9344 | 4.9542 | 4.9376 | 5.0009 | 5.0767 | 5.1092 | 4.9973 | 5.0289 | 4.937 | 4.7594 | 4.9282 | 4.7486 | 4.8639 | 4.9294 | 5.0004 | 4.8963 | 5.0169 | 4.9897 | 4.9792 | 4.9637 | 4.9633 | 5.0076 | 4.8345 | 4.867 | 4.8987 | 4.8122 | 4.8401 | 4.983 | 4.8192 | 5.0072 | 4.9913 | 5.0274 | 4.8587 | 4.9944 | 4.949 | 5.0084 | 4.9571 | 4.9427 | 4.9848 | 4.846 | 4.989 | 4.9879 | 5.0353 | 5.0095 | 5.0704 | 5.0398 | 4.9683 | 5.0944 | 5.0417 | 5.0467 | 4.8222 | 5.0425 | 4.9166 | 4.8625 | 4.8781 | 4.9492 | 4.829 | 4.9163 | 4.8291 | 4.9266 | 4.9761 | 4.9279 | 4.9331 | 4.8658 | 4.8965 | 4.9406 | 4.9376 | 4.8892 | 4.8987 | 4.894 | 4.9529 | 4.9651 | 4.9804 | 5.0177 | 4.7458 | 4.8464 | 4.8677 | 4.7227 | 4.8595 | 4.8662 | 4.8468 | 4.8636 | 4.9066 | 4.7884 | 4.9133 | 4.9451 | 4.9495 | 4.9707 | 4.9129 | 5.0173 | 4.8801 | 4.8699 | 4.9009 | 5.0334 | 4.8808 | 5.0112 | 4.9294 | 5.0063 | 4.997 | 5.0224 | 4.958 | 5.0289 | 4.9976 | 5.0769 | 4.9678 | 4.9109
2025-05-24 | 3.7153 | 3.6746 | 3.7667 | 3.7811 | 3.6992 | 3.6074 | 3.8653 | 3.6045 | 3.7379 | 3.7848 | 3.7985 | 3.7621 | 3.7811 | 3.7705 | 3.8197 | 3.825 | 3.7679 | 3.799 | 3.7561 | 3.8144 | 3.9242 | 3.8758 | 3.9076 | 3.9015 | 3.8621 | 3.8258 | 3.8962 | 3.8652 | 3.95 | 3.9242 | 3.8682 | 3.8909 | 3.7205 | 3.6882 | 3.7201 | 3.7456 | 3.8078 | 3.8198 | 3.7242 | 3.7871 | 3.7402 | 3.7882 | 3.8606 | 3.8765 | 3.8626 | 3.9493 | 3.9021 | 3.8649 | 3.7555 | 3.8346 | 3.8541 | 3.7585 | 3.7294 | 3.6936 | 3.654 | 3.7271 | 3.7339 | 3.5947 | 3.4002 | 3.596 | 3.7909 | 3.7094 | 3.7427 | 4.0217 | 3.9634 | 4.0426 | 4.0317 | 4.0262 | 4.0021 | 3.9344 | 4.0666 | 4.019 | 3.9555 | 3.8734 | 3.9548 | 3.9939 | 3.9726 | 3.8585 | 4.0031 | 4.0566 | 3.9424 | 3.9778 | 4.0818 | 4.0317 | 4.0304 | 4.0628 | 4.0202 | 3.9589 | 4.0614 | 4.0286 | 4.0124 | 3.8834 | 3.9893 | 4.0321 | 4.0887 | 4.0238 | 3.9876 | 4.0349 | 4.009 | 4.0036 | 3.9632 | 4.0507 | 3.9858 | 4.039 | 4.2277 | 3.9772 | 4.1011 | 3.9955 | 4.0052 | 4.1239 | 4.1035 | 4.0983 | 4.0461 | 3.996 | 3.9714 | 3.9655 | 3.9997 | 4.0338 | 3.9451 | 3.9924 | 4.0245 | 3.9476 | 4.0054 | 4.0437 | 4.0908 | 4.0956 | 4.0107 | 4.1021 | 3.7899 | 4.0055 | 3.9855 | 3.9551 | 4.0017 | 4.0645 | 3.98 | 4.0435 | 3.9711 | 4.0621 | 3.9587 | 3.9714 | 4.0104 | 3.9921 | 4.0217 | 4.0587 | 4.0238 | 3.9952 | 4.0286 | 4.1017 | 4.0638 | 3.9102 | 4.081 | 4.0342 | 4.1251 | 3.97 | 4.0214 | 4.0131 | 4.0908 | 4.0355 | 3.9124 | 3.9044 | 4.0069 | 3.9058 | 3.9831 | 4.0258 | 4.0856 | 3.8698 | 3.9161 | 3.9834 | 3.9471 | 3.9444 | 3.9214 | 3.9683 | 3.9788 | 4.0098 | 4.0423 | 3.9906 | 3.9864 | 4.014 | 4.0397 | 4.0008 | 4.0683 | 3.8929 | 4.031 | 4.0079 | 4.0518 | 4.0306 | 3.9883 | 4.0385 | 3.9811 | 4.0257 | 3.9373 | 4.0265 | 3.963 | 4.0155 | 4.0159 | 4.0012 | 4.0333 | 3.9356 | 4.076 | 4.0404 | 3.994 | 4.011 | 4.0833 | 3.9776 | 4.0294 | 4.0911 | 4.0359 | 3.92 | 3.8918 | 4.0016 | 3.9424 | 3.9535 | 3.9616 | 4.0208 | 4.1107 | 3.9239 | 4.1126 | 4.0768 | 3.8985 | 3.8895 | 4.0081 | 3.8912 | 3.8448 | 3.8584 | 3.8949 | 3.8088 | 3.9182 | 3.9179 | 4.0004 | 3.898 | 3.9867 | 3.8716 | 4.0471 | 3.9347 | 4.0455 | 3.9784 | 3.9894 | 4.0216 | 3.9587 | 3.9202 | 3.9179 | 3.9306 | 4.0302 | 3.956 | 3.8991 | 3.8802 | 3.9662 | 3.8977 | 3.9509 | 3.8962 | 3.943 | 3.9015 | 3.9901 | 4.0013 | 3.9261 | 3.94 | 3.9613 | 3.8683 | 3.8415 | 3.9854 | 3.9622 | 3.9893 | 3.993 | 3.8487 | 3.903 | 4.062 | 4.0673 | 4.0014 | 4.0506 | 4.0057 | 3.8628 | 3.981 | 3.9217 | 3.9688 | 4.0638 | 4.0925 | 3.9885 | 4.1122 | 4.0281 | 3.8915 | 3.898 | 3.8953 | 3.9187 | 3.7177 | 3.8341 | 3.8707 | 3.7993 | 3.8107 | 3.9214 | 3.7954 | 3.938 | 3.9512 | 3.952 | 3.9294 | 3.9242 | 3.8877 | 3.9452 | 3.898 | 3.89 | 3.9499 | 3.8006 | 3.9261 | 3.9151 | 3.9803 | 3.9492 | 3.9962 | 3.9628 | 3.8224 | 4.0179 | 3.9754 | 3.9702 | 3.8206 | 3.9671 | 3.891 | 3.8372 | 3.8544 | 3.8964 | 3.8168 | 3.8884 | 3.8462 | 3.8642 | 3.8909 | 3.9123 | 3.888 | 3.8361 | 3.8966 | 3.903 | 3.9407 | 3.9192 | 3.8803 | 3.9137 | 4.0063 | 4.009 | 4.0502 | 4.0279 | 3.8809 | 3.9916 | 3.9392 | 3.8734 | 3.9123 | 3.9594 | 3.9688 | 3.9575 | 3.8925 | 3.829 | 3.9674 | 3.9757 | 3.9841 | 3.9668 | 3.9631 | 4.0232 | 3.9068 | 3.9639 | 3.9755 | 3.987 | 3.9493 | 3.9673 | 3.9503 | 3.9392 | 3.9643 | 3.9396 | 3.9666 | 4.0242 | 4.0063 | 4.0169 | 4.0086 | 3.9395
2025-05-25 | 3.2121 | 3.1595 | 3.2667 | 3.272 | 3.2053 | 3.0881 | 3.3634 | 3.1288 | 3.2652 | 3.2864 | 3.3129 | 3.278 | 3.2917 | 3.3008 | 3.3417 | 3.3379 | 3.2847 | 3.3349 | 3.303 | 3.3538 | 3.453 | 3.4076 | 3.4273 | 3.4386 | 3.4121 | 3.3705 | 3.4341 | 3.4144 | 3.4803 | 3.4727 | 3.4015 | 3.4159 | 3.2273 | 3.2065 | 3.2313 | 3.2544 | 3.311 | 3.3206 | 3.2364 | 3.3022 | 3.2303 | 3.301 | 3.3773 | 3.3501 | 3.3757 | 3.4537 | 3.4424 | 3.4147 | 3.3515 | 3.3859 | 3.3944 | 3.3183 | 3.2872 | 3.2609 | 3.2251 | 3.3086 | 3.3091 | 3.1634 | 3.1861 | 3.1718 | 3.3076 | 3.2596 | 3.2852 | 3.578 | 3.5114 | 3.5417 | 3.5407 | 3.5894 | 3.5072 | 3.5048 | 3.5801 | 3.5977 | 3.509 | 3.4804 | 3.3147 | 3.5 | 3.4614 | 3.501 | 3.5687 | 3.5669 | 3.4631 | 3.5592 | 3.5977 | 3.5783 | 3.6201 | 3.5841 | 3.6021 | 3.5576 | 3.5635 | 3.56 | 3.5556 | 3.4234 | 3.5214 | 3.5255 | 3.5756 | 3.607 | 3.5889 | 3.5442 | 3.579 | 3.5069 | 3.4812 | 3.599 | 3.5001 | 3.6118 | 3.6808 | 3.5583 | 3.6315 | 3.5507 | 3.5262 | 3.6573 | 3.6418 | 3.6077 | 3.6364 | 3.5801 | 3.5342 | 3.6287 | 3.5904 | 3.5918 | 3.5528 | 3.5138 | 3.5687 | 3.5901 | 3.5588 | 3.5776 | 3.5983 | 3.6046 | 3.53 | 3.6094 | 3.558 | 3.5618 | 3.5473 | 3.5732 | 3.5914 | 3.6194 | 3.5449 | 3.6049 | 3.6385 | 3.5128 | 3.5559 | 3.509 | 3.5152 | 3.5645 | 3.5797 | 3.5562 | 3.548 | 3.5997 | 3.4848 | 3.5931 | 3.5936 | 3.5166 | 3.577 | 3.5959 | 3.6644 | 3.578 | 3.6032 | 3.5687 | 3.5711 | 3.6077 | 3.6032 | 3.5531 | 3.5725 | 3.5707 | 3.4983 | 3.6336 | 3.6656 | 3.5516 | 3.4282 | 3.4894 | 3.4705 | 3.4709 | 3.4701 | 3.4769 | 3.4864 | 3.5295 | 3.5435 | 3.5057 | 3.5091 | 3.5276 | 3.5412 | 3.4929 | 3.5247 | 3.4268 | 3.5351 | 3.5113 | 3.5533 | 3.5351 | 3.4977 | 3.5404 | 3.4868 | 3.5435 | 3.4524 | 3.545 | 3.4811 | 3.517 | 3.5179 | 3.5008 | 3.5155 | 3.4847 | 3.5779 | 3.5224 | 3.5444 | 3.5568 | 3.5862 | 3.544 | 3.5393 | 3.6057 | 3.6192 | 3.5179 | 3.5432 | 3.5277 | 3.5226 | 3.5517 | 3.5299 | 3.5565 | 3.593 | 3.5124 | 3.5937 | 3.5562 | 3.437 | 3.3566 | 3.5258 | 3.4707 | 3.4022 | 3.4052 | 3.5031 | 3.4485 | 3.4915 | 3.5108 | 3.5302 | 3.5267 | 3.5196 | 3.4357 | 3.5687 | 3.4855 | 3.5699 | 3.5204 | 3.5263 | 3.5392 | 3.4578 | 3.4548 | 3.4133 | 3.4563 | 3.5683 | 3.5636 | 3.4529 | 3.4686 | 3.5024 | 3.4286 | 3.471 | 3.4253 | 3.4806 | 3.4376 | 3.4761 | 3.4918 | 3.4481 | 3.466 | 3.4862 | 3.5711 | 3.4673 | 3.569 | 3.5561 | 3.5585 | 3.6287 | 3.4902 | 3.6011 | 3.6139 | 3.5998 | 3.5909 | 3.5985 | 3.6272 | 3.5076 | 3.5201 | 3.5754 | 3.5338 | 3.5719 | 3.5972 | 3.5803 | 3.6206 | 3.5782 | 3.4512 | 3.4441 | 3.4562 | 3.4751 | 3.3946 | 3.4187 | 3.4373 | 3.3794 | 3.3885 | 3.4932 | 3.5386 | 3.5038 | 3.5053 | 3.5075 | 3.4524 | 3.454 | 3.4296 | 3.4833 | 3.4384 | 3.4463 | 3.4827 | 3.5583 | 3.4645 | 3.4611 | 3.5207 | 3.4835 | 3.5073 | 3.5131 | 3.5461 | 3.5421 | 3.4952 | 3.478 | 3.4202 | 3.5194 | 3.4911 | 3.4485 | 3.4238 | 3.4532 | 3.3938 | 3.4361 | 3.4583 | 3.4376 | 3.4415 | 3.5135 | 3.4507 | 3.4115 | 3.4421 | 3.429 | 3.4032 | 3.5326 | 3.4195 | 3.4784 | 3.4164 | 3.5459 | 3.5322 | 3.5133 | 3.4044 | 3.4974 | 3.46 | 3.3573 | 3.4436 | 3.469 | 3.4679 | 3.475 | 3.5131 | 3.4615 | 3.4949 | 3.4929 | 3.5195 | 3.4673 | 3.4835 | 3.5228 | 3.4355 | 3.4421 | 3.4462 | 3.478 | 3.4765 | 3.4862 | 3.4408 | 3.4101 | 3.4709 | 3.4219 | 3.4592 | 3.49 | 3.5024 | 3.5039 | 3.5302 | 3.4836
2025-05-26 | 2.067 | 2.0311 | 2.1038 | 2.1053 | 2.0689 | 1.9848 | 2.1699 | 2.0114 | 2.1144 | 2.1121 | 2.1295 | 2.1114 | 2.1205 | 2.1205 | 2.1545 | 2.1455 | 2.1077 | 2.1547 | 2.1364 | 2.1568 | 2.225 | 2.1932 | 2.2189 | 2.2159 | 2.1947 | 2.1674 | 2.2182 | 2.1939 | 2.2485 | 2.2356 | 2.1902 | 2.1788 | 2.0818 | 2.0646 | 2.0774 | 2.0989 | 2.1276 | 2.1284 | 2.0788 | 2.1324 | 2.0879 | 2.1341 | 2.1865 | 2.163 | 2.1959 | 2.2496 | 2.2446 | 2.2339 | 2.1736 | 2.2017 | 2.206 | 2.1545 | 2.1277 | 2.1077 | 2.0912 | 2.1386 | 2.1606 | 2.0575 | 2.0703 | 2.0549 | 2.1182 | 2.1178 | 2.1371 | 2.2912 | 2.2488 | 2.2748 | 2.2681 | 2.3057 | 2.2554 | 2.2478 | 2.3043 | 2.3185 | 2.2647 | 2.2473 | 2.2633 | 2.2579 | 2.2334 | 2.245 | 2.2902 | 2.293 | 2.2136 | 2.2913 | 2.3057 | 2.2835 | 2.3237 | 2.3009 | 2.3027 | 2.2775 | 2.2902 | 2.2754 | 2.2747 | 2.2112 | 2.2409 | 2.2636 | 2.2823 | 2.2985 | 2.2937 | 2.2895 | 2.2798 | 2.2201 | 2.2085 | 2.2788 | 2.2167 | 2.3026 | 2.3775 | 2.2733 | 2.3237 | 2.2767 | 2.2405 | 2.3406 | 2.3302 | 2.3364 | 2.3186 | 2.2991 | 2.2647 | 2.3302 | 2.3085 | 2.3019 | 2.285 | 2.2402 | 2.2881 | 2.3147 | 2.2861 | 2.2969 | 2.3244 | 2.3271 | 2.2729 | 2.3268 | 2.2836 | 2.2885 | 2.2816 | 2.305 | 2.3171 | 2.3399 | 2.2864 | 2.3199 | 2.3575 | 2.2981 | 2.3187 | 2.2843 | 2.2895 | 2.3219 | 2.3395 | 2.3178 | 2.3054 | 2.3433 | 2.3323 | 2.3319 | 2.3198 | 2.2778 | 2.3099 | 2.3354 | 2.376 | 2.3192 | 2.3313 | 2.3037 | 2.3251 | 2.3292 | 2.3278 | 2.2912 | 2.3023 | 2.3071 | 2.2643 | 2.3542 | 2.3778 | 2.2944 | 2.2574 | 2.3095 | 2.2816 | 2.2902 | 2.305 | 2.2989 | 2.2989 | 2.3303 | 2.3526 | 2.3231 | 2.3193 | 2.339 | 2.3545 | 2.3067 | 2.3399 | 2.2821 | 2.3481 | 2.3348 | 2.3545 | 2.3348 | 2.3141 | 2.3443 | 2.3148 | 2.3367 | 2.2706 | 2.3292 | 2.2955 | 2.3239 | 2.3147 | 2.2992 | 2.3433 | 2.2521 | 2.3137 | 2.2869 | 2.2973 | 2.3077 | 2.3298 | 2.3008 | 2.3248 | 2.3538 | 2.3541 | 2.2877 | 2.2988 | 2.2905 | 2.2947 | 2.3678 | 2.2796 | 2.3026 | 2.3148 | 2.3377 | 2.3226 | 2.5815 | 2.2671 | 2.2529 | 2.296 | 2.253 | 2.2008 | 2.2062 | 2.2716 | 2.2325 | 2.2677 | 2.2981 | 2.3073 | 2.2991 | 2.3002 | 2.2288 | 2.3367 | 2.2815 | 2.3336 | 2.3073 | 2.3069 | 2.3246 | 2.2868 | 2.2587 | 2.2774 | 2.2692 | 2.3477 | 2.3548 | 2.2673 | 2.2737 | 2.3002 | 2.2281 | 2.2802 | 2.2408 | 2.2995 | 2.2625 | 2.3383 | 2.3017 | 2.2741 | 2.2875 | 2.3006 | 2.2717 | 2.2081 | 2.2681 | 2.264 | 2.303 | 2.3168 | 2.2847 | 2.3007 | 2.3006 | 2.2957 | 2.2927 | 2.3056 | 2.3241 | 2.2427 | 2.2455 | 2.2836 | 2.2544 | 2.285 | 2.3016 | 2.2934 | 2.3193 | 2.2963 | 2.2536 | 2.237 | 2.2343 | 2.2536 | 2.2181 | 2.2415 | 2.2283 | 2.1965 | 2.2139 | 2.2782 | 2.3043 | 2.2744 | 2.271 | 2.2944 | 2.2722 | 2.0595 | 2.2275 | 2.2763 | 2.2548 | 2.2514 | 2.2821 | 2.2177 | 2.2605 | 2.2579 | 2.2924 | 2.2837 | 2.2834 | 2.2856 | 2.3171 | 2.3036 | 2.2754 | 2.3261 | 2.2695 | 2.3127 | 2.2804 | 2.2498 | 2.2311 | 2.2563 | 2.2147 | 2.2793 | 2.2756 | 2.2296 | 2.2578 | 2.3264 | 2.2927 | 2.2662 | 2.2617 | 2.2703 | 2.2819 | 2.3174 | 2.2488 | 2.2912 | 2.2885 | 2.3454 | 2.3548 | 2.3305 | 2.2326 | 2.2797 | 2.2793 | 2.1892 | 2.2531 | 2.2662 | 2.2565 | 2.2666 | 2.295 | 2.2423 | 2.2775 | 2.3077 | 2.2845 | 2.2416 | 2.2673 | 2.3034 | 2.2635 | 2.2449 | 2.255 | 2.272 | 2.2677 | 2.2797 | 2.2674 | 2.2327 | 2.2595 | 2.2465 | 2.2806 | 2.2701 | 2.2951 | 2.3034 | 2.2873 | 2.2633
2025-05-27 | 4.3724 | 4.327 | 4.4409 | 4.4591 | 4.3924 | 4.2711 | 4.5631 | 4.275 | 4.4273 | 4.4902 | 4.5015 | 4.4538 | 4.4833 | 4.4803 | 4.5326 | 4.528 | 4.4737 | 4.4904 | 4.4439 | 4.5121 | 4.6129 | 4.5485 | 4.5879 | 4.6045 | 4.5621 | 4.4871 | 4.5614 | 4.4492 | 4.6576 | 4.6227 | 4.5182 | 4.5439 | 4.4265 | 4.3844 | 4.4179 | 4.4585 | 4.5311 | 4.5423 | 4.4432 | 4.5152 | 4.4689 | 4.5029 | 4.5589 | 4.6352 | 4.625 | 4.6932 | 4.5851 | 4.5517 | 4.3068 | 4.4773 | 4.5682 | 4.4583 | 4.381 | 4.3202 | 4.2638 | 4.3268 | 4.3394 | 4.2349 | 4.1757 | 4.1961 | 4.4136 | 4.324 | 4.4729 | 4.6232 | 4.5859 | 4.7892 | 4.7084 | 4.6356 | 4.6947 | 4.519 | 4.7447 | 4.6263 | 4.5694 | 4.4931 | 4.5528 | 4.6613 | 4.6288 | 4.6249 | 4.6422 | 4.7836 | 4.5079 | 4.5632 | 4.7581 | 4.6281 | 4.5945 | 4.6836 | 4.6021 | 4.5267 | 4.783 | 4.648 | 4.6294 | 4.4993 | 4.6025 | 4.7264 | 4.7543 | 4.6791 | 4.5127 | 4.6425 | 4.6753 | 4.6075 | 4.6306 | 4.6694 | 4.6525 | 4.6222 | 4.6111 | 4.5728 | 4.7391 | 4.6049 | 4.6073 | 4.7571 | 4.746 | 4.6184 | 4.763 | 4.5711 | 4.5524 | 4.5418 | 4.5587 | 4.6291 | 4.6498 | 4.6477 | 4.597 | 4.5373 | 4.5963 | 4.6775 | 4.7402 | 4.7602 | 4.6729 | 4.7778 | 4.5169 | 4.5769 | 4.5511 | 4.754 | 4.5366 | 4.6922 | 4.5649 | 4.5145 | 4.675 | 4.8968 | 4.6997 | 4.7802 | 4.8737 | 4.8012 | 4.8309 | 4.9693 | 4.7823 | 4.883 | 4.5459 | 4.9957 | 4.8194 | 4.8236 | 4.8905 | 4.735 | 4.777 | 4.6049 | 4.658 | 4.726 | 4.8178 | 4.5383 | 4.4952 | 4.5393 | 4.6922 | 4.6608 | 4.8019 | 4.5962 | 4.7267 | 4.6999 | 5.0147 | 5.0673 | 5.0087 | 4.9815 | 4.6005 | 4.9467 | 4.9429 | 4.9501 | 4.9637 | 4.9331 | 5.0506 | 5.0522 | 5.0128 | 5.0679 | 5.1248 | 4.7583 | 4.9683 | 4.9203 | 4.958 | 4.9259 | 4.8817 | 4.9203 | 4.8828 | 4.9093 | 4.8254 | 4.8983 | 4.7914 | 4.8522 | 4.9262 | 4.9032 | 4.9595 | 4.7673 | 5.0245 | 5.0616 | 4.9276 | 4.9976 | 4.8558 | 4.8146 | 4.5359 | 4.8835 | 5.0444 | 4.9429 | 4.8972 | 5.0774 | 5.0543 | 5.0226 | 4.8188 | 5.0145 | 5.0844 | 5.0869 | 5.1504 | 4.8387 | 4.8352 | 4.9343 | 5.1433 | 4.8898 | 4.8013 | 4.9498 | 4.7835 | 4.6376 | 4.609 | 4.6307 | 4.8077 | 4.8093 | 4.7241 | 4.6247 | 4.8359 | 4.7114 | 4.8834 | 4.8281 | 4.8191 | 4.8454 | 4.7141 | 4.6389 | 4.6883 | 4.735 | 4.8823 | 4.8862 | 4.7767 | 4.7462 | 4.8465 | 4.7888 | 4.8768 | 4.874 | 4.7634 | 4.7541 | 4.8684 | 5.0071 | 4.7683 | 4.7982 | 4.8303 | 4.6589 | 4.55 | 4.6966 | 4.6407 | 4.5479 | 4.5964 | 4.51 | 4.5259 | 4.7278 | 4.7369 | 4.6116 | 4.6682 | 4.5588 | 4.4661 | 4.6429 | 4.506 | 4.603 | 4.7881 | 4.8121 | 4.5533 | 4.8521 | 4.65 | 4.6973 | 4.6776 | 4.6602 | 4.6939 | 4.5571 | 4.0461 | 4.6311 | 4.5582 | 4.5654 | 4.6546 | 4.5131 | 4.6576 | 4.6436 | 4.7393 | 4.7083 | 4.6933 | 4.6104 | 4.6267 | 4.5912 | 4.5738 | 4.6105 | 4.531 | 4.5958 | 4.598 | 4.6367 | 4.6151 | 4.7845 | 4.6401 | 4.2491 | 4.7306 | 4.6865 | 4.8163 | 4.5734 | 4.7179 | 4.7017 | 4.6576 | 4.6173 | 4.7075 | 4.6769 | 4.6434 | 4.564 | 4.7233 | 4.7637 | 4.7099 | 4.6961 | 4.6158 | 4.6572 | 4.6849 | 4.7447 | 4.6415 | 4.6892 | 4.7005 | 4.7838 | 4.7971 | 4.8312 | 4.8277 | 4.7335 | 4.7881 | 4.7967 | 4.6797 | 4.76 | 4.7518 | 4.775 | 4.7716 | 4.6587 | 4.6415 | 4.8116 | 4.8077 | 4.7709 | 4.8521 | 4.8254 | 4.8823 | 4.7292 | 4.834 | 4.8273 | 4.9027 | 4.7577 | 4.8359 | 4.7538 | 4.8575 | 4.8423 | 4.8685 | 4.8485 | 4.7352 | 4.5479 | 4.8995 | 4.5389 | 4.6898
2025-05-28 | 4.8014 | 4.7153 | 4.8659 | 4.8545 | 4.8227 | 4.6712 | 4.9862 | 4.6962 | 4.8447 | 4.8955 | 4.9083 | 4.8629 | 4.8523 | 4.8811 | 4.928 | 4.9159 | 4.8692 | 4.9187 | 4.8644 | 4.9295 | 5.0689 | 4.997 | 5.0705 | 5.0576 | 5.0076 | 4.9477 | 5.0227 | 4.9121 | 5.0886 | 5.072 | 4.9803 | 4.9902 | 4.7561 | 4.7632 | 4.8046 | 4.8126 | 4.882 | 4.9171 | 4.7803 | 4.8549 | 4.7689 | 4.7696 | 4.9202 | 4.9189 | 4.9218 | 5.0347 | 4.9705 | 4.9315 | 4.7903 | 4.8932 | 4.9098 | 4.8093 | 4.767 | 4.7198 | 4.6623 | 4.7404 | 4.7849 | 4.5799 | 4.6438 | 4.5814 | 4.847 | 4.7532 | 4.7845 | 5.1839 | 5.1087 | 5.2333 | 5.205 | 5.2181 | 5.1958 | 5.0759 | 5.2591 | 5.2122 | 5.1218 | 5.0419 | 5.1346 | 5.1944 | 5.154 | 5.0697 | 5.1259 | 5.2336 | 5.0704 | 5.1019 | 5.2557 | 5.1861 | 5.1846 | 5.2457 | 5.1811 | 5.0959 | 5.2491 | 5.1829 | 5.1598 | 5.0483 | 5.1929 | 5.2412 | 5.293 | 5.2315 | 5.1663 | 5.2622 | 5.2084 | 5.176 | 5.1623 | 5.2264 | 5.169 | 5.2188 | 5.2919 | 5.2867 | 5.3337 | 5.1843 | 5.1781 | 5.3392 | 5.3023 | 5.3161 | 5.2381 | 5.1407 | 5.0914 | 5.1163 | 5.1128 | 5.136 | 5.1629 | 5.0642 | 5.1373 | 5.1329 | 5.1086 | 5.1598 | 5.2191 | 5.2264 | 5.1266 | 5.2405 | 5.107 | 5.1125 | 5.0883 | 5.185 | 5.0956 | 5.1787 | 5.0732 | 4.8754 | 5.1403 | 5.1156 | 4.9844 | 5.0221 | 5.0621 | 5.058 | 5.1001 | 5.1653 | 5.0852 | 5.1539 | 5.1056 | 5.2352 | 5.1792 | 5.1079 | 5.1885 | 5.1049 | 5.2577 | 5.0511 | 5.1004 | 4.9375 | 5.1732 | 5.158 | 5.1021 | 4.9976 | 5.1201 | 5.1225 | 5.087 | 5.081 | 5.1556 | 5.0253 | 4.9815 | 5.0571 | 5.0344 | 5.0423 | 5.0427 | 5.0582 | 5.0782 | 5.1376 | 5.1459 | 5.0918 | 5.0786 | 5.0831 | 5.11 | 5.0639 | 5.1526 | 4.9527 | 5.0979 | 5.0767 | 5.124 | 5.1308 | 5.0514 | 5.1323 | 5.0454 | 5.1126 | 5.0178 | 5.1198 | 5.0597 | 5.124 | 5.1143 | 5.094 | 5.1627 | 4.984 | 5.1137 | 4.98 | 5.0239 | 5.0648 | 5.1749 | 5.0052 | 5.073 | 5.1692 | 5.0983 | 4.97 | 5.0792 | 5.074 | 5.0123 | 5.202 | 4.9967 | 5.1138 | 5.1896 | 5.1863 | 5.2111 | 5.2577 | 4.9186 | 4.9113 | 5.0818 | 4.9292 | 4.8939 | 4.8718 | 4.9244 | 4.8907 | 5.0111 | 5.0168 | 5.1327 | 5.1228 | 5.106 | 4.988 | 5.1786 | 5.0527 | 5.1609 | 5.126 | 5.1397 | 5.1621 | 5.0534 | 5.0093 | 4.9922 | 5.0007 | 5.1566 | 5.1923 | 5.0094 | 5.0292 | 5.0761 | 4.9679 | 5.0663 | 5.0041 | 5.0635 | 5.0093 | 5.0662 | 5.1069 | 5.0127 | 5.0351 | 5.0695 | 5.1488 | 4.9116 | 5.142 | 5.1083 | 5.1274 | 5.1347 | 5.0905 | 4.914 | 5.2044 | 5.2014 | 5.1072 | 5.1552 | 5.1201 | 4.9299 | 5.0901 | 4.9686 | 5.0458 | 5.1901 | 5.2446 | 5.0792 | 5.2508 | 5.142 | 5.0918 | 5.0779 | 5.0748 | 5.0892 | 4.9441 | 5.0185 | 5.0484 | 5.0064 | 4.9667 | 5.1308 | 5.0021 | 5.1172 | 5.1398 | 5.1556 | 5.0869 | 5.1032 | 5.0259 | 5.0947 | 5.0201 | 5.0083 | 5.0834 | 5.053 | 5.0671 | 5.0747 | 5.1259 | 5.0933 | 5.1799 | 5.1263 | 5.164 | 5.1881 | 5.1254 | 5.1495 | 4.9027 | 5.1726 | 5.102 | 5.0718 | 5.0422 | 5.0952 | 4.9959 | 4.963 | 5.0139 | 5.0722 | 5.0824 | 5.1316 | 5.071 | 5.0306 | 5.0463 | 5.046 | 5.0639 | 5.0911 | 5.0695 | 5.0989 | 5.1209 | 5.1821 | 5.1923 | 5.1903 | 4.9836 | 5.1047 | 5.0908 | 4.9409 | 5.0751 | 5.0878 | 5.0946 | 5.1076 | 5.1428 | 5.0366 | 5.1374 | 5.1491 | 5.1308 | 5.1363 | 5.124 | 5.1935 | 5.0367 | 5.068 | 5.089 | 5.1609 | 5.0838 | 5.1424 | 5.056 | 5.0946 | 5.129 | 5.1087 | 5.1256 | 5.1929 | 5.1381 | 5.1911 | 5.1166 | 5.0638
2025-05-29 | 1.6356 | 1.6085 | 1.6606 | 1.6591 | 1.6652 | 1.5801 | 1.7077 | 1.6038 | 1.6795 | 1.678 | 1.6727 | 1.6629 | 1.6917 | 1.672 | 1.7159 | 1.7038 | 1.6547 | 1.6954 | 1.6735 | 1.6977 | 1.7402 | 1.7098 | 1.7508 | 1.7409 | 1.7341 | 1.7098 | 1.7485 | 1.7402 | 1.7614 | 1.7545 | 1.7189 | 1.7136 | 1.6788 | 1.6619 | 1.6643 | 1.6794 | 1.6994 | 1.689 | 1.6712 | 1.7089 | 1.6727 | 1.714 | 1.7621 | 1.7434 | 1.7654 | 1.8155 | 1.8056 | 1.8024 | 1.7286 | 1.7572 | 1.7588 | 1.7237 | 1.697 | 1.6798 | 1.6609 | 1.7012 | 1.7171 | 1.6388 | 1.6414 | 1.6273 | 1.6689 | 1.676 | 1.7155 | 1.7864 | 1.7536 | 1.7754 | 1.7636 | 1.7905 | 1.7605 | 1.7595 | 1.8054 | 1.8119 | 1.7805 | 1.7576 | 1.7816 | 1.772 | 1.763 | 1.7526 | 1.7861 | 1.7912 | 1.7529 | 1.787 | 1.7981 | 1.7778 | 1.746 | 1.7937 | 1.7958 | 1.7722 | 1.7391 | 1.7757 | 1.775 | 1.7305 | 1.7471 | 1.7754 | 1.7729 | 1.8106 | 1.8057 | 1.8054 | 1.7843 | 1.7146 | 1.724 | 1.7798 | 1.7348 | 1.7902 | 1.8523 | 1.7643 | 1.7961 | 1.7598 | 1.7205 | 1.8085 | 1.8064 | 1.8226 | 1.8016 | 1.7951 | 1.7678 | 1.832 | 1.805 | 1.804 | 1.7819 | 1.7502 | 1.7957 | 1.8264 | 1.8001 | 1.8023 | 1.8392 | 1.8492 | 1.7964 | 1.8475 | 1.7995 | 1.8147 | 1.8144 | 1.8375 | 1.8444 | 1.8685 | 1.8261 | 1.8678 | 1.8885 | 1.8961 | 1.8746 | 1.8413 | 1.8288 | 1.8668 | 1.8772 | 1.8675 | 1.8219 | 1.8854 | 1.882 | 1.8878 | 1.8823 | 1.8402 | 1.8627 | 1.8816 | 1.9176 | 1.8723 | 1.8758 | 1.8499 | 1.8675 | 1.8668 | 1.8678 | 1.8482 | 1.8506 | 1.8599 | 1.8247 | 1.8925 | 1.9175 | 1.8488 | 1.794 | 1.8367 | 1.8091 | 1.8296 | 1.8409 | 1.839 | 1.8401 | 1.87 | 1.8889 | 1.8681 | 1.85 | 1.8658 | 1.8855 | 1.8413 | 1.8796 | 1.8442 | 1.8828 | 1.8825 | 1.8923 | 1.8764 | 1.8655 | 1.8881 | 1.8673 | 1.8813 | 1.8314 | 1.8734 | 1.853 | 1.8753 | 1.8631 | 1.85 | 1.898 | 1.8275 | 1.8641 | 1.845 | 1.844 | 1.8521 | 1.8644 | 1.8521 | 1.8698 | 1.8776 | 1.8712 | 1.8282 | 1.8271 | 1.8087 | 1.6722 | 1.8763 | 1.841 | 1.8595 | 1.8666 | 1.8797 | 1.8685 | 1.8481 | 1.8145 | 1.7995 | 1.8366 | 1.8021 | 1.7906 | 1.7621 | 1.8225 | 1.7916 | 1.8203 | 1.8542 | 1.8552 | 1.8505 | 1.8348 | 1.8001 | 1.8516 | 1.8222 | 1.8858 | 1.8642 | 1.8568 | 1.8214 | 1.6599 | 1.808 | 1.6626 | 1.8218 | 1.9199 | 1.8956 | 1.852 | 1.8547 | 1.8654 | 1.8012 | 1.8505 | 1.8147 | 1.8622 | 1.8315 | 1.7605 | 1.8278 | 1.7967 | 1.8491 | 1.8614 | 1.7957 | 1.7744 | 1.8002 | 1.7975 | 1.8195 | 1.8292 | 1.8236 | 1.8214 | 1.8221 | 1.821 | 1.8149 | 1.8235 | 1.8491 | 1.8004 | 1.7954 | 1.8332 | 1.8122 | 1.8376 | 1.8398 | 1.82 | 1.8553 | 1.82 | 1.7993 | 1.7789 | 1.7555 | 1.7646 | 1.7309 | 1.763 | 1.7895 | 1.7672 | 1.7438 | 1.8178 | 1.804 | 1.7831 | 1.8001 | 1.8171 | 1.7857 | 1.7579 | 1.7371 | 1.7804 | 1.7577 | 1.7516 | 1.7873 | 1.748 | 1.7755 | 1.7694 | 1.8032 | 1.7971 | 1.7878 | 1.7876 | 1.8137 | 1.8036 | 1.7885 | 1.686 | 1.6692 | 1.8286 | 1.8027 | 1.7878 | 1.7747 | 1.8004 | 1.7582 | 1.6614 | 1.7829 | 1.7567 | 1.8006 | 1.8595 | 1.818 | 1.8274 | 1.802 | 1.8121 | 1.5542 | 1.8363 | 1.7995 | 1.7716 | 1.6484 | 1.8607 | 1.8446 | 1.6444 | 1.7818 | 1.8091 | 1.8199 | 1.7302 | 1.7919 | 1.7934 | 1.7799 | 1.7848 | 1.8188 | 1.7653 | 1.8026 | 1.8171 | 1.805 | 1.7744 | 1.7896 | 1.8265 | 1.8139 | 1.7837 | 1.7863 | 1.8112 | 1.7943 | 1.8154 | 1.8125 | 1.7912 | 1.802 | 1.7983 | 1.8301 | 1.802 | 1.8316 | 1.8367 | 1.8069 | 1.7934
2025-05-30 | 0.92982 | 0.89713 | 0.94015 | 0.93561 | 0.94318 | 0.89825 | 0.9694 | 0.90303 | 0.95303 | 0.93636 | 0.94545 | 0.94242 | 0.95985 | 0.93864 | 0.975 | 0.96515 | 0.92344 | 0.95853 | 0.94697 | 0.95833 | 0.98485 | 0.96894 | 0.98636 | 0.96742 | 0.96439 | 0.96591 | 0.99621 | 0.98182 | 1.0023 | 0.98409 | 0.97879 | 0.95076 | 0.9553 | 0.9378 | 0.93142 | 0.94817 | 0.96093 | 0.94976 | 0.9447 | 0.97289 | 0.94773 | 0.97718 | 1.0021 | 0.9905 | 0.99708 | 1.0347 | 1.0302 | 1.0242 | 0.96699 | 0.9986 | 1.0007 | 0.96012 | 0.95382 | 0.94893 | 0.93232 | 0.95241 | 0.97446 | 0.92216 | 0.92412 | 0.91446 | 0.9447 | 0.94745 | 0.95894 | 1.0093 | 0.99275 | 1.0107 | 1.0076 | 1.0155 | 0.9981 | 0.99896 | 1.0255 | 1.0286 | 1.0117 | 0.99774 | 1.0117 | 1.0076 | 1.0018 | 0.98758 | 1.0069 | 1.0169 | 0.98965 | 1.0079 | 1.0131 | 1.0025 | 1.0221 | 1.0112 | 1.013 | 0.99879 | 1.0152 | 1.0035 | 1.0041 | 0.96894 | 0.97999 | 0.99344 | 0.99551 | 1.0121 | 1.0095 | 1.0117 | 0.99931 | 0.96284 | 0.96465 | 1.0017 | 0.97348 | 1.01 | 1.039 | 0.99413 | 1.0141 | 0.99655 | 0.97101 | 1.0235 | 1.0217 | 1.0286 | 1.0094 | 1.0123 | 0.99931 | 1.04 | 1.0197 | 1.0197 | 1.0117 | 0.98654 | 1.0179 | 1.0355 | 1.0184 | 1.0198 | 1.0483 | 1.0556 | 1.0214 | 1.0521 | 1.0193 | 1.0286 | 1.0283 | 1.049 | 1.0473 | 1.0628 | 1.0383 | 1.0635 | 1.0794 | 1.0386 | 1.0762 | 1.0542 | 1.0618 | 1.07 | 1.0745 | 1.0725 | 1.0638 | 1.0801 | 1.0749 | 1.0779 | 1.0747 | 1.048 | 1.0615 | 1.0742 | 1.0945 | 1.0676 | 1.0697 | 1.0528 | 1.0683 | 1.0621 | 1.0618 | 1.0528 | 1.0538 | 1.06 | 1.0424 | 1.08 | 1.0994 | 1.053 | 1.0276 | 1.0574 | 1.0287 | 1.0416 | 1.0469 | 1.0491 | 1.0427 | 1.0571 | 1.0767 | 1.0642 | 1.054 | 1.0726 | 1.0839 | 1.0504 | 1.0776 | 1.0602 | 1.0726 | 1.0786 | 1.0775 | 1.0635 | 1.0563 | 1.0673 | 1.0673 | 1.0578 | 1.0397 | 1.0495 | 1.0491 | 1.0567 | 1.0397 | 1.0401 | 1.0861 | 1.0474 | 1.0675 | 1.0683 | 1.062 | 1.0699 | 1.0778 | 1.0678 | 1.0791 | 1.0914 | 1.0812 | 1.0646 | 1.0618 | 1.0597 | 0.94806 | 1.0655 | 1.0799 | 1.0781 | 1.0695 | 1.0797 | 1.072 | 1.0636 | 1.0515 | 1.0438 | 1.0681 | 1.0439 | 1.0187 | 1.0183 | 1.0474 | 1.0362 | 1.0265 | 1.0543 | 1.0549 | 1.0326 | 1.009 | 1.0215 | 1.0279 | 1.004 | 1.0765 | 1.051 | 1.0506 | 0.9478 | 0.72214 | 1.0129 | 0.7326 | 1.0152 | 1.0844 | 1.0479 | 1.0769 | 1.0668 | 1.0699 | 1.0395 | 1.0648 | 1.0484 | 1.0593 | 1.0395 | 0.88211 | 0.98752 | 0.94266 | 1.0455 | 1.0376 | 1.0086 | 0.997 | 1.0126 | 1.0107 | 1.0219 | 1.0302 | 1.031 | 1.0268 | 1.0265 | 1.0279 | 1.0252 | 1.0325 | 1.0452 | 1.0184 | 1.0154 | 1.0393 | 1.0283 | 1.0379 | 1.0405 | 1.0276 | 1.0522 | 1.0304 | 1 | 0.98564 | 0.96183 | 0.96107 | 0.95087 | 0.97506 | 0.99244 | 0.97506 | 0.95427 | 1.0098 | 0.99827 | 0.98224 | 1 | 1.0163 | 0.99683 | 0.95675 | 0.95776 | 0.99125 | 0.97497 | 0.96966 | 1 | 1.0107 | 0.99431 | 0.97194 | 1.0049 | 1.0076 | 0.98365 | 0.98749 | 1.0072 | 1.0004 | 0.99325 | 0.82967 | 0.8798 | 1.0147 | 0.99798 | 0.98864 | 0.97855 | 1.0063 | 0.96464 | 0.82455 | 0.99508 | 0.95133 | 0.99333 | 1.0555 | 0.99125 | 1.0417 | 1.0182 | 0.97481 | 0.75054 | 1.038 | 1.0126 | 0.99529 | 0.58477 | 1.0392 | 1.0518 | 0.85047 | 0.96696 | 0.97406 | 1.0028 | 0.98154 | 0.96173 | 0.97518 | 0.96472 | 0.96845 | 0.99985 | 0.95911 | 0.98901 | 0.98509 | 0.99948 | 0.96422 | 0.96978 | 1.0016 | 0.98259 | 0.99275 | 0.992 | 0.97214 | 0.96297 | 0.97518 | 0.98544 | 0.96429 | 0.99051 | 0.97017 | 1.0067 | 0.9729 | 1.0024 | 1.0094 | 0.97331 | 1.007
2025-05-31 | 3.185 | 3.0997 | 3.2083 | 3.203 | 3.203 | 3.0714 | 3.2907 | 3.1076 | 3.2386 | 3.2273 | 3.2417 | 3.2159 | 3.2432 | 3.2379 | 3.2848 | 3.2621 | 3.2305 | 3.2687 | 3.2205 | 3.2621 | 3.3492 | 3.3 | 3.3409 | 3.3311 | 3.3152 | 3.2848 | 3.3318 | 3.2864 | 3.3682 | 3.3455 | 3.3144 | 3.3136 | 3.1962 | 3.1722 | 3.1962 | 3.2257 | 3.2648 | 3.2528 | 3.2068 | 3.26 | 3.178 | 3.2218 | 3.2878 | 3.2778 | 3.3012 | 3.3589 | 3.3264 | 3.3065 | 3.1913 | 3.2805 | 3.3944 | 3.2321 | 3.1977 | 3.1622 | 3.1215 | 3.2001 | 3.1909 | 3.0687 | 3.0927 | 3.0522 | 3.2061 | 3.1831 | 3.2133 | 3.4334 | 3.362 | 3.424 | 3.3958 | 3.4172 | 3.4004 | 3.3568 | 3.4517 | 3.4372 | 3.3834 | 3.3459 | 3.3778 | 3.4069 | 3.3831 | 3.3092 | 3.4068 | 3.4545 | 3.352 | 3.3958 | 3.4603 | 3.4311 | 3.432 | 3.4448 | 3.421 | 3.3776 | 3.3471 | 3.4155 | 3.4058 | 3.3399 | 3.3782 | 3.4193 | 3.4331 | 3.441 | 3.4044 | 3.4641 | 3.421 | 3.3564 | 3.3773 | 3.4092 | 3.3555 | 3.4124 | 3.4417 | 3.411 | 3.451 | 3.393 | 3.3485 | 3.4717 | 3.461 | 3.3823 | 3.3133 | 3.3997 | 3.3741 | 3.3427 | 3.4137 | 3.4303 | 3.452 | 3.3844 | 3.4237 | 3.4406 | 3.4109 | 3.4524 | 3.4928 | 3.4883 | 3.4072 | 3.4855 | 3.3399 | 3.412 | 3.3958 | 3.4555 | 3.4268 | 3.4745 | 3.4061 | 3.4614 | 3.4462 | 3.3161 | 3.3057 | 3.4193 | 3.4413 | 3.4472 | 3.4689 | 3.4941 | 3.45 | 3.4931 | 3.2129 | 3.5227 | 3.4897 | 3.4369 | 3.2937 | 3.4651 | 3.5635 | 3.4324 | 3.4551 | 3.3861 | 3.4199 | 3.3916 | 3.3899 | 3.2564 | 3.4369 | 3.392 | 3.43 | 3.4563 | 3.51 | 3.3315 | 3.3432 | 3.3964 | 3.3764 | 3.3828 | 3.3855 | 3.3862 | 3.3859 | 3.4312 | 3.4494 | 3.4146 | 3.4097 | 3.4305 | 3.438 | 3.4254 | 3.4921 | 3.3254 | 3.4327 | 3.421 | 3.4407 | 3.4282 | 3.3976 | 3.4282 | 3.3919 | 3.432 | 3.3621 | 3.4195 | 3.3734 | 3.4033 | 3.4143 | 3.3992 | 3.4552 | 3.3718 | 3.483 | 3.4831 | 3.4262 | 3.4424 | 3.5084 | 3.4187 | 3.4687 | 3.5052 | 3.482 | 3.4052 | 3.3524 | 3.3797 | 2.9049 | 3.3867 | 3.4275 | 3.3544 | 3.4223 | 3.2951 | 3.3669 | 3.3883 | 3.2198 | 3.2767 | 3.4525 | 3.351 | 3.2654 | 3.3127 | 3.3519 | 3.275 | 3.2906 | 3.3256 | 3.3846 | 3.385 | 3.3367 | 3.3416 | 3.3583 | 3.309 | 3.4156 | 3.3917 | 3.3889 | 3.3049 | 3.022 | 3.3143 | 2.9663 | 3.33 | 3.4356 | 3.4144 | 3.387 | 3.3516 | 3.3787 | 3.296 | 3.3952 | 3.3827 | 3.3389 | 3.3285 | 3.0747 | 3.3688 | 3.2373 | 3.3382 | 3.2918 | 3.3516 | 3.2785 | 3.3936 | 3.3766 | 3.2491 | 3.4197 | 3.4228 | 3.4325 | 3.4598 | 3.4632 | 3.4271 | 3.4515 | 3.3646 | 3.2503 | 3.3855 | 3.375 | 3.3925 | 3.4938 | 3.4982 | 3.4018 | 3.5045 | 3.4266 | 3.3379 | 3.308 | 3.2846 | 3.2944 | 3.2336 | 3.2804 | 3.3193 | 3.2604 | 3.2407 | 3.3235 | 3.2823 | 3.3186 | 3.3386 | 3.3429 | 3.3333 | 3.3036 | 3.2858 | 3.336 | 3.3083 | 3.2992 | 3.3314 | 3.2776 | 3.3242 | 3.3003 | 3.3136 | 3.333 | 3.3509 | 3.3379 | 3.3575 | 3.3837 | 3.321 | 3.1766 | 3.0653 | 3.3615 | 3.3176 | 3.2847 | 3.2664 | 3.3139 | 3.2624 | 3.1027 | 3.2022 | 3.2873 | 3.2947 | 3.3371 | 3.2062 | 3.278 | 3.2399 | 3.2705 | 3.1102 | 3.3142 | 3.2692 | 3.2971 | 2.9804 | 3.2814 | 3.2967 | 2.9129 | 3.2519 | 3.3688 | 3.3531 | 3.244 | 3.3337 | 3.3539 | 3.3251 | 3.3427 | 3.3655 | 3.2978 | 3.363 | 3.3752 | 3.3464 | 3.3504 | 3.3493 | 3.394 | 3.3067 | 3.229 | 3.2403 | 3.3862 | 3.2778 | 3.3673 | 3.3053 | 3.3057 | 3.3404 | 3.3214 | 3.3383 | 3.3888 | 3.3615 | 3.3917 | 3.363 | 3.3424
2025-06-01 | 2.7209 | 2.6675 | 2.7591 | 2.7591 | 2.7364 | 2.6052 | 2.8447 | 2.6644 | 2.7674 | 2.7909 | 2.7962 | 2.7652 | 2.7826 | 2.7924 | 2.822 | 2.8182 | 2.7679 | 2.8254 | 2.7826 | 2.8273 | 2.9076 | 2.8636 | 2.8947 | 2.9015 | 2.8848 | 2.8477 | 2.903 | 2.8894 | 2.9333 | 2.9205 | 2.8811 | 2.8818 | 2.7333 | 2.7121 | 2.7392 | 2.7648 | 2.8038 | 2.8006 | 2.7432 | 2.7959 | 2.7462 | 2.7996 | 2.8634 | 2.8348 | 2.864 | 2.9334 | 2.9182 | 2.8985 | 2.8307 | 2.8583 | 2.8607 | 2.8064 | 2.7807 | 2.7474 | 2.7175 | 2.7957 | 2.8051 | 2.6844 | 2.6893 | 2.6627 | 2.7848 | 2.7596 | 2.7764 | 3.0128 | 2.9548 | 2.9775 | 2.9796 | 3.0217 | 2.9729 | 2.9496 | 3.0197 | 3.0304 | 2.9689 | 2.9338 | 2.9645 | 2.9578 | 2.9257 | 2.9489 | 3.0014 | 2.9962 | 2.9696 | 3.0036 | 3.029 | 3.0083 | 3.0511 | 3.0238 | 3.0263 | 2.994 | 2.9962 | 2.9914 | 2.9872 | 2.9055 | 2.961 | 2.979 | 3.0107 | 3.038 | 3.0267 | 3.0107 | 3.01 | 2.9387 | 2.9242 | 3.0186 | 2.943 | 3.0342 | 3.1387 | 2.9931 | 3.0504 | 2.9879 | 2.951 | 3.0683 | 3.0583 | 3.078 | 3.0537 | 3.0263 | 2.9634 | 2.9365 | 3.0197 | 3.0414 | 2.9907 | 3.0259 | 2.9976 | 3.0324 | 2.9957 | 3.0202 | 3.0504 | 3.0428 | 2.972 | 3.0459 | 3.0041 | 3.0069 | 2.9862 | 3.0104 | 3.0273 | 3.05 | 2.9948 | 3.0466 | 3.0707 | 3.0666 | 2.7937 | 3.109 | 2.9855 | 3.02 | 3.0376 | 3.0141 | 3.0145 | 3.0507 | 2.8606 | 3.0473 | 3.0403 | 2.9791 | 3.0242 | 3.049 | 3.1032 | 3.0266 | 3.0411 | 3.009 | 3.04 | 2.9534 | 3.0359 | 2.9965 | 3.0135 | 3.0152 | 2.9617 | 3.0648 | 3.0983 | 3.0094 | 2.9324 | 2.9887 | 2.9686 | 2.9732 | 2.9796 | 2.9773 | 2.9807 | 3.017 | 3.0329 | 3.003 | 3.0098 | 3.0238 | 3.0385 | 2.9929 | 3.0234 | 2.9351 | 3.0321 | 3.0076 | 3.0401 | 3.0223 | 2.9928 | 3.0261 | 2.9864 | 3.0219 | 2.9463 | 3.0253 | 2.9701 | 3.0049 | 3.0024 | 2.9845 | 3.0127 | 2.9517 | 3.0305 | 2.9886 | 3.0115 | 3.0213 | 3.0485 | 3.0086 | 3.0506 | 3.0678 | 3.0732 | 2.9924 | 3.0056 | 2.8672 | 2.5118 | 3.0136 | 3.021 | 3.0216 | 3.0341 | 3.0631 | 3.0402 | 3.0159 | 2.9788 | 2.8851 | 3.0007 | 2.9493 | 2.8971 | 2.8981 | 2.9732 | 2.9235 | 2.966 | 2.9806 | 2.9961 | 2.9906 | 2.8787 | 2.9779 | 3.0169 | 2.945 | 3.0283 | 2.9874 | 2.991 | 2.9702 | 2.9274 | 2.942 | 2.9031 | 2.9397 | 3.0341 | 3.0259 | 2.9596 | 2.9588 | 2.9831 | 2.9476 | 2.9643 | 2.9495 | 2.9625 | 2.9308 | 2.9629 | 2.9581 | 2.9158 | 2.9461 | 2.9483 | 2.9909 | 2.9394 | 3.0001 | 2.9833 | 3.0333 | 3.0436 | 2.9884 | 3.0232 | 3.0323 | 3.0247 | 3.0203 | 3.0323 | 3.0479 | 2.9691 | 2.9709 | 3.0182 | 2.9811 | 3.0154 | 3.0185 | 3.0056 | 3.0426 | 3.0109 | 2.9615 | 2.9482 | 2.941 | 2.955 | 2.8855 | 2.9138 | 2.9656 | 2.9282 | 2.8961 | 3.0011 | 2.9869 | 2.9667 | 2.9894 | 2.9869 | 2.948 | 2.9373 | 2.9517 | 2.9699 | 2.9606 | 2.9632 | 2.9606 | 3.0357 | 2.9416 | 2.9378 | 2.981 | 2.9545 | 2.9736 | 2.9735 | 3.0019 | 2.9964 | 2.9595 | 2.9176 | 2.9148 | 2.9893 | 2.954 | 2.939 | 2.9252 | 2.9464 | 2.8972 | 2.8755 | 2.9224 | 2.9046 | 2.927 | 2.9738 | 2.9155 | 2.9106 | 2.924 | 2.9162 | 2.8822 | 2.9899 | 2.9054 | 2.9321 | 2.8795 | 3.0055 | 2.9867 | 2.9454 | 2.9315 | 2.9951 | 2.9749 | 2.8732 | 2.9554 | 2.9689 | 2.967 | 2.9678 | 3.001 | 2.9412 | 2.9745 | 2.9631 | 2.9951 | 2.9472 | 2.9694 | 3.0008 | 2.9774 | 2.9689 | 2.9768 | 2.9898 | 2.9913 | 2.9954 | 2.9863 | 2.9486 | 2.9782 | 2.9498 | 2.9808 | 2.979 | 3.0047 | 3.0004 | 3.0047 | 2.953
2025-06-02 | 2.5303 | 2.4673 | 2.5636 | 2.5583 | 2.5523 | 2.4305 | 2.6435 | 2.4803 | 2.5841 | 2.597 | 2.5985 | 2.5773 | 2.5886 | 2.597 | 2.625 | 2.6098 | 2.5718 | 2.6324 | 2.5985 | 2.6341 | 2.7159 | 2.6674 | 2.7121 | 2.7023 | 2.697 | 2.6523 | 2.6977 | 2.6652 | 2.7348 | 2.6992 | 2.6773 | 2.6856 | 2.5402 | 2.5239 | 2.5447 | 2.5686 | 2.6029 | 2.5869 | 2.5523 | 2.5861 | 2.525 | 2.5884 | 2.6581 | 2.6192 | 2.6491 | 2.712 | 2.6971 | 2.6875 | 2.6259 | 2.6539 | 2.6547 | 2.5932 | 2.5671 | 2.5404 | 2.5117 | 2.5836 | 2.6028 | 2.479 | 2.4928 | 2.4736 | 2.5674 | 2.5621 | 2.5704 | 2.8085 | 2.7471 | 2.7802 | 2.774 | 2.8157 | 2.7735 | 2.746 | 2.8099 | 2.8275 | 2.7754 | 2.7498 | 2.7381 | 2.7615 | 2.7049 | 2.6856 | 2.7836 | 2.7674 | 2.7578 | 2.7768 | 2.8168 | 2.7922 | 2.8395 | 2.8019 | 2.803 | 2.778 | 2.794 | 2.7664 | 2.7764 | 2.7429 | 2.7881 | 2.804 | 2.8216 | 2.8575 | 2.8422 | 2.823 | 2.8168 | 2.7507 | 2.7388 | 2.8068 | 2.7485 | 2.8395 | 2.9234 | 2.8109 | 2.8499 | 2.7968 | 2.754 | 2.8592 | 2.8492 | 2.8765 | 2.8503 | 2.8016 | 2.7419 | 2.8337 | 2.7985 | 2.814 | 2.7781 | 2.7885 | 2.7654 | 2.7902 | 2.7608 | 2.7857 | 2.8175 | 2.804 | 2.7405 | 2.8023 | 2.7626 | 2.7633 | 2.7405 | 2.7647 | 2.7726 | 2.8047 | 2.7498 | 2.8012 | 2.8164 | 2.8333 | 2.7902 | 2.7533 | 2.7619 | 2.784 | 2.8033 | 2.7874 | 2.7816 | 2.8109 | 2.7985 | 2.798 | 2.788 | 2.7276 | 2.7575 | 2.8137 | 2.8541 | 2.7809 | 2.7974 | 2.7512 | 2.7885 | 2.775 | 2.7843 | 2.7346 | 2.7498 | 2.7491 | 2.7074 | 2.8112 | 2.8413 | 2.7413 | 2.6455 | 2.6969 | 2.6799 | 2.689 | 2.6969 | 2.6984 | 2.7033 | 2.7532 | 2.7638 | 2.7268 | 2.7105 | 2.7286 | 2.743 | 2.6964 | 2.7143 | 2.6291 | 2.737 | 2.715 | 2.7585 | 2.7509 | 2.7063 | 2.7494 | 2.6829 | 2.7358 | 2.6432 | 2.72 | 2.6916 | 2.7222 | 2.704 | 2.6917 | 2.7448 | 2.6677 | 2.7381 | 2.6994 | 2.7236 | 2.7363 | 2.7683 | 2.7365 | 2.7759 | 2.7922 | 2.8042 | 2.7266 | 2.7387 | 2.28 | 1.9111 | 2.7266 | 2.7253 | 2.7367 | 2.7398 | 2.7317 | 2.7493 | 2.7272 | 2.6939 | 2.6646 | 2.7168 | 2.6669 | 2.6005 | 2.624 | 2.6913 | 2.647 | 2.6334 | 2.6499 | 2.6652 | 2.6746 | 2.6009 | 2.659 | 2.7182 | 2.6508 | 2.6911 | 2.666 | 2.6668 | 2.6743 | 2.6303 | 2.6288 | 2.6056 | 2.6471 | 2.7057 | 2.7316 | 2.6664 | 2.6508 | 2.6554 | 2.6164 | 2.6393 | 2.6381 | 2.6587 | 2.6235 | 2.6594 | 2.6557 | 2.6497 | 2.6504 | 2.6646 | 2.7169 | 2.683 | 2.7254 | 2.7095 | 2.7609 | 2.7682 | 2.7428 | 2.7555 | 2.7565 | 2.7619 | 2.7616 | 2.7594 | 2.7833 | 2.7056 | 2.6917 | 2.7491 | 2.7054 | 2.7464 | 2.752 | 2.735 | 2.7716 | 2.749 | 2.698 | 2.6731 | 2.6633 | 2.6788 | 2.6213 | 2.6618 | 2.6837 | 2.6379 | 2.6164 | 2.7135 | 2.6508 | 2.6844 | 2.6924 | 2.6885 | 2.6897 | 2.6647 | 2.6944 | 2.7093 | 2.6811 | 2.7103 | 2.7004 | 2.6653 | 2.6807 | 2.6625 | 2.708 | 2.6811 | 2.6822 | 2.6879 | 2.706 | 2.704 | 2.6726 | 2.6805 | 2.6026 | 2.6877 | 2.6669 | 2.6407 | 2.6209 | 2.6313 | 2.5845 | 2.2427 | 2.6095 | 2.6252 | 2.6546 | 2.6994 | 2.6706 | 2.6351 | 2.619 | 2.6344 | 2.631 | 2.6846 | 2.602 | 2.6487 | 2.5542 | 2.7025 | 2.7159 | 2.6409 | 2.6882 | 2.7383 | 2.7312 | 2.6123 | 2.6975 | 2.7017 | 2.6863 | 2.6901 | 2.7155 | 2.6527 | 2.6852 | 2.6688 | 2.6979 | 2.6638 | 2.6825 | 2.7237 | 2.7223 | 2.702 | 2.6942 | 2.7476 | 2.7101 | 2.742 | 2.7112 | 2.6837 | 2.7144 | 2.6813 | 2.7108 | 2.7113 | 2.7214 | 2.7265 | 2.7174 | 2.6986
2025-06-03 | 2.0877 | 2.0335 | 2.1197 | 2.1144 | 2.1129 | 2.0167 | 2.1783 | 2.0803 | 2.15 | 2.1568 | 2.1424 | 2.1318 | 2.1485 | 2.1462 | 2.172 | 2.153 | 2.1292 | 2.1754 | 2.1477 | 2.1765 | 2.2477 | 2.203 | 2.2424 | 2.2394 | 2.2424 | 2.197 | 2.2348 | 2.2159 | 2.2689 | 2.2568 | 2.2197 | 2.2295 | 2.1076 | 2.0869 | 2.1005 | 2.1252 | 2.1555 | 2.138 | 2.1205 | 2.1396 | 2.0856 | 2.1398 | 2.1976 | 2.1623 | 2.1908 | 2.2438 | 2.2359 | 2.2352 | 2.1461 | 2.2059 | 2.1987 | 2.1603 | 2.1392 | 2.1001 | 2.078 | 2.1414 | 2.1579 | 2.0526 | 2.0631 | 2.0334 | 2.1159 | 2.1218 | 2.1349 | 2.3244 | 2.2654 | 2.297 | 2.2878 | 2.3326 | 2.2996 | 2.2733 | 2.3257 | 2.3444 | 2.2919 | 2.28 | 2.2899 | 2.2947 | 2.2569 | 2.2581 | 2.303 | 2.2809 | 2.2819 | 2.3039 | 2.323 | 2.3034 | 2.3451 | 2.3247 | 2.3254 | 2.3014 | 2.3088 | 2.2978 | 2.2957 | 2.2522 | 2.2795 | 2.2954 | 2.3037 | 2.3468 | 2.3352 | 2.3292 | 2.3133 | 2.2424 | 2.2417 | 2.3095 | 2.2555 | 2.3295 | 2.4089 | 2.3157 | 2.3433 | 2.3154 | 2.2709 | 2.362 | 2.3492 | 2.3744 | 2.3492 | 2.3236 | 2.2798 | 2.3547 | 2.3251 | 2.3323 | 2.2981 | 2.314 | 2.295 | 2.3313 | 2.2973 | 2.3185 | 2.3458 | 2.3357 | 2.2816 | 2.3382 | 2.3002 | 2.3047 | 2.294 | 2.3116 | 2.3299 | 2.3489 | 2.304 | 2.3451 | 2.3647 | 2.3502 | 2.3263 | 2.2881 | 2.2774 | 2.3206 | 2.3337 | 2.3178 | 2.3095 | 2.305 | 2.3299 | 2.3337 | 2.331 | 2.2763 | 2.3036 | 2.3413 | 2.3859 | 2.3323 | 2.3371 | 2.3019 | 2.3316 | 2.333 | 2.3406 | 2.3006 | 2.3095 | 2.3099 | 2.265 | 2.3155 | 2.3872 | 2.3009 | 2.2608 | 2.3084 | 2.2937 | 2.3035 | 2.3148 | 2.308 | 2.3054 | 2.3398 | 2.3466 | 2.3296 | 2.3254 | 2.3348 | 2.3519 | 2.3024 | 2.3338 | 2.2738 | 2.3458 | 2.3273 | 2.3458 | 2.3371 | 2.311 | 2.3409 | 2.3042 | 2.3356 | 2.2702 | 2.3318 | 2.2925 | 2.3197 | 2.3187 | 2.2984 | 2.346 | 2.2487 | 2.3058 | 2.2747 | 2.2915 | 2.3046 | 2.3325 | 2.3008 | 2.3316 | 2.3432 | 2.3497 | 2.2963 | 2.3056 | 2.28 | 2.2678 | 2.3104 | 2.3051 | 2.3124 | 2.3049 | 2.337 | 2.318 | 2.5728 | 2.2681 | 2.2503 | 2.2828 | 2.2485 | 2.2113 | 2.2465 | 2.2671 | 2.2331 | 2.2759 | 2.2977 | 2.3057 | 2.3155 | 2.3254 | 2.3043 | 2.3407 | 2.2894 | 2.3273 | 2.3108 | 2.3089 | 2.321 | 2.2374 | 2.2643 | 2.2303 | 2.2684 | 2.3587 | 2.4176 | 2.3273 | 2.3017 | 2.303 | 2.2527 | 2.2908 | 2.2808 | 2.2995 | 2.2613 | 2.2987 | 2.2961 | 2.2722 | 2.2755 | 2.2972 | 2.2649 | 2.2408 | 2.2753 | 2.2637 | 2.3064 | 2.3276 | 2.3101 | 2.3086 | 2.3173 | 2.3155 | 2.3104 | 2.3166 | 2.3388 | 2.2689 | 2.2236 | 2.3033 | 2.2717 | 2.309 | 2.3121 | 2.2964 | 2.3283 | 2.3023 | 2.2857 | 2.2589 | 2.2513 | 2.263 | 2.2173 | 2.2521 | 2.2744 | 2.2551 | 2.2237 | 2.3197 | 2.2443 | 2.2868 | 2.3005 | 2.3087 | 2.2786 | 2.2611 | 2.2725 | 2.2972 | 2.2814 | 2.2984 | 2.2947 | 2.2499 | 2.2719 | 2.2692 | 2.2984 | 2.2909 | 2.2893 | 2.2973 | 2.3228 | 2.3095 | 2.2857 | 2.2947 | 2.293 | 2.3183 | 2.2845 | 2.2692 | 2.2561 | 2.2825 | 2.2379 | 2.2688 | 2.261 | 2.2496 | 2.2798 | 2.3451 | 2.3103 | 2.2976 | 2.2699 | 2.2826 | 2.2255 | 2.3159 | 2.2681 | 2.2838 | 2.1507 | 2.3469 | 2.3548 | 2.2991 | 2.2509 | 2.2856 | 2.2954 | 2.1791 | 2.2722 | 2.2662 | 2.2427 | 2.2617 | 2.2886 | 2.2307 | 2.2779 | 2.3352 | 2.2755 | 2.2453 | 2.2669 | 2.3002 | 2.3013 | 2.2513 | 2.2535 | 2.3049 | 2.2717 | 2.3066 | 2.2759 | 2.2641 | 2.2774 | 2.2665 | 2.3006 | 2.28 | 2.2951 | 2.3124 | 2.2916 | 2.2746
2025-06-04 | 3.4984 | 3.4083 | 3.5523 | 3.5424 | 3.4917 | 3.3485 | 3.6511 | 3.4773 | 3.5485 | 3.5568 | 3.5947 | 3.5674 | 3.5455 | 3.5439 | 3.5879 | 3.5894 | 3.5423 | 3.5981 | 3.55 | 3.6015 | 3.728 | 3.6371 | 3.6909 | 3.6977 | 3.703 | 3.628 | 3.6773 | 3.65 | 3.7682 | 3.7189 | 3.6674 | 3.6871 | 3.4364 | 3.4115 | 3.4641 | 3.4888 | 3.5702 | 3.5606 | 3.4811 | 3.5311 | 3.4591 | 3.5 | 3.5638 | 3.5219 | 3.5789 | 3.644 | 3.6508 | 3.6425 | 3.5501 | 3.6267 | 3.6041 | 3.5475 | 3.531 | 3.4714 | 3.4344 | 3.543 | 3.5578 | 3.3899 | 3.4169 | 3.3839 | 3.5652 | 3.5167 | 3.511 | 3.9072 | 3.9234 | 3.9391 | 3.9337 | 3.93 | 3.8846 | 3.7971 | 3.881 | 3.9117 | 3.8261 | 3.8108 | 3.813 | 3.8405 | 3.7554 | 3.8175 | 3.8613 | 3.8747 | 3.8206 | 3.9015 | 3.9379 | 3.9001 | 3.97 | 3.956 | 3.9683 | 3.9139 | 3.9072 | 3.8744 | 3.863 | 3.8879 | 3.9648 | 3.9855 | 4.0048 | 4.0504 | 4.0124 | 4.0162 | 4.01 | 3.9567 | 3.9509 | 3.9841 | 3.8703 | 3.9945 | 4.1884 | 3.9848 | 4.0107 | 3.9334 | 3.962 | 4.0173 | 4.001 | 3.9444 | 4.0064 | 3.9459 | 3.8019 | 3.8968 | 3.8696 | 3.9044 | 3.8392 | 3.8896 | 3.8244 | 3.8765 | 3.8452 | 3.8828 | 3.8768 | 3.8475 | 3.7992 | 3.8727 | 3.8537 | 3.8458 | 3.8064 | 3.8209 | 3.8375 | 3.8723 | 3.794 | 3.8575 | 3.8716 | 3.6743 | 3.6025 | 3.5901 | 3.5928 | 3.6387 | 3.6611 | 3.6784 | 3.6522 | 3.6957 | 3.7088 | 3.7879 | 3.744 | 3.6602 | 3.7365 | 3.7233 | 3.842 | 3.7636 | 3.8033 | 3.7705 | 3.8154 | 3.8271 | 3.8323 | 3.7564 | 3.7905 | 3.6732 | 3.6649 | 3.8383 | 3.8713 | 3.7496 | 3.6281 | 3.6228 | 3.6206 | 3.613 | 3.6319 | 3.6281 | 3.647 | 3.6508 | 3.6515 | 3.6281 | 3.6568 | 3.667 | 3.6587 | 3.6286 | 3.6693 | 3.6436 | 3.6738 | 3.6508 | 3.681 | 3.6568 | 3.6206 | 3.6704 | 3.6338 | 3.6807 | 3.6584 | 3.6909 | 3.6364 | 3.655 | 3.6595 | 3.6448 | 3.6496 | 3.6352 | 3.7203 | 3.6366 | 3.6657 | 3.6871 | 3.7201 | 3.6453 | 3.7018 | 3.7187 | 3.7069 | 3.6606 | 3.6385 | 3.6219 | 3.6414 | 3.7634 | 3.7238 | 3.7677 | 3.748 | 3.7666 | 3.74 | 3.7001 | 3.6303 | 3.6273 | 3.6539 | 3.6337 | 3.6271 | 3.6764 | 3.61 | 3.6184 | 3.6952 | 3.6977 | 3.7296 | 3.7374 | 3.7606 | 3.7243 | 3.7998 | 3.6978 | 3.7547 | 3.7057 | 3.7151 | 3.7355 | 3.6387 | 3.632 | 3.5811 | 3.6148 | 3.7547 | 3.8776 | 3.6966 | 3.6787 | 3.7009 | 3.6552 | 3.675 | 3.6656 | 3.6667 | 3.6159 | 3.6574 | 3.6738 | 3.6114 | 3.6249 | 3.6357 | 3.8287 | 3.6964 | 3.8506 | 3.8263 | 3.8115 | 3.9027 | 3.8573 | 3.8886 | 3.9079 | 3.9001 | 3.881 | 3.885 | 3.8744 | 3.7685 | 3.7416 | 3.7881 | 3.7791 | 3.8156 | 3.8331 | 3.8294 | 3.8639 | 3.8447 | 3.8655 | 3.8345 | 3.8243 | 3.8454 | 3.7396 | 3.7963 | 3.853 | 3.7842 | 3.7566 | 3.8768 | 3.7674 | 3.8333 | 3.8556 | 3.8464 | 3.8302 | 3.8127 | 3.8413 | 3.8581 | 3.8385 | 3.8551 | 3.8267 | 3.7902 | 3.8168 | 3.8089 | 3.8684 | 3.8354 | 3.8419 | 3.8574 | 3.8802 | 3.8754 | 3.8333 | 3.8571 | 3.7192 | 3.9008 | 3.8432 | 3.823 | 3.7916 | 3.7976 | 3.7276 | 3.6907 | 3.7534 | 3.7861 | 3.8214 | 3.8521 | 3.8013 | 3.7695 | 3.7628 | 3.7856 | 3.7269 | 3.8386 | 3.748 | 3.7457 | 3.6978 | 3.8081 | 3.8148 | 3.7457 | 3.7351 | 3.8106 | 3.8084 | 3.6552 | 3.7718 | 3.7662 | 3.7763 | 3.7643 | 3.8062 | 3.7288 | 3.7798 | 3.7677 | 3.8095 | 3.7772 | 3.7892 | 3.8516 | 3.8397 | 3.8095 | 3.8129 | 3.8705 | 3.819 | 3.8701 | 3.8847 | 3.8414 | 3.8641 | 3.8505 | 3.8183 | 3.8449 | 3.9011 | 3.8827 | 3.8579 | 3.7471
2025-06-05 | 3.1683 | 3.0726 | 3.2023 | 3.1962 | 3.1197 | 2.9924 | 3.2739 | 3.125 | 3.178 | 3.1803 | 3.225 | 3.1992 | 3.1409 | 3.1841 | 3.1833 | 3.203 | 3.1802 | 3.2265 | 3.2045 | 3.2439 | 3.3439 | 3.3023 | 3.3205 | 3.3098 | 3.3227 | 3.2992 | 3.3038 | 3.2894 | 3.3758 | 3.3568 | 3.3083 | 3.3159 | 3.0432 | 3.0215 | 3.0662 | 3.0877 | 3.1619 | 3.1683 | 3.0644 | 3.118 | 3.0568 | 3.0984 | 3.1595 | 3.1469 | 3.1718 | 3.233 | 3.2245 | 3.2177 | 3.1436 | 3.2128 | 3.1738 | 3.1204 | 3.1198 | 3.0925 | 3.0601 | 3.154 | 3.1687 | 3.0288 | 3.0663 | 3.0396 | 3.1871 | 3.1354 | 3.0997 | 3.4658 | 3.4255 | 3.4528 | 3.452 | 3.4645 | 3.4412 | 3.3816 | 3.4603 | 3.4617 | 3.403 | 3.3775 | 3.4006 | 3.4358 | 3.3788 | 3.3844 | 3.4431 | 3.461 | 3.3758 | 3.4461 | 3.4127 | 3.4888 | 3.4965 | 3.4852 | 3.4737 | 3.437 | 3.4696 | 3.4462 | 3.4503 | 3.3337 | 3.4144 | 3.431 | 3.4524 | 3.4648 | 3.4505 | 3.4482 | 3.4358 | 3.4192 | 3.4145 | 3.4572 | 3.3666 | 3.462 | 3.5221 | 3.44 | 3.4959 | 3.4534 | 3.4627 | 3.5269 | 3.5124 | 3.4289 | 3.5034 | 3.4545 | 3.3806 | 3.364 | 3.4327 | 3.461 | 3.4248 | 3.4634 | 3.4251 | 3.4172 | 3.3939 | 3.4325 | 3.4375 | 3.4051 | 3.3616 | 3.4193 | 3.3882 | 3.3313 | 3.3264 | 3.3471 | 3.363 | 3.3758 | 3.3164 | 3.3685 | 3.3943 | 3.411 | 3.3241 | 3.2888 | 3.2802 | 3.3592 | 3.353 | 3.334 | 3.3126 | 3.3558 | 3.3168 | 3.3427 | 3.3089 | 3.2536 | 3.2968 | 3.3254 | 3.3859 | 3.3026 | 3.3316 | 3.3006 | 3.3071 | 3.2781 | 3.2284 | 3.2826 | 3.3081 | 3.2968 | 3.2333 | 3.3651 | 3.3992 | 3.285 | 3.4157 | 3.4592 | 3.4067 | 3.3813 | 3.3488 | 3.3352 | 3.3186 | 3.339 | 3.3624 | 3.3473 | 3.4399 | 3.4607 | 3.4131 | 3.4115 | 3.4153 | 3.2442 | 3.3953 | 3.3571 | 3.387 | 3.3515 | 3.3182 | 3.3307 | 3.311 | 3.3341 | 3.2729 | 3.3337 | 3.232 | 3.0767 | 3.2944 | 3.2504 | 3.3016 | 3.309 | 3.429 | 3.3956 | 3.4437 | 3.4612 | 3.5267 | 3.438 | 3.5066 | 3.556 | 3.5728 | 3.5036 | 3.5204 | 3.2978 | 3.3305 | 3.4764 | 3.3942 | 3.4019 | 3.4337 | 3.4717 | 3.4545 | 3.4467 | 3.3811 | 3.4426 | 3.4752 | 3.436 | 3.3632 | 3.3917 | 3.4008 | 3.3371 | 3.2157 | 3.2139 | 3.2669 | 3.2637 | 3.2504 | 3.2231 | 3.3006 | 3.2272 | 3.3104 | 3.2661 | 3.2567 | 3.2743 | 3.2208 | 3.1969 | 3.1898 | 3.1991 | 3.3093 | 3.3359 | 3.2602 | 3.2335 | 3.283 | 3.2638 | 3.2747 | 3.2747 | 3.2425 | 3.2257 | 3.3173 | 3.3176 | 3.2261 | 3.259 | 3.2769 | 3.1358 | 3.285 | 3.354 | 3.3387 | 3.3048 | 2.8748 | 3.2778 | 3.3696 | 3.4009 | 3.4028 | 3.38 | 3.3945 | 3.3627 | 3.2752 | 3.299 | 3.3027 | 3.2702 | 3.3203 | 3.3233 | 3.3203 | 3.3521 | 3.367 | 3.3896 | 3.3692 | 3.3314 | 3.3923 | 3.2547 | 3.3458 | 3.35 | 3.2668 | 3.24 | 3.3333 | 3.2937 | 3.3031 | 3.308 | 3.3155 | 3.3702 | 3.3099 | 3.3352 | 3.3478 | 3.3345 | 3.3523 | 3.339 | 3.2818 | 3.314 | 3.2912 | 3.3379 | 3.3113 | 3.3371 | 3.3132 | 3.319 | 3.3313 | 3.302 | 3.3952 | 3.2912 | 3.3917 | 3.3229 | 3.2989 | 3.2616 | 3.2802 | 3.2215 | 3.2481 | 3.2375 | 3.2547 | 3.301 | 3.3124 | 3.29 | 3.2137 | 3.2384 | 3.2451 | 3.2687 | 3.3182 | 3.2288 | 3.2406 | 3.292 | 3.2932 | 3.2967 | 3.3089 | 3.1924 | 3.2758 | 3.2619 | 3.1509 | 3.2343 | 3.2182 | 3.2567 | 3.2085 | 3.2616 | 3.1894 | 3.2304 | 3.2418 | 3.2765 | 3.2496 | 3.2571 | 3.314 | 3.3042 | 3.2975 | 3.2986 | 3.3387 | 3.2967 | 3.3285 | 3.3556 | 3.3454 | 3.3348 | 3.2457 | 3.2104 | 3.3178 | 3.3838 | 3.3422 | 3.3175 | 3.3157
2025-06-06 | 3.2329 | 3.1603 | 3.2833 | 3.2826 | 3.2318 | 3.1093 | 3.368 | 3.2114 | 3.2758 | 3.2864 | 3.3303 | 3.2977 | 3.2871 | 3.2947 | 3.3152 | 3.3197 | 3.2879 | 3.3254 | 3.3273 | 3.35 | 3.4606 | 3.4114 | 3.4114 | 3.4015 | 3.4341 | 3.4265 | 3.4333 | 3.3894 | 3.4886 | 3.4568 | 3.4227 | 3.4053 | 3.2091 | 3.1738 | 3.2113 | 3.2432 | 3.3126 | 3.2863 | 3.2356 | 3.2711 | 3.2106 | 3.2582 | 3.3176 | 3.3004 | 3.3158 | 3.3878 | 3.3499 | 3.3347 | 3.2182 | 3.3105 | 3.3065 | 3.2509 | 3.2381 | 3.1898 | 3.1354 | 3.2351 | 3.2513 | 3.1136 | 3.1398 | 3.0967 | 3.2659 | 3.2062 | 3.2273 | 3.5776 | 3.5407 | 3.6016 | 3.5852 | 3.5324 | 3.5165 | 3.4855 | 3.5832 | 3.529 | 3.4731 | 3.4206 | 3.4507 | 3.4852 | 3.4387 | 3.3285 | 3.5707 | 3.6128 | 3.481 | 3.5632 | 3.6536 | 3.6061 | 3.5852 | 3.6284 | 3.5667 | 3.539 | 3.6187 | 3.5718 | 3.5604 | 3.5186 | 3.5756 | 3.6594 | 3.6611 | 3.6363 | 3.5962 | 3.6632 | 3.6225 | 3.5768 | 3.6194 | 3.6211 | 3.5646 | 3.598 | 3.697 | 3.5597 | 3.6318 | 3.5045 | 3.548 | 3.6273 | 3.6484 | 3.6573 | 3.6523 | 3.5548 | 3.4914 | 3.4945 | 3.5183 | 3.5359 | 3.5932 | 3.5666 | 3.5141 | 3.4896 | 3.4711 | 3.5148 | 3.5383 | 3.5335 | 3.462 | 3.5376 | 3.48 | 3.4651 | 3.442 | 3.5114 | 3.4589 | 3.5297 | 3.4496 | 3.4979 | 3.4957 | 3.4758 | 3.3683 | 3.4783 | 3.4489 | 3.3934 | 3.4645 | 3.4893 | 3.4607 | 3.4748 | 3.3385 | 3.5487 | 3.5136 | 3.4683 | 3.5456 | 3.4741 | 3.5915 | 3.441 | 3.4565 | 3.3799 | 3.5352 | 3.5148 | 3.4807 | 3.2809 | 3.5028 | 3.2926 | 3.4555 | 3.4593 | 3.5117 | 3.531 | 3.2396 | 3.3027 | 3.2906 | 3.3197 | 3.3352 | 3.3571 | 3.3934 | 3.4546 | 3.4324 | 3.3715 | 3.3163 | 3.3447 | 3.3825 | 3.3456 | 3.3973 | 3.2316 | 3.3677 | 3.3401 | 3.3855 | 3.3908 | 3.3307 | 3.4051 | 3.3231 | 3.3893 | 3.2933 | 3.4006 | 3.4263 | 3.4206 | 3.4198 | 3.4321 | 3.4389 | 3.2936 | 3.4107 | 3.3646 | 3.333 | 3.3356 | 3.379 | 3.3268 | 3.3684 | 3.4022 | 3.3728 | 3.2953 | 3.3442 | 3.3621 | 3.3025 | 3.401 | 3.3199 | 3.3277 | 3.4062 | 3.4138 | 3.4268 | 3.3865 | 3.2696 | 3.2931 | 3.329 | 3.2956 | 3.2758 | 3.2795 | 3.2398 | 3.2023 | 3.3256 | 3.3206 | 3.4133 | 3.4133 | 3.4682 | 3.3946 | 3.4941 | 3.3905 | 3.4133 | 3.3842 | 3.416 | 3.4199 | 3.364 | 3.3528 | 3.3199 | 3.3569 | 3.3622 | 3.4458 | 3.374 | 3.2877 | 3.3167 | 3.3397 | 3.3438 | 3.3442 | 3.364 | 3.2982 | 3.3068 | 3.3023 | 3.3386 | 3.3333 | 3.3539 | 3.3891 | 3.4263 | 3.5656 | 3.5082 | 3.4256 | 3.3687 | 3.4471 | 3.4937 | 3.5275 | 3.526 | 3.4762 | 3.514 | 3.4611 | 3.3524 | 3.458 | 3.3894 | 3.4655 | 3.557 | 3.5614 | 3.4421 | 3.571 | 3.4858 | 3.4989 | 3.4917 | 3.4686 | 3.4626 | 3.3991 | 3.4358 | 3.5344 | 3.4902 | 3.4308 | 3.5389 | 3.3813 | 3.4951 | 3.5136 | 3.5671 | 3.4937 | 3.4603 | 3.4696 | 3.4654 | 3.4767 | 3.4824 | 3.424 | 3.325 | 3.4251 | 3.427 | 3.4494 | 3.4399 | 3.5115 | 3.4634 | 3.5091 | 3.5095 | 3.4556 | 3.5593 | 3.3213 | 3.5694 | 3.5217 | 3.5161 | 3.4989 | 3.5579 | 3.509 | 3.5374 | 3.4862 | 3.4945 | 3.489 | 3.5658 | 3.5019 | 3.4832 | 3.5202 | 3.5131 | 3.5412 | 3.5355 | 3.5243 | 3.6032 | 3.6228 | 3.6841 | 3.6774 | 3.6668 | 3.4163 | 3.4903 | 3.4892 | 3.3976 | 3.487 | 3.4739 | 3.5352 | 3.5064 | 3.5748 | 3.5243 | 3.5314 | 3.54 | 3.5972 | 3.6008 | 3.5911 | 3.6311 | 3.4594 | 3.4989 | 3.5086 | 3.5483 | 3.4983 | 3.5341 | 3.4601 | 3.4729 | 3.5161 | 3.4898 | 3.5695 | 3.614 | 3.5593 | 3.5918 | 3.5648 | 3.4357
2025-06-07 | 3.9258 | 3.8413 | 3.9788 | 3.9758 | 3.9803 | 3.8633 | 4.0933 | 3.9174 | 4.0152 | 4.0462 | 4.0477 | 4.0189 | 4.0485 | 4.0379 | 4.0667 | 4.0568 | 4.012 | 4.0295 | 4.0174 | 4.0508 | 4.1818 | 4.1303 | 4.1621 | 4.1576 | 4.1432 | 4.1583 | 4.1614 | 4.1061 | 4.1674 | 4.1697 | 4.1402 | 4.1386 | 3.9886 | 3.945 | 3.9817 | 3.9992 | 4.067 | 4.0335 | 3.9985 | 4.0136 | 3.95 | 4.0371 | 4.1456 | 4.1367 | 4.1192 | 4.2207 | 4.1602 | 4.1371 | 3.9963 | 4.0921 | 4.1173 | 4.0232 | 3.9856 | 3.9565 | 3.886 | 3.9608 | 3.9657 | 3.8114 | 3.8219 | 3.7955 | 3.9848 | 3.9283 | 4.0081 | 4.2478 | 4.1943 | 4.2489 | 4.2391 | 4.225 | 4.2139 | 4.1767 | 4.3054 | 4.2426 | 4.1981 | 4.1214 | 4.1808 | 4.2139 | 4.1735 | 4.0521 | 4.1577 | 4.2578 | 4.0718 | 4.1634 | 4.2512 | 4.2504 | 4.1943 | 4.2713 | 4.2063 | 4.15 | 4.2605 | 4.2208 | 4.2412 | 4.0455 | 4.1629 | 4.1925 | 4.234 | 4.2029 | 4.1502 | 4.2095 | 4.196 | 4.1984 | 4.2139 | 4.2188 | 4.1501 | 4.2057 | 4.3437 | 4.2032 | 4.2716 | 4.2001 | 4.2129 | 4.3064 | 4.293 | 4.2391 | 4.2971 | 4.1602 | 4.1829 | 4.2419 | 4.1922 | 4.2564 | 4.3019 | 4.2826 | 4.2609 | 4.2536 | 4.2266 | 4.281 | 4.352 | 4.3447 | 4.2519 | 4.354 | 4.2374 | 4.2391 | 4.2039 | 4.323 | 4.2447 | 4.333 | 4.2371 | 4.3071 | 4.4055 | 4.2371 | 4.1321 | 4.1563 | 4.2195 | 4.1598 | 4.1932 | 4.2636 | 4.2267 | 4.2481 | 4.098 | 4.2983 | 4.2824 | 4.2201 | 4.2972 | 4.2536 | 4.3957 | 4.2253 | 4.2629 | 4.1881 | 4.3634 | 4.2164 | 4.2657 | 4.2312 | 4.2619 | 4.2353 | 4.215 | 4.2692 | 4.3392 | 4.2183 | 4.0635 | 4.1413 | 4.1444 | 4.1599 | 4.1568 | 4.1644 | 4.175 | 4.2222 | 4.2317 | 4.1943 | 4.1708 | 4.1939 | 4.2184 | 4.1817 | 4.2372 | 4.062 | 4.2139 | 4.1833 | 4.2275 | 4.2196 | 4.1527 | 4.2082 | 4.1402 | 4.1999 | 4.1066 | 4.2014 | 4.1712 | 3.65 | 4.1873 | 4.1833 | 4.2183 | 4.0902 | 4.2591 | 4.1849 | 4.1518 | 4.169 | 4.2434 | 4.1379 | 4.1936 | 4.2364 | 4.1707 | 4.0463 | 4.0827 | 3.5131 | 4.0229 | 4.219 | 4.1755 | 4.2386 | 4.2681 | 4.2786 | 4.289 | 4.25 | 3.9488 | 3.9503 | 4.1724 | 4.0214 | 3.9348 | 3.9869 | 4.0406 | 3.9393 | 4.1352 | 4.1277 | 4.2221 | 4.2386 | 4.281 | 4.2229 | 4.3214 | 4.1968 | 4.2547 | 4.2119 | 4.2237 | 4.2406 | 4.19 | 4.1448 | 4.1227 | 4.128 | 4.2508 | 4.3642 | 4.1888 | 4.1482 | 4.1841 | 4.1272 | 4.179 | 4.1624 | 4.1463 | 4.0764 | 4.1317 | 4.1755 | 4.1097 | 4.11 | 4.0517 | 4.0898 | 4.072 | 4.2646 | 4.2414 | 4.1717 | 4.2406 | 4.2302 | 4.2589 | 4.2868 | 4.2946 | 4.2345 | 4.2839 | 4.2834 | 4.1371 | 4.2527 | 4.1829 | 4.2658 | 4.3681 | 4.3703 | 4.2338 | 4.3295 | 4.2597 | 4.206 | 4.178 | 4.1735 | 4.1716 | 4.0351 | 4.1111 | 4.2132 | 4.1693 | 4.113 | 4.2562 | 4.0759 | 4.1863 | 4.257 | 4.2841 | 4.1647 | 4.1849 | 4.1754 | 4.1979 | 4.1604 | 4.1672 | 4.171 | 4.0845 | 4.1756 | 4.1741 | 4.2279 | 4.1964 | 4.247 | 4.2165 | 4.2509 | 4.2599 | 4.2214 | 4.2198 | 4.0291 | 4.2468 | 4.1736 | 4.1706 | 4.1631 | 4.244 | 4.1618 | 4.1489 | 4.1384 | 4.1597 | 4.2041 | 4.2181 | 4.1885 | 4.1504 | 4.1459 | 4.1538 | 4.1485 | 4.1937 | 4.1629 | 4.219 | 4.2037 | 4.3097 | 4.3171 | 4.2645 | 4.2016 | 4.2898 | 4.2539 | 4.1452 | 4.2435 | 4.2801 | 4.2547 | 4.2711 | 4.2887 | 4.0943 | 4.2822 | 4.2896 | 4.2539 | 4.2221 | 4.2578 | 4.2967 | 4.1705 | 4.1953 | 4.2184 | 4.2755 | 4.2254 | 4.2652 | 4.1633 | 4.2268 | 4.2397 | 4.2214 | 4.2779 | 4.2915 | 4.1672 | 4.2735 | 4.2335 | 4.1723
2025-06-08 | 4.7049 | 4.6013 | 4.75 | 4.7235 | 4.7311 | 4.6219 | 4.8738 | 4.6576 | 4.7803 | 4.7833 | 4.8303 | 4.7947 | 4.7644 | 4.7758 | 4.7992 | 4.7939 | 4.7791 | 4.8014 | 4.8091 | 4.8485 | 5.0008 | 4.9303 | 4.9758 | 4.9348 | 4.95 | 4.9621 | 4.9598 | 4.9053 | 4.9985 | 4.9833 | 4.9455 | 4.953 | 4.6803 | 4.6635 | 4.7065 | 4.7089 | 4.7927 | 4.7855 | 4.7189 | 4.7456 | 4.6773 | 4.7625 | 4.8696 | 4.8238 | 4.8246 | 4.9291 | 4.9229 | 4.8757 | 4.7751 | 4.8548 | 4.8526 | 4.7549 | 4.7201 | 4.7046 | 4.6512 | 4.718 | 4.6882 | 4.5238 | 4.5423 | 4.516 | 4.7682 | 4.6823 | 4.7009 | 5.1712 | 5.0932 | 5.0921 | 5.1149 | 5.1087 | 5.0759 | 5.0483 | 5.1663 | 5.1356 | 5.0462 | 4.9647 | 5.0455 | 5.1079 | 5.0346 | 5.1815 | 5.1925 | 5.195 | 5.0766 | 5.1772 | 5.2564 | 5.2175 | 5.1877 | 5.2096 | 5.1569 | 5.0717 | 5.1318 | 5.1415 | 5.1542 | 4.893 | 4.9748 | 4.9903 | 5.0576 | 5.0528 | 4.9429 | 5.0428 | 5.0628 | 5.0635 | 5.0422 | 5.1056 | 4.9759 | 5.1039 | 5.2288 | 5.0787 | 5.1798 | 5.0811 | 5.117 | 5.216 | 5.1943 | 5.1787 | 5.2045 | 5.0754 | 5.1208 | 5.1304 | 5.1473 | 5.1787 | 5.2557 | 5.2081 | 5.0704 | 5.1104 | 5.0786 | 5.1652 | 5.1615 | 5.1615 | 5.0524 | 5.1801 | 5.0566 | 5.1153 | 5.0721 | 5.0963 | 5.0873 | 5.1518 | 5.0638 | 5.1273 | 5.1133 | 4.9714 | 4.8552 | 4.8868 | 4.9037 | 4.9117 | 4.9734 | 5.0238 | 5.0041 | 5.0397 | 5.0428 | 5.1017 | 5.1402 | 5.0159 | 5.1206 | 5.0732 | 5.2203 | 5.03 | 5.0914 | 5.0342 | 5.1522 | 4.9258 | 5.0852 | 4.9924 | 5.0452 | 5.0732 | 4.9689 | 5.0628 | 5.1301 | 5.0606 | 4.8084 | 4.8148 | 4.8333 | 4.836 | 4.8375 | 4.8571 | 4.8878 | 4.9516 | 4.9611 | 4.9403 | 4.8379 | 4.8689 | 4.9441 | 4.8635 | 4.948 | 4.8258 | 4.9694 | 4.9361 | 4.9955 | 4.9879 | 4.9361 | 5.0151 | 4.9055 | 5.0215 | 4.8844 | 5.0457 | 4.9989 | 4.8299 | 5.0171 | 5.0171 | 5.0179 | 4.8707 | 4.9874 | 4.8568 | 4.8528 | 4.8932 | 4.9632 | 4.8339 | 4.8881 | 4.913 | 4.8539 | 4.8362 | 4.812 | 4.8247 | 4.8488 | 5.0405 | 4.8012 | 4.9572 | 5.0565 | 5.0193 | 5.0004 | 4.9455 | 4.7904 | 4.8078 | 4.9172 | 4.818 | 4.7918 | 4.7875 | 4.7965 | 4.8062 | 5.0632 | 5.0417 | 5.1166 | 5.1315 | 5.1205 | 5.0811 | 5.1676 | 5.0508 | 5.1676 | 5.0934 | 5.1048 | 5.1272 | 5.028 | 5.0093 | 4.9409 | 4.9824 | 5.1703 | 5.2119 | 4.9639 | 5 | 5.073 | 4.9895 | 5.0369 | 4.991 | 5.0404 | 4.9159 | 4.9544 | 4.9458 | 4.9836 | 4.9641 | 4.834 | 5.2665 | 5.1475 | 5.2392 | 5.207 | 5.113 | 5.1979 | 5.1096 | 5.1971 | 5.2137 | 5.1938 | 5.1464 | 5.1541 | 5.109 | 4.9889 | 5.0772 | 4.9758 | 5.0494 | 5.1217 | 5.1195 | 5.045 | 5.1409 | 5.0988 | 5.1935 | 5.1644 | 5.15 | 5.1712 | 4.9754 | 5.0964 | 5.1735 | 5.0933 | 5.0283 | 5.1977 | 4.8927 | 5.1508 | 5.1988 | 5.2111 | 5.1452 | 5.1183 | 5.156 | 5.137 | 5.1293 | 5.1426 | 5.1001 | 4.9626 | 5.0967 | 5.0849 | 5.1487 | 5.1134 | 5.153 | 5.1422 | 5.1943 | 5.1889 | 5.1282 | 5.1676 | 5.0444 | 5.2579 | 5.203 | 5.1592 | 5.1413 | 5.1897 | 5.0731 | 5.0878 | 5.1085 | 5.1648 | 5.1966 | 5.2306 | 5.1783 | 5.1454 | 5.1353 | 5.1405 | 5.1491 | 5.2078 | 5.148 | 5.2037 | 5.2092 | 5.2641 | 5.2747 | 5.2524 | 5.0942 | 5.2205 | 5.2101 | 5.046 | 5.2015 | 5.2123 | 5.2175 | 5.2325 | 5.2751 | 5.1708 | 5.2394 | 5.2394 | 5.2426 | 5.2123 | 5.2394 | 5.2881 | 5.1841 | 5.179 | 5.2145 | 5.2794 | 5.2194 | 5.2654 | 5.1727 | 5.1837 | 5.2377 | 5.1998 | 5.2202 | 5.2549 | 5.2684 | 5.2885 | 5.2527 | 5.0252
2025-06-09 | 4.4761 | 4.3692 | 4.5076 | 4.4879 | 4.4886 | 4.3751 | 4.593 | 4.3955 | 4.5152 | 4.5561 | 4.5341 | 4.503 | 4.5742 | 4.5583 | 4.6098 | 4.6023 | 4.5191 | 4.5439 | 4.5159 | 4.5591 | 4.722 | 4.6629 | 4.7311 | 4.7144 | 4.7061 | 4.7189 | 4.7303 | 4.6932 | 4.7727 | 4.7606 | 4.728 | 4.7485 | 4.4871 | 4.4506 | 4.4952 | 4.5191 | 4.6172 | 4.6021 | 4.547 | 4.5662 | 4.4985 | 4.5785 | 4.6824 | 4.6842 | 4.6674 | 4.7836 | 4.754 | 4.7083 | 4.6204 | 4.6971 | 4.684 | 4.5787 | 4.5368 | 4.5556 | 4.5152 | 4.5528 | 4.5148 | 4.3619 | 4.3658 | 4.3595 | 4.5758 | 4.5143 | 4.5418 | 4.8975 | 4.8216 | 4.8162 | 4.8475 | 4.8575 | 4.8398 | 4.7833 | 4.8861 | 4.8644 | 4.7919 | 4.7178 | 4.7978 | 4.8597 | 4.7983 | 4.9458 | 4.9614 | 4.9551 | 4.8575 | 4.9537 | 5.0069 | 5.2489 | 4.9434 | 4.9834 | 4.903 | 4.8301 | 4.8651 | 4.8982 | 4.8837 | 4.7378 | 4.8654 | 4.8986 | 4.9334 | 4.9355 | 4.8638 | 4.9344 | 4.9268 | 4.873 | 4.8939 | 4.8827 | 4.8109 | 4.8499 | 5.1429 | 4.8451 | 4.9113 | 4.8502 | 4.8634 | 4.9434 | 4.9134 | 4.9331 | 4.9524 | 4.8506 | 4.9161 | 4.9859 | 4.9451 | 5.0021 | 5.0262 | 5.0407 | 4.8223 | 4.9679 | 4.9416 | 5.0238 | 5.0145 | 4.9703 | 4.8885 | 4.9741 | 4.7153 | 4.9048 | 4.8423 | 4.832 | 4.8644 | 4.8651 | 4.8251 | 4.8992 | 4.8947 | 4.7343 | 4.6073 | 4.6084 | 4.6515 | 4.6366 | 4.6743 | 4.6836 | 4.6801 | 4.6877 | 4.6404 | 4.7269 | 4.7295 | 4.61 | 4.7091 | 4.7039 | 4.8356 | 4.6974 | 4.7591 | 4.6922 | 4.814 | 4.7647 | 4.6618 | 4.637 | 4.6784 | 4.5066 | 4.5535 | 4.8376 | 4.8375 | 4.6623 | 4.7052 | 4.7593 | 4.7268 | 4.7029 | 4.692 | 4.7029 | 4.6878 | 4.7407 | 4.7256 | 4.7177 | 4.754 | 4.7668 | 4.7646 | 4.252 | 4.7526 | 4.5335 | 4.7426 | 4.6954 | 4.7475 | 4.6289 | 4.6478 | 4.7007 | 4.6141 | 4.6882 | 4.5559 | 4.678 | 4.5998 | 4.6444 | 4.6512 | 4.6218 | 4.6901 | 4.5676 | 4.7252 | 4.6641 | 4.6782 | 4.7017 | 4.7862 | 4.6762 | 4.7512 | 4.8132 | 4.7959 | 4.6949 | 4.7913 | 3.7557 | 4.7007 | 4.836 | 4.6985 | 4.7166 | 4.7488 | 4.7898 | 4.7463 | 4.724 | 4.6324 | 4.5052 | 4.6866 | 4.5855 | 4.5568 | 4.575 | 4.5636 | 4.4501 | 4.6104 | 4.6022 | 4.657 | 4.7108 | 4.6491 | 4.6202 | 4.6856 | 4.5765 | 4.7657 | 4.6966 | 4.6715 | 4.633 | 4.5328 | 4.5358 | 4.4741 | 4.55 | 4.7622 | 4.7959 | 4.6927 | 4.6625 | 4.6919 | 4.652 | 4.6578 | 4.6501 | 4.5948 | 4.5313 | 4.5885 | 4.6378 | 4.5429 | 4.5829 | 4.4995 | 4.8073 | 4.8303 | 4.8983 | 4.8552 | 4.8737 | 4.8842 | 4.8127 | 4.8641 | 4.9172 | 4.9263 | 4.8935 | 4.8787 | 4.8172 | 4.6615 | 4.7179 | 4.6602 | 4.6785 | 4.7013 | 4.7427 | 4.7481 | 4.791 | 4.8216 | 4.9565 | 4.9282 | 4.8987 | 4.9592 | 4.7298 | 4.8707 | 4.8779 | 4.7838 | 4.7022 | 4.8942 | 4.7716 | 4.873 | 4.8844 | 4.8806 | 4.8956 | 4.8829 | 4.9228 | 4.9288 | 4.9056 | 4.9264 | 4.9078 | 4.6165 | 4.8764 | 4.8779 | 4.9025 | 4.8718 | 4.9082 | 4.8991 | 4.8938 | 4.9028 | 4.8631 | 4.9219 | 4.6932 | 4.9357 | 4.8501 | 4.8161 | 4.7862 | 4.8571 | 4.7629 | 4.5918 | 4.8113 | 4.8069 | 4.8465 | 4.8598 | 4.8296 | 4.7757 | 4.7795 | 4.7926 | 4.8135 | 4.8674 | 4.7896 | 4.8964 | 4.8874 | 4.9655 | 4.9804 | 4.9592 | 5.0602 | 5.1547 | 5.1215 | 4.9275 | 5.0606 | 5.0553 | 5.0325 | 5.0101 | 5.0295 | 4.917 | 4.9639 | 4.9843 | 4.9522 | 4.9108 | 4.971 | 5.0247 | 5.0792 | 5.1095 | 5.105 | 5.1499 | 5.0714 | 5.1331 | 5.0471 | 5.0549 | 5.0942 | 5.0518 | 5.0546 | 5.0599 | 5.0848 | 5.0655 | 4.9953 | 4.7664
2025-06-10 | 4.5837 | 4.4609 | 4.6561 | 4.628 | 4.6106 | 4.4715 | 4.7888 | 4.5705 | 4.6652 | 4.7045 | 4.7295 | 4.6864 | 4.6955 | 4.7068 | 4.7439 | 4.7227 | 4.6802 | 4.6994 | 4.6962 | 4.7212 | 4.8909 | 4.8076 | 4.8515 | 4.8326 | 4.8492 | 4.8424 | 4.8333 | 4.7492 | 4.8932 | 4.8682 | 4.8212 | 4.8167 | 4.5909 | 4.5463 | 4.5925 | 4.6212 | 4.7153 | 4.6954 | 4.6371 | 4.6483 | 4.5773 | 4.6769 | 4.8024 | 4.7763 | 4.7529 | 4.8842 | 4.8358 | 4.791 | 4.6852 | 4.7348 | 4.7676 | 4.6635 | 4.6205 | 4.6052 | 4.5387 | 4.5647 | 4.5988 | 4.4116 | 4.4369 | 4.3992 | 4.647 | 4.5637 | 4.6195 | 5.0883 | 5.0342 | 5.054 | 5.0876 | 5.0507 | 5.0441 | 4.9676 | 5.1101 | 5.0707 | 4.9952 | 4.9 | 4.9834 | 5.0285 | 4.9545 | 5.0493 | 5.0524 | 5.0835 | 4.9569 | 5.0384 | 5.1449 | 5.1284 | 5.0649 | 5.1703 | 5.061 | 4.9991 | 4.9827 | 5.0728 | 5.0628 | 4.9041 | 5.0269 | 5.0656 | 5.1225 | 5.0807 | 4.974 | 5.1028 | 5.0839 | 5.096 | 5.1071 | 5.0845 | 4.9867 | 5.0331 | 5.2329 | 5.0714 | 5.1394 | 5.0155 | 5.0621 | 5.1504 | 5.1391 | 5.1536 | 5.1776 | 5.0123 | 5.0045 | 4.9965 | 5.0145 | 5.0141 | 5.118 | 5.0997 | 5.0086 | 5.0141 | 4.9906 | 5.0714 | 5.0694 | 5.0569 | 4.9569 | 5.0642 | 4.9386 | 4.9676 | 4.9369 | 4.9593 | 4.9517 | 4.9993 | 4.9355 | 5.0248 | 5.0519 | 4.9327 | 4.8194 | 4.8644 | 4.9141 | 4.9241 | 4.9065 | 4.9448 | 4.9348 | 4.9634 | 4.8347 | 5.0335 | 5.0155 | 4.9066 | 4.971 | 4.9365 | 5.0571 | 4.8592 | 4.9065 | 4.8799 | 4.9824 | 4.9358 | 4.8278 | 4.9061 | 4.892 | 4.9186 | 4.832 | 4.9408 | 4.9772 | 4.8597 | 4.7952 | 4.881 | 4.8515 | 4.836 | 4.8337 | 4.8428 | 4.8636 | 4.938 | 4.9286 | 4.8987 | 4.8957 | 4.9051 | 4.9263 | 4.8651 | 4.9189 | 4.7229 | 4.9165 | 4.8632 | 4.9233 | 4.9252 | 4.8473 | 4.9373 | 4.8303 | 4.904 | 4.8008 | 4.9172 | 4.8802 | 4.9271 | 4.8992 | 4.8718 | 4.9357 | 4.7713 | 4.9169 | 4.8383 | 4.8685 | 4.901 | 4.9866 | 4.8427 | 4.9249 | 4.9567 | 4.9027 | 4.7699 | 4.8526 | 3.8387 | 4.7799 | 4.9078 | 4.8044 | 4.8438 | 4.8936 | 4.9063 | 4.9306 | 4.932 | 4.759 | 4.656 | 4.8659 | 4.7478 | 4.654 | 4.7039 | 4.757 | 4.6448 | 4.726 | 4.7453 | 4.8359 | 4.9031 | 4.865 | 4.8471 | 4.9415 | 4.834 | 4.9211 | 4.9019 | 4.905 | 4.894 | 4.8606 | 4.8266 | 4.8071 | 4.8154 | 4.905 | 5.0628 | 4.8226 | 4.7817 | 4.8203 | 4.7458 | 4.8218 | 4.7656 | 4.883 | 4.7843 | 4.8026 | 4.7757 | 4.8292 | 4.8314 | 4.7144 | 4.8551 | 4.8771 | 4.9751 | 4.9171 | 4.9402 | 4.95 | 4.8192 | 4.8651 | 5.0542 | 5.0546 | 4.9833 | 5.005 | 4.9232 | 4.7709 | 4.8485 | 4.7483 | 4.8427 | 4.9233 | 4.9542 | 4.8788 | 4.9773 | 4.9668 | 5.042 | 5.0166 | 5.0204 | 5.0385 | 4.859 | 4.9739 | 5.037 | 4.946 | 4.9225 | 5.068 | 4.8678 | 5.0457 | 5.0325 | 5.0183 | 5.019 | 5.0087 | 5.0479 | 5.0323 | 5.0174 | 4.9788 | 4.989 | 4.8806 | 4.9807 | 4.9958 | 5.0083 | 4.9913 | 5.0436 | 5.0372 | 5.0272 | 5.0321 | 4.9873 | 4.7881 | 4.8355 | 5.0786 | 5.0179 | 4.9959 | 4.9566 | 4.9667 | 4.8513 | 4.9122 | 4.8698 | 4.9682 | 4.9627 | 5.0478 | 4.9981 | 4.948 | 4.8998 | 4.9406 | 4.9152 | 4.9866 | 4.9019 | 4.874 | 4.8968 | 4.9423 | 4.9451 | 4.9478 | 4.8501 | 4.9619 | 4.9776 | 4.7477 | 4.9346 | 4.8643 | 4.9017 | 4.8494 | 4.9458 | 4.6012 | 4.9207 | 4.9451 | 4.9757 | 4.9289 | 4.9368 | 5.002 | 4.9775 | 4.9645 | 4.9862 | 5.0573 | 4.9922 | 5.0516 | 4.9368 | 4.9133 | 4.9959 | 4.9427 | 4.9666 | 4.9843 | 4.9792 | 4.9929 | 4.9419 | 4.8941
2025-06-11 | 5.008 | 4.9091 | 5.0598 | 5.0485 | 5.0538 | 4.9514 | 5.1798 | 4.9568 | 5.0735 | 5.1227 | 5.122 | 5.0932 | 5.125 | 5.1174 | 5.1636 | 5.1402 | 5.0901 | 5.1005 | 5.0848 | 5.1326 | 5.2924 | 5.2227 | 5.2629 | 5.2523 | 5.247 | 5.2606 | 5.2538 | 5.2492 | 5.2947 | 5.2788 | 5.2371 | 5.2598 | 5.0152 | 4.9904 | 5.0439 | 5.0558 | 5.1571 | 5.138 | 5.0636 | 5.0774 | 5.0045 | 5.0999 | 5.2178 | 5.22 | 5.1806 | 5.3111 | 5.2855 | 5.2339 | 5.1051 | 5.1696 | 5.1921 | 5.0703 | 5.0231 | 5.0193 | 4.953 | 5.0763 | 4.9845 | 4.8135 | 4.8243 | 4.8074 | 5.0697 | 4.9713 | 5.0418 | 5.4448 | 5.3872 | 5.4275 | 5.4589 | 5.4065 | 5.4488 | 5.3213 | 5.5059 | 5.4006 | 5.3182 | 5.2217 | 5.332 | 5.4441 | 5.3723 | 5.4331 | 5.4203 | 5.4689 | 5.3064 | 5.378 | 5.5224 | 5.4899 | 5.3754 | 5.5069 | 5.3975 | 5.3143 | 5.4617 | 5.4603 | 5.4503 | 5.2308 | 5.3706 | 5.4272 | 5.4821 | 5.392 | 5.267 | 5.4541 | 5.4068 | 5.4441 | 5.46 | 5.4272 | 5.343 | 5.3599 | 5.5787 | 5.3899 | 5.5197 | 5.3844 | 5.4465 | 5.5345 | 5.5166 | 5.5097 | 5.5661 | 5.7601 | 5.3906 | 5.3637 | 5.3741 | 5.4593 | 5.5321 | 5.529 | 5.4589 | 5.4279 | 5.4062 | 5.5022 | 5.5228 | 5.5128 | 5.4037 | 5.5224 | 5.4444 | 5.4241 | 5.3861 | 5.4531 | 5.3558 | 5.4545 | 5.3651 | 5.4451 | 5.54 | 5.4134 | 5.2533 | 5.3654 | 5.4272 | 5.3413 | 5.3858 | 5.4693 | 5.4241 | 5.5007 | 5.4141 | 5.5437 | 5.502 | 5.4008 | 5.4865 | 5.4006 | 5.5438 | 5.284 | 5.3551 | 5.3792 | 5.4965 | 5.4182 | 5.3464 | 5.3989 | 5.3696 | 5.1953 | 5.3199 | 5.3274 | 5.4013 | 5.4246 | 5.4067 | 5.4796 | 5.4626 | 5.4546 | 5.4392 | 5.4622 | 5.4754 | 5.5287 | 5.5336 | 5.4962 | 5.4819 | 5.4958 | 5.5283 | 5.4532 | 5.5022 | 5.2734 | 5.5204 | 5.466 | 5.5348 | 5.5231 | 5.4656 | 5.5163 | 5.39 | 5.4739 | 5.3394 | 5.469 | 5.3878 | 5.4626 | 5.4337 | 5.4075 | 5.502 | 5.2874 | 5.4992 | 5.3889 | 5.3549 | 5.3983 | 5.5387 | 5.3251 | 5.4133 | 5.5228 | 5.401 | 5.2615 | 5.4421 | 4.1336 | 5.3443 | 5.4542 | 5.3326 | 5.4215 | 5.5027 | 5.3604 | 5.5077 | 5.4775 | 5.0124 | 5.2701 | 5.4008 | 5.2407 | 5.1352 | 5.2538 | 5.1789 | 5.0145 | 5.3611 | 5.2697 | 5.4258 | 5.4478 | 5.4243 | 5.4261 | 5.4619 | 5.3626 | 5.4839 | 5.4207 | 5.4411 | 5.3505 | 5.3386 | 5.3386 | 5.2654 | 5.3304 | 5.4788 | 5.5345 | 5.394 | 5.3861 | 5.394 | 5.3753 | 5.3791 | 5.3708 | 5.3809 | 5.3039 | 5.3442 | 5.3644 | 5.3095 | 5.3652 | 5.0759 | 5.315 | 5.3421 | 5.458 | 5.4211 | 5.3831 | 5.3643 | 5.3443 | 5.4166 | 5.4981 | 5.5177 | 5.4007 | 5.4706 | 5.3496 | 5.1784 | 5.3643 | 5.1529 | 5.3598 | 5.4662 | 5.4792 | 5.3239 | 5.497 | 5.4299 | 5.4358 | 5.4206 | 5.4131 | 5.4252 | 5.2298 | 5.3292 | 5.4482 | 5.3647 | 5.2989 | 5.4887 | 5.2081 | 5.4501 | 5.4894 | 5.4687 | 5.3877 | 5.4056 | 5.4429 | 5.4578 | 5.4137 | 5.4149 | 5.4323 | 5.2136 | 5.4243 | 5.4152 | 5.4736 | 5.4384 | 5.4465 | 5.4649 | 5.4856 | 5.4806 | 5.4317 | 5.4411 | 5.2444 | 5.4746 | 5.4418 | 5.4156 | 5.3955 | 5.4278 | 5.309 | 5.3798 | 5.34 | 5.3819 | 5.3646 | 5.4706 | 5.3723 | 5.3588 | 5.3428 | 5.3618 | 5.3185 | 5.443 | 5.3779 | 5.385 | 5.3862 | 5.4639 | 5.4513 | 5.3952 | 5.3125 | 5.4829 | 5.4414 | 5.2815 | 5.422 | 5.4489 | 5.4452 | 5.4455 | 5.4863 | 5.3117 | 5.4509 | 5.4553 | 5.4728 | 5.4111 | 5.4431 | 5.4973 | 5.3935 | 5.4205 | 5.4489 | 5.4827 | 5.4524 | 5.4938 | 5.39 | 5.3787 | 5.4654 | 5.3999 | 5.44 | 5.4738 | 5.4376 | 5.4772 | 5.3811 | 5.3542
2025-06-12 | 4.6922 | 4.5853 | 4.7705 | 4.7295 | 4.7326 | 4.6188 | 4.9097 | 4.6826 | 4.7811 | 4.8197 | 4.8652 | 4.8205 | 4.8144 | 4.8258 | 4.8697 | 4.8667 | 4.8078 | 4.827 | 4.8485 | 4.8727 | 5.0727 | 4.9795 | 5.0197 | 4.9902 | 5.0341 | 5.0333 | 5.0106 | 4.9939 | 5.0871 | 5.0561 | 5.0023 | 5.0015 | 4.678 | 4.6715 | 4.7233 | 4.7337 | 4.8421 | 4.8437 | 4.7356 | 4.7695 | 4.6803 | 4.7682 | 4.8807 | 4.8677 | 4.8216 | 4.9522 | 4.9202 | 4.8831 | 4.8209 | 4.8939 | 4.882 | 4.7665 | 4.7136 | 4.7384 | 4.7003 | 4.823 | 4.748 | 4.5736 | 4.5982 | 4.5647 | 4.8439 | 4.7349 | 4.7243 | 5.2271 | 5.1394 | 5.1405 | 5.1667 | 5.1601 | 5.1474 | 5.1204 | 5.2426 | 5.1805 | 5.1197 | 5.0186 | 5.1135 | 5.1634 | 5.0855 | 5.2833 | 5.2802 | 5.2826 | 5.1394 | 5.2331 | 5.3326 | 5.2958 | 5.2384 | 5.2778 | 5.2157 | 5.1014 | 5.1839 | 5.2405 | 5.2319 | 5.0411 | 5.1898 | 5.2188 | 5.2878 | 5.2402 | 5.1502 | 5.2502 | 5.0776 | 5.2518 | 5.2684 | 5.2005 | 5.1201 | 5.1722 | 5.3792 | 5.2095 | 5.2692 | 5.1598 | 5.2036 | 5.2712 | 5.2433 | 5.2729 | 5.2865 | 5.1299 | 5.2043 | 5.2277 | 5.2384 | 5.2978 | 5.2823 | 5.3537 | 5.2512 | 5.1839 | 5.1757 | 5.2969 | 5.2212 | 5.1629 | 5.1052 | 5.1829 | 5.1577 | 5.1042 | 5.0414 | 5.0783 | 5.0483 | 5.0908 | 5.0155 | 5.1025 | 5.0202 | 5.0673 | 4.9698 | 5.0217 | 5.059 | 5.0141 | 5.0742 | 5.1387 | 5.0897 | 5.1667 | 5.0725 | 5.2125 | 5.172 | 5.0678 | 5.144 | 5.1194 | 5.2063 | 4.9986 | 5.0148 | 4.8623 | 5.0925 | 5.0048 | 4.9051 | 5.0369 | 5.0273 | 5.0694 | 4.9883 | 5.0271 | 5.0718 | 5.0833 | 4.9977 | 5.051 | 5.0197 | 4.9845 | 4.9501 | 4.9603 | 4.986 | 5.0627 | 5.0722 | 5.0314 | 5.054 | 5.059 | 5.0605 | 5.019 | 5.0895 | 4.9232 | 5.0782 | 5.099 | 5.0949 | 5.085 | 5.1036 | 5.124 | 5.0261 | 5.1077 | 4.9837 | 5.1122 | 5.0552 | 5.1168 | 5.094 | 5.0742 | 5.1409 | 4.9515 | 5.1018 | 4.989 | 4.9921 | 4.9218 | 5.1077 | 4.967 | 5.0563 | 5.1036 | 5.0481 | 4.9251 | 5.036 | 3.6828 | 4.8464 | 5.0764 | 5.015 | 5.0349 | 5.1307 | 5.1287 | 5.1124 | 5.0632 | 4.9009 | 4.8985 | 4.979 | 4.8705 | 4.7398 | 4.7406 | 4.836 | 4.6899 | 4.9929 | 4.9575 | 5.0644 | 5.0993 | 5.1005 | 5.0804 | 5.1519 | 5.0258 | 5.1283 | 5.0895 | 5.104 | 4.865 | 5.0355 | 4.9761 | 4.9802 | 5.003 | 5.1142 | 5.102 | 5.0263 | 4.9895 | 5.0428 | 4.9802 | 5.0526 | 5.0329 | 5.0262 | 4.9462 | 5.0561 | 5.0501 | 5.0168 | 5.003 | 4.8961 | 5.2455 | 5.1345 | 5.2392 | 5.1945 | 5.1786 | 5.1688 | 4.9841 | 5.0898 | 5.2076 | 5.2031 | 5.1362 | 5.147 | 5.0929 | 4.9787 | 5.1034 | 4.9401 | 5.051 | 5.0955 | 5.1068 | 5.0229 | 5.1421 | 5.1024 | 5.2521 | 5.2305 | 5.2249 | 5.237 | 5.0261 | 5.1561 | 5.24 | 5.1444 | 5.1092 | 5.2683 | 5.0669 | 5.2336 | 5.2502 | 5.2536 | 5.2238 | 5.2262 | 5.2683 | 5.2846 | 5.267 | 5.2723 | 5.2526 | 4.9401 | 5.2196 | 5.2275 | 5.204 | 5.1877 | 5.2654 | 5.2309 | 5.237 | 5.2325 | 5.1635 | 5.2684 | 5.0775 | 5.281 | 5.2067 | 5.1876 | 5.1626 | 5.2087 | 5.0835 | 5.1562 | 5.1317 | 5.1589 | 5.1837 | 5.253 | 5.1977 | 5.1633 | 5.1574 | 5.179 | 4.9578 | 5.2099 | 5.1617 | 5.2261 | 5.2826 | 5.3509 | 5.3571 | 5.3493 | 5.2131 | 5.3558 | 5.3192 | 5.1693 | 5.3304 | 5.3304 | 5.317 | 5.3125 | 5.3641 | 5.2302 | 5.3049 | 5.3179 | 5.3319 | 5.2801 | 5.3187 | 5.3752 | 5.2662 | 5.2919 | 5.3248 | 5.3736 | 5.3265 | 5.3764 | 5.2512 | 5.2794 | 5.3454 | 5.2998 | 5.3371 | 5.3607 | 5.3222 | 5.3599 | 5.2692 | 5.079
2025-06-13 | 4.3293 | 4.2424 | 4.3894 | 4.3742 | 4.3939 | 4.2908 | 4.5126 | 4.3242 | 4.4402 | 4.4705 | 4.4591 | 4.4364 | 4.4379 | 4.4803 | 4.4955 | 4.5114 | 4.445 | 4.4904 | 4.4515 | 4.4992 | 4.6318 | 4.5659 | 4.6288 | 4.6197 | 4.5576 | 4.5606 | 4.5833 | 4.5894 | 4.5742 | 4.547 | 4.5258 | 4.5606 | 4.3295 | 4.3293 | 4.3772 | 4.3604 | 4.4498 | 4.4649 | 4.3697 | 4.4011 | 4.3409 | 4.433 | 4.5527 | 4.5117 | 4.5154 | 4.6078 | 4.6092 | 4.5585 | 4.4768 | 4.5492 | 4.4106 | 4.4322 | 4.3932 | 4.3885 | 4.3349 | 4.4682 | 4.4052 | 4.2384 | 4.2372 | 4.217 | 4.4053 | 4.3463 | 4.3827 | 4.7805 | 4.7088 | 4.7002 | 4.7322 | 4.7481 | 4.7268 | 4.696 | 4.7899 | 4.7346 | 4.6781 | 4.5999 | 4.6653 | 4.7468 | 4.675 | 4.6694 | 4.7412 | 4.7174 | 4.5994 | 4.6991 | 4.7843 | 4.7605 | 4.7326 | 4.7951 | 4.732 | 4.6511 | 4.7319 | 4.7284 | 4.7547 | 4.5483 | 4.6259 | 4.6818 | 4.6981 | 4.7792 | 4.6737 | 4.7415 | 4.7226 | 4.6602 | 4.7399 | 4.7053 | 4.6403 | 4.658 | 4.9917 | 4.6573 | 4.7353 | 4.7426 | 4.696 | 4.8299 | 4.774 | 4.5859 | 4.771 | 4.671 | 4.6546 | 4.725 | 4.7001 | 4.754 | 4.7698 | 4.7692 | 4.7422 | 4.7547 | 4.7302 | 4.7879 | 4.8361 | 4.8233 | 4.6218 | 4.8565 | 4.7553 | 4.7578 | 4.7578 | 4.7712 | 4.7899 | 4.8064 | 4.7177 | 4.7371 | 4.7821 | 4.7326 | 4.6079 | 4.6698 | 4.6856 | 4.6791 | 4.7298 | 4.7643 | 4.7067 | 4.7802 | 4.7481 | 4.8741 | 4.8261 | 4.7677 | 4.8163 | 4.7239 | 4.873 | 4.6815 | 4.6787 | 4.6946 | 4.7419 | 4.705 | 4.5676 | 4.7384 | 4.7053 | 4.7733 | 4.696 | 4.6515 | 4.7112 | 4.7803 | 4.3632 | 4.4713 | 4.5461 | 4.5899 | 4.5964 | 4.6315 | 4.6689 | 4.7513 | 4.7816 | 4.7048 | 4.4433 | 4.5193 | 4.6644 | 4.5147 | 4.5754 | 4.4232 | 4.6361 | 4.5903 | 4.647 | 4.8122 | 4.729 | 4.8307 | 4.5461 | 4.7215 | 4.5317 | 4.7041 | 4.7423 | 4.7997 | 4.7349 | 4.7381 | 4.8373 | 4.5403 | 4.613 | 4.48 | 4.4302 | 4.4458 | 4.5236 | 4.4247 | 4.456 | 4.4851 | 4.4284 | 4.3214 | 4.396 | 4.3971 | 4.3724 | 4.5849 | 4.5686 | 4.6307 | 4.6409 | 4.6207 | 4.6175 | 4.5413 | 4.13 | 4.3281 | 4.4727 | 4.3562 | 4.2952 | 4.1352 | 4.3865 | 4.3602 | 4.7802 | 4.7734 | 4.8544 | 4.894 | 4.8077 | 4.8206 | 4.8568 | 4.7724 | 4.8603 | 4.8089 | 4.8442 | 4.7755 | 4.7769 | 4.7421 | 4.7264 | 4.6995 | 4.8132 | 4.8195 | 4.7288 | 4.6868 | 4.719 | 4.6543 | 4.7068 | 4.6561 | 4.7271 | 4.6045 | 4.6797 | 4.5896 | 4.6782 | 4.624 | 4.4797 | 4.6214 | 4.6572 | 4.7567 | 4.7061 | 4.7306 | 4.7429 | 4.7142 | 4.7311 | 4.813 | 4.8485 | 4.7884 | 4.8191 | 4.7341 | 4.5921 | 4.7121 | 4.6091 | 4.6952 | 4.7741 | 4.7671 | 4.6563 | 4.7877 | 4.7549 | 4.7846 | 4.777 | 4.763 | 4.8197 | 4.6122 | 4.7547 | 4.7623 | 4.6788 | 4.655 | 4.7986 | 4.6287 | 4.7589 | 4.7732 | 4.7802 | 4.802 | 4.7687 | 4.8166 | 4.7987 | 4.7812 | 4.7774 | 4.7554 | 4.7324 | 4.7755 | 4.7592 | 4.8017 | 4.7717 | 4.7702 | 4.7831 | 4.7736 | 4.7885 | 4.7544 | 4.7496 | 4.6307 | 4.769 | 4.7208 | 4.6909 | 4.6703 | 4.7155 | 4.5972 | 4.6778 | 4.6257 | 4.7057 | 4.739 | 4.7847 | 4.7477 | 4.6815 | 4.6647 | 4.6879 | 4.504 | 4.7321 | 4.6829 | 4.7002 | 4.7414 | 4.8167 | 4.8273 | 4.8356 | 4.8778 | 5.0064 | 4.9843 | 4.8131 | 4.9495 | 4.9514 | 4.9092 | 4.8957 | 4.9081 | 4.7694 | 4.8509 | 4.8666 | 4.8434 | 4.8116 | 4.8607 | 4.9168 | 4.9365 | 4.9495 | 4.957 | 5.0035 | 4.9336 | 4.9768 | 4.894 | 4.8987 | 4.929 | 4.9035 | 4.925 | 4.9356 | 4.9219 | 4.9286 | 4.8308 | 4.6678
2025-06-14 | 3.4777 | 3.4163 | 3.5167 | 3.522 | 3.497 | 3.388 | 3.6052 | 3.4523 | 3.5311 | 3.5477 | 3.5561 | 3.5303 | 3.5424 | 3.5386 | 3.5659 | 3.5561 | 3.5191 | 3.5542 | 3.5417 | 3.5712 | 3.672 | 3.6379 | 3.6462 | 3.6462 | 3.6477 | 3.6515 | 3.6553 | 3.6508 | 3.6848 | 3.6765 | 3.6447 | 3.6583 | 3.4659 | 3.441 | 3.4769 | 3.4992 | 3.5614 | 3.5518 | 3.497 | 3.5231 | 3.475 | 3.5342 | 3.6117 | 3.598 | 3.5994 | 3.691 | 3.6723 | 3.6405 | 3.5489 | 3.6029 | 3.4736 | 3.5149 | 3.4841 | 3.4886 | 3.4385 | 3.5297 | 3.5047 | 3.3689 | 3.3778 | 3.3463 | 3.5106 | 3.4626 | 3.4993 | 3.7968 | 3.7636 | 3.7809 | 3.7895 | 3.8068 | 3.7978 | 3.7312 | 3.5597 | 3.8057 | 3.7536 | 3.7058 | 3.7498 | 3.7796 | 3.7215 | 3.7605 | 3.7778 | 3.7923 | 3.7302 | 3.7841 | 3.8233 | 3.8171 | 3.8075 | 3.8196 | 3.7817 | 3.7588 | 3.7968 | 3.7833 | 3.7961 | 3.6839 | 3.7757 | 3.7816 | 3.8168 | 3.8144 | 3.7883 | 3.7874 | 3.7933 | 3.781 | 3.7875 | 3.8085 | 3.7154 | 3.8133 | 3.9948 | 3.7971 | 3.8523 | 3.7919 | 3.8133 | 3.8744 | 3.8527 | 3.8734 | 3.8617 | 3.7771 | 3.7533 | 3.8033 | 3.784 | 3.8112 | 3.834 | 3.8216 | 3.7961 | 3.7805 | 3.7435 | 3.8009 | 3.8164 | 3.8116 | 3.7229 | 3.8068 | 3.7512 | 3.7512 | 3.7208 | 3.7484 | 3.7512 | 3.7864 | 3.7322 | 3.793 | 3.8268 | 3.7785 | 3.7057 | 3.7129 | 3.7367 | 3.7181 | 3.7422 | 3.7633 | 3.7478 | 3.8006 | 3.6577 | 3.7962 | 3.7801 | 3.9358 | 3.7774 | 3.7647 | 3.8405 | 3.7281 | 3.7564 | 3.7654 | 3.7864 | 3.6625 | 3.7415 | 3.5807 | 3.7353 | 3.7467 | 3.7484 | 3.7788 | 3.8161 | 3.7608 | 3.6255 | 3.6954 | 3.672 | 3.5374 | 3.6807 | 3.6901 | 3.6909 | 3.7286 | 3.7498 | 3.7079 | 3.7011 | 3.7226 | 3.7506 | 3.7036 | 3.7324 | 3.5952 | 3.7423 | 3.7324 | 3.6795 | 3.7309 | 3.726 | 3.7317 | 3.6674 | 3.7007 | 3.6243 | 3.6927 | 3.6772 | 3.7158 | 3.6925 | 3.6806 | 3.7345 | 3.6373 | 3.7523 | 3.6715 | 3.6893 | 3.7083 | 3.7618 | 3.6875 | 3.7363 | 3.7746 | 3.7506 | 3.6528 | 3.7059 | 3.6888 | 3.6322 | 3.749 | 3.6977 | 3.7104 | 3.7524 | 3.7727 | 3.7557 | 3.7232 | 3.6296 | 3.6155 | 3.6891 | 3.6068 | 3.5505 | 3.5665 | 3.6142 | 3.5327 | 3.6271 | 3.6196 | 3.69 | 3.6958 | 3.7017 | 3.6723 | 3.7406 | 3.6495 | 3.7162 | 3.6758 | 3.686 | 3.6837 | 3.5666 | 3.6608 | 3.5494 | 3.6469 | 3.706 | 3.7323 | 3.6554 | 3.6346 | 3.6648 | 3.641 | 3.6519 | 3.641 | 3.641 | 3.5853 | 3.5957 | 3.6294 | 3.6058 | 3.6335 | 3.6002 | 3.7302 | 3.6486 | 3.724 | 3.7037 | 3.7353 | 3.7435 | 3.7088 | 3.7368 | 3.7705 | 3.7772 | 3.7421 | 3.7627 | 3.7461 | 3.6317 | 3.6712 | 3.6592 | 3.6761 | 3.7402 | 3.7406 | 3.7008 | 3.7627 | 3.737 | 3.6961 | 3.689 | 3.678 | 3.6931 | 3.6062 | 3.6466 | 3.698 | 3.6459 | 3.6104 | 3.7245 | 3.6643 | 3.6893 | 3.7105 | 3.7127 | 3.6901 | 3.6865 | 3.7085 | 3.7226 | 3.7137 | 3.7258 | 3.7088 | 3.6777 | 3.7012 | 3.6852 | 3.7327 | 3.7046 | 3.7119 | 3.7129 | 3.7166 | 3.725 | 3.694 | 3.3893 | 3.2854 | 3.7214 | 3.6761 | 3.6555 | 3.6413 | 3.6694 | 3.5975 | 3.0549 | 3.5393 | 3.6244 | 3.5597 | 3.6604 | 3.4522 | 3.6155 | 3.5501 | 3.5871 | 3.2504 | 3.6969 | 3.6213 | 3.584 | 3.206 | 3.4553 | 3.4537 | 3.2441 | 3.5998 | 3.6839 | 3.6623 | 3.5557 | 3.6421 | 3.6604 | 3.663 | 3.6593 | 3.6929 | 3.6219 | 3.6739 | 3.6617 | 3.6925 | 3.6479 | 3.6723 | 3.7166 | 3.6364 | 3.66 | 3.6753 | 3.6868 | 3.6835 | 3.6914 | 3.6546 | 3.6401 | 3.6813 | 3.6562 | 3.6852 | 3.6929 | 3.7096 | 3.7111 | 3.6876 | 3.6738
2025-06-15 | 4.0654 | 3.9936 | 4.1227 | 4.1136 | 4.0803 | 3.94 | 4.2272 | 4.0318 | 4.1045 | 4.1485 | 4.1773 | 4.1311 | 4.1553 | 4.1333 | 4.1773 | 4.1652 | 4.1204 | 4.1571 | 4.1591 | 4.1856 | 4.3242 | 4.2735 | 4.2773 | 4.2758 | 4.2932 | 4.2992 | 4.3008 | 4.2917 | 4.3341 | 4.3227 | 4.2879 | 4.2788 | 4.0553 | 4.0287 | 4.0774 | 4.1037 | 4.1866 | 4.1523 | 4.0977 | 4.1276 | 4.0758 | 4.1462 | 4.2198 | 4.1981 | 4.2105 | 4.309 | 4.2788 | 3.9019 | 4.1785 | 4.2324 | 4.2361 | 4.1349 | 4.0974 | 4.0952 | 4.049 | 4.1575 | 4.0927 | 3.9572 | 3.9641 | 3.9353 | 4.1379 | 4.0709 | 4.0902 | 4.4665 | 4.4337 | 4.4365 | 4.4645 | 4.4745 | 4.4558 | 4.3979 | 4.4955 | 4.4707 | 4.4044 | 4.3286 | 4.3992 | 4.4394 | 4.3644 | 4.4124 | 4.4448 | 4.4665 | 4.3879 | 4.4329 | 4.4693 | 4.4906 | 4.4434 | 4.4596 | 4.4376 | 4.3947 | 4.4507 | 4.4403 | 4.4655 | 4.2702 | 4.4044 | 4.4161 | 4.472 | 4.4503 | 4.3813 | 4.4155 | 4.4438 | 4.4484 | 4.4188 | 4.47 | 4.3359 | 4.4593 | 4.6843 | 4.4513 | 4.5307 | 4.4496 | 4.4907 | 4.5504 | 4.5338 | 4.5424 | 4.5291 | 4.4221 | 4.4199 | 4.4541 | 4.4438 | 4.4896 | 4.4976 | 4.5104 | 4.4627 | 4.4406 | 4.3947 | 4.4729 | 4.4834 | 4.4748 | 4.3761 | 4.4752 | 4.4106 | 4.403 | 4.3678 | 4.3989 | 4.3872 | 4.4431 | 4.3758 | 4.4469 | 4.4812 | 4.332 | 4.2365 | 4.1843 | 4.3182 | 4.2636 | 4.3012 | 4.3351 | 4.3237 | 4.3685 | 4.2585 | 4.3741 | 4.3988 | 4.2973 | 4.4048 | 4.3602 | 4.4883 | 4.3337 | 4.3827 | 4.3923 | 4.3747 | 4.3875 | 4.3668 | 4.0549 | 4.3509 | 4.0952 | 4.3558 | 4.3935 | 4.4382 | 4.3709 | 4.2528 | 4.3371 | 4.3042 | 4.0937 | 4.2577 | 4.2698 | 4.2714 | 4.3039 | 4.3296 | 4.2766 | 4.3386 | 4.3511 | 4.3288 | 4.2996 | 4.3086 | 4.1219 | 4.3008 | 4.277 | 4.3114 | 4.3008 | 4.2872 | 4.3012 | 4.2105 | 4.2532 | 4.1553 | 4.2517 | 4.2498 | 4.2891 | 4.2516 | 4.2456 | 4.302 | 4.1577 | 4.3091 | 4.2331 | 4.2639 | 4.2871 | 4.3614 | 4.2409 | 4.3372 | 4.3987 | 4.3519 | 4.2354 | 4.3114 | 4.3096 | 4.0547 | 4.1903 | 4.2376 | 4.2681 | 4.3112 | 4.339 | 4.3212 | 4.2927 | 4.2 | 4.1993 | 4.2604 | 4.1535 | 4.0487 | 4.1119 | 4.1381 | 4.0329 | 4.2008 | 4.1676 | 4.2488 | 4.2398 | 4.3014 | 4.2543 | 4.3458 | 4.2334 | 4.252 | 4.2057 | 4.2284 | 4.2524 | 4.2005 | 4.208 | 4.1672 | 4.0958 | 4.239 | 4.2308 | 4.1958 | 4.1485 | 4.1864 | 4.165 | 4.175 | 4.1571 | 4.1635 | 4.0872 | 4.1635 | 4.1687 | 4.1328 | 4.1594 | 4.1366 | 4.3656 | 4.2803 | 4.3864 | 4.3497 | 4.3748 | 4.3531 | 4.3273 | 4.3587 | 4.4095 | 4.4263 | 4.3929 | 4.4224 | 4.3464 | 4.1466 | 4.267 | 4.2232 | 4.2684 | 4.3721 | 4.376 | 4.3123 | 4.4014 | 4.3749 | 4.3813 | 4.3866 | 4.3787 | 4.381 | 4.2305 | 4.3039 | 4.4017 | 4.3178 | 4.2823 | 4.4082 | 4.2398 | 4.3723 | 4.381 | 4.3817 | 4.3556 | 4.3619 | 4.3881 | 4.3885 | 4.3857 | 4.405 | 4.3811 | 4.2703 | 4.3553 | 4.3489 | 4.3921 | 4.3557 | 4.3912 | 4.3694 | 4.3723 | 4.3714 | 4.3397 | 4.3791 | 4.1434 | 4.4202 | 4.3593 | 4.3474 | 4.322 | 4.3369 | 4.2502 | 3.8533 | 4.2347 | 4.301 | 4.325 | 4.3799 | 4.3137 | 4.2659 | 4.2924 | 4.279 | 4.1945 | 4.3766 | 4.2865 | 4.2881 | 4.0165 | 4.356 | 4.3489 | 4.0848 | 4.1441 | 4.2696 | 4.2554 | 4.1302 | 4.2431 | 4.2345 | 4.2536 | 4.2353 | 4.2951 | 4.2192 | 4.279 | 4.2936 | 4.3126 | 4.2725 | 4.2747 | 4.3206 | 4.249 | 4.3096 | 4.3059 | 4.3187 | 4.3385 | 4.3235 | 4.2857 | 4.2779 | 4.0854 | 4.3026 | 4.2971 | 4.3171 | 4.3626 | 4.3308 | 4.3053 | 4.2932
2025-06-16 | 1.508 | 1.453 | 1.5295 | 1.5136 | 1.5136 | 1.4442 | 1.5731 | 1.4939 | 1.5417 | 1.5364 | 1.5492 | 1.5371 | 1.5417 | 1.5348 | 1.5576 | 1.5455 | 1.5239 | 1.567 | 1.5667 | 1.5682 | 1.6265 | 1.6098 | 1.6061 | 1.5955 | 1.6227 | 1.6197 | 1.6288 | 1.6205 | 1.6424 | 1.6356 | 1.6189 | 1.6 | 1.5152 | 1.492 | 1.5016 | 1.5183 | 1.5439 | 1.5239 | 1.5159 | 1.5375 | 1.4992 | 1.5471 | 1.5825 | 1.5592 | 1.5775 | 1.6223 | 1.622 | 1.6062 | 1.5654 | 1.5918 | 1.5982 | 1.5468 | 1.539 | 1.539 | 1.5256 | 1.5458 | 1.5571 | 1.4825 | 1.4936 | 1.4715 | 1.5273 | 1.5374 | 1.5293 | 1.6798 | 1.6563 | 1.6698 | 1.6608 | 1.687 | 1.6679 | 1.6532 | 1.6825 | 1.6957 | 1.6591 | 1.6536 | 1.6591 | 1.6623 | 1.6288 | 1.6536 | 1.6667 | 1.6708 | 1.6522 | 1.6782 | 1.6767 | 1.6789 | 1.6912 | 1.6782 | 1.6742 | 1.6675 | 1.6781 | 1.6591 | 1.6677 | 1.6004 | 1.6335 | 1.6449 | 1.6553 | 1.6777 | 1.6705 | 1.6687 | 1.6646 | 1.6346 | 1.6544 | 1.6694 | 1.6252 | 1.6867 | 1.7488 | 1.6805 | 1.6915 | 1.6767 | 1.6563 | 1.706 | 1.6977 | 1.7139 | 1.6916 | 1.6768 | 1.6553 | 1.6994 | 1.6829 | 1.6805 | 1.6943 | 1.6743 | 1.6725 | 1.6767 | 1.6515 | 1.6717 | 1.6915 | 1.6881 | 1.6442 | 1.6877 | 1.656 | 1.6605 | 1.6491 | 1.6625 | 1.6746 | 1.686 | 1.657 | 1.6825 | 1.6999 | 1.6919 | 1.674 | 1.6042 | 1.6553 | 1.6777 | 1.6812 | 1.6729 | 1.6618 | 1.6932 | 1.6832 | 1.689 | 1.6832 | 1.6566 | 1.6726 | 1.6805 | 1.7101 | 1.6774 | 1.6753 | 1.6736 | 1.6781 | 1.6791 | 1.6791 | 1.6118 | 1.6646 | 1.6718 | 1.6784 | 1.6968 | 1.7112 | 1.671 | 1.599 | 1.6459 | 1.6092 | 1.5472 | 1.627 | 1.624 | 1.6255 | 1.6553 | 1.6795 | 1.6587 | 1.6481 | 1.6659 | 1.6856 | 1.6472 | 1.6772 | 1.6288 | 1.6754 | 1.6822 | 1.6825 | 1.6614 | 1.6761 | 1.6723 | 1.6515 | 1.6576 | 1.6198 | 1.641 | 1.655 | 1.6618 | 1.6393 | 1.6393 | 1.6873 | 1.6217 | 1.6649 | 1.6432 | 1.6489 | 1.6586 | 1.6737 | 1.6588 | 1.677 | 1.687 | 1.6804 | 1.6473 | 1.6487 | 1.6435 | 1.6262 | 1.7507 | 1.6683 | 1.6699 | 1.6601 | 1.6849 | 1.6707 | 1.6484 | 1.6336 | 1.6168 | 1.6487 | 1.6132 | 1.5733 | 1.5722 | 1.6421 | 1.6354 | 1.6145 | 1.6309 | 1.6538 | 1.6436 | 1.6515 | 1.6177 | 1.6672 | 1.6401 | 1.6652 | 1.6452 | 1.6468 | 1.6472 | 1.4846 | 1.6177 | 1.5074 | 1.5482 | 1.6994 | 1.7229 | 1.6766 | 1.6461 | 1.6507 | 1.6162 | 1.6429 | 1.6315 | 1.6412 | 1.6072 | 1.5519 | 1.6457 | 1.6039 | 1.6274 | 1.6319 | 1.6544 | 1.6341 | 1.6586 | 1.647 | 1.6761 | 1.6853 | 1.6663 | 1.6696 | 1.674 | 1.6739 | 1.6644 | 1.6726 | 1.6863 | 1.6433 | 1.6314 | 1.661 | 1.6346 | 1.661 | 1.7007 | 1.6521 | 1.6781 | 1.6637 | 1.6538 | 1.6406 | 1.6085 | 1.6104 | 1.5888 | 1.6236 | 1.6447 | 1.6172 | 1.5964 | 1.6678 | 1.6553 | 1.6304 | 1.6534 | 1.6742 | 1.6488 | 1.6083 | 1.6233 | 1.645 | 1.6341 | 1.642 | 1.6435 | 1.6521 | 1.6413 | 1.6238 | 1.6462 | 1.6519 | 1.6298 | 1.6371 | 1.6553 | 1.6508 | 1.5524 | 1.6519 | 1.6091 | 1.6734 | 1.6502 | 1.6312 | 1.6199 | 1.6512 | 1.6066 | 1.4839 | 1.6533 | 1.5969 | 1.6456 | 1.7048 | 1.6726 | 1.6726 | 1.6398 | 1.6555 | 1.6084 | 1.6902 | 1.6397 | 1.6519 | 1.4007 | 1.6876 | 1.6994 | 1.5369 | 1.5882 | 1.6151 | 1.6386 | 1.5557 | 1.5986 | 1.617 | 1.6005 | 1.6042 | 1.639 | 1.5833 | 1.6209 | 1.6327 | 1.6383 | 1.6008 | 1.6071 | 1.6515 | 1.6134 | 1.5542 | 1.5874 | 1.6126 | 1.613 | 1.596 | 1.6105 | 1.5965 | 1.5175 | 1.5973 | 1.6401 | 1.6153 | 1.6409 | 1.6535 | 1.6091 | 1.632
2025-06-17 | 1.5008 | 1.4617 | 1.528 | 1.5121 | 1.4992 | 1.4275 | 1.5723 | 1.4886 | 1.5295 | 1.5197 | 1.5462 | 1.5288 | 1.5235 | 1.5136 | 1.5379 | 1.5341 | 1.5128 | 1.5574 | 1.5614 | 1.5614 | 1.6212 | 1.6053 | 1.5841 | 1.5856 | 1.6076 | 1.6106 | 1.6227 | 1.6129 | 1.6409 | 1.6242 | 1.6136 | 1.5909 | 1.4864 | 1.4641 | 1.4841 | 1.496 | 1.5247 | 1.504 | 1.4886 | 1.5207 | 1.4841 | 1.5285 | 1.5576 | 1.5336 | 1.5504 | 1.5933 | 1.5965 | 1.5753 | 1.5397 | 1.575 | 1.5667 | 1.5185 | 1.5087 | 1.5224 | 1.5076 | 1.5297 | 1.5497 | 1.4748 | 1.4864 | 1.4652 | 1.5227 | 1.5143 | 1.4993 | 1.686 | 1.6698 | 1.6836 | 1.6774 | 1.6449 | 1.6734 | 1.6577 | 1.6888 | 1.6984 | 1.6615 | 1.6536 | 1.6577 | 1.6602 | 1.627 | 1.6594 | 1.6708 | 1.6739 | 1.6536 | 1.6875 | 1.6846 | 1.6847 | 1.7015 | 1.7789 | 1.6908 | 1.5469 | 1.6815 | 1.6929 | 1.666 | 1.6456 | 1.6767 | 1.695 | 1.7026 | 1.7239 | 1.719 | 1.7108 | 1.7067 | 1.6706 | 1.6887 | 1.7043 | 1.6592 | 1.7181 | 1.7899 | 1.6994 | 1.7188 | 1.6856 | 1.6843 | 1.726 | 1.7195 | 1.736 | 1.7162 | 1.7024 | 1.6532 | 1.6988 | 1.6808 | 1.6822 | 1.6922 | 1.6774 | 1.6698 | 1.6646 | 1.64 | 1.6656 | 1.6725 | 1.6649 | 1.6263 | 1.6646 | 1.6394 | 1.6373 | 1.6187 | 1.6301 | 1.6435 | 1.648 | 1.6256 | 1.6522 | 1.6641 | 1.6332 | 1.6165 | 1.5973 | 1.6087 | 1.6101 | 1.6184 | 1.619 | 1.6156 | 1.637 | 1.6318 | 1.6281 | 1.6283 | 1.5985 | 1.6238 | 1.6349 | 1.6621 | 1.628 | 1.6356 | 1.6297 | 1.6408 | 1.6353 | 1.6346 | 1.6059 | 1.6163 | 1.6142 | 1.6218 | 1.6644 | 1.6746 | 1.6201 | 1.528 | 1.579 | 1.5446 | 1.5423 | 1.5593 | 1.5616 | 1.5635 | 1.5903 | 1.613 | 1.5828 | 1.5767 | 1.5986 | 1.6194 | 1.5798 | 1.6063 | 1.5895 | 1.6096 | 1.6119 | 1.6153 | 1.5964 | 1.607 | 1.6024 | 1.6013 | 1.5945 | 1.5748 | 1.5918 | 1.5941 | 1.6009 | 1.5766 | 1.5758 | 1.6179 | 1.5593 | 1.5951 | 1.5891 | 1.584 | 1.5879 | 1.6 | 1.5878 | 1.6067 | 1.6192 | 1.6115 | 1.5777 | 1.5781 | 1.5755 | 1.5548 | 1.618 | 1.5957 | 1.5958 | 1.5914 | 1.5673 | 1.5971 | 1.6575 | 1.5689 | 1.5705 | 1.6011 | 1.5693 | 1.5251 | 1.5315 | 1.5828 | 1.5827 | 1.5691 | 1.5823 | 1.6028 | 1.5875 | 1.5977 | 1.5714 | 1.6099 | 1.5863 | 1.6126 | 1.5863 | 1.5918 | 1.5832 | 1.5037 | 1.5669 | 1.5269 | 1.5037 | 1.6358 | 1.6327 | 1.6068 | 1.5751 | 1.5922 | 1.5579 | 1.584 | 1.5624 | 1.5829 | 1.5519 | 1.5837 | 1.5553 | 1.5332 | 1.5654 | 1.5762 | 1.6252 | 1.6007 | 1.6292 | 1.6163 | 1.6474 | 1.6536 | 1.6286 | 1.6371 | 1.638 | 1.6425 | 1.6439 | 1.6423 | 1.6449 | 1.6089 | 1.5958 | 1.6227 | 1.5931 | 1.6095 | 1.6104 | 1.6135 | 1.6318 | 1.6302 | 1.6444 | 1.6436 | 1.6077 | 1.6194 | 1.5881 | 1.6209 | 1.6342 | 1.6081 | 1.5899 | 1.6478 | 1.6363 | 1.616 | 1.6293 | 1.6492 | 1.6496 | 1.6063 | 1.6225 | 1.6438 | 1.6416 | 1.6458 | 1.6401 | 1.5853 | 1.6276 | 1.6136 | 1.6325 | 1.6356 | 1.6214 | 1.6177 | 1.6315 | 1.625 | 1.5313 | 1.5655 | 1.5555 | 1.6655 | 1.636 | 1.6207 | 1.6091 | 1.6278 | 1.5785 | 1.5467 | 1.6148 | 1.5844 | 1.6283 | 1.6839 | 1.6121 | 1.6435 | 1.6297 | 1.6046 | 1.5441 | 1.6759 | 1.6177 | 1.5954 | 1.4765 | 1.6444 | 1.6405 | 1.564 | 1.5657 | 1.5915 | 1.6125 | 1.5385 | 1.5747 | 1.5904 | 1.5885 | 1.5867 | 1.6207 | 1.565 | 1.6056 | 1.6013 | 1.6214 | 1.586 | 1.5985 | 1.6315 | 1.5841 | 1.5755 | 1.5859 | 1.5852 | 1.6013 | 1.6005 | 1.5963 | 1.5797 | 1.5874 | 1.5887 | 1.6323 | 1.598 | 1.6338 | 1.635 | 1.6115 | 1.6065
2025-06-18 | 3.8222 | 3.7703 | 3.9045 | 3.9023 | 3.9053 | 3.7593 | 4.0406 | 3.8621 | 3.9348 | 3.9826 | 4.0129 | 3.9742 | 3.9788 | 3.9818 | 4.0212 | 4.0205 | 3.9769 | 4.0383 | 4.0205 | 4.0477 | 4.1864 | 4.1379 | 4.1492 | 4.1492 | 4.1735 | 4.1712 | 4.1712 | 4.1689 | 4.2689 | 4.2394 | 4.2008 | 4.2 | 3.8492 | 3.8445 | 3.9059 | 3.9211 | 4.0112 | 4.0088 | 3.8856 | 3.9593 | 3.8742 | 3.903 | 3.9605 | 3.9759 | 3.9927 | 4.0543 | 4.0288 | 3.9892 | 3.9053 | 4.0544 | 4.0418 | 3.979 | 3.9618 | 3.9717 | 3.9164 | 3.9965 | 3.9321 | 3.7987 | 3.778 | 3.7949 | 4.0652 | 3.9952 | 3.9069 | 4.3068 | 4.2378 | 4.3067 | 4.1877 | 4.1253 | 4.1158 | 4.1622 | 4.2405 | 4.1473 | 4.1142 | 4.168 | 4.0749 | 4.1364 | 4.1696 | 4.4244 | 4.4099 | 4.4651 | 4.2491 | 4.3469 | 4.421 | 4.3911 | 4.342 | 4.3543 | 4.3095 | 4.2412 | 4.3568 | 4.3354 | 4.2864 | 4.089 | 4.1877 | 4.2774 | 4.3164 | 4.2692 | 4.2089 | 4.3502 | 4.2698 | 4.2208 | 4.29 | 4.256 | 4.2122 | 4.2302 | 4.4952 | 4.1957 | 4.2619 | 4.1025 | 4.1649 | 4.245 | 4.2719 | 4.2447 | 4.3976 | 4.2572 | 4.2892 | 4.3447 | 4.3468 | 4.4213 | 4.5583 | 4.5048 | 4.3185 | 4.2854 | 4.3308 | 4.4394 | 4.3899 | 4.3602 | 4.3589 | 4.4344 | 4.3602 | 4.3354 | 4.2729 | 4.3585 | 4.2698 | 4.2874 | 4.185 | 4.1932 | 4.1988 | 4.1867 | 4.0637 | 4.0901 | 4.1408 | 4.1515 | 4.1442 | 4.2246 | 4.1297 | 4.2443 | 4.0925 | 4.3286 | 4.2272 | 4.2424 | 4.3052 | 4.1487 | 4.257 | 4.156 | 4.1598 | 4.2795 | 4.2177 | 4.1084 | 4.1353 | 4.2571 | 4.2716 | 4.2678 | 4.3354 | 4.1554 | 4.2039 | 4.2276 | 4.0329 | 4.1047 | 4.0967 | 4.0805 | 4.1398 | 4.1413 | 4.1364 | 4.1591 | 4.1878 | 4.1704 | 4.1274 | 4.161 | 4.2173 | 4.2024 | 4.2703 | 4.1465 | 4.2169 | 4.2075 | 4.2354 | 4.2079 | 4.223 | 4.2328 | 4.22 | 4.2468 | 4.2075 | 4.2608 | 4.0869 | 4.2343 | 4.252 | 4.2448 | 4.2242 | 4.1359 | 4.2602 | 4.2559 | 4.1323 | 4.1202 | 4.1907 | 4.1392 | 4.1666 | 4.1922 | 4.1424 | 4.0303 | 3.9953 | 4.1089 | 4.0779 | 4.054 | 4.1281 | 4.1821 | 4.2555 | 4.2371 | 4.2754 | 4.2434 | 4.0267 | 4.0196 | 4.2371 | 4.0909 | 3.9999 | 4.0676 | 3.945 | 3.873 | 4.108 | 4.093 | 4.2335 | 4.208 | 4.2504 | 4.2147 | 4.2908 | 4.1848 | 4.1947 | 4.1837 | 4.2174 | 4.25 | 4.196 | 4.1758 | 4.1695 | 3.9987 | 4.5447 | 4.5369 | 4.0942 | 4.0394 | 4.1079 | 4.0626 | 4.2622 | 4.1115 | 4.165 | 4.1444 | 4.1669 | 4.1822 | 4.1642 | 4.1612 | 4.1893 | 4.2186 | 4.1348 | 4.3328 | 4.2768 | 4.1232 | 4.2978 | 4.2866 | 4.2439 | 4.4202 | 4.4782 | 4.3857 | 4.4356 | 4.2854 | 4.1567 | 4.2548 | 4.1564 | 4.2095 | 4.3472 | 4.355 | 4.2721 | 4.389 | 4.3931 | 4.373 | 4.3707 | 4.3662 | 4.4051 | 4.3046 | 4.3707 | 4.3598 | 4.294 | 4.2702 | 4.3613 | 4.2467 | 4.3341 | 4.3299 | 4.373 | 4.4714 | 4.4631 | 4.4718 | 4.4737 | 4.4699 | 4.46 | 4.4365 | 3.846 | 4.4164 | 4.3951 | 4.3993 | 4.4001 | 4.4566 | 4.4084 | 4.3469 | 4.4151 | 4.3302 | 4.3721 | 4.1844 | 4.3992 | 4.2704 | 4.2906 | 4.2648 | 4.3127 | 4.2415 | 4.2274 | 4.174 | 4.2582 | 4.2892 | 4.2969 | 4.27 | 4.2143 | 4.2539 | 4.2723 | 4.2147 | 4.2657 | 4.2547 | 4.2237 | 4.1452 | 4.2692 | 4.3171 | 4.2877 | 4.2308 | 4.3078 | 4.2827 | 4.1646 | 4.2394 | 4.2569 | 4.2483 | 4.2424 | 4.2558 | 4.156 | 4.2465 | 4.2543 | 4.2532 | 4.3039 | 4.261 | 4.303 | 4.2472 | 4.3029 | 4.3029 | 4.5251 | 4.2383 | 4.2678 | 4.2326 | 4.2885 | 4.2517 | 4.2889 | 4.2767 | 4.3055 | 4.2841 | 4.3132 | 4.2476 | 4.2029
2025-06-19 | 3.2392 | 3.1858 | 3.2871 | 3.2811 | 3.2523 | 3.1245 | 3.3657 | 3.2152 | 3.2864 | 3.2985 | 3.3167 | 3.2818 | 3.303 | 3.2795 | 3.3197 | 3.3098 | 3.2751 | 3.3054 | 3.2992 | 3.3235 | 3.4311 | 3.3902 | 3.3932 | 3.3932 | 3.397 | 3.4076 | 3.4098 | 3.3992 | 3.4394 | 3.4288 | 3.4015 | 3.3955 | 3.2462 | 3.2153 | 3.2448 | 3.2703 | 3.3278 | 3.3038 | 3.2742 | 3.3022 | 3.2674 | 3.3181 | 3.3932 | 3.3925 | 3.3808 | 3.4732 | 3.4316 | 3.3837 | 3.294 | 3.3496 | 3.3688 | 3.2828 | 3.2489 | 3.2464 | 3.2003 | 3.2841 | 3.2587 | 3.1381 | 2.9744 | 3.1071 | 3.2712 | 3.2174 | 3.2551 | 3.5342 | 3.5079 | 3.5358 | 3.5435 | 3.5518 | 3.5528 | 3.4762 | 3.5666 | 3.5455 | 3.4938 | 3.453 | 3.4955 | 3.5249 | 3.4791 | 3.4144 | 3.5138 | 3.5307 | 3.4676 | 3.5218 | 3.56 | 3.5469 | 3.5366 | 3.5534 | 3.5206 | 3.5006 | 3.5455 | 3.4658 | 3.5276 | 3.4627 | 3.5335 | 3.5669 | 3.5921 | 3.5759 | 3.5546 | 3.5749 | 3.5607 | 3.5372 | 3.5574 | 3.5652 | 3.4949 | 3.5756 | 3.685 | 3.5545 | 3.6097 | 3.5418 | 3.5635 | 3.6218 | 3.6014 | 3.5217 | 3.6224 | 3.54 | 3.4817 | 3.5386 | 3.5069 | 3.5442 | 3.5711 | 3.5594 | 3.5228 | 3.5107 | 3.4787 | 3.5335 | 3.5514 | 3.5573 | 3.4645 | 3.5542 | 3.4876 | 3.49 | 3.461 | 3.5024 | 3.4997 | 3.5383 | 3.4852 | 3.5449 | 3.5844 | 3.6087 | 3.533 | 3.5376 | 3.5683 | 3.5493 | 3.5745 | 3.5939 | 3.5676 | 3.6125 | 3.5773 | 3.6205 | 3.5853 | 3.5447 | 3.5964 | 3.5783 | 3.6349 | 3.5173 | 3.53 | 3.5455 | 3.5569 | 3.5207 | 3.5003 | 3.5059 | 3.5072 | 3.5321 | 3.5814 | 3.4997 | 3.587 | 3.5559 | 3.4849 | 3.548 | 3.5287 | 3.5336 | 3.5238 | 3.5348 | 3.5404 | 3.5722 | 3.5922 | 3.554 | 3.5631 | 3.5741 | 3.5903 | 3.5722 | 3.6098 | 3.5155 | 3.5831 | 3.5718 | 3.5915 | 3.5726 | 3.5658 | 3.5646 | 3.5597 | 3.5684 | 3.537 | 3.5688 | 3.5246 | 3.5495 | 3.55 | 3.5341 | 3.5631 | 3.4919 | 3.6063 | 3.6068 | 3.5554 | 3.5677 | 3.6365 | 3.5351 | 3.5888 | 3.6405 | 3.6008 | 3.5118 | 3.5593 | 3.5703 | 3.526 | 3.6091 | 3.5498 | 3.5969 | 3.6158 | 3.6333 | 3.6326 | 3.6238 | 3.5116 | 3.5031 | 3.6529 | 3.5524 | 3.4608 | 3.5209 | 2.2628 | 0.27342 | 3.4152 | 3.4116 | 3.4808 | 3.4969 | 3.4721 | 3.4399 | 3.5165 | 3.4384 | 3.5259 | 3.4933 | 3.4949 | 3.4643 | 3.3636 | 3.4795 | 3.3644 | 3.3247 | 3.5259 | 3.4772 | 3.4855 | 3.4582 | 3.4894 | 3.4843 | 3.489 | 3.4926 | 3.4806 | 3.4769 | 3.4339 | 3.5169 | 3.4492 | 3.487 | 3.5187 | 3.5083 | 3.4246 | 3.4943 | 3.4699 | 3.4926 | 3.5018 | 3.4752 | 3.4075 | 3.5197 | 3.5298 | 3.5032 | 3.5176 | 3.4963 | 3.4087 | 3.444 | 3.4241 | 3.4354 | 3.5043 | 3.5012 | 3.4564 | 3.5264 | 3.4904 | 3.4815 | 3.4803 | 3.455 | 3.4649 | 3.3912 | 3.4195 | 3.4754 | 3.4244 | 3.3942 | 3.489 | 3.4268 | 3.4543 | 3.4709 | 3.4873 | 3.473 | 3.4611 | 3.4791 | 3.4905 | 3.5093 | 3.4968 | 3.4638 | 3.5826 | 3.4528 | 3.438 | 3.4831 | 3.4524 | 3.4801 | 3.4585 | 3.4777 | 3.4857 | 3.4536 | 3.3744 | 3.2745 | 3.506 | 3.4443 | 3.4223 | 3.407 | 3.4409 | 3.3822 | 3.2597 | 3.3945 | 3.4054 | 3.4427 | 3.4679 | 3.4148 | 3.3931 | 3.4126 | 3.4096 | 3.259 | 3.4664 | 3.4062 | 3.4443 | 3.0958 | 3.4262 | 3.4537 | 3.1829 | 3.4159 | 3.4888 | 3.4843 | 3.3625 | 3.4537 | 3.4462 | 3.46 | 3.4372 | 3.4728 | 3.4073 | 3.4537 | 3.4772 | 3.4608 | 3.4454 | 3.4615 | 3.4992 | 3.4412 | 3.4784 | 3.4933 | 3.4902 | 3.4958 | 3.4918 | 3.4605 | 3.4584 | 3.4787 | 3.4737 | 3.5051 | 3.4929 | 3.5122 | 3.5016 | 3.4851 | 3.4578
2025-06-20 | 3.3732 | 3.319 | 3.3955 | 3.4159 | 3.3659 | 3.2422 | 3.4713 | 3.3402 | 3.3939 | 3.4326 | 3.4227 | 3.3992 | 3.4114 | 3.3992 | 3.425 | 3.4023 | 3.4179 | 3.4322 | 3.4114 | 3.4409 | 3.5242 | 3.4902 | 3.5076 | 3.4902 | 3.5068 | 3.5061 | 3.5182 | 3.5235 | 3.5515 | 3.5432 | 3.5152 | 3.5227 | 3.2636 | 3.2727 | 3.3461 | 3.3612 | 3.4354 | 3.4091 | 3.3144 | 3.3836 | 3.2909 | 3.3174 | 3.3516 | 3.3406 | 3.3735 | 3.4139 | 3.4055 | 3.3609 | 3.2891 | 3.3894 | 3.4003 | 3.3125 | 3.2908 | 3.3078 | 3.2804 | 3.3457 | 3.3152 | 3.2167 | 3.2252 | 3.2128 | 3.4 | 3.367 | 3.283 | 3.6304 | 3.5752 | 3.6466 | 3.5994 | 3.5704 | 3.5728 | 3.5238 | 3.6197 | 3.5659 | 3.5386 | 3.4672 | 3.539 | 3.5559 | 3.5346 | 3.3347 | 3.4938 | 3.6501 | 3.5386 | 3.6131 | 3.6701 | 3.6396 | 3.6498 | 3.6667 | 3.6306 | 3.6091 | 3.6894 | 3.6194 | 3.618 | 3.47 | 3.5828 | 3.627 | 3.6591 | 3.6618 | 3.6244 | 3.6701 | 3.6549 | 3.6158 | 3.6205 | 3.6542 | 3.5836 | 3.6408 | 3.7612 | 3.6046 | 3.6674 | 3.5649 | 3.6135 | 3.6725 | 3.6743 | 3.6863 | 3.5979 | 3.6349 | 3.56 | 3.5349 | 3.5952 | 3.648 | 3.6791 | 3.6756 | 3.608 | 3.5842 | 3.5869 | 3.6468 | 3.647 | 3.6115 | 3.589 | 3.6377 | 3.6011 | 3.5787 | 3.5107 | 3.5621 | 3.5131 | 3.5145 | 3.4634 | 3.499 | 3.3817 | 3.3637 | 3.3044 | 3.3268 | 3.4003 | 3.2923 | 3.3264 | 3.411 | 3.4037 | 3.4013 | 3.4048 | 3.4196 | 3.4127 | 3.3543 | 3.4429 | 3.4158 | 3.4932 | 3.373 | 3.4331 | 3.4337 | 3.3892 | 3.4268 | 3.4462 | 3.3195 | 3.4068 | 3.3803 | 3.4199 | 3.4683 | 3.4979 | 3.2576 | 3.1882 | 3.2385 | 3.2169 | 3.2392 | 3.2441 | 3.2574 | 3.2657 | 3.2884 | 3.3054 | 3.2615 | 3.2377 | 3.2619 | 3.2974 | 3.2611 | 3.2804 | 3.1988 | 3.2774 | 3.243 | 3.2899 | 3.28 | 3.2664 | 3.2778 | 3.2411 | 3.2683 | 3.2241 | 3.2717 | 3.2989 | 3.2887 | 3.2746 | 3.2881 | 3.2881 | 3.2087 | 3.3049 | 3.2904 | 3.265 | 3.2766 | 3.3305 | 3.2594 | 3.3069 | 3.3381 | 3.3281 | 3.2649 | 3.2471 | 3.315 | 3.2865 | 3.4764 | 3.2823 | 3.3038 | 3.3085 | 3.3298 | 3.3161 | 3.4406 | 3.1482 | 3.2475 | 3.3562 | 3.2959 | 3.1933 | 3.2474 | 3.2553 | 3.3516 | 3.2699 | 3.2521 | 3.3387 | 3.2653 | 3.3874 | 3.3161 | 3.3936 | 3.2492 | 3.2967 | 3.2512 | 3.2932 | 3.2429 | 3.1464 | 3.2586 | 3.1195 | 3.2107 | 3.2759 | 3.2622 | 3.1684 | 3.1917 | 3.2394 | 3.2216 | 3.2394 | 3.216 | 3.2227 | 3.2044 | 3.1412 | 3.173 | 3.1371 | 3.1891 | 3.1745 | 3.6175 | 3.4745 | 3.6103 | 3.565 | 3.5994 | 3.5839 | 3.4612 | 3.5217 | 3.5903 | 3.6158 | 3.5854 | 3.5985 | 3.5376 | 3.4434 | 3.4871 | 3.465 | 3.455 | 3.5396 | 3.5549 | 3.495 | 3.5867 | 3.5639 | 3.5775 | 3.5839 | 3.5537 | 3.554 | 3.4656 | 3.4837 | 3.5745 | 3.5249 | 3.4792 | 3.585 | 3.5066 | 3.5457 | 3.5608 | 3.606 | 3.5437 | 3.5571 | 3.5624 | 3.5776 | 3.5897 | 3.5821 | 3.5495 | 3.4071 | 3.5419 | 3.537 | 3.5768 | 3.5427 | 3.605 | 3.5404 | 3.5567 | 3.5679 | 3.5302 | 3.3799 | 3.2984 | 3.6333 | 3.5778 | 3.5389 | 3.5288 | 3.5742 | 3.5384 | 3.3083 | 3.4555 | 3.5561 | 3.5208 | 3.6032 | 3.4436 | 3.5318 | 3.5497 | 3.4746 | 3.3688 | 3.6078 | 3.584 | 3.5259 | 3.2814 | 3.5392 | 3.5832 | 3.356 | 3.4944 | 3.598 | 3.5823 | 3.4772 | 3.5587 | 3.537 | 3.5864 | 3.5314 | 3.5957 | 3.5053 | 3.5883 | 3.5989 | 3.6267 | 3.6425 | 3.6248 | 3.679 | 3.5504 | 3.626 | 3.6316 | 3.6362 | 3.6153 | 3.6211 | 3.5878 | 3.6205 | 3.6275 | 3.6397 | 3.6503 | 3.6759 | 3.6927 | 3.6699 | 3.6432 | 3.448
2025-06-21 | 3.5367 | 3.4737 | 3.5341 | 3.5545 | 3.55 | 3.4184 | 3.609 | 3.475 | 3.5568 | 3.6015 | 3.5485 | 3.5348 | 3.5985 | 3.5917 | 3.6098 | 3.5879 | 3.5622 | 3.5686 | 3.5295 | 3.5682 | 3.6523 | 3.6295 | 3.6621 | 3.6561 | 3.6258 | 3.6447 | 3.6553 | 3.6614 | 3.6977 | 3.6773 | 3.6561 | 3.6568 | 3.4939 | 3.4761 | 3.5303 | 3.5534 | 3.6132 | 3.5758 | 3.5348 | 3.5726 | 3.5288 | 3.5621 | 3.6082 | 3.6455 | 3.6477 | 3.7004 | 3.6991 | 3.6519 | 3.5422 | 3.6211 | 3.6488 | 3.5598 | 3.5195 | 3.521 | 3.4503 | 3.5423 | 3.4913 | 3.3843 | 3.4018 | 3.3567 | 3.5424 | 3.4992 | 3.5345 | 3.7484 | 3.7001 | 3.7473 | 3.7167 | 3.7029 | 3.6848 | 3.666 | 3.7633 | 3.7271 | 3.7105 | 3.6098 | 3.7129 | 3.7027 | 3.7367 | 3.8123 | 3.8106 | 3.8378 | 3.7108 | 3.7903 | 3.8385 | 3.807 | 3.7836 | 3.7886 | 3.7579 | 3.7076 | 3.784 | 3.764 | 3.7453 | 3.4834 | 3.5797 | 3.637 | 3.6653 | 3.696 | 3.6533 | 3.7305 | 3.7239 | 3.6227 | 3.6537 | 3.7015 | 3.653 | 3.6743 | 3.8478 | 3.6121 | 3.7029 | 3.6425 | 3.6387 | 3.7391 | 3.7595 | 3.754 | 3.6209 | 3.7287 | 3.7371 | 3.7022 | 3.7957 | 3.8385 | 3.8951 | 3.891 | 3.7926 | 3.794 | 3.7821 | 3.8438 | 3.8447 | 3.8368 | 3.7812 | 3.8413 | 3.7602 | 3.8112 | 3.7471 | 3.7888 | 3.7695 | 3.8002 | 3.7443 | 3.8182 | 3.8182 | 3.8496 | 3.7746 | 3.8268 | 3.8064 | 3.7995 | 3.803 | 3.854 | 3.8178 | 3.8578 | 3.8254 | 3.8615 | 3.8264 | 3.7843 | 3.8313 | 3.8182 | 3.8677 | 3.7277 | 3.7647 | 3.6791 | 3.6787 | 3.7533 | 3.735 | 3.7488 | 3.746 | 3.7685 | 3.8251 | 3.8128 | 3.8471 | 3.6944 | 3.7389 | 3.7899 | 3.7498 | 3.7351 | 3.7362 | 3.7385 | 3.7502 | 3.7729 | 3.819 | 3.8042 | 3.7982 | 3.8001 | 3.8405 | 3.8099 | 3.8959 | 3.7926 | 3.8447 | 3.8545 | 3.8511 | 3.8163 | 3.8364 | 3.8243 | 3.8541 | 3.8401 | 3.8175 | 3.8522 | 3.7634 | 3.7868 | 3.8218 | 3.7849 | 3.8147 | 3.77 | 3.9181 | 3.9058 | 3.8437 | 3.8547 | 3.9232 | 3.7359 | 3.8601 | 3.9118 | 3.8485 | 3.7413 | 3.8001 | 3.7699 | 3.7905 | 3.8968 | 3.8308 | 3.8807 | 3.9125 | 3.9382 | 3.9532 | 3.9495 | 3.5479 | 3.7508 | 3.9529 | 3.8197 | 3.7397 | 3.7984 | 3.7813 | 3.9375 | 3.7623 | 3.7366 | 3.8411 | 3.8144 | 3.8128 | 3.7949 | 3.832 | 3.7512 | 3.8552 | 3.7885 | 3.7971 | 3.801 | 3.6025 | 3.7217 | 3.6196 | 3.7265 | 3.8591 | 3.8744 | 3.845 | 3.8058 | 3.8316 | 3.842 | 3.8297 | 3.8342 | 3.7269 | 3.7288 | 3.7127 | 3.7916 | 3.6989 | 3.7456 | 3.7725 | 3.697 | 3.6728 | 3.8677 | 3.8285 | 3.7807 | 3.8527 | 3.7978 | 3.8472 | 3.8658 | 3.8724 | 3.8342 | 3.8611 | 3.8166 | 3.7119 | 3.7635 | 3.7331 | 3.7745 | 3.8636 | 3.8523 | 3.7779 | 3.8767 | 3.8351 | 3.8885 | 3.893 | 3.8545 | 3.8707 | 3.7661 | 3.7982 | 3.8919 | 3.8095 | 3.7834 | 3.8806 | 3.7719 | 3.8466 | 3.839 | 3.8794 | 3.8516 | 3.8714 | 3.8516 | 3.8798 | 3.854 | 3.8316 | 3.8278 | 3.6819 | 3.8115 | 3.8206 | 3.8134 | 3.7986 | 3.8943 | 3.8157 | 3.8258 | 3.8357 | 3.7909 | 3.8214 | 3.6537 | 3.9433 | 3.8678 | 3.842 | 3.8125 | 3.8452 | 3.7896 | 3.6346 | 3.7602 | 3.8587 | 3.9125 | 3.8772 | 3.854 | 3.7942 | 3.8069 | 3.8211 | 3.6802 | 3.8469 | 3.8116 | 3.8057 | 3.6527 | 3.8305 | 3.8658 | 3.7225 | 3.7587 | 3.8361 | 3.8391 | 3.6922 | 3.7774 | 3.7819 | 3.8047 | 3.783 | 3.832 | 3.7669 | 3.8454 | 3.854 | 3.8458 | 3.8581 | 3.8399 | 3.8932 | 3.828 | 3.891 | 3.8925 | 3.8972 | 3.8558 | 3.8663 | 3.8786 | 3.8984 | 3.8835 | 3.9223 | 3.8819 | 3.9135 | 3.9462 | 3.8595 | 3.8662 | 3.7573
2025-06-22 | 4.1651 | 4.0861 | 4.1848 | 4.1924 | 4.1977 | 4.0782 | 4.3175 | 4.1295 | 4.2053 | 4.2826 | 4.2758 | 4.2545 | 4.3121 | 4.2985 | 4.3545 | 4.3621 | 4.2528 | 4.2927 | 4.2492 | 4.3008 | 4.4144 | 4.3826 | 4.4424 | 4.4409 | 4.3629 | 4.3932 | 4.4121 | 4.4371 | 4.425 | 4.4227 | 4.3985 | 4.4295 | 4.2265 | 4.1794 | 4.2265 | 4.2616 | 4.3636 | 4.3557 | 4.2652 | 4.3222 | 4.2659 | 4.3124 | 4.38 | 4.3933 | 4.4006 | 4.4891 | 4.4839 | 4.4301 | 4.3178 | 4.4431 | 4.4479 | 4.3437 | 4.3218 | 4.3271 | 4.239 | 4.3513 | 4.2554 | 4.1325 | 4.1246 | 4.0967 | 4.322 | 4.258 | 4.2984 | 4.4834 | 4.4362 | 4.4939 | 4.4724 | 4.4199 | 4.4292 | 4.4048 | 4.5397 | 4.4369 | 4.4286 | 4.4079 | 4.4051 | 4.4459 | 4.4563 | 4.442 | 4.5507 | 4.5818 | 4.4279 | 4.5152 | 4.6211 | 4.5527 | 4.5124 | 4.5411 | 4.491 | 4.4303 | 4.5242 | 4.5031 | 4.4972 | 4.1028 | 4.2567 | 4.2933 | 4.3785 | 4.3558 | 4.2756 | 4.3979 | 4.4089 | 4.3755 | 4.3626 | 4.4479 | 4.3498 | 4.4124 | 4.5311 | 4.3813 | 4.4855 | 4.3768 | 4.4248 | 4.5155 | 4.5262 | 4.519 | 4.5767 | 4.4358 | 4.4734 | 4.5449 | 4.4962 | 4.5911 | 4.6518 | 4.6667 | 4.589 | 4.5932 | 4.5736 | 4.6299 | 4.7067 | 4.6856 | 4.6066 | 4.7516 | 4.6177 | 4.6315 | 4.6156 | 4.7236 | 4.6177 | 4.7046 | 4.6125 | 4.6484 | 4.7825 | 4.6197 | 4.4911 | 4.5583 | 4.6322 | 4.559 | 4.51 | 4.7039 | 4.6332 | 4.715 | 4.6591 | 4.7958 | 4.7474 | 4.7197 | 4.7984 | 4.6425 | 4.7698 | 4.5728 | 4.609 | 4.7039 | 4.7643 | 4.6898 | 4.6325 | 4.578 | 4.6667 | 4.6184 | 4.8054 | 4.5764 | 4.6477 | 4.7572 | 4.5423 | 4.6024 | 4.582 | 4.6028 | 4.5828 | 4.6047 | 4.6088 | 4.6224 | 4.6519 | 4.6364 | 4.5896 | 4.6232 | 4.6807 | 4.6706 | 4.7474 | 4.6205 | 4.6856 | 4.6829 | 4.6871 | 4.6444 | 4.6704 | 4.661 | 4.6935 | 4.6973 | 4.6939 | 4.7279 | 4.6799 | 4.6727 | 4.7032 | 4.7008 | 4.677 | 4.6215 | 4.7968 | 4.7492 | 4.5887 | 4.6082 | 4.7057 | 4.5588 | 4.6069 | 4.6967 | 4.5922 | 4.4873 | 4.4206 | 4.6599 | 4.6246 | 4.5921 | 4.6386 | 4.7202 | 4.8336 | 4.6825 | 4.8232 | 4.7466 | 4.4427 | 4.5328 | 4.7276 | 4.5914 | 4.4363 | 4.5924 | 4.4928 | 4.5086 | 4.6186 | 4.5651 | 4.7233 | 4.7382 | 4.7076 | 4.667 | 4.7633 | 4.6576 | 4.7802 | 4.7323 | 4.7347 | 4.7465 | 4.6655 | 4.6722 | 4.6457 | 4.6528 | 4.7162 | 4.7567 | 4.624 | 4.5709 | 4.6829 | 4.6374 | 4.7111 | 4.6782 | 4.6666 | 4.6531 | 4.7055 | 4.741 | 4.633 | 4.6472 | 4.6871 | 4.5836 | 4.4066 | 4.7287 | 4.7018 | 4.6664 | 4.6471 | 4.6389 | 4.6887 | 4.7374 | 4.7522 | 4.6335 | 4.7313 | 4.6537 | 4.4795 | 4.6974 | 4.5201 | 4.6932 | 4.7872 | 4.802 | 4.6239 | 4.8306 | 4.6992 | 4.619 | 4.6398 | 4.6156 | 4.6107 | 4.4955 | 4.537 | 4.6712 | 4.6013 | 4.5374 | 4.6708 | 4.4859 | 4.6387 | 4.6965 | 4.7131 | 4.6103 | 4.6107 | 4.6126 | 4.624 | 4.6162 | 4.5787 | 4.6041 | 4.4867 | 4.5992 | 4.5882 | 4.6375 | 4.6155 | 4.67 | 4.628 | 4.6814 | 4.6869 | 4.6476 | 4.6652 | 4.4263 | 4.6829 | 4.6113 | 4.547 | 4.6083 | 4.6758 | 4.5922 | 4.6457 | 4.6022 | 4.5832 | 4.5816 | 4.6617 | 4.5997 | 4.5574 | 4.5971 | 4.6161 | 4.6072 | 4.6591 | 4.6154 | 4.633 | 4.7449 | 4.7363 | 4.7684 | 4.7547 | 4.5698 | 4.7107 | 4.6703 | 4.5683 | 4.6475 | 4.6707 | 4.7058 | 4.6629 | 4.7148 | 4.6012 | 4.686 | 4.7017 | 4.695 | 4.6674 | 4.679 | 4.7233 | 4.5647 | 4.6894 | 4.7197 | 4.6719 | 4.6921 | 4.6651 | 4.6008 | 4.6122 | 4.6606 | 4.5561 | 4.7029 | 4.7079 | 4.6943 | 4.6998 | 4.6319 | 4.5609
2025-06-23 | 1.1156 | 1.0758 | 1.1182 | 1.1083 | 1.103 | 1.0562 | 1.153 | 1.0879 | 1.1167 | 1.1038 | 1.1348 | 1.1205 | 1.1227 | 1.1106 | 1.1288 | 1.1258 | 1.0957 | 1.1411 | 1.1356 | 1.1295 | 1.178 | 1.1689 | 1.1545 | 1.1386 | 1.1462 | 1.1629 | 1.178 | 1.175 | 1.1939 | 1.1606 | 1.1742 | 1.1311 | 1.1008 | 1.0718 | 1.0869 | 1.0941 | 1.1292 | 1.0893 | 1.0871 | 1.1204 | 1.0856 | 1.1248 | 1.1401 | 1.1404 | 1.1316 | 1.1715 | 1.1716 | 1.1526 | 1.118 | 1.1479 | 1.129 | 1.0943 | 1.0974 | 1.107 | 1.1001 | 1.1057 | 1.121 | 1.0666 | 1.0807 | 1.0661 | 1.1212 | 1.1123 | 1.0872 | 1.2105 | 1.1988 | 1.2219 | 1.205 | 1.2257 | 1.2024 | 1.1929 | 1.2157 | 1.2177 | 1.1984 | 1.1834 | 1.1932 | 1.1955 | 1.1916 | 1.2019 | 1.2108 | 1.2257 | 1.1946 | 1.2196 | 1.2191 | 1.2266 | 1.2295 | 1.2165 | 1.2114 | 1.2093 | 1.2284 | 1.2039 | 1.2084 | 1.1649 | 1.2101 | 1.2084 | 1.2167 | 1.2226 | 1.2216 | 1.2264 | 1.2129 | 0.48521 | 0.94877 | 1.2239 | 1.1908 | 1.2274 | 1.2764 | 1.2112 | 1.2315 | 1.2077 | 1.2291 | 1.2395 | 1.2305 | 1.2395 | 1.2404 | 1.224 | 1.2008 | 1.2302 | 1.217 | 1.2229 | 1.2398 | 1.2288 | 1.2088 | 1.2095 | 1.1973 | 1.2179 | 1.2288 | 1.2284 | 1.1988 | 1.2288 | 1.2101 | 1.2098 | 1.1915 | 1.2095 | 1.2026 | 1.2133 | 1.1936 | 1.2095 | 1.2291 | 1.1994 | 1.1765 | 1.1698 | 1.1836 | 1.1756 | 1.1818 | 1.1932 | 1.1843 | 1.2039 | 1.1963 | 1.1883 | 1.1981 | 1.1825 | 1.1877 | 1.1974 | 1.215 | 1.186 | 1.1929 | 1.1988 | 1.2164 | 1.2032 | 1.195 | 1.1818 | 1.1901 | 1.1839 | 1.2057 | 1.2123 | 1.225 | 1.1919 | 1.1058 | 1.1568 | 1.1104 | 1.1296 | 1.1289 | 1.1383 | 1.1323 | 1.1463 | 1.1772 | 1.1606 | 1.144 | 1.1708 | 1.1909 | 1.1504 | 1.1781 | 1.1861 | 1.1701 | 1.1859 | 1.1791 | 1.1515 | 1.167 | 1.167 | 1.1829 | 1.167 | 1.1629 | 1.1618 | 1.1731 | 1.1708 | 1.1421 | 1.1472 | 1.1869 | 1.1603 | 1.1811 | 1.1809 | 1.1638 | 1.1614 | 1.1793 | 1.1597 | 1.174 | 1.1965 | 1.1832 | 1.1585 | 1.1606 | 1.1617 | 1.1457 | 1.148 | 1.1774 | 1.1864 | 1.1841 | 1.1697 | 1.1981 | 1.163 | 1.1489 | 1.1427 | 1.195 | 1.161 | 1.1477 | 1.1472 | 1.1647 | 1.1945 | 1.1631 | 1.1749 | 1.1966 | 1.1766 | 1.1833 | 1.1449 | 1.2029 | 1.1811 | 1.2057 | 1.1695 | 1.179 | 1.2068 | 1.1116 | 1.1467 | 1.1307 | 1.1527 | 1.2323 | 1.2166 | 1.2174 | 1.1617 | 1.1821 | 1.1591 | 1.1762 | 1.1583 | 1.1714 | 1.158 | 1.2054 | 1.1781 | 1.1426 | 1.1609 | 1.1722 | 1.2052 | 1.1783 | 1.2044 | 1.1969 | 1.2165 | 1.2196 | 1.1949 | 1.2159 | 1.2031 | 1.2037 | 1.205 | 1.2034 | 1.2188 | 1.184 | 1.1884 | 1.1978 | 1.1715 | 1.1931 | 1.19 | 1.1839 | 1.2051 | 1.1952 | 1.2132 | 1.2143 | 1.172 | 1.1682 | 1.1523 | 1.1859 | 1.2079 | 1.1825 | 1.1568 | 1.2116 | 1.2074 | 1.1837 | 1.206 | 1.2222 | 1.2135 | 1.1667 | 1.1781 | 1.2127 | 1.2036 | 1.1942 | 1.2165 | 1.2025 | 1.2036 | 1.1782 | 1.1961 | 1.2089 | 1.1849 | 1.1794 | 1.1946 | 1.1917 | 1.1817 | 1.2245 | 1.1692 | 1.2333 | 1.2095 | 1.1352 | 1.1808 | 1.2115 | 1.1588 | 1.1808 | 1.2331 | 1.1499 | 1.2064 | 1.2705 | 1.2581 | 1.2406 | 1.217 | 1.2417 | 1.1725 | 1.2514 | 1.2041 | 1.1476 | 1.2316 | 1.2586 | 1.252 | 1.2822 | 1.1755 | 1.198 | 1.2144 | 1.1714 | 1.1684 | 1.2036 | 1.1953 | 1.1894 | 1.2208 | 1.1714 | 1.197 | 1.2088 | 1.226 | 1.1832 | 1.1825 | 1.2288 | 1.1449 | 1.1916 | 1.1923 | 1.1739 | 1.1959 | 1.1908 | 1.2034 | 1.177 | 1.1811 | 1.1837 | 1.2194 | 1.1943 | 1.2339 | 1.2335 | 1.1876 | 1.178
2025-06-24 | 2.2608 | 2.1707 | 2.2803 | 2.2523 | 2.2561 | 2.1519 | 2.365 | 2.2356 | 2.2955 | 2.2985 | 2.3477 | 2.3174 | 2.2947 | 2.3174 | 2.3311 | 2.3311 | 2.2998 | 2.3668 | 2.3705 | 2.3629 | 2.4705 | 2.4318 | 2.4402 | 2.4273 | 2.4606 | 2.4606 | 2.4652 | 2.4576 | 2.5068 | 2.4811 | 2.4727 | 2.4462 | 2.2621 | 2.2137 | 2.236 | 2.2568 | 2.3102 | 2.2982 | 2.2705 | 2.3134 | 2.2705 | 2.3039 | 2.3454 | 2.3399 | 2.3699 | 2.4124 | 2.4109 | 2.3938 | 2.3441 | 2.4047 | 2.3908 | 2.335 | 2.3182 | 2.3423 | 2.3218 | 2.3485 | 2.3306 | 2.223 | 2.2708 | 2.233 | 2.3621 | 2.3296 | 2.3138 | 2.5649 | 2.5248 | 2.5493 | 2.5352 | 2.5335 | 2.4949 | 2.5072 | 2.5383 | 2.53 | 2.479 | 2.4983 | 2.4538 | 2.4535 | 2.4426 | 2.5607 | 2.5725 | 2.5814 | 2.5238 | 2.5771 | 2.5818 | 2.5808 | 2.578 | 2.579 | 2.5559 | 2.5467 | 2.5631 | 2.5511 | 2.5504 | 2.5028 | 2.5283 | 2.5707 | 2.5611 | 2.5611 | 2.56 | 2.5801 | 2.5556 | 2.5126 | 2.5519 | 2.5556 | 2.4992 | 2.5625 | 2.6853 | 2.5535 | 2.578 | 2.5255 | 2.53 | 2.5859 | 2.579 | 2.6066 | 2.5019 | 2.561 | 2.53 | 2.5776 | 2.5697 | 2.5769 | 2.6218 | 2.5763 | 2.5576 | 2.5518 | 2.5307 | 2.5693 | 2.5735 | 2.5531 | 2.5138 | 2.5645 | 2.53 | 2.5314 | 2.5045 | 2.53 | 2.521 | 2.5362 | 2.4855 | 2.5159 | 2.5595 | 2.5452 | 2.4949 | 2.4817 | 2.5 | 2.5107 | 2.5069 | 2.5138 | 2.3927 | 2.5217 | 2.4921 | 2.5242 | 2.4957 | 2.4758 | 2.5 | 2.4907 | 2.542 | 2.4807 | 2.489 | 2.4972 | 2.3951 | 2.5121 | 2.51 | 2.4714 | 2.4834 | 2.4406 | 2.5069 | 2.5165 | 2.539 | 2.4888 | 2.407 | 2.4622 | 2.4414 | 2.4573 | 2.4444 | 2.4584 | 2.4656 | 2.4917 | 2.5106 | 2.4819 | 2.4739 | 2.4853 | 2.4928 | 2.4679 | 2.4965 | 2.4343 | 2.4845 | 2.4826 | 2.5034 | 2.4819 | 2.4796 | 2.4751 | 2.4698 | 2.4826 | 2.4596 | 2.4679 | 2.4301 | 2.4403 | 2.4504 | 2.4317 | 2.4833 | 2.4514 | 2.5004 | 2.5114 | 2.4827 | 2.4957 | 2.5487 | 2.484 | 2.5244 | 2.5538 | 2.5425 | 2.4897 | 2.5175 | 2.5151 | 2.5108 | 2.4718 | 2.4706 | 2.5071 | 2.5 | 2.4346 | 2.4515 | 2.5109 | 2.4827 | 2.4816 | 2.567 | 2.5184 | 2.4421 | 2.482 | 2.4936 | 2.554 | 2.3955 | 2.3887 | 2.4415 | 2.4392 | 2.4415 | 2.4105 | 2.467 | 2.4123 | 2.4725 | 2.4474 | 2.4423 | 2.4372 | 2.3694 | 2.4 | 2.366 | 2.3963 | 2.4827 | 2.4529 | 2.4494 | 2.3421 | 2.4419 | 2.2841 | 0.41954 | 1.4461 | 2.4262 | 2.4303 | 2.4318 | 2.4396 | 2.3981 | 2.4266 | 2.4516 | 2.4208 | 2.4874 | 2.5295 | 2.5168 | 2.3726 | 2.5373 | 2.4079 | 2.4796 | 2.5435 | 2.5558 | 2.5401 | 2.5514 | 2.5338 | 2.4705 | 2.4824 | 2.4725 | 2.4732 | 2.5118 | 2.5113 | 2.4892 | 2.537 | 2.5321 | 2.4664 | 2.4615 | 2.4478 | 2.4452 | 2.4161 | 2.4365 | 2.4766 | 2.4365 | 2.4172 | 2.4958 | 2.4393 | 2.4607 | 2.4713 | 2.498 | 2.4897 | 2.4742 | 2.4829 | 2.5194 | 2.5192 | 2.5226 | 2.5108 | 2.4507 | 2.4915 | 2.4653 | 2.49 | 2.4827 | 2.4818 | 2.4767 | 2.4773 | 2.4813 | 2.4647 | 2.4164 | 2.3466 | 2.4619 | 2.4452 | 2.3111 | 2.4165 | 2.4544 | 2.4035 | 2.4295 | 2.4104 | 2.4074 | 2.449 | 2.4856 | 2.4325 | 2.4404 | 2.4168 | 2.4393 | 2.4049 | 2.4788 | 2.4144 | 2.4152 | 2.5071 | 2.5027 | 2.5118 | 2.5361 | 2.4684 | 2.5028 | 2.5249 | 2.4086 | 2.4834 | 2.4819 | 2.4699 | 2.477 | 2.4987 | 2.4968 | 2.4902 | 2.4725 | 2.4931 | 2.4593 | 2.4784 | 2.5192 | 2.4743 | 2.4785 | 2.477 | 2.5027 | 2.4907 | 2.5043 | 2.4822 | 2.4757 | 2.4864 | 2.4741 | 2.5153 | 2.5023 | 2.5024 | 2.5181 | 2.5471 | 2.4556
2025-06-25 | 3.5295 | 3.4466 | 3.5742 | 3.5735 | 3.5174 | 3.3865 | 3.6901 | 3.5167 | 3.5485 | 3.5879 | 3.653 | 3.6152 | 3.5917 | 3.5977 | 3.6152 | 3.6189 | 3.5941 | 3.6507 | 3.6409 | 3.6758 | 3.7735 | 3.7523 | 3.747 | 3.7409 | 3.7402 | 3.7598 | 3.7629 | 3.7561 | 3.8045 | 3.7826 | 3.7553 | 3.7652 | 3.5212 | 3.4793 | 3.5159 | 3.5534 | 3.634 | 3.6196 | 3.5242 | 3.5941 | 3.5371 | 3.5735 | 3.6338 | 3.652 | 3.6601 | 3.7279 | 3.7038 | 3.6526 | 3.5844 | 3.6853 | 3.654 | 3.5794 | 3.5491 | 3.5728 | 3.5269 | 3.6193 | 3.5685 | 3.4537 | 3.4888 | 3.4583 | 3.628 | 3.5669 | 3.5403 | 3.8658 | 3.8247 | 3.8885 | 3.7633 | 3.8254 | 3.7875 | 3.7867 | 3.8575 | 3.8351 | 3.7636 | 3.7075 | 3.7674 | 3.7684 | 3.7496 | 3.8385 | 3.8454 | 3.8941 | 3.8064 | 3.8446 | 3.8761 | 3.9008 | 3.8754 | 3.8698 | 3.8647 | 3.8365 | 3.8996 | 3.8654 | 3.8634 | 3.636 | 3.7736 | 3.7916 | 3.8606 | 3.813 | 3.6937 | 3.7916 | 3.8099 | 3.2572 | 3.7929 | 3.8644 | 3.7469 | 3.8661 | 3.9389 | 3.8161 | 3.9041 | 3.7826 | 3.8547 | 3.9144 | 3.93 | 3.8382 | 3.9456 | 3.8532 | 3.774 | 3.7343 | 3.8461 | 3.8796 | 3.922 | 3.8927 | 3.8509 | 3.8095 | 3.7641 | 3.8348 | 3.8975 | 3.8872 | 3.8085 | 3.9051 | 3.7222 | 3.8344 | 3.7905 | 3.8447 | 3.8012 | 3.8182 | 3.7374 | 3.7671 | 3.877 | 3.922 | 3.7765 | 3.7874 | 3.8427 | 3.8409 | 3.8389 | 3.8937 | 3.6052 | 3.9137 | 3.658 | 3.798 | 3.7956 | 3.8254 | 3.8405 | 3.8019 | 3.8458 | 3.7222 | 3.7398 | 3.696 | 3.7598 | 3.7326 | 3.7284 | 3.7529 | 3.8002 | 3.6104 | 3.8754 | 3.7391 | 3.7971 | 3.8203 | 3.8889 | 3.9365 | 0 | 3.8878 | 3.8624 | 3.8715 | 3.8681 | 3.8953 | 3.9237 | 3.8692 | 3.9289 | 3.9369 | 3.932 | 3.927 | 3.9524 | 3.8319 | 3.9172 | 3.8912 | 3.9233 | 3.9108 | 3.9063 | 3.9036 | 3.8953 | 3.9002 | 3.8723 | 3.9176 | 3.8273 | 3.7834 | 3.8865 | 3.848 | 3.8929 | 3.8011 | 3.9246 | 3.708 | 3.8809 | 3.8939 | 3.9907 | 3.8429 | 3.9325 | 4.0188 | 3.9717 | 3.8626 | 3.899 | 3.931 | 3.913 | 3.8028 | 3.8887 | 3.9313 | 3.9439 | 3.9304 | 3.8763 | 3.977 | 3.8553 | 3.856 | 4.0403 | 3.9023 | 3.8258 | 3.8853 | 3.8663 | 4.0081 | 3.7741 | 3.7498 | 3.8375 | 3.8097 | 3.7892 | 3.7822 | 3.8144 | 3.7624 | 3.8776 | 3.7763 | 3.8316 | 3.7614 | 3.6462 | 3.8077 | 3.6025 | 3.7845 | 3.8701 | 3.8736 | 3.8379 | 3.3842 | 3.7834 | 3.2347 | 0 | 0 | 3.8155 | 3.8234 | 3.7781 | 3.8693 | 3.7613 | 3.8248 | 3.8514 | 3.7598 | 3.6585 | 3.7509 | 3.7402 | 3.7637 | 3.7667 | 3.7047 | 3.8031 | 3.8151 | 3.8168 | 3.7752 | 3.8511 | 3.8275 | 3.6369 | 3.7897 | 3.7341 | 3.7611 | 3.847 | 3.8492 | 3.7898 | 3.8916 | 3.8194 | 3.7252 | 3.7528 | 3.743 | 3.7623 | 3.6557 | 3.6413 | 3.7483 | 3.6742 | 3.6576 | 3.7551 | 3.7315 | 3.7339 | 3.7676 | 3.7516 | 3.7726 | 3.7663 | 3.7945 | 3.8063 | 3.821 | 3.821 | 3.8176 | 3.7764 | 3.7713 | 3.7505 | 3.7873 | 3.7637 | 3.7883 | 3.7641 | 3.7884 | 3.7853 | 3.7452 | 3.6652 | 3.5428 | 3.7575 | 3.6686 | 3.5127 | 3.6578 | 3.6921 | 3.6185 | 3.5269 | 3.6367 | 3.6303 | 3.6625 | 3.6866 | 3.5995 | 3.6174 | 3.6421 | 3.626 | 3.5546 | 3.7209 | 3.6366 | 3.5247 | 3.7465 | 3.71 | 3.7991 | 3.7641 | 3.6159 | 3.7295 | 3.6981 | 3.6036 | 3.6847 | 3.691 | 3.7273 | 3.6978 | 3.7404 | 3.6772 | 3.7021 | 3.7166 | 3.7198 | 3.6929 | 3.7339 | 3.7633 | 3.6695 | 3.7322 | 3.7505 | 3.7241 | 3.7356 | 3.7079 | 3.7056 | 3.6962 | 3.7086 | 3.6868 | 3.7437 | 3.7404 | 3.752 | 3.7339 | 3.7512 | 3.7609
2025-06-26 | 4.4689 | 4.0861 | 4.4795 | 4.472 | 4.4811 | 4.2726 | 4.5907 | 4.4114 | 4.5242 | 4.5477 | 4.5379 | 4.5341 | 4.5576 | 4.5773 | 4.6144 | 4.6167 | 4.555 | 4.5399 | 4.5114 | 4.5606 | 4.7106 | 4.4212 | 4.7326 | 4.728 | 4.6598 | 4.6833 | 4.7068 | 4.6917 | 4.7136 | 4.7174 | 4.6886 | 4.6902 | 4.4667 | 4.4219 | 4.4721 | 4.4721 | 4.5845 | 4.5933 | 4.4985 | 4.5175 | 4.4121 | 4.4957 | 4.6137 | 4.6308 | 4.5526 | 4.67 | 4.4377 | 4.5403 | 4.4138 | 4.5457 | 4.5337 | 4.4133 | 4.3506 | 4.3699 | 4.3743 | 4.5311 | 4.4657 | 4.3093 | 4.3299 | 4.2851 | 4.5152 | 4.414 | 4.2632 | 4.7208 | 4.7095 | 4.838 | 4.8382 | 4.7671 | 4.8073 | 4.6611 | 4.844 | 4.7536 | 4.685 | 4.5759 | 4.668 | 4.7904 | 4.7854 | 4.7992 | 4.7805 | 4.9137 | 4.6746 | 4.7417 | 4.8758 | 4.8023 | 4.658 | 4.6501 | 4.6465 | 4.5858 | 4.8192 | 4.7547 | 4.7522 | 4.5977 | 4.734 | 4.8178 | 4.8861 | 4.7464 | 4.6359 | 4.8461 | 4.735 | 3.8128 | 4.8384 | 4.7095 | 4.6736 | 4.7488 | 5.0652 | 4.7943 | 4.8954 | 4.7457 | 4.8144 | 4.7985 | 4.8427 | 4.7905 | 4.839 | 4.5898 | 4.735 | 4.6501 | 4.6905 | 4.7419 | 4.873 | 4.7885 | 4.7581 | 4.6777 | 4.6335 | 4.7157 | 4.7923 | 4.7764 | 4.6639 | 4.7833 | 4.6256 | 4.6242 | 4.6318 | 4.7547 | 4.6052 | 4.7122 | 4.6139 | 4.6532 | 4.8092 | 4.5528 | 4.5219 | 4.538 | 4.6401 | 4.5756 | 4.5959 | 4.7398 | 4.4517 | 4.7032 | 4.4979 | 4.8525 | 4.7533 | 4.7486 | 4.796 | 4.6515 | 4.7887 | 4.5404 | 4.5883 | 4.6598 | 4.7443 | 4.6335 | 4.5997 | 4.6856 | 4.6484 | 4.7219 | 4.8437 | 4.5797 | 4.6656 | 4.6396 | 4.6988 | 4.7423 | 0 | 4.7358 | 4.7158 | 4.709 | 4.6882 | 4.6776 | 4.7252 | 4.7483 | 4.7249 | 4.7347 | 4.8103 | 4.7913 | 4.8452 | 4.5758 | 4.7846 | 4.74 | 4.7793 | 4.7593 | 4.7506 | 4.7902 | 4.6833 | 4.7657 | 4.6391 | 4.7638 | 4.7891 | 4.7986 | 4.8361 | 4.8437 | 4.8361 | 4.4304 | 4.6234 | 4.7092 | 4.5884 | 4.6048 | 4.7367 | 4.5637 | 4.6635 | 4.7771 | 4.6611 | 4.5843 | 4.7117 | 4.5784 | 4.6758 | 4.4486 | 4.4211 | 4.5243 | 4.5973 | 4.6032 | 4.6707 | 4.6743 | 4.4008 | 4.54 | 4.6964 | 4.5277 | 4.3718 | 4.5481 | 4.3893 | 4.6094 | 4.4377 | 4.4159 | 4.6268 | 4.5754 | 4.708 | 4.6075 | 4.706 | 4.6016 | 4.5263 | 4.5275 | 4.6554 | 4.7068 | 4.5735 | 4.6685 | 4.5978 | 4.7294 | 4.5145 | 4.5565 | 4.5141 | 4.1579 | 4.418 | 4.1142 | 0 | 0 | 4.6427 | 4.572 | 4.4849 | 4.5679 | 4.6782 | 4.6359 | 4.618 | 4.7649 | 4.4776 | 4.6731 | 4.6504 | 4.5872 | 4.5712 | 4.4775 | 4.6408 | 4.7253 | 4.7789 | 4.6587 | 4.7363 | 4.5871 | 4.4412 | 4.6027 | 4.213 | 4.529 | 4.6865 | 4.7122 | 4.5727 | 4.7695 | 4.6917 | 4.7113 | 4.6973 | 4.6618 | 4.7048 | 4.5325 | 4.6568 | 4.7147 | 4.65 | 4.5911 | 4.7377 | 4.5832 | 4.6984 | 4.7271 | 4.7901 | 4.7679 | 4.7171 | 4.7355 | 4.739 | 4.7452 | 4.7626 | 4.7433 | 4.5282 | 4.6864 | 4.6845 | 4.7205 | 4.7342 | 4.7623 | 4.7364 | 4.7128 | 4.777 | 4.7746 | 4.8305 | 4.5427 | 4.7536 | 4.7918 | 4.6931 | 4.6961 | 4.7548 | 4.691 | 4.7918 | 4.6953 | 4.8666 | 4.9258 | 4.9204 | 4.9181 | 4.9077 | 4.8718 | 4.9499 | 4.9746 | 4.7718 | 4.8681 | 4.221 | 4.9278 | 4.927 | 5.0353 | 5.0275 | 4.8849 | 4.9469 | 4.9327 | 4.7858 | 4.8703 | 4.8871 | 4.8781 | 4.8621 | 4.9193 | 4.8232 | 4.9608 | 4.9843 | 4.9574 | 5.0417 | 5.0035 | 5.0616 | 4.9468 | 4.9574 | 4.9593 | 5.1001 | 4.8937 | 5.0306 | 5.0257 | 5.1515 | 5.0632 | 5.1409 | 5.033 | 5.088 | 5.1264 | 5.0946 | 5.0361 | 4.6815
2025-06-27 | 2.9274 | 2.7145 | 2.9386 | 2.9492 | 2.9083 | 2.8026 | 3.0099 | 2.872 | 2.9129 | 2.9515 | 2.9667 | 2.9341 | 2.9697 | 2.9439 | 2.9742 | 2.9803 | 2.9338 | 2.9609 | 2.9432 | 2.9727 | 3.0568 | 3.0341 | 3.0417 | 3.0402 | 3.0174 | 3.0364 | 3.0576 | 3.0636 | 3.0742 | 3.0583 | 3.0447 | 3.0379 | 2.9144 | 2.8708 | 2.9107 | 2.9211 | 2.988 | 2.9609 | 2.9136 | 2.9545 | 2.9235 | 2.9857 | 3.0347 | 3.0424 | 3.0219 | 3.1042 | 3.0623 | 3.0376 | 2.9841 | 3.0049 | 3.011 | 2.9369 | 2.9026 | 2.9013 | 2.8757 | 2.951 | 2.9288 | 2.8317 | 2.8355 | 2.8171 | 2.9561 | 2.9021 | 2.7625 | 3.1615 | 3.1525 | 3.1533 | 3.1774 | 3.186 | 3.1664 | 3.1142 | 3.1922 | 3.1749 | 3.138 | 3.068 | 3.1408 | 3.145 | 3.1544 | 3.1315 | 3.148 | 3.1501 | 3.1132 | 3.1458 | 3.1705 | 3.175 | 3.166 | 3.1472 | 3.154 | 3.1222 | 3.1601 | 3.1622 | 3.1736 | 2.9952 | 3.1004 | 3.1004 | 3.1694 | 3.1425 | 3.1314 | 3.1073 | 3.1456 | 3.0754 | 3.0916 | 3.1698 | 3.0778 | 3.1749 | 3.234 | 3.1215 | 3.2129 | 3.1632 | 3.1929 | 3.2322 | 3.2246 | 3.2198 | 3.2113 | 3.1548 | 3.1266 | 3.1994 | 3.1511 | 3.1946 | 3.099 | 3.197 | 3.1829 | 3.1636 | 3.1335 | 3.1649 | 3.186 | 3.1953 | 3.1101 | 3.195 | 3.1529 | 3.1511 | 3.1166 | 3.1494 | 3.0663 | 3.186 | 3.147 | 3.1925 | 3.2219 | 3.2357 | 3.1568 | 3.1884 | 3.1753 | 3.1712 | 3.1894 | 3.1925 | 3.1791 | 3.2291 | 3.1746 | 3.2161 | 3.1951 | 3.1609 | 3.2048 | 3.1946 | 3.223 | 3.1401 | 3.1705 | 3.1128 | 3.1994 | 3.1725 | 3.1511 | 3.0756 | 3.1532 | 3.1694 | 3.1984 | 3.1925 | 3.2146 | 3.1064 | 3.0998 | 3.1568 | 0.5291 | 2.9546 | 3.1168 | 3.1421 | 3.1531 | 3.1735 | 3.2045 | 3.1727 | 3.1391 | 3.1723 | 3.2135 | 3.1683 | 3.1922 | 3.1573 | 3.2029 | 3.1912 | 3.2181 | 3.1912 | 3.1924 | 3.1912 | 3.1905 | 3.1878 | 3.1682 | 3.2067 | 3.1614 | 3.1829 | 3.1683 | 3.1583 | 3.175 | 3.1387 | 3.2247 | 3.1951 | 3.169 | 3.1636 | 3.1955 | 3.1593 | 3.195 | 3.2138 | 3.1957 | 3.099 | 3.1397 | 3.1453 | 3.0923 | 3.0817 | 3.1862 | 3.1845 | 3.2296 | 3.2268 | 3.2133 | 3.1825 | 3.1162 | 3.094 | 3.2291 | 3.1477 | 3.0758 | 3.1031 | 3.1362 | 3.2284 | 3.1147 | 3.0766 | 3.1484 | 3.1499 | 3.1268 | 3.0956 | 3.1794 | 3.1169 | 3.2009 | 3.1381 | 3.1519 | 3.166 | 3.133 | 3.1315 | 3.1158 | 3.1225 | 3.1868 | 3.1986 | 3.1499 | 2.908 | 3.1323 | 2.9611 | 1.3728 | 1.2955 | 3.1266 | 3.1136 | 3.1913 | 3.164 | 3.1203 | 3.1334 | 3.1614 | 3.1333 | 3.047 | 3.1366 | 3.121 | 3.1569 | 3.1564 | 3.1198 | 3.1555 | 3.1629 | 3.1704 | 3.1571 | 3.1672 | 3.1421 | 3.0781 | 3.1088 | 3.104 | 3.0903 | 3.1506 | 3.1419 | 3.1223 | 3.1715 | 3.1351 | 3.0756 | 3.1005 | 3.0703 | 3.0767 | 2.9853 | 3.0174 | 3.1062 | 3.0408 | 3.0019 | 3.0994 | 3.0745 | 3.0801 | 3.1213 | 3.1052 | 3.0679 | 3.0663 | 3.0955 | 3.1275 | 3.1267 | 3.1122 | 3.1339 | 3.0723 | 3.1115 | 3.0895 | 3.1377 | 3.1157 | 3.1128 | 3.1145 | 3.1198 | 3.1313 | 3.1008 | 3.1181 | 3.0008 | 3.1052 | 3.0642 | 3.0496 | 3.0343 | 3.0619 | 3.0608 | 2.967 | 3.0584 | 3.0114 | 3.0616 | 3.0986 | 3.0818 | 3.0078 | 3.0489 | 3.0721 | 3.081 | 3.1127 | 3.0251 | 3.0522 | 3.1071 | 3.1071 | 3.1162 | 3.1193 | 2.9936 | 3.087 | 3.056 | 2.9917 | 3.0306 | 3.0575 | 3.0848 | 3.0534 | 3.0889 | 3.022 | 3.0459 | 3.0573 | 3.0908 | 3.0542 | 3.1044 | 3.0985 | 3.0298 | 3.0982 | 3.1177 | 3.062 | 3.109 | 3.0747 | 3.0769 | 3.0648 | 3.0837 | 3.0769 | 3.0875 | 3.0844 | 3.1436 | 3.1119 | 3.0742 | 3.085
2025-06-28 | 4.1236 | 3.7967 | 4.1182 | 4.1152 | 4.0955 | 3.9658 | 4.2104 | 4.0439 | 4.1318 | 4.1727 | 4.1583 | 4.1356 | 4.1674 | 4.1689 | 4.1962 | 4.1803 | 4.1515 | 4.1778 | 4.1508 | 4.1871 | 4.3091 | 4.2644 | 4.2985 | 4.3 | 4.2811 | 4.2833 | 4.2932 | 4.2962 | 4.3318 | 4.3159 | 4.2864 | 4.3083 | 4.0924 | 4.0574 | 4.0997 | 4.1268 | 4.201 | 4.1738 | 4.1121 | 4.1411 | 4.075 | 4.1312 | 4.2164 | 4.2208 | 4.2178 | 4.3061 | 4.2761 | 4.2285 | 4.1278 | 4.2261 | 4.2522 | 4.1574 | 4.1003 | 4.107 | 4.047 | 4.147 | 4.0746 | 3.9439 | 3.9752 | 3.9298 | 4.1439 | 4.0916 | 4.085 | 4.4134 | 4.3713 | 4.4254 | 4.4158 | 4.4041 | 4.4168 | 4.3185 | 4.4317 | 4.3989 | 4.3237 | 4.2622 | 4.3261 | 4.3817 | 4.3892 | 4.2937 | 4.4075 | 4.4541 | 4.3275 | 4.3872 | 4.4717 | 4.4361 | 4.3975 | 4.4228 | 4.386 | 4.3176 | 4.4313 | 4.4127 | 4.4117 | 4.1542 | 4.2674 | 4.3395 | 4.3709 | 4.3451 | 4.2825 | 4.3965 | 4.3585 | 4.2074 | 4.3618 | 4.3654 | 4.3023 | 4.343 | 4.5169 | 4.3416 | 4.4289 | 4.3827 | 4.3551 | 4.4807 | 4.4562 | 4.4507 | 4.4902 | 4.3402 | 4.3661 | 4.4231 | 4.3899 | 4.4503 | 4.4444 | 4.4783 | 4.4355 | 4.4158 | 4.3907 | 4.4563 | 4.4993 | 4.4896 | 4.3996 | 4.5028 | 4.4075 | 4.4117 | 4.3754 | 4.4303 | 4.393 | 4.4438 | 4.3741 | 4.4296 | 4.491 | 4.4983 | 4.4092 | 4.4479 | 4.4655 | 4.4486 | 4.47 | 4.5045 | 4.4527 | 4.5131 | 4.4686 | 4.5307 | 4.501 | 4.447 | 4.5119 | 4.4569 | 4.5427 | 4.4079 | 4.4144 | 4.2695 | 4.4634 | 4.4451 | 4.2709 | 4.3602 | 4.4303 | 4.2088 | 4.4955 | 4.4015 | 4.472 | 4.4856 | 4.3345 | 4.3836 | 4.3696 | 4.3798 | 4.3779 | 4.3961 | 4.415 | 4.4683 | 4.4921 | 4.4539 | 4.3885 | 4.4051 | 4.48 | 4.4317 | 4.5172 | 4.4174 | 4.4826 | 4.4751 | 4.5004 | 4.4769 | 4.4875 | 4.4815 | 4.4792 | 4.5004 | 4.4645 | 4.506 | 4.4237 | 4.4448 | 4.4567 | 4.4262 | 4.4813 | 4.3908 | 4.5098 | 4.5059 | 4.4029 | 4.4069 | 4.4833 | 4.391 | 4.4389 | 4.4782 | 4.4478 | 4.3339 | 4.4156 | 4.3952 | 4.3321 | 4.2656 | 4.4313 | 4.4765 | 4.52 | 4.4691 | 4.5509 | 4.526 | 4.3086 | 4.2916 | 4.4884 | 4.3772 | 4.2484 | 4.2828 | 4.3692 | 4.4801 | 4.3699 | 4.3371 | 4.4427 | 4.4474 | 4.4474 | 4.4154 | 4.4937 | 4.3952 | 4.4596 | 4.4274 | 4.4505 | 4.4545 | 4.4079 | 4.396 | 4.393 | 4.3788 | 4.4533 | 4.4505 | 4.4207 | 4.1351 | 4.3881 | 4.1119 | 4.3799 | 4.2625 | 4.3915 | 4.3821 | 4.4334 | 4.458 | 4.3863 | 4.3937 | 4.4423 | 4.2165 | 4.1655 | 4.4253 | 4.4191 | 4.411 | 4.4178 | 4.4186 | 4.4316 | 4.4652 | 4.4792 | 4.4301 | 4.4559 | 4.4459 | 4.3227 | 4.4063 | 4.3322 | 4.3786 | 4.5055 | 4.4894 | 4.3895 | 4.5154 | 4.4238 | 4.3549 | 4.3617 | 4.359 | 4.3583 | 4.2419 | 4.2952 | 4.3806 | 4.302 | 4.2763 | 4.3949 | 4.285 | 4.3617 | 4.3847 | 4.396 | 4.3742 | 4.3885 | 4.3965 | 4.4231 | 4.419 | 4.4149 | 4.4107 | 4.2838 | 4.3811 | 4.3644 | 4.4232 | 4.3921 | 4.4243 | 4.3925 | 4.3949 | 4.4171 | 4.3933 | 4.3897 | 4.2338 | 4.4004 | 4.3253 | 4.3093 | 4.2872 | 4.3492 | 4.2733 | 4.3223 | 4.2993 | 4.3042 | 4.3352 | 4.3836 | 4.3347 | 4.2876 | 4.301 | 4.3261 | 4.3511 | 4.3652 | 4.3144 | 4.3811 | 4.4494 | 4.4423 | 4.4427 | 4.4486 | 4.2704 | 4.387 | 4.3956 | 4.2416 | 4.3691 | 4.3653 | 4.381 | 4.3616 | 4.4121 | 4.3362 | 4.4015 | 4.4113 | 4.3911 | 4.384 | 4.396 | 4.436 | 4.3435 | 4.3978 | 4.4199 | 4.427 | 4.4106 | 4.4221 | 4.321 | 4.3619 | 4.3919 | 4.5879 | 4.5918 | 4.4278 | 4.4109 | 4.4262 | 4.3862 | 4.3588
2025-06-29 | 3.8142 | 3.5239 | 3.8265 | 3.8333 | 3.8121 | 3.6674 | 3.9273 | 3.7614 | 3.847 | 3.8833 | 3.878 | 3.8508 | 3.8788 | 3.878 | 3.9068 | 3.8947 | 3.8549 | 3.8923 | 3.8697 | 3.903 | 4.0197 | 3.9811 | 4.0288 | 4.0121 | 3.997 | 4.0023 | 4.0182 | 4.003 | 4.0386 | 4.0341 | 4.0083 | 4.0227 | 3.8242 | 3.7711 | 3.8094 | 3.8365 | 3.8995 | 3.8804 | 3.8341 | 3.8581 | 3.8091 | 3.8631 | 3.9605 | 3.9357 | 3.9459 | 4.042 | 4.0295 | 3.9845 | 3.9144 | 3.9623 | 3.9795 | 3.8774 | 3.8225 | 3.8516 | 3.7901 | 3.8852 | 3.8522 | 3.6928 | 3.7181 | 3.6919 | 3.8636 | 3.8097 | 3.8416 | 4.1536 | 4.1032 | 4.0973 | 4.1115 | 4.138 | 4.0978 | 4.0883 | 4.1622 | 4.1567 | 4.1004 | 4.0292 | 4.0959 | 4.0909 | 4.0938 | 4.1253 | 4.1473 | 4.1297 | 4.1049 | 4.1501 | 4.1573 | 4.1742 | 4.1743 | 4.1461 | 4.1472 | 4.1044 | 4.118 | 4.1398 | 4.1484 | 3.911 | 4.0328 | 4.0469 | 4.0908 | 4.1125 | 4.0844 | 4.0645 | 4.1049 | 4.0722 | 4.0725 | 4.1301 | 4.0149 | 4.146 | 4.3182 | 4.119 | 4.1639 | 4.1115 | 4.0994 | 4.1915 | 4.1846 | 4.2157 | 4.1886 | 4.1382 | 4.1215 | 4.2177 | 4.1636 | 4.2026 | 4.1912 | 4.1891 | 4.1843 | 4.1784 | 4.1378 | 4.1822 | 4.2005 | 4.1912 | 4.1018 | 4.2026 | 4.0697 | 4.156 | 4.1208 | 4.1467 | 4.1646 | 4.1981 | 4.1322 | 4.1839 | 4.2183 | 4.2823 | 4.2032 | 4.1829 | 4.1974 | 4.2226 | 4.2315 | 4.2153 | 4.2019 | 4.2647 | 4.2236 | 4.2619 | 4.2288 | 4.0945 | 4.2202 | 4.217 | 4.2748 | 4.1684 | 4.1722 | 4.2019 | 4.1905 | 4.1901 | 4.1722 | 4.1767 | 4.1736 | 4.2119 | 4.2239 | 4.1944 | 4.234 | 4.2049 | 4.195 | 4.2517 | 4.2196 | 4.2237 | 4.2026 | 4.206 | 4.1965 | 4.2339 | 4.2551 | 4.2264 | 4.2653 | 4.2664 | 4.2763 | 4.2583 | 4.2875 | 4.2294 | 4.2729 | 4.2577 | 4.2668 | 4.2381 | 4.2525 | 4.2389 | 4.2638 | 4.2691 | 4.2472 | 4.2785 | 4.1909 | 4.2079 | 4.2262 | 4.1968 | 4.2218 | 4.2127 | 4.3253 | 4.2841 | 4.2741 | 4.2963 | 4.3711 | 4.2465 | 4.3192 | 4.3617 | 4.3468 | 4.2368 | 4.2811 | 4.2861 | 4.2461 | 4.1867 | 4.2906 | 4.3348 | 4.3383 | 4.3744 | 4.3394 | 4.3171 | 4.2618 | 4.2473 | 4.4043 | 4.3228 | 4.1908 | 4.2421 | 4.2942 | 4.3984 | 4.1662 | 4.1252 | 4.2009 | 4.2355 | 4.1884 | 4.1624 | 4.2378 | 4.1538 | 4.2814 | 4.2445 | 4.2339 | 4.2159 | 4.1728 | 4.174 | 4.1545 | 4.1605 | 4.2818 | 4.3171 | 4.2512 | 3.9777 | 4.2284 | 3.9531 | 4.1998 | 4.0865 | 4.1915 | 4.199 | 4.2663 | 4.2779 | 4.1777 | 4.1889 | 4.2424 | 4.1912 | 4.1037 | 4.1789 | 4.1634 | 4.1983 | 4.2121 | 4.1686 | 4.1933 | 4.2086 | 4.2065 | 4.1779 | 4.1912 | 4.2014 | 4.1099 | 4.117 | 4.1178 | 4.1137 | 4.1959 | 4.1658 | 4.1359 | 4.2089 | 4.1623 | 4.1172 | 4.1172 | 4.1134 | 4.1126 | 4.0015 | 4.0446 | 4.1402 | 4.0782 | 4.045 | 4.1686 | 3.9938 | 4.1251 | 4.1557 | 4.1611 | 4.0956 | 4.106 | 4.1263 | 4.1541 | 4.1487 | 4.1498 | 4.1418 | 4.0118 | 4.1187 | 4.1134 | 4.1524 | 4.1278 | 4.1413 | 4.1437 | 4.1629 | 4.1615 | 4.1246 | 4.133 | 4.0257 | 4.1476 | 4.0928 | 4.0742 | 4.0652 | 4.1008 | 4.0221 | 4.0981 | 4.0745 | 4.0549 | 4.0883 | 4.1418 | 4.1037 | 4.0506 | 4.0678 | 4.0902 | 4.0955 | 4.1397 | 4.0502 | 4.1276 | 4.2072 | 4.1951 | 4.1954 | 4.2005 | 4.088 | 4.1792 | 4.162 | 4.0218 | 4.1414 | 4.1534 | 4.1437 | 4.1455 | 4.171 | 4.0977 | 4.1448 | 4.1601 | 4.1467 | 4.1089 | 4.1397 | 4.1684 | 4.1063 | 4.1455 | 4.1564 | 4.1515 | 4.1705 | 4.1534 | 4.0906 | 4.0883 | 4.1325 | 4.1052 | 4.1609 | 4.1411 | 4.148 | 4.1503 | 4.1515 | 4.1225
2025-06-30 | 4.0351 | 3.9139 | 4.0947 | 4.0879 | 4.0424 | 3.9165 | 4.2295 | 4.028 | 4.0886 | 4.1159 | 4.2091 | 4.1538 | 4.1167 | 4.1364 | 4.1523 | 4.1568 | 4.1156 | 4.1635 | 4.2121 | 4.2129 | 4.4114 | 4.3371 | 4.3326 | 4.3015 | 4.3788 | 4.3886 | 4.3788 | 4.3402 | 4.4773 | 4.4409 | 4.3992 | 4.3818 | 4.0265 | 3.9777 | 4.0359 | 4.071 | 4.1388 | 4.1204 | 4.0621 | 4.0781 | 4.022 | 4.087 | 4.1526 | 4.1579 | 4.1659 | 4.2424 | 4.2064 | 4.1734 | 4.0593 | 4.254 | 4.217 | 4.1392 | 4.1104 | 4.1463 | 4.0925 | 4.1742 | 4.0901 | 3.9306 | 3.9968 | 3.9332 | 4.2197 | 4.1218 | 4.0645 | 4.5231 | 4.4959 | 4.6269 | 4.5262 | 4.4272 | 4.4631 | 4.3623 | 4.5135 | 4.4127 | 4.3323 | 4.2598 | 4.283 | 4.3456 | 4.3254 | 4.2723 | 4.6111 | 4.7077 | 4.6549 | 4.5562 | 4.7419 | 4.5974 | 4.5421 | 4.6364 | 4.5177 | 4.4593 | 4.6663 | 4.5383 | 4.4738 | 4.2719 | 4.3896 | 4.5466 | 4.5866 | 4.5079 | 4.4162 | 4.6449 | 4.3437 | 4.2266 | 4.3405 | 4.5466 | 4.5498 | 4.4796 | 4.7843 | 4.4168 | 4.362 | 4.3785 | 4.4051 | 4.5538 | 4.5576 | 4.5718 | 4.3277 | 4.4816 | 4.4683 | 4.4541 | 4.4731 | 4.5452 | 4.7329 | 4.6511 | 4.4934 | 4.4496 | 4.4668 | 4.5808 | 4.5711 | 4.5383 | 4.4938 | 4.5725 | 4.3585 | 4.4358 | 4.3765 | 4.4707 | 4.3737 | 4.4476 | 4.3489 | 4.3509 | 4.5166 | 4.6025 | 4.413 | 4.4503 | 4.3789 | 4.4952 | 4.4786 | 4.5528 | 4.4355 | 4.5266 | 4.2598 | 4.5476 | 4.419 | 4.4174 | 4.4575 | 4.4075 | 4.4856 | 4.3088 | 4.3295 | 4.421 | 4.4917 | 4.2636 | 4.2726 | 4.2598 | 4.3961 | 4.3333 | 4.4634 | 4.2698 | 4.3582 | 4.3052 | 4.6757 | 4.8039 | 4.7676 | 4.7611 | 4.7423 | 4.7305 | 4.7215 | 4.7109 | 4.7041 | 4.729 | 4.7842 | 4.7804 | 4.8246 | 4.7929 | 4.8668 | 4.6086 | 4.794 | 4.7339 | 4.7101 | 4.6345 | 4.6353 | 4.582 | 4.6466 | 4.5937 | 4.5756 | 4.5801 | 4.4233 | 4.4815 | 4.5131 | 4.4464 | 4.5631 | 4.4939 | 4.7511 | 4.8006 | 4.695 | 4.7587 | 4.9504 | 4.6223 | 4.7341 | 4.9108 | 4.7659 | 4.6992 | 4.8626 | 4.9249 | 4.8928 | 4.7392 | 4.568 | 4.7555 | 4.708 | 4.7987 | 4.7889 | 4.8548 | 4.687 | 4.7224 | 4.9612 | 4.7534 | 4.6573 | 4.7921 | 4.6477 | 4.9334 | 4.2443 | 4.1976 | 4.3901 | 4.3654 | 4.4294 | 4.3795 | 4.4611 | 4.3736 | 4.4211 | 4.3862 | 4.3901 | 4.425 | 4.3736 | 4.3631 | 4.3451 | 4.3567 | 4.4243 | 4.4859 | 4.4392 | 4.1657 | 4.3689 | 4.2229 | 4.3693 | 4.3306 | 4.3593 | 4.402 | 4.4883 | 4.5885 | 4.3866 | 4.3231 | 4.5055 | 4.6318 | 4.5722 | 4.6744 | 4.6296 | 4.6043 | 4.5588 | 4.2541 | 4.4234 | 4.548 | 4.5731 | 4.5103 | 4.477 | 4.4045 | 4.3296 | 4.5162 | 4.286 | 4.4384 | 4.4959 | 4.5007 | 4.3482 | 4.5501 | 4.4441 | 4.842 | 4.8099 | 4.7661 | 4.8065 | 4.616 | 4.7037 | 4.791 | 4.6875 | 4.6754 | 4.7347 | 4.4199 | 4.6875 | 4.6538 | 4.7393 | 4.729 | 4.719 | 4.6849 | 4.6689 | 4.6602 | 4.6322 | 4.6109 | 4.5857 | 4.5882 | 4.5927 | 4.5529 | 4.5612 | 4.7182 | 4.5939 | 4.6054 | 4.6115 | 4.573 | 4.8936 | 4.5693 | 4.9544 | 4.818 | 4.7511 | 4.7081 | 4.7107 | 4.6484 | 4.4042 | 4.559 | 4.8426 | 4.9188 | 4.8053 | 4.8602 | 4.7514 | 4.7028 | 4.7638 | 4.6587 | 4.683 | 4.697 | 4.5133 | 4.6994 | 4.6617 | 4.7567 | 4.7488 | 4.556 | 4.6569 | 4.698 | 4.5081 | 4.6397 | 4.5892 | 4.6214 | 4.5788 | 4.6244 | 4.5182 | 4.646 | 4.6586 | 4.6625 | 4.7476 | 4.6535 | 4.7508 | 4.6896 | 4.7481 | 4.7664 | 4.8454 | 4.6817 | 4.7686 | 4.7271 | 4.8571 | 4.7604 | 4.8469 | 4.7437 | 4.7872 | 4.7822 | 4.7908 | 4.6837 | 4.5014
2025-07-01 | 4.0263 | 3.9298 | 4.0439 | 4.0439 | 3.9992 | 3.8702 | 4.1492 | 3.9689 | 4.0235 | 4.0674 | 4.1038 | 4.0712 | 4.0652 | 4.0735 | 4.0917 | 4.0848 | 4.0534 | 4.1021 | 4.0939 | 4.1265 | 4.2553 | 4.2098 | 4.2159 | 4.2061 | 4.2364 | 4.2273 | 4.2235 | 4.2061 | 4.297 | 4.2705 | 4.225 | 4.2242 | 3.9629 | 3.929 | 3.988 | 4.0016 | 4.0766 | 4.0686 | 3.9712 | 4.0239 | 3.9568 | 4.0171 | 4.1012 | 4.1082 | 4.0848 | 4.1722 | 4.1696 | 4.1109 | 4.0862 | 4.1228 | 4.1122 | 4.0022 | 3.9524 | 4.0083 | 3.9565 | 4.063 | 4.0255 | 3.8717 | 3.9002 | 3.872 | 4.0561 | 3.9896 | 3.9721 | 4.4161 | 4.383 | 4.4088 | 4.4293 | 4.4427 | 4.384 | 4.3399 | 4.4096 | 4.432 | 4.3492 | 4.2817 | 4.3464 | 4.3474 | 4.3416 | 4.4272 | 4.4151 | 4.4068 | 4.3627 | 4.4091 | 4.4137 | 4.4351 | 4.4355 | 4.4048 | 4.4134 | 4.3867 | 4.4306 | 4.4041 | 4.4172 | 4.2067 | 4.3344 | 4.3188 | 4.3758 | 4.353 | 4.3356 | 4.2988 | 4.3437 | 4.3153 | 4.3326 | 4.4044 | 4.251 | 4.4344 | 4.3847 | 4.3951 | 4.4755 | 4.4189 | 4.442 | 4.519 | 4.5014 | 4.509 | 4.387 | 4.4214 | 4.3634 | 4.3627 | 4.4217 | 4.4327 | 4.4396 | 4.4158 | 4.3854 | 4.352 | 4.3034 | 4.3777 | 4.3575 | 4.3357 | 4.254 | 4.3447 | 4.3009 | 4.3171 | 4.2433 | 4.2443 | 4.3123 | 4.3106 | 4.2616 | 4.3219 | 4.3193 | 4.2947 | 4.2295 | 4.186 | 4.216 | 4.2181 | 4.234 | 4.2264 | 4.2136 | 4.2747 | 4.1311 | 4.2486 | 4.2308 | 4.1833 | 4.2131 | 4.2302 | 4.2532 | 4.1863 | 4.2246 | 4.1453 | 4.2519 | 4.2274 | 4.235 | 4.1674 | 4.2026 | 4.1891 | 4.2222 | 4.3356 | 4.3209 | 4.1811 | 4.1141 | 4.1912 | 4.155 | 4.1704 | 4.1814 | 4.2086 | 4.2286 | 4.2683 | 4.2937 | 4.2468 | 4.1674 | 4.1852 | 4.271 | 4.1897 | 4.2628 | 4.2204 | 4.2789 | 4.2702 | 4.2955 | 4.2695 | 4.2698 | 4.2668 | 4.2725 | 4.2638 | 4.2453 | 4.2732 | 4.2158 | 4.2479 | 4.2325 | 4.2079 | 4.2627 | 4.1298 | 4.2239 | 4.186 | 4.1194 | 4.1277 | 4.1928 | 4.1271 | 4.1714 | 4.2144 | 4.2161 | 4.1009 | 4.1187 | 4.1444 | 4.0912 | 4.1293 | 4.1582 | 4.1468 | 4.2225 | 4.2028 | 4.2147 | 4.1531 | 4.1274 | 4.0455 | 4.1845 | 4.108 | 3.9914 | 4.025 | 4.0938 | 4.1485 | 4.1437 | 4.107 | 4.2033 | 4.175 | 4.2017 | 4.1642 | 4.2206 | 4.1407 | 4.2296 | 4.1864 | 4.2017 | 4.1601 | 4.0532 | 4.1698 | 4.0439 | 4.1504 | 4.2088 | 4.2308 | 4.1452 | 4.0099 | 4.1688 | 4.0327 | 4.1703 | 4.097 | 4.1717 | 4.1661 | 4.119 | 4.1657 | 4.1085 | 4.1306 | 4.211 | 4.2147 | 4.1423 | 4.3014 | 4.2653 | 4.3001 | 4.2788 | 4.2247 | 4.2671 | 4.2554 | 4.284 | 4.3079 | 4.2889 | 4.2723 | 4.1715 | 4.1464 | 4.2091 | 4.1451 | 4.1968 | 4.1815 | 4.2151 | 4.2444 | 4.2436 | 4.3522 | 4.3564 | 4.3314 | 4.3492 | 4.22 | 4.2653 | 4.3605 | 4.2706 | 4.2457 | 4.3496 | 4.3202 | 4.3103 | 4.3386 | 4.3516 | 4.3421 | 4.3452 | 4.3695 | 4.4011 | 4.4096 | 4.4171 | 4.3967 | 4.3396 | 4.325 | 4.3242 | 4.3356 | 4.3144 | 4.3581 | 4.3185 | 4.3409 | 4.3127 | 4.2766 | 4.3305 | 4.1973 | 4.425 | 4.3265 | 4.307 | 4.2809 | 4.3183 | 4.2271 | 4.0506 | 4.2725 | 4.2767 | 4.325 | 4.3515 | 4.2536 | 4.2566 | 4.2693 | 4.288 | 4.1642 | 4.3527 | 4.279 | 4.1531 | 4.3827 | 4.2979 | 4.3524 | 4.3984 | 4.184 | 4.3123 | 4.279 | 4.1874 | 4.2779 | 4.3108 | 4.3208 | 4.3164 | 4.3425 | 4.2775 | 4.3281 | 4.3367 | 4.3369 | 4.2878 | 4.3183 | 4.3556 | 4.2318 | 4.2868 | 4.3235 | 4.2877 | 4.3503 | 4.2861 | 4.2654 | 4.2563 | 4.2906 | 4.2955 | 4.3348 | 4.3262 | 4.3666 | 4.3528 | 4.3493 | 4.2367
2025-07-02 | 3.3708 | 3.2719 | 3.397 | 3.3826 | 3.3053 | 3.1746 | 3.505 | 3.328 | 3.3356 | 3.3924 | 3.475 | 3.422 | 3.4023 | 3.4197 | 3.4462 | 3.4833 | 3.4123 | 3.4888 | 3.4894 | 3.5023 | 3.6417 | 3.6114 | 3.6091 | 3.6144 | 3.6273 | 3.6432 | 3.6515 | 3.6356 | 3.7083 | 3.7 | 3.6508 | 3.6318 | 3.3318 | 3.2695 | 3.315 | 3.3604 | 3.4553 | 3.453 | 3.3523 | 3.4242 | 3.3697 | 3.4201 | 3.4709 | 3.5102 | 3.5175 | 3.5832 | 3.5932 | 3.5571 | 3.5196 | 3.5855 | 3.5858 | 3.5098 | 3.482 | 3.4997 | 3.4378 | 3.5164 | 3.453 | 3.3443 | 3.3706 | 3.3394 | 3.5114 | 3.4602 | 3.4494 | 3.7346 | 3.6977 | 3.6933 | 3.697 | 3.7219 | 3.6769 | 3.6753 | 3.7291 | 3.7084 | 3.658 | 3.5771 | 3.6425 | 3.6436 | 3.631 | 3.8012 | 3.8264 | 3.8306 | 3.7422 | 3.795 | 3.8043 | 3.8005 | 3.7899 | 3.6631 | 3.7504 | 3.7152 | 3.725 | 3.7643 | 3.7571 | 3.6059 | 3.7181 | 3.7895 | 3.8137 | 3.8578 | 3.827 | 3.8309 | 3.8485 | 3.6122 | 3.7731 | 3.8068 | 3.7341 | 3.8188 | 4.0231 | 3.7357 | 3.8019 | 3.6981 | 3.7464 | 3.8043 | 3.7761 | 3.8192 | 3.8054 | 3.7475 | 3.7536 | 3.8364 | 3.8213 | 3.8437 | 3.8765 | 3.8547 | 3.7867 | 3.7809 | 3.7615 | 3.812 | 3.8492 | 3.8499 | 3.7861 | 3.8992 | 3.8064 | 3.8226 | 3.7695 | 3.7888 | 3.8288 | 3.844 | 3.7754 | 3.8019 | 3.8644 | 3.8061 | 3.7378 | 3.7333 | 3.7519 | 3.765 | 3.7905 | 3.8233 | 3.7836 | 3.8747 | 3.8492 | 3.8766 | 3.8284 | 3.8016 | 3.8429 | 3.8233 | 3.873 | 3.7764 | 3.8078 | 3.8206 | 3.8337 | 3.8271 | 3.7995 | 3.8409 | 3.8233 | 3.7574 | 3.8706 | 3.8175 | 3.862 | 3.8294 | 3.7166 | 3.763 | 3.7184 | 3.715 | 3.7101 | 3.7286 | 3.7381 | 3.7509 | 3.8122 | 3.7812 | 3.7509 | 3.7717 | 3.8137 | 3.7694 | 3.8069 | 3.7348 | 3.8205 | 3.7952 | 3.8375 | 3.8088 | 3.8182 | 3.8292 | 3.8005 | 3.8269 | 3.7797 | 3.8621 | 3.8394 | 3.8401 | 3.8456 | 3.8377 | 3.8274 | 3.6871 | 3.7599 | 3.6597 | 3.7251 | 3.7315 | 3.7714 | 3.7166 | 3.7776 | 3.8113 | 3.7967 | 3.702 | 3.6357 | 3.7613 | 3.6069 | 3.645 | 3.73 | 3.7151 | 3.781 | 3.7184 | 3.7668 | 3.7411 | 3.7081 | 3.6835 | 3.8093 | 3.7387 | 3.6254 | 3.6738 | 3.6862 | 3.7858 | 3.8258 | 3.7819 | 3.8721 | 3.8681 | 3.9129 | 3.8331 | 3.9403 | 3.8323 | 3.9038 | 3.8509 | 3.8689 | 3.8764 | 3.7841 | 3.8189 | 3.7714 | 3.8099 | 3.8465 | 3.8422 | 3.7469 | 3.5957 | 3.8069 | 3.6208 | 3.8254 | 3.6866 | 3.8084 | 3.7669 | 3.7662 | 3.7505 | 3.7725 | 3.7643 | 3.777 | 3.9985 | 3.8784 | 3.9427 | 3.9404 | 3.9446 | 3.921 | 3.8569 | 3.8954 | 3.8918 | 3.8622 | 3.8356 | 3.8561 | 3.879 | 3.8101 | 3.8245 | 3.832 | 3.803 | 3.8967 | 3.8479 | 3.8294 | 3.9069 | 3.8426 | 3.9014 | 3.8934 | 3.8598 | 3.8768 | 3.7611 | 3.8065 | 3.8908 | 3.8296 | 3.7691 | 3.8896 | 3.8333 | 3.8394 | 3.8908 | 3.923 | 3.8679 | 3.8679 | 3.8954 | 3.9186 | 3.9298 | 3.9075 | 3.917 | 3.8345 | 3.8206 | 3.8203 | 3.8267 | 3.8218 | 3.8642 | 3.832 | 3.8851 | 3.875 | 3.8381 | 3.8976 | 3.7963 | 4.0155 | 3.9265 | 3.8596 | 3.8574 | 3.9306 | 3.899 | 3.8521 | 3.9625 | 3.9105 | 3.9867 | 3.9822 | 3.9452 | 3.9127 | 3.9725 | 3.9617 | 3.8996 | 4.0155 | 3.9627 | 3.8791 | 4.1103 | 4.102 | 4.1052 | 4.1185 | 4.0506 | 4.1515 | 4.1123 | 4.0069 | 4.0824 | 4.0902 | 4.1171 | 4.0861 | 4.122 | 4.0525 | 4.073 | 4.0581 | 4.0682 | 4.0465 | 4.0887 | 4.1228 | 4.0788 | 4.1493 | 4.1672 | 4.1276 | 4.1412 | 4.1231 | 4.0831 | 4.1091 | 4.1269 | 4.1209 | 4.1468 | 4.1337 | 4.1907 | 4.1327 | 4.1071 | 3.7784
2025-07-03 | 4.3046 | 4.197 | 4.3091 | 4.2977 | 4.2629 | 4.1359 | 4.3818 | 4.1992 | 4.2765 | 4.3265 | 4.3129 | 4.2773 | 4.3394 | 4.3038 | 4.3523 | 4.3152 | 4.2831 | 4.2751 | 4.2606 | 4.2955 | 4.4205 | 4.3689 | 4.397 | 4.3856 | 4.372 | 4.3811 | 4.3955 | 4.3773 | 4.4189 | 4.4068 | 4.3833 | 4.3841 | 4.2985 | 4.2337 | 4.2592 | 4.2879 | 4.3772 | 4.3373 | 4.3023 | 4.3373 | 4.297 | 4.3466 | 4.423 | 4.4335 | 4.4393 | 4.5268 | 4.4578 | 4.3884 | 4.2023 | 4.3015 | 4.393 | 4.2719 | 4.1804 | 4.1463 | 4.0884 | 4.2155 | 4.1606 | 4.0484 | 4.0487 | 3.9729 | 4.2235 | 4.1409 | 4.2705 | 4.3344 | 4.3164 | 4.531 | 4.3502 | 4.323 | 4.3667 | 4.2619 | 4.4199 | 4.3133 | 4.3016 | 4.216 | 4.2105 | 4.3723 | 4.2825 | 4.256 | 4.343 | 4.5342 | 4.2678 | 4.2973 | 4.4337 | 4.3781 | 4.3423 | 4.3243 | 4.3117 | 4.2727 | 4.5349 | 4.3506 | 4.3506 | 4.1722 | 4.3413 | 4.3796 | 4.4714 | 4.3561 | 4.3022 | 4.5183 | 4.3647 | 4.3763 | 4.4127 | 4.3496 | 4.2791 | 4.3333 | 4.5845 | 4.3326 | 4.3875 | 4.3064 | 4.4717 | 4.3996 | 4.3941 | 4.3789 | 4.5385 | 4.2727 | 4.3202 | 4.3209 | 4.3171 | 4.3616 | 4.5349 | 4.431 | 4.3447 | 4.3037 | 4.2742 | 4.3701 | 4.4155 | 4.5179 | 4.372 | 4.4821 | 4.2264 | 4.3589 | 4.2405 | 4.4351 | 4.2867 | 4.3765 | 4.2754 | 4.3223 | 4.4921 | 4.6104 | 4.3524 | 4.3841 | 4.6518 | 4.3678 | 4.4293 | 4.6643 | 4.3706 | 4.6615 | 4.4289 | 4.4654 | 4.3724 | 4.5556 | 4.3683 | 4.4055 | 4.3919 | 4.226 | 4.2298 | 4.2861 | 4.4306 | 4.2919 | 4.2812 | 4.2246 | 4.216 | 4.2516 | 4.5845 | 4.2722 | 4.3061 | 4.2994 | 4.6251 | 4.6153 | 4.562 | 4.5627 | 4.5329 | 4.5646 | 4.5839 | 4.6149 | 4.6028 | 4.5552 | 4.6062 | 4.6202 | 4.6179 | 4.6258 | 4.6455 | 4.5123 | 4.5975 | 4.5597 | 4.582 | 4.5597 | 4.5548 | 4.5745 | 4.5684 | 4.5862 | 4.5586 | 4.5941 | 4.5348 | 4.5839 | 4.5722 | 4.5452 | 4.5964 | 4.3181 | 4.4353 | 4.3689 | 4.3619 | 4.3779 | 4.4888 | 4.3501 | 4.4352 | 4.7209 | 4.6942 | 4.4716 | 4.5719 | 4.4206 | 4.727 | 4.3625 | 4.3541 | 4.3968 | 4.4505 | 4.3665 | 4.4534 | 4.4109 | 4.4489 | 4.5236 | 4.7654 | 4.5691 | 4.4775 | 4.6248 | 4.4209 | 4.7293 | 4.4017 | 4.3482 | 4.48 | 4.4753 | 4.3932 | 4.3911 | 4.4643 | 4.3941 | 4.5428 | 4.4823 | 4.4945 | 4.4192 | 4.319 | 4.473 | 4.3455 | 4.4554 | 4.5255 | 4.5487 | 4.4674 | 4.3736 | 4.4906 | 4.3949 | 4.4808 | 4.4431 | 4.4633 | 4.4543 | 4.3803 | 4.532 | 4.4199 | 4.4786 | 4.4928 | 4.2718 | 4.2663 | 4.2782 | 4.2471 | 4.2983 | 4.3047 | 4.1918 | 4.1697 | 4.3603 | 4.3611 | 4.2987 | 4.3282 | 4.3573 | 4.18 | 4.2466 | 4.1944 | 4.2429 | 4.3053 | 4.2936 | 4.2482 | 4.3646 | 4.315 | 4.3462 | 4.3507 | 4.3364 | 4.3662 | 4.2381 | 4.3008 | 4.3549 | 4.2971 | 4.246 | 4.3655 | 4.2405 | 4.3262 | 4.3549 | 4.3837 | 4.3754 | 4.3472 | 4.3619 | 4.3676 | 4.3804 | 4.3868 | 4.3622 | 4.2679 | 4.3204 | 4.3125 | 4.347 | 4.3295 | 4.3849 | 4.3318 | 4.3579 | 4.379 | 4.3556 | 4.2873 | 4.2751 | 4.4095 | 4.316 | 4.2939 | 4.2906 | 4.3349 | 4.2638 | 4.2704 | 4.2475 | 4.3085 | 4.3732 | 4.3612 | 4.2995 | 4.2794 | 4.2913 | 4.3205 | 4.2487 | 4.3612 | 4.3042 | 4.292 | 4.3783 | 4.3104 | 4.4074 | 4.3964 | 4.4438 | 4.5246 | 4.2024 | 4.3399 | 4.4173 | 4.43 | 4.4192 | 4.3964 | 4.4106 | 4.304 | 4.354 | 4.3642 | 4.3736 | 4.3745 | 4.3827 | 4.4494 | 4.4456 | 4.5257 | 4.5062 | 4.5004 | 4.4566 | 4.4599 | 4.4431 | 4.5063 | 4.4591 | 4.4984 | 4.4462 | 4.4629 | 4.5 | 4.4867 | 4.4093 | 4.3843
2025-07-04 | 3.2512 | 3.1866 | 3.2477 | 3.2652 | 3.2614 | 3.1587 | 3.3298 | 3.1962 | 3.2864 | 3.3159 | 3.2917 | 3.2742 | 3.3295 | 3.3167 | 3.3508 | 3.3356 | 3.2887 | 3.3166 | 3.2879 | 3.3121 | 3.4091 | 3.3833 | 3.4061 | 3.4258 | 3.3939 | 3.3977 | 3.4091 | 3.4045 | 3.4356 | 3.428 | 3.4045 | 3.4 | 3.3364 | 3.2791 | 3.2879 | 3.3365 | 3.3796 | 3.3509 | 3.3455 | 3.3684 | 3.3523 | 3.3809 | 3.4244 | 3.4466 | 3.4635 | 3.5137 | 3.5034 | 3.4657 | 3.3417 | 3.4131 | 3.4611 | 3.3677 | 3.3225 | 3.3209 | 3.2576 | 3.3422 | 3.2742 | 3.1837 | 3.1733 | 3.1565 | 3.2886 | 3.2731 | 3.36 | 3.5003 | 3.4834 | 3.5303 | 3.4972 | 3.4983 | 3.4795 | 3.4358 | 3.5235 | 3.4938 | 3.4531 | 3.3938 | 3.3468 | 3.4632 | 3.4127 | 3.4959 | 3.4972 | 3.5262 | 3.4444 | 3.4831 | 3.5331 | 3.5213 | 3.5014 | 3.5047 | 3.4766 | 3.4578 | 3.539 | 3.4917 | 3.5052 | 3.3375 | 3.4334 | 3.4696 | 3.5093 | 3.471 | 3.4057 | 3.4969 | 3.4617 | 3.4477 | 3.4906 | 3.4841 | 3.4204 | 3.4914 | 3.6611 | 3.4655 | 3.5449 | 3.4817 | 3.4962 | 3.5714 | 3.5621 | 3.3727 | 3.5843 | 3.4636 | 3.4614 | 3.5393 | 3.4934 | 3.5311 | 3.5745 | 3.5497 | 3.528 | 3.54 | 3.5014 | 3.5408 | 3.6242 | 3.6501 | 3.5418 | 3.6494 | 3.4714 | 3.5697 | 3.5524 | 3.6166 | 3.579 | 3.6408 | 3.5732 | 3.6097 | 3.6079 | 3.549 | 3.4603 | 3.5507 | 3.5455 | 3.511 | 3.5335 | 3.5945 | 3.5642 | 3.6135 | 3.5245 | 3.6291 | 3.6276 | 3.6255 | 3.6599 | 3.5921 | 3.6795 | 3.5652 | 3.5939 | 3.5518 | 3.6429 | 3.5414 | 3.4203 | 3.607 | 3.6215 | 3.6222 | 3.6649 | 3.6019 | 3.6308 | 3.6313 | 3.4335 | 3.4887 | 3.4588 | 3.4664 | 3.4615 | 3.4735 | 3.4717 | 3.4902 | 3.5193 | 3.5023 | 3.4815 | 3.5008 | 3.5397 | 3.5079 | 3.5635 | 3.4802 | 3.5404 | 3.5325 | 3.5472 | 3.52 | 3.5302 | 3.5333 | 3.5268 | 3.5378 | 3.5132 | 3.5491 | 3.5537 | 3.5427 | 3.5437 | 3.5504 | 3.5433 | 3.4786 | 3.561 | 3.5396 | 3.4949 | 3.494 | 3.558 | 3.4769 | 3.5301 | 3.5661 | 3.5533 | 3.4615 | 3.4034 | 3.521 | 3.5004 | 3.462 | 3.5067 | 3.5 | 3.5663 | 3.4678 | 3.5739 | 3.5614 | 3.3978 | 3.4702 | 3.5806 | 3.5091 | 3.4418 | 3.4698 | 3.4767 | 3.5696 | 3.473 | 3.4455 | 3.5612 | 3.5432 | 3.5922 | 3.5255 | 3.6287 | 3.5359 | 3.5648 | 3.5357 | 3.5522 | 3.5267 | 3.5161 | 3.5217 | 3.5012 | 3.5165 | 3.5487 | 3.5283 | 3.5137 | 3.4313 | 3.5114 | 3.423 | 3.5283 | 3.398 | 3.5008 | 3.4799 | 3.5023 | 3.5213 | 3.4851 | 3.481 | 3.5086 | 3.5079 | 3.3949 | 3.5059 | 3.486 | 3.4963 | 3.5299 | 3.4451 | 3.5364 | 3.5629 | 3.5878 | 3.5472 | 3.5814 | 3.5599 | 3.4526 | 3.5284 | 3.4945 | 3.5374 | 3.6682 | 3.6255 | 3.5254 | 3.6631 | 3.5604 | 3.4872 | 3.4879 | 3.4656 | 3.4735 | 3.4116 | 3.4252 | 3.4921 | 3.4463 | 3.4108 | 3.5049 | 3.43 | 3.4686 | 3.4875 | 3.5222 | 3.4853 | 3.4762 | 3.4833 | 3.5194 | 3.5063 | 3.5047 | 3.5085 | 3.4476 | 3.479 | 3.4611 | 3.5233 | 3.4918 | 3.5115 | 3.485 | 3.4936 | 3.504 | 3.4905 | 3.4635 | 3.3728 | 3.5135 | 3.4533 | 3.4272 | 3.42 | 3.4702 | 3.4215 | 3.3823 | 3.423 | 3.4372 | 3.4623 | 3.4974 | 3.4541 | 3.4111 | 3.4425 | 3.4552 | 3.4133 | 3.4789 | 3.4352 | 3.3874 | 3.5286 | 3.5251 | 3.5636 | 3.5538 | 3.3935 | 3.4671 | 3.346 | 3.3632 | 3.441 | 3.4488 | 3.466 | 3.4567 | 3.4937 | 3.4414 | 3.4984 | 3.5204 | 3.4956 | 3.4822 | 3.4925 | 3.5322 | 3.4334 | 3.4784 | 3.4836 | 3.4867 | 3.4733 | 3.4694 | 3.4412 | 3.4478 | 3.466 | 3.4662 | 3.511 | 3.5181 | 3.5063 | 3.5165 | 3.5063 | 3.4779
2025-07-05 | 2.7201 | 2.634 | 2.7394 | 2.7326 | 2.6886 | 2.5695 | 2.8355 | 2.6909 | 2.7417 | 2.7402 | 2.8121 | 2.7894 | 2.728 | 2.7561 | 2.7674 | 2.7765 | 2.7592 | 2.8182 | 2.8167 | 2.8409 | 2.9106 | 2.8947 | 2.9061 | 2.8803 | 2.8924 | 2.9023 | 2.9318 | 2.9114 | 2.9303 | 2.9303 | 2.9258 | 2.9265 | 2.6492 | 2.6053 | 2.6555 | 2.6882 | 2.7552 | 2.7576 | 2.6773 | 2.7392 | 2.6902 | 2.6897 | 2.7212 | 2.7178 | 2.7588 | 2.7923 | 2.8036 | 2.7762 | 2.7433 | 2.8409 | 2.8218 | 2.7687 | 2.7439 | 2.7819 | 2.7562 | 2.7887 | 2.7567 | 2.6466 | 2.7045 | 2.6718 | 2.8242 | 2.8025 | 2.7133 | 2.9382 | 2.9082 | 2.9585 | 2.9344 | 2.9199 | 2.938 | 2.9044 | 2.9824 | 2.931 | 2.9113 | 2.859 | 2.901 | 2.9177 | 2.9159 | 2.9651 | 2.9762 | 3.0304 | 2.9237 | 2.9606 | 2.9928 | 2.9881 | 2.951 | 2.9524 | 2.939 | 2.9058 | 2.4779 | 2.9527 | 2.9489 | 2.7716 | 2.8109 | 2.873 | 2.8778 | 2.8675 | 2.8365 | 2.9213 | 2.8723 | 2.8535 | 2.8676 | 2.892 | 2.8462 | 2.8778 | 3.0179 | 2.8803 | 2.931 | 2.8975 | 2.8713 | 2.9634 | 2.9545 | 2.9517 | 2.986 | 2.9037 | 2.9534 | 3.0117 | 2.9762 | 3.0321 | 3.0794 | 3.0531 | 3.0197 | 3.0131 | 2.9989 | 3.0509 | 3.0666 | 3.0386 | 3.0117 | 3.0794 | 3.0021 | 3.0197 | 2.9776 | 3.038 | 2.97 | 2.9955 | 2.931 | 2.9386 | 2.9423 | 2.8551 | 2.793 | 2.7981 | 2.8244 | 2.8333 | 2.8492 | 2.912 | 2.8568 | 2.9262 | 2.8416 | 2.9798 | 2.9583 | 2.9646 | 3.0075 | 2.8937 | 2.9913 | 2.8899 | 2.9041 | 2.8216 | 2.8357 | 2.9438 | 2.8492 | 2.8347 | 2.9165 | 2.9431 | 3.0238 | 2.9028 | 2.9427 | 2.9668 | 2.8692 | 2.8836 | 2.8371 | 2.8277 | 2.7816 | 2.7748 | 2.7676 | 2.7944 | 2.8246 | 2.8065 | 2.8844 | 2.8832 | 2.8462 | 2.8794 | 2.9158 | 2.8189 | 2.845 | 2.8367 | 2.8416 | 2.8307 | 2.8337 | 2.8492 | 2.836 | 2.8481 | 2.8163 | 2.8481 | 2.8783 | 2.8515 | 2.8552 | 2.8683 | 2.8671 | 2.8227 | 2.9302 | 2.8619 | 2.8961 | 2.9223 | 3.0327 | 2.8496 | 2.9244 | 3.0251 | 2.9814 | 2.926 | 2.8846 | 3.0115 | 2.9947 | 2.9167 | 2.9435 | 2.9662 | 2.9435 | 2.9658 | 2.9753 | 3.0019 | 2.8522 | 2.9478 | 3.076 | 2.9942 | 2.9017 | 2.9624 | 2.9118 | 3.0282 | 2.784 | 2.7676 | 2.8634 | 2.8595 | 2.8783 | 2.8127 | 2.9137 | 2.8231 | 2.8724 | 2.8513 | 2.8583 | 2.8732 | 2.8276 | 2.8201 | 2.8467 | 2.8381 | 2.8689 | 2.8375 | 2.8332 | 2.7659 | 2.8179 | 2.7626 | 2.8544 | 2.819 | 2.825 | 2.8037 | 2.822 | 2.8844 | 2.7876 | 2.7985 | 2.81 | 3.0676 | 2.9985 | 3.0582 | 3.0312 | 3.0203 | 3.0217 | 2.9894 | 2.7305 | 3.0559 | 3.0602 | 3.0134 | 3.0398 | 2.9852 | 2.8195 | 2.9533 | 2.884 | 2.9137 | 2.9941 | 2.9784 | 2.9343 | 3.0352 | 3.0259 | 2.9444 | 2.958 | 2.8511 | 2.9342 | 2.9203 | 2.9093 | 2.9837 | 2.9732 | 2.9346 | 3.0363 | 2.9375 | 3.0087 | 3.0128 | 3.0567 | 2.9865 | 2.9889 | 2.9905 | 3.0122 | 3.0038 | 2.9909 | 3.0015 | 2.9041 | 2.9795 | 2.975 | 2.989 | 2.9769 | 3.0474 | 2.9879 | 3.0144 | 3.0163 | 2.975 | 2.9651 | 2.8268 | 2.9762 | 2.9267 | 2.9173 | 2.9226 | 2.9996 | 2.9517 | 2.9659 | 2.9207 | 2.905 | 2.9305 | 2.9756 | 2.939 | 2.9072 | 2.9237 | 2.9121 | 2.8841 | 2.9631 | 2.9349 | 2.9188 | 2.9965 | 2.998 | 2.9474 | 3.0012 | 2.8071 | 2.8732 | 2.8751 | 2.8093 | 2.8766 | 2.8728 | 2.8885 | 2.8983 | 2.9169 | 2.8893 | 2.9486 | 2.9356 | 2.9233 | 2.9187 | 2.9133 | 2.9392 | 2.8215 | 2.8627 | 2.8859 | 2.8944 | 2.8818 | 2.8897 | 2.8521 | 2.8654 | 2.8889 | 2.8772 | 2.9341 | 2.9265 | 2.9195 | 2.927 | 2.9093 | 2.8929
2025-07-06 | 2.5327 | 2.4601 | 2.5402 | 2.5326 | 2.5212 | 2.4282 | 2.6113 | 2.4833 | 2.5591 | 2.5644 | 2.5788 | 2.5636 | 2.5682 | 2.5712 | 2.5939 | 2.5856 | 2.551 | 2.5981 | 2.5803 | 2.5977 | 2.6644 | 2.6508 | 2.6553 | 2.6576 | 2.6348 | 2.6508 | 2.6712 | 2.6659 | 2.6705 | 2.6667 | 2.6576 | 2.65 | 2.5333 | 2.4904 | 2.512 | 2.5391 | 2.5845 | 2.5726 | 2.5379 | 2.5797 | 2.5394 | 2.5635 | 2.611 | 2.6148 | 2.6389 | 2.6845 | 2.6816 | 2.6579 | 2.5947 | 2.6434 | 2.6613 | 2.5954 | 2.5577 | 2.5735 | 2.5366 | 2.5836 | 2.5645 | 2.4642 | 2.484 | 2.4611 | 2.5697 | 2.5589 | 2.5711 | 2.7177 | 2.7015 | 2.7016 | 2.7074 | 2.7343 | 2.7189 | 2.7032 | 2.7591 | 2.746 | 2.7184 | 2.6785 | 2.7122 | 2.7078 | 2.7136 | 2.5828 | 2.6118 | 2.717 | 2.5818 | 2.7093 | 2.7057 | 2.7244 | 2.7112 | 2.6861 | 2.7002 | 2.6777 | 2.7019 | 2.7063 | 2.725 | 2.5404 | 2.6018 | 2.5959 | 2.6315 | 2.6356 | 2.6213 | 2.6132 | 2.6259 | 1.4372 | 2.6248 | 2.6643 | 2.581 | 2.6908 | 2.6794 | 2.6791 | 2.7177 | 2.7098 | 2.6808 | 2.7533 | 2.7357 | 2.7419 | 2.7203 | 2.6908 | 2.7022 | 2.7778 | 2.7329 | 2.7591 | 2.7547 | 2.7426 | 2.7678 | 2.7723 | 2.737 | 2.759 | 2.8085 | 2.8054 | 2.7405 | 2.8144 | 2.6767 | 2.7723 | 2.7488 | 2.7792 | 2.7736 | 2.8006 | 2.7547 | 2.7902 | 2.8333 | 2.8182 | 2.7727 | 2.7553 | 2.765 | 2.7833 | 2.7916 | 2.7947 | 2.7778 | 2.8213 | 2.7971 | 2.8301 | 2.8026 | 2.7839 | 2.8155 | 2.7888 | 2.8454 | 2.7757 | 2.7761 | 2.8019 | 2.7164 | 2.717 | 2.7795 | 2.7805 | 2.7816 | 2.8002 | 2.8216 | 2.7927 | 2.8233 | 2.8038 | 2.7268 | 2.7755 | 2.7411 | 2.7502 | 2.7336 | 2.7351 | 2.7324 | 2.7589 | 2.7819 | 2.7566 | 2.7789 | 2.7902 | 2.7952 | 2.7798 | 2.802 | 2.7605 | 2.7865 | 2.7834 | 2.7899 | 2.7623 | 2.7778 | 2.768 | 2.7838 | 2.7834 | 2.7664 | 2.7816 | 2.7517 | 2.7543 | 2.7544 | 2.7421 | 2.7726 | 2.7537 | 2.8262 | 2.8183 | 2.7926 | 2.8083 | 2.863 | 2.7777 | 2.8322 | 2.8662 | 2.8479 | 2.7815 | 2.8193 | 2.8216 | 2.7947 | 2.7122 | 2.8035 | 2.8281 | 2.8281 | 2.7284 | 2.8423 | 2.8305 | 2.7737 | 2.7661 | 2.8749 | 2.8152 | 2.7504 | 2.7627 | 2.8013 | 2.8641 | 2.7044 | 2.6898 | 2.7637 | 2.7594 | 2.7524 | 2.7147 | 2.794 | 2.7342 | 2.7838 | 2.7606 | 2.7645 | 2.7732 | 2.6553 | 2.7166 | 2.6523 | 2.7166 | 2.7955 | 2.8061 | 2.7677 | 2.7271 | 2.7578 | 2.6987 | 2.7559 | 2.7353 | 2.7301 | 2.7297 | 2.7278 | 2.776 | 2.7174 | 2.7241 | 2.7618 | 2.7244 | 2.6635 | 2.7135 | 2.7141 | 2.7312 | 2.7482 | 2.7493 | 2.7425 | 2.7758 | 2.7879 | 2.7606 | 2.7915 | 2.7807 | 2.6987 | 2.7225 | 2.7318 | 2.7325 | 2.8083 | 2.7765 | 2.7486 | 2.8195 | 2.7751 | 2.6194 | 2.6251 | 2.4841 | 2.489 | 2.5809 | 2.579 | 2.6432 | 2.6149 | 2.5873 | 2.6784 | 2.6536 | 2.6425 | 2.6712 | 2.6845 | 2.6298 | 2.625 | 2.6385 | 2.6549 | 2.6663 | 2.6739 | 2.6822 | 2.5756 | 2.6754 | 2.6473 | 2.722 | 2.6959 | 2.6591 | 2.6773 | 2.681 | 2.6964 | 2.6933 | 2.5969 | 2.5486 | 2.6218 | 2.5944 | 2.5847 | 2.5839 | 2.6258 | 2.5737 | 2.6531 | 2.6028 | 2.5491 | 2.571 | 2.646 | 2.5977 | 2.566 | 2.5753 | 2.5888 | 2.5249 | 2.6542 | 2.5754 | 2.564 | 2.6476 | 2.6578 | 2.6413 | 2.6558 | 2.5596 | 2.5992 | 2.6116 | 2.5054 | 2.582 | 2.4688 | 2.5824 | 2.5865 | 2.6123 | 2.5645 | 2.5989 | 2.6452 | 2.5944 | 2.5651 | 2.5859 | 2.6162 | 2.5681 | 2.5895 | 2.5974 | 2.5938 | 2.6035 | 2.5918 | 2.5781 | 2.5514 | 2.5835 | 2.5667 | 2.6103 | 2.5911 | 2.6032 | 2.6032 | 2.5981 | 2.6838
Formulas:
Date = [Date, row above]+1

## Inv_SY
| 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 130.68 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 125.4 | 132 | 132 | 132 | 132 | 132 | 132 | 125.4 | 132 | 132 | 132 | 125.4 | 132 | 138.16 | 144.24 | 149.2 | 136.4 | 136.8 | 143.3 | 140.16 | 136.8 | 125.4 | 137.9 | 125.4 | 125.4 | 142.9 | 132 | 125.4 | 144.9 | 132 | 138.6 | 125.4 | 125.4 | 132 | 125.6 | 148.8 | 163.6 | 136.4 | 144.8 | 132 | 142.6 | 125.2 | 143.8 | 148.8 | 289.8 | 289.8 | 288.9 | 289.8 | 289.8 | 289.35 | 289.8 | 289.8 | 289.8 | 289.8 | 287.55 | 289.8 | 277.2 | 277.2 | 289.8 | 289.8 | 289.8 | 289.8 | 302.4 | 289.8 | 277.2 | 289.8 | 277.2 | 277.2 | 289.35 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 315 | 289.8 | 289.8 | 277.2 | 277.2 | 289.8 | 288.45 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 264.6 | 277.2 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 277.2 | 277.2 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 277.2 | 289.8 | 315 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 277.2 | 302.4 | 277.2 | 252 | 289.8 | 264.6 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 289.8 | 302.4 | 289.8 | 277.2 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 252 | 226.8 | 277.2 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 252 | 252 | 252 | 293.02 | 278.04 | 254.8 | 292.74 | 293.02 | 290.5 | 305.76 | 293.02 | 318.5 | 293.02 | 280.28 | 280.28 | 267.54 | 293.02 | 278.74 | 305.76 | 254.8 | 254.8 | 279.72 | 216.58 | 254.8 | 305.76 | 304.36 | 304.36 | 304.92 | 305.48 | 304.92 | 329.28 | 330.26 | 280.28 | 280.28 | 254.8 | 254.8 | 254.8 | 267.54 | 254.8 | 267.54 | 254.8 | 254.8 | 254.8 | 254.8 | 267.54 | 267.54 | 267.54 | 267.54 | 254.8 | 254.8 | 254.8 | 267.54 | 254.8 | 267.54 | 254.8 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 280.28 | 292.88 | 293.02 | 279.72 | 292.88 | 305.76 | 292.33 | 292.47 | 280.28 | 293.02 | 293.02 | 280.28 | 304.64 | 305.48 | 278.6 | 305.48 | 305.76 | 229.32 | 229.32 | 293.02 | 242.06 | 280.28 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 264.6 | 289.8 | 264.6 | 264.6 | 252 | 252 | 252 | 262.8 | 262.8 | 263.7 | 263.7 | 263.7 | 288.9 | 263.7 | 263.7 | 263.7 | 263.7 | 238.5 | 263.7 | 264.6 | 252 | 252 | 254.8 | 293.02 | 252 | 267.54 | 267.54 | 267.54 | 252 | 242.06 | 267.54 | 280.28 | 254.8 | 254.8 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 279.37 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 267.54 | 254.8 | 254.8 | 267.54 | 242.06 | 254.8 | 254.8 | 280.28 | 267.54 | 267.54 | 254.8 | 280.28 | 267.54 | 280.28 | 254.8 | 267.54 | 254.8 | 254.8 | 242.06 | 254.8 | 254.8 | 254.8
Date | BLK1_INV1 | BLK1_INV2 | BLK1_INV3 | BLK1_INV4 | BLK1_INV5 | BLK1_INV6 | BLK1_INV7 | BLK1_INV8 | BLK1_INV9 | BLK1_INV10 | BLK1_INV11 | BLK1_INV12 | BLK1_INV13 | BLK1_INV14 | BLK1_INV15 | BLK1_INV16 | BLK1_INV17 | BLK1_INV18 | BLK1_INV19 | BLK1_INV20 | BLK1_INV21 | BLK1_INV22 | BLK1_INV23 | BLK1_INV24 | BLK1_INV25 | BLK1_INV26 | BLK1_INV27 | BLK1_INV28 | BLK1_INV29 | BLK1_INV30 | BLK1_INV31 | BLK1_INV32 | BLK1_INV33 | BLK1_INV34 | BLK1_INV35 | BLK1_INV36 | BLK1_INV37 | BLK1_INV38 | BLK1_INV39 | BLK1_INV40 | BLK1_INV41 | BLK1_INV42 | BLK1_INV43 | BLK1_INV44 | BLK1_INV45 | BLK1_INV46 | BLK1_INV47 | BLK1_INV48 | BLK1_INV49 | BLK1_INV50 | BLK1_INV51 | BLK1_INV52 | BLK1_INV53 | BLK1_INV54 | BLK1_INV55 | BLK1_INV56 | BLK1_INV57 | BLK1_INV58 | BLK1_INV59 | BLK1_INV60 | BLK1_INV61 | BLK1_INV62 | BLK1_INV63 | BLK2_INV1 | BLK2_INV2 | BLK2_INV3 | BLK2_INV4 | BLK2_INV5 | BLK2_INV6 | BLK2_INV7 | BLK2_INV8 | BLK2_INV9 | BLK2_INV10 | BLK2_INV11 | BLK2_INV12 | BLK2_INV13 | BLK2_INV14 | BLK2_INV15 | BLK2_INV16 | BLK2_INV17 | BLK2_INV18 | BLK2_INV19 | BLK2_INV20 | BLK2_INV21 | BLK2_INV22 | BLK2_INV23 | BLK2_INV24 | BLK2_INV25 | BLK2_INV26 | BLK2_INV27 | BLK2_INV28 | BLK3_INV1 | BLK3_INV2 | BLK3_INV3 | BLK3_INV4 | BLK3_INV5 | BLK3_INV6 | BLK3_INV7 | BLK3_INV8 | BLK3_INV9 | BLK3_INV10 | BLK3_INV11 | BLK3_INV12 | BLK3_INV13 | BLK3_INV14 | BLK3_INV15 | BLK3_INV16 | BLK3_INV17 | BLK3_INV18 | BLK3_INV19 | BLK3_INV20 | BLK3_INV21 | BLK3_INV22 | BLK3_INV23 | BLK4_INV1 | BLK4_INV2 | BLK4_INV3 | BLK4_INV4 | BLK4_INV5 | BLK4_INV6 | BLK4_INV7 | BLK4_INV8 | BLK4_INV9 | BLK4_INV10 | BLK4_INV11 | BLK4_INV12 | BLK4_INV13 | BLK4_INV14 | BLK4_INV15 | BLK4_INV16 | BLK4_INV17 | BLK4_INV18 | BLK4_INV19 | BLK4_INV20 | BLK4_INV21 | BLK4_INV22 | BLK4_INV23 | BLK5_INV1 | BLK5_INV2 | BLK5_INV3 | BLK5_INV4 | BLK5_INV5 | BLK5_INV6 | BLK5_INV7 | BLK5_INV8 | BLK5_INV9 | BLK5_INV10 | BLK5_INV11 | BLK5_INV12 | BLK5_INV13 | BLK5_INV14 | BLK5_INV15 | BLK5_INV16 | BLK5_INV17 | BLK5_INV18 | BLK5_INV19 | BLK5_INV20 | BLK5_INV21 | BLK5_INV22 | BLK5_INV23 | BLK5_INV24 | BLK5_INV25 | BLK5_INV26 | BLK5_INV27 | BLK5_INV28 | BLK5_INV29 | BLK6_INV1 | BLK6_INV2 | BLK6_INV3 | BLK6_INV4 | BLK6_INV5 | BLK6_INV6 | BLK6_INV7 | BLK6_INV8 | BLK6_INV9 | BLK6_INV10 | BLK6_INV11 | BLK6_INV12 | BLK6_INV13 | BLK6_INV14 | BLK6_INV15 | BLK6_INV16 | BLK6_INV17 | BLK6_INV18 | BLK6_INV19 | BLK6_INV20 | BLK6_INV21 | BLK6_INV22 | BLK6_INV23 | BLK6_INV24 | BLK6_INV25 | BLK6_INV26 | BLK6_INV27 | BLK6_INV28 | BLK6_INV29 | BLK6_INV30 | BLK6_INV31 | BLK7_INV1 | BLK7_INV2 | BLK7_INV3 | BLK7_INV4 | BLK7_INV5 | BLK7_INV6 | BLK7_INV7 | BLK7_INV8 | BLK7_INV9 | BLK7_INV10 | BLK7_INV11 | BLK7_INV12 | BLK7_INV13 | BLK7_INV14 | BLK7_INV15 | BLK7_INV16 | BLK7_INV17 | BLK7_INV18 | BLK7_INV19 | BLK7_INV20 | BLK7_INV21 | BLK7_INV22 | BLK7_INV23 | BLK7_INV24 | BLK7_INV25 | BLK7_INV26 | BLK7_INV27 | BLK7_INV28 | BLK7_INV29 | BLK8_INV1 | BLK8_INV2 | BLK8_INV3 | BLK8_INV4 | BLK8_INV5 | BLK8_INV6 | BLK8_INV7 | BLK8_INV8 | BLK8_INV9 | BLK8_INV10 | BLK8_INV11 | BLK8_INV12 | BLK8_INV13 | BLK8_INV14 | BLK8_INV15 | BLK8_INV16 | BLK8_INV17 | BLK8_INV18 | BLK8_INV19 | BLK8_INV20 | BLK8_INV21 | BLK8_INV22 | BLK8_INV23 | BLK8_INV24 | BLK8_INV25 | BLK8_INV26 | BLK8_INV27 | BLK8_INV28 | BLK8_INV29 | BLK8_INV30 | BLK8_INV31 | BLK9_INV1 | BLK9_INV2 | BLK9_INV3 | BLK9_INV4 | BLK9_INV5 | BLK9_INV6 | BLK9_INV7 | BLK9_INV8 | BLK9_INV9 | BLK9_INV10 | BLK9_INV11 | BLK9_INV12 | BLK9_INV13 | BLK9_INV14 | BLK9_INV15 | BLK9_INV16 | BLK9_INV17 | BLK9_INV18 | BLK9_INV19 | BLK9_INV20 | BLK9_INV21 | BLK9_INV22 | BLK10_INV1 | BLK10_INV2 | BLK10_INV3 | BLK10_INV4 | BLK10_INV5 | BLK10_INV6 | BLK10_INV7 | BLK10_INV8 | BLK10_INV9 | BLK10_INV10 | BLK10_INV11 | BLK10_INV12 | BLK10_INV13 | BLK10_INV14 | BLK10_INV15 | BLK10_INV16 | BLK10_INV17 | BLK10_INV18 | BLK10_INV19 | BLK10_INV20 | BLK10_INV21 | BLK10_INV22 | BLK10_INV23 | BLK10_INV24 | BLK10_INV25 | BLK10_INV26 | BLK10_INV27 | BLK10_INV28 | BLK10_INV29 | BLK10_INV30 | BLK10_INV31 | BLK11_INV1 | BLK11_INV2 | BLK11_INV3 | BLK11_INV4 | BLK11_INV5 | BLK11_INV6 | BLK11_INV7 | BLK11_INV8 | BLK11_INV9 | BLK11_INV10 | BLK11_INV11 | BLK11_INV12 | BLK11_INV13 | BLK11_INV14 | BLK11_INV15 | BLK11_INV16 | BLK11_INV17 | BLK11_INV18 | BLK11_INV19 | BLK11_INV20 | BLK11_INV21 | BLK11_INV22 | BLK11_INV23 | BLK11_INV24 | BLK11_INV25 | BLK12_INV1 | BLK12_INV2 | BLK12_INV3 | BLK12_INV4 | BLK12_INV5 | BLK12_INV6 | BLK12_INV7 | BLK12_INV8 | BLK12_INV9 | BLK12_INV10 | BLK12_INV11 | BLK12_INV12 | BLK12_INV13 | BLK12_INV14 | BLK12_INV15 | BLK12_INV16 | BLK12_INV17 | BLK12_INV18 | BLK12_INV19 | BLK12_INV20 | BLK12_INV21 | BLK12_INV22 | BLK12_INV23 | BLK12_INV24 | BLK12_INV25 | BLK12_INV26 | BLK12_INV27 | BLK12_INV28 | BLK12_INV29 | BLK12_INV30 | BLK12_INV31
2025-03-29 | -11.96% | -14.91% | -9.329% | -9.153% | -9.504% | -14.67% | -6.652% | -11.17% | -7.879% | -7.484% | -7.835% | -8.011% | -7.572% | -7.484% | -6.254% | -6.869% | -8.533% | -7.054% | -7.528% | -6.561% | -3.75% | -4.409% | -4.013% | -4.628% | -3.574% | -3.662% | -3.179% | -3.794% | -3.091% | -2.739% | -3.881% | -3.794% | -9.373% | -11.17% | -10.2% | -8.58% | -7.146% | -7.516% | -8.758% | -7.978% | -10.82% | -6.732% | -4.936% | -5.219% | -4.668% | -2.445% | -2.253% | -2.692% | -5.186% | -3.408% | -3.283% | -5.891% | -6.994% | -6.356% | -7.933% | -5.329% | -5.809% | -10.01% | -10.29% | -10.72% | -7.835% | -7.248% | -7.407% | 2.288% | 2.589% | 0.3389% | 0.9077% | 2.589% | 0.6839% | -1.213% | 0.8277% | 2.869% | -1.373% | -0.4201% | -1.774% | -0.8649% | -3.229% | 1.348% | 1.988% | 2.128% | 0.8077% | 2.897% | 1.488% | 3.152% | 3.029% | 1.959% | 1.917% | 1.546% | 1.948% | 0.1274% | 0.5075% | -6.396% | -2.154% | -1.553% | 0.1674% | 1.288% | 0.4379% | 1.208% | 0.4475% | -0.7185% | -0.5093% | 0.2274% | -1.836% | 1.788% | 0.8277% | -2.154% | 2.268% | -0.0127% | -0.3128% | 2.649% | 2.849% | 3.589% | 1.423% | 2.106% | 1.208% | 4.77% | 2.288% | 2.989% | 3.409% | 3.109% | 2.989% | 3.069% | 2.796% | 3.172% | 4.009% | 3.429% | 3.489% | 2.989% | 2.168% | 1.148% | 1.268% | 3.669% | 1.668% | 3.089% | 0.5276% | 3.369% | 3.967% | 5.37% | 3.696% | 1.248% | 1.128% | 3.989% | 4.169% | 2.889% | 3.989% | 5.01% | 2.068% | 3.235% | 1.401% | 0.6622% | 1.685% | 1.548% | 4.623% | 2.468% | 4.629% | 2.088% | 3.629% | 3.189% | 3.749% | 1.688% | 1.968% | 1.888% | 1.308% | 5.486% | 7.591% | 1.666% | -1.141% | 0.7877% | -2.193% | -2.061% | -1.031% | -1.009% | -0.856% | 2.037% | 2.431% | -0.1328% | 0.3932% | 1.094% | 2.366% | -3.032% | -0.5418% | -1.262% | 1.138% | -0.8121% | 0.9192% | 2.672% | 0.3055% | 2.453% | 0.2836% | 1.094% | 0.06448% | 2.103% | -0.06701% | 0.5466% | 0.7877% | 0.2124% | 1.524% | -0.498% | 2.152% | 1.91% | 1.36% | 1.699% | 2.381% | 0.3439% | 3.163% | 4.323% | 4.39% | 18.55% | 3.301% | 0.3087% | 1.046% | 19.2% | 3.094% | 30.4% | 2.525% | 2.201% | 3.202% | 1.172% | -0.2251% | -1.214% | 1.396% | -0.6158% | -2.43% | -2.917% | 0.3967% | -1.06% | -3.527% | -0.5888% | -0.5019% | -0.7523% | -1.39% | -2.076% | 0.4766% | -1.295% | -1.572% | -0.1606% | -0.5247% | -0.2744% | -1.035% | -1.577% | -1.664% | -1.317% | 1.137% | 1.091% | -0.3654% | -0.6883% | -0.9116% | -1.729% | -0.5702% | -0.9484% | -0.9484% | -1.1% | 1.522% | 0.222% | -0.9701% | -0.6667% | -0.2765% | -0.05092% | -0.07424% | 2.233% | 2.243% | 3.252% | 3.606% | 3.307% | 3.238% | 3.59% | 2.589% | 1.58% | 2.618% | 4.71% | -0.7221% | 0.9472% | 3.663% | 2.487% | 3.65% | 4.004% | 3.025% | 4.711% | 2.659% | -0.834% | -1.689% | -2.193% | -2.916% | -0.4396% | -3.223% | -0.9875% | -3.354% | -2.215% | -0.7026% | -1.473% | -2.039% | -1.272% | -0.06373% | -2.457% | -3.285% | -2.582% | -0.7065% | -1.771% | -1.683% | -1.375% | 147.6% | -1.815% | -2.717% | -0.6495% | -1.485% | -2.722% | -1.441% | -1.053% | -0.708% | -0.662% | 1.956% | -0.3001% | 0.5346% | -0.3416% | -0.775% | -1.707% | -0.8001% | -3.171% | -1.057% | -1.189% | -2.618% | -2.186% | 1.176% | -0.1898% | -0.9268% | -0.9051% | -0.71% | -0.3416% | 1.375% | -2.027% | -2.277% | 1.387% | 1.888% | -2.277% | 2.752% | -1.534% | 1.587% | 0.4604% | 1.002% | 1.587% | 0.7638% | -0.5366% | 0.6555% | 2.021% | -0.4283% | 0.9773% | 6.667% | 0.8289% | -1.925% | -0.3199% | 6.667% | 0.7766% | -1.707% | -1.404% | 1.751% | -0.8785% | 1.371% | 1.48% | -1.344% | 0.2653% | -1.663% | 0.1808% | 1.285% | -1.663% | 2.07% | 1.478%
2025-03-30 | -10.02% | -13.28% | -7.731% | -7.561% | -7.806% | -13.32% | -5.782% | -9.583% | -6.672% | -6.502% | -6.218% | -6.426% | -6.559% | -6.37% | -5.273% | -5.5% | -7.192% | -6.516% | -7.712% | -6.067% | -3.553% | -4.46% | -3.383% | -3.629% | -3.855% | -3.874% | -3.799% | -4.309% | -3.666% | -3.269% | -4.271% | -4.025% | -8.695% | -9.819% | -8.725% | -7.471% | -6.038% | -5.68% | -7.107% | -6.814% | -9.054% | -6.168% | -4.255% | -4.839% | -4.31% | -2.048% | -2.329% | -3.274% | -4.672% | -3.845% | -3.755% | -5.942% | -6.669% | -6.491% | -8.081% | -6.003% | -6.074% | -10.16% | -10.33% | -10.69% | -6.521% | -7.718% | -6.829% | 2.464% | 0.3372% | 0.097% | 1.345% | 2.886% | 1.218% | -0.9199% | 1.164% | 3.179% | -0.7305% | -0.1099% | -1.006% | -0.08901% | -2.249% | 1.172% | 1.62% | 1.637% | -1.945% | 2.659% | 1.345% | 3.134% | 2.998% | 2.161% | 1.972% | 1.545% | 1.603% | 0.3716% | 0.7591% | -3.262% | -0.9285% | -0.455% | 1.181% | 1.861% | 1.293% | 1.19% | 1.31% | 0.3251% | 0.4781% | 0.673% | -1.486% | 2.3% | 1.723% | -2.194% | 2.783% | 0.983% | 0.7591% | 2.998% | 3.187% | 4.177% | 1.811% | 2.224% | 2.18% | 5.047% | 3.11% | 3.583% | 4.444% | 3.971% | 2.86% | 2.851% | 2.756% | 3.143% | 3.334% | 2.834% | 0.0875% | 2.412% | 2.231% | 1.017% | 1.078% | 3.239% | 1.474% | 2.74% | 0.5094% | 3.23% | 3.224% | 4.858% | 3.4% | 1.198% | 0.7591% | 3.506% | 3.756% | 2.24% | 1.155% | 4.496% | 2.033% | 3.035% | 1.454% | 0.7842% | 1.782% | 1.482% | 4.452% | 2.516% | 4.272% | 2.042% | 3.489% | 3.006% | 3.626% | 1.551% | 1.784% | 1.784% | 0.8538% | 5.06% | 6.743% | 1.693% | 0.3306% | 1.792% | -0.5747% | -0.3766% | 0.6607% | 0.6136% | 1.085% | 3.565% | 3.669% | 0.7079% | 1.783% | 2.038% | 3.075% | -1.416% | 1.198% | 0.3971% | 2.915% | 1.953% | 1.811% | 3.462% | 1.651% | 3.735% | 1.67% | 2.754% | 1.311% | 1.849% | 1.236% | 2.17% | 3.07% | 2.446% | 2.693% | -0.6036% | 1.691% | 1.281% | 1.06% | 1.253% | 1.891% | 0.4371% | 2.556% | 2.977% | 3.714% | 0.5224% | 2.508% | -0.5574% | -0.1608% | 3.074% | 1.816% | 1.594% | 2.084% | 1.535% | 2.426% | 1.076% | 0.1596% | -1.2% | -1.192% | -0.8574% | -2.534% | -2.92% | 0.01506% | -3.939% | -1.953% | 0.6382% | 0.5171% | 0.615% | -0.188% | -0.3895% | 1.966% | 0.03022% | 1.536% | 1.379% | 1.026% | 1.398% | 0.7764% | 0.282% | 0.09551% | 0.2727% | 0.6542% | 1.056% | -0.3741% | 0.7857% | 0.5563% | -0.01642% | 1.026% | 0.3753% | 0.7018% | 0.4966% | 1.532% | 1.28% | 1.019% | 0.8137% | 1.429% | -0.09188% | -0.2068% | 1.951% | 2.008% | 3.278% | 3.351% | 2.994% | 3.039% | 3.46% | 2.59% | 1.551% | 2.543% | 4.279% | 0.619% | 0.1792% | 2.996% | 1.816% | 3.166% | 3.623% | 2.837% | 4.107% | 2.267% | 0.5664% | 0.1798% | 0.09488% | -0.603% | -3.121% | -1.584% | 0.9059% | -1.159% | -2.48% | 1.179% | 0.4405% | -0.04657% | 0.6607% | 1.664% | -0.4752% | -0.4653% | -0.226% | 0.8374% | 0.3324% | 0.569% | 0.6163% | 6.558% | -0.1123% | -0.453% | 1.099% | 0.2567% | -0.1357% | 0.1337% | 0.6136% | 0.8715% | 1.099% | 2.446% | 0.4438% | 2.347% | 1.215% | 1.038% | 0.2168% | 0.9507% | -0.9138% | -0.1563% | -1.223% | -0.5602% | -0.5602% | 1.168% | -0.1097% | -0.6786% | -0.8558% | -0.7532% | -0.548% | 1.493% | -1.363% | -2.205% | 1.447% | 1.389% | 1.389% | 2.319% | -1.005% | 2.315% | 0.8137% | 1.756% | 1.112% | 1.504% | 0.5712% | 1.7% | 2.894% | 0.9349% | 2.192% | 5.982% | 1.746% | -0.7179% | 1.212% | 2.77% | 1.466% | -0.5201% | -0.06305% | 2.73% | 0.08618% | 2.147% | 2.152% | -0.1586% | 1.392% | 0.03721% | 0.5073% | 2.581% | 2.26% | 3.24% | 2.809%
2025-03-31 | -9.923% | -13.4% | -7.819% | -7.665% | -7.742% | -13.11% | -5.99% | -9.72% | -6.666% | -6.551% | -6.397% | -6.493% | -6.57% | -6.436% | -5.341% | -5.61% | -7.314% | -6.667% | -7.588% | -6.205% | -3.881% | -4.669% | -3.516% | -4.208% | -4.016% | -3.996% | -4.016% | -4.515% | -3.9% | -3.535% | -4.534% | -4.304% | -8.702% | -9.741% | -8.75% | -7.456% | -6.121% | -5.677% | -6.935% | -6.869% | -9.202% | -6.193% | -4.136% | -4.807% | -4.362% | -2.065% | -2.42% | -3.334% | -4.453% | -4.065% | -4.007% | -6.136% | -6.921% | -6.699% | -8.368% | -5.748% | -6.299% | -10.46% | -10.63% | -10.99% | -6.878% | -7.644% | -6.944% | 2.514% | 0.3093% | 0.1391% | 1.28% | 2.882% | 1.254% | -0.8806% | 1.149% | 1.28% | -6.349% | 1.888% | -0.8981% | -0.02475% | -2.092% | 1.009% | 1.429% | 1.508% | 1.018% | 2.527% | 1.342% | 3.03% | 2.952% | 2.299% | 1.914% | 1.526% | 1.578% | 0.3268% | 0.7118% | -2.464% | -0.9593% | -0.4956% | 0.9742% | 1.727% | 1.235% | 1.14% | 1.044% | 0.2314% | 0.4692% | 0.6068% | -1.463% | 2.182% | -0.8543% | 2.059% | 2.733% | 1.062% | 0.633% | 2.943% | 3.17% | 4.159% | 1.804% | 2.353% | 2.068% | 4.78% | 2.995% | 3.363% | 4.29% | 3.634% | 2.689% | 2.715% | 2.555% | 2.93% | 3.24% | 2.672% | 2.917% | 2.147% | 1.998% | 0.8255% | 0.9655% | 2.96% | 1.315% | 2.532% | 0.3793% | 3.1% | 3.067% | 5.568% | 4.036% | 1.718% | 1.21% | 4.22% | 7.186% | 2.575% | 1.473% | 4.719% | 2.287% | 3.305% | 1.739% | 0.9631% | 1.803% | 1.744% | 4.64% | 2.698% | 4.176% | 2.033% | 3.442% | 2.882% | 3.459% | 1.569% | 1.744% | 1.788% | 0.8605% | 4.95% | 6.644% | 1.722% | 1.488% | 2.934% | 0.5772% | 0.8359% | 1.756% | 1.794% | 2.072% | 4.525% | 4.544% | 1.995% | 2.887% | 3.117% | 4.027% | -0.4409% | 2.427% | 1.128% | 3.768% | 2.81% | 2.925% | 4.563% | 2.465% | 4.41% | 2.321% | 3.49% | 1.919% | 2.379% | 1.44% | 2.503% | 3.513% | 2.728% | 3.272% | 2.132% | 2.518% | 14.14% | 2.03% | 2.27% | 3.018% | 1.459% | 3.577% | 4.016% | 2.132% | 2.197% | 2.197% | 0.6661% | 1.154% | 2.761% | 2.487% | 2.356% | 2.674% | 2.401% | 3.155% | 2.086% | 1.061% | -0.09905% | 1.367% | 0.1665% | -1.669% | -1.987% | 0.9184% | -0.4098% | -2.164% | 0.5502% | 0.3756% | 0.913% | 0.1069% | -0.3859% | 1.809% | -0.03523% | 1.54% | 1.56% | 1.032% | 1.261% | 0.7419% | 0.268% | 0.2112% | 0.4007% | 0.8234% | 1.301% | 0.04722% | 1.311% | 0.7438% | 0.268% | 1.281% | 0.8746% | 0.8746% | 0.8935% | 1.974% | 2.23% | 1.367% | 1.225% | 1.936% | -0.5625% | -0.5378% | 1.552% | 1.604% | 2.787% | 2.926% | 2.737% | 2.558% | 3.092% | 2.287% | 1.258% | 2.233% | 4.07% | 0.4975% | 0.02802% | 2.672% | 1.533% | 2.96% | 3.313% | 2.443% | 3.815% | 1.952% | 0.2035% | -0.5248% | -0.429% | -1.138% | 0.2801% | -1.78% | 0.261% | -1.742% | -2.959% | 0.7976% | 0.02059% | -0.3906% | 0.2035% | 1.249% | -0.9038% | -0.783% | -0.5092% | 0.8416% | 0.03588% | 0.2666% | 0.3532% | -2.915% | -0.4545% | -0.7622% | 0.4686% | -0.1276% | -0.6101% | 0.007033% | 0.3472% | 0.686% | 0.6658% | 1.619% | -0.1959% | 1.461% | 0.3723% | 0.268% | -0.4901% | 0.4042% | -1.569% | -1.514% | -1.947% | -1.426% | -1.386% | 0.3818% | -0.945% | -1.4% | -1.533% | -1.788% | -1.571% | 0.6962% | -2.082% | -2.978% | 0.5448% | 0.4055% | 0.5448% | 1.401% | -2.386% | 1.017% | 0.05954% | 0.4102% | 0.1069% | 0.2396% | -0.6986% | 0.4481% | 1.699% | -0.2058% | 1.102% | 5.471% | 0.6661% | -1.548% | 0.08703% | 1.629% | 0.514% | -1.902% | -1.267% | 1.779% | -0.9334% | 1.434% | 0.6859% | -1.177% | 0.3154% | 5.471% | -0.6792% | 1.437% | 1.251% | 2.097% | 1.56%
2025-04-01 | -9.621% | -12.99% | -7.402% | -7.248% | -7.44% | -12.75% | -5.512% | -9.322% | -6.308% | -6.193% | -5.982% | -6.097% | -6.154% | -6.097% | -4.887% | -5.214% | -6.893% | -6.226% | -7.114% | -5.751% | -3.467% | -4.273% | -3.621% | -3.39% | -3.697% | -3.697% | -3.544% | -4.043% | -3.563% | -3.121% | -4.1% | -3.812% | -8.458% | -9.459% | -8.428% | -7.014% | -5.64% | -5.357% | -6.673% | -6.408% | -8.611% | -5.625% | -3.604% | -4.354% | -3.872% | -1.546% | -1.859% | -2.821% | -4.348% | -3.547% | -3.683% | -5.594% | -6.364% | -6.151% | -7.748% | -5.209% | -5.733% | -9.879% | -9.982% | -10.38% | -6.346% | -7.202% | -6.042% | 2.837% | 0.7478% | 0.4301% | 1.753% | 3.353% | 1.719% | -0.3889% | 1.727% | 3.729% | -0.1528% | 0.417% | -0.3976% | 0.4553% | -1.629% | 1.272% | 1.823% | 1.954% | 1.491% | 2.876% | 1.517% | 3.426% | 3.196% | 2.384% | 2.21% | 1.789% | 1.867% | 1.867% | -1.071% | -5.233% | -1.01% | -0.4151% | 1.211% | 1.841% | 1.303% | 1.194% | 1.237% | 0.373% | 0.5558% | 0.7827% | -1.477% | 2.4% | 3.554% | 2.173% | 2.977% | 1.36% | 0.8877% | 3.31% | 3.476% | 4.35% | 1.993% | 2.548% | 2.488% | 5.452% | 3.379% | 3.948% | 4.682% | 4.184% | 3.344% | 3.388% | 3.225% | 3.481% | 3.913% | 3.397% | 3.685% | 2.934% | 2.724% | 1.552% | 1.683% | 3.694% | 2.068% | 3.301% | 1.063% | 3.729% | 3.792% | 1.552% | -4.4% | 1.911% | 1.517% | 2.934% | 4.49% | 2.899% | 1.867% | 5.084% | 2.741% | 3.691% | 2.172% | 1.397% | 2.387% | 2.208% | 5.21% | 3.275% | 4.918% | 2.802% | 4.228% | 3.677% | 4.254% | 2.147% | 2.488% | 2.322% | 1.334% | 5.649% | 7.349% | 2.311% | 0.6233% | 2.117% | -0.1045% | 0.1828% | 1.112% | 1.16% | 1.523% | 4.013% | 4.004% | 1.418% | 2.146% | 2.452% | 3.448% | -0.9314% | 1.798% | 0.6015% | 3.218% | 2.251% | 2.471% | 4.042% | 1.964% | 3.975% | 1.849% | 3.113% | 1.533% | 2.041% | 1.313% | 2.194% | 3.181% | 2.497% | 2.789% | 0.1681% | 2.457% | 2.176% | 2.038% | 2.304% | 2.973% | 1.48% | 3.584% | 3.944% | 4.639% | 1.385% | 3.356% | 0.2941% | 0.6437% | 10.05% | 2.64% | 2.405% | 2.833% | 2.404% | 3.221% | 2.027% | 1.041% | 1.506% | 0.2821% | 1.211% | -0.08555% | -1.506% | -9.377% | 0.6421% | -2.158% | 0.5085% | 0.3069% | 0.824% | -0.001366% | -0.4162% | 1.928% | -0.008942% | 1.421% | 1.321% | 0.9135% | 1.172% | 0.7392% | 0.1426% | 0.1142% | 0.3509% | 0.5356% | 1.102% | -0.4389% | 0.8908% | 0.4958% | 0.04788% | 1.023% | 0.5309% | 0.6824% | 0.6445% | 1.611% | 1.743% | 1.118% | 0.9476% | 1.658% | -0.2509% | -0.2079% | 1.898% | 1.96% | 3.244% | 3.303% | 3.317% | 3.033% | 3.627% | 2.944% | 1.941% | 2.949% | 4.673% | 1.051% | 0.5143% | 3.357% | 2.243% | 2.944% | 3.309% | -18.57% | 25.08% | -9.626% | 0.06788% | -0.5929% | -0.6695% | -1.234% | -6.233% | -2.106% | 0.269% | -1.905% | -3.197% | 0.4509% | -0.1703% | -0.6982% | -0.09491% | 0.9388% | -1.494% | -1.354% | -0.8086% | 0.5508% | -0.2536% | 0.01545% | 0.15% | 8.201% | -0.4842% | -1.041% | 0.8514% | -0.1863% | -1.082% | -0.09985% | 0.1445% | 0.5768% | 0.6774% | 1.092% | -0.7831% | 1.09% | 0.2278% | -0.008942% | -0.8329% | -0.04656% | -2.034% | -1.572% | -2.357% | -1.632% | -1.821% | -0.8613% | -1.411% | -1.884% | -1.818% | -2.026% | -1.761% | 0.464% | -2.607% | -3.641% | 0.1478% | -0.2798% | 0.3367% | 0.9632% | -3.845% | 0.493% | -0.5772% | -0.08471% | -0.2646% | -0.5109% | -0.7666% | -0.07524% | 1.535% | -0.5109% | 0.9036% | 4.195% | 0.6729% | -1.479% | 0.008579% | 1.649% | -0.1786% | -2.31% | -1.43% | 1.5% | -0.9108% | 1.317% | 0.9424% | -1.344% | 0.2941% | -1.125% | -0.6776% | 1.472% | 1.351% | 2.057% | 1.719%
2025-04-02 | -8.297% | -11.63% | -7.572% | -7.62% | -7.86% | -11.94% | -5.609% | -9.566% | -6.611% | -6.467% | -6.515% | -6.803% | -6.779% | -6.443% | -5.578% | -5.914% | -7.335% | -6.299% | -6.827% | -5.89% | -3.56% | -4.256% | -3.656% | -3.824% | -3.391% | -3.56% | -3.199% | -3.68% | -3.031% | -2.815% | -3.728% | -3.656% | -8.076% | -9.333% | -8.726% | -7.563% | -6.299% | -6.273% | -7.452% | -7.184% | -10.82% | -6.757% | -4.505% | -5.39% | -4.463% | -2.241% | -2.519% | -3.195% | -4.935% | -4.082% | -3.648% | -6.076% | -6.848% | -6.52% | -8.077% | -5.989% | -6.178% | -10.26% | -10.3% | -10.77% | -7.236% | -7.761% | -6.973% | 1.994% | -0.1951% | 0.006091% | 0.6695% | 2.388% | 1.089% | -1.038% | 0.9321% | 2.946% | -0.8298% | 0.1006% | -0.9502% | 0.5546% | -1.493% | 0.6804% | 1.512% | 1.337% | -12.28% | 2.065% | 0.8993% | 2.488% | 2.431% | 1.619% | 1.516% | 1.133% | 1.271% | 0.05665% | 0.385% | -1.804% | -0.3264% | -1.246% | 1.162% | 1.972% | 1.667% | 1.359% | 0.6804% | -0.02891% | 0.3944% | 0.07854% | -1.872% | 2.016% | 5.693% | 2.005% | 2.399% | 1.348% | 0.6476% | 2.716% | 2.606% | 3.734% | 1.471% | 1.825% | 1.26% | 3.996% | 2.53% | 2.563% | 3.427% | 2.508% | 2.3% | 0.4944% | 1.367% | 2.202% | 2.749% | 2.234% | 2.311% | 2.147% | 0.9868% | 0.8884% | 0.5819% | 2.453% | 1.249% | 2.475% | 0.4287% | 2.683% | 3.85% | 3.931% | 2.714% | 1.775% | 0.385% | 2.924% | 3.241% | 1.775% | 0.6367% | 3.58% | 1.468% | 2.225% | 0.7958% | -0.01747% | 0.8063% | 1.042% | 3.773% | 2.147% | 3.613% | 1.37% | 2.628% | 2.705% | 3.296% | 0.9978% | 1.37% | 1.282% | 0.03476% | 4.613% | 6.24% | 0.8749% | -0.1706% | 1.939% | -0.638% | -0.662% | 0.8482% | 0.4887% | 1.244% | 3.629% | 3.917% | 1.256% | 2.083% | 2.622% | 2.838% | -1.119% | 1.352% | 0.9092% | 3.054% | 2.478% | 2.502% | 3.401% | 2.095% | 3.713% | 1.807% | 2.478% | 1.112% | 2.239% | 0.8482% | 2.059% | 2.845% | 2.002% | 3.135% | -1.508% | 2.658% | 9.531% | 0.8502% | 0.7538% | 1.366% | 0.6009% | -0.2095% | -1.78% | 3.113% | 0.1624% | -2.35% | -0.7223% | -0.3827% | 1.262% | 1.12% | 1.454% | 1.653% | 2.2% | 2.378% | 0.5145% | -0.7267% | -2.052% | -0.416% | -1.597% | -3.896% | -3.99% | -0.8253% | -2.33% | -2.316% | 0.468% | 0.4204% | 0.5573% | 0.408% | -0.4615% | 1.852% | -0.1296% | 1.167% | 1.391% | 1.03% | 1.192% | 0.6409% | 0.04821% | 0.1549% | 0.08378% | 1.005% | 1.03% | 0.009688% | 0.7832% | 0.5076% | -0.8053% | -98.88% | -99.36% | 0.7713% | 0.3683% | 1.826% | 1.554% | 0.7832% | 0.4987% | 1.245% | -0.573% | -0.5949% | 1.111% | 1.304% | 0.7478% | 3.443% | 2.521% | 2.657% | 3.138% | 2.226% | 1.349% | 2.256% | 3.573% | 0.05983% | -0.3947% | 1.897% | 0.9225% | 24.74% | 1.967% | -20.04% | 23.35% | -10.93% | -2.196% | -0.1226% | -0.1466% | -0.2545% | -2.268% | -0.8178% | 0.8362% | -0.674% | -1.801% | 1.639% | 0.8227% | 0.2489% | 0.9201% | 2.077% | 0.5546% | 0.1141% | 0.127% | 1.491% | 0.567% | 0.6151% | 1.024% | 35.43% | 0.06192% | -0.04632% | 1.192% | 0.6392% | 0.6215% | 0.6151% | 1.867% | 1.297% | 1.297% | 2.536% | 1.262% | 2.656% | 1.376% | 1.032% | 0.2497% | 1.36% | -0.4653% | -2.299% | -0.3015% | -0.3762% | -0.01521% | 2.146% | 0.7476% | 0.09563% | -0.3548% | -0.4022% | 0.143% | 2.021% | -0.6998% | -0.3762% | 1.18% | 2.86% | 2.437% | 2.549% | 0.2379% | 2.751% | 2.146% | 1.566% | 1.447% | 2.111% | 0.3209% | 2.111% | 2.775% | 0.6172% | 2.362% | 7.042% | 1.696% | -0.5963% | 1.553% | 3.196% | 2.595% | -0.03476% | 0.09563% | 3.146% | 0.5698% | 2.917% | 2.097% | 0.1093% | 1.601% | 0.2586% | 1.18% | 2.705% | 2.462% | 3.657% | 2.91%
2025-04-03 | -7.425% | -10.45% | -6.698% | -6.66% | -7.133% | -11.21% | -4.967% | -8.761% | -6.168% | -6.111% | -5.733% | -6.111% | -6.206% | -6.111% | -5.146% | -5.146% | -6.728% | -6.11% | -6.736% | -5.619% | -3.329% | -4.162% | -3.026% | -3.708% | -3.518% | -3.518% | -3.253% | -3.651% | -2.932% | -2.724% | -3.67% | -3.405% | -7.682% | -8.979% | -7.983% | -7.027% | -5.572% | -5.433% | -6.641% | -6.449% | -9.575% | -6.132% | -4.093% | -4.457% | -4.11% | -1.755% | -2.234% | -3.146% | -4.502% | -3.857% | -3.554% | -5.944% | -6.635% | -6.367% | -8.027% | -5.773% | -6.168% | -10.2% | -10.33% | -10.65% | -6.433% | -7.393% | -6.777% | 2.357% | 0.4518% | 0.3756% | 1.357% | 2.952% | 1.679% | 1.374% | 1.521% | 2.236% | -0.1947% | 0.3082% | -0.3499% | 1.089% | -1.228% | -0.6085% | 1.969% | 1.693% | -2.445% | 2.429% | 1.081% | 2.882% | 2.719% | 1.809% | 1.9% | 1.48% | 1.495% | 0.6156% | 0.9776% | -1.298% | 0.3742% | 0.9863% | 1.883% | 2.124% | 1.901% | 1.047% | 1.193% | 0.8452% | 0.7461% | 0.6846% | -1.711% | 2.486% | 6.279% | 2.193% | 2.995% | 2.003% | 1.667% | 3.305% | 3.184% | 4.124% | 1.984% | 2.188% | 1.685% | 4.46% | 0.3225% | 3.176% | 3.538% | 3.107% | 2.71% | 2.547% | 1.819% | 2.711% | 3.012% | 2.676% | 2.797% | 2.641% | 1.633% | 1.555% | 1.357% | 3.184% | 1.952% | 3.098% | 1.141% | 3.305% | 4.279% | 4.417% | 2.94% | 1.245% | 0.8914% | 3.193% | 1.719% | 2.141% | 1.435% | 4.098% | 2.116% | 2.873% | 1.487% | 0.6559% | 1.661% | 1.771% | 4.288% | 2.693% | 4.253% | 2.047% | 3.314% | 3.512% | 3.857% | 1.65% | 1.986% | 1.874% | 0.6242% | 4.998% | 6.452% | 1.584% | -0.6405% | 1.087% | -1.198% | -1.377% | -0.03626% | -0.1496% | 0.7662% | 2.957% | 3.278% | 0.5491% | 1.446% | 1.786% | 1.824% | -1.353% | 0.7631% | -0.02897% | 2.286% | 1.72% | 2.088% | 2.862% | 1.569% | 3.155% | 1.229% | 2.22% | 0.804% | 2.173% | 0.6152% | 1.701% | 2.494% | 1.79% | 2.236% | -4.258% | 1.897% | 1.142% | 1.483% | 1.275% | 1.74% | 1.14% | 2.596% | 1.102% | 3.363% | 0.2272% | -0.1739% | -0.4438% | -0.3537% | 0.5569% | 1.687% | 2.946% | 2.465% | 2.562% | 2.76% | 1.05% | -1.875% | -1.53% | 0.09505% | -1.096% | -2.799% | -3.268% | -0.25% | -1.832% | -2.313% | -0.1204% | -0.02501% | 0.1809% | -0.2799% | -0.7426% | 1.544% | -0.4998% | 0.5927% | 0.6711% | 0.475% | 0.6515% | 0.4993% | -0.1263% | -0.2477% | -0.2757% | -0.1427% | 0.2789% | -1.094% | -0.1076% | -0.2995% | -0.7519% | 0.2005% | -0.4251% | 0.1165% | -0.07029% | 0.9195% | 1.013% | 0.3872% | 0.1725% | 0.8074% | 0.4322% | 0.08633% | 1.897% | 2.116% | 3.558% | 4.09% | 1.292% | 0.9441% | 3.873% | 3.022% | 2.093% | 3.133% | 4.169% | 0.7339% | 0.04254% | 2.435% | 1.483% | 25.5% | 2.608% | -19.55% | 24.57% | -10.37% | 0.6057% | -0.2062% | -0.1496% | -0.2817% | -3.293% | -1.358% | 0.7946% | -0.8388% | -2.378% | 1.078% | 0.7018% | -0.1401% | 0.6529% | 1.472% | -0.2029% | -0.302% | -0.1025% | 0.8766% | 0.1723% | 0.1344% | 0.4091% | 6.679% | -0.2446% | -0.4624% | 1.11% | 0.1533% | 0.2088% | 0.3144% | 1.399% | 1.096% | 1.036% | 1.661% | -0.1235% | 1.8% | 0.7327% | 0.5273% | -0.229% | 0.5505% | -1.028% | -0.3131% | -1.243% | -0.8682% | -1.025% | 0.7327% | -0.6959% | -1.48% | -1.2% | -1.331% | -0.7426% | 1.358% | -1.78% | -1.594% | 1.387% | 1.504% | 0.2005% | 1.779% | -0.3411% | 2.441% | 1.246% | 1.769% | 0.9008% | 1.76% | 0.4993% | 1.928% | 2.376% | 0.7701% | 1.789% | 5.593% | 1.47% | -0.7283% | 1.22% | 2.603% | 1.484% | -0.145% | 0.2192% | 2.475% | 0.6016% | 2.339% | 1.832% | -0.3486% | 0.8074% | -0.1525% | 0.5142% | 2.357% | 2.21% | 2.867% | 2.593%
2025-04-04 | -6.577% | -9.977% | -6.034% | -6.08% | -6.127% | -9.936% | -4.144% | -7.972% | -4.927% | -4.927% | -5.042% | -5.25% | -5.25% | -5.158% | -4.973% | -4.027% | 0.6112% | -5.849% | -9.541% | -5.342% | -4.442% | -2.02% | -2.712% | -2.043% | -2.274% | -2.02% | -2.205% | -1.905% | -2.343% | -1.697% | -1.536% | -2.435% | -2.366% | -1.647% | -7.718% | -7.038% | -5.97% | -4.731% | -9.541% | -0.7488% | -10.28% | -14.55% | -8.029% | 2.088% | -3.766% | -3.97% | -11.05% | -7.761% | -9.74% | 2.133% | 15.56% | 1.274% | -3.873% | -9.251% | -9.504% | -3.74% | -9.214% | -4.263% | 12.93% | -9.975% | -13.9% | 3.118% | -8.909% | 3.328% | 1.079% | 1.446% | 1.877% | 3.706% | 2.625% | 0.3643% | 2.403% | 4.305% | 0.6375% | 1.626% | 0.5745% | 2.114% | 0.1035% | 1.783% | 2.729% | 2.655% | 2.729% | 3.222% | 2.077% | 3.707% | 3.632% | 2.905% | 2.63% | 2.467% | 2.634% | 1.279% | 1.657% | 0.1541% | 1.604% | 2.235% | -11.49% | 3.422% | 3.124% | 2.97% | 2.161% | 1.718% | 2.158% | 1.531% | -0.644% | 0.1436% | 7.226% | 3.779% | 3.822% | 2.918% | 2.098% | 4.053% | 3.822% | 5.114% | 2.948% | 3.103% | 2.455% | 5.093% | 3.864% | 3.822% | 4.683% | 3.632% | 3.569% | 3.548% | 2.652% | 3.575% | 1.457% | 3.643% | 3.853% | 3.538% | 2.361% | 2.256% | 2.109% | 4.179% | 2.834% | 4.189% | 1.888% | 4.032% | 5.388% | 5.03% | 3.782% | 1.92% | 1.636% | 3.927% | 4.284% | 2.35% | 4.242% | 4.641% | 3.506% | 3.63% | 2.305% | 1.345% | 16.86% | 2.34% | 5.262% | 3.632% | 4.904% | 2.655% | 3.506% | 4.263% | 4.673% | 2.34% | 2.666% | 2.634% | 1.352% | 5.8% | 7.3% | 2.257% | 1.038% | 2.799% | 0.6235% | 0.6235% | 1.878% | 1.636% | 2.246% | 4.433% | 4.652% | 2.396% | 3.167% | 3.409% | 3.535% | 0.2892% | 2.409% | 1.224% | 3.777% | 3.271% | 3.524% | 4.099% | 3.029% | 4.375% | 2.361% | 3.662% | 1.901% | 3.478% | 1.728% | 2.753% | 3.697% | 2.912% | 3.915% | -0.2293% | 2.397% | 1.948% | 2.155% | 2.255% | 3.068% | 2.008% | 3.543% | 3.779% | 4.614% | 1.807% | 3.034% | 1.1% | 1.132% | 6.958% | -2.096% | 2.593% | 2.785% | 3.404% | 3.451% | 1.868% | 0.3942% | 0.5558% | 0.876% | -0.3279% | -2.395% | -2.555% | 0.2889% | -7.976% | -1.692% | 0.9483% | 1.075% | 1.087% | 0.4659% | 0.1324% | -0.3587% | 0.7471% | 1.721% | 2.103% | 1.84% | 0.07152% | -38.89% | 0.5763% | -40.63% | 0.5763% | 1.494% | 1.793% | 0.6333% | 1.589% | 0.9918% | -0.4139% | 7.446% | 1.02% | 1.157% | 1.191% | -36.47% | -0.357% | -3.578% | 0.7015% | 0.5194% | 0.5029% | 0.5046% | 2.057% | 2.326% | 3.624% | 4.458% | 3.558% | 3.655% | 4.262% | 3.429% | 2.462% | 3.415% | 4.592% | 0.9647% | 0.4203% | 2.659% | 1.978% | 37.18% | 34.26% | -19.14% | 25% | 3.197% | 1.533% | 0.3703% | 0.543% | 0.3013% | -1.425% | -0.2512% | 1.245% | -0.2397% | -1.275% | 1.648% | 1.268% | 0.8192% | 1.164% | 2.235% | 1.171% | 0.7605% | 0.7913% | 1.591% | 0.9323% | 1.002% | 1.279% | 30.04% | 0.4588% | 0.632% | 1.464% | 0.9785% | 1.088% | 0.9554% | 2.327% | 1.981% | 1.679% | -17.21% | -28.93% | -4.472% | 0.1438% | -0.2318% | -1.074% | -1.076% | -1.204% | -30.19% | -6.918% | -0.789% | -15.93% | 2.136% | -22.11% | 0.7698% | -14.68% | -1.86% | -34.23% | 2.411% | -0.02409% | -11.87% | -46.7% | -32.41% | 17.13% | -47.75% | 0.1893% | 2.978% | 2.159% | 1.988% | 1.84% | 2.136% | 0.7812% | 2.568% | 3.103% | 1.259% | 2.653% | 18.56% | 2.295% | 0.1678% | 2.187% | 3.657% | 2.741% | -11.93% | -0.3229% | 3.561% | 0.6333% | 3.388% | 2.296% | 0.5376% | 2.067% | 0.5018% | 1.267% | 3.25% | 2.761% | 3.92% | 3.346%
2025-04-05 | -7.979% | -11.26% | -7.324% | -7.448% | -7.589% | -11.46% | -5.921% | -9.67% | -6.672% | -6.654% | -6.442% | -6.76% | -6.725% | -6.707% | -5.684% | -5.737% | -7.347% | -6.735% | -7.412% | -6.337% | -3.868% | -4.749% | -3.497% | -4.308% | -4.15% | -4.203% | -3.991% | -4.344% | -3.762% | -3.674% | -4.485% | -4.256% | -8.083% | -9.278% | -8.387% | -7.552% | -6.178% | -6.066% | -7.077% | -6.976% | -9.776% | -6.717% | -4.494% | -5.182% | -4.824% | -2.504% | -2.858% | -3.786% | -5.261% | -4.69% | -4.272% | -6.63% | -7.337% | -7.044% | -8.636% | -6.101% | -6.789% | -11.13% | -11.03% | -11.63% | -7.042% | -8.496% | -7.429% | 1.784% | -0.1919% | -0.2517% | 0.5712% | 2.266% | 1.017% | -1.076% | 0.9568% | 2.724% | -0.7462% | -0.3096% | -0.7221% | 0.6917% | -1.156% | 0.5149% | 1.382% | 1.069% | 0.5149% | 1.785% | 0.539% | 2.262% | 2.178% | 1.347% | 1.229% | 0.7356% | 0.8925% | -0.01522% | 0.4105% | -1.718% | -0.1036% | 0.5471% | -14.09% | 1.736% | 1.49% | 1.037% | 0.9005% | -1.861% | 0.4313% | 0.1615% | -2.017% | 1.929% | 5.793% | 1.993% | 2.419% | 1.583% | 0.9568% | 2.62% | 2.499% | 3.583% | 1.492% | 1.657% | 1.069% | 3.792% | 2.346% | 2.499% | 2.981% | 2.298% | 2.049% | 1.953% | 1.229% | 2.035% | 2.483% | 2.033% | 2.218% | 1.953% | 1.077% | 0.8764% | 0.8202% | 2.772% | 1.503% | 2.66% | 0.6515% | 2.684% | 3.698% | 3.849% | 2.547% | -11.53% | 0.3784% | 2.66% | 2.957% | 1.551% | 0.9728% | 3.367% | 1.551% | 2.396% | 1.107% | 0.2466% | 1.191% | 1.198% | 3.859% | 2.443% | 3.648% | 1.439% | 2.74% | 2.981% | 1.382% | 1.19% | 1.407% | 1.447% | 0.1053% | 4.479% | 5.801% | 1.078% | 0.7533% | 2.346% | 0.2606% | 0.1902% | 1.325% | 1.202% | 1.756% | 3.639% | 3.929% | 1.668% | 2.627% | 2.847% | 2.918% | -0.04735% | 1.995% | 1.002% | 3.181% | 2.733% | 2.909% | 3.357% | 2.495% | 3.78% | 2.038% | 3.093% | 1.448% | 3.067% | 1.158% | 2.293% | 3.214% | 2.391% | 3.057% | -0.8359% | 1.551% | 1.02% | 1.319% | 1.269% | 1.899% | 1.169% | 2.588% | 2.48% | 3.446% | 0.5735% | 1.695% | -0.07549% | -0.03349% | 5.647% | 1.298% | 1.257% | 2.098% | 2.206% | 2.393% | 0.8947% | -0.09506% | -1.387% | -0.08679% | -1.11% | -3.059% | -3.347% | -0.423% | -1.839% | 0.9058% | 1.886% | 0.6907% | 1.495% | 1.915% | 0.4727% | 3.103% | 0.4118% | 2.399% | 1.632% | 1.285% | 1.522% | 0.7685% | 0.4727% | 0.2117% | 0.4988% | 2.262% | 3.441% | 0.846% | 1.43% | 1.074% | -0.02328% | 6.163% | 0.6467% | 1.09% | 0.7859% | 1.682% | 1.952% | 1.204% | 0.9164% | 1.673% | 0.2745% | -0.4626% | 1.301% | 1.474% | 2.884% | 3.499% | 2.591% | 0.6002% | 3.198% | 2.27% | 1.381% | 2.326% | 3.635% | 0.408% | -0.2405% | 1.925% | 0.8795% | 24.52% | 1.879% | -20.1% | 23.95% | -10.97% | 1.228% | 0.3222% | 0.3398% | 0.1638% | -2.502% | -0.6104% | 1.176% | -0.3201% | -1.93% | 1.668% | 0.9809% | 0.4541% | 1.123% | 2.179% | 0.5069% | 0.2205% | 0.3538% | 1.408% | 0.744% | 0.5851% | 1.026% | -5.094% | 0.1967% | 0.1349% | 1.318% | 0.744% | 0.7593% | 0.744% | 1.941% | 1.551% | 1.412% | 2.755% | 1.182% | 2.918% | 1.526% | 1.256% | 0.5075% | 1.542% | -0.3571% | 0.3248% | -0.5809% | 0.1973% | 0.4714% | 1.995% | 0.8816% | 0.1507% | -0.1103% | -0.2408% | 0.03763% | 2.043% | -0.3235% | -0.1133% | 1.513% | 3.203% | 3.057% | 2.993% | -0.6411% | 2.448% | 1.604% | 1.961% | 1.352% | 2.048% | 0.6989% | 2.256% | 2.996% | 1.256% | 2.829% | 6.163% | 2.065% | 0.05641% | 0.9191% | 3.13% | 1.803% | 4.24% | 0.3248% | 2.783% | 0.748% | 2.631% | 1.745% | 0.04198% | 1.543% | 0.3983% | 1.074% | 2.759% | 0.3161% | 3.523% | 2.956%
2025-04-06 | -8.976% | -11.98% | -8.377% | -8.377% | -8.417% | -12.15% | -6.579% | -10.23% | -7.399% | -7.12% | -7.299% | -7.459% | -7.379% | -6.96% | -6.162% | -6.361% | -7.947% | -6.959% | -7.699% | -6.581% | -4.186% | -4.864% | -3.607% | -3.607% | -4.146% | -4.265% | -3.966% | -4.365% | -3.866% | -3.467% | -4.465% | -3.986% | -8.717% | -9.859% | -9.165% | -8.115% | -6.791% | -6.434% | -7.699% | -7.589% | -10.39% | -7.271% | -5.111% | -5.198% | -4.87% | -2.631% | -2.957% | -3.582% | -4.847% | -4.257% | -3.876% | -5.877% | -6.961% | -6.733% | -8.415% | -5.944% | -6.787% | -10.77% | -10.87% | -11.24% | -7.938% | -7.841% | -6.697% | 1.541% | -0.6049% | -0.7695% | -0.1139% | 1.441% | 0.1052% | -1.441% | 0.4407% | 2.086% | -1.323% | -0.8351% | -1.414% | -0.1267% | -1.961% | 0.4953% | 4.923% | 1.114% | 5.651% | 1.641% | 0.5498% | 3.609% | 2.041% | 1.29% | 1.138% | 0.5787% | 0.6226% | 0.3771% | 0.04977% | -3.142% | -0.8867% | -0.7231% | 0.8953% | 1.759% | 1.23% | 0.5862% | -0.2503% | -4.128% | -0.3453% | -0.5685% | -2.716% | 1.032% | 2.205% | 0.959% | 1.377% | 0.468% | -0.3776% | 1.741% | 1.705% | 2.732% | 0.6559% | 1.252% | -0.223% | 2.514% | 1.086% | 1.168% | 1.823% | 1.104% | 0.959% | 0.9772% | 0.1585% | 0.9094% | 1.586% | 1.095% | 1.241% | 1.023% | -0.06842% | -0.06842% | -0.1139% | 1.932% | 0.5862% | 1.959% | -0.3503% | 1.495% | 2.953% | 1.104% | 2.351% | -5.987% | 1.832% | 2.723% | 2.905% | 1.414% | 0.3953% | 3.305% | 2.014% | 2.231% | 0.804% | 0.149% | 0.9313% | 0.7226% | 3.544% | 2.059% | 3.196% | 1.277% | 2.368% | 2.677% | 3.059% | 1.077% | 1.25% | 1.441% | 0.01341% | 3.889% | 5.332% | 0.8809% | 1.453% | 3.235% | 1.074% | 0.9148% | 2.179% | 1.801% | 2.438% | 4.261% | 4.759% | 2.588% | 3.842% | 3.862% | 3.872% | 0.8372% | 2.91% | 1.964% | 4.311% | 3.753% | 3.902% | 4.41% | 3.554% | 4.808% | 3.006% | 4.151% | 2.478% | 4.022% | 1.96% | 3.086% | 4.225% | 3.273% | 3.89% | 0.04738% | 2.718% | 1.942% | 2.537% | 2.619% | 3.4% | 2.333% | 3.905% | 4.047% | 4.804% | 1.897% | 2.903% | 1.263% | 1.297% | 6.723% | 2.644% | 2.893% | 3.328% | 3.665% | 3.813% | 2.158% | 0.8252% | -0.1568% | 1.35% | 0.6709% | -1.644% | -1.921% | -0.4551% | -1.149% | -0.00208% | 1.417% | 1.87% | 2.376% | 0.8562% | 0.5938% | 2.149% | -0.204% | 2.759% | 1.146% | 1.084% | 1.518% | -0.3616% | -0.09564% | -1.396% | -0.2729% | 1.477% | 2.707% | 0.1117% | 0.9483% | 1.249% | -0.4994% | 4.238% | 0.2983% | 0.4953% | 0.2392% | 0.8006% | 1.52% | 0.5839% | 0.2983% | 1.116% | -0.09609% | -0.7505% | 0.9376% | 1.244% | 2.605% | 3.419% | 2.663% | 2.596% | 3.326% | 2.511% | 1.639% | 2.724% | 3.817% | 0.2103% | -0.2786% | 2.151% | 1.118% | 25.07% | 2.56% | -19.79% | 24.31% | -10.53% | 0.7057% | -0.1606% | 0.09827% | -0.001314% | -2.312% | -0.8378% | 0.7953% | -0.7482% | -1.913% | 1.363% | 0.8135% | 0.2377% | 0.9248% | 1.81% | 0.2934% | 0.3562% | 0.3527% | 1.436% | 0.6897% | 0.6198% | 1.119% | -7.701% | 23.27% | 0.2001% | 0.2301% | 1.649% | 11.55% | -8.893% | 0.4468% | 6.975% | 1.527% | 1.766% | 0.8207% | 2.343% | 1.106% | 0.8498% | 0.2097% | 1.161% | -0.4103% | 0.09148% | -0.6413% | -0.2813% | -0.2916% | 1.756% | 0.19% | -0.2532% | -0.4108% | -0.6964% | -0.5585% | 1.804% | -0.5398% | -0.00208% | 0.9286% | 3.214% | 2.376% | 2.118% | -1.199% | 1.864% | 1.027% | 1.204% | 1.076% | 1.451% | 0.1604% | 1.756% | 2.445% | 0.7415% | 2.5% | 3.514% | 1.618% | -0.4756% | 1.539% | 2.697% | 1.192% | -1.031% | -0.3123% | 2.252% | 0.2235% | 2.199% | 1.117% | -0.6329% | 1.096% | -0.1779% | 0.7321% | 2.235% | 1.766% | 2.914% | 2.594%
2025-04-07 | -8.448% | -10.79% | -7.413% | -7.373% | -8.034% | -11.9% | -5.743% | -9.698% | -7.192% | -6.831% | -6.451% | -6.952% | -6.851% | -6.691% | -5.909% | -5.789% | -7.435% | -6.57% | -7.132% | -6.09% | -3.484% | -4.326% | -3.263% | -3.865% | -4.105% | -3.785% | -4.206% | -3.765% | -3.123% | -2.903% | -3.905% | -3.564% | -8.455% | -9.819% | -8.68% | -7.815% | -6.211% | -6.169% | -7.673% | -7.224% | -9.838% | -6.619% | -4.732% | -4.936% | -4.704% | -2.319% | -2.729% | -3.694% | -4.53% | -4.041% | -3.998% | -6.328% | -7.087% | -6.708% | -8.252% | -5.939% | -6.237% | -10.05% | -10.18% | -10.67% | -6.731% | -7.814% | -7.315% | 2.011% | 0.1488% | 0.002891% | 1.19% | 2.632% | 1.228% | -0.4812% | 1.153% | 2.669% | -0.6911% | -0.6778% | -0.892% | 0.2721% | -1.608% | 0.8792% | 1.756% | 1.436% | 0.7332% | 2.171% | 0.8975% | 2.62% | 2.577% | 1.599% | 1.503% | 1.201% | 1.29% | 0.2675% | 0.6875% | -2.243% | 0.4227% | 0.5232% | 2.568% | 2.888% | 2.502% | 1.19% | 0.9705% | 0.7684% | 0.4821% | 0.6327% | -1.657% | 2.24% | 5.946% | 1.628% | 2.742% | 1.473% | 1.381% | 3.089% | 2.961% | 3.737% | 1.707% | 1.942% | 1.281% | 4.203% | 2.587% | 2.943% | 3.162% | 2.87% | 2.413% | 2.066% | 1.351% | 2.105% | 2.532% | 2.13% | 2.285% | 2.13% | 1.181% | 0.9066% | 0.8245% | 2.879% | 1.546% | 2.678% | 0.4866% | 2.468% | 3.775% | 3.335% | 1.872% | -3.85% | -0.3716% | 1.92% | 2.267% | 1.044% | -3.074% | 3.025% | 0.9979% | 1.179% | 0.4821% | -0.2529% | 0.9231% | 0.5962% | 3.277% | 1.874% | 3.573% | 1.381% | 2.714% | 2.806% | 3.217% | 0.7879% | 1.181% | 1.053% | -0.2894% | 4.472% | 5.746% | 0.7112% | -0.7429% | 1.117% | -1.043% | -1.113% | 0.0271% | 0.1271% | 0.8871% | 2.567% | 3.097% | 0.6971% | 1.227% | 1.667% | 2.167% | -1.24% | 0.9254% | 0.02391% | 2.377% | 1.797% | 2.177% | 2.837% | 1.707% | 3.237% | 1.207% | 2.297% | 0.6471% | 2.447% | 0.6371% | 1.907% | 2.656% | 1.889% | 2.236% | -1.755% | 0.778% | 0.04248% | 0.3361% | 0.1861% | 0.5997% | 0.1394% | 1.513% | 1.492% | 2.29% | -0.8204% | 0.2086% | -1.25% | -1.584% | 3.563% | 0.7538% | 0.4059% | 1.59% | 1.308% | 1.712% | -0.4029% | -1.591% | -2.982% | -1.191% | -2.466% | -3.857% | -4.73% | -1.541% | -2.827% | 1.379% | 2.342% | 2.514% | 2.815% | 1.964% | 1.341% | 2.877% | 0.2531% | 3.604% | 1.071% | 1.299% | 2.202% | -0.09301% | 0.2037% | -0.8249% | 0.03556% | 2.369% | 3.241% | 0.4682% | 0.3323% | 1.548% | -0.2216% | 4.882% | -0.182% | 0.4707% | -0.06334% | 0.7674% | 1.064% | 0.3718% | 0.2432% | 0.7476% | 0.4352% | -0.6243% | 1.55% | 1.648% | 3.233% | 3.601% | 2.432% | 2.582% | 3.145% | 2.191% | 1.297% | 2.437% | 3.547% | 0.4391% | 0.2811% | 2.397% | 1.178% | 1.812% | 1.755% | 2.462% | 3.122% | 1.832% | 1.297% | 0.5271% | 0.5271% | 0.4771% | -2.293% | -0.6629% | 1.457% | -0.1929% | -1.803% | 1.497% | 0.8975% | 0.3871% | 1.327% | 2.173% | 0.3876% | 0.1881% | 0.3196% | 1.347% | 0.6795% | 0.3886% | 1.091% | -5.63% | 0.05744% | 0.09757% | 1.412% | 0.6695% | 0.7004% | 0.5491% | 1.917% | 1.469% | 1.396% | 3.76% | 1.432% | 3.537% | 1.836% | 1.618% | 0.9059% | 1.795% | 0.05013% | -2.931% | 0.4069% | 0.3955% | 0.6655% | 2.419% | 1.43% | 0.2432% | 0.8861% | 0.4311% | 1.034% | 2.742% | 0.3021% | 0.2606% | 3.677% | 4.227% | 3.635% | 4.549% | -0.2512% | 3.329% | 1.836% | 3.072% | 1.954% | 2.686% | 1.855% | 2.923% | 3.932% | 2.192% | 3.355% | 3.843% | 3.082% | 0.7716% | 2.462% | 3.999% | 2.144% | 0.9355% | 1.559% | 3.21% | 1.823% | 3.2% | 3.107% | 0.8732% | 2.409% | 1.143% | 1.901% | 3.581% | 3.989% | 4.342% | 3.864%
2025-04-08 | -7.978% | -10.76% | -7.089% | -7.205% | -7.37% | -11.14% | -5.631% | -9.503% | -6.461% | -6.378% | -6.18% | -6.51% | -6.411% | -6.378% | -5.436% | -5.436% | -7.02% | -6.794% | -7.519% | -6.329% | -3.766% | -4.857% | -3.815% | -4.113% | -4.477% | -4.162% | -3.931% | -4.311% | -3.865% | -3.716% | -4.477% | -4.212% | -7.899% | -9.022% | -8.065% | -7.334% | -5.872% | -5.75% | -6.742% | -6.777% | -9.371% | -6.452% | -4.249% | -4.637% | -4.924% | -2.476% | -2.996% | -4.084% | -5.223% | -4.622% | -4.438% | -6.617% | -7.372% | -7.392% | -8.7% | -6.539% | -8.954% | -11.12% | -11.32% | -11.68% | -7.238% | -8.524% | -7.574% | 1.939% | -0.0491% | -0.2515% | 0.6815% | 2.338% | 1.11% | -0.9152% | 1.111% | 2.82% | -0.4935% | -0.2462% | -0.4633% | 0.7934% | -0.9782% | 0.5685% | -0.4633% | 1.096% | 0.6438% | 1.856% | 0.7116% | 2.368% | -0.4332% | 1.581% | 1.337% | 0.3251% | 0.93% | 0.07141% | 0.5158% | -1.194% | 1.118% | 0.9074% | 2.158% | 2.783% | 2.071% | 1.397% | 0.8396% | 2.604% | 0.9903% | 0.2748% | -1.859% | 1.924% | 6.812% | 2.451% | 2.474% | 1.623% | 1.088% | 2.67% | 2.549% | 3.574% | -45.71% | 1.699% | 0.8622% | 3.694% | 2.316% | 2.557% | 2.926% | 2.331% | 2.15% | 2.037% | 1.282% | 2.014% | 2.564% | 2.06% | 2.263% | 2.075% | 1.186% | 0.9677% | 0.9978% | 2.881% | 1.638% | 2.655% | 0.7568% | 2.64% | 3.675% | 4.025% | 1.822% | -11.44% | -0.5838% | 2.858% | 3.114% | 1.743% | 0.6363% | 3.604% | 2.828% | 2.959% | 3.329% | 0.4785% | 1.908% | 3.4% | 6.039% | 2.429% | 3.732% | 1.63% | 2.896% | 3.046% | 3.453% | 1.397% | 1.585% | 1.487% | 0.1543% | 3.805% | 5.426% | 1.313% | 1.064% | 2.591% | 0.6768% | 0.5696% | 1.592% | 1.601% | 2.219% | 3.952% | 4.323% | 2.054% | 2.821% | 3.019% | 3.234% | 0.2627% | 2.251% | 1.085% | 3.308% | 2.92% | 3.226% | 3.795% | 2.755% | 4.084% | 2.236% | 3.399% | 1.65% | 3.275% | 1.337% | 2.508% | 3.398% | 2.593% | 3.19% | -0.6335% | 1.682% | 1.277% | 1.512% | 1.437% | 2.039% | 1.465% | 2.838% | 2.574% | 3.657% | 0.6125% | 1.788% | 0.1986% | -0.0078% | 5.24% | 1.394% | 1.217% | 2.39% | 2.289% | 2.513% | 0.975% | -0.09098% | -1.302% | -0.0832% | -1.097% | -2.829% | -3.316% | -0.4596% | -2.189% | 1.812% | 2.847% | 2.939% | 3.495% | 2.442% | 1.969% | 3.35% | 0.6963% | 3.992% | 1.791% | 1.893% | 2.579% | 1.169% | 0.6229% | 0.5168% | 0.5494% | 2.776% | 3.915% | 1.123% | 1.602% | 2.193% | 0.2068% | 4.934% | 0.7289% | 1.161% | 0.8758% | 2.01% | 2.197% | 1.316% | 1.063% | 1.855% | 0.2932% | -0.5785% | 1.393% | 1.454% | 2.842% | 3.178% | 2.625% | 2.591% | 3.151% | 2.212% | 1.333% | 2.357% | 3.457% | 0.2435% | 0.1616% | 1.294% | 1.294% | 2.108% | 2.117% | 2.443% | 3.235% | 1.703% | 1.015% | 0.2314% | 0.2314% | 0.06638% | -2.986% | -0.874% | 1.106% | -0.4615% | -2.037% | 1.493% | 0.7944% | 0.3468% | 1.196% | 2.125% | 0.2194% | 0.1848% | 0.2285% | 1.35% | 0.6479% | 0.5072% | 1.045% | -1.536% | 0.1762% | 0.07683% | 1.459% | 0.681% | 0.6026% | 0.5817% | 1.774% | 1.475% | 1.406% | 2.733% | 1.028% | 2.835% | 1.276% | 1.112% | 0.4597% | 1.449% | -0.4441% | 0.9818% | -0.6257% | -0.08527% | 0.2745% | 1.773% | 0.6963% | -0.06242% | -0.1766% | -0.3561% | 0.215% | 1.94% | -0.3251% | 0.000394% | 1.979% | 2.973% | 1.936% | 3.607% | -1.115% | 2.124% | 1.3% | 1.618% | 1.145% | 1.463% | 0.6065% | 1.659% | 2.899% | 1.08% | 2.604% | 2.193% | 2.148% | 0.09688% | 1.594% | 2.99% | 1.601% | -0.5274% | -1.955% | 2.759% | 0.6826% | 2.597% | 1.843% | 0.1032% | 1.577% | 0.3687% | 0.9084% | 2.667% | 2.587% | 3.41% | 2.879%
2025-04-09 | -8.968% | -11.34% | -8.166% | -8.293% | -8.799% | -12.4% | -6.421% | -10.7% | -8.071% | -7.944% | -7.437% | -8.198% | -7.469% | -8.103% | -7.089% | -6.645% | -8.701% | -7.767% | -8.388% | -7.406% | -4.586% | -5.568% | -4.491% | -4.523% | -4.871% | -4.935% | -4.238% | -4.618% | -3.953% | -4.238% | -4.84% | -4.84% | -8.641% | -10.9% | -9.501% | -8.468% | -6.967% | -7.467% | -8.451% | -7.734% | -10.38% | -6.26% | -4.51% | -3.991% | -4.755% | -2.059% | -2.862% | -4.09% | -6.3% | -4.932% | -4.874% | -7.729% | -8.315% | -7.771% | -9.064% | -7.182% | -8.558% | -11.03% | -11.06% | -11.34% | -7.437% | -8.547% | -8.645% | 0.872% | -0.6863% | -0.652% | 0.4247% | 1.593% | 0.03171% | -1.942% | 0.1794% | 1.449% | -1.61% | -1.829% | -1.725% | -0.5316% | -2.176% | 0.165% | 1.175% | 0.8575% | -0.2968% | 1.343% | 0.006241% | 1.52% | 1.536% | 0.2227% | 0.4339% | 0.06061% | 0.4535% | -0.5276% | -0.1813% | -2.995% | -0.8018% | -0.8451% | 1.218% | 0.771% | 0.7669% | -0.9605% | 0.6555% | 0.8713% | -1.075% | 0.4535% | -0.555% | 0.9297% | 5.893% | -0.1236% | 1.781% | 2.315% | 2.892% | 3.152% | 2.113% | 2.517% | 0.5387% | 0.8411% | 0.4247% | 3.484% | 1.767% | 2.43% | 2.401% | 2.459% | 1.637% | 1.276% | 0.5093% | 1.324% | 1.997% | 1.752% | 1.651% | 1.824% | 0.6555% | 0.3525% | -0.8595% | 2.676% | 1.377% | 2.719% | 0.3237% | 1.983% | 3.949% | 5.085% | 3.183% | 1.161% | 0.8575% | 3.31% | 3.484% | 2.3% | 1.305% | 4.248% | 2.82% | 2.923% | 2.808% | 0.4791% | 2.015% | 3.166% | 4.964% | 2.156% | 3.657% | 1.752% | 2.906% | 2.733% | 2.964% | 1.348% | 1.565% | 1.795% | 0.6844% | 4.26% | 5.691% | 1.324% | 1.044% | 3.367% | 0.3333% | 0.1911% | -1.215% | 0.9654% | 1.85% | 3.099% | 4.569% | 2.198% | 2.783% | 4.031% | 4.363% | 0.82% | 3.136% | 2.018% | 3.794% | 3.731% | 3.889% | 3.541% | 2.988% | 3.873% | 2.783% | 3.004% | 1.756% | 3.431% | 1.329% | 2.735% | 3.01% | 2.081% | 3.176% | 0.106% | -1.494% | 2.42% | -2.327% | 2.775% | 3.033% | 2.581% | 4.059% | 4.294% | 4.829% | 1.762% | 2.314% | 1.325% | 0.4485% | 3.359% | 3.033% | 2.371% | 3.733% | 3.446% | 3.561% | 1.838% | 1.186% | -0.464% | 1.872% | 0.09377% | -0.9384% | -2.183% | -0.949% | -0.2174% | 1.956% | 3.105% | 3.585% | 3.273% | 2.108% | 0.6374% | 3.47% | 1.106% | 4.996% | 1.862% | 2.289% | 3.273% | 1.012% | 0.528% | 0.4654% | 0.9656% | 4.34% | 4.947% | 2.174% | 1.122% | 2.961% | 1.466% | 6.67% | 1.106% | 1.45% | 0.9968% | 3.982% | 2.872% | 0.778% | 1.45% | 1.997% | 0.5983% | -0.8741% | 1.804% | 1.756% | 3.552% | 4.277% | 2.302% | 3.082% | 2.911% | 1.776% | 0.9622% | -1.535% | 3.219% | 0.7179% | 0.5595% | 2.607% | 1.391% | 1.948% | 1.51% | 2.375% | 3.043% | 1.658% | 0.4913% | 0.1753% | -1.089% | -1.405% | -3.586% | -1.974% | 0.7284% | -1.389% | -3.507% | 0.6177% | 3.152% | 0.3965% | 1.993% | 1.865% | -0.3581% | -1.802% | -1.43% | 0.1772% | -0.5135% | -1.195% | -0.2123% | -18.48% | -0.8307% | -1.291% | 0.2952% | -0.2281% | 1.302% | 0.5172% | 3.968% | 3.259% | 0.5048% | 3.963% | -0.06527% | 3.475% | 1.622% | 0.9031% | 0.09035% | 1.583% | -0.9996% | 1.153% | 1.106% | -1.141% | 0.08956% | 2.607% | 1.763% | 0.2466% | 1.075% | 0.8406% | 1.56% | 3.485% | -0.04172% | 0.4178% | 3.749% | 4.537% | 5.029% | 5.062% | -0.06595% | 3.138% | 1.778% | 3.185% | 0.2779% | 2.638% | 3.154% | 2.513% | 3.966% | 1.653% | 2.847% | 3.388% | 3.216% | 0.3133% | 1.583% | 3.766% | 1.464% | 0.6999% | -3.848% | 1.944% | 1.135% | 1.794% | 3.105% | -0.04172% | 1.106% | -0.07454% | 1.14% | 2.611% | 3.864% | 3.897% | 2.732%
2025-04-10 | -8.064% | -10.42% | -7.227% | -7.207% | -7.384% | -11.2% | -5.432% | -9.385% | -6.363% | -6.187% | -6.207% | -6.54% | -6.246% | -6.187% | -5.245% | -5.383% | -6.949% | -6.412% | -7.089% | -5.932% | -3.421% | -4.382% | -3.303% | -3.754% | -3.695% | -3.735% | -3.44% | -3.813% | -3.323% | -3.087% | -3.95% | -3.578% | -7.698% | -8.89% | -8.023% | -7.155% | -5.689% | -5.71% | -6.834% | -6.598% | -9.365% | -6.17% | -3.96% | -4.595% | -4.311% | -1.907% | -2.388% | -3.326% | -4.838% | -3.989% | -3.632% | -5.975% | -6.899% | -6.765% | -8.238% | -6.022% | -6.372% | -10.49% | -10.61% | -11.33% | -6.658% | -8.025% | -6.935% | 2.064% | 0.04428% | -0.08327% | 0.9647% | 2.439% | 1.22% | -0.8404% | 1.117% | 2.743% | -0.5723% | -0.3076% | -0.7242% | 0.7055% | -1.228% | 0.6251% | 1.635% | 1.349% | 0.7234% | 2.024% | 0.8396% | 2.527% | 2.439% | 1.621% | 1.509% | 1.14% | 1.09% | 0.1783% | 0.643% | -1.278% | 0.6072% | 0.7234% | 1.983% | 2.68% | 2.095% | 2.117% | 2.573% | 1.63% | 0.7709% | 2.966% | 0.8177% | 2.403% | 7.22% | 1.876% | 4.056% | 3.628% | 3.35% | 4.11% | 2.788% | 4.879% | 2.438% | 1.948% | 1.331% | 4.012% | 2.528% | 2.886% | 3.127% | 2.537% | 2.421% | 2.323% | 1.546% | 2.238% | 2.868% | 2.287% | 2.528% | 2.35% | 1.349% | 1.134% | 1.188% | 3.476% | 1.939% | 3.359% | 0.9647% | 2.796% | 4.246% | 4.825% | 3.007% | 1.501% | 0.8753% | 3.485% | 3.788% | 2.385% | 3.788% | 3.485% | 3.261% | 3.405% | 3.394% | 0.7616% | 2.093% | 3.485% | 5.951% | 2.868% | 4.11% | 1.921% | 3.288% | 3.306% | 3.779% | 1.662% | 1.822% | 1.805% | 0.4643% | 4.439% | 5.951% | 1.472% | 0.6859% | 2.271% | 0.3532% | 0.2358% | 1.136% | 1.107% | 1.723% | 3.514% | 3.916% | 1.704% | 2.692% | 2.819% | 2.956% | 0.1506% | 1.893% | 0.5% | 2.859% | 2.614% | 2.976% | 3.475% | 2.32% | 3.612% | -0.694% | 3.005% | 1.087% | 2.673% | 0.7251% | 1.978% | 2.689% | 1.908% | 2.576% | -0.2951% | 2.366% | 14.66% | -2.774% | 2.445% | 3.208% | 2.258% | 1.64% | 3.713% | 4.601% | 1.668% | 2.722% | 1.186% | 1.013% | 8.817% | 1.919% | 1.947% | 2.892% | 3.233% | 3.3% | 6.826% | 0.7168% | -0.3429% | 1.01% | -0.04183% | -1.717% | -2.292% | 0.3175% | -1.36% | 0.5875% | 1.567% | 1.418% | 2.17% | 1.205% | 0.6249% | 2.373% | -0.2947% | 2.617% | 0.7168% | 0.8286% | 1.255% | 0.6055% | -0.06236% | -0.2075% | -0.1011% | 1.591% | 2.719% | -0.06575% | 0.499% | 0.7067% | -0.7786% | 4.274% | -0.3818% | 0.2667% | -0.06236% | 1.119% | 0.9249% | 0.6249% | 0.3538% | 1.06% | -0.003844% | -0.9459% | 1.163% | 1.224% | 2.715% | 3.622% | 2.5% | 2.938% | 3.091% | 2.179% | 1.251% | 2.454% | 3.459% | 0.08858% | 0.06004% | 1.453% | 1.454% | 2.343% | 2.027% | 2.533% | 3.343% | 1.983% | -0.3906% | -1.252% | -1.193% | -1.438% | -5.137% | -2.26% | -0.42% | -1.927% | -3.17% | 0.5098% | 2.546% | 0.6566% | 1.185% | 0.5411% | -1.144% | -1.278% | -0.9795% | 0.06503% | -0.4925% | -0.7871% | -0.3943% | -0.388% | -1.131% | -1.367% | 0.3324% | -0.7184% | 1.075% | 0.5877% | 2.996% | 2.771% | 0.1712% | 0.8693% | -0.6486% | 0.8905% | -0.4398% | -0.6431% | -1.814% | -0.6098% | -2.402% | -0.9916% | -2.572% | -1.733% | -1.58% | -0.1398% | -1.33% | -2.201% | -2.076% | -1.969% | -1.621% | 0.1272% | -2.617% | -2.068% | -1.001% | 1.113% | 0.6152% | 0.8489% | -1.998% | 0.954% | -0.0914% | 0.4603% | -0.1979% | 0.3054% | -0.7012% | 0.2764% | 1.428% | -0.4398% | 0.8998% | 1.123% | 0.6733% | -1.3% | 0.1375% | 1.55% | 0.2456% | -1.708% | -4.728% | 1.327% | -1.131% | 1.264% | 0.3195% | -1.316% | 0.3635% | -1.133% | -0.5129% | 1.321% | 1.286% | 1.865% | 1.55%
2025-04-11 | -7.568% | -10.63% | -6.944% | -6.872% | -7.016% | -11.59% | -4.567% | -8.992% | -5.615% | -5.435% | -5.866% | -6.19% | -5.579% | -5.328% | -4.393% | -5.004% | -6.547% | -5.148% | -5.471% | -4.717% | -1.95% | -2.813% | -1.914% | -2.561% | -1.771% | -2.094% | -1.483% | -1.95% | -1.339% | -1.124% | -2.238% | -2.058% | -6.549% | -8.098% | -7.984% | -6.434% | -5.148% | -5.45% | -6.334% | -6.018% | -9.208% | -5.351% | -3.142% | -3.969% | -3.102% | -0.721% | -1.111% | -1.514% | -4.133% | -2.401% | -1.601% | -3.979% | -5.49% | -5.148% | -6.687% | -4.584% | -5.052% | -9.106% | -9.125% | -9.567% | -12.59% | -6.092% | -5.6% | 3.591% | 1.464% | 1.205% | 1.545% | 3.051% | 2.228% | 0.007127% | 2.266% | 3.46% | 0.1053% | 0.9051% | -0.0256% | 1.679% | -0.4429% | 1.431% | 2.298% | 1.464% | 1.627% | 2.38% | 2.904% | 3.03% | 3.706% | 4.091% | 2.808% | 1.851% | 2.413% | -7.046% | 1.284% | -0.6638% | 0.8745% | 1.627% | 2.331% | 3.215% | 2.47% | 3.035% | 2.609% | 1.627% | 1.593% | 2.74% | 1.051% | 2.724% | 7.453% | 2.904% | 4.049% | 3.575% | 3.067% | 4.197% | 2.838% | 4.753% | 2.9% | 1.764% | 1.922% | 4.638% | 3.313% | 3.591% | 4.851% | 3.689% | 3.477% | 3.558% | 2.38% | 3.612% | 4.753% | 4.246% | 1.725% | 4% | 2.216% | 2.118% | 2.216% | 4.917% | 3.329% | 5.228% | 2.2% | 4.131% | 6.349% | 5.751% | 3.961% | 2.626% | 2.38% | 4.753% | 5.015% | 4.328% | 3.918% | 4.409% | 3.755% | 4.878% | 4.497% | 2.004% | 3.283% | 4.442% | 7.273% | 3.706% | 5.015% | 2.969% | 4.295% | 2.642% | 3.166% | 2.658% | 2.953% | 3.051% | 2.429% | 5.564% | 7.47% | 2.876% | -1.456% | 0.5519% | -0.6849% | -0.2189% | 0.5877% | -0.03963% | 0.5698% | 2.703% | 3.276% | 1.412% | 2.004% | 2.075% | 2.595% | 0.3099% | 2.087% | -0.2034% | 2.326% | 2.255% | 2.792% | 2.864% | 2.237% | 2.9% | 1.018% | 2.774% | 0.5339% | 2.416% | 0.01414% | 1.036% | 1.947% | 1.044% | 2.324% | 0.9313% | 4.118% | 3.954% | 3.669% | 3.861% | 5.137% | -0.5132% | 5.091% | 5.916% | 5.981% | 3.725% | 4.707% | 3.719% | 3.197% | 8.892% | 3.861% | 4.624% | 4.587% | 5.561% | 5.448% | 3.716% | 1.55% | 0.7235% | 2.593% | 0.8963% | -1.447% | -1.343% | 1.21% | -0.4262% | -1.182% | 0.3582% | 0.4919% | 1.106% | 0.1941% | -0.6063% | 1.702% | -1.014% | 1.758% | -0.0479% | -0.01068% | 0.2685% | -1.369% | -1.528% | -1.829% | -1.156% | 2.074% | 2.986% | 0.2313% | -0.03904% | 0.101% | -2.113% | 1.441% | -0.8899% | -0.6595% | -0.7658% | 0.7941% | 0.8473% | -0.5708% | -0.5177% | 0.1028% | 0.7474% | -0.07299% | 1.789% | 1.899% | 2.89% | 4.078% | 3.1% | 3.424% | 3.776% | 2.89% | 1.886% | 3.252% | 4.103% | 0.3542% | 1.1% | 2.248% | 1.875% | 3.799% | 3.654% | 3.003% | 4.821% | 3.049% | -1.707% | -2.728% | -3.051% | -3.158% | -5.65% | -3.75% | -2.083% | -3.75% | -4.718% | -1.366% | -0.09106% | -1.491% | -1.008% | -0.8946% | -2.212% | -3.134% | -2.676% | -1.304% | -2.144% | -2.108% | -1.785% | -6.642% | -2.432% | -3.062% | -1.119% | -2.108% | -0.8328% | -1.083% | 0.8207% | 5.862% | 0.7616% | -1.593% | -3.244% | -2.005% | -2.751% | -3.336% | -4.116% | -3.153% | -4.878% | -3.035% | -4.464% | -4.441% | -3.975% | -2.042% | -3.407% | -4.364% | -4.808% | -4.205% | -3.159% | -2.116% | -5.297% | -3.398% | -0.7552% | -0.5505% | -0.4202% | -0.1782% | -3.017% | -0.5886% | 0.3332% | -1.262% | -1.847% | -0.8722% | -2.521% | -0.9963% | -0.4645% | -2.273% | -0.5691% | 0.5105% | -1.067% | -3.114% | -1.574% | 0.1196% | -0.9955% | -3.23% | -3.407% | 0.02655% | -2.891% | -0.2518% | -1.334% | -2.97% | -1.528% | -3.305% | -1.518% | -0.2536% | -0.9413% | 0.08239% | -0.234%
2025-04-12 | -6.066% | -8.561% | -5.453% | -5.372% | -6.001% | -9.828% | -3.347% | -7.561% | -5.008% | -4.704% | -4.359% | -4.866% | -4.947% | -4.582% | -3.893% | -3.893% | -5.426% | -4.509% | -2.738% | -4.076% | -1.401% | -2.313% | -1.421% | -1.968% | -1.847% | -1.705% | -1.482% | -1.745% | -1.198% | -0.9957% | -1.968% | -1.543% | -6.487% | -7.772% | -6.876% | -5.916% | -4.423% | -4.295% | -5.818% | -5.404% | -8.108% | -5.26% | -3.251% | -3.433% | -3.023% | -0.6375% | -1.402% | -2.161% | -3.966% | -2.326% | -2.621% | -4.766% | -5.498% | -5.103% | -6.552% | -4.13% | -4.984% | -8.674% | -8.8% | -9.399% | -14.59% | -6.109% | -5.523% | 2.862% | 1.219% | 1.646% | 2.318% | 3.259% | 2.505% | 0.2135% | 2.659% | 3.241% | 0.5088% | 0.3% | 0.2135% | 1.951% | 0.2819% | -1.623% | 2.281% | 2.355% | 1.893% | -1.822% | 3.462% | 3.196% | 3.499% | 4.238% | 2.897% | 1.95% | 2.687% | 0.6011% | 1.884% | 0.2135% | 2.004% | 2.604% | 3.711% | 3.518% | 2.895% | 2.945% | 2.973% | 2.964% | 2.376% | 3.508% | 1.804% | 3.361% | 8.271% | 3.167% | 4.828% | 3.887% | 4.007% | 5.013% | 3.841% | 2.299% | -0.6844% | 2.077% | 1.856% | 4.118% | 2.788% | 3.499% | -2.315% | 3.518% | 3.49% | -4.853% | 2.212% | 3.273% | 4.219% | 3.693% | 1.45% | 3.527% | 1.986% | 1.782% | 1.755% | 4.21% | 2.669% | 4.459% | 1.598% | 0.1858% | 2.964% | 3.924% | 2.19% | 1.284% | 0.998% | 2.669% | 3.213% | 3.37% | 3.462% | 2.355% | 2.908% | 3.524% | 3.229% | 0.9283% | 2.488% | 3.278% | 5.896% | 2.465% | 3.896% | 0.5365% | 2.096% | 0.9057% | 0.7303% | -3.488% | 2.318% | -3.303% | 1.081% | 4.281% | 5.954% | 1.951% | -1.705% | 0.06361% | -0.9978% | -0.735% | -0.179% | -0.0678% | 0.7106% | 2.217% | 2.732% | 0.7813% | 1.014% | 1.388% | 1.762% | -0.2508% | 1.433% | -0.8664% | 1.802% | 1.661% | 2.419% | 2.48% | 1.822% | 2.742% | 0.66% | 2.409% | 0.1849% | 2.429% | 0.3264% | 1.398% | 2.254% | 1.607% | 2.052% | -0.9517% | 1.816% | 1.445% | 1.007% | 1.13% | 2.173% | 0.9397% | -1.682% | 2.797% | -1.928% | 0.2391% | 0.2487% | 0.5136% | -0.3675% | 4.593% | 1.211% | 2.873% | 2.558% | 2.649% | 2.696% | 1.053% | -2.778% | -3.508% | -2.454% | -2.001% | -3.88% | -3.958% | -1.656% | -3.382% | -0.1044% | 0.9167% | 1.708% | 1.792% | 1.655% | 0.6536% | 2.862% | -0.1162% | 2.348% | 0.4481% | 0.763% | 1.372% | -0.1062% | -0.4461% | -0.7561% | -0.4861% | 0.3641% | -35.86% | -0.7486% | -0.5361% | 0.5531% | -1.526% | 3.923% | -0.906% | -0.3462% | -0.6661% | 0.2737% | 0.6336% | -0.05625% | -0.4661% | 0.1437% | 0.6399% | -0.7947% | 1.266% | 1.291% | -0.5664% | 2.925% | 1.899% | 2.536% | 3.283% | 2.663% | 1.358% | 3.035% | 2.689% | -0.824% | 0.1908% | 0.9535% | 0.9485% | 3.246% | 2.651% | 2.344% | 3.978% | 2.491% | -0.007148% | -0.7552% | -0.8461% | -0.644% | -3.09% | -1.796% | -0.0678% | -1.827% | -2.817% | 0.3972% | 0.3981% | 0.09394% | 0.6196% | 0.6833% | -0.5586% | -0.7708% | -0.8387% | 0.291% | -0.4976% | -0.2947% | -0.102% | -3.483% | -0.9439% | -1.208% | 0.395% | -0.6193% | 1.235% | 0.2327% | 1.812% | 2.19% | 0.333% | 1.477% | -1.764% | 1.532% | 0.1137% | -0.3562% | -1.026% | -0.2083% | -1.525% | -0.816% | -2.328% | -1.231% | -1.032% | 0.1437% | -0.926% | -2.286% | -1.646% | -1.656% | -0.6561% | 0.06779% | -2.25% | -0.5806% | 1.466% | 2.012% | 1.823% | 2.18% | -1.046% | 1.433% | 0.4236% | 0.8535% | -0.1262% | 0.9635% | -0.09624% | 1.083% | 1.513% | -0.08624% | 1.424% | 1.823% | 1.013% | -0.3425% | 0.973% | 2.296% | 0.43% | -0.4561% | -0.4062% | 1.96% | -0.4575% | 1.393% | 0.8785% | -0.5386% | 0.7335% | -0.5491% | 0.3327% | 2.21% | 1.844% | 2.369% | 2.285%
2025-04-13 | -6.323% | -9.432% | -5.806% | -6.074% | -6.007% | -9.19% | -3.92% | -8.138% | -5.034% | -4.933% | -4.799% | -5.118% | -5.017% | -4.816% | -3.977% | -4.245% | -5.864% | -5.299% | -5.957% | -4.799% | -2.215% | -3.356% | -2.265% | -2.718% | -2.702% | -2.668% | -2.567% | -2.836% | -2.198% | -2.098% | -3.054% | -2.618% | -6.292% | -7.295% | -6.659% | -5.882% | -2.685% | -4.38% | -5.453% | -5.458% | -8.205% | -5.565% | -3.239% | -3.622% | -3.461% | -1.041% | -1.791% | -2.435% | -4.654% | -0.4673% | -5.824% | -5.242% | -6.12% | -6.152% | -7.494% | -5.598% | -6.051% | -10.15% | 33.12% | -10.61% | -15.3% | -7.336% | -5.954% | 2.178% | 0.2449% | 0.5419% | 1.101% | 1.636% | 1.725% | -0.8327% | 1.972% | 2.064% | -0.42% | -0.6113% | -0.3665% | 1.67% | 0.1435% | 1.315% | 1.735% | 1.98% | 0.1685% | 1.136% | 2.943% | 2.62% | 2.049% | 3.923% | 1.813% | 0.4314% | 1.712% | 0.9251% | 1.032% | -0.7868% | 1.208% | 1.857% | 2.889% | 2.362% | 0.6976% | 1.942% | 2.224% | 2.468% | 2.077% | 2.339% | 1.136% | 1.85% | 7.841% | 7.834% | 4.02% | 2.438% | 2.675% | 3.844% | 3.829% | 4.135% | 12.57% | 0.1115% | 1.391% | 2.247% | 1.735% | 2.752% | 3.974% | 3.325% | 2.583% | 2.476% | 1.662% | 3.1% | 3.416% | 2.759% | 0.8334% | 2.553% | 1.72% | 1.215% | 1.108% | 2.95% | 1.078% | 3.516% | 0.9327% | 2.499% | 4.578% | 2.538% | -0.2445% | 0.9098% | 0.8792% | 1.643% | 2.438% | 2.377% | 1.506% | 3.485% | -0.3206% | 3.675% | 3.568% | 1.102% | 2.424% | 2.301% | 5.749% | 0.6117% | 2.576% | 1.781% | 3.011% | 2.836% | 2.094% | -3.408% | 1.536% | -0.7486% | 0.9862% | 1.825% | 3.791% | 2.037% | 0.5011% | 2.142% | -4.119% | 1.003% | 0.9112% | 1.472% | 1.983% | 3.489% | 3.715% | 2.066% | 2.669% | 2.786% | 2.878% | 0.9736% | 2.408% | -0.008335% | 2.753% | 2.661% | 3.163% | 3.213% | 2.619% | 3.305% | 1.48% | 3.23% | 0.9949% | 2.962% | 0.7773% | 1.757% | 2.705% | 1.949% | 1.51% | -0.902% | 2.326% | 9.199% | 0.9404% | 1.668% | 3.503% | 0.7492% | 2.023% | 3.583% | 2.9% | 0.2441% | 2.109% | 1.11% | 0.1561% | 5.677% | 0.7129% | 1.802% | 2.863% | 1.45% | 3.162% | 25.19% | -1.279% | -6.181% | 0.5286% | -1.363% | -3.538% | -2.663% | -1.833% | -4.592% | -0.1984% | 0.734% | 1.689% | 2.159% | 0.4811% | 0.9613% | -0.9183% | 0.1086% | 2.524% | 1.02% | 1.177% | 0.6463% | -13.02% | -0.1149% | -5.322% | -0.148% | 1.733% | 2.976% | -0.05776% | 0.953% | 0.9592% | -0.8517% | 4.306% | -0.1232% | 0.3239% | 0.1831% | -11.47% | -0.4708% | -5.885% | 0.2494% | -2.598% | 0.5365% | -0.7412% | 1.282% | 1.039% | 1.27% | 1.285% | 1.362% | 0.9503% | 3.31% | 2.764% | 1.003% | 2.575% | 1.461% | -2.167% | 0.06156% | -1.406% | 0.9882% | 2.77% | 2.393% | 1.139% | 3.656% | 2.014% | -0.3778% | -0.4866% | -0.361% | -0.3694% | -3.433% | -1.374% | 0.2249% | -1.951% | -2.495% | 0.5932% | 0.4436% | 0.9112% | 1.33% | 0.6045% | -0.1162% | -0.2129% | -0.07466% | 1.063% | -0.02096% | -0.1385% | 0.441% | -1.796% | -0.3149% | -0.4577% | 0.2982% | -0.06295% | 1.424% | 0.9701% | 1.757% | 2.687% | 0.2617% | 0.5594% | -2.603% | 1.308% | 0.2742% | -0.1314% | -0.7192% | -0.01074% | -1.642% | -1.266% | -2.593% | -1.223% | -1.17% | 0.2907% | -1.39% | -1.696% | -2.019% | -2.499% | -2.284% | -0.09531% | -1.996% | -0.9096% | -3.891% | 0.3768% | -9.602% | -9.836% | -3.029% | 0.8123% | 0.15% | 0.5888% | 0.1252% | 0.7957% | -1.001% | 0.8454% | 1.284% | -0.2473% | 1.35% | 1.698% | 0.8206% | -0.7358% | 0.6463% | 1.924% | 0.1493% | -9.544% | -4.403% | 2.098% | -3.335% | 1.648% | -0.1747% | -1.362% | 0.6715% | -1.292% | -0.588% | 1.762% | 0.655% | 2.141% | 1.898%
2025-04-14 | -7.241% | -9.932% | -6.642% | -6.713% | -6.962% | -10.17% | -4.692% | -8.737% | -5.915% | -5.755% | -5.471% | -5.915% | -5.95% | -5.613% | -4.903% | -5.027% | -6.494% | -5.746% | -6.412% | -5.311% | -2.684% | -3.642% | -2.772% | -3.021% | -3.198% | -3.056% | -2.897% | -3.181% | -2.595% | -2.471% | -3.394% | -3.003% | -7.317% | -8.288% | -7.727% | -6.868% | -5.485% | -5.298% | -6.589% | -6.475% | -9.039% | -6.169% | -3.913% | -4.454% | -4.163% | -1.793% | -2.265% | -3.12% | -4.665% | -3.735% | -3.607% | -5.828% | -6.641% | -6.431% | -7.807% | -5.81% | -6.159% | -10.36% | -10.35% | -10.75% | -15.7% | -7.426% | -6.699% | -0.3831% | -0.3022% | 0.3896% | 1.291% | 2.657% | 1.521% | -0.4316% | 1.687% | 2.997% | -0.04349% | 0.07042% | -0.1163% | 1.178% | -0.5382% | 1.323% | 2.212% | 1.768% | 1.072% | 2.208% | 2.738% | 2.945% | 3.66% | 4.001% | 2.683% | 1.529% | 1.493% | 0.6438% | 1.04% | -0.3588% | 1.63% | 1.598% | 2.584% | 3.264% | 2.687% | 2.374% | 2.714% | 2.454% | 1.592% | 2.964% | 1.017% | 2.94% | 7.864% | 3.078% | 4.137% | 3.676% | 3.353% | 4.242% | 3.086% | 4.832% | 2.71% | 1.786% | 1.76% | 3.927% | 2.924% | 3.328% | 3.87% | 0.8864% | 2.722% | 2.778% | 1.854% | 3.004% | 3.256% | 2.601% | 0.6519% | 2.471% | 1.808% | 1.517% | 1.469% | 3.684% | 2.229% | 3.757% | 1.105% | 1.145% | 4.204% | 3.813% | 2.062% | 0.9834% | 0.4012% | 2.738% | 3.126% | 1.994% | 1.363% | 3.781% | 1.072% | 3.164% | 3.324% | 0.5946% | 1.876% | 2.94% | 5.695% | 2.431% | 3.425% | 1.808% | 3.061% | 3.296% | 3.433% | -2.728% | 1.897% | 1.792% | 0.4578% | 3.796% | 5.366% | 1.491% | -0.09701% | 1.639% | 0.2838% | 0.2484% | 0.6646% | 0.7532% | 1.267% | 2.985% | 3.295% | 1.488% | 2.117% | 2.268% | 2.462% | 0.2395% | 1.82% | 0.02818% | 2.329% | 2.276% | 2.843% | 2.923% | 2.206% | 3.065% | 1.223% | 2.994% | 3.073% | 2.808% | 0.3723% | 1.532% | 2.295% | 1.523% | 2.127% | -0.4942% | 1.926% | 1.621% | 1.586% | 1.809% | 2.781% | 1.598% | 2.889% | 3.148% | 3.672% | 0.9438% | 2.056% | 0.8809% | 0.3775% | 3.401% | 1.506% | 1.455% | 2.568% | -1.853% | 2.71% | 1.498% | -0.4482% | -1.307% | 0.01744% | -1.073% | -3.218% | -3.425% | -0.7131% | -2.306% | 0.5091% | 1.621% | 1.649% | 2.09% | 1.649% | 0.9335% | 2.743% | 0.04011% | 2.513% | 0.775% | 0.9129% | 1.235% | -0.4153% | -0.3365% | -1.072% | -0.3803% | 1.768% | 2.789% | -0.1263% | 0.7933% | 0.8577% | -0.8883% | 4.564% | -0.4504% | 0.04011% | -0.03872% | 0.1102% | 0.8547% | 0.1978% | 0.03135% | 0.8284% | 0.693% | -0.2626% | 1.729% | 1.757% | 2.922% | 3.621% | 2.482% | 3.026% | 3.569% | 2.569% | 1.569% | 2.766% | 3.441% | -0.004078% | 0.4844% | 1.361% | 1.284% | 2.633% | 1.989% | 2.385% | 3.562% | 2.348% | 0.2129% | -4.684% | -0.4955% | -0.5752% | -3.073% | -1.434% | 0.2307% | -1.417% | -2.506% | 1.267% | 2.123% | 0.9037% | 1.453% | 1.179% | -0.3091% | -0.5044% | -0.3401% | 0.8458% | 0.00403% | 0.084% | 0.2973% | 0.06513% | -3.079% | -0.698% | 0.7949% | -0.1737% | 1.306% | 0.8926% | 2.507% | 2.666% | 0.6394% | 1.115% | -0.3742% | 1.383% | 0.3554% | -0.003684% | -0.6431% | 0.02564% | -1.714% | -1.694% | -1.623% | -1.267% | -1.037% | 0.4868% | -0.6869% | -1.598% | -1.694% | -1.825% | -1.212% | 0.652% | -2.039% | -2.039% | -0.5861% | -0.4114% | 2.026% | 1.364% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-04-15 | -6.512% | -8.804% | -5.781% | -5.781% | -6.363% | -9.724% | -3.763% | -7.864% | -5.349% | -5.143% | -4.711% | -5.199% | -5.274% | -4.993% | -4.223% | -4.092% | -5.781% | -5.07% | -5.687% | -4.617% | -1.84% | -2.891% | -1.802% | -2.234% | -2.515% | -2.271% | -2.102% | -2.309% | -1.746% | -1.633% | -2.665% | -2.102% | -6.569% | -7.935% | -7.045% | -6.196% | -4.694% | -4.378% | -5.875% | -5.445% | -8.033% | -5.354% | -3.289% | -3.038% | -3.274% | -0.8654% | -1.715% | -2.599% | -4.52% | -2.838% | -2.609% | -4.89% | -8.784% | -5.62% | -6.89% | -4.837% | -5.38% | -9.31% | -9.45% | -9.688% | -14.81% | -6.503% | -5.805% | 2.681% | 0.8684% | 1.071% | 1.911% | 2.638% | 2.027% | -0.1575% | 2.364% | 2.766% | 0.1076% | -0.05686% | -0.08906% | 1.655% | 0.1802% | -2.406% | -0.003575% | 2.45% | 1.074% | 1.868% | 2.946% | 3.13% | 3.219% | 3.988% | 2.611% | 1.393% | 2.108% | 0.877% | 1.621% | -0.4139% | 1.45% | 1.98% | 3.031% | 2.604% | 1.82% | 2.39% | 2.382% | 2.432% | 1.753% | 2.724% | 1.014% | 2.57% | 5.22% | 2.535% | 4.151% | 3.065% | 3.245% | 4.365% | 3.271% | -0.02067% | 0.8965% | 1.7% | -4.808% | 3.869% | 0.971% | 3.63% | -5.33% | -0.431% | 3.236% | 3.1% | 2.397% | 3.585% | 4.143% | 3.681% | 1.629% | 3.57% | 0.01352% | 1.963% | 1.86% | 3.972% | 2.373% | 4.202% | 1.535% | 3.288% | 2.674% | 4.074% | 1.852% | 1.475% | 1.373% | 2.074% | 3.245% | 2.33% | 1.732% | 4.279% | 3.134% | 4.122% | 3.687% | 1.494% | 3.061% | 3.108% | 6.093% | 2.236% | 3.707% | -0.09761% | 3.664% | 1.458% | -1.098% | -3.816% | 2.262% | -34.34% | 1.569% | 3.744% | 5.339% | 2.468% | 0.728% | 2.338% | 0.9901% | 1.018% | 1.121% | 1.43% | 1.973% | 3.359% | 3.677% | 2.02% | 2.638% | 2.881% | 2.984% | 1.36% | 3.141% | 0.09979% | 2.881% | 2.704% | 3.293% | 3.284% | 2.601% | 3.425% | 1.683% | 3.256% | 1.149% | 3.134% | 0.7841% | 1.908% | 2.962% | 2.235% | 2.756% | -0.07939% | 3.059% | 2.832% | 2.03% | 2.398% | 3.926% | 1.867% | 1.375% | 4.279% | -5.212% | 1.386% | 1.183% | 2.242% | 1.256% | 6.213% | -3.578% | 2.356% | 3.737% | -4.425% | 3.946% | 2.547% | -4.251% | -2.915% | -2.484% | -0.6071% | -2.679% | -1.899% | -0.835% | -2.735% | 0.3434% | 1.271% | 2.191% | 2.473% | 2.045% | 1.001% | 2.91% | 0.223% | 3.144% | 1.248% | 1.393% | 1.238% | -1.601% | 0.04703% | -2.175% | -0.03631% | 2.2% | 3.289% | 0.1878% | 0.7693% | 1.559% | -0.3512% | 4.719% | 0.3434% | 0.26% | 0.05629% | -0.6104% | 1.362% | -0.1937% | 0.2045% | 0.7415% | -1.159% | -2.544% | 1.916% | 1.829% | -2.113% | 3.058% | -0.8012% | 0.4812% | 3.87% | 3.26% | 1.789% | 3.278% | 3.144% | -0.3351% | 0.9484% | 1.157% | 1.972% | 3.617% | 2.882% | 2.542% | 4.468% | 2.765% | -0.01172% | -5.021% | -0.5454% | -0.6297% | -2.755% | -1.575% | 0.1943% | -1.257% | -2.334% | 1.028% | 1.151% | 0.7748% | 1.393% | 1.419% | -0.1934% | -0.449% | -0.411% | 0.7297% | 0.0289% | 0.04769% | 0.3389% | 5.796% | -4.941% | -0.8542% | 1.072% | -0.06505% | 1.592% | 0.912% | 2.301% | 2.854% | 1.124% | 0.7517% | -1.694% | 1.645% | 0.09333% | -0.1011% | -0.7216% | 0.4063% | -1.059% | -3.648% | -1.831% | -1.057% | -0.8526% | 0.1582% | -0.8605% | -1.74% | -1.444% | -1.629% | -1.703% | 0.2623% | -1.728% | -0.4053% | -1.28% | 2.492% | 4.622% | 1.316% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100% | -100%
2025-04-16 | -9.023% | -10.8% | -8.428% | -8.384% | -8.34% | -11.58% | -6.279% | -10.64% | -7.683% | -7.18% | -7.18% | -7.815% | -7.092% | -6.873% | -6.063% | -5.932% | -8.217% | -7.042% | -7.552% | -6.611% | -3.655% | -4.903% | -3.59% | -4.115% | -4.049% | -4.115% | -3.699% | -3.699% | -3.064% | -3.13% | -4.203% | -3.458% | -7.859% | -9.069% | -8.632% | -7.733% | -6.304% | -6.028% | -7.355% | -6.926% | -9.676% | -6.735% | -4.252% | -4.079% | -4.459% | -1.851% | -2.754% | -3.619% | -4.937% | -3.59% | -3.988% | -6.311% | -14.71% | -6.21% | -7.782% | -5.969% | -6.532% | -10.55% | -10.42% | -22.01% | -2.911% | -11.79% | -14.92% | 1.907% | -0.2272% | 0.2637% | 0.5805% | 1.907% | 0.2276% | -1.474% | 0.1817% | 1.498% | -1.523% | -1.165% | -1.733% | -0.8105% | -2.614% | -4.276% | 3.263% | 2.335% | 0.6304% | 2.888% | 3.213% | 3.026% | 4.459% | 4.308% | 2.817% | 1.945% | 1.857% | 0.3412% | 0.1717% | 1.249% | 2.734% | 3.303% | 3.761% | 4.619% | 4.469% | 4.021% | 3.851% | 2.723% | 2.254% | 3.592% | 1.572% | 3.642% | 9.196% | 3.004% | 4.09% | 2.575% | 3.452% | 3.702% | 2.794% | 4.739% | 3.258% | 2.598% | 1.288% | 4.061% | 3.572% | 3.841% | 4.918% | -0.7357% | 2.335% | 2.395% | 2.317% | 3.307% | 3.223% | 2.166% | 1.348% | 2.814% | 3.293% | 2.625% | 1.887% | 3.831% | 2.286% | 3.392% | 0.4409% | 1.757% | 1.608% | 6.334% | 3.322% | 2.535% | -0.6659% | 5.117% | 4.948% | 3.801% | 2.196% | 5.905% | 4.28% | 5.236% | 4.34% | 2.703% | 3.341% | 3.981% | 5.857% | 2.904% | 3.592% | 2.744% | 2.844% | 4.18% | 3.791% | -1.394% | 3.223% | 1.807% | 2.475% | 3.213% | 4.758% | 2.734% | 3.367% | 5.3% | 3.957% | 3.793% | 3.738% | 4.131% | 3.967% | 5.54% | 5.715% | 4.535% | 6.086% | 5.835% | 6.217% | 3.845% | 6.082% | 3.641% | 6.425% | 5.813% | 6.217% | 5.42% | 5.868% | 6.053% | 4.393% | 6.425% | 3.804% | 5.398% | 2.22% | 3.793% | 5.084% | 4.327% | 4.189% | 2.552% | 5.791% | 5.517% | 5.246% | 5.027% | 5.829% | 5.471% | 6.733% | 6.859% | 4.84% | 4.698% | 6.152% | 5.007% | 4.702% | 9.89% | 4.658% | 4.745% | 6.016% | 1.292% | 6.534% | 4.892% | 3.279% | 0.8864% | 2.975% | 2.416% | 0.8665% | 0.9854% | 1.834% | 0.07932% | 1.553% | 2.894% | 2.681% | 2.681% | 3.09% | -3.396% | 6.435% | -2.219% | 6.356% | 4.292% | 2.999% | 2.148% | -3.677% | -0.2965% | 1.723% | -0.653% | 7.116% | 3.815% | 5.086% | -2.64% | 8.443% | -1.344% | 7.206% | 2.609% | 2.361% | 2.112% | 2.317% | 1.162% | 3.765% | 0.9888% | 2.598% | 2.213% | 1.101% | 2.769% | 2.583% | 3.982% | 4.469% | 3.219% | 3.753% | 3.708% | 2.828% | 2.138% | 3.172% | 4.626% | 0.63% | 0.4958% | 1.585% | 1.133% | 2.85% | 1.829% | 3.292% | 3.621% | 2.791% | -1.275% | -6.648% | -1.995% | -1.701% | -4.059% | -2.847% | -1.045% | -3.219% | -3.939% | -1.198% | -0.297% | -1.275% | -3.502% | -0.2371% | -1.888% | -2.267% | -1.885% | -1.599% | -2.077% | -2.176% | -1.957% | 23.4% | -7.677% | -2.713% | -1.288% | -2.746% | -1.097% | -1.595% | 0.9533% | 0.1872% | -1.785% | -1.787% | -3.316% | 0.9784% | -0.6098% | -1.193% | -1.755% | -1.98% | -2.611% | -4.314% | -1.447% | -1.855% | -1.844% | 0.7512% | -0.977% | -1.236% | -0.923% | -0.923% | -4.433% | 0.9532% | -1.526% | -0.1086% | -3.59% | 2.523% | 4.11% | -0.9592% | -7.879% | -4.606% | -7.684% | -5.135% | -5.459% | -5.708% | -5.902% | -5.362% | -4.044% | -5.535% | -3.806% | -3.602% | -4.26% | -7.064% | -4.634% | -3.522% | -5.138% | -8.484% | -7.998% | -4.52% | -6.973% | -3.947% | -4.488% | -6.233% | -4.649% | -7.015% | -7.129% | -4.234% | -4.747% | -3.692% | -3.885%
2025-04-17 | -6.198% | -8.544% | -5.251% | -5.08% | -5.613% | -9.617% | -2.424% | -6.832% | -4.337% | -3.861% | -2.947% | -3.747% | -4.013% | -3.518% | -2.928% | -2.832% | -4.194% | -3.492% | -3.842% | -2.794% | 0.2338% | -1.137% | -0.03287% | -0.9851% | -0.4519% | -0.2233% | 0.005219% | -0.509% | 0.4813% | 0.5575% | -0.6233% | -0.3376% | -6.222% | -7.241% | -6.178% | -5.417% | -3.773% | -3.432% | -5.461% | -4.795% | -7.994% | -5.431% | -3.644% | -4.367% | -3.283% | -1.371% | -1.734% | -2.213% | -5.266% | -1.67% | -1.967% | -4.091% | -12.72% | -4.474% | -5.727% | -4.034% | -4.257% | -8.204% | -8.117% | -8.726% | -13.38% | -5.367% | -5.138% | 3.238% | 1.763% | 2.594% | 2.665% | 1.737% | 2.799% | 2.362% | 2.796% | 1.746% | -0.1798% | -1.165% | -0.7524% | 1.945% | 0.1766% | 1.841% | 2.457% | 4.4% | 1.087% | 1.771% | 4.097% | 3.759% | 2.431% | 4.593% | 2.516% | 0.9572% | 1.278% | 3.186% | 3.663% | -1.915% | -0.006334% | 1.217% | 2.579% | 1.338% | -0.03305% | 2.154% | 1.572% | 1.392% | 1.147% | 2.44% | 1.324% | 1.677% | 7.22% | 1.304% | 3.863% | 1.616% | 2.067% | 3.984% | 3.663% | -0.5268% | 4.32% | 0.9203% | 1.902% | 2.397% | 1.772% | 3.368% | 5.554% | 1.356% | 3.516% | 2.761% | 2.09% | 3.895% | 5.381% | 4.791% | 2.657% | 4.852% | 2.509% | 1.781% | 1.234% | 3.021% | 0.7917% | 3.576% | 1.069% | 2.197% | 4.348% | 1.468% | -1.589% | 0.2105% | 1.616% | 0.5228% | 1.659% | 3.637% | 1.468% | 3.169% | 1.937% | 5.01% | 3.858% | 2.553% | 4.638% | 2.11% | 6.42% | 0.2626% | 2.466% | 2.622% | 3.594% | 0.2279% | 2.162% | -0.6569% | 2.119% | -3.45% | -0.1191% | 1.389% | 3.637% | 3.65% | 0.358% | 1.109% | -0.5636% | -0.6206% | -1.618% | -0.4686% | -0.07904% | 1.622% | 2.344% | 0.396% | 1.584% | 1.622% | 1.185% | 0.767% | 3.351% | -1.093% | 1.365% | 2.011% | 2.401% | 1.783% | 1.565% | 2.106% | 1.318% | 2.448% | 0.301% | 2.306% | 0.757% | 1.422% | 3.251% | 2.702% | 2.882% | -1.852% | 2.171% | 1.919% | 0.3205% | -1.852% | 3.785% | -0.4406% | 1.117% | 4.149% | 2.284% | 0.1252% | 1.175% | 3.314% | 1.048% | 6.153% | 0.768% | 2.787% | 4.534% | -0.2316% | 4.593% | 3.048% | -1.838% | -4.905% | -0.6104% | -1.947% | -3.674% | -2.03% | -2.429% | -4.919% | -1.265% | -0.117% | 2.097% | 1.899% | 2.61% | -0.0213% | 3.823% | 0.2324% | 3.004% | 1.209% | 1.396% | 1.88% | -0.1622% | -0.6697% | -0.5945% | -0.1435% | 2.906% | 3.577% | 0.5181% | -0.1904% | 2.008% | -0.7448% | 5.57% | 1.031% | -0.0213% | -0.2562% | 1.069% | 2.403% | 0.05387% | -0.04949% | 0.4297% | 0.9324% | -1.272% | 1.331% | 0.5863% | -1.049% | 1.023% | 1.631% | 2.579% | 4.269% | 4.609% | 1.82% | 3.776% | 1.196% | -4.703% | 1.902% | 1.222% | 1.705% | 5.021% | 4.134% | 0.8252% | 5.798% | 2.843% | -1.124% | -4.649% | -1.59% | -0.7631% | -3.452% | -2.017% | -0.4781% | -2.388% | -2.806% | -0.193% | -1.039% | -0.3736% | -2.378% | 0.3381% | 0.1685% | -0.3702% | -1.03% | -0.1121% | -0.5007% | -0.4816% | -0.2814% | -31.37% | -3.256% | -0.7295% | 1.12% | -0.09074% | 2.086% | 0.5194% | 1.289% | 3.291% | 1.834% | -0.3699% | -4.769% | 0.6274% | -1.327% | -1.553% | -1.666% | -0.5797% | -1.877% | -3.366% | -3.454% | -1.643% | -1.682% | -0.6885% | -2.276% | -2.662% | -2.417% | -2.944% | -3.648% | -1.249% | -2.422% | -0.9816% | -2.067% | 1.169% | -0.2515% | -1.061% | -0.05889% | 1.454% | 0.9653% | 0.9747% | -0.06828% | 0.1384% | -1.186% | -0.322% | -0.04009% | -1.553% | 0.5674% | 0.6365% | -0.867% | -1.607% | -0.7942% | 0.7154% | 0.1611% | -0.1153% | -0.5381% | 1.811% | -1.238% | 0.5425% | -0.5475% | -1.337% | -0.4629% | -1.001% | -0.1726% | 1.052% | 0.7647% | 0.9226% | 0.7548%
2025-04-18 | -5.878% | -8.487% | -5.052% | -5.276% | -5.483% | -8.554% | -2.686% | -7.418% | -4.428% | -4.284% | -3.373% | -4.092% | -4.348% | -4.06% | -3.261% | -3.229% | -4.734% | -4.447% | -4.764% | -3.709% | -0.6545% | -1.998% | -0.6864% | -1.694% | -1.422% | -0.9903% | -1.07% | -1.918% | -0.7984% | -0.5745% | -1.438% | -1.006% | -5.308% | -6.467% | -5.945% | -5.171% | -3.69% | -3.505% | -4.636% | -4.532% | -6.939% | -4.749% | -2.458% | -2.659% | -2.767% | -0.4379% | -2.219% | -3.02% | -6.323% | -2.685% | -2.296% | -4.4% | -13.29% | -5.493% | -6.696% | -5.884% | -5.474% | -9.46% | -9.167% | -9.878% | -13.59% | -5.994% | -5.546% | 1.499% | -0.1837% | 1.567% | 1.222% | 0.45% | 1.832% | -1.145% | 2.766% | 0.8724% | -0.8901% | -1.891% | -0.9557% | 1.696% | 0.4245% | 0.5082% | 1.652% | 3.924% | -0.3803% | 0.3337% | 3.698% | 2.298% | 0.8433% | 3.508% | 0.8889% | -0.9913% | 2.489% | 1.164% | 0.9379% | -4.284% | -1.895% | -0.2565% | 0.887% | -0.3585% | -2.152% | 2.089% | 0.1805% | -0.2684% | 0.2417% | 0.8578% | 0.6054% | -0.5624% | 3.269% | -0.2492% | 2.074% | 0.6903% | 0.2752% | 2.533% | -0.5041% | 2.307% | 3.531% | -0.8166% | -0.4386% | 1.557% | 0.9015% | 2.671% | 0.6102% | 4.281% | 2.853% | 0.4354% | 1.521% | 3.668% | 4.594% | 3.982% | 2.067% | 3.888% | 1.419% | 0.8214% | 0.3116% | 1.921% | -0.1181% | 2.497% | 0.1149% | 1.069% | 0.5768% | -2.915% | -0.403% | 1.28% | 2.628% | 1.2% | 2.132% | 4.485% | 1.55% | 3.494% | 1.448% | 5.077% | 2.56% | 1.293% | 2.853% | 1.251% | 4.776% | -0.9193% | 0.8287% | 0.9671% | 2.067% | 1.404% | 0.836% | 0.8724% | 0.7049% | 0.8651% | 1.521% | -0.3084% | 2.14% | 2.054% | 0.6917% | 1.753% | 0.7874% | 0.931% | 0.1812% | 1.665% | 2.359% | 3.922% | 3.938% | 1.808% | 1.601% | 1.944% | 2.136% | 1.287% | 3.44% | -1.517% | 1.816% | 1.761% | 2.654% | 3.196% | 2.064% | 2.957% | 0.7794% | 2.502% | 0.3168% | 2.175% | 0.2849% | 1.721% | 3.046% | 2.15% | 3.364% | -1.979% | 1.996% | 2.759% | -0.667% | -0.04881% | 2.824% | -0.9069% | 0.6139% | 3.088% | 1.406% | -0.8372% | 1.317% | 2.252% | 0.1169% | 4.496% | -0.6929% | 1.433% | 3.049% | 0.5912% | 3.641% | 6.767% | -3.282% | -3.031% | -2.219% | -3.181% | -5.404% | -3.562% | -4.427% | -6.692% | -1.116% | -0.536% | 1.93% | 0.9362% | 1.342% | 0.09011% | 2.245% | -1.022% | 2.369% | 1.085% | 1.226% | 0.4392% | -2.774% | -0.9749% | -3.01% | -1.314% | 1.574% | 2.361% | -0.9525% | -0.05979% | 0.6794% | -1.669% | 3.546% | 0.08222% | -0.7935% | -0.6988% | -1.811% | 1.1% | -1.527% | -0.5253% | -0.4227% | -0.4456% | -0.9739% | 1.262% | 0.6516% | 0.208% | 0.5082% | 1.054% | 2.254% | 3.764% | 3.776% | 0.7723% | 2.732% | 0.7946% | -6.033% | 1.564% | -2.502% | 1.219% | 4.162% | 3.481% | -0.1064% | 4.915% | 2.107% | 0.9071% | 0.253% | 0.2929% | -0.1299% | -2.3% | -0.8718% | 1.122% | -0.8% | -1.135% | 1.162% | -0.861% | 1.25% | 1.322% | 1.924% | 1.178% | 1.279% | 0.7469% | 1.831% | 0.9633% | 0.8833% | 1.291% | -9.867% | 0.5071% | 0.4591% | 1.251% | 0.4751% | 3.348% | 1.356% | 1.019% | 3.649% | 2.276% | 0.9031% | -3.809% | 3.431% | 1.447% | 0.8238% | 0.1769% | 1.162% | 0.01412% | -3.87% | -2.441% | 1.292% | 1.135% | 1.605% | -0.5489% | 0.04277% | -0.2176% | -0.9592% | -1.093% | 0.3924% | 0.6132% | 0.4806% | 1.077% | 2.568% | 1.06% | 1.475% | 0.5556% | 2.315% | 1.344% | 1.881% | 0.9895% | 2.354% | 0.7922% | 2.26% | 2.425% | 1.344% | 3.355% | 3.546% | 1.873% | 1.584% | 1.955% | 2.369% | 0.458% | 0.3189% | 0.1611% | 3.57% | -0.7092% | 2.039% | 0.08903% | 0.8617% | 1.045% | 0.8368% | 1.309% | 3.485% | 2.61% | 3.504% | 3.057%
2025-04-19 | -6.933% | -8.984% | -5.977% | -5.858% | -6.587% | -9.669% | -3.792% | -8.451% | -5.824% | -5.4% | -4.689% | -5.4% | -5.299% | -5.265% | -4.468% | -4.231% | -5.898% | -5.452% | -6.163% | -4.943% | -2.045% | -3.282% | -2.062% | -2.74% | -2.977% | -2.638% | -2.418% | -2.638% | -2.129% | -2.096% | -3.197% | -2.502% | -6.824% | -8.039% | -7.129% | -6.487% | -4.81% | -4.596% | -6.231% | -5.845% | -7.79% | -5.396% | -3.274% | -3.487% | -3.814% | -1.227% | -1.972% | -3.077% | -4.762% | -3.431% | -3.614% | -5.895% | -14.62% | -6.489% | -7.691% | -6.699% | -5.753% | -9.75% | -9.839% | -10.19% | -14.87% | -7.117% | -6.648% | 2.28% | 1.145% | 1.042% | 2.357% | 1.771% | -0.4909% | -0.383% | 2.504% | 1.67% | -0.1669% | -1.478% | -0.5374% | 1.49% | 0.08577% | -4.822% | -5.825% | 2.025% | -0.1283% | 0.615% | 2.797% | 2.822% | 1.717% | 4.169% | 1.95% | 0.3208% | 2.079% | 1.539% | 1.732% | -1.124% | 1.061% | 1.74% | 3.222% | 2.087% | 0.2691% | 2.01% | 2.265% | 2.797% | 1.7% | 2.751% | 1.394% | 1.91% | 8.394% | 1.477% | 4.48% | 1.832% | 2.836% | 4.295% | 3.646% | 4.21% | 3.431% | 0.4651% | 1.323% | 1.91% | -2.405% | 2.766% | 3.523% | 3.315% | 2.921% | 2.581% | 1.756% | 3.023% | 3.237% | 2.782% | 0.69% | 2.666% | 1.755% | 1.169% | 0.9061% | 2.712% | 0.6359% | 3.137% | 0.6051% | 2.018% | -2.747% | 3.006% | -0.1854% | 1.253% | 1.246% | 1.57% | 2.049% | 2.628% | 1.94% | 3.917% | 2.164% | 3.701% | 3.345% | 1.143% | 2.7% | 2.18% | 5.469% | 0.02612% | 1.886% | 1.74% | 2.705% | 2.427% | -0.5451% | 0.057% | 1.346% | 1.748% | 0.9138% | 1.088% | 3.068% | 2.015% | 1.546% | 3.085% | 1.622% | 1.512% | 0.7091% | 2.155% | 2.78% | 3.812% | 3.854% | 2.053% | 3.076% | 3.347% | 3.677% | 1.661% | 2.482% | 0.231% | 3.279% | 2.806% | 3.66% | 3.727% | 2.772% | 3.727% | 1.91% | 3.491% | 1.208% | 3.431% | 1.022% | 2.299% | 2.939% | 2.22% | 2.655% | -0.7982% | 2.688% | 2.238% | 1.215% | 1.484% | 3.404% | 0.797% | 2.446% | 4.147% | 2.966% | 0.3747% | 3.033% | 2.119% | 0.9959% | 12.6% | 0.7532% | 20.9% | 1.545% | -6.046% | 19.19% | 8.721% | -23.68% | -0.834% | -1.01% | 0.5612% | -1.842% | -3.232% | -9.596% | -2.84% | 0.694% | 0.7578% | 2.045% | 2.168% | 1.852% | 0.8817% | 2.914% | 0.1459% | 3.072% | 0.8073% | 1.009% | 1.492% | 0.1543% | 0.1292% | -0.6568% | 0.1793% | 2.036% | 3.029% | -0.176% | 0.4135% | 1.088% | -0.1468% | 4.477% | -0.4979% | 0.1877% | -0.2053% | 0.3633% | 1.133% | 0.288% | 0.4636% | 0.8148% | 0.8616% | -1.24% | 1.393% | 0.9835% | 0.8379% | 0.8409% | 1.02% | 1.951% | 3.368% | 2.752% | 0.8279% | 2.689% | 1.094% | -2.325% | 0.9479% | -1.586% | 1.653% | 2.653% | 1.795% | 0.7287% | 3.599% | 2.107% | -2.723% | -0.7451% | -1.049% | -1.109% | -4.736% | -2.487% | -0.1364% | -1.937% | -3.248% | 0.3794% | -0.329% | 0.2779% | 1.276% | 0.8089% | -1.224% | -1.126% | -0.7547% | 0.4455% | -2.078% | -0.2451% | 0.07723% | -15.82% | -0.6354% | -0.9068% | 0.968% | -0.3215% | 0.9341% | 0.6286% | 0.8021% | 2.584% | 0.7911% | -0.5974% | -3.875% | 1.306% | -0.13% | -0.3892% | -0.9244% | -0.04335% | -2.047% | -2.438% | -1.597% | -1.537% | -1.317% | 0.02883% | -1.418% | -1.919% | -1.159% | -1.827% | -3.057% | 0.08508% | -1.835% | -0.5799% | -1.511% | 1.949% | 0.9653% | -0.773% | 0.6643% | 3.399% | 1.843% | 2.646% | 1.124% | 2.136% | 1.066% | 2.061% | 2.579% | 1.066% | 1.808% | 1.843% | 1.626% | -0.3378% | 1% | 2.291% | 1.684% | -0.916% | 1.383% | 3.055% | 1.045% | 2.529% | 2.099% | -2.424% | 1.751% | 0.2805% | 0.658% | 2.389% | 2.906% | 2.827% | 2.344%
2025-04-20 | -5.669% | -7.612% | -4.873% | -4.848% | -5.971% | -8.681% | -2.592% | -7.841% | -5.447% | -4.973% | -3.776% | -4.524% | -4.898% | -4.848% | -4.275% | -3.477% | -5.196% | -4.251% | -4.848% | -3.801% | -0.9327% | -2.005% | -1.132% | -2.13% | -1.581% | -1.432% | -1.332% | -1.432% | -0.4089% | -0.4089% | -2.005% | -1.681% | -6.195% | -7.769% | -6.824% | -5.853% | -4.12% | -4.094% | -5.971% | -4.986% | -6.819% | -4.473% | -2.967% | -2.243% | -2.532% | -0.06468% | -1.144% | -2.117% | -4.935% | -2.496% | -2.391% | -5.458% | -13.66% | -5.299% | -6.53% | -4.227% | -4.883% | -8.458% | -8.411% | -8.902% | -14.15% | -5.531% | -5.77% | 3.142% | 2.085% | 2.665% | 3.324% | 3.017% | 2.346% | 0.5403% | -0.5958% | -0.9366% | -0.02777% | -0.9286% | 0.4039% | 2.058% | 0.7277% | 2.006% | 2.642% | 3.38% | 0.7561% | 2.001% | 3.619% | 3.531% | 2.96% | 4.338% | 2.64% | 1.459% | 3.483% | 2.335% | 2.778% | 0.1994% | 2.358% | 2.96% | 4.38% | 3.096% | 2.039% | 3.414% | 3.176% | 3.519% | 2.319% | 3.687% | 2.243% | 2.971% | 8.708% | 2.278% | 5.073% | 2.756% | 3.903% | 5.493% | 4.789% | 4.744% | 4.479% | 1.571% | 1.801% | 2.915% | -1.698% | 3.494% | -2.925% | 4.051% | 3.301% | 2.96% | 2.01% | 3.459% | 4.528% | 4.039% | 1.994% | 4.062% | 2.142% | 2.188% | 1.688% | 3.46% | 1.858% | 3.858% | 1.301% | 2.574% | -1.992% | 3.38% | -0.2077% | 0.5403% | 1.097% | 1.029% | 1.79% | 2.665% | 1.915% | 3.801% | 2.449% | 4.754% | 3.047% | 1.298% | 3.145% | 2.426% | 5.325% | 0.7902% | 2.744% | 2.131% | 3.165% | 2.846% | 2.028% | 1.779% | 2.051% | 2.29% | 1.517% | 2.481% | 4.653% | 2.165% | -1.244% | 0.4353% | -1.381% | -1.406% | -1.444% | -1.033% | -0.361% | 0.4602% | 1.456% | -0.07484% | 0.51% | 1.033% | 1.095% | -0.1476% | 1.918% | -1.6% | 0.9579% | 0.9828% | 1.704% | 1.381% | 0.8832% | 1.543% | 0.2736% | 1.095% | -0.3735% | 1.48% | -0.1868% | 0.51% | 1.355% | 1.015% | 1.303% | -0.5533% | 2.792% | 11.12% | -0.1321% | 2.132% | 3.471% | 0.5576% | 2.233% | 4.112% | 2.66% | 0.2903% | 1.982% | 1.965% | 0.4691% | 10.91% | 1.677% | 20.55% | 3.781% | 3.469% | 3.749% | 2.593% | -1.025% | -1.23% | 1.366% | -1.206% | -4.534% | -2.437% | -1.886% | -4.021% | -1.448% | -1.143% | 1.288% | 1.042% | 0.732% | -1.001% | 2.205% | -0.3238% | 2.244% | -0.1079% | 0.5382% | 1.184% | -2.662% | -1.161% | -3.831% | -0.8899% | 1.081% | 2.063% | -0.9865% | -1.591% | 0.3961% | -0.9637% | 3.626% | -0.9022% | -0.9145% | -1.333% | -0.7668% | 0.5991% | -1.542% | -0.8037% | -0.6069% | 1.289% | -3.451% | 1.851% | 1.786% | -1.383% | 2.216% | -2.177% | 2.403% | 3.532% | 3.233% | 1.278% | 3.462% | 1.932% | -1.204% | 1.226% | -0.234% | 0.9883% | 3.267% | 3.368% | 1.447% | 3.98% | 2.722% | -4.591% | -0.06239% | -0.7592% | -0.697% | -3.658% | -1.667% | 0.1616% | -2.103% | -2.986% | 0.4726% | -1.062% | -4.455% | 0.6095% | 0.7538% | -0.1476% | -1.193% | -0.9438% | -0.02933% | -4.89% | -0.7451% | -0.4579% | -2.919% | -1.244% | -1.756% | 0.1538% | -1.07% | 0.8386% | -0.6951% | 0.1367% | 1.551% | -0.2391% | 1.494% | -3.126% | 1.721% | -0.2992% | -0.6315% | -1.333% | -0.1868% | -2.209% | -1.259% | -2.035% | -2.007% | -1.697% | -0.3361% | -1.308% | -2.92% | -1.604% | -1.751% | -1.111% | -0.1608% | -2.292% | -1.18% | 1.094% | 1.649% | 0.7837% | 1.779% | -2.859% | 0.2053% | -1.087% | 0.4391% | -1.911% | -0.2746% | -0.2008% | 0.1069% | 1.03% | -0.4469% | 0.241% | -0.1208% | 0.5376% | -0.9436% | 0.1764% | 1.766% | -2.294% | -5.664% | -1.05% | -0.06909% | -1.096% | -0.3361% | -0.5554% | -6.788% | -0.41% | -1.904% | -0.1466% | 1.396% | 1.688% | 1.533% | 1.197%
2025-04-21 | -6.362% | -8.38% | -5.623% | -5.439% | -6.305% | -9.732% | -3.493% | -8.131% | -5.66% | -5.07% | -4.775% | -5.31% | -5.052% | -5.052% | -4.388% | -4.204% | -5.78% | -5.178% | -5.9% | -4.757% | -2.194% | -3.134% | -2.176% | -2.692% | -2.968% | -2.784% | -2.452% | -2.452% | -2.047% | -1.881% | -3.153% | -2.434% | -6.342% | -7.701% | -6.944% | -5.993% | -4.421% | -4.382% | -5.974% | -5.411% | -7.467% | -5.068% | -3.094% | -3.064% | -3.029% | -0.5947% | -1.481% | -2.573% | -4.202% | -3.215% | -2.994% | -5.62% | -13.98% | -5.964% | -7.445% | -5.124% | -5.566% | -9.208% | -9.283% | -9.881% | -14.66% | -7.015% | -6.116% | 2.199% | 0.7628% | 0.6555% | 1.913% | 2.82% | -1.368% | -0.2365% | 2.224% | 2.686% | 0.2506% | -2.088% | 0.007021% | 3.771% | 0.02267% | 0.6116% | 1.67% | 1.569% | 0.6788% | 1.618% | 2.232% | 2.56% | 3.013% | 2.929% | 2.2% | 1.062% | 1.519% | 0.914% | 1.107% | -0.9083% | 1.3% | 1.435% | 2.803% | 2.501% | 1.872% | 1.258% | 1.913% | 2.121% | 0.8479% | 2.619% | 0.1292% | 2.644% | 7.363% | 2.14% | 4.113% | 3.123% | 3.148% | 4.718% | 3.643% | 4.433% | 2.781% | 1.445% | 1.342% | 3.492% | 2.249% | 3.173% | 3.139% | 3.064% | 2.82% | 2.493% | 1.515% | 2.683% | 3.257% | 2.887% | 0.7544% | 2.677% | 1.527% | 1.267% | 1.107% | 3.265% | 1.871% | 3.509% | 0.9392% | 2.232% | -0.1793% | 4.256% | 2.035% | 1.401% | 1.124% | 2.619% | 2.283% | 2.661% | 1.863% | 3.945% | 3.013% | 3.561% | 3.131% | 2.718% | 2.589% | 3.064% | 7.241% | 1.779% | 1.813% | 1.796% | 2.988% | 2.812% | 2.761% | 1.325% | 1.594% | 1.771% | 0.8804% | 3.429% | 4.617% | 1.726% | 0.6928% | 2.358% | 0.9871% | 0.9228% | 0.886% | 1.272% | 1.999% | 2.965% | 3.553% | 1.87% | 2.569% | 2.771% | 3.02% | 1.353% | 2.968% | 0.08413% | 2.974% | 2.707% | 3.424% | 3.158% | 2.496% | 3.351% | 1.668% | 3.057% | 0.8124% | 3.057% | 0.6928% | 1.916% | 2.695% | 2.029% | 2.425% | -0.4026% | 2.731% | 2.168% | 1.846% | 2.189% | 3.343% | 1.807% | 3.243% | 4.061% | 3.459% | 0.7556% | 2.536% | 1.715% | 0.5691% | 10.53% | 1.512% | 1.777% | 3.276% | 3.628% | 3.363% | 7.821% | -1.305% | -0.9631% | 1.548% | -0.8018% | -2.123% | -1.592% | -8.576% | -2.348% | 0.06965% | 0.7295% | 1.605% | 1.748% | 1.137% | 0.08661% | 2.359% | -0.1226% | 2.617% | 0.6688% | 0.9362% | 1.032% | -1.924% | -0.09532% | -2.397% | -0.05893% | 1.28% | 2.35% | -0.8594% | -0.25% | 1.06% | -0.2863% | 4.776% | -0.4046% | 0.123% | -0.3682% | -0.8139% | 0.9508% | -0.3773% | 0.1685% | 0.6051% | 0.4691% | -1.427% | 1.184% | 1.349% | 2.586% | 2.945% | 1.672% | 2.364% | 3.117% | 2.396% | 1.159% | 2.319% | 2.373% | -0.9677% | -0.2703% | 0.4822% | 0.7404% | 2.399% | 1.21% | 1.956% | 3.273% | 2.058% | -2.747% | -1.073% | -1.165% | -1.073% | -3.602% | -2.416% | -0.2729% | -2.057% | -2.885% | 0.748% | 0.9559% | -1.772% | 1.337% | 0.8216% | -1.004% | -0.994% | -0.7752% | 0.4287% | -2.683% | -0.2925% | 0.05824% | -1.257% | -0.6985% | -0.9477% | 0.6304% | -0.394% | 1.141% | 0.4182% | 2.247% | 2.357% | 0.4836% | -0.4296% | -3.359% | 0.8988% | -0.6866% | -0.9231% | -1.36% | -0.4435% | -2.146% | -2.288% | -1.91% | -2.149% | -2.101% | -0.632% | -2.015% | -3.079% | -1.933% | -2.415% | -3.552% | 0.204% | -2.521% | -0.9167% | -1.967% | 1.748% | 1.815% | -2.56% | -1.778% | 0.8325% | -0.541% | -0.03165% | -0.9504% | 0.3686% | -0.35% | -0.3045% | 1.014% | -0.3045% | 0.4873% | 0.3822% | 0.4323% | -1.372% | 0.0575% | 1.27% | -0.4166% | -3.579% | -0.5137% | 1.815% | -0.4339% | 0.4505% | 0.5472% | -5.167% | 0.07751% | -1.289% | -0.6302% | 0.9804% | 1.376% | 1.404% | 1.28%
2025-04-22 | -9.342% | -13.25% | -8.566% | -8.987% | -9.24% | -13% | -5.954% | -11.68% | -7.47% | -8.397% | -7.47% | -7.976% | -7.639% | -8.144% | -6.628% | -6.965% | -9.076% | -6.592% | -6.459% | -6.375% | -2.414% | -3.509% | -2.161% | -3.088% | -2.161% | -2.751% | -1.656% | -2.077% | -0.8128% | -2.245% | -2.498% | -3.004% | -8.65% | -11.29% | -11.38% | -9.431% | -7.834% | -9.076% | -9.661% | -7.657% | -11.6% | -6.773% | -4.73% | -6.001% | -4.781% | -2.445% | -2.182% | -2.143% | -5.964% | -2.968% | -3.197% | -7.96% | -7.863% | -6.189% | -7.199% | -6.666% | -5.657% | -11.38% | -9.997% | -11.04% | -7.639% | -6.741% | -9.64% | 2.64% | 0.4903% | 1.535% | 0.9126% | 2.601% | 0.7235% | 0.02973% | 1.757% | 3.139% | -0.1622% | 0.1935% | -0.4693% | 0.7643% | -1.001% | 1.987% | 3.024% | 3.446% | 1.335% | 3.403% | 3.484% | 3.212% | 4.521% | 3.774% | 2.891% | 2.261% | 1.335% | 0.8742% | 1.22% | -2.235% | -0.5844% | -0.08542% | 0.6823% | 2.064% | 1.562% | 2.294% | 1.22% | 0.001817% | -0.239% | 1.834% | -0.4662% | 2.563% | 4.214% | 2.333% | 3.254% | 2.41% | 1.181% | 3.561% | 3.216% | 4.444% | 2.704% | 2.45% | 2.218% | 5.25% | 4.252% | 4.329% | 5.519% | 4.137% | 3.408% | 3.791% | 2.69% | 4.015% | 5.135% | 4.29% | 2.294% | 4.367% | 2.717% | 2.486% | 2.294% | 4.828% | 3.638% | 4.828% | 1.795% | 2.793% | 0.9649% | 4.789% | -0.7687% | 4.022% | 1.335% | 3.638% | 3.715% | 3.369% | 1.719% | 4.367% | 3.484% | 3.654% | 3.44% | 0.7643% | 1.968% | 3.446% | 5.773% | 3.024% | 4.022% | 2.102% | 3.331% | 3.983% | 4.482% | 2.102% | 2.486% | 2.486% | 1.603% | 4.911% | 6.709% | 1.888% | -1.836% | 1.317% | -2.299% | -1.879% | -1.416% | -2.761% | -0.9116% | 1.022% | 3.166% | 1.317% | -0.1969% | 2.115% | 3.503% | -0.9894% | 2.557% | 1.848% | 2.41% | 3.376% | 3.04% | 1.653% | 2.325% | 2.325% | 1.989% | 1.148% | 0.2655% | 1.064% | 0.1394% | 0.6018% | 0.2907% | -0.3272% | 3.646% | -0.1584% | 2.26% | 2.638% | 1.457% | 2.081% | 2.89% | 2.121% | 3.448% | 4.532% | 3.866% | 2.078% | 2.713% | 1.783% | 1.36% | 0.1677% | 3.285% | 3.249% | 2.638% | 3.833% | 3.03% | 0.7021% | -0.4985% | -0.589% | 0.7267% | -1.574% | -2.264% | -1.574% | -0.6466% | -2.12% | -0.8193% | 1.84% | 2.288% | 1.284% | -0.1128% | -2.042% | 1.764% | -0.004735% | 3.292% | 0.3237% | 0.9786% | 1.153% | -2.666% | -2.79% | -2.915% | -1.003% | 6.741% | -65.03% | 4.384% | 1.118% | 1.764% | -2% | 0.8476% | -0.67% | 0.7021% | -0.5037% | 4.527% | 0.7437% | -2.957% | -0.2126% | 0.03684% | 2.316% | 1.105% | 3.144% | 3.276% | 4.941% | 5.65% | 3.882% | 4.213% | 4.38% | 3.6% | 2.233% | 3.388% | 4.833% | 1.85% | 1.655% | 3.38% | 2.667% | 3.224% | 2.06% | 3.258% | 4.639% | 3.586% | 1.232% | 0.1394% | -2.593% | -2.93% | -2.719% | -1.164% | -0.02876% | -1.458% | -2.972% | 1.989% | 0.9893% | 0.1814% | 1.485% | 3.116% | 0.9087% | 1.262% | -2.73% | 0.8253% | -0.8265% | -1.375% | 1.283% | 1.073% | -0.06721% | -2.345% | -0.3203% | 0.7343% | -0.8886% | -0.6156% | 3.461% | 1.836% | -0.06239% | 4.34% | 0.3351% | 3.337% | 1.45% | 0.1616% | -0.5868% | 1.924% | -2.576% | -1.793% | 3.11% | -3.082% | 0.4547% | 6.565% | 5.026% | 4.527% | 2.324% | 3.529% | 1.908% | 5.277% | 1.11% | 3.161% | -3.736% | 4.864% | 5.344% | 6.829% | 0.03684% | 1.742% | 2.906% | 1.45% | -1.585% | 1.243% | -0.8363% | 0.411% | 2.989% | -1.46% | 1.633% | 2.987% | 2.365% | -1.979% | -0.986% | 3.511% | 0.8079% | -2.042% | -2.167% | 1.241% | -1.454% | 0.7437% | 1.086% | -2.077% | -1.169% | -2.427% | 2.507% | 0.9625% | 2.376% | 3.904% | -0.06918%
2025-04-23 | -6.745% | -9.772% | -6.089% | -6.035% | -6.523% | -10.2% | -3.84% | -8.423% | -5.275% | -5.573% | -5.004% | -5.601% | -5.221% | -5.438% | -4.244% | -4.407% | -6.173% | -5.231% | -5.845% | -4.895% | -2.127% | -3.321% | -2.29% | -3.24% | -3.24% | -3.077% | -2.29% | -2.643% | -2.046% | -2.263% | -3.05% | -2.969% | -6.089% | -7.887% | -7.259% | -6.316% | -4.888% | -5.402% | -6.035% | -5.316% | -7.826% | -5.118% | -2.559% | -3.467% | -3.048% | -0.5574% | -1.047% | -1.913% | -5.466% | -3.097% | -2.738% | -5.64% | -6.271% | -5.699% | -7.44% | -5.833% | -5.403% | -9.805% | -9.571% | -10.41% | -5.818% | -7.15% | -6.309% | 2.075% | 0.3319% | 0.4214% | 1.209% | 2.346% | 1.54% | -0.06355% | 2.173% | 2.594% | 0.4803% | 0.2825% | 0.2825% | 1.766% | 0.04713% | -0.6939% | 2.038% | 1.593% | -1.992% | 1.564% | 2.544% | 2.489% | 2.594% | 3.032% | 2.089% | 0.9212% | 1.247% | 0.7645% | 1.074% | -0.459% | 0.9623% | 1.568% | 2.136% | 2.581% | 0.367% | 2.26% | 2.26% | 1.262% | 0.9387% | 2.322% | 0.2179% | 2.371% | 6.635% | 2.297% | 3.657% | 2.433% | 1.976% | 4.275% | 3.397% | 4.188% | 2.984% | 1.21% | -0.8422% | 2.989% | -2.77% | 3.175% | 3.323% | 2.964% | 2.742% | -1.942% | 1.998% | 2.954% | 3.558% | 3.113% | 1.123% | 3.125% | -2.325% | 1.902% | 1.716% | 3.83% | 2.198% | 4.324% | 1.815% | 2.68% | 0.2797% | 4.831% | 2.118% | 5.09% | 2.186% | 4.67% | 4.04% | 3.545% | 3.113% | 5.103% | -0.1006% | 4.582% | 6.077% | 0.09881% | 3.386% | 3.966% | 2.429% | 2.198% | 3.681% | 2.693% | 0.4432% | -0.1501% | -0.6321% | 2.384% | 2.742% | 2.334% | 1.667% | 3.187% | 5.14% | 0.3572% | 1.265% | 2.659% | 0.994% | 0.9534% | 0.8722% | 0.9534% | 0.7369% | 2.754% | 3.62% | 2.158% | 2.794% | 3.133% | 3.241% | 1.595% | 3.124% | 0.3443% | 2.903% | 3.052% | 3.458% | 2.849% | 2.456% | 2.889% | 1.874% | 2.984% | 1.035% | 2.632% | 0.6963% | 0.7775% | 2.021% | 0.7849% | 2.689% | 1.063% | 4.035% | 3.459% | 3.203% | 3.776% | 5.158% | 2.85% | 0.3906% | 5.798% | 5.268% | 3.024% | 4.57% | 3.686% | 3.141% | 2.964% | 3.142% | 3.487% | 4.26% | 5.215% | 4.554% | 3.271% | 1.139% | -3.314% | 2.664% | 1.113% | -0.5736% | -0.6377% | 0.3436% | -1.83% | -0.8223% | 0.3534% | 1.364% | 0.1272% | 0.8863% | -0.8253% | 2.728% | -0.008676% | 2.629% | 0.7879% | 0.9144% | 1.35% | -0.6781% | -0.8119% | -0.7985% | -0.2095% | 2.123% | -6.381% | 0.1694% | 0.7143% | 1.28% | -0.9056% | 1.659% | -0.04884% | 0.4197% | -0.02206% | 1.464% | 1.785% | -0.089% | 0.3662% | 1.022% | 1.465% | 0.08396% | 2.114% | 2.116% | -1.579% | 2.674% | -1.884% | 3.041% | 3.791% | 3.092% | 1.393% | 3.305% | 2.663% | -2.063% | 0.5857% | 0.0478% | 1.842% | 3.224% | 2.022% | 2.029% | 4.021% | 2.769% | -0.5626% | -1.415% | -2.349% | -2.39% | -3.229% | -2.796% | -0.6168% | -2.552% | -3.026% | 0.7233% | -1.213% | -0.2919% | 0.4932% | 0.9128% | -1.134% | -2.441% | -1.585% | -0.1678% | -1.12% | -1.269% | -0.9159% | -3.41% | -1.215% | -2.682% | 0.03482% | -0.9159% | -0.944% | -0.4949% | 1.319% | 1.467% | -0.3379% | -0.5897% | -3.533% | 0.4012% | -0.7985% | -1.642% | -2.285% | -0.8922% | -3.096% | -4.279% | -2.662% | -2.754% | -1.785% | -0.06223% | -1.521% | -2.204% | -2.392% | -1.749% | -2.418% | -0.371% | -3.064% | -0.5054% | -3.654% | 0.8863% | -1.096% | -1.813% | -0.6647% | 1.169% | 0.8214% | 0.8615% | -0.7584% | 0.9418% | -0.9056% | 0.6607% | 0.8883% | -0.5843% | 0.9847% | 1.111% | 1.076% | -0.862% | 0.1272% | 2.137% | -0.7073% | -1.24% | -1.24% | 1.266% | -1.346% | 0.7678% | -0.4517% | -1.841% | -0.1158% | -1.616% | -0.3226% | 1.21% | 1.21% | 2.053% | 1.336%
2025-04-24 | -6.926% | -9.728% | -5.955% | -6.256% | -7.09% | -10.73% | -3.173% | -8.617% | -5.932% | -5.747% | -4.219% | -5.562% | -5.793% | -6.025% | -4.891% | -5.423% | -6.585% | -5.05% | -4.451% | -4.266% | -0.6085% | -2.09% | -1.604% | -2.669% | -0.9326% | -1.835% | -1.558% | -2.345% | 0.0396% | -0.1687% | -2.229% | -2.02% | -7.599% | -8.607% | -7.901% | -6.78% | -5.464% | -5.732% | -7.298% | -6.512% | -9.242% | -6.574% | -4.483% | -6.017% | -4.833% | -2.768% | -2.851% | -3.966% | -4.66% | -3.947% | -4.755% | -7.121% | -7.678% | -6.737% | -8.023% | -5.902% | -5.999% | -10.01% | -9.633% | -10.32% | -6.256% | -7.537% | -7.981% | 4.365% | 2.615% | 2.881% | 3.701% | 4.997% | 2.848% | 1.508% | 3.711% | 5.335% | 1.845% | 1.888% | 1.202% | 2.517% | 0.2909% | 2.836% | 3.911% | 3.205% | 2.035% | 4.361% | 5.061% | 4.413% | 6.252% | 5.846% | 4.876% | 4.084% | 3.88% | 2.425% | 2.942% | 6.284% | 7.517% | 8.382% | 8.192% | 9.331% | 9.246% | 8.698% | 7.855% | 6.276% | 6.254% | 6.99% | 5.033% | 7.222% | 7.117% | 6.621% | 6.895% | 5.461% | 4.987% | 7.127% | 6.273% | 8.108% | 6.383% | 4.953% | 2.404% | 4.091% | 1.181% | 3.933% | 4.934% | 3.753% | 2.383% | 0.03164% | 1.647% | 3.223% | 2.088% | 0.9067% | -0.03161% | 1.202% | 1.297% | 0.5693% | -0.01053% | 2.351% | 0.8856% | 2.562% | -0.9067% | -0.5377% | -2.432% | 0.7275% | -1.21% | -2.667% | -3.057% | -0.6853% | -0.6536% | -1.497% | -2.056% | 0.1371% | 0.6958% | -2.454% | -0.1656% | -2.189% | -0.7738% | -0.2952% | 0.1823% | -0.1898% | 0.9067% | 0.04219% | -0.8118% | 1.771% | -3.458% | 0.1582% | 0.6748% | -0.7275% | -1.56% | 1.734% | 2.857% | -0.5909% | -2.37% | -0.6838% | -2.116% | -1.515% | -1.157% | -1.226% | -0.857% | 0.06679% | 0.8404% | -0.3489% | -0.6953% | -0.2912% | 0.7712% | -1.732% | -0.01404% | -2.244% | 0.7365% | 0.3555% | 0.8404% | 0.2169% | -0.118% | 0.598% | -0.8108% | 0.725% | -1.504% | 0.7827% | -1.377% | -0.7761% | 0.281% | -0.4222% | -0.09487% | -3.685% | -1.353% | -2.104% | -2.205% | -1.891% | -1.009% | -1.662% | -2.1% | 0.1599% | -4.227% | -1.563% | -0.4079% | -1.467% | -2.35% | -2.444% | -2.192% | -1.193% | -1.109% | -2.688% | -0.9908% | -2.911% | -2.142% | -3.981% | -1.732% | -3.005% | -3.803% | -3.856% | -4.084% | -3.851% | -0.397% | 0.7804% | 1.997% | 1.086% | 1.793% | 0.7944% | 2.968% | 0.1548% | 0.9897% | -0.4972% | 0.522% | 1.217% | -2.118% | -1.318% | -2.997% | -1.695% | -5.977% | -16.35% | -1.301% | -2.929% | -1.301% | -3.123% | -1.037% | -3.26% | -0.8159% | -1.867% | -2.963% | -1.627% | -1.889% | -1.638% | -1.181% | 1.358% | -0.06056% | 2.154% | 2.315% | 3.893% | 4.273% | 0.9218% | 3.308% | 3.691% | 2.801% | 1.456% | 2.546% | 3.343% | -0.06198% | -0.3776% | 1.288% | 0.7159% | 1.778% | 0.5127% | 2.113% | 2.72% | 2.198% | 2.723% | 1.649% | 1.245% | 2.145% | -0.5914% | 1.164% | 1.891% | -0.2681% | -0.7069% | 2.93% | 1.919% | 2.249% | 2.803% | 2.888% | 2.524% | 1.445% | 2.112% | 3.147% | 2.505% | 2.332% | 2.343% | 1.771% | 1.266% | 1.161% | 1.393% | 1.521% | 3.024% | 2.216% | 4.293% | 3.749% | 1.966% | 2.309% | -0.7235% | 4.076% | 1.948% | 1.331% | 0.486% | 1.906% | 0.1579% | -0.3248% | -0.2334% | 0.4501% | 1.277% | 2.53% | 0.8286% | 0.5546% | 0.6802% | -0.2677% | -1.787% | 2.53% | 0.2942% | 2.537% | -1.612% | 1.721% | 1.805% | -1.72% | 1.285% | 3.284% | 2.325% | 2.644% | 1.685% | 2.873% | 1.206% | 2.976% | 3.215% | 1.48% | 2.908% | 3.256% | 2.519% | 0.4229% | 2.045% | 3.412% | 1.947% | 0.6345% | 0.7601% | 2.644% | 0.8676% | 2.165% | 2.535% | 0.8817% | 1.422% | 1.026% | 1.361% | 2.455% | 3.004% | 3.532% | 2.968%
2025-04-25 | -6.306% | -8.616% | -5.61% | -5.496% | -6.309% | -9.387% | -3.521% | -8.227% | -5.528% | -5.089% | -4.699% | -5.284% | -4.91% | -5.187% | -4.098% | -4.016% | -5.621% | -5.177% | -5.967% | -4.813% | -2.082% | -3.366% | -2.098% | -2.569% | -2.992% | -3.057% | -2.407% | -2.569% | -1.903% | -1.903% | -2.992% | -2.293% | -6.292% | -7.658% | -6.837% | -5.912% | -4.492% | -4.441% | -5.821% | -5.313% | -7.235% | -5.069% | -2.94% | -3.117% | -3.29% | -0.6826% | -1.504% | -5.104% | -4.821% | -3.139% | -2.739% | -5.306% | -6.094% | -5.749% | -7.344% | -5% | -5.681% | -9.601% | -9.396% | -9.759% | -5.154% | -6.899% | -6.058% | 2.056% | 0.5381% | 0.6953% | 1.738% | 2.041% | 1.577% | -0.4986% | 2.049% | 1.738% | -0.01731% | -1.175% | -0.1802% | 1.508% | 0.1224% | 1.567% | 2.175% | 1.901% | 0.2789% | 1.764% | 3.174% | 2.909% | 2.552% | 1.539% | 2.058% | 0.7463% | 1.708% | 1.286% | 1.434% | -0.7652% | 1.338% | 1.975% | 3.108% | 2.323% | 0.7792% | 1.967% | 2.352% | 2.383% | 1.454% | 2.811% | 0.5548% | 2.315% | 5.329% | 2.115% | 4.389% | 2.278% | 2.782% | 4.655% | 4.004% | 4.366% | 3.771% | 0.7649% | 1.39% | 2.315% | 1.782% | 3.122% | -1.217% | 3.278% | 2.752% | 2.545% | 1.857% | 2.909% | 3.293% | 2.982% | 0.9676% | 2.848% | -0.3579% | 1.56% | 1.323% | 3.345% | 1.471% | 3.944% | 1.323% | -0.1284% | -0.01697% | 2.819% | -0.2972% | 1.056% | -0.4986% | 1.33% | 2.152% | 2.486% | 2.108% | 3.752% | -3.246% | 3.862% | 3.644% | 1.307% | 2.973% | 2.611% | 5.588% | -1.439% | 2.53% | -0.1284% | 1.819% | 3.271% | 0.4122% | 1.708% | 2.167% | 1.967% | 0.9824% | 1.991% | 4.048% | 2.22% | 0.8999% | 1.054% | 1.24% | 1.054% | -1.971% | 1.013% | 1.443% | 2.181% | 2.927% | 1.516% | 1.987% | 2.473% | 2.66% | 1.491% | 2.927% | -0.226% | 2.595% | 2.441% | 2.968% | 2.554% | 2.149% | 2.66% | 1.565% | 2.854% | 0.8755% | 2.992% | 0.908% | 1.695% | 2.462% | 1.976% | 2.121% | 0.06309% | 3.154% | 2.161% | 1.427% | 2.033% | 3.465% | 0.9541% | -1.416% | 3.815% | 3.132% | 0.1247% | 2.575% | 1.532% | 0.3341% | -1.532% | 1.719% | 2.027% | 3.677% | 1.353% | 3.434% | 2.012% | -1.102% | -1.367% | 1.101% | -1.048% | -2.417% | -2.42% | -1.369% | -3.767% | -0.0208% | 0.5228% | 1.673% | 2.119% | 1.302% | 0.1761% | 2.557% | 0.1119% | 2.65% | 1.033% | 1.235% | 1.344% | -0.8747% | -0.4095% | -1.613% | -0.3212% | 3.004% | 1.673% | -0.2727% | 0.537% | 1.504% | 0.05577% | 1.488% | 0.09587% | 0.3044% | -0.1207% | 0.03171% | 1.275% | 0.08785% | 0.3365% | 0.8499% | 0.1783% | -3.619% | 1.33% | 1.223% | 1.444% | 1.502% | 1.738% | 2.232% | 3.532% | 3.007% | 1.147% | 2.965% | 2.03% | -1.784% | -0.1574% | -0.8571% | 1.214% | 3.022% | 1.834% | 1.931% | 3.948% | 2.414% | -0.1545% | -0.5681% | -0.7465% | -0.2599% | -3.455% | -1.606% | 0.03206% | -1.858% | -2.766% | 0.9323% | -1.535% | 0.5025% | 0.9485% | 0.878% | -0.2717% | -0.5016% | -0.1974% | 0.8887% | 0.3897% | 0.17% | 0.04795% | -0.9315% | -0.3752% | -0.6845% | 0.52% | -0.6112% | 1.297% | 0.4874% | 1.443% | 1.593% | 0.6736% | -0.5085% | -3.753% | 1.449% | -0.4014% | -0.7223% | -1.083% | -0.178% | -1.912% | -2.254% | -2.379% | -1.334% | -1.208% | -0.3052% | -1.733% | -2.543% | -1.861% | -2.062% | -2.896% | -0.3941% | -2.218% | -0.3653% | -2.041% | 1.723% | 1.656% | -1.452% | -0.9148% | 1.588% | 0.529% | 1.219% | 0.07181% | 0.6975% | 0.4007% | 1.235% | 1.724% | 0.3365% | 1.218% | 1.656% | 1.099% | -0.2811% | 0.8306% | 2.111% | -0.5185% | -0.2651% | 0.03171% | 1.959% | -0.151% | 1.484% | 0.4386% | -0.7865% | 0.6493% | -0.4917% | 0.2832% | 1.98% | 2.06% | 2.153% | 2.128%
2025-04-26 | -6.364% | -8.701% | -5.786% | -5.755% | -6.196% | -9.202% | -3.656% | -8.4% | -5.424% | -5.062% | -4.857% | -5.345% | -5.062% | -5.235% | -4.164% | -4.337% | -5.717% | -5.237% | -6.038% | -4.889% | -2.164% | -3.456% | -2.054% | -2.731% | -3.156% | -3.298% | -2.7% | -2.967% | -2.306% | -2.212% | -3.377% | -2.605% | -6.322% | -7.624% | -6.878% | -6.065% | -4.806% | -4.723% | -5.833% | -5.634% | -7.55% | -5.307% | -2.845% | -3.318% | -3.47% | -0.8532% | -1.782% | -5.779% | -4.43% | -3.308% | -2.989% | -5.657% | -6.433% | -5.925% | -7.655% | -5.103% | -5.918% | -10.03% | -9.667% | -10.35% | -5.518% | -7.423% | -6.067% | 2.201% | 0.5156% | -0.3584% | 1.391% | 2.531% | 1.261% | -0.04386% | 2% | 2.624% | 0.5802% | -0.281% | 0.4582% | 1.71% | 0.2329% | 0.8384% | 1.204% | 1.391% | 0.6447% | 1.874% | 2.459% | 2.692% | 2.703% | 0.7878% | 2.258% | 0.9521% | 0.5228% | 0.9388% | 1.398% | -0.04386% | 2.079% | 1.936% | 2.861% | 2.99% | 1.567% | 1.864% | 2.567% | 2.625% | 1.448% | 2.675% | -0.001204% | 2.66% | 5.357% | 2.875% | 4.102% | 2.926% | 2.911% | 4.676% | 3.758% | 4.554% | -1.09% | 1.005% | 1.434% | 2.811% | 2.287% | 3.119% | 3.134% | 2.761% | 2.538% | 2.639% | 1.823% | 2.662% | 3.076% | 2.603% | 0.7308% | 1.713% | -0.6392% | 1.635% | 1.391% | 3.349% | 1.807% | 3.758% | 1.247% | -0.4383% | -0.6894% | 3.514% | 0.5578% | 1.434% | 0.9459% | 2.036% | 1.778% | 1.534% | 2.122% | 3.643% | 0.6949% | 3.247% | 4.548% | 0.7428% | 2.61% | 2.926% | 5.375% | 1.19% | 2.531% | 1.936% | 3.083% | 0.7953% | 2.653% | 1.312% | 1.756% | -0.2519% | -0.2519% | 2.356% | 4.174% | -0.2395% | -0.03737% | 1.722% | 0.6775% | 0.6382% | 0.6539% | 1.102% | 1.762% | 2.908% | 3.427% | 1.746% | 1.927% | 1.864% | 2.524% | 0.7788% | 2.133% | -0.337% | 2.531% | 2.335% | 3.003% | 2.853% | 2.005% | 2.924% | 1.259% | 2.901% | 0.3633% | 2.736% | 0.5989% | 1.644% | 2.066% | 1.496% | 2.198% | -0.7947% | 1.889% | 1.213% | 1.075% | 1.497% | 2.635% | 1.075% | 2.319% | 3.088% | 2.823% | -0.008254% | -0.6238% | 0.4724% | -0.1563% | -1.939% | 1.102% | 0.789% | 2.208% | 2.652% | 2.187% | 0.8116% | -1.101% | -1.773% | -0.2704% | -1.571% | -2.5% | -3.01% | -1.865% | -3.598% | -0.05275% | 0.8298% | 1.001% | 1.433% | 0.6585% | -0.3201% | 2.241% | -0.4211% | 1.988% | 0.43% | 0.6829% | 0.7074% | -1.268% | -0.4755% | -1.804% | -0.3512% | 1.801% | 0.4871% | -1.756% | -0.2346% | 0.2914% | -1.237% | 0.1771% | -1.229% | 0.09169% | -0.6075% | -2.146% | 0.4025% | -0.2968% | -0.01708% | 0.418% | 1.201% | -0.2505% | 2.043% | 1.998% | 2.688% | 2.665% | 2.149% | 2.903% | 3.633% | 2.915% | 1.539% | 2.78% | 2.265% | -2.038% | -1.905% | -0.7585% | 0.8026% | 2.044% | 0.9476% | 1.965% | 3.054% | 2.231% | 0.6304% | -0.05308% | -0.1159% | 0.1983% | -2.638% | -1.318% | 0.7325% | -1.192% | -1.986% | 1.927% | 0.5945% | 1.408% | 1.942% | 1.711% | -0.3924% | -0.2275% | -0.2148% | 1.264% | 0.3905% | 0.4378% | 0.6033% | 0.8% | -0.08244% | -0.3347% | 1.171% | 0.1146% | 1.585% | 1.061% | 2.681% | 2.494% | 0.9438% | 0.09557% | -2.533% | 1.901% | 0.3325% | 0.1305% | -0.3123% | 0.5066% | -1.437% | -2.946% | -1.38% | -0.7691% | -0.7447% | 0.6977% | -1.439% | -1.563% | -1.128% | -1.555% | -2.379% | 0.9127% | -1.373% | 0.1037% | -1.014% | 2.053% | 0.7482% | 0.324% | -0.996% | 1.529% | 0.5967% | 1.055% | 0.2315% | 1.242% | 0.2937% | 1.412% | 2.034% | 0.4646% | 1.482% | 1.238% | 1.63% | -0.1062% | 0.9766% | 2.331% | 0.2736% | -0.3822% | -0.07924% | 1.801% | 0.2513% | 1.583% | 0.7408% | -0.8181% | 1.04% | -0.4265% | 0.09557% | 1.86% | 1.801% | 2.314% | 2.282%
2025-04-27 | -3.687% | -6.676% | -2.996% | -3.39% | -3.974% | -6.934% | -0.5491% | -5.552% | -2.949% | -2.365% | -1.528% | -1.876% | -2.743% | -2.018% | -1.434% | -1.26% | -2.508% | -1.827% | -2.459% | -1.355% | 1.548% | 0.1756% | 0.9802% | 0.7909% | 0.3176% | 0.1756% | 0.5542% | 0.4753% | 1.154% | 1.043% | -0.2031% | 0.5542% | -4.747% | -5.746% | -5.032% | -3.919% | -2.242% | -1.511% | -3.58% | -2.923% | -5.489% | -3.782% | -2.06% | -3.37% | -1.923% | -0.4003% | -0.9872% | -1.533% | -5.043% | -0.8493% | -0.9946% | -3.567% | -4.084% | -3.252% | -4.854% | -3.283% | -3.296% | -7.388% | -6.777% | -7.48% | -2.128% | -3.973% | -3.926% | 4.287% | 2.512% | 4.504% | 4.56% | 3.475% | 4.334% | 1.585% | 5.544% | 3.446% | 1.7% | 0.4673% | 1.534% | 4.857% | 3.219% | 4.711% | 4.452% | 5.803% | -2.447% | 3.516% | 6.967% | 5.263% | 3.719% | 6.848% | 3.595% | 2.261% | 5.544% | 4.15% | 3.446% | 3.087% | 4.351% | 7.348% | 7.032% | 5.329% | 3.554% | 7.399% | 5.113% | 4.241% | 5.496% | 4.546% | 3.822% | 3.525% | 7.772% | 3.539% | 5.853% | 3.324% | 3.496% | 6.17% | 6.098% | 2.555% | 2.821% | 2.303% | -2.67% | 0.5641% | 2.871% | 4.387% | 0.406% | 5.753% | 4.33% | 3.597% | 2.956% | 5.075% | 5.609% | 4.926% | 3.036% | 4.51% | 2.591% | 2.023% | -10.32% | -70.46% | 0.9306% | 2.835% | 1.074% | 1.283% | -2.957% | -0.6433% | -3.388% | -1.254% | 0.1041% | -2.282% | -1.276% | 0.7294% | 0.1113% | 0.4778% | -2.196% | 1.98% | 1.877% | -0.1768% | 1.954% | -0.1187% | 4.191% | -1.24% | 0.4491% | -2.965% | -68.13% | -0.823% | 0.3628% | -3.813% | 0.715% | -1.082% | 0.1041% | 0.52% | 2.569% | 1.514% | -0.8309% | 0.9008% | 0.4758% | 0.4207% | -0.3428% | -0.3979% | -0.6577% | -0.453% | -0.4609% | -0.9253% | 0.7198% | 1.121% | 0.5781% | 1.516% | 2.749% | -3.332% | 0.1845% | -0.2563% | -0.4373% | -1.02% | -1.358% | -1.217% | -1.374% | -0.7915% | -1.681% | -0.9647% | -2.688% | -2.287% | -0.4015% | -1.054% | -0.6164% | -1.948% | 2.181% | 1.733% | -0.4886% | 0.255% | 3.06% | -0.9865% | -3.1% | 2.736% | -3.391% | -1.244% | -1.809% | 1.738% | 0.8094% | -2.118% | 0.7437% | 2.117% | 1.929% | 0.7704% | 3.671% | 2.247% | -2.185% | -1.961% | 0.7555% | -1.991% | -2.839% | -2.114% | -3.056% | -3.867% | -2.27% | -1.37% | 1.463% | 1.708% | 1.381% | -0.605% | 2.329% | -0.8697% | 2.468% | 0.7192% | 0.6456% | 1.177% | -1.726% | -2.777% | -3.026% | -3.213% | 2.64% | 1.577% | -0.2617% | -0.1613% | 1.463% | -0.823% | 1.112% | 0.9675% | -1.96% | -1.851% | -0.5972% | 2.299% | -3.049% | -2.559% | -1.36% | -0.7239% | -0.1948% | 2.139% | 1.604% | -1.254% | 1.132% | -0.5271% | 0.3154% | 3.98% | 3.887% | 0.9161% | 2.769% | 0.6697% | -2.75% | 0.2635% | -2.709% | 0.3963% | 2.955% | 1.638% | 0.0418% | 3.456% | 2.189% | 1.767% | 1.145% | 1.412% | 1.57% | -1.169% | 0.5545% | 1.263% | -0.5317% | -0.6183% | 2.089% | -1.779% | 1.751% | 1.318% | 2.466% | 2.285% | 2.425% | 1.933% | 1.949% | 1.759% | 1.901% | 1.127% | -1.884% | -0.137% | -0.002713% | 0.8424% | -0.1449% | 3.49% | 0.5738% | 1.405% | 2.904% | 1.342% | 3.237% | -2.098% | 3.673% | 1.076% | 0.5393% | 0.1423% | 1.681% | -0.002721% | -3.439% | -2.946% | 1.25% | 1.12% | 0.8741% | 0.2902% | -0.9553% | -0.893% | -0.7218% | -0.1224% | -0.7882% | -0.5478% | 1.071% | 2.885% | 2.526% | 2.746% | 3.229% | -2.146% | -2.255% | -2.925% | 0.04112% | 0.07226% | -0.02894% | -0.1146% | 0.4771% | 1.123% | 0.4537% | 2.428% | 2.092% | 1.17% | -0.1662% | 1.978% | 2.844% | -0.9617% | -3.081% | -3.571% | 1.676% | -3.406% | 1.894% | 0.1009% | -0.2535% | 1.497% | -0.0001399% | 0.5802% | 3.43% | 3.229% | 3.539% | 0.4249%
2025-04-28 | -5.433% | -9.402% | -4.788% | -4.995% | -4.995% | -8.765% | -2.224% | -7.32% | -3.238% | -2.98% | -3.807% | -4.013% | -3.393% | -3.135% | -2.102% | -3.135% | -4.236% | -2.17% | -2.308% | -1.74% | 1.773% | 0.5847% | 1.566% | 0.4814% | 1.67% | 0.8947% | 2.186% | 1.411% | 2.496% | 2.548% | 1.05% | 1.256% | -4.375% | -6.031% | -5.868% | -4.399% | -3.529% | -3.855% | -5.098% | -4.399% | -7.474% | -3.693% | -0.9262% | -2.646% | -0.9008% | 1.204% | 1.65% | 1.602% | -1.17% | 0.6002% | 0.9896% | -1.939% | -3.664% | -2.205% | -4.021% | -2.363% | -2.018% | -6.844% | -6.425% | -7.242% | -4.581% | -3.574% | -3.66% | 5.796% | 3.231% | 4.308% | 4.078% | 6.149% | 4.145% | 3.09% | 5.066% | 6.831% | 3.184% | 3.896% | 2.925% | 4.528% | 0.4691% | 4.243% | 5.301% | 5.419% | 4.243% | 5.943% | 6.502% | 5.906% | 7.372% | 7.136% | 5.93% | 5.135% | 5.584% | 3.584% | 4.078% | 3.513% | 4.949% | 5.654% | 5.466% | 7.537% | 6.836% | 7.113% | 5.937% | 4.479% | 5.143% | 5.725% | 3.667% | 6.643% | 10.9% | 7.372% | 7.208% | 6.431% | 4.666% | 7.913% | 6.949% | 8.313% | 6.722% | 5.586% | 1.325% | 7.443% | 6.455% | 6.172% | 7.443% | 5.513% | 5.513% | 6.36% | 5.045% | 6.078% | 7.396% | 6.36% | 4.407% | 6.219% | 4.643% | 4.501% | -2.299% | -18.98% | 5.819% | 7.325% | 4.501% | 5.325% | 3.2% | 6.807% | 5.883% | 3.937% | 3.843% | 5.96% | 6.196% | 5.631% | 4.478% | 6.596% | 6.337% | 6.127% | 6.191% | 3.2% | 4.319% | 6.337% | 8.913% | 5.984% | 6.502% | -14.21% | -100% | 13.7% | 14.53% | 4.36% | 4.737% | 4.596% | 3.372% | 6.574% | 7.937% | 4.184% | -2.298% | -2.659% | -2.195% | -2.092% | -2.195% | -2.349% | -2.633% | -0.6485% | -0.2619% | -1.886% | -2.014% | -1.834% | -1.447% | -0.6601% | -2.611% | -2.089% | -1.628% | -1.576% | -0.5454% | -0.597% | -1.551% | -0.8031% | -2.762% | -0.4423% | -3.226% | -0.9835% | -2.53% | -2.324% | -2.311% | -2.473% | -1.31% | 1.631% | 4.286% | 3.842% | 3.429% | 3.935% | 5.329% | 4.087% | 5.75% | 6.39% | 6.611% | 4.207% | 4.839% | 3.434% | 3.26% | -1.896% | 4.31% | 4.779% | 4.484% | 5.756% | 5.166% | 2.979% | 1.612% | 0.2641% | 2.303% | 0.8179% | -2.827% | -2.917% | 1.519% | -0.8883% | -3.092% | -2.362% | -2.769% | -2.26% | -1.779% | -3.219% | -1.056% | -3.295% | -2.1% | -2.501% | -1.966% | -2.394% | -2.862% | -3.397% | -3.168% | -3.346% | -0.6009% | -30.42% | -3.01% | -2.938% | -1.27% | -3.397% | -1.779% | -1.154% | -1.97% | -1.817% | -1.995% | -2.276% | -3.372% | -3.372% | -3.27% | 2.723% | 2.564% | 2.422% | 4.123% | 5.847% | 6.585% | 5.487% | 5.506% | 5.788% | 4.703% | 4.4% | 5.083% | 6.395% | 2.865% | 2.338% | 4.138% | 3.061% | 5.091% | 3.931% | 4.959% | 6.265% | 5.083% | -1.061% | -2.169% | -2.169% | -2.092% | -2.221% | -2.401% | -2.298% | -3.097% | -2.581% | -1.808% | -2.017% | -2.556% | -2.994% | -2.176% | -2.825% | -2.906% | -2.485% | -2.822% | -2.792% | -3.697% | -3.62% | -2.514% | -3.749% | -2.844% | -2.559% | -2.508% | -1.042% | -2.973% | -1.576% | -1.553% | -3.339% | -7.64% | -6.096% | -7.452% | -6.787% | -8.011% | -8.444% | -8.318% | -11.09% | -10.38% | -9.297% | -8.71% | -8.443% | -6.201% | -7.883% | -9.361% | -10.23% | -8.087% | -6.43% | -5.803% | -11.44% | -8.175% | -5.713% | -5.954% | -6.596% | -4.749% | -5.564% | -2.785% | -2.327% | -3.932% | -3.601% | -3.168% | -4.646% | -3.321% | -2.76% | -4.773% | -3.465% | -3.92% | -2.683% | -5.68% | -4% | -2.18% | -2.435% | -5.411% | -5.615% | -1.083% | -4.552% | -1.536% | -2.922% | -4.99% | -2.709% | -5.632% | -3.143% | -2.694% | -3.866% | -3.17% | -7.881%
2025-04-29 | -7.945% | -11.49% | -7.389% | -7.601% | -7.662% | -11.47% | -4.874% | -9.634% | -6.023% | -5.993% | -6.114% | -6.569% | -6.296% | -6.054% | -5.083% | -5.811% | -7.018% | -5.389% | -5.932% | -5.174% | -2.048% | -3.141% | -1.805% | -3.08% | -2.746% | -3.474% | -1.987% | -2.534% | -1.593% | -1.775% | -2.958% | -3.08% | -7.692% | -9.126% | -8.551% | -7.402% | -6.347% | -6.539% | -7.54% | -6.922% | -10.15% | -6.806% | -4.28% | -5.69% | -4.285% | -2.124% | -2.172% | -2.824% | -5.299% | -3.93% | -3.211% | -5.861% | -6.973% | -6.18% | -7.636% | -5.988% | -5.893% | -10.57% | -9.621% | -10.5% | -6.812% | -7.421% | -6.97% | 2.279% | -0.08448% | 0.5179% | 0.6204% | 2.445% | 0.7631% | -0.4162% | 1.436% | 3.053% | -0.278% | 0.363% | -0.3747% | 1.004% | -1.034% | 0.1919% | 1.173% | 1.021% | 0.4684% | 1.885% | 2.472% | 2.405% | 3.744% | 3.706% | 2.752% | 2.147% | 1.823% | 0.5098% | 0.6895% | -0.1121% | 1.436% | 1.92% | 2.044% | 3.938% | 3.354% | 3.633% | 2.79% | 1.119% | 1.466% | 2.611% | 0.6053% | 3.343% | 7.476% | 3.661% | 3.772% | 2.998% | 1.602% | 4.338% | 3.426% | 5.112% | 3.452% | 2.506% | 0.9245% | 3.316% | 2.403% | 2.265% | 2.97% | 1.823% | 1.671% | 2.307% | 1.22% | 2.058% | 2.97% | 2.155% | 0.3163% | 2.113% | 1.118% | 0.9798% | 0.8554% | -15.5% | 2.072% | 3.495% | 0.6895% | 1.394% | -0.7159% | 2.625% | 1.523% | -0.3471% | -0.4991% | 1.768% | 2.044% | 1.146% | 0.344% | 2.431% | 2.334% | 2.189% | 2.415% | -0.007837% | 1.345% | 2.307% | 5.178% | 11.55% | 15.44% | 14.97% | -100% | 16.14% | 16.86% | 1.256% | 1.505% | 1.629% | 0.1367% | 3.991% | 5.361% | 1.061% | -0.8624% | 1.393% | -0.2115% | 0.07611% | 0.394% | -0.04499% | 0.3032% | 1.772% | 2.71% | 1.408% | 1.529% | 1.741% | 2.604% | 0.009503% | 2.026% | 0.5557% | 2.15% | 2.468% | 2.544% | 1.908% | 1.666% | 2.226% | 1.408% | 2.665% | 0.4394% | 2.786% | 0.5% | 1.015% | 1.663% | 0.9473% | 2.505% | -1.511% | 0.857% | 0.1995% | 0.1572% | 0.5126% | 1.908% | 0.569% | 1.962% | 2.734% | 3.082% | 0.5082% | 1.151% | -0.05048% | -0.3213% | -2.572% | 0.7262% | 0.9698% | 1.19% | 2.256% | 1.518% | -0.1428% | -1.514% | -2.838% | -1.035% | -2.346% | -3.404% | -3.778% | -1.615% | -2.428% | 0.1224% | 2.052% | 1.834% | 1.677% | 1.551% | 0.1142% | 2.605% | -0.03551% | 2.62% | 1.331% | 1.504% | 0.5925% | -1.787% | -0.6943% | -1.817% | -0.2601% | 3.988% | 0.9227% | 0.6083% | 1.507% | 1.504% | -1.742% | 0.7655% | -0.305% | 0.9825% | -0.05048% | 0.08426% | 0.5184% | -0.6344% | 0.2939% | 0.8328% | -0.1492% | -0.9985% | -1.196% | 0.6378% | 2.407% | 3.006% | 2.312% | 2.167% | 2.981% | 2.399% | 0.9637% | 2.509% | 3.253% | -1.594% | -2.365% | 0.9889% | 0.3463% | 2.145% | 0.9925% | 2.235% | 2.991% | 2.18% | 0.9995% | -0.2721% | -0.9987% | -0.6808% | -3.012% | -0.6202% | -0.07527% | -1.619% | -2.134% | 2.211% | 1.187% | 1.272% | 1.439% | 2.267% | 0.8201% | -0.5468% | -0.3053% | 1.508% | 0.1746% | 0.1594% | 0.9189% | -1.187% | -0.007639% | -0.4178% | 0.4177% | 0.7518% | 1.556% | 1.132% | 2.801% | 2.489% | 1.059% | -2.174% | -2.96% | 2.314% | 0.6981% | -0.05048% | -0.5745% | 0.9314% | -1.543% | -2.73% | -1.321% | -0.7751% | 0.6554% | 2.689% | -1.353% | 0.8927% | -0.5296% | -0.4847% | -2.955% | 1.954% | -0.4293% | 0.7026% | -10.74% | 2.668% | 3.595% | -1.262% | 0.6532% | 2.21% | 2.644% | 1.057% | 0.9376% | 2.001% | -0.1703% | 1.507% | 2.584% | -0.0954% | 2.322% | 3.595% | 2.105% | -0.05363% | 1.127% | 3.265% | 2.252% | 0.02437% | -1.667% | 3.013% | -0.09199% | 2.465% | 1.423% | -0.3349% | 1.027% | -0.03626% | 1.001% | 2.164% | 2.165% | 3.579% | 0.5768%
2025-04-30 | -6.782% | -9.606% | -6.355% | -6.526% | -6.402% | -9.142% | -4.14% | -8.744% | -5.332% | -5.006% | -5.239% | -5.471% | -5.285% | -5.053% | -4.277% | -4.68% | -5.884% | -5.247% | -6.138% | -4.898% | -2.401% | -3.362% | -2.587% | -2.695% | -3.316% | -4.122% | -2.912% | -3.316% | -2.587% | -2.478% | -3.688% | -3.223% | -6.604% | -7.5% | -7.271% | -6.243% | -5.296% | -4.79% | -6.014% | -6.08% | -8.077% | -5.977% | -3.304% | -3.715% | -3.64% | -1.283% | -1.728% | -2.51% | -4.234% | -3.797% | -3.178% | -5.775% | -6.812% | -6.342% | -7.932% | -6.106% | -6.458% | -10.63% | -10.36% | -10.94% | -6.247% | -7.794% | -5.969% | 1.986% | 0.05074% | 0.04355% | 0.7501% | 2.34% | 0.454% | -0.2954% | 1.584% | 2.876% | 0.2203% | -0.1204% | 0.1991% | 1.186% | -0.2832% | 0.6795% | 1.753% | 1.061% | 0.4887% | 2.171% | 2.749% | 2.516% | 3.427% | 1.991% | 2.309% | 1.232% | 1.068% | 0.3828% | 0.7572% | 0.05074% | 1.909% | 1.838% | 2.198% | 3.208% | 2.621% | 2.198% | 2.078% | 1.895% | 1.393% | 2.502% | 0.2138% | 2.919% | 7.249% | 3.286% | 3.696% | 2.848% | 1.965% | 4.141% | 3.343% | 4.847% | 3.104% | 1.822% | 1.294% | 3.102% | 2.65% | 2.657% | 3.053% | 2.142% | 1.767% | 2.509% | 1.578% | 2.494% | 2.94% | 2.135% | 0.5099% | 2.029% | 1.449% | 1.421% | 1.259% | -15.55% | 2.106% | 3.668% | 1.103% | 1.647% | -0.7928% | 3.682% | 2.016% | 1.315% | 0.7854% | 2.756% | 3.124% | 2.149% | 1.831% | 2.573% | 3.293% | 3.38% | 3.356% | 0.9132% | 2.036% | 3.166% | 5.564% | 6.995% | 10.19% | 14.13% | -100% | 14.65% | 13.64% | 1.803% | 1.986% | 2.092% | 0.4181% | 3.424% | 5.073% | 1.475% | 0.1789% | 1.85% | 1.038% | 0.9526% | 1.115% | 1.045% | 1.626% | 3.011% | 3.32% | 1.92% | 2.013% | 1.92% | 2.593% | 0.801% | 2.234% | 0.2116% | 2.415% | 2.624% | 2.987% | 2.879% | 2.129% | 3.134% | 1.572% | 3.343% | 0.736% | 3.104% | 0.8133% | 1.788% | 2.304% | 1.67% | 2.645% | -0.3221% | 2.177% | 1.332% | 1.263% | 1.571% | 2.917% | 1.584% | 3.08% | 3.338% | -0.7134% | 1.039% | 2.193% | 0.9222% | 0.3975% | 1.575% | 1.383% | 1.485% | 2.353% | 3.107% | 2.547% | 1.575% | -2.587% | -1.628% | -0.1818% | -1.09% | -2.84% | -3.46% | -0.3873% | -1.501% | 0.03802% | 1.331% | 1.3% | 1.798% | 1.027% | 0.3865% | 2.264% | 0.04219% | 2.144% | 1.091% | 1.099% | 0.8261% | -0.4399% | -0.4628% | -0.8684% | -0.1032% | 2.505% | 2.521% | -0.7486% | 1.098% | 0.8261% | -1.22% | 1.879% | -0.4628% | 0.4707% | 0.03454% | 0.04219% | 1.144% | 0.3177% | 0.4095% | 1.205% | 0.2644% | -0.582% | -2.998% | 1.27% | 2.389% | 2.803% | 1.909% | 2.133% | 2.952% | 2.284% | 1.11% | 2.28% | 2.777% | -0.722% | -2.43% | 0.05539% | 0.332% | 2.164% | 0.8699% | 1.914% | 2.724% | -1.467% | 0.02417% | -0.9739% | -0.8501% | -0.5329% | -3.403% | -1.84% | -0.4555% | -2.289% | -2.661% | 1.517% | 0.411% | 0.8598% | 0.7592% | 1.069% | -0.9132% | -0.8076% | -0.5293% | 0.6937% | -0.4496% | 0.0783% | 0.03172% | 1.05% | -0.799% | -1.078% | 0.5286% | -0.4884% | 0.8414% | 0.4044% | 1.958% | 1.768% | 0.1348% | -0.7486% | -1.684% | 0.6466% | -0.5394% | -0.899% | -1.136% | -0.4257% | -2.587% | -2.238% | -2.277% | -1.568% | -1.231% | 0.08045% | -2.085% | -2.016% | -2.276% | -2.177% | -2.406% | -0.1124% | -2.348% | -0.2987% | -1.03% | 0.9386% | 1.075% | -0.138% | -1.052% | 0.685% | 0.6467% | -0.2256% | -0.06493% | 0.4401% | -0.9679% | 0.5243% | 1.075% | -0.5241% | 0.9065% | 0.9949% | 0.6926% | -0.98% | 0.3119% | 1.445% | 0.805% | -0.9373% | -0.9602% | 1.927% | -0.634% | 1.488% | 0.4324% | -1.054% | 0.6926% | -1.022% | -0.6201% | 1.109% | 0.3762% | 1.533% | 1.364%
2025-05-01 | -7.318% | -10.34% | -6.432% | -6.523% | -7.116% | -10.79% | -3.934% | -8.986% | -5.382% | -5.109% | -5.519% | -6.021% | -5.245% | -5.2% | -4.196% | -4.835% | -6.213% | -4.388% | -4.698% | -4.014% | -0.729% | -1.687% | -0.729% | -1.596% | -1.048% | -2.417% | -0.3184% | -0.9114% | 0.1378% | 0.0466% | -1.459% | -1.322% | -6.249% | -7.846% | -7.51% | -6.261% | -5.253% | -5.589% | -6.523% | -5.637% | -8.621% | -4.903% | -2.488% | -3.772% | -2.583% | -0.215% | -0.3067% | -0.8482% | -3.487% | -1.665% | -1.371% | -4.19% | -5.891% | -4.787% | -6.26% | -4.34% | -4.167% | -8.446% | -8.468% | -8.959% | -6.021% | -6.027% | -5.786% | 3.234% | 1.093% | 1.742% | 1.924% | 3.795% | 1.771% | 0.8647% | 2.839% | 4.21% | 1.031% | 1.424% | 0.8854% | 1.995% | 0.3659% | 1.987% | 3.213% | 2.963% | 1.779% | 3.552% | 4.002% | 3.69% | 5.062% | 4.428% | 3.625% | 2.895% | 2.984% | 1.55% | 1.904% | 0.6153% | 2.195% | 2.631% | 3.192% | 4.647% | 4.189% | 4.189% | 3.317% | 2.234% | 2.104% | 3.504% | 1.107% | 4.293% | 5.062% | 4.273% | 5.062% | 3.878% | 2.672% | 5.748% | 4.792% | 6.039% | 4.28% | 3.32% | 2.485% | 5.228% | 4.189% | 4.127% | 4.834% | 3.441% | 3.296% | 4.002% | 2.625% | 3.538% | 4.792% | 3.961% | 1.8% | 3.857% | -2.065% | 2.236% | 1.945% | -14.2% | 3.483% | 4.937% | 2.278% | 2.797% | 0.9091% | 5.561% | 4.285% | 2.298% | 2.298% | 4.252% | 4.48% | 3.67% | 2.86% | 4.834% | 4.356% | 3.994% | 3.931% | 1.191% | 2.445% | 4.605% | 6.67% | 13% | 13.33% | 16.01% | -100% | 17.3% | 18.13% | 1.987% | 2.382% | 2.278% | 1.072% | 5.783% | 7.182% | 1.995% | 1.071% | 3.507% | 2.187% | 2.278% | 2.892% | 2.46% | 2.938% | 4.485% | 5.077% | 3.62% | 3.325% | 3.734% | 5.054% | 2.039% | 4.083% | 2.365% | 4.508% | 4.394% | 4.667% | 4.394% | 3.803% | 4.576% | 3.165% | 4.349% | 1.8% | 4.371% | 1.754% | 2.938% | 3.425% | 2.493% | 4.691% | -0.09988% | 2.813% | 2.265% | 2.053% | 2.181% | 3.441% | 2.749% | 4.298% | 4.897% | 5.1% | 2.507% | 0.5522% | 2.099% | 1.544% | 3.484% | 2.198% | 2.335% | 2.595% | 3.66% | 3.243% | 1.364% | -0.2052% | -2.081% | 0.3725% | -1.273% | -1.967% | -2.221% | -0.2741% | -1.792% | 0.5522% | 2.808% | 2.477% | 1.461% | -2.297% | 0.7036% | -6.149% | -2.65% | 3.588% | 2.17% | 2.265% | -15.79% | -38.06% | 0.3659% | -38.48% | 1.289% | 5.55% | 6.117% | -0.1225% | 1.446% | 2.075% | -1.052% | 4.935% | 0.09584% | 2.189% | 1.019% | -23.76% | -4.946% | -9.988% | 1.086% | 0.9512% | 0.2943% | -0.7306% | -0.2232% | 1.335% | 3.114% | 3.793% | 0.03292% | 2.662% | 3.173% | 2.695% | 1.647% | 2.808% | 3.759% | 0.3594% | -1.911% | 2.074% | 1.331% | 2.467% | 1.154% | 2.572% | 3.467% | 2.443% | 0.9122% | -0.3396% | -0.5444% | 0.2522% | -2.183% | -0.6127% | -0.06647% | -1.386% | -1.728% | 2.437% | 1.01% | 1.527% | 1.413% | 2.397% | 0.7005% | -0.2315% | 0.06806% | 1.626% | 0.7998% | 1.211% | 1.416% | 1.096% | 0.09191% | -0.04511% | 0.503% | 0.8227% | 1.578% | 1.211% | 3.552% | 2.469% | 0.9873% | -28.13% | -17.32% | 2.684% | 0.3434% | 0.2759% | -0.03921% | 1.346% | -1.06% | -27.34% | -2.499% | -1.115% | 0.3502% | 3.36% | -6.229% | 1.491% | 0.7486% | -2.965% | -40.67% | 3.035% | 0.9647% | -1.233% | -53.98% | -0.1698% | 5.881% | -36.14% | -1.142% | 0.501% | 0.7036% | -0.3318% | -0.3543% | 0.411% | -1.412% | 0.3885% | 1.514% | -1.007% | 1.083% | 1.39% | 0.9062% | -1.633% | -0.02795% | 1.886% | 0.5092% | -1.682% | -1.502% | 0.9647% | -0.9089% | 0.8836% | 0.07947% | -1.304% | -0.2193% | -1.162% | 1.319% | 0.6313% | 1.012% | 2.265% | 1.201%
2025-05-02 | -2.704% | -5.175% | -1.828% | -1.736% | -2.782% | -5.354% | 0.4819% | -4.689% | -1.443% | -1.241% | -0.8011% | -1.296% | -1.443% | -1.315% | -0.3977% | -0.7094% | -1.951% | -1.468% | -2.14% | -0.8378% | 1.656% | 0.5927% | 1.73% | 0.8678% | 0.556% | -0.1593% | 1.198% | -0.1593% | 1.473% | 1.583% | 0.3726% | 0.9228% | -3.424% | -4.364% | -3.707% | -2.819% | -1.507% | -0.8697% | -2.8% | -2.105% | -4.249% | -2.856% | -1.505% | -0.2648% | -0.2825% | 1.528% | -1.285% | -1.735% | -6.067% | -0.937% | -0.02556% | -2.482% | -3.499% | -3.468% | -4.605% | -5.081% | -3.574% | -6.868% | -6.609% | -7.443% | -1.957% | -3.822% | -3.078% | 1.569% | 0.6756% | 4.199% | 2.421% | 1.202% | 3.35% | -0.6275% | 4.117% | 1.168% | -0.09289% | -1.104% | -0.2767% | 2.911% | 2.221% | -1.329% | -1.505% | 4.994% | -0.8447% | 0.09123% | 4.41% | 2.055% | 0.5086% | 3.523% | 0.7455% | -0.724% | -0.8447% | 1.862% | 1.478% | -1.212% | 0.1995% | 3.19% | 3.825% | 0.5503% | -1.292% | 4.76% | 0.709% | 1.392% | 2.16% | 1.235% | 2.053% | 0.7508% | 7.15% | 0.8093% | 3.566% | 0.5503% | 1.026% | 3.733% | 3.29% | 3.006% | 5.598% | -1.333% | 0.7926% | 0.7592% | -2.415% | 2.288% | 1.912% | 4.401% | 2.513% | 2.396% | 1.977% | 3.671% | 6.866% | 6.214% | 4.476% | 6.197% | -0.8029% | 1.227% | 0.8594% | -12.21% | 0.0157% | 3.14% | 0.7174% | 1.01% | 2.824% | 2.747% | -0.6385% | 1.494% | 3.892% | 1.294% | 1.745% | 6.632% | 1.711% | 1.578% | 1.753% | 6.544% | 3.301% | 3.409% | 4.614% | 1.302% | 5.397% | 4.735% | 6.013% | 9.981% | -100% | 8.035% | 8.979% | 1.62% | 1.152% | 2.071% | 4.351% | 0.1633% | 2.639% | 0.9988% | 1.215% | 2.158% | 1.316% | 1.252% | 0.6024% | 1.325% | 1.774% | 2.579% | 2.826% | 2.03% | 2.039% | 2.167% | 2.643% | 3.346% | 7.037% | -1.324% | 2.423% | 2.268% | 2.798% | 2.469% | 1.874% | 2.35% | 1.508% | 2.478% | 0.8403% | 2.295% | 0.5933% | 1.225% | 3.461% | 2.981% | 3.461% | -0.001094% | 5.256% | 7.313% | 1.244% | 0.5524% | 6.416% | 0.5669% | -1.711% | 6.638% | 3.271% | 1.055% | 2.212% | 6.763% | 2.816% | 3.09% | 1.343% | 4.339% | 6.742% | 0.08885% | 8.36% | 7.307% | -2.695% | -2.438% | 0.05912% | -0.4263% | -1.877% | 0.6455% | -2.029% | -2.54% | -2.443% | -1.597% | 1.878% | 0.8044% | 0.7664% | -1.272% | 2.23% | -0.8741% | 3.066% | 1.926% | 1.869% | 1.659% | -0.4759% | -0.856% | -0.6931% | -0.4759% | 3.094% | 2.705% | 0.6334% | -0.3312% | 1.945% | -0.9284% | -74.44% | -74.82% | -0.2588% | -0.6388% | 0.7185% | 4.202% | -0.2316% | -0.1231% | 0.3384% | 1.564% | -3.226% | 1.238% | 0.7639% | -2.896% | 0.02851% | 0.3343% | 1.106% | 3.24% | 4.113% | 0.3955% | 2.921% | 0.1658% | -2.844% | 0.5173% | -2.796% | 1.089% | 5.755% | 4.33% | -0.2324% | 6.21% | 2.23% | -1.447% | -1.657% | -1.621% | -1.657% | -3.085% | -3.359% | -1.237% | -2.902% | -2.911% | -0.2942% | -2.85% | -0.4771% | -0.4589% | 1.146% | -0.2754% | -0.189% | -1.122% | -0.1824% | -1.175% | -1.019% | -0.6699% | -2.714% | -0.9178% | -1.487% | -0.2201% | -0.9729% | 2.943% | -0.3119% | -0.5412% | 2.318% | 1.233% | -0.2787% | -2.521% | 0.1377% | -2.684% | -2.792% | -2.376% | -0.6693% | -1.301% | -2.62% | -3.195% | -2.027% | -1.979% | -2.494% | -3.453% | -3.552% | -3.815% | -3.824% | -3.046% | -3.373% | -2.692% | -0.9152% | 0.4529% | 0.5004% | 0.6144% | 0.5574% | -3.272% | -1.589% | -2.231% | -1.779% | -2.458% | -1.48% | -2.358% | -1.643% | -1.136% | -1.915% | 0.1774% | 0.6144% | -1.317% | 0.1194% | -0.4687% | 0.3674% | -2.625% | -2.847% | -2.829% | 0.04434% | -3.246% | -1.716% | -3.583% | -1.856% | -1.996% | -1.694% | -1.143% | 1.559% | -0.8107% | 0.1679% | 0.3959%
2025-05-03 | -6.98% | -9.081% | -5.825% | -5.505% | -6.45% | -9.139% | -3.088% | -8.202% | -5.124% | -4.469% | -3.996% | -4.515% | -4.042% | -4.042% | -2.991% | -2.732% | -4.702% | -4.301% | -5.261% | -3.89% | -0.6896% | -2.076% | -0.6439% | -1.299% | -1.878% | -2.274% | -1.01% | -1.452% | -0.4763% | -0.5372% | -1.634% | -0.9944% | -5.368% | -6.755% | -6.146% | -5.167% | -3.467% | -2.874% | -4.484% | -3.852% | -5.551% | -3.786% | -2.019% | -1.557% | -1.41% | -65.37% | -0.8809% | -1.493% | -5.781% | -1.432% | -0.8995% | -3.232% | -4.272% | -4.2% | -5.537% | -6.491% | -4.886% | -8.594% | -8.663% | -8.573% | -3.189% | -5.382% | -3.982% | 1.2% | -0.5215% | 1.592% | 1.089% | -0.5631% | 0.5926% | -1.965% | 2.338% | -0.6256% | -2.146% | -3.793% | -2.583% | -0.1577% | -1.072% | 0.1101% | 2.033% | 4.511% | -1.327% | 0.3158% | 5.031% | 2.469% | 0.0685% | 3.855% | 3.26% | -1.312% | 3.011% | 1.79% | 0.8598% | -3.499% | -2.638% | -0.6464% | 0.9708% | -1.646% | -3.422% | 1.401% | -0.5562% | -0.506% | -0.1214% | 0.3947% | 0.5368% | -1.347% | 5.573% | -1.563% | 1.727% | -1.535% | -1.111% | 1.873% | 2.033% | 1.353% | 4.201% | -2.008% | -0.8547% | 0.1518% | 0.1865% | 2.734% | 6.468% | 5.371% | 2.442% | 0.367% | 2.324% | 4.196% | 5.968% | 5.378% | 3.942% | 5.573% | 2.796% | 2.144% | 1.304% | -13.25% | -0.05644% | 3.199% | 1.103% | -0.9102% | 2.273% | 0.1796% | -3.825% | -0.3063% | 2.442% | -0.7991% | 0.596% | 4.421% | 1.332% | 3.06% | -1.327% | 5.894% | 3.449% | 2.97% | 4.67% | 0.8528% | 5.342% | 1.471% | 3.768% | 7.225% | -100% | 7.711% | 5.6% | 1.852% | 0.9153% | -0.1328% | 3.213% | -1.088% | 1.269% | 3.347% | 0.4155% | 1.541% | 0.8945% | 0.8717% | -0.09379% | 1.153% | 1.693% | 2.407% | 2.993% | 2.118% | 1.366% | 1.974% | 2.993% | 2.826% | 5.027% | -0.7745% | 2.749% | 2.825% | 3.282% | 3.061% | 2.673% | 3.327% | 2.065% | 3.244% | 1.252% | 3.046% | 1.715% | 2.681% | 4.159% | 3.752% | 4.215% | -1.622% | 3.541% | 3.993% | -0.7647% | -0.2554% | 3.393% | -1.333% | -0.09069% | 3.613% | -1.972% | -2.001% | -0.4941% | 2.387% | -0.3104% | -0.4135% | -1.023% | 4.68% | 4.467% | 2.783% | 4.913% | 3.259% | -3.306% | -3.846% | -2.346% | -3.396% | -3.448% | -3.363% | -3.505% | -4.425% | -1.563% | -1.434% | 3.172% | -1.319% | 2.344% | 0.7406% | 4.167% | 1.086% | 3.812% | 2.738% | 3.267% | 2.936% | -0.003735% | 0.7782% | -0.6804% | 0.7105% | 2.983% | 3.338% | -0.309% | -0.8684% | 1.523% | -1.38% | -78.13% | -78.47% | 1.154% | 0.1842% | -0.06388% | 2.763% | 0.07897% | 0.7857% | 0.7331% | 2.987% | -1.719% | 1.468% | 2.164% | -1.197% | 0.6081% | -1.94% | 0.3792% | 4.357% | 5.181% | 1.44% | 3.561% | -0.1049% | -2.309% | 1.348% | -3.547% | 1.266% | 4.672% | 3.479% | -0.4271% | 5.478% | 2.771% | 2.316% | 2.582% | 2.932% | 2.346% | 0.1647% | -0.2762% | 2.932% | 0.6588% | 1.442% | 3.646% | 0.07544% | 4.057% | 3.745% | 3.608% | 3.409% | 4.223% | 3.185% | 4.065% | 2.841% | 2.574% | 3.237% | 0.2619% | 2.681% | 2.917% | 3.016% | 2.764% | 6.648% | 3.848% | 2.483% | 6.107% | 4.431% | 3.765% | -2.624% | 4.886% | 1.936% | 1.786% | 1.289% | 3.297% | 0.9907% | -1.718% | -0.6377% | 2.067% | 1.649% | 2.199% | 0.4098% | 0.05642% | 0.9586% | 0.4023% | -0.3421% | 0.7588% | 1.909% | 2.975% | 2.312% | 4.665% | 2.944% | 2.47% | 1.974% | 3.861% | 2.928% | 3.289% | 2.116% | 3.357% | 2.004% | -0.4398% | 3.319% | 2.372% | 4.207% | 4.049% | 3.064% | 3.118% | 3.259% | 4.586% | 0.3886% | 2.492% | 2.282% | 4.846% | 0.2809% | 2.658% | 0.7187% | 2.265% | 2.38% | 2.336% | 2.533% | 4.597% | 3.149% | 4.586% | 4.672%
2025-05-04 | -4.949% | -7.054% | -3.878% | -3.686% | -4.55% | -7.283% | -1.371% | -6.726% | -3.734% | -3.078% | -2.902% | -3.462% | -3.11% | -3.446% | -2.566% | -3.03% | -3.753% | -3.753% | -4.39% | -3.158% | -0.3261% | -1.686% | -0.6621% | -1.622% | -1.574% | -1.99% | -1.174% | -1.814% | -0.6461% | -0.7101% | -2.038% | -1.494% | -4.886% | -5.791% | -5.033% | -4.562% | -3.265% | -3.416% | -4.534% | -4.326% | -6.038% | -3.791% | -1.407% | -1.678% | -2.326% | 0.03118% | -0.7477% | -2.184% | -4.488% | -3.16% | -2.829% | -5.509% | -6.703% | -6.358% | -7.343% | -6.022% | -5.363% | -9.231% | -9.217% | -9.592% | -4.678% | -6.815% | -5.926% | 3.575% | 2.161% | 2.845% | 4.034% | 4.231% | 3.539% | 1.228% | 4.326% | 4.092% | 2.066% | 0.6765% | 1.87% | 3.392% | 2.142% | 1.87% | 2.62% | 2.897% | 1.017% | 2.144% | 4.063% | 3.742% | 3.181% | 4.527% | 3.239% | 1.758% | 3.655% | 2.606% | 2.956% | 1.272% | 3.866% | 4.362% | 5.645% | 4.318% | 2.731% | 3.728% | 3.75% | 5.159% | 3.895% | 4.581% | 2.346% | 4.42% | 7.452% | 4.457% | 6.723% | 3.859% | 4.763% | 6.92% | 6.118% | 6.563% | 3.63% | 1.914% | 2.212% | 2.598% | -0.178% | 3.531% | 1.163% | 3.91% | 2.613% | 0.5872% | 2.043% | 3.369% | 3.313% | 2.664% | 1.112% | 2.854% | 2.081% | 1.33% | 0.9224% | -15.21% | 0.9297% | 3.218% | 0.7475% | 1.192% | -2.695% | 3.743% | 0.6726% | 1.877% | 2.387% | 2.307% | 2.956% | 3.385% | 2.467% | 4.1% | 0.9588% | 4.336% | 3.687% | 1.716% | 3.079% | 2.854% | 5.41% | -2.277% | 1.935% | -0.1124% | -3.734% | 2.584% | -0.4549% | 1.731% | 1.535% | -0.7027% | 1.221% | 1.201% | 3.152% | 2.142% | 1.603% | 2.792% | 1.85% | 1.339% | 0.6132% | 1.818% | 2.409% | 3.566% | 3.806% | 2.361% | 2.361% | 2.425% | 3.255% | 1.755% | 3.191% | -0.128% | 2.968% | 2.792% | 3.566% | 3.463% | 2.433% | 3.295% | 1.866% | 3.455% | 1.028% | 3.455% | 1.036% | 2.098% | 2.66% | 2.183% | 2.627% | 0.1737% | 3.725% | 2.974% | 1.633% | 2.091% | 4.205% | 1.27% | 2.934% | 4.95% | 3.583% | 1.02% | 3.815% | 3.052% | 1.63% | -0.5964% | 1.636% | 2.096% | 4.35% | 3.714% | 4.014% | 2.665% | -0.5329% | -2.893% | 1.659% | -0.6814% | -2.454% | -2.177% | -1.224% | -2.63% | -0.3891% | -0.3816% | 0.9852% | 0.02379% | 0.3885% | -0.7529% | 2.063% | -0.6109% | 2.419% | 0.4382% | 0.5045% | 0.9355% | 0.3364% | -0.6582% | -0.2556% | -0.1215% | 2.419% | -0.4569% | -1.004% | -0.1846% | -1.659% | -2.797% | -37.31% | -37.01% | -0.08198% | -0.5161% | 0.9284% | 1.71% | 0.2574% | 0.5021% | 0.9837% | -1.225% | -3.571% | -2.399% | 1.222% | 1.505% | 0.9037% | 0.6269% | 1.886% | 3.054% | 2.653% | 0.844% | 2.21% | 0.5607% | -2.509% | -1.684% | -2.274% | 0.9106% | 2.352% | 1.026% | 0.498% | 2.845% | 1.299% | -0.7357% | -0.8793% | -0.8953% | -0.8793% | -4.128% | -3.082% | -0.4483% | -2.97% | -3.154% | 0.4775% | -1.271% | 0.4536% | 0.8127% | 0.5737% | -1.781% | -1.304% | -0.6665% | 0.4023% | -0.533% | -0.477% | 0.2278% | -1.388% | -0.5651% | -1.27% | 0.6683% | -0.5971% | 0.6791% | 0.2198% | 0.4376% | 1.588% | 0.07923% | 0.4714% | -3.336% | 0.3893% | -1.487% | -1.345% | -1.677% | -1.027% | -3.532% | -2.024% | -2.627% | -2.372% | -2.628% | -1.25% | -2.371% | -3.705% | -2.466% | -2.576% | -2.048% | -0.7374% | -2.861% | -1.211% | 0.8609% | 0.836% | 1.035% | 1.093% | -2.979% | -0.4293% | -1.44% | -0.4767% | -1.653% | -0.2635% | -1.1% | -4.787% | 0.5258% | -0.6424% | -0.142% | 0.4548% | 0.1706% | -1.36% | -0.7139% | 0.5211% | -1.956% | -1.637% | -1.4% | 0.04866% | -1.61% | -0.453% | -0.9542% | -2.081% | -0.524% | 3.936% | -1.684% | 0.3152% | 0.09839% | 0.4879% | 0.7532%
2025-05-05 | -6.04% | -7.442% | -4.516% | -4.23% | -4.992% | -8.036% | -2.259% | -7.123% | -4.021% | -3.431% | -3.774% | -4.078% | -3.374% | -3.488% | -2.613% | -2.822% | -4.177% | -3.677% | -4.82% | -3.393% | -0.9194% | -1.89% | -0.8053% | -1.015% | -2.061% | -2.746% | -1.053% | -1.452% | -0.9004% | -0.7292% | -2.08% | -1.243% | -4.687% | -5.72% | -5.259% | -4.458% | -3.196% | -3.136% | -4.402% | -3.997% | -5.848% | -3.687% | -1.586% | -1.936% | -1.715% | 0.3424% | -0.692% | -1.488% | -5.103% | -2.107% | -1.335% | -3.902% | -5.058% | -5.095% | -6.295% | -5.436% | -4.611% | -8.267% | -8.378% | -8.823% | -4.421% | -5.87% | -4.41% | 1.614% | -0.007063% | 1.635% | 1.969% | 1.276% | 2.11% | -0.7958% | 2.974% | 1.371% | -0.3017% | -1.234% | -0.2757% | 2.237% | -1.071% | -1.264% | 1.804% | 2.931% | -0.4751% | 0.968% | 4.014% | 2.363% | 1.432% | 3.387% | 1.249% | 0.1311% | 2.654% | 1.44% | 1.059% | -2.538% | -0.1804% | 1.111% | 2.264% | 0.2443% | -1.197% | 0.5303% | 0.3483% | 0.8774% | 0.8683% | 1.527% | 0.4% | 0.8163% | 6.528% | 0.8857% | 3.46% | 0.773% | 0.903% | 3.737% | 3.399% | 1.284% | 2.909% | -0.1193% | -0.8131% | -1.012% | -0.7178% | 2.411% | -2.928% | 3.832% | 2.108% | -0.5964% | 2.146% | 3.487% | 4.786% | 4.136% | 2.411% | 4.214% | -3.344% | 1.943% | 1.406% | -13.93% | 1.232% | 3.98% | 1.553% | 0.4176% | -0.1012% | 3.13% | 0.3819% | 1.718% | 2.714% | 1.978% | 3.122% | 2.09% | 2.732% | 4.578% | 0.435% | 5.544% | 4.091% | 2.807% | 4.387% | 3.156% | 6.535% | -3.015% | 2.359% | 2.61% | -4.02% | -0.2497% | -0.9258% | -1.021% | 1.9% | 2.472% | 2.22% | 2.039% | 4.24% | 3.134% | 1.637% | 2.9% | 1.979% | 1.799% | 1.134% | 1.979% | 2.435% | 3.346% | 3.64% | 2.672% | 2.928% | 2.729% | 3.593% | 3.041% | 4.888% | -0.4002% | 3.222% | 3.042% | 3.65% | 3.621% | 2.909% | 3.707% | 1.913% | 3.46% | 0.8303% | 3.355% | 1.561% | 2.738% | 3.689% | 3.101% | 4.337% | -0.463% | 4.096% | 3.614% | 1.202% | 2.066% | 5.355% | 0.836% | 2.529% | 5.698% | 1.809% | 1.23% | 4.178% | 2.257% | 1.869% | -1.419% | 1.493% | 3.427% | 3.21% | 4.593% | 5.01% | 3.966% | -2.245% | -2.612% | 2.728% | -0.9208% | -3.043% | -1.728% | -1.454% | -4.081% | -0.3835% | 0.3603% | 2.352% | 2.323% | 1.909% | 0.1636% | 2.835% | 0.04153% | 3.792% | 1.781% | 1.722% | 1.446% | -0.8785% | 0.02275% | -1.076% | 0.4734% | 3.91% | 1.337% | 0.9822% | 1.018% | 2.303% | 0.2105% | -37.09% | -37.53% | 0.3701% | -0.5593% | -0.0148% | 2.68% | 0.5391% | 0.6048% | 0.6424% | -1.656% | -0.6641% | -1.697% | 1.037% | -0.3125% | 0.9592% | 1.044% | 2.017% | 3.524% | 3.917% | 0.9942% | 3.138% | 1.124% | -3.002% | -0.1615% | -1.324% | 1.247% | 3.834% | 2.345% | 0.5142% | 4.388% | 2.26% | -0.641% | -0.8024% | -0.622% | -0.3847% | -2.264% | -2.093% | -0.3088% | -1.761% | -2.093% | 1.201% | -1.897% | 0.9348% | 1.277% | 2.005% | 0.2902% | 0.5195% | 0.3358% | 1.272% | 0.3172% | 0.2696% | 0.7649% | -1.652% | 0.04101% | -0.1781% | 1.441% | 0.4696% | 2.586% | 1.136% | 1.295% | 2.981% | 1.686% | 0.1345% | -2.975% | 1.018% | -1.16% | -1.066% | -1.104% | 0.6789% | -1.257% | -1.733% | -2.418% | -1.315% | -1.315% | -0.3528% | -1.733% | -2.315% | -1.104% | -2.09% | -2.54% | -0.6524% | -0.7724% | 0.9428% | -1.226% | 2.421% | 0.8442% | 0.7654% | -1.62% | 0.4264% | -0.0148% | 0.2293% | -2.362% | 0.4452% | -0.6814% | -2.306% | 0.8395% | -0.2683% | 1.367% | 1.317% | 0.7175% | 0.3617% | 0.8639% | 2.027% | -2.113% | -0.7189% | -0.6532% | 1.278% | -1.656% | 0.2011% | -1.773% | -0.7626% | 0.05091% | -0.5851% | 0.1345% | 1.939% | 1.071% | 1.938% | 2.037%
2025-05-06 | -6.9% | -9.172% | -5.938% | -5.398% | -6.11% | -9.731% | -3.07% | -7.729% | -4.442% | -4.074% | -4.025% | -4.368% | -4.319% | -4.197% | -3.289% | -4.148% | -4.654% | -3.647% | -4.466% | -3.142% | -0.6402% | -1.45% | -0.6892% | -1.744% | -1.548% | -2.259% | -0.6892% | -1.597% | -0.4439% | -0.1006% | -1.646% | -1.401% | -5.668% | -6.848% | -6.538% | -5.402% | -4.266% | -4.834% | -5.619% | -5.273% | -7.532% | -4.72% | -2.064% | -2.73% | -2.635% | -0.1546% | -1.375% | -2.111% | -4.831% | -3.369% | -2.967% | -5.689% | -6.867% | -6.939% | -7.702% | -5.659% | -5.266% | -9.683% | -9.001% | -10.12% | -5.472% | -6.893% | -6.243% | 2.725% | 1.038% | 1.655% | 1.831% | 3.172% | 1.408% | 1.139% | 3.317% | 3.853% | 0.8369% | 0.2636% | 0.1107% | 0.55% | -0.6413% | 0.8369% | 3.049% | 3.027% | 1.217% | 2.706% | 0.5911% | 3.084% | 3.406% | 3.645% | 2.582% | 1.643% | 2.502% | 1.675% | 2.01% | -0.1239% | 1.753% | 2.122% | 2.468% | 3.161% | 2.771% | 3.351% | 2.189% | 1.531% | 1.157% | 2.859% | 0.7925% | 2.893% | 7.16% | 2.982% | 4.244% | 3.116% | 2.39% | 4.937% | 4.054% | 5.339% | 4.31% | 2.524% | 2.021% | 3.451% | -0.7495% | 3.328% | 4.289% | 3.161% | 2.3% | 2.781% | 1.94% | 3.283% | 3.194% | 1.898% | 0.7364% | 1.787% | -1.587% | 0.3565% | -0.4255% | -16.3% | 0.6135% | 2.189% | -0.02333% | -0.8724% | -1.552% | 3.518% | 1.517% | 0.6917% | 1.284% | 2.155% | 2.535% | 1.44% | 1.384% | 2.803% | 2.043% | 2.138% | 1.55% | -0.5596% | 0.6096% | 2.066% | 4.151% | 0.714% | 1.273% | 0.5464% | -4.246% | 1.541% | 1.708% | -0.1686% | 0.4347% | -3.263% | -1.051% | 2.631% | 3.853% | -0.1741% | -0.04567% | 1.41% | 0.1623% | 0.05221% | 0.1868% | 0.2847% | 0.6518% | 2.059% | 2.193% | 1.521% | 1.704% | 1.545% | 2.463% | 0.738% | 2.31% | -0.3844% | 2.12% | 2.157% | 2.805% | 1.9% | 1.79% | 1.949% | 1.153% | 2.181% | -0.0212% | 1.459% | -1.428% | 0.01551% | 0.6738% | -0.3412% | 1.483% | 0.04923% | 3.495% | 2.515% | 1.793% | 2.568% | 4.651% | 1.683% | 3.684% | 5.433% | 4.635% | 2.321% | -0.7167% | 2.849% | 2.193% | -0.2262% | 2.594% | 3.214% | 3.748% | 4.667% | 3.831% | 2.894% | 0.4125% | -0.4447% | 2.183% | -0.2241% | -2.06% | -2.284% | 0.2899% | -1.772% | -0.1622% | 0.8427% | 0.8635% | 1.232% | 0.5205% | -1.071% | 0.1647% | -1.616% | 2.871% | 0.8635% | -1.818% | -1.614% | -3.77% | -2.681% | -3.286% | -2.899% | 3.202% | 3.938% | -1.042% | 0.3202% | 1.207% | -3.431% | 0.4823% | -0.04285% | -1.713% | -1.459% | -1.713% | 0.6348% | -1.737% | -1.495% | -0.5632% | -1.271% | -0.05771% | -2.348% | 1.693% | 0.2408% | 2.488% | 0.972% | 1.765% | 2.46% | 1.905% | 0.3586% | 1.674% | 2.216% | -1.043% | -1.954% | 0.2819% | 0.296% | 1.369% | 0.1407% | 0.8116% | 2.226% | 1.247% | -0.4617% | -1.22% | -1.184% | -0.8899% | -3.068% | -2.016% | -0.8532% | -2.823% | -2.995% | 0.5294% | -1.107% | 0.1012% | -0.1191% | 0.6995% | -0.5724% | -0.9964% | -0.4329% | 0.6513% | -0.1834% | -0.07286% | 0.406% | -0.4851% | -1.301% | -1.988% | -0.6499% | -1.644% | 0.1822% | -0.6376% | 0.9699% | 0.7766% | -0.7523% | -1.767% | -2.282% | 0.2884% | -1.229% | -1.894% | -1.919% | -0.7651% | -2.669% | -3.455% | -1.537% | -1.69% | -1.652% | 0.2234% | -2.306% | -1.689% | -0.9626% | -1.979% | -1.846% | 0.4759% | -1.398% | 1.753% | -1.004% | 3.697% | 1.778% | 1.448% | 0.6832% | 1.784% | 2.099% | 1.264% | -1.737% | 1.99% | 1.542% | 1.361% | 3.515% | 1.615% | 3.329% | 3.811% | 3.14% | 1.37% | 2.846% | 4.078% | 2.148% | 1.458% | 1.361% | 4.18% | 1.363% | 3.019% | 2.344% | 1.283% | 2.269% | 0.3934% | 2.287% | 3.283% | 1.905% | 2.973% | 3.684%
2025-05-07 | -7.357% | -9.712% | -6.275% | -6.313% | -7.816% | -11.34% | -3.71% | -9.395% | -6.594% | -5.843% | -5.091% | -5.918% | -5.974% | -5.88% | -4.978% | -4.79% | -6.19% | -5.22% | -5.749% | -4.696% | -1.726% | -2.873% | -1.933% | -2.534% | -2.685% | -3.155% | -1.895% | -2.534% | -1.087% | -1.218% | -2.609% | -2.196% | -7.986% | -9.158% | -7.951% | -7.417% | -5.735% | -5.478% | -7.478% | -6.348% | -8.361% | -6.288% | -4.293% | -4.739% | -4.322% | -2.239% | -2.179% | -3.133% | -4.57% | -3.328% | -3.404% | -5.984% | -7.14% | -6.793% | -7.637% | -5.246% | -5.684% | -9.64% | -9.389% | -9.807% | -5.429% | -7.011% | -6.752% | 2.694% | 0.8184% | 1.004% | 1.94% | 2.968% | 1.061% | 0.3047% | 2.163% | 2.968% | 0.3647% | -0.2997% | 0.1506% | 0.9434% | -0.6321% | -0.5857% | 3.31% | 2.505% | 1.392% | 3.198% | -0.6029% | 3.656% | 4.337% | 3.772% | 3.333% | 2.09% | 2.077% | 1.812% | 1.906% | -0.7741% | 1.795% | 2.026% | 3.293% | 3.584% | 2.946% | 2.069% | 2.959% | 2.465% | 1.409% | 3.524% | 0.8172% | 3.567% | 6.016% | 2.694% | 4.44% | 2.711% | 2.574% | 5.219% | 4.492% | 1.221% | 4.015% | 2.662% | 2.197% | 4.363% | 0.4674% | 4.021% | 3.704% | 3.627% | 2.317% | 2.873% | 2.286% | 3.351% | 3.002% | 2.291% | 0.9126% | 2.685% | 2.342% | 1.94% | 1.486% | -5.064% | 2.24% | 3.627% | 1.127% | 1.135% | -0.9274% | 3.096% | 1.237% | -0.06345% | -0.346% | 1.666% | 1.889% | 1.05% | 0.8441% | 2.745% | 2.462% | 2.411% | 2.329% | 0.2004% | 1.92% | 2.642% | 4.54% | 1.829% | 2.745% | -0.6799% | -3.334% | 2.865% | 3.027% | 0.2191% | 1.769% | 1.812% | -0.0292% | 3.354% | 4.62% | 1.319% | -1.47% | 0.1612% | -0.8985% | -1.217% | -1.048% | -0.8797% | -0.07324% | 0.9958% | 1.887% | 0.6301% | 0.3956% | 0.4707% | 1.549% | -0.2364% | 1.494% | -0.8558% | 1.652% | 1.53% | 2.234% | 1.549% | 0.8082% | 1.99% | 0.7895% | 2.187% | -0.2045% | 2.506% | -0.03573% | 0.7801% | 1.477% | 0.9944% | 1.034% | -0.9246% | 2.093% | 0.6539% | 0.8061% | 0.9045% | 1.934% | 0.7821% | -0.1878% | 2.64% | 2.657% | -0.09507% | 0.56% | 0.006523% | -0.7637% | -1.19% | 1.31% | 0.9168% | 2.426% | 2.598% | 2.22% | 0.7253% | -0.8572% | -2.187% | -0.2951% | -1.691% | -2.935% | -1.268% | -0.3053% | -1.984% | 0.3564% | 1.242% | 1.579% | 1.53% | 1.014% | -0.1419% | 2.309% | 0.0158% | 2.825% | 0.8779% | 0.3423% | 0.7415% | -2.711% | -0.4201% | -3.898% | -0.5314% | 2.738% | 2.835% | -1.177% | -0.1233% | 1.219% | -2.414% | 0.03064% | -1.004% | 0.1364% | -0.7911% | -2.294% | -0.03057% | -1.44% | -0.1975% | -0.03057% | 2.198% | 0.2496% | -1.314% | 2.961% | 4.418% | 4.474% | 0.06473% | 3.809% | 4.641% | 3.733% | 2.471% | 3.508% | 3.726% | -0.4576% | -0.5436% | 2.182% | 1.845% | 2.435% | 1.234% | 2.81% | 3.409% | 2.853% | 0.405% | 0.1612% | 0.2644% | 0.4894% | -2.127% | -1.283% | 0.5738% | -1.339% | -1.48% | 2.168% | 1.401% | 1.999% | 2.477% | 2.55% | -0.2069% | 0.2953% | 0.6584% | 1.98% | 0.8324% | 0.9359% | 1.566% | 0.2736% | 0.6442% | 0.3901% | 2.103% | 1.002% | 2.612% | 1.933% | 3.546% | 3.397% | 1.91% | -0.2907% | -3.338% | 1.89% | -0.114% | -3.119% | -0.1882% | 0.9649% | -1.532% | -2.692% | -0.7325% | -0.8166% | -0.5342% | 0.5815% | -1.069% | -1.904% | -0.4294% | -0.9858% | -3.592% | 1.341% | -1.196% | 0.7902% | -3.806% | 2.611% | -0.3784% | -1.527% | -0.2624% | 1.963% | 1.314% | 1.843% | -1.069% | 1.899% | 1.036% | 1.936% | 2.418% | 1.064% | 1.745% | 1.832% | 2.158% | 0.5288% | 1.384% | 2.699% | 0.3033% | 1.008% | 1.379% | 2.105% | 1.366% | 0.869% | 1.516% | 0.08907% | 1.88% | 0.3812% | 0.8876% | 2.487% | 2.913% | 2.991% | 2.923%
2025-05-08 | -7.899% | -9.971% | -6.909% | -6.853% | -8.203% | -11.85% | -4.592% | -10.28% | -7.219% | -6.375% | -6.235% | -6.937% | -6.235% | -6.459% | -5.56% | -5.391% | -7.159% | -5.65% | -6.544% | -5.503% | -2.72% | -3.423% | -2.664% | -3.057% | -3.817% | -4.351% | -2.326% | -2.664% | -1.961% | -1.708% | -3.339% | -2.355% | -7.612% | -9.231% | -8.225% | -7.515% | -5.828% | -6.124% | -7.612% | -6.331% | -8.034% | -5.366% | -3.538% | -3.963% | -3.529% | -1.337% | -1.497% | -2.604% | -3.975% | -3.295% | -3.573% | -6.29% | -7.62% | -7.026% | -7.68% | -5.517% | -5.547% | -9.327% | -9.353% | -9.67% | -6.263% | -7.159% | -6.783% | 1.106% | -0.3544% | -0.005425% | 0.7341% | 2.271% | -0.03268% | -0.8922% | 1.234% | 2.015% | -0.4696% | -1.265% | -0.713% | -0.1227% | -1.287% | 0.1194% | 1.567% | 1.106% | 0.1066% | 1.569% | -2.595% | 1.859% | -2.544% | 2.22% | 2.153% | 1.135% | 1.054% | 0.2475% | 0.5805% | -1.494% | 1.144% | 1.362% | 2.617% | 3.001% | 2.937% | 1.451% | 1.912% | 1.377% | 0.2254% | 2.476% | -0.3769% | 2.95% | 7.048% | 1.451% | 3.475% | 1.797% | 1.746% | 4.32% | 3.423% | 4.179% | 2.67% | 1.899% | 0.9647% | 4.038% | 2.45% | 3.001% | 1.925% | 2.079% | 1.861% | 2.412% | 1.296% | 2.14% | 2.681% | 2.181% | 0.2603% | 2.463% | 1.323% | 1.221% | 0.6829% | -5.823% | 2.053% | 3.257% | 0.8622% | 1.093% | -0.8725% | 3.782% | 2.089% | 0.3884% | 0.4012% | 2.04% | 2.258% | 1.656% | 1.349% | 3.167% | 2.898% | 2.368% | 2.133% | -0.02899% | 1.633% | 3.065% | 4.339% | 1.861% | 2.604% | 1.592% | -1.93% | 2.181% | 2.565% | 0.5421% | 1.067% | 1.041% | -0.1879% | 4.023% | 0.6573% | 0.5199% | -0.6825% | 1.548% | 0.4116% | -0.416% | 0.3414% | 0.7061% | 1.351% | 2.137% | 3.034% | 1.562% | 1.057% | 1.646% | 2.894% | 0.3807% | 1.912% | -0.5645% | 2.487% | 2.165% | 3.133% | 2.642% | 1.856% | 3.062% | 1.295% | 2.543% | -0.03728% | 2.866% | 0.5238% | 2.067% | 2.001% | 1.441% | 2.325% | -2.336% | 0.6167% | -0.3437% | -0.417% | -0.2715% | 0.7214% | 0.1855% | 1.844% | 2.447% | 2.68% | -0.06827% | 0.7527% | -0.09539% | -1.209% | -2.805% | -0.4456% | -1.159% | 0.4137% | 0.689% | 0.5778% | -1.328% | -1.987% | -3.012% | -2.451% | -2.508% | -2.808% | -2.508% | -1.921% | -2.358% | 0.3952% | 1.534% | 1.943% | 1.04% | 1.521% | -0.3035% | 2.861% | 0.4595% | 2.526% | 0.4283% | 1.069% | 1.987% | -0.9832% | -0.2064% | -1.122% | 0.09882% | 2.38% | 2.54% | -1.218% | -1.51% | 0.4574% | -1.788% | -0.4748% | -2.384% | 0.2792% | -1.205% | -0.0399% | -0.3312% | -0.4144% | -0.1647% | 0.09882% | -0.05503% | -1.871% | -0.6895% | 0.7819% | 2.577% | 2.844% | 1.272% | 1.578% | 2.368% | 1.869% | 0.9824% | 2.209% | 2.284% | -0.3058% | -2.503% | 1.638% | 0.003451% | 1.003% | -0.2434% | 1.755% | 1.942% | 1.507% | 0.4396% | -0.02325% | -0.4861% | 0.0609% | -2.786% | -2.309% | 0.08895% | -1.496% | -2.169% | 1.534% | 0.9519% | 0.9866% | 1.393% | 1.824% | -0.6502% | -0.9742% | -0.44% | 0.8451% | -0.005732% | -0.005732% | 0.9091% | 0.7525% | -0.5124% | -0.6813% | 1.191% | 0.1772% | 1.519% | 0.712% | 2.642% | 1.942% | 0.6458% | 2.162% | -1.323% | 2.737% | 0.3069% | -2.135% | -0.01216% | 0.7783% | -1.323% | -0.2202% | 0.6732% | -0.9117% | -0.1398% | 1.944% | 0.8756% | -0.8445% | 0.9866% | -0.06764% | -0.6364% | 2.449% | -0.2854% | 1.346% | -3.053% | 4.055% | 3.851% | 2.162% | -0.4561% | 1.93% | 1.361% | -1.288% | 0.5705% | 1.902% | 1.25% | 1.833% | 2.61% | 0.7369% | 1.506% | 1.958% | 2.513% | 89.15% | 1.375% | 3.079% | 1.176% | 1.431% | 1.652% | 1.87% | 1.931% | 1.639% | 2.474% | 0.4137% | 1.861% | 0.6468% | 1.506% | 2.372% | 3.633% | 3.502% | 3.05%
2025-05-09 | -6.58% | -9.362% | -5.933% | -6.199% | -7.395% | -10.03% | -3.755% | -9.174% | -5.883% | -5.733% | -4.969% | -5.717% | -6.199% | -5.683% | -5.135% | -5.185% | -6.09% | -5.443% | -5.999% | -4.902% | -1.811% | -3.174% | -2.459% | -2.974% | -2.925% | -3.456% | -2.692% | -3.473% | -1.878% | -2.01% | -3.49% | -3.274% | -7.744% | -8.469% | -7.63% | -7.385% | -6.038% | -5.81% | -7.229% | -6.597% | -8.625% | -6.615% | -4.261% | -5.433% | -4.952% | -3.009% | -3% | -3.948% | -5.181% | -4.655% | -4.287% | -6.712% | -7.927% | -7.691% | -8.294% | -6.399% | -6.882% | -11.09% | -10.64% | -11.04% | -6.265% | -7.899% | -7.182% | 2.529% | 0.8026% | 0.3041% | 2.294% | 4.027% | 2.021% | 0.6436% | 2.597% | 3.967% | 1.022% | 1.027% | 0.9085% | 1.95% | 0.4223% | -0.6585% | 0.7798% | 0.477% | -0.1058% | 0.9335% | 0.5603% | 2.013% | 2.074% | 2.108% | 1.609% | 0.3376% | 0.7344% | -2.99% | 0.7571% | 3.157% | 4.815% | 5.019% | 4.951% | 5.458% | 4.466% | 4.323% | 3.853% | 4.087% | 3.311% | 3.354% | 0.8332% | 4.323% | 9.024% | 4.716% | 5.572% | 4.307% | 3.929% | 5.973% | 4.701% | 5.852% | 3.662% | 2.053% | 1.423% | 2.718% | 2.195% | 2.536% | 1.885% | 1.529% | 1.507% | 2.226% | 1.166% | 2.013% | 2.324% | 1.416% | 0.04555% | 1.908% | 1.022% | 1.09% | 0.8555% | -7.176% | 1.597% | 3.248% | 0.954% | 1.166% | -1.738% | 2.809% | 0.6917% | 0.6587% | 0.07583% | 1.65% | 2.294% | 1.438% | 1.045% | 2.862% | 2.347% | 2.82% | 2.283% | -1.722% | 3.248% | 2.12% | 4.019% | 0.8783% | 1.726% | 1.544% | -2.233% | 0.4695% | 0.007702% | 1.62% | 1.56% | 1.855% | -0.068% | 2.007% | 3.384% | -1.635% | 1.266% | 1.059% | 2.211% | 1.987% | 1.855% | 2.07% | 2.352% | 3.372% | 3.704% | 2.941% | 2.875% | 2.883% | 3.82% | 1.959% | 3.441% | 1.087% | 3.563% | 3.273% | 3.737% | 3.198% | 2.526% | 3.389% | 2.385% | 3.563% | 1.39% | 3.538% | 1.233% | 2.402% | 2.751% | 2.29% | 3.222% | -0.5672% | 2.139% | 0.9077% | 1.004% | 1.282% | 2.795% | 1.051% | 2.6% | 3.167% | 2.952% | 0.2972% | 1.745% | 0.8831% | 0.481% | -1.463% | 0.8216% | 0.8819% | 2.208% | 2.67% | 2.086% | 1.156% | -0.7353% | -0.9563% | -0.07693% | -1.21% | -1.398% | -3.225% | -1.01% | -3.801% | 1.933% | 3.06% | 3.077% | 3.086% | 2.44% | 1.646% | 3.99% | 1.432% | 4.007% | 2.673% | 2.81% | 2.871% | 0.7519% | 0.8667% | 0.2025% | 0.8749% | 4.283% | 4.352% | 0.8044% | 2.195% | 2.475% | 0.3091% | 1.424% | 0.4977% | 1.933% | 0.8749% | 1.49% | 2.334% | 0.8503% | 1.162% | 1.916% | -0.5012% | -1.905% | -0.005691% | 0.01173% | 0.7237% | 1.015% | 0.4855% | 0.7074% | 1.792% | 1.567% | 0.6157% | 1.589% | 1.163% | -3.273% | -1.004% | -1.341% | 0.1615% | 1.281% | -0.1446% | 0.9152% | 1.705% | 0.8842% | 0.1966% | -0.6574% | -0.7154% | -0.05214% | -2.689% | -1.71% | -0.5828% | -2.025% | -2.282% | 1.241% | -1.287% | 0.7438% | 0.6194% | 1.376% | -0.6872% | -0.6785% | -0.4194% | 0.791% | -0.1603% | -0.2518% | 0.4803% | -0.1288% | -0.8175% | -1.034% | 1.229% | -0.09371% | 1.025% | 0.4886% | 1.722% | 1.515% | 0.5141% | 0.5289% | -1.518% | 1.785% | -0.3879% | -2.667% | -0.8389% | 0.07016% | -2.074% | -2.856% | -1.362% | -1.116% | -0.6076% | 0.5797% | -0.8881% | -1.454% | -1.159% | -1.413% | -1.716% | 0.5768% | -1.184% | 0.503% | 0.5805% | 2.501% | 2.974% | 1.433% | -0.09268% | 1.08% | 1.105% | -2.462% | 0.1041% | 1.449% | -0.3551% | 1.309% | 1.58% | 0.04672% | 1.166% | 0.9938% | 0.9323% | -0.633% | 0.3911% | 1.467% | 0.4694% | -0.2567% | -0.2321% | 1.588% | -0.1803% | 0.7027% | 0.4459% | -0.6851% | 0.4239% | -0.6765% | -0.1685% | 0.8715% | 0.9077% | 1.588% | 1.398%
2025-05-10 | -7.651% | -10.15% | -6.815% | -6.926% | -7.883% | -10.55% | -4.519% | -9.845% | -6.336% | -5.89% | -5.794% | -6.336% | -5.937% | -5.826% | -4.805% | -5.124% | -6.426% | -5.973% | -6.91% | -5.571% | -2.875% | -3.944% | -3.051% | -3.194% | -4.231% | -4.327% | -3.258% | -3.753% | -3.115% | -3.035% | -4.151% | -3.753% | -7.979% | -8.625% | -7.803% | -7.416% | -5.704% | -5.436% | -7.086% | -6.342% | -8.425% | -6.514% | -4.114% | -5.329% | -4.775% | -2.785% | -2.883% | -3.74% | -4.766% | -4.291% | -3.987% | -6.466% | -7.698% | -7.338% | -8.204% | -6.247% | -6.923% | -10.95% | -10.65% | -10.99% | -6.336% | -7.949% | -6.904% | 1.306% | -0.575% | -1.956% | 0.551% | 2.004% | 0.1399% | -0.6113% | 1.408% | 2.287% | 0.04974% | -0.5071% | 0.02795% | 0.6788% | -0.5591% | -1.163% | 1.532% | 0.6091% | -0.1537% | 1.081% | 1.67% | -0.7414% | 1.917% | 2.456% | 1.438% | 0.5109% | 0.6527% | -2.929% | 0.3548% | 0.5292% | 2.294% | 2.229% | 2.723% | 3.406% | 2.164% | 2.447% | 2.498% | 2.076% | 1.446% | 2.309% | -0.168% | 2.549% | 7.379% | 2.963% | 3.66% | 2.142% | 1.75% | 4.023% | 3.268% | 1.038% | 2.959% | 1.286% | 0.8488% | 2.556% | 1.8% | 2.679% | 2.214% | 1.895% | 1.415% | 2.44% | 1.628% | 2.441% | 2.665% | 1.844% | 0.4929% | 2.345% | 1.648% | 1.633% | 1.277% | -7.062% | 2.004% | 3.42% | 1.299% | 1.444% | -1.227% | 2.723% | 0.433% | 0.08606% | -0.4006% | 1.873% | 2.047% | 1.001% | 0.7834% | 2.374% | 0.05701% | 2.517% | 1.986% | 0.1699% | 1.24% | 2.026% | 4.113% | 1.197% | 2.062% | 1.474% | -2.195% | 1.103% | 0.3694% | 0.965% | 1.256% | 1.074% | -0.7057% | 2.571% | 3.718% | 0.5269% | -1.075% | -2.38% | 0.588% | 0.6437% | 1.24% | 1.527% | 1.988% | 3.102% | 3.659% | 2.672% | 1.543% | 1.638% | 3.229% | 1.006% | 2.919% | 0.7851% | 3.301% | 3.206% | 3.866% | 3.381% | 2.855% | 3.635% | 2.505% | 3.898% | 1.455% | 3.802% | 1.049% | 2.251% | 2.744% | 2.201% | 2.994% | -0.9994% | 1.594% | 0.3753% | 0.1452% | 0.3297% | 1.388% | 0.5144% | 1.752% | 1.444% | -0.3887% | -1.832% | -0.8182% | -1.666% | -2.228% | -1.894% | 0.597% | 0.7223% | 1.549% | 2.263% | 1.51% | 0.6957% | -2.308% | -2.717% | -1.209% | -2.385% | -2.446% | -2.274% | -1.269% | -3.825% | 0.8267% | 2.006% | 1.697% | 1.796% | 1.078% | 0.1829% | 2.548% | -0.2577% | 3.242% | 2.028% | 1.871% | 0.9619% | -1.139% | 0.1987% | -1.186% | 0.05703% | 3.548% | 0.0531% | 0.06136% | 1.914% | 2.168% | -0.242% | 1.003% | -0.06887% | 1.363% | 0.655% | 0.4977% | 0.8596% | 0.238% | 1.064% | 1.3% | 0.5413% | -0.3196% | 1.357% | 0.9834% | 1.808% | 1.878% | 1.402% | 1.749% | 2.967% | 2.42% | 1.393% | 2.239% | 1.63% | -1.55% | -2.646% | -1.041% | 0.2252% | 0.9986% | -0.03871% | -1.646% | 1.745% | 1.525% | 1.972% | 1.248% | 1.36% | 1.758% | -2.61% | 0.1186% | 1.376% | 0.05493% | -0.1997% | 3.07% | 1.612% | 2.649% | 2.283% | 3.103% | 1.065% | 1.123% | 1.189% | 2.366% | 1.378% | 1.514% | 1.817% | 2.234% | 0.6678% | 0.6758% | 2.041% | 1.163% | 2.848% | 2.065% | 2.991% | 2.744% | 1.608% | 1.582% | -0.6905% | 3.295% | 1.308% | -2.516% | 1.025% | 1.917% | -0.2382% | -0.5095% | -0.06708% | 0.8297% | 1.276% | 2.095% | 0.3875% | 0.655% | 0.6% | 0.6314% | -0.2735% | 2.594% | 0.8545% | 1.672% | 1.573% | 3.102% | 2.862% | 2.598% | 0.6865% | 1.89% | 2.473% | -1.517% | 1.93% | 2.488% | 1.387% | 2.614% | 3.425% | 1.544% | 2.961% | 2.862% | 3.055% | 1.832% | 2.556% | 3.788% | 2.171% | 1.167% | 1.332% | 3.523% | 1.893% | 2.78% | 2.351% | 1.276% | 2.78% | 1.821% | 1.788% | 3.136% | 3.49% | 4.11% | 3.788%
2025-05-11 | -7.432% | -9.773% | -6.407% | -6.46% | -7.934% | -11.7% | -3.96% | -9.917% | -6.568% | -5.871% | -5.389% | -6.273% | -5.924% | -6.005% | -5.013% | -5.013% | -6.417% | -5.232% | -5.817% | -4.799% | -1.959% | -3.057% | -2.28% | -2.682% | -2.843% | -3.915% | -1.905% | -2.388% | -1.101% | -1.503% | -2.843% | -2.522% | -7.613% | -8.87% | -7.912% | -7.347% | -5.712% | -5.881% | -7.425% | -6.191% | -8.095% | -5.852% | -3.876% | -4.468% | -3.874% | -1.546% | -1.622% | -2.498% | -4.055% | -3.347% | -3.099% | -6.179% | -7.852% | -6.782% | -7.548% | -5.502% | -5.303% | -9.445% | -8.951% | -9.709% | -5.898% | -6.875% | -6.574% | 2.543% | 0.7851% | 1.466% | 1.578% | 3.299% | 0.9296% | 0.07721% | 2.079% | 3.165% | 0.2847% | -0.4804% | 0.1382% | 0.7346% | -0.7327% | 1.115% | 2.359% | 1.859% | 0.602% | 2.843% | 3.25% | 2.827% | 4.373% | 3.669% | 3.223% | 2.176% | 2.359% | 1.383% | 1.469% | 0.1382% | 2.359% | 2.628% | 3.653% | 4.471% | 4.265% | 3.568% | 3.385% | 2.406% | 1.628% | 3.812% | 1.134% | 4.422% | 8.242% | 3.275% | 4.813% | 3.092% | 2.543% | 5.447% | 4.727% | 5.679% | 3.994% | 3.401% | 1.249% | 3.922% | 2.872% | 3.092% | 2.518% | 2.213% | 1.761% | 2.298% | 1.398% | 2.329% | 2.787% | 1.969% | 0.3945% | 2.347% | 1.371% | 1.298% | 0.6386% | -3.389% | 1.835% | 3.006% | 0.7485% | 1.163% | -1.141% | 3.97% | 2.311% | 0.4311% | 0.4311% | 2.396% | 2.555% | 1.713% | 1.273% | 2.274% | 2.811% | 2.546% | 2.2% | 0.288% | 1.783% | 2.945% | 4.489% | 2.103% | 2.506% | 1.7% | -2.095% | 2.286% | 2.701% | 0.9559% | 1.456% | 1.432% | 0.01618% | 3.638% | 4.825% | 0.9515% | 0.4654% | 2.337% | 1.227% | 0.8531% | 1.308% | 1.374% | 1.815% | 2.658% | 3.54% | 2.404% | 2.35% | 3.326% | 3.647% | 1.545% | 3.143% | 0.977% | 3.513% | 3.166% | 3.821% | 3.166% | 2.537% | 3.54% | 2.444% | 3.46% | 1.013% | 3.553% | 0.9065% | 2.337% | 2.569% | 1.966% | 2.962% | -0.9984% | 2.237% | 1.123% | 1.174% | 1.633% | 2.697% | 1.62% | 3.154% | 3.808% | 3.842% | 0.9274% | 1.621% | 1.437% | 0.7035% | 2.018% | 1.84% | 1.359% | 2.289% | 2.748% | 2.076% | 1.3% | 0.3133% | -2.293% | 0.7979% | -0.8835% | -2.13% | -2.728% | 1.086% | -0.6813% | 1.028% | 2.341% | 2.4% | 1.859% | 2.178% | 0.1943% | 2.719% | 0.5776% | 3.524% | 1.928% | 2.011% | 1.234% | -4.406% | 0.4058% | -5.556% | 0.3926% | 3.982% | 3.83% | -0.001386% | 0.7231% | 2.095% | 0.04885% | 1.012% | -0.3081% | 1.199% | 0.08851% | -1.974% | 0.3397% | -0.9823% | 0.7892% | 1.159% | 0.2207% | -1.253% | 1.005% | 0.9524% | 2.72% | 3.032% | 1.631% | 1.739% | 2.644% | 2.164% | 1.223% | 2.24% | 2.447% | 0.1389% | -2.184% | 1.598% | 0.5562% | 1.269% | 0.0819% | 1.778% | 2.135% | 1.394% | 1.067% | 0.4253% | 0.2115% | 0.6392% | -3.571% | -0.9648% | 0.4654% | -1.5% | -1.473% | 2.083% | 1.115% | 1.334% | 1.602% | 2.275% | -0.06925% | -0.01311% | 0.2384% | 1.598% | 1.023% | 0.7815% | 1.519% | 1.368% | 0.1779% | 0.01698% | 1.385% | 0.5937% | 2.087% | 1.238% | 3.112% | 2.12% | 0.8851% | -7.358% | -11.4% | 3.552% | 0.5644% | 0.419% | 0.2207% | 1.18% | -1.27% | -11.53% | -2.82% | -0.5289% | -0.6399% | 1.781% | -4.301% | -0.08335% | -1.577% | -1.776% | -14.24% | 2.573% | 0.2624% | 0.6094% | -26.39% | -1.639% | -0.05691% | -20.74% | -0.4799% | 1.12% | 1.186% | -1.987% | 0.3397% | 1.503% | 0.7098% | 1.543% | 2.362% | 0.4455% | 1.498% | 1.886% | 2.124% | 0.2792% | 1.067% | 2.553% | 0.6498% | -0.07013% | 0.7627% | 1.539% | 1.142% | 1.08% | 1.849% | -0.001386% | 1.252% | 0.2901% | 1.095% | 1.609% | 2.983% | 2.983% | 2.511%
2025-05-12 | -3.204% | -5.659% | -2.023% | -2.133% | -3.969% | -7.172% | 0.4164% | -5.291% | -2.151% | -1.656% | -0.9948% | -1.637% | -2.206% | -1.38% | -0.8662% | -0.701% | -1.755% | -1.156% | -2.427% | -0.701% | 2.126% | 0.7676% | 1.392% | 1.373% | 0.9879% | 0.07001% | 1.686% | 0.4923% | 2.2% | 2.016% | 0.6024% | 0.9512% | -4.648% | -5.427% | -4.267% | -3.9% | -2.045% | -1.601% | -3.987% | -2.799% | -4.997% | -3.553% | -1.91% | -2.786% | -1.918% | -0.2111% | -0.7629% | -1.555% | -3.484% | -0.8878% | -1.186% | -3.948% | -5.307% | -4.156% | -4.492% | -3.815% | -2.874% | -6.961% | -6.398% | -7.468% | -1.913% | -3.995% | -4.348% | 4.339% | 2.759% | 4.883% | 4.331% | 3.871% | 3.823% | 2.09% | 5.61% | 4.038% | 2.558% | 1.01% | 2.399% | 4.178% | 3.286% | -1.832% | 4.339% | 5.677% | 2.14% | 3.51% | 6.279% | 5.052% | 6.697% | 6.154% | 4.047% | 2.483% | 5.527% | 3.604% | 3.846% | 0.9194% | 3.043% | 4.473% | 5.569% | 4.189% | 3.07% | 5.426% | 4.139% | 4.047% | 4.222% | 4.9% | 3.878% | 4.44% | 8.947% | 4.055% | 6.137% | 3.378% | 3.361% | 6.463% | 6.012% | 4.574% | 4.257% | 3.374% | 3.612% | 4.214% | -0.7363% | 5.201% | 2.6% | 5.845% | 4.331% | 2.098% | 3.968% | 5.673% | 6.271% | 4.507% | 3.921% | 5.544% | 3.846% | 3.42% | 2.107% | -1.062% | 2.065% | 3.16% | 1.438% | -1.146% | -0.2893% | -1.071% | -2.846% | -2.542% | -1.706% | -2.124% | -1.062% | 0.04976% | -1.221% | 0.1668% | -0.4938% | 1.083% | 0.05603% | -3.026% | 0.7003% | -0.2847% | 1.592% | -1.138% | 0.125% | -1.489% | -2.024% | 0.03303% | 1.229% | -1.69% | -0.1927% | -0.3014% | -1.096% | 1.314% | 2.349% | -0.2281% | -5.395% | -4.003% | -4.782% | -5.047% | -5.011% | -4.736% | -3.802% | -2.84% | -1.778% | -2.968% | -3.564% | -3.023% | -2.52% | -3.627% | -1.402% | -4.625% | -2.346% | -2.19% | -1.549% | -1.558% | -2.337% | -1.082% | -2.392% | -0.972% | -2.95% | -0.7705% | -2.62% | -1.467% | -0.7998% | -1.194% | -0.9152% | -4.225% | -0.669% | -2.071% | -3.778% | -3.175% | -0.9087% | -4.158% | -2.439% | -0.8324% | -3.688% | -4.411% | -2.984% | -2.404% | -3.465% | -2.457% | -2.137% | -1.367% | 0.1834% | -4.428% | 0.0402% | -1.355% | -4.998% | -4.593% | -2.603% | -4.935% | -5.974% | -4.633% | -4.528% | -6.191% | -1.765% | -1.324% | 0.2499% | -1.357% | -1.148% | -2.16% | -0.3302% | -2.993% | 0.773% | -1.015% | -0.7392% | -2.632% | -4.56% | -3.301% | -4.433% | -3.383% | 1.191% | 1.572% | -2.508% | -1.707% | -0.644% | -3.075% | -1.139% | -2.658% | -2.821% | -3.355% | -3.627% | -2.368% | -3.482% | -2.83% | -3.509% | 2.808% | -3.857% | 3.193% | 2.78% | 0.942% | 3.339% | 0.03768% | 1.547% | 5.316% | 5.36% | 3.027% | 4.192% | 2.542% | -0.2626% | 0.2882% | -0.4372% | 1.088% | 2.005% | 1.17% | 1.258% | 3.334% | 3.431% | 1.235% | 1.043% | 1.116% | 1.391% | -1.842% | -0.4316% | 1.281% | -0.06532% | -0.5599% | 2.847% | 0.3257% | 2.481% | 2.673% | 3.768% | 1.787% | 2.114% | 1.809% | 2.888% | 2.068% | 2.261% | 2.702% | -0.5277% | 1.553% | 1.084% | 2.977% | 1.838% | 4.206% | 2.619% | 3.003% | 4.383% | 3.335% | 0.7159% | -4.449% | 2.893% | 0.2857% | 0.6842% | 0.6571% | 2.325% | 0.5808% | -3.129% | -1.316% | 0.2214% | 0.345% | 0.7295% | -0.9914% | -1.218% | -0.4389% | -1.037% | -3.147% | 1.044% | 0.4497% | 0.03119% | -5.418% | 2.713% | 2.047% | -3.811% | -0.9189% | 0.4578% | 0.2676% | -2.133% | -0.2215% | 0.9107% | 0.08645% | 0.7295% | 1.264% | 0.02304% | 2% | 2.523% | 1.608% | 1.692% | 1.087% | 2.314% | -1.065% | -0.2306% | -0.2577% | 1.762% | -0.7971% | 0.4216% | -0.4945% | -0.3873% | 0.7114% | -0.14% | 0.4782% | 2.443% | 1.657% | 2.342% | 2.447%
2025-05-13 | -5.395% | -7.71% | -4.445% | -4.64% | -6.06% | -9.669% | -1.807% | -7.842% | -4.473% | -4.417% | -2.858% | -4.027% | -4.334% | -4.417% | -3.276% | -3.276% | -4.691% | -3.284% | -3.498% | -2.83% | 0.7893% | -0.742% | -0.5471% | -1.243% | -0.4636% | -1.104% | 0.2047% | -0.5193% | 1.458% | 0.678% | -0.5471% | -0.9647% | -6.199% | -7.446% | -6.567% | -6.01% | -4.193% | -4.34% | -5.865% | -4.457% | -9.735% | -4.581% | -2.666% | -3.472% | -2.989% | -0.7007% | -1.026% | -2.094% | -4.526% | -2.619% | -2.57% | -5.335% | -6.582% | -5.901% | -6.191% | -4.661% | -4.44% | -8.765% | -7.739% | -8.759% | -3.638% | -5.253% | -5.776% | 5.158% | 3.585% | 4.633% | 4.815% | 5.602% | 3.772% | 2.888% | 5.132% | 5.437% | 2.609% | 1.891% | 2.152% | 3.189% | 1.651% | 0.8585% | 4.549% | 4.638% | 3.014% | 4.471% | 5.5% | 5.271% | 5.132% | 5.708% | 5.125% | 3.784% | 5.259% | 4.27% | 4.333% | 2.634% | 4.397% | 4.955% | 5.893% | 5.538% | 4.854% | 5.399% | 4.815% | 4.754% | 3.905% | 5.475% | 2.885% | 6.134% | 6.096% | 5.411% | 7.263% | 5.17% | 4.815% | 7.834% | 7.085% | 7.39% | 4.311% | 5.178% | 3.687% | 5.323% | 4.536% | 5.284% | -6.636% | 4.739% | 3.94% | 4.295% | 3.786% | 5.019% | 4.917% | 1.34% | 2.85% | 4.549% | 0.8078% | 3.23% | 2.203% | -7.613% | 2.799% | 4.029% | 1.962% | 2.051% | 0.2988% | 2.761% | 0.8636% | 0.1483% | 0.5922% | 1.264% | 1.848% | 1.772% | 1.328% | 2.621% | 2.368% | 2.884% | 2.271% | -3.811% | 2.526% | 2.571% | 4.992% | 1.924% | 2.672% | -1.272% | -2.439% | 2.913% | 3.205% | 1.366% | 2.051% | 1.442% | 0.4527% | 3.535% | 4.803% | -4.726% | -3.176% | -2.148% | -2.884% | -2.967% | -2.8% | -2.537% | -1.745% | -0.6059% | 0.4219% | -0.9532% | -1.87% | -0.6476% | -0.6198% | -1.703% | 0.03067% | -2.764% | -0.9254% | -0.4115% | 0.5886% | 0.2274% | -0.6337% | 0.4636% | -0.6615% | 0.4913% | -1.717% | 0.3663% | -1.203% | -0.3004% | -0.2594% | -0.5365% | 0.6594% | -1.981% | 1.146% | 0.1879% | -1.058% | -0.6386% | 0.742% | -0.6198% | 0.7536% | 1.371% | -3.85% | -1.551% | 0.04892% | 0.1151% | -0.9773% | -2.695% | -0.3434% | 1.976% | 1.356% | 0.9981% | 1.24% | 0.1975% | -5.043% | -5.512% | -1.431% | -1.166% | -4.764% | -4.866% | -2.394% | -4.442% | -1.957% | -1.157% | -0.1294% | -0.8073% | -0.2304% | -2.358% | 1.515% | -1.547% | 0.4764% | -1.226% | -0.7208% | -0.07172% | -1.904% | -2.907% | -2.426% | -2.509% | 0.837% | 1.111% | -2.495% | -2.426% | -1.283% | -3.718% | -1.745% | -3.278% | -2.11% | -2.646% | -0.8602% | -0.558% | -2.303% | -1.863% | -1.3% | 0.1014% | -0.9299% | 3.25% | 3.127% | 2.144% | 4.477% | -3.799% | 0.08856% | 4.966% | 4.604% | 3.287% | 4.035% | 3.329% | 0.9511% | -0.3503% | 1.625% | 1.628% | 2.842% | 1.72% | 2.535% | 3.685% | 3.143% | 0.1024% | -0.2726% | -0.342% | -0.592% | -2.662% | -1.675% | -0.06424% | -1.689% | -2.078% | 1.714% | -0.8408% | 1.297% | 1.769% | 2.234% | -0.04063% | -0.4198% | 0.2007% | 1.991% | 1.155% | 1.029% | 1.81% | -0.01037% | 1.016% | -0.1273% | 2.242% | 1.029% | 2.119% | 1.503% | 2.7% | 2.628% | 1.578% | 0.07252% | -4.978% | 1.141% | -0.9839% | -1.162% | -1.41% | 0.5865% | -1.918% | -4.24% | -1.223% | -2.206% | -1.226% | -0.036% | -1.176% | -2.275% | -1.382% | -0.9289% | -1.355% | 0.6774% | -1.831% | -1.514% | -0.3602% | 2.337% | 3.419% | 0.6206% | -2.22% | -1.176% | -2.179% | -3.594% | -1.849% | -0.06348% | -1.025% | -0.1322% | 0.6783% | -1.066% | 0.08694% | 0.8226% | 0.8844% | -0.3541% | -0.2448% | 1.154% | -1.748% | -1.671% | -1.836% | -0.2015% | -1.603% | -1.176% | -0.8558% | -2.019% | -0.8053% | -1.831% | -0.865% | 0.1621% | 0.7937% | 1.198% | 1.053%
2025-05-14 | -5.348% | -7.732% | -4.481% | -4.42% | -6.301% | -9.754% | -2.204% | -8.059% | -4.825% | -4.38% | -3.652% | -4.501% | -4.764% | -4.279% | -3.612% | -3.713% | -4.795% | -3.752% | -4.42% | -3.268% | -0.6402% | -1.772% | -1.206% | -1.327% | -1.611% | -2.561% | -1.408% | -1.732% | -0.155% | -0.5795% | -2.338% | -2.298% | -7.19% | -7.859% | -6.753% | -6.199% | -4.391% | -4.05% | -6.624% | -5.029% | -11.88% | -5.481% | -3.661% | -4.068% | -3.541% | -1.622% | -1.864% | -2.605% | -4.581% | -3.224% | -3.121% | -6.072% | -7.817% | -6.687% | -6.954% | -4.988% | -4.936% | -8.793% | -8.288% | -8.979% | -4.582% | -5.86% | -6.173% | 3.939% | 2.549% | 3.847% | 4.427% | 5.136% | 3.308% | 1.508% | 4.013% | 4.722% | 2.033% | 1.69% | 1.987% | 3.408% | 1.646% | -0.4621% | 3.092% | 2.687% | -0.416% | 3.341% | 4.565% | 3.87% | 4.86% | 5.458% | 4.082% | 3.64% | 4.317% | 2.77% | 2.88% | 3.092% | 5.661% | 6.499% | 7.273% | 7.411% | 6.73% | 6.573% | 6.462% | 5.439% | 5.121% | 6.683% | 4.343% | 6.628% | 11.63% | 5.827% | 7.623% | 5.072% | 5.201% | 7.871% | 7.199% | 5.1% | 7.223% | 4.948% | -1.567% | 2.936% | 2.3% | 2.696% | 3.193% | 2.042% | 2.438% | -2.727% | 1.425% | 2.301% | 2.816% | 2.042% | 0.7994% | 2.558% | -0.4621% | 1.886% | 0.9744% | -3.62% | 1.205% | 2.687% | 0.05358% | 0.3482% | -0.1348% | 3.258% | 0.7832% | -0.1582% | 2.669% | 1.61% | 1.545% | 1.112% | 0.7902% | 2.484% | 2.006% | 2.387% | 5.009% | -0.3851% | 1.582% | 1.822% | 4.127% | 0.827% | 1.444% | 1.343% | -3.003% | 2.033% | 0.6429% | -1.742% | 1.159% | 1.26% | 0.07199% | 1.594% | 3.304% | -1.762% | -1.481% | 0.3145% | -0.1999% | -0.3007% | -0.22% | -0.1192% | 0.3346% | 1.273% | 1.797% | 0.2237% | 0.3346% | 1.051% | 1.363% | 0.258% | 1.315% | -1.627% | 1.162% | 0.7683% | 1.646% | 1.373% | 0.4557% | 1.484% | 0.2741% | 1.474% | -0.5932% | 1.444% | -0.5226% | 0.4052% | 0.9251% | 0.3533% | 0.8933% | -1.337% | 2.02% | 0.2978% | 0.1061% | 0.6571% | 1.971% | 0.2507% | -0.2172% | 2.851% | -3.55% | -0.6895% | -1.737% | 0.2195% | -1.428% | 0.04106% | 0.1808% | 0.06739% | 1.911% | 1.942% | 1.828% | 0.6085% | -4.069% | -5.04% | -0.6559% | -2.519% | -3.815% | -4.313% | -1.643% | -3.809% | -1.185% | -0.3944% | 0.9785% | 0.2454% | 0.6853% | -1.027% | 1.806% | -0.6084% | 1.219% | -0.4667% | 0.01503% | 0.2664% | -3.251% | -1.735% | -3.63% | -1.556% | 0.8214% | 1.272% | -2.886% | -2.104% | -0.8752% | -2.653% | -1.818% | -2.583% | -1.197% | -2.164% | -2.344% | -0.8876% | -1.995% | -1.047% | -0.6582% | 1.71% | 0.02183% | 2.433% | 2.333% | 0.2861% | 3.611% | 2.51% | 0.3901% | 4.023% | 3.671% | 2.087% | 3.709% | 2.669% | -2.051% | -1.393% | 0.9278% | 0.7219% | 2.016% | 1.016% | 2.314% | 2.975% | 2.995% | 0.2842% | -0.07884% | -0.04859% | 0.3548% | -2.671% | -1.834% | 0.2136% | -1.874% | -1.713% | 1.343% | -0.4068% | 1% | 0.8086% | 1.423% | -0.3244% | -0.1338% | -0.1458% | 0.8391% | 0.1306% | 0.01932% | 0.1104% | -2.184% | -0.9521% | -1.053% | 0.7985% | -0.5878% | 1.592% | 0.4747% | 2.12% | 1.857% | 1.01% | -0.7076% | -3.405% | 1.285% | -0.9874% | -0.8577% | -1.706% | 0.2156% | -1.721% | -1.566% | -1.385% | -1.713% | -1.608% | -0.4488% | -1.895% | -2.683% | -1.217% | -1.925% | -2.982% | 0.5318% | -1.566% | 0.7795% | -2.048% | 2.256% | 1.586% | -0.9589% | -1.287% | 0.1497% | 0.04994% | -2.773% | -0.5286% | 0.419% | -0.349% | 0.6085% | 0.798% | -0.5585% | 0.5177% | 0.7481% | 0.6983% | 0.009514% | 0.214% | 1.387% | -0.1659% | 0.1896% | 0.1995% | 1.314% | -0.242% | 0.6284% | 0.91% | -0.03734% | 0.5087% | 0.1407% | 0.004554% | 1.189% | 1.764% | 1.984% | 1.911%
2025-05-15 | -7.162% | -10.08% | -6.15% | -6.15% | -7.554% | -11.6% | -3.568% | -9.717% | -5.808% | -5.846% | -5.429% | -5.998% | -5.277% | -5.732% | -4.366% | -4.783% | -6.683% | -4.126% | -5.239% | -4.442% | -1.558% | -2.355% | -2.544% | -2.658% | -3.607% | -3.417% | -1.254% | -1.709% | -0.533% | -1.747% | -2.355% | -3.911% | -6.491% | -8.121% | -7.921% | -6.603% | -5.325% | -6.084% | -7.022% | -5.325% | -11.92% | -4.707% | -2.8% | -3.291% | -2.485% | 0.1155% | -0.1142% | -0.6873% | -3.578% | -2.609% | -2.42% | -5.552% | -6.607% | -5.931% | -6.973% | -4.65% | -4.222% | -8.489% | -8.214% | -8.66% | -6.074% | -6.114% | -5.651% | 1.605% | 0.06701% | 0.9509% | 0.9313% | 2.591% | 0.4477% | -2.025% | 2.02% | 2.885% | 0.3781% | -0.2649% | 0.1016% | 0.5494% | -0.6614% | 0.1016% | 1.623% | 1.554% | 0.2744% | 1.944% | 2.21% | 1.995% | 3.109% | 2.266% | 2.049% | 1.452% | 1.726% | 0.7066% | 0.8449% | -1.731% | 0.309% | 0.793% | 1.692% | 2.591% | 2.239% | 1.675% | 1.346% | -0.02885% | -0.3541% | 1.83% | -0.9756% | 2.677% | 6.342% | 1.761% | 3.299% | 1.83% | 0.7411% | 4.181% | 3.386% | 4.164% | 2.649% | 1.905% | 0.9831% | 3.853% | 2.556% | 2.781% | 2.228% | 1.64% | 2.28% | 2.694% | 1.543% | 2.411% | 3.42% | 3.178% | 0.8967% | 3.369% | 1.64% | 1.796% | 1.329% | -1.783% | 2.746% | 3.939% | 1.605% | 1.968% | 4.887% | 5.235% | 3.655% | 1.761% | 1.847% | 3.42% | 3.697% | 3.127% | 2.504% | 4.388% | 4.095% | 3.857% | 3.186% | 1.453% | 2.812% | 3.974% | 5.565% | 2.988% | 3.248% | 2.66% | -1.178% | 3.248% | 3.49% | 1.796% | 2.401% | 2.47% | 1.225% | 4.528% | 5.961% | 1.869% | 0.5288% | 3.047% | 0.7938% | 1.078% | 1.381% | 1.608% | 2.081% | 2.971% | 4.353% | 2.687% | 2.479% | 4.145% | 4.77% | 2.295% | 4.164% | 2.013% | 4.126% | 4.221% | 4.561% | 3.35% | 2.933% | 3.88% | 3.255% | 3.671% | 1.362% | 3.198% | 1.797% | 2.744% | 2.255% | 1.838% | 4.243% | -0.4001% | 2.948% | 2.036% | 2.382% | 3.139% | 3.689% | 2.38% | 4.164% | 4.938% | 4.575% | 2.09% | 1.947% | 2.12% | 1.463% | 1.539% | 2.773% | 2.626% | 3.216% | 3.691% | 3.185% | 2.604% | 0.6435% | -0.4078% | 1.403% | -0.2621% | -1.822% | -2.628% | 1.35% | -0.4673% | 0.8922% | 2.662% | 2.921% | 1.604% | 0.8564% | -0.6134% | 2.272% | 0.2105% | 4.238% | 2.134% | 2.488% | -0.3821% | -8.552% | -0.08911% | -9.058% | 0.379% | 5.339% | 5.968% | 0.8761% | 1.708% | 2.94% | -0.1078% | 1.977% | 0.2292% | 2.102% | 0.7722% | -4.152% | 0.07941% | -2.654% | 1.69% | 1.128% | 0.4096% | -1.105% | 1.224% | 1.291% | 2.983% | 3.412% | 1.943% | 2.202% | 2.822% | 2.54% | 1.549% | 2.644% | 2.839% | 0.4405% | -0.1356% | 2.408% | 0.8728% | 1.905% | 0.6162% | 2.216% | 2.75% | 2.09% | 0.09335% | -0.6639% | -1.913% | -1.686% | -3.352% | -2.178% | -0.7207% | -2.917% | -3.049% | 1.267% | 0.43% | 0.3773% | 1.002% | 2.076% | -0.3487% | -2.078% | -1.813% | 1.065% | -0.6858% | -0.8948% | 0.6059% | -8.43% | -0.1919% | -1.693% | 1.176% | 0.416% | 0.146% | 0.07403% | 2.327% | 1.281% | 0.3868% | -2.25% | -6.76% | 1.798% | -0.37% | -1.025% | -1.325% | 0.8241% | -2.838% | -5.931% | -0.5555% | -2.82% | -1.562% | 1.203% | -2.598% | -0.2576% | -0.1827% | -1.063% | -8.627% | 2.207% | -0.9523% | 0.129% | -16.82% | -0.4215% | -0.7164% | -14.68% | -1.868% | -1.231% | 0.7535% | -3.422% | -1.924% | 0.07941% | -1.231% | -0.37% | 1.016% | -1.793% | -0.5198% | 0.2666% | 1.072% | -1.472% | -0.9523% | 1.8% | -0.1802% | -1.718% | -1.643% | 0.188% | -0.6449% | 0.1918% | 0.6777% | -1.621% | -0.3325% | -1.719% | -0.3625% | 0.0597% | 2.016% | 2.331% | 0.4043%
2025-05-16 | -5.178% | -7.956% | -3.937% | -4.314% | -6.35% | -10.12% | -1.509% | -7.984% | -4.54% | -4.063% | -3.309% | -4.264% | -4.591% | -4.239% | -3.535% | -3.837% | -4.649% | -3.141% | -3.158% | -2.505% | 0.4865% | -0.8708% | -0.2173% | -0.8457% | -0.4435% | -1.424% | -0.1922% | -0.9965% | 1.215% | 0.7127% | -1.047% | -1.172% | -6.224% | -7.295% | -6.607% | -5.681% | -4.384% | -4.464% | -6.099% | -4.887% | -8.285% | -4.894% | -2.723% | -3.549% | -2.7% | -0.4686% | -0.691% | -1.45% | -3.287% | -2.506% | -2.098% | -5.377% | -6.86% | -5.964% | -6.701% | -4.067% | -4.036% | -8.402% | -7.809% | -8.382% | -4.666% | -5.672% | -5.601% | 4.488% | 2.909% | 4.481% | 4.706% | 6.687% | 4.513% | 2.794% | 4.74% | 6.16% | 3.126% | 3.125% | 3.035% | 4.594% | 2.38% | -0.7663% | 2.737% | 2.977% | 2.039% | 9.603% | 4.099% | 4.415% | 5.301% | 5.492% | 5.324% | 4.605% | 4.981% | 3.206% | 3.79% | 5.507% | 7.282% | 7.694% | 8.003% | 8.438% | 8.347% | 7.248% | 6.767% | 5.923% | 5.049% | 6.561% | 3.804% | 7.889% | 11.8% | 7.248% | 8.415% | 6.893% | 6.217% | 8.656% | 7.82% | 9.033% | 5.061% | 5.659% | 2.21% | 4.763% | 3.286% | 3.321% | 2.989% | 2.222% | 3.275% | 1.146% | 2.069% | 3.11% | 3.928% | 3.218% | 1.684% | 3.893% | 2.485% | 2.771% | 1.695% | -3.537% | 2.783% | 3.756% | 1.581% | 1.34% | 4.307% | 4.191% | 2.196% | 0.4701% | 0.9738% | 2.233% | 2.748% | 2.187% | 1.901% | 3.103% | 2.474% | 2.595% | 2.296% | 0.8% | 2.296% | 2.783% | 5.149% | 2.142% | 2.371% | 2.061% | -4.063% | 2.542% | 2.76% | 0.7907% | 1.363% | 1.947% | 0.5617% | 3.404% | 4.775% | 1.339% | -0.268% | 1.262% | 0.1708% | -0.5689% | -1.02% | -1.158% | -0.8448% | 0.1959% | 0.7601% | -0.3809% | 1.726% | 1.976% | 0.9357% | 0.2423% | 0.5846% | -2.563% | 0.9231% | 0.1959% | 1.149% | 0.4592% | -0.3683% | 0.6348% | -0.5815% | 0.9858% | -1.484% | 0.5846% | -1.422% | -0.732% | -0.4028% | -1.048% | -0.3765% | -0.3962% | 2.894% | 1.537% | 2.918% | 4.11% | 5.447% | 1.953% | 3.102% | 5.927% | 6.307% | 3.457% | -0.2011% | 4.117% | 4.178% | -0.01872% | 2.463% | 2.865% | 3.06% | 3.189% | 3.331% | 3.27% | 1.682% | -1.644% | 2.444% | 1.179% | 0.3307% | -0.5513% | 2.268% | 0.7188% | -1.704% | -0.722% | -0.8072% | -0.703% | -1.966% | -2.22% | 0.3907% | -2.158% | 0.6121% | -0.8072% | -0.8983% | -0.8202% | -1.203% | -2.344% | -2.244% | -2.182% | 0.7423% | 0.2605% | -2.474% | -1.55% | -1.081% | -2.678% | -2.213% | -2.815% | -1.6% | -2.344% | -0.3347% | -0.5207% | -2.034% | -1.649% | -0.9051% | -0.6864% | -2.082% | 0.4757% | 0.3189% | 1.985% | 3.038% | 1.87% | -0.9802% | 2.616% | 2.763% | 2.004% | 3.066% | 2.677% | -0.6902% | -1.362% | 1.829% | 0.3907% | 0.5499% | 0.4052% | 2.231% | 2.221% | 1.941% | -3.039% | -3.754% | -3.729% | -2.964% | -5.547% | -3.917% | -3.704% | -3.541% | -4.268% | -1.948% | -2.289% | -2.074% | -2.136% | -2.18% | -4.115% | -3.905% | -3.398% | -1.883% | -2.922% | -2.469% | -1.853% | -1.238% | -2.532% | -4.18% | -0.5441% | -2.507% | -2.027% | -1.752% | -0.7445% | -1.074% | -1.812% | -3.633% | -3.736% | -3.431% | -4.762% | -5.568% | -5.803% | -5.195% | -4.413% | -3.522% | -5.327% | -5.234% | -3.112% | -4.167% | -4.427% | -5.171% | -5.369% | -4.067% | -2.716% | -3.403% | -4.258% | -4.141% | -2.383% | -1.888% | -1.042% | -1.315% | -2.096% | -1.166% | -0.3099% | -1.786% | -1.624% | -0.6943% | -1.476% | -0.8679% | -1.215% | -2.492% | -2.018% | -1.042% | -0.8059% | -1.837% | -1.354% | 0.2996% | 0.154% | -0.5579% | -0.8803% | 0.9506% | -2.166% | 0.9178% | 0.9944% | -1.042% | 0.3473% | -1.029% | -0.6379% | 0.3839% | 0.8725% | 0.7293% | 0.7163%
2025-05-17 | -7.255% | -9.68% | -6.249% | -6.134% | -7.544% | -11.17% | -3.659% | -9.646% | -5.615% | -5.299% | -5.183% | -5.702% | -5.385% | -5.155% | -3.917% | -4.118% | -5.921% | -4.012% | -4.867% | -3.917% | -1.008% | -2.016% | -1.095% | -1.671% | -1.987% | -2.362% | -0.9796% | -1.325% | 0.2585% | -0.4613% | -1.613% | -1.901% | -7.775% | -8.649% | -7.649% | -6.679% | -4.861% | -4.861% | -7.314% | -5.164% | -7.746% | -5.985% | -4.349% | -4.926% | -3.509% | -1.654% | -1.416% | -1.738% | -3.751% | -2.051% | -1.889% | -4.582% | -5.969% | -5.388% | -6.321% | -3.984% | -4.42% | -8.473% | -7.744% | -8.497% | -5.126% | -5.466% | -5.205% | 2.73% | 0.7625% | 1.629% | 1.471% | 2.887% | 0.7222% | 0.7231% | 2.533% | 3.176% | 0.5264% | -0.1409% | 0.0674% | 0.5711% | -0.7726% | 2.441% | 3.648% | 3.346% | 1.471% | 3.477% | 4.526% | 3.574% | 4.802% | 4.218% | 3.505% | 2.587% | 2.494% | 2.061% | 1.943% | -0.5097% | 1.431% | 1.851% | 2.69% | 3.884% | 3.126% | 3.11% | 2.926% | 0.9276% | 0.955% | 3.071% | 0.5753% | 3.399% | 7.32% | 2.441% | 3.845% | 2.153% | 1.012% | 4.723% | 4.081% | 1.667% | 4.096% | 2.984% | 2.113% | 4.579% | 3.74% | 3.831% | 4.225% | 2.69% | 3.149% | 3.569% | 2.696% | 3.67% | 4.382% | 4.067% | 2.074% | 4.238% | 2.638% | 2.808% | 2.179% | 0.592% | 3.215% | 4.33% | 2.126% | 2.179% | 2.518% | 3.005% | 1.172% | -0.2211% | -0.3129% | 1.707% | 1.877% | 1.431% | 0.6576% | 2.559% | 2.218% | 2.587% | 5.576% | 0.4889% | 1.986% | 2.166% | 4.57% | 2.113% | 2.507% | 1.733% | -11.05% | 3.359% | 1.051% | 1.667% | 2.376% | -0.6015% | 0.4477% | 3.816% | 4.999% | 1.435% | -2.942% | -0.8738% | -2.08% | -2.339% | -2.368% | -2.497% | -1.851% | -0.845% | 0.04554% | -0.9025% | -0.5147% | 0.2035% | 0.4334% | -0.9097% | 0.565% | -1.979% | 0.3328% | 0.3041% | 0.7494% | -0.04065% | -0.6008% | 0.1461% | -0.4285% | 0.5339% | -1.549% | 0.4046% | -1.434% | -0.9169% | -0.5326% | -1.091% | -0.1706% | -0.09834% | 2.755% | -1.984% | 1.36% | 2.262% | 3.346% | 1.072% | 2.976% | 3.628% | 3.728% | 1.134% | -1.443% | 1.034% | 0.641% | 2.129% | 1.992% | 2.954% | 3.371% | 4.108% | 3.756% | 2.559% | -3.602% | -1.548% | 0.4128% | -1.08% | -2.332% | -3.461% | 0.3046% | -1.489% | -1.754% | -0.751% | -0.07435% | -0.5666% | -0.4174% | -2.574% | 1.343% | -1.352% | 0.8952% | -0.8798% | -0.5069% | -0.05943% | -2.247% | -2.886% | -2.73% | -2.29% | 1.686% | 2.029% | -1.491% | -1.025% | -0.4323% | -3.554% | -1.357% | -2.261% | -1.636% | -2.304% | -0.1589% | -0.04522% | -2.261% | -1.906% | -0.9402% | 3.046% | 1.351% | 3.521% | 3.116% | 4.53% | 4.776% | 0.1115% | 3.468% | 4.077% | 3.728% | 2.587% | 3.765% | 1.431% | 0.8284% | -0.63% | 2.695% | 1.681% | 2.874% | 1.764% | 2.924% | 3.615% | 3.087% | 0.7206% | -0.1125% | -0.687% | -0.1987% | -2.181% | -1.879% | -0.1412% | -2.281% | -2.31% | 1.252% | -0.5621% | 0.7925% | 0.6919% | 1.73% | -0.01982% | -0.8192% | -0.7444% | 0.9188% | -0.4778% | -0.5643% | -0.1031% | -0.01554% | -0.7949% | -1.429% | 0.4158% | -0.8525% | 0.779% | 0.05549% | 1.597% | 0.7041% | -0.2762% | -0.08926% | -2.718% | 1.172% | -0.5993% | -1.494% | -1.523% | -0.3516% | -2.744% | -3.369% | -1.171% | -1.641% | -0.6561% | 0.3383% | -0.4856% | -2.332% | -1.082% | -1.196% | -0.6135% | 0.8511% | -2.207% | 0.2538% | -1.283% | 2.64% | 2.476% | 2.626% | 0.4094% | 1.29% | 2.682% | -1.409% | 1.034% | 2.143% | 0.8924% | 1.787% | 2.341% | 0.1252% | 1.328% | 0.5372% | 2.285% | 0.8827% | 1.477% | 3.297% | 1.703% | 1.475% | 1.077% | 3.371% | -2.758% | 3.137% | 2.341% | 0.8505% | 2.37% | 1.029% | 2.223% | 3.049% | 3.446% | 3.565% | 2.909%
2025-05-18 | -5.904% | -8.742% | -4.791% | -4.744% | -6.163% | -10.07% | -2.077% | -8.481% | -4.366% | -3.893% | -3.987% | -4.46% | -3.845% | -3.94% | -2.663% | -3.136% | -4.859% | -2.369% | -2.994% | -2.332% | 0.7896% | -0.1563% | 0.695% | 0.2693% | -0.5347% | -1.055% | 0.9788% | 0.4585% | 1.972% | 1.263% | -0.01444% | -1.291% | -5.264% | -6.8% | -6.452% | -5.257% | -3.863% | -4.062% | -5.406% | -3.714% | -6.21% | -3.057% | -1.2% | -1.971% | -0.3737% | 1.915% | 2.142% | 1.494% | -1.582% | 0.07395% | 0.605% | -2.934% | -4.731% | -4.047% | -4.973% | -3.054% | -1.905% | -6.352% | -6.153% | -7.394% | -4.224% | -4.066% | -3.423% | 4.225% | 2.373% | 3.513% | 3.191% | 5.001% | 2.812% | 2.653% | 4.764% | 5.561% | 2.954% | 2.305% | 2.631% | 3.085% | 1.553% | 2.287% | 4.161% | 4.139% | 2.761% | 4.321% | 4.786% | 4.346% | 5.626% | 4.639% | 4.594% | 3.848% | 4.247% | 3.234% | 3.45% | 0.7139% | 2.567% | 2.954% | 3.859% | 4.786% | 4.509% | 3.838% | 3.471% | 1.846% | 1.531% | 4.053% | 1.142% | 4.979% | 8.491% | 4.139% | 5.647% | 4.139% | 2.48% | 6.703% | 5.884% | 6.681% | 5.233% | 4.391% | 3.407% | 6.724% | 5.109% | 5.195% | 4.764% | 3.407% | 4.958% | 5.518% | 4.121% | 4.931% | 6.444% | 6.121% | 3.751% | 6.315% | 4.096% | 4.419% | 4.01% | 5.303% | 5.281% | 6.811% | 4.376% | 4.549% | 7.972% | 7.069% | 5.738% | 3.945% | 4.118% | 5.647% | 6.164% | 5.755% | 4.979% | 6.854% | 6.617% | 6.711% | 5.932% | 4.323% | 7.026% | 6.681% | 8.583% | 6.143% | 5.992% | 5.518% | 3.751% | 4.527% | 6.444% | 5.066% | 5.367% | 5.54% | 4.29% | 7.129% | 8.771% | 5.044% | -4.111% | -1.94% | -3.191% | -3.45% | -3.143% | -3.332% | -2.2% | -0.6187% | 0.4431% | -0.949% | -1.161% | -0.3591% | -0.02881% | -1.521% | -0.5715% | -2.771% | 0.2071% | -0.02881% | 1.127% | 0.4431% | -0.5951% | 0.5611% | -0.6895% | 1.175% | -1.657% | 0.5139% | -0.3355% | -0.2884% | -0.5798% | -0.6045% | 0.08916% | 2.867% | 5.647% | 3.596% | 3.968% | 4.955% | 5.823% | 3.89% | 5.85% | 6.654% | 6.404% | 3.934% | 3.867% | 3.05% | 2.952% | 7.734% | 4.502% | 5.678% | 5.923% | 6.821% | 6.159% | 8.899% | 1.827% | 0.8189% | 2.727% | 1.023% | -0.3273% | -1.68% | 3.105% | 1.306% | -1.679% | -0.387% | -0.2021% | -0.6922% | -1.942% | -3.321% | 1.145% | -1.197% | 0.9985% | -0.8882% | -0.5207% | -0.3492% | -0.9407% | -2.481% | -1.711% | -1.874% | 2.273% | 0.9495% | -3.657% | -1.454% | -0.9862% | -7.965% | -2.26% | -3.251% | -1.781% | -2.388% | 0.8795% | -1.034% | -2.037% | -1.477% | -0.8474% | 2.041% | 0.4009% | 2.867% | 2.759% | 4.643% | 5.339% | 4.007% | 3.914% | 4.914% | 4.87% | 3.847% | 4.981% | 4.866% | 2.084% | 1.894% | 4.23% | 3.196% | 5.632% | 4.298% | -19.42% | 26.38% | 4.246% | -3.946% | -4.535% | -4.937% | -4.701% | -6.423% | -6.423% | -4.488% | -7.296% | -6.871% | -2.931% | -2.733% | -3.214% | -3.12% | -3.032% | -4.717% | -5.535% | -4.547% | -4.761% | -4.162% | -4.044% | -3.215% | -2.538% | -3.357% | -5.133% | -1.463% | -3.476% | -3.617% | -2.789% | -1.657% | -2.141% | -2.884% | -7.038% | -7.275% | -6.674% | -7.241% | -8.128% | -8.151% | -7.665% | -10.53% | -6.518% | -7.159% | -8.753% | -8.141% | -6.518% | -7.685% | -9.505% | -8.501% | -6.868% | -5.351% | -5.001% | -10.3% | -7.455% | -5.593% | -5.054% | -4.441% | -4.196% | -5.141% | -4.324% | -2.714% | -6.915% | -4.511% | -3.041% | -4.231% | -3.438% | -2.924% | -4.931% | -4.637% | -3.951% | -2.551% | -4.699% | -4.343% | -2.456% | -3.194% | -3.788% | -3.811% | -2.285% | -7.805% | -2.154% | -2.325% | -4.882% | -2.784% | -5.078% | -2.873% | -3.074% | -2.53% | -2.677% | -2.554%
2025-05-19 | -6.605% | -8.308% | -5.517% | -5.303% | -6.968% | -9.976% | -2.847% | -9.133% | -5.564% | -4.803% | -4.446% | -5.231% | -4.779% | -4.779% | -4.779% | -3.804% | 1.159% | -5.303% | -8.919% | -4.898% | -3.708% | -1.21% | -2.209% | -1.282% | -1.496% | -2.328% | -3.042% | -1.305% | -1.829% | -0.5915% | -0.8533% | -2.019% | -2.281% | -1.571% | -7.256% | -7.256% | -6.53% | -5.528% | -8.943% | -4.151% | -6.207% | -14.69% | -14.16% | -2.381% | 2.188% | -4.165% | -10.6% | -7.826% | -9.464% | 2.177% | 15.17% | 1.145% | -3.694% | -9.745% | -10.62% | -4.702% | -9.367% | -4.523% | 12.89% | -9.644% | -12.96% | 4.399% | -3.867% | 1.808% | 0.2797% | 1.386% | 1.32% | 2.144% | 0.5659% | 0.1171% | 2.458% | 2.382% | 0.4748% | -2.682% | 0.1171% | 0.623% | -0.4646% | 0.3122% | 1.721% | 1.797% | 0.2147% | 1.523% | 2.599% | 1.994% | 2.631% | 2.504% | 2.096% | 0.7396% | 1.851% | 0.7891% | 1.353% | -1.693% | 0.4206% | 0.5831% | 1.634% | 1.851% | 1.041% | 1.548% | -1.368% | 0.1359% | -0.8499% | 1.862% | -0.7753% | 2.025% | 5.85% | 1.158% | 3.065% | 1.613% | 0.6915% | 4.084% | 3.455% | 0.323% | 1.925% | 1.507% | 0.9299% | 3.347% | 1.916% | 2.664% | 2.306% | 1.45% | 2.642% | 3.076% | 2.311% | 2.923% | 4.138% | 3.759% | 2.209% | 4.246% | 2.686% | 2.729% | 1.949% | 2.978% | 2.426% | 3.704% | 1.634% | 1.45% | 4.781% | 5.189% | 2.876% | 2.252% | 2.35% | 3.52% | 3.975% | 3.78% | 2.967% | 4.528% | 3.802% | 4.215% | 2.707% | 1.416% | 3.058% | 3.704% | 5.201% | 1.884% | 2.241% | 2.068% | -2.863% | 2.751% | 1.212% | -2.863% | 2.035% | -2.679% | 0.8758% | 2.967% | 4.615% | -0.4986% | 0.5955% | 2.127% | 1.225% | 0.6905% | 0.8923% | 0.9041% | 1.877% | 2.72% | 3.646% | 2.59% | 2.59% | 2.886% | 3.527% | 2.273% | 4.054% | 0.4644% | 3.682% | 3.326% | 4.121% | 3.587% | 2.625% | 3.527% | 2.483% | 3.492% | 1.094% | 3.088% | 0.8567% | 2.412% | 2.609% | 1.699% | 3.332% | 1.128% | 4.363% | 2.838% | 2.62% | 3.454% | 4.784% | 2.174% | 4.215% | 5.128% | 5.094% | 2.42% | -2.522% | -0.09904% | 2.618% | 0.1685% | 2.03% | 3.146% | 4.649% | 4.713% | 5.006% | 4.088% | -0.3632% | -0.1835% | 1.282% | -0.3977% | -1.259% | -2.221% | 0.6273% | -1.621% | -0.2586% | 0.425% | 1.161% | 0.6681% | 0.5202% | -1.484% | 2.271% | -0.4512% | 2.48% | 1.075% | 0.853% | 1.346% | 0.3236% | -0.6743% | -0.3456% | -0.06382% | 2.529% | 2.308% | -0.07145% | -0.3808% | 1.05% | -2.576% | 0.6065% | -0.4395% | 0.4879% | -0.416% | 1.967% | 2.178% | 0.171% | 0.6053% | 1.38% | -1.558% | -3.284% | 0.5926% | 0.2106% | 1.359% | 1.886% | -2.619% | 1.168% | 2.957% | 3.272% | 1.922% | 3.058% | 1.694% | -3.099% | -0.5026% | 0.2628% | 0.4175% | 2.157% | 2.28% | 1.568% | 2.372% | 2.005% | -0.4727% | -1.161% | -1.351% | -0.4609% | -3.428% | -2.847% | -1.636% | -3.713% | -3.191% | -0.4134% | -1.877% | -0.2353% | -0.6627% | -0.195% | -0.868% | -0.9802% | -0.9742% | -0.8786% | -0.4546% | -0.6928% | 0.26% | -1.397% | -0.5856% | -1.11% | 1.32% | -0.3593% | 0.8848% | 0.2362% | 0.6905% | 0.5279% | 0.1789% | 1.05% | -2.237% | 0.7148% | -1.66% | -2.529% | -2.388% | -1.466% | -3.869% | -2.459% | -2.242% | -2.389% | -2.339% | -0.8386% | -1.696% | -3.28% | -1.625% | -1.343% | -0.6038% | -0.6982% | -2.29% | -0.8357% | 0.2367% | 1.161% | 1.938% | 1.457% | -2.705% | -1.872% | -0.6508% | -4.008% | -1.778% | -0.8269% | -1.766% | -0.909% | -0.2164% | -1.801% | -2.561% | -2.253% | -0.0873% | -0.7416% | -0.8973% | 0.8037% | -0.8861% | -0.8856% | -0.7682% | 0.36% | -4.842% | 0.2062% | -0.1689% | -1.329% | -0.0286% | -0.9959% | 0.02716% | 0.7116% | 1.346% | 1.1% | 0.8284%
2025-05-20 | -8.06% | -10.7% | -7.009% | -6.813% | -8.382% | -11.99% | -4.421% | -11.05% | -6.421% | -5.99% | -6.303% | -6.852% | -6.107% | -5.95% | -4.891% | -5.597% | -6.821% | -5.211% | -5.597% | -4.774% | -1.911% | -3.048% | -2.146% | -3.087% | -2.656% | -3.676% | -1.793% | -2.538% | -0.8517% | -1.479% | -3.048% | -2.891% | -7.284% | -8.555% | -8.349% | -6.863% | -5.789% | -6.285% | -7.401% | -5.913% | -8.225% | -5.764% | -3.388% | -4.633% | -3.233% | -0.6546% | -0.727% | -1.156% | -4.497% | -2.854% | -2.684% | -5.769% | -7.739% | -6.999% | -7.864% | -5.661% | -4.705% | -9.347% | -8.947% | -10.1% | -2.068% | -2.436% | -14.41% | 1.451% | -0.5499% | 0.8709% | 0.5576% | 2.29% | 0.3383% | -0.1927% | 1.897% | 2.916% | 0.2004% | -0.2759% | 0.111% | 0.5901% | -0.9226% | -1.032% | 0.7006% | 0.5041% | -0.6571% | 1.161% | 1.772% | 1.057% | 2.666% | 2.178% | 1.785% | 1.126% | 1.487% | 0.254% | 0.3254% | -0.5142% | 0.6291% | 1.362% | 1.755% | 2.987% | 2.752% | 2.237% | -0.1569% | -0.3997% | -0.325% | 1.737% | -1.09% | 2.63% | 6.256% | 2.255% | 3.184% | 1.665% | -0.2105% | 3.88% | 3.219% | 4.363% | 2.837% | 1.953% | -0.1927% | 2.737% | 1.451% | 1.201% | 0.9328% | -0.7643% | 1.004% | 1.772% | 0.422% | 1.094% | 2.666% | 2.237% | -0.04974% | 2.398% | 0.379% | 0.7542% | 0.5041% | 1.594% | 1.772% | 3.184% | 0.9864% | 1.058% | 4.251% | 4.684% | 3.294% | 1.344% | 1.272% | 3.344% | 3.648% | 2.755% | 2.112% | 3.72% | 3.737% | 5.521% | 2.771% | 1.318% | 4.568% | 3.505% | 5.4% | 2.898% | 2.576% | 1.862% | 2.523% | 2.63% | 3.219% | 1.772% | 1.933% | 2.148% | 0.6648% | 3.627% | 5.131% | 1.748% | 0.6453% | 2.7% | 1.134% | 0.9387% | 1.702% | 1.095% | 1.858% | 3.091% | 4.187% | 3.189% | 3.071% | 3.776% | 4.461% | 2.206% | 4.066% | 2.383% | 4.363% | 4.343% | 4.695% | 3.815% | 3.169% | 4.226% | 3.384% | 4.089% | 1.663% | 3.58% | 1.878% | 2.934% | 2.801% | 2% | 4.507% | 0.7954% | 3.21% | 1.57% | 2.254% | 3.357% | 4.361% | 1.929% | 4.082% | 4.988% | 5.018% | 2.736% | 2.883% | 2.442% | 2.633% | 1.223% | 2.42% | 3.439% | 3.399% | 4.737% | 3.858% | 2.877% | 1.252% | 0.4928% | 2.16% | 0.5799% | -1.536% | -1.695% | 1.802% | 0.04216% | 0.8516% | 2.736% | 2.545% | 2.098% | 2.017% | -0.5381% | 3.399% | 1.087% | 4.09% | 2.647% | 2.586% | 2.891% | 0.2165% | -0.01567% | 0.352% | 0.9712% | 5.898% | 5.654% | 2.667% | 2.345% | 3.013% | -0.3833% | 2.078% | 0.6616% | 2.616% | 1.068% | 4.532% | 3.042% | 1.165% | 1.726% | 2.655% | -0.9401% | -2.197% | -0.3% | -0.2606% | 1.091% | 1.76% | 0.8385% | 0.684% | 1.313% | 1.237% | 0.05332% | 1.203% | 1.811% | -0.9263% | -0.8073% | 0.9379% | 0.456% | 23.04% | 1.071% | 0.707% | 0.5211% | -12.34% | -1.272% | -2.27% | -2.994% | -2.466% | -4.422% | -3.679% | -2.485% | -3.816% | -3.62% | 0.09743% | -1.818% | -0.6852% | -0.7635% | 0.6648% | -1.533% | -3.095% | -2.861% | -0.3989% | -1.799% | -1.76% | -0.2481% | -3.233% | -1.74% | -2.506% | -0.1303% | -0.8959% | -0.9089% | -0.7781% | 0.9387% | -0.1364% | -0.917% | 1.611% | -0.9007% | 0.5621% | -1.97% | -2.667% | -2.396% | -0.5062% | -3.885% | 1.378% | 0.05734% | -3.205% | -1.518% | 1.513% | 0.4681% | -0.4801% | 0.003685% | 0.1972% | 0.1585% | 1.236% | -0.8274% | 0.8183% | -0.3804% | 3.907% | 3.419% | 4.232% | -1.68% | -1.893% | 0.8938% | -4.099% | -1.351% | 0.1585% | -2.26% | -0.1318% | 1.01% | -1.757% | -4.607% | -3.083% | 0.352% | -1.703% | -1.01% | 1.184% | 0.3713% | -1.525% | -1.544% | 0.5136% | -5.355% | 0.5455% | -0.2567% | -1.782% | -0.7316% | -1.742% | 1.001% | -0.142% | 0.5745% | 1.469% | 0.04626%
2025-05-21 | -8.234% | -11.08% | -6.905% | -7.018% | -8.821% | -12.57% | -4.158% | -11.3% | -6.567% | -8.145% | -6.116% | -6.961% | -6.398% | -7.243% | -5.214% | -5.609% | -7.996% | -5.09% | -5.609% | -4.82% | -1.777% | -2.96% | -3.411% | -3.749% | -4.144% | -4.425% | -1.495% | -2.059% | -0.3116% | -1.889% | -2.566% | -5.045% | -8.088% | -9.895% | -9.361% | -7.937% | -6.454% | -8.293% | -8.934% | -6.098% | -8.765% | -5.665% | -3.639% | -5.278% | -5.278% | -5.268% | -8.513% | -0.9687% | -10.93% | 8.231% | 1.49% | -4.792% | -7.152% | -11.29% | -7.377% | -7.655% | -10.77% | -0.6796% | 2.429% | -8.957% | -2.171% | -2.043% | -7.29% | 1.748% | -0.1% | 1.602% | 0.978% | 2.775% | 0.4667% | 0.2593% | 2.467% | 3.262% | 0.7213% | -0.04268% | 0.439% | 0.7108% | -0.6846% | -1.306% | 1.568% | 1.568% | 0.1053% | 1.887% | 2.338% | 1.596% | 3.185% | 2.294% | 2.214% | 1.315% | 2.056% | 0.901% | 0.8497% | -0.9984% | 0.593% | 1.286% | 2.03% | 3.134% | 2.865% | 2.467% | 1.825% | -0.3626% | -0.6309% | 2.03% | -1.412% | 3.108% | 6.599% | 1.851% | 3.622% | 1.825% | 0.1823% | 4.443% | 3.724% | 4.52% | 3.061% | 2.214% | 0.6957% | 3.776% | 2.467% | 2.415% | 1.928% | 0.4133% | 1.979% | 2.569% | 1.301% | 2.053% | 3.442% | 3.339% | 0.8497% | 3.365% | 1.26% | 1.312% | 0.978% | 2.492% | 2.518% | 3.673% | 1.26% | 2.775% | 4.682% | 4.52% | 2.96% | 1.004% | 1.337% | 2.903% | 3.365% | 2.826% | 1.928% | 3.57% | 3.493% | 3.421% | 2.453% | 0.9523% | 2.458% | 3.442% | 4.776% | 2.672% | 3.237% | 1.953% | 3.262% | 3.083% | 0.3106% | 1.517% | 2.082% | 1.26% | 0.747% | 4.322% | 5.778% | 0.0668% | -0.7625% | 1.824% | -0.3971% | 0.05274% | 0.9523% | 0.5869% | 0.4744% | 1.936% | 3.539% | 1.964% | 1.543% | 3.173% | 4.073% | 1.188% | 2.92% | 1.489% | 3.201% | 3.286% | 3.651% | 2.414% | 1.852% | 2.892% | 2.33% | 2.527% | 0.2495% | 2.189% | 0.9805% | 1.824% | 1.484% | 0.6867% | 3.757% | -0.004704% | 2.467% | 1.244% | 1.539% | 2.382% | 3.065% | 1.595% | 3.473% | 4.397% | 4.057% | 1.966% | 2.099% | 1.706% | 1.569% | 3.544% | -0.4976% | 2.675% | 2.762% | 3.58% | 2.947% | 1.53% | -0.6922% | -0.5532% | 1.671% | -0.7114% | -3.109% | -2.883% | 0.4147% | -1.325% | -0.0774% | 1.993% | 2.237% | 1.098% | 1.128% | -2.298% | 3.171% | 0.6771% | 3.463% | 1.449% | 1.828% | 2.908% | -0.3238% | -1.186% | -0.0458% | -0.2404% | 5.857% | 6.266% | 2.149% | 0.5103% | 2.003% | -1.631% | 1.157% | -0.7131% | 1.622% | -0.3238% | 5.293% | 2.095% | -0.4351% | 0.6771% | 1.344% | -0.0774% | -1.862% | 0.6046% | 0.3886% | 2.151% | 2.738% | 0.0532% | 1.43% | 2.178% | 2.001% | 1.062% | 2.099% | 2.676% | -0.4795% | -0.3826% | 1.469% | 0.5242% | 24.37% | 1.076% | 1.544% | 1.718% | 1.648% | -0.5938% | -1.437% | -2.815% | -2.843% | -3.827% | -3.124% | -2.056% | -3.658% | -3.911% | 0.362% | -1.614% | -0.5095% | -0.3689% | 0.9819% | -0.8187% | -3.623% | -2.743% | 0.2285% | -1.214% | -1.58% | 0.5071% | -2.93% | -1.101% | -2.483% | 0.3378% | -0.3674% | -0.538% | -0.7341% | 1.458% | -0.02175% | -0.6121% | 3.843% | -1.655% | 1.454% | -1.297% | -2.298% | -2.214% | -0.2284% | -4.275% | 2.151% | 0.7719% | -4.04% | -1.033% | 3.068% | 2.012% | 0.7883% | 1.233% | 1.789% | 2.29% | 2.671% | 0.1057% | 1.682% | 2.062% | 4.806% | 5.098% | 5.477% | -2.771% | -2.798% | 0.5659% | -4.467% | -2.854% | -0.5463% | -1.297% | -0.7687% | 1.066% | -2.493% | -0.5657% | 2.47% | 0.8717% | -1.509% | -1.646% | 1.478% | -0.05086% | -2.02% | -1.742% | -0.6825% | -1.856% | -0.2404% | 0.2676% | -2.025% | -1.297% | -2.171% | 1.098% | -0.5565% | 1.507% | 2.12% | -0.3906%
2025-05-22 | -2.278% | -3.772% | -0.7645% | -0.4968% | -1.648% | -5.289% | 1.872% | -4.728% | -0.2022% | 1.217% | -0.06833% | -0.711% | 1.699% | 1.003% | 2.743% | 2.074% | -0.136% | 1.02% | -0.3897% | 1.217% | 3.814% | 2.609% | 3.359% | 4.136% | 2.663% | 1.592% | 3.547% | 3.172% | 4.671% | 4.27% | 2.636% | 2.716% | 0.5743% | -0.8406% | -0.1924% | 0.8505% | 2.457% | 1.837% | 0.6011% | 2.119% | 0.012% | 2.482% | 5.154% | 4.461% | 4.771% | 6.753% | 6.724% | 5.894% | 2.883% | 3.151% | 4.56% | 2.115% | 1.013% | -0.5249% | -1.896% | 1.09% | 1.072% | -2.961% | -3.223% | -3.574% | -0.04155% | -1.308% | 1.813% | -15.7% | -17.47% | 5.731% | 5.403% | -17.06% | -16.67% | -17.39% | -14.62% | -14.42% | -17.4% | -17.77% | -17.22% | -16.97% | -18.01% | -17.1% | -15.43% | 6.939% | -17.22% | -15.38% | -14.81% | -15.45% | -14.34% | -15.3% | -15.01% | -16.03% | 6.5% | -15.94% | -16.17% | -18.25% | -16.17% | -15.67% | -14.37% | -14% | -14.21% | 7.525% | -15.15% | -16.67% | -17.34% | -14.5% | -18.64% | -13.9% | -10.94% | -15.23% | -13.87% | -15.6% | 5.073% | -12.86% | -13.62% | -12.98% | 4.487% | -15.07% | -16.36% | -14.36% | -15.31% | -15.37% | 7.757% | -16.99% | -15.65% | -15.21% | -16.23% | -15.83% | 9.379% | 9.989% | 7% | 9.842% | 7.622% | 8.037% | -17.04% | 9.232% | -15.73% | -14.77% | -16.38% | -14.66% | 12.04% | 13.55% | -13.85% | -15.28% | 9.537% | -13.7% | -13.34% | 11.44% | -14.25% | -13.29% | -13.59% | -13.63% | -14.48% | 9.416% | -14.92% | -13.42% | -12.46% | -15.39% | -14.43% | -15.48% | 10.93% | -15.2% | -15.21% | -16.21% | -15.69% | -16.08% | 8.549% | -13.51% | 12.9% | -15.86% | 10.94% | 12.74% | 11.3% | 11.3% | 11.45% | 10.94% | 11.14% | 12.34% | 13.32% | 12.25% | 13.08% | 13.58% | 13.76% | 11.97% | 13.61% | 10.58% | 13.62% | 12.92% | 13.72% | 13.05% | 11.86% | 13.29% | 11.94% | 12.93% | 10.36% | 12.72% | 9.831% | 12.36% | 11.87% | 10.55% | 13.25% | -16.3% | -14% | 10.45% | -13.37% | -13.43% | -12.86% | -13.53% | -12.64% | 14.65% | 14.96% | 11.88% | 12.21% | 11.86% | 11.46% | 12.86% | 10.81% | 11.77% | -13.51% | -12.39% | -13.25% | -14.53% | -19.2% | -16.19% | 11.99% | -15.84% | -17.86% | 7.908% | -15.16% | -15.24% | 9.941% | 11.01% | 11.07% | 11.28% | 9.879% | 7.699% | 11.97% | 9.271% | 13.54% | 12.04% | 11.52% | 11.75% | 9.852% | 8.875% | 8.809% | 9.099% | 13.79% | 14.3% | 9.685% | 10.12% | 11.99% | 9.205% | 10.96% | 9.443% | 10.37% | 9.641% | 13.01% | 12.38% | 9.628% | 10.06% | 11.29% | -18.61% | -20.23% | -17.59% | -22.16% | -16.48% | -15.64% | -16.31% | 9.238% | -15.95% | -16.36% | -16.52% | -16.1% | 10.39% | -18.25% | -17.76% | -16.21% | -17.47% | -16.49% | -15.58% | -16.33% | -16.26% | -16.3% | 6.985% | 6.544% | 6.598% | 7.292% | 4.754% | 5.502% | 6.117% | 4.594% | 4.941% | 8.281% | 7.476% | 8.161% | 7.947% | 8.533% | 7.019% | 6.359% | 5.687% | 7.597% | 6.479% | 6.452% | 7.672% | 6.477% | 6.171% | 6.104% | 8.289% | 6.935% | 8.497% | 7.806% | 9.537% | 8.66% | 8.085% | 9.838% | 5.8% | 8.954% | 6.444% | 5.493% | 6.087% | 7.005% | 4.784% | 7.831% | 7.532% | 5.773% | 6.55% | 8.61% | 7.487% | 6.206% | 7.976% | 7.448% | 8.505% | 8.945% | 7.216% | 8.783% | 10.85% | 11.27% | 11.81% | 11.61% | 6.444% | 6.483% | 8.214% | 3.854% | 6.814% | 8.029% | 6.206% | 8.056% | 9.165% | 7.316% | 8.409% | 9.311% | 9.099% | 7.967% | 7.84% | 9.588% | 8.44% | 7.672% | 7.752% | 9.047% | 7.369% | 8.941% | 8.327% | 7.271% | 8.214% | 7.313% | 8.492% | 8.712% | 9.699% | 9.99% | 9.81%
2025-05-23 | -7.376% | -9.926% | -5.976% | -6.67% | -8.922% | -10.79% | -3.654% | -9.91% | -6.809% | -6.315% | -5.189% | -5.59% | -6.871% | -6.068% | -5.035% | -4.711% | -5.964% | -4.908% | -5.93% | -4.279% | -1.039% | -2.659% | -1.734% | -1.795% | -2.381% | -3.554% | -2.166% | -3.029% | -0.6074% | -1.055% | -2.551% | -2.891% | -8.706% | -8.968% | -8.351% | -7.815% | -6.159% | -5.314% | -8.197% | -6.678% | -8.367% | -7.321% | -5.091% | -5.732% | -5.315% | -3.298% | -3.508% | -3.783% | -6.388% | -3.457% | -3.53% | -5.436% | -6.002% | -6.772% | -8.001% | -7.248% | -6.246% | -10.84% | -9.668% | -10.34% | -4.726% | -7.167% | -6.561% | 1.477% | -0.5113% | 2.28% | 2.257% | 0.9151% | 0.1994% | -1.79% | 1.815% | 0.7816% | -1.699% | -3.068% | -1.664% | 0.5584% | -0.2497% | 1.548% | 1.618% | 2.496% | -1.137% | 0.791% | 4.471% | 1.998% | 1.59% | 3.96% | 1.587% | -0.434% | 0.367% | 1.66% | 0.3319% | -0.961% | 1.168% | 2.833% | 3.901% | 1.091% | -0.7713% | 2.342% | 0.7746% | 1.822% | 1.168% | 1.245% | -1.267% | 0.9432% | 5.18% | 1.372% | 3.838% | 0.4795% | 0.9502% | 3.747% | 3.22% | 3.002% | 4.523% | -0.3305% | 0.05085% | 0.5568% | 0.5427% | 1.758% | 2.721% | 1.625% | 1.4% | -0.01941% | 1.646% | 2.858% | 1.07% | 3.114% | 1.723% | 3.529% | 2.089% | 1.168% | 0.4233% | 2.18% | 0.36% | 2.159% | 0.09301% | 1.309% | 4.195% | 0.7113% | -2.627% | -1.65% | -0.694% | -0.0967% | -0.01239% | 1.203% | -0.5042% | -0.7783% | -1.495% | 3.328% | 1.155% | 0.9844% | 1.637% | -0.6307% | 2.353% | -1.874% | -0.3918% | -2.465% | 2.257% | -2.486% | -0.1318% | -1.298% | -0.8626% | -2.584% | 0.5638% | -0.3336% | 1.056% | 0.5216% | -0.5404% | 1.168% | 0.8295% | 1.307% | 0.8679% | 1.93% | 1.33% | 1.707% | 2.23% | 2.399% | 1.968% | 2.184% | 3.508% | 2.639% | 4.58% | 0.08822% | 3.454% | 3.161% | 3.4% | 2.515% | 2.361% | 3.007% | 2.515% | 4.47% | 1.999% | 4.901% | 1.545% | 2.299% | 4.319% | 3.439% | 2.663% | 0.7652% | 4.89% | 3.213% | 1.425% | 1.87% | 4.345% | 0.5691% | 2.044% | 3.764% | 1.349% | -1.36% | -3.024% | -0.04261% | 0.4385% | -0.9396% | 2.141% | 4.548% | 6.266% | 5.898% | 6.349% | 4.763% | -2.335% | -1.236% | 2.778% | -1.084% | -3.325% | -1.551% | -1.197% | -3.722% | 2.069% | 1.756% | 3.381% | 4.428% | 0.6078% | -0.3699% | 2.406% | 0.4902% | 6.258% | 5.003% | 4.148% | 3.333% | 0.9545% | 1.716% | 0.5739% | 1.624% | 6.985% | 6.769% | 4.212% | 3.885% | 5.235% | 2.187% | 4.108% | 2.911% | 3.261% | 2.035% | 2.697% | 4.608% | 2.18% | 3.048% | 2.507% | 1.517% | -1.564% | 1.377% | -0.0127% | 0.4796% | 0.8821% | 0.5433% | 1.832% | 3.377% | 4.038% | 1.759% | 2.403% | 0.5311% | -3.085% | 0.3527% | -3.305% | -0.9559% | 0.376% | 1.823% | -0.2981% | 2.159% | 1.604% | 1.391% | 1.076% | 1.068% | 1.968% | -1.556% | -0.8944% | -0.2479% | -2.01% | -1.441% | 1.468% | -1.867% | 1.961% | 1.638% | 2.372% | -1.062% | 1.701% | 0.7762% | 1.985% | 0.9419% | 0.6485% | 1.506% | -1.322% | 1.591% | 1.567% | 2.533% | 2.008% | 3.249% | 2.625% | 1.168% | 3.738% | 2.663% | 2.766% | -1.806% | 2.679% | 0.1172% | -0.9864% | -0.6667% | 0.7802% | -1.668% | 0.1096% | -1.666% | 0.3201% | 1.327% | 0.3456% | 0.4521% | -0.9179% | -0.2938% | 0.6043% | 0.5434% | -0.4414% | -0.2473% | -0.3433% | 0.8555% | 1.103% | 1.415% | 2.174% | -3.361% | -1.314% | -0.8798% | -3.833% | -1.047% | -0.9103% | -1.306% | -0.9636% | -0.08828% | -2.493% | 0.04834% | 0.6957% | 0.787% | 1.217% | 0.04035% | 2.166% | -0.6266% | -0.8342% | -0.2024% | 2.494% | -0.6121% | 2.043% | 0.376% | 1.942% | 1.754% | 2.27% | 0.9594% | 2.403% | 1.767% | 3.381% | 1.159%
2025-05-24 | -5.69% | -6.722% | -4.386% | -4.021% | -6.098% | -8.428% | -1.882% | -8.502% | -5.117% | -3.925% | -3.579% | -4.502% | -4.021% | -4.29% | -3.04% | -2.906% | -4.354% | -3.565% | -4.656% | -3.175% | -0.3865% | -1.617% | -0.8096% | -0.9634% | -1.963% | -2.886% | -1.098% | -1.886% | 0.2673% | -0.3865% | -1.81% | -1.233% | -5.559% | -6.378% | -5.569% | -4.921% | -3.342% | -3.038% | -5.463% | -3.868% | -5.059% | -3.841% | -2.002% | -1.599% | -1.952% | 0.2508% | -0.9474% | -1.892% | -4.67% | -2.662% | -2.167% | -4.593% | -5.331% | -6.242% | -7.246% | -5.391% | -5.219% | -8.752% | -13.69% | -8.719% | -3.771% | -5.84% | -4.996% | 2.088% | 0.6081% | 2.617% | 2.342% | 2.202% | 1.589% | -0.1277% | 3.227% | 2.018% | 0.4066% | -1.677% | 0.3891% | 1.381% | 0.8406% | -2.055% | 1.615% | 2.973% | 0.07377% | 0.9741% | 3.612% | 2.342% | 2.307% | 3.13% | 2.049% | 0.4926% | 3.096% | 2.264% | 1.852% | -1.424% | 1.265% | 2.351% | 3.788% | 2.141% | 1.222% | 2.421% | 1.764% | 1.628% | 0.6025% | 2.824% | 1.176% | 2.526% | 7.318% | 0.9584% | 4.103% | 1.423% | 1.668% | 4.681% | 4.164% | 4.033% | 2.707% | 1.436% | 0.8095% | 0.6606% | 1.528% | 2.395% | 0.1438% | 1.344% | 2.158% | 0.2052% | 1.674% | 2.645% | 3.84% | 3.963% | 1.808% | 4.129% | -3.798% | 1.677% | 1.169% | 0.3979% | 1.58% | 3.175% | 1.029% | 2.64% | 0.804% | 3.113% | 0.489% | 0.8095% | 1.799% | 1.335% | 2.088% | 3.026% | 2.141% | 1.414% | 2.264% | 4.119% | 3.157% | -0.7436% | 3.591% | 2.404% | 4.712% | 0.7745% | 2.08% | 1.869% | 3.84% | 2.439% | -0.6883% | -0.8897% | 1.712% | -0.8547% | 1.107% | 2.191% | 3.709% | -1.769% | -0.5932% | 1.114% | 0.1935% | 0.1263% | -0.4589% | 0.7307% | 0.9993% | 1.786% | 2.611% | 1.297% | 1.191% | 1.892% | 2.544% | 1.557% | 3.271% | -1.183% | 2.323% | 1.738% | 2.851% | 2.314% | 1.239% | 2.515% | 1.057% | 2.189% | -0.05595% | 2.208% | 0.5964% | 1.93% | 1.939% | 1.567% | 2.383% | -0.09901% | 3.467% | 2.563% | 1.384% | 1.816% | 3.651% | 0.9687% | 2.283% | 3.848% | 2.448% | -0.494% | -1.209% | 1.578% | 0.07425% | 0.3563% | 0.5619% | 2.065% | 4.346% | -0.3946% | 4.395% | 3.487% | -1.04% | -1.269% | 1.742% | -1.226% | -2.404% | -2.058% | -1.132% | -3.316% | -0.5392% | -0.5483% | 1.547% | -1.054% | 1.198% | -1.724% | 2.732% | -0.12% | 2.692% | 0.9886% | 1.268% | 2.084% | 0.4872% | -0.4901% | -0.547% | -0.2244% | 2.304% | 0.4208% | -1.024% | -1.505% | 0.6798% | -1.059% | 0.2913% | -1.097% | 0.08869% | -0.9645% | 1.284% | 1.569% | -0.3383% | 0.01278% | 0.5536% | -1.807% | -2.487% | 1.166% | 0.5764% | 1.266% | 1.359% | -2.303% | -0.9266% | 3.111% | 3.245% | 1.573% | 2.821% | 1.682% | -1.947% | 1.054% | -0.4511% | 0.7445% | 3.155% | 3.885% | 1.244% | 4.385% | 2.25% | -1.217% | -1.054% | -1.121% | -0.526% | -5.63% | -2.675% | -1.744% | -3.558% | -3.27% | -0.4589% | -3.658% | -0.03676% | 0.299% | 0.3177% | -0.2565% | -0.3874% | -1.313% | 0.1456% | -1.053% | -1.255% | 0.2659% | -3.524% | -0.3405% | -0.6197% | 1.036% | 0.2467% | 1.441% | 0.5932% | -2.972% | 1.99% | 0.912% | 0.7794% | -3.018% | 0.7005% | -1.23% | -2.596% | -2.16% | -1.093% | -3.113% | -1.297% | -2.369% | -1.91% | -1.233% | -0.6893% | -1.306% | -2.625% | -1.088% | -0.9265% | 0.03176% | -0.5151% | -1.502% | -0.6552% | 1.696% | 1.766% | 2.812% | 2.244% | -1.486% | 1.322% | -0.006191% | -1.676% | -0.6893% | 0.5062% | 0.7434% | 0.4587% | -1.192% | -2.805% | 0.7097% | 0.9189% | 1.132% | 0.6934% | 0.6001% | 2.124% | -0.8291% | 0.62% | 0.9141% | 1.208% | 0.2487% | 0.7054% | 0.2759% | -0.007614% | 0.6295% | 0.002348% | 0.6898% | 2.151% | 1.696% | 1.965% | 1.756%
2025-05-25 | -7.793% | -9.304% | -6.228% | -6.075% | -7.989% | -11.35% | -3.45% | -10.19% | -6.271% | -5.662% | -4.901% | -5.901% | -5.51% | -5.249% | -4.075% | -4.183% | -5.71% | -4.268% | -5.184% | -3.727% | -0.878% | -2.183% | -1.617% | -1.291% | -2.052% | -3.248% | -1.422% | -1.987% | -0.09507% | -0.3125% | -2.357% | -1.944% | -7.359% | -7.954% | -7.244% | -6.58% | -4.955% | -4.68% | -7.098% | -5.207% | -7.272% | -5.242% | -3.053% | -3.831% | -3.097% | -0.859% | -1.184% | -1.98% | -3.793% | -2.805% | -2.56% | -4.744% | -5.639% | -6.394% | -7.42% | -5.024% | -5.008% | -9.192% | -8.54% | -8.952% | -5.053% | -6.432% | -5.696% | 2.709% | 0.7972% | 1.668% | 1.639% | 3.036% | 0.6762% | 0.609% | 2.768% | 3.274% | 0.7279% | -0.0912% | -4.849% | 0.4703% | -0.6377% | 0.5001% | 2.442% | 2.392% | -0.5895% | 2.17% | 3.274% | 2.718% | 3.917% | 2.883% | 3.401% | 2.125% | 2.293% | 2.194% | 2.065% | -1.729% | 1.084% | 1.203% | 2.64% | 3.541% | 3.022% | 1.738% | 2.739% | 0.6671% | -0.06815% | 3.313% | 0.4728% | 3.68% | 5.661% | 2.144% | 4.244% | 1.926% | 1.223% | 4.987% | 4.541% | 3.561% | 4.387% | 2.769% | 1.451% | 4.165% | 3.066% | 3.105% | 1.986% | 0.8666% | 2.442% | 3.056% | 2.158% | 2.697% | 3.293% | 3.472% | 1.332% | 3.61% | 2.134% | 2.243% | 1.827% | 2.57% | 3.095% | 3.898% | 1.758% | 3.482% | 4.447% | 0.8368% | 2.074% | 0.7279% | 0.9062% | 2.323% | 2.758% | 2.085% | 1.847% | 3.333% | 0.03451% | 3.142% | 3.157% | 0.9467% | 2.68% | 3.224% | 5.19% | 2.709% | 3.432% | 2.442% | 2.511% | 3.561% | 3.432% | 1.996% | 2.55% | 2.501% | 0.4208% | 4.305% | 5.225% | 1.951% | -1.591% | 0.1666% | -0.3759% | -0.365% | -0.3867% | -0.1914% | 0.07979% | 1.317% | 1.718% | 0.6331% | 0.7307% | 1.262% | 1.653% | 0.2653% | 1.179% | -1.632% | 1.479% | 0.7958% | 2% | 1.479% | 0.4052% | 1.631% | 0.09064% | 1.718% | -0.8966% | 1.761% | -0.0721% | 0.9585% | 0.9829% | 0.4931% | 0.9146% | 0.03244% | 2.707% | 1.113% | 1.746% | 2.1% | 2.946% | 1.732% | 1.6% | 3.503% | 3.892% | 0.9845% | 1.712% | 1.265% | 1.12% | 1.954% | 1.328% | 2.093% | 3.14% | 0.8275% | 3.161% | 2.083% | -1.338% | -3.647% | 1.21% | -0.3694% | -2.337% | -2.252% | 0.5593% | -1.008% | 0.2266% | 0.7796% | 1.338% | 1.236% | 1.034% | -1.374% | 2.442% | 0.05296% | 2.476% | 1.056% | 1.225% | 1.597% | -0.741% | -0.8269% | -2.018% | -0.7839% | 2.431% | 2.295% | -0.8816% | -0.4299% | 0.5379% | -1.578% | -0.3633% | -1.674% | -0.08652% | -1.32% | -0.2153% | 0.2354% | -1.02% | -0.505% | 0.07442% | 2.511% | -0.4686% | 2.452% | 2.079% | 2.148% | 4.164% | 0.19% | 3.371% | 3.74% | 3.334% | 3.079% | 3.299% | 4.123% | 0.6884% | 1.047% | 2.634% | 1.441% | 2.533% | 3.259% | 2.775% | 3.932% | 2.715% | -0.9291% | -1.135% | -0.7881% | -0.2457% | -2.556% | -1.862% | -1.331% | -2.99% | -2.73% | 0.2751% | 1.58% | 0.5788% | 0.6222% | 0.6868% | -0.8966% | -0.851% | -1.55% | -0.01027% | -1.299% | -1.07% | -0.02496% | 2.145% | -0.5475% | -0.6455% | 1.064% | -0.003189% | 0.681% | 0.8459% | 1.794% | 1.678% | 0.3336% | -0.1606% | -1.819% | 1.029% | 0.2139% | -1.009% | -1.717% | -0.8738% | -2.579% | -1.363% | -0.7259% | -1.321% | -1.208% | 0.8577% | -0.9449% | -2.071% | -1.192% | -1.567% | -2.308% | 1.406% | -1.839% | -0.1493% | -1.929% | 1.788% | 1.394% | 0.8534% | -2.275% | 0.3963% | -0.6766% | -3.627% | -1.149% | -0.4191% | -0.4513% | -0.2475% | 0.8469% | -0.6337% | 0.3239% | 0.2676% | 1.029% | -0.4677% | -0.00283% | 1.124% | -1.381% | -1.192% | -1.074% | -0.1606% | -0.2036% | 0.07442% | -1.228% | -2.11% | -0.3655% | -1.772% | -0.7013% | 0.1845% | 0.5379% | 0.583% | 1.338%
2025-05-26 | -8.674% | -10.26% | -7.048% | -6.981% | -8.588% | -12.3% | -4.129% | -11.13% | -6.579% | -6.68% | -5.91% | -6.713% | -6.311% | -6.311% | -4.805% | -5.207% | -6.877% | -4.798% | -5.609% | -4.705% | -1.692% | -3.098% | -1.96% | -2.094% | -3.031% | -4.236% | -1.994% | -3.065% | -0.6547% | -1.224% | -3.232% | -3.734% | -8.019% | -8.78% | -8.216% | -7.265% | -5.996% | -5.961% | -8.152% | -5.785% | -7.751% | -5.709% | -3.391% | -4.431% | -2.978% | -0.6037% | -0.8246% | -1.3% | -3.964% | -2.723% | -2.531% | -4.809% | -5.991% | -6.877% | -7.606% | -5.512% | -4.537% | -9.093% | -8.528% | -9.206% | -6.412% | -6.427% | -5.576% | 1.234% | -0.6411% | 0.5096% | 0.2127% | 1.875% | -0.3491% | -0.6868% | 1.814% | 2.439% | 0.06025% | -0.7087% | -0.0007388% | -0.2371% | -1.321% | -0.8088% | 1.188% | 1.31% | -2.196% | 1.239% | 1.875% | 0.8946% | 2.667% | 1.66% | 1.739% | 0.6281% | 1.188% | 0.5329% | 0.5024% | -2.303% | -0.9917% | 0.01451% | 0.8378% | 1.554% | 1.341% | 1.158% | 0.7311% | -1.911% | -2.421% | 0.6853% | -2.06% | 1.737% | 5.046% | 0.4414% | 2.667% | 0.5939% | -1.007% | 3.414% | 2.957% | 3.231% | 2.443% | 1.58% | 0.06025% | 2.957% | 1.997% | 1.707% | 0.9598% | -1.022% | 1.097% | 2.271% | 1.006% | 1.484% | 2.698% | 2.82% | 0.4262% | 2.805% | 0.8988% | 1.112% | 0.8073% | 1.844% | 2.378% | 3.384% | 1.021% | 2.5% | 4.162% | 1.539% | 2.449% | 0.9293% | 1.158% | 2.591% | 3.369% | 2.408% | 1.859% | 3.536% | 3.048% | 3.03% | 2.495% | 0.6396% | 2.06% | 3.186% | 4.981% | 2.469% | 3.003% | 1.783% | 2.728% | 2.911% | 2.85% | 1.234% | 1.722% | 1.936% | 0.045% | 4.015% | 5.061% | 1.373% | -0.2621% | 2.042% | 0.8066% | 1.191% | 1.842% | 1.575% | 1.575% | 2.961% | 3.946% | 2.643% | 2.476% | 3.345% | 4.029% | 1.92% | 3.386% | 0.8309% | 3.745% | 3.161% | 4.029% | 3.161% | 2.243% | 3.578% | 2.276% | 3.245% | 0.3223% | 2.911% | 1.424% | 2.677% | 2.27% | 1.586% | 3.533% | -0.4965% | 2.227% | 1.042% | 1.5% | 1.961% | 2.937% | 1.658% | 2.715% | 4.001% | 4.012% | 1.079% | 1.567% | 1.202% | 1.388% | 4.617% | 0.7186% | 1.736% | 2.273% | 3.287% | 2.618% | 14.06% | 0.1695% | -0.4585% | 1.443% | -0.453% | -2.762% | -2.525% | 0.3677% | -1.362% | 0.1958% | 1.536% | 1.944% | 1.58% | 1.632% | -1.523% | 3.245% | 0.8053% | 3.106% | 1.944% | 1.927% | 2.707% | 1.036% | -0.2021% | 0.6236% | 0.2603% | 3.73% | 4.042% | 0.1753% | 0.4585% | 1.632% | -1.556% | 0.7475% | -0.9948% | 1.598% | -0.03695% | 3.316% | 1.697% | 0.475% | 1.07% | 1.648% | 0.3692% | -2.44% | 0.2122% | 0.03305% | 1.754% | 2.366% | 0.9475% | 1.655% | 1.646% | 1.434% | 1.298% | 1.867% | 2.684% | -0.9103% | -0.786% | 0.8977% | -0.3941% | 0.9594% | 1.692% | 1.328% | 2.472% | 1.457% | -0.4291% | -1.164% | -1.281% | -0.4291% | -1.999% | -0.9634% | -1.548% | -2.95% | -2.182% | 0.6563% | 1.814% | 0.4893% | 0.339% | 1.376% | 0.3941% | -9.004% | -1.58% | 0.5723% | -0.3741% | -0.5249% | 0.8323% | -2.014% | -0.1228% | -0.24% | 1.285% | 0.8993% | 0.8897% | 0.9831% | 2.376% | 1.779% | 0.5344% | 2.776% | 0.2725% | 2.183% | 0.7558% | -0.5984% | -1.424% | -0.3072% | -2.146% | 0.7062% | 0.5426% | -1.489% | -0.2409% | 2.787% | 1.301% | 0.1282% | -0.06998% | 0.3099% | 0.8218% | 2.388% | -0.6397% | 1.233% | 1.112% | 3.626% | 4.042% | 2.967% | -1.358% | 0.7227% | 0.7062% | -3.274% | -0.4498% | 0.1282% | -0.3012% | 0.1447% | 1.4% | -0.9287% | 0.6261% | 1.961% | 0.9374% | -0.9592% | 0.1753% | 1.771% | 0.006587% | -0.8131% | -0.3672% | 0.3833% | 0.1958% | 0.7227% | 0.18% | -1.351% | -0.1691% | -0.7438% | 0.7648% | 0.3003% | 1.406% | 1.771% | 1.06%
2025-05-27 | -6.769% | -7.738% | -5.308% | -4.92% | -6.342% | -8.929% | -2.702% | -8.846% | -5.599% | -4.258% | -4.016% | -5.033% | -4.403% | -4.468% | -3.353% | -3.45% | -4.609% | -4.252% | -5.243% | -3.789% | -1.641% | -3.014% | -2.174% | -1.819% | -2.723% | -4.323% | -2.74% | -5.13% | -0.688% | -1.431% | -3.66% | -3.111% | -5.615% | -6.513% | -5.799% | -4.932% | -3.385% | -3.147% | -5.259% | -3.725% | -4.71% | -3.987% | -2.791% | -1.164% | -1.383% | 0.07156% | -2.233% | -2.945% | -8.167% | -4.532% | -2.594% | -4.937% | -6.586% | -7.881% | -9.084% | -7.741% | -7.473% | -9.7% | -10.96% | -10.53% | -5.889% | -7.8% | -4.626% | -1.421% | -2.216% | 2.119% | 0.3961% | -1.156% | 0.1027% | -3.643% | 1.169% | -1.355% | -2.569% | -4.194% | -2.922% | -0.6096% | -1.302% | -1.384% | -1.017% | 2% | -3.879% | -2.701% | 1.456% | -1.317% | -2.032% | -0.1326% | -1.871% | -3.479% | 1.985% | -0.8915% | -1.289% | -4.063% | -1.863% | 0.7787% | 1.375% | -0.2293% | -3.777% | -1.009% | -0.3102% | -1.756% | -1.263% | -0.4353% | -0.7972% | -1.443% | -1.679% | -2.495% | 1.051% | -1.811% | -1.76% | 1.434% | 1.198% | -1.524% | 1.561% | -2.533% | -2.93% | -3.158% | -2.797% | -1.296% | -0.8547% | -0.8988% | -1.98% | -3.253% | -1.994% | -0.2634% | 1.073% | 1.5% | -0.3617% | 1.875% | -3.687% | -2.407% | -2.959% | 1.367% | -3.268% | 0.0503% | -2.665% | -3.739% | -0.3172% | 4.413% | 0.2098% | 1.927% | 3.92% | 2.375% | 3.008% | 5.959% | 1.971% | 4.119% | -3.069% | 6.521% | 2.763% | 2.852% | 4.278% | 0.9627% | 1.859% | -1.811% | -0.6781% | 0.7714% | 2.729% | -3.231% | -4.151% | -3.209% | 0.0503% | -0.6193% | 2.39% | -1.996% | 0.7861% | 0.2135% | 6.928% | 8.048% | 6.799% | 6.219% | -1.904% | 5.477% | 5.397% | 5.55% | 5.84% | 5.187% | 7.693% | 7.725% | 6.887% | 8.06% | 9.274% | 1.46% | 5.936% | 4.913% | 5.719% | 5.034% | 4.091% | 4.913% | 4.115% | 4.679% | 2.89% | 4.446% | 2.165% | 3.463% | 5.04% | 4.549% | 5.75% | 1.651% | 7.135% | 7.927% | 5.069% | 6.562% | 3.538% | 2.659% | -3.283% | 4.13% | 7.559% | 5.396% | 4.422% | 8.263% | 7.77% | 7.095% | 2.75% | 6.923% | 8.413% | 8.466% | 9.82% | 3.173% | 3.099% | 5.212% | 9.668% | 4.264% | 2.376% | 5.543% | 1.996% | -1.115% | -1.725% | -1.261% | 2.513% | 2.546% | 0.7304% | -1.388% | 3.115% | 0.4606% | 4.128% | 2.948% | 2.756% | 3.316% | 0.5164% | -1.086% | -0.03351% | 0.9627% | 4.103% | 4.187% | 1.852% | 1.202% | 3.341% | 2.11% | 3.986% | 3.928% | 1.568% | 1.369% | 3.808% | 6.765% | 1.672% | 2.31% | 2.995% | -0.6595% | -2.982% | 0.1443% | -1.048% | -3.026% | -1.992% | -3.835% | -3.495% | 0.8088% | 1.003% | -1.668% | -0.4617% | -2.794% | -4.771% | -1.002% | -3.92% | -1.853% | 2.094% | 2.606% | -2.912% | 3.46% | -0.8497% | 0.1586% | -0.2605% | -0.6312% | 0.08604% | -2.831% | -13.73% | -1.252% | -2.807% | -2.654% | -0.752% | -3.768% | -0.6876% | -0.9857% | 1.054% | 0.3943% | 0.07274% | -1.695% | -1.346% | -2.103% | -2.475% | -1.691% | -3.387% | -2.006% | -1.958% | -1.133% | -1.594% | 2.018% | -1.06% | -9.399% | 0.8681% | -0.0711% | 2.697% | -2.483% | 0.5973% | 0.2534% | -0.687% | -1.548% | 0.3774% | -0.2751% | -0.9899% | -2.683% | 0.7137% | 1.576% | 0.4287% | 0.1339% | -1.58% | -0.695% | -0.1052% | 1.17% | -1.03% | -0.01438% | 0.2283% | 2.002% | 2.287% | 3.015% | 2.94% | 0.9308% | 2.094% | 2.278% | -0.2168% | 1.497% | 1.321% | 1.816% | 1.744% | -0.6631% | -1.03% | 2.597% | 2.513% | 1.728% | 3.46% | 2.889% | 4.103% | 0.8392% | 3.075% | 2.931% | 4.538% | 1.448% | 3.115% | 1.364% | 3.576% | 3.25% | 3.81% | 3.383% | 0.9669% | -3.027% | 4.471% | -3.219%
2025-05-28 | -5.181% | -6.881% | -3.907% | -4.132% | -4.76% | -7.752% | -1.531% | -7.259% | -4.326% | -3.324% | -3.07% | -3.967% | -4.177% | -3.608% | -2.681% | -2.92% | -3.842% | -2.866% | -3.937% | -2.651% | 0.1021% | -1.319% | 0.132% | -0.1223% | -1.11% | -2.292% | -0.8105% | -2.995% | 0.491% | 0.1619% | -1.648% | -1.454% | -6.077% | -5.937% | -5.118% | -4.96% | -3.59% | -2.897% | -5.598% | -4.126% | -5.822% | -5.809% | -2.834% | -2.862% | -2.804% | -0.5735% | -1.842% | -2.613% | -5.4% | -3.368% | -3.04% | -5.026% | -5.862% | -6.793% | -7.928% | -6.386% | -5.506% | -9.555% | -8.294% | -9.527% | -4.281% | -6.133% | -5.516% | 2.373% | 0.8872% | 3.348% | 2.788% | 3.047% | 2.607% | 0.2398% | 3.858% | 2.931% | 1.146% | -0.4318% | 1.398% | 2.581% | 1.783% | 0.1171% | 1.228% | 3.354% | 0.1308% | 0.752% | 3.79% | 2.417% | 2.386% | 3.592% | 2.317% | 0.6346% | 3.661% | 2.352% | 1.896% | -0.3053% | 2.55% | 3.504% | 4.526% | 3.313% | 2.026% | 3.92% | 2.857% | 2.217% | 1.947% | 3.211% | 2.078% | 3.061% | 4.506% | 4.403% | 5.33% | 2.38% | 2.257% | 5.439% | 4.71% | 4.983% | 3.443% | 1.519% | 0.5465% | 1.037% | 0.9689% | 1.426% | 1.957% | 0.008117% | 1.453% | 1.364% | 0.885% | 1.897% | 3.068% | 3.211% | 1.242% | 3.49% | 0.8531% | 0.9621% | 0.4851% | 2.393% | 0.6282% | 2.271% | 0.1853% | -3.719% | 1.512% | 1.023% | -1.567% | -0.8232% | -0.03277% | -0.1145% | 0.7168% | 2.005% | 0.4238% | 1.78% | 0.8258% | 3.386% | 2.28% | 0.8708% | 2.463% | 0.8122% | 3.831% | -0.2508% | 0.7236% | -2.493% | 2.161% | 1.862% | 0.7577% | -1.307% | 1.112% | 1.16% | 0.4579% | 0.3406% | 1.814% | -0.7607% | -1.625% | -0.1324% | -0.5802% | -0.4235% | -0.416% | -0.11% | 0.2856% | 1.457% | 1.622% | 0.5542% | 0.293% | 0.3826% | 0.9125% | 0.002325% | 1.753% | -2.193% | 0.6737% | 0.2557% | 1.189% | 1.323% | -0.2443% | 1.353% | -0.3638% | 0.9647% | -0.9086% | 1.107% | -0.08014% | 1.189% | 0.9976% | 0.5979% | 1.954% | -1.576% | 0.9851% | -1.655% | -0.7871% | 0.02115% | 2.194% | -1.156% | 0.1829% | 2.083% | 0.6816% | -1.851% | 0.3048% | 0.2022% | -1.017% | 2.729% | -1.324% | 0.9883% | 2.484% | 2.419% | 2.91% | 3.83% | -2.868% | -3.011% | 0.3563% | -2.658% | -3.354% | -3.792% | -2.753% | -3.418% | -1.041% | -0.9282% | 1.36% | 1.167% | 0.8333% | -1.496% | 2.267% | -0.2186% | 1.918% | 1.229% | 1.5% | 1.942% | -0.2038% | -1.075% | -1.414% | -1.245% | 1.833% | 2.538% | -1.073% | -0.6836% | 0.2442% | -1.894% | 0.05047% | -1.178% | -0.004529% | -1.075% | 0.04715% | 0.8517% | -1.008% | -0.5655% | 0.1136% | 1.679% | -3.006% | 1.544% | 0.8798% | 1.256% | 1.402% | 0.5274% | -2.958% | 2.778% | 2.717% | 0.8568% | 1.806% | 1.113% | -2.643% | 0.5198% | -1.88% | -0.3551% | 2.495% | 3.572% | 0.3042% | 3.693% | 1.545% | 0.5542% | 0.2781% | 0.2184% | 0.502% | -2.364% | -0.8937% | -0.304% | -1.132% | -1.916% | 1.323% | -1.218% | 1.054% | 1.502% | 1.813% | 0.4568% | 0.7781% | -0.7484% | 0.6118% | -0.8624% | -1.095% | 0.3882% | -0.2135% | 0.06617% | 0.2159% | 1.227% | 0.5829% | 2.293% | 1.234% | 1.98% | 2.455% | 1.217% | 1.694% | -3.18% | 2.15% | 0.7558% | 0.1579% | -0.4253% | 0.6214% | -1.341% | -1.99% | -0.9846% | 0.1667% | 0.3682% | 1.339% | 0.1431% | -0.6541% | -0.3441% | -0.3515% | 0.002859% | 0.5397% | 0.1125% | 0.6937% | 1.128% | 2.337% | 2.538% | 2.5% | -1.584% | 0.8074% | 0.5343% | -2.426% | 0.2243% | 0.4753% | 0.6081% | 0.8665% | 1.56% | -0.536% | 1.453% | 1.686% | 1.324% | 1.433% | 1.19% | 2.562% | -0.5336% | 0.08405% | 0.4974% | 1.918% | 0.3964% | 1.553% | -0.1532% | 0.6085% | 1.287% | 0.8875% | 1.221% | 2.551% | 1.469% | 2.515% | 1.043%
2025-05-29 | -8.8% | -10.31% | -7.403% | -7.488% | -7.15% | -11.89% | -4.776% | -10.57% | -6.347% | -6.432% | -6.728% | -7.277% | -5.671% | -6.77% | -4.32% | -4.996% | -7.732% | -5.465% | -6.685% | -5.334% | -2.968% | -4.658% | -2.377% | -2.926% | -3.306% | -4.658% | -2.503% | -2.968% | -1.785% | -2.165% | -4.151% | -4.446% | -6.39% | -7.332% | -7.199% | -6.354% | -5.242% | -5.82% | -6.812% | -4.709% | -6.728% | -4.427% | -1.742% | -2.786% | -1.563% | 1.233% | 0.6832% | 0.5042% | -3.612% | -2.02% | -1.928% | -3.885% | -5.376% | -6.334% | -7.386% | -5.14% | -4.255% | -8.617% | -8.476% | -9.263% | -6.939% | -6.548% | -4.34% | -0.3888% | -2.217% | -1.005% | -1.659% | -0.158% | -1.833% | -1.89% | 0.6694% | 1.035% | -0.7159% | -1.995% | -0.6582% | -1.192% | -1.695% | -2.274% | -0.4081% | -0.1195% | -2.255% | -0.3536% | 0.2654% | -0.8699% | -2.64% | 0.01522% | 0.1359% | -1.178% | -3.025% | -0.9853% | -1.024% | -3.506% | -2.582% | -1.005% | -1.139% | 0.958% | 0.6879% | 0.6694% | -0.5043% | -4.39% | -3.867% | -0.7544% | -3.267% | -0.1772% | 3.286% | -1.62% | 0.1499% | -1.87% | -4.064% | 0.8426% | 0.7271% | 1.631% | 0.4578% | 0.09568% | -1.428% | 2.151% | 0.6502% | 0.5925% | -0.639% | -2.409% | 0.1307% | 1.843% | 0.3773% | 0.498% | 2.555% | 3.113% | 0.1691% | 3.017% | 0.3423% | 1.189% | 1.17% | 2.459% | 2.844% | 4.191% | 1.824% | 4.152% | 5.306% | 5.73% | 4.529% | 2.67% | 1.978% | 4.094% | 4.672% | 4.133% | 1.593% | 5.133% | 4.941% | 5.265% | 4.957% | 2.61% | 3.865% | 4.922% | 6.927% | 4.402% | 4.595% | 3.152% | 4.133% | 4.094% | 4.152% | 3.055% | 3.19% | 3.71% | 1.747% | 5.529% | 6.923% | 3.093% | 0.03629% | 2.418% | 0.8792% | 2.017% | 2.649% | 2.544% | 2.607% | 4.272% | 5.326% | 4.167% | 3.155% | 4.04% | 5.136% | 2.67% | 4.809% | 2.831% | 4.989% | 4.968% | 5.515% | 4.63% | 4.019% | 5.284% | 4.125% | 4.904% | 2.123% | 4.462% | 3.324% | 4.567% | 3.887% | 3.157% | 5.835% | 1.904% | 3.945% | 2.877% | 2.82% | 3.274% | 3.959% | 3.275% | 4.263% | 4.694% | 4.34% | 1.94% | 1.88% | 0.8545% | -6.755% | 4.624% | 2.655% | 3.687% | 4.081% | 4.815% | 4.191% | 3.05% | 1.178% | 0.3421% | 2.412% | 0.487% | -0.1535% | -1.744% | 1.622% | -0.09809% | 1.502% | 3.392% | 3.446% | 3.184% | 2.308% | 0.3751% | 3.249% | 1.605% | 5.153% | 3.949% | 3.534% | 1.564% | -7.441% | 0.8128% | -7.295% | 1.584% | 7.057% | 5.7% | 3.271% | 3.418% | 4.015% | 0.4376% | 3.184% | 1.188% | 3.835% | 2.126% | -1.834% | 1.917% | 0.1875% | 3.105% | 3.793% | 0.1297% | -1.056% | 0.3814% | 0.2305% | 1.458% | 1.998% | 1.687% | 1.562% | 1.602% | 1.542% | 1.2% | 1.682% | 3.105% | 0.3941% | 0.1131% | 2.219% | 1.05% | 2.466% | 2.588% | 1.485% | 3.454% | 1.483% | 0.3313% | -0.8067% | -2.113% | -1.607% | -3.483% | -1.692% | -0.2166% | -1.46% | -2.766% | 1.364% | 0.5925% | -0.5748% | 0.3735% | 1.321% | -0.4273% | -1.976% | -3.14% | -0.7213% | -1.991% | -2.329% | -0.3412% | -2.53% | -0.9967% | -1.335% | 0.5469% | 0.2085% | -0.3088% | -0.3201% | 1.132% | 0.5684% | -0.2724% | -5.986% | -6.926% | 1.962% | 0.521% | -0.3127% | -1.042% | 0.3914% | -1.959% | -7.357% | -0.5865% | -2.047% | 0.4043% | 3.689% | 1.376% | 1.897% | 0.4793% | 1.042% | -13.34% | 2.392% | 0.3386% | -1.215% | -8.087% | 3.753% | 2.855% | -8.306% | -0.6462% | 0.8753% | 1.48% | -3.522% | -0.08343% | -6.462e-05% | -0.7504% | -0.4794% | 1.417% | -1.563% | 0.5137% | 1.323% | 0.646% | -1.061% | -0.2085% | 1.849% | 1.144% | -0.542% | -0.3961% | 0.9951% | 0.05015% | 1.23% | 1.065% | -0.1209% | 0.4793% | 0.273% | 2.046% | 0.4826% | 2.133% | 2.418% | 0.7544%
2025-05-30 | -7.662% | -10.91% | -6.636% | -7.088% | -6.335% | -10.8% | -3.732% | -10.32% | -5.357% | -7.012% | -6.11% | -6.411% | -4.68% | -6.787% | -3.176% | -4.154% | -8.295% | -4.811% | -5.959% | -4.831% | -2.198% | -3.777% | -2.047% | -3.928% | -4.229% | -4.078% | -1.069% | -2.499% | -0.4673% | -2.273% | -2.799% | -5.583% | -5.132% | -6.87% | -7.503% | -5.84% | -4.573% | -5.682% | -6.185% | -3.385% | -5.884% | -2.96% | -0.4864% | -1.637% | -0.9833% | 2.756% | 2.302% | 1.71% | -3.971% | -0.8316% | -0.6202% | -4.654% | -5.279% | -5.765% | -7.414% | -5.419% | -3.229% | -8.423% | -8.228% | -9.187% | -6.185% | -5.911% | -4.77% | 0.2323% | -1.413% | 0.3726% | 0.06092% | 0.8491% | -0.8817% | -0.7958% | 1.843% | 2.151% | 0.4721% | -0.9174% | 0.4721% | 0.05937% | -0.5138% | -1.927% | -0.007611% | 0.9861% | -1.721% | 0.09519% | 0.6092% | -0.4422% | 1.5% | 0.4176% | 0.5967% | -0.8131% | 0.8148% | -0.3503% | -0.2818% | -3.777% | -2.68% | -1.344% | -1.138% | 0.5064% | 0.2528% | 0.4721% | -0.7615% | -4.383% | -4.204% | -0.5216% | -3.327% | 0.3008% | 3.179% | -1.276% | 0.712% | -1.036% | -3.571% | 1.637% | 1.466% | 2.151% | 0.2453% | 0.5251% | -0.7615% | 3.282% | 1.26% | 1.26% | 0.4721% | -2.029% | 1.089% | 2.837% | 1.134% | 1.277% | 4.104% | 4.824% | 1.432% | 4.481% | 1.226% | 2.151% | 2.117% | 4.173% | 4.002% | 5.544% | 3.111% | 5.612% | 7.189% | 3.145% | 6.873% | 4.687% | 5.441% | 6.263% | 6.709% | 6.503% | 5.647% | 7.257% | 6.743% | 7.045% | 6.729% | 4.072% | 5.415% | 6.675% | 8.69% | 6.023% | 6.229% | 4.55% | 6.092% | 5.475% | 5.441% | 4.55% | 4.653% | 5.27% | 3.522% | 7.254% | 9.176% | 4.573% | 2.047% | 5.012% | 2.159% | 3.435% | 3.961% | 4.186% | 3.548% | 4.974% | 6.926% | 5.687% | 4.674% | 6.513% | 7.639% | 4.312% | 7.013% | 5.29% | 6.513% | 7.113% | 7.001% | 5.612% | 4.899% | 5.988% | 5.988% | 5.049% | 3.248% | 4.224% | 4.186% | 4.937% | 3.248% | 3.287% | 7.858% | 4.011% | 6.008% | 6.089% | 5.468% | 6.248% | 7.033% | 6.043% | 7.163% | 8.38% | 7.366% | 5.727% | 5.444% | 5.231% | -5.851% | 5.813% | 7.245% | 7.063% | 6.206% | 7.217% | 6.462% | 5.621% | 4.419% | 3.66% | 6.074% | 3.665% | 1.167% | 1.124% | 4.018% | 2.897% | 1.936% | 4.7% | 4.763% | 2.542% | 0.2035% | 1.445% | 2.074% | -0.2995% | 6.907% | 4.374% | 4.335% | -5.877% | -28.29% | 0.5913% | -27.25% | 0.8141% | 7.687% | 4.062% | 6.946% | 5.936% | 6.245% | 3.227% | 5.738% | 4.118% | 5.194% | 3.227% | -12.4% | -1.933% | -6.387% | 3.821% | 3.041% | 0.1645% | -0.9913% | 0.5542% | 0.365% | 1.484% | 2.308% | 2.388% | 1.966% | 1.936% | 2.079% | 1.808% | 2.538% | 3.793% | 1.134% | 0.8398% | 3.215% | 2.113% | 3.066% | 3.326% | 2.045% | 4.493% | 2.326% | -0.693% | -2.119% | -4.484% | -4.559% | -5.572% | -3.17% | -1.444% | -3.17% | -5.234% | 0.2828% | -0.8643% | -2.457% | -0.693% | 0.9228% | -1.008% | -4.988% | -4.887% | -1.562% | -3.178% | -3.706% | -0.693% | 0.3726% | -1.258% | -3.48% | -0.2034% | 0.06022% | -2.317% | -1.936% | 0.02013% | -0.6536% | -1.363% | -17.61% | -12.63% | 0.7651% | -0.8934% | -1.821% | -2.824% | -0.06244% | -4.205% | -18.12% | -1.182% | -5.526% | -1.356% | 4.823% | -1.562% | 3.449% | 1.111% | -3.195% | -25.47% | 3.086% | 0.5542% | -1.161% | -41.93% | 3.204% | 4.452% | -15.54% | -3.974% | -3.269% | -0.4109% | -2.527% | -4.494% | -3.158% | -4.197% | -3.826% | -0.7078% | -4.754% | -1.784% | -2.174% | -0.7449% | -4.246% | -3.694% | -0.5371% | -2.422% | -1.413% | -1.487% | -3.46% | -4.371% | -3.158% | -2.139% | -4.24% | -1.636% | -3.655% | -0.03039% | -3.384% | -0.4591% | 0.2424% | -3.343%
2025-05-31 | -4.71% | -7.262% | -4.012% | -4.17% | -4.17% | -8.109% | -1.546% | -7.026% | -3.105% | -3.445% | -3.014% | -3.785% | -2.969% | -3.128% | -1.722% | -2.402% | -3.35% | -2.204% | -3.649% | -2.402% | 0.2041% | -1.269% | -0.04522% | -0.3399% | -0.8158% | -1.722% | -0.3172% | -1.677% | 0.7707% | 0.09078% | -0.8385% | -0.8612% | -4.374% | -5.091% | -4.376% | -3.493% | -2.324% | -2.682% | -4.057% | -2.467% | -4.918% | -3.608% | -1.634% | -1.934% | -1.234% | 0.493% | -0.4791% | -1.076% | -4.521% | -1.852% | 1.556% | -3.302% | -4.33% | -5.392% | -6.608% | -4.257% | -4.534% | -8.189% | -7.473% | -8.684% | -4.08% | -4.766% | -3.862% | 2.722% | 0.585% | 2.441% | 1.597% | 2.237% | 1.734% | 0.4301% | 3.269% | 2.836% | 1.225% | 0.1027% | 1.06% | 1.93% | 1.218% | -0.9945% | 1.927% | 3.352% | 0.2856% | 1.598% | 3.527% | 2.653% | 2.681% | 3.063% | 2.351% | 1.052% | 0.1411% | 2.185% | 1.896% | -0.07572% | 1.07% | 2.299% | 2.712% | 2.949% | 1.856% | 3.641% | 2.35% | 0.4189% | 1.045% | 1.999% | 0.3919% | 2.092% | 2.97% | 2.051% | 3.249% | 1.514% | 0.1824% | 3.868% | 3.548% | 1.194% | -0.8711% | 1.714% | 0.9463% | 0.006873% | 2.134% | 2.629% | 3.28% | 1.256% | 2.433% | 2.939% | 2.049% | 3.29% | 4.498% | 4.364% | 1.937% | 4.281% | -0.07572% | 2.082% | 1.597% | 3.383% | 2.526% | 3.951% | 1.906% | 3.558% | 3.106% | -0.7881% | -1.098% | 2.299% | 2.959% | 3.135% | 3.785% | 4.539% | 3.218% | 4.508% | -3.875% | 5.395% | 4.408% | 2.826% | -1.459% | 3.672% | 6.614% | 2.691% | 3.372% | 1.308% | 2.319% | 1.473% | 1.421% | -2.574% | 2.825% | 1.483% | 2.619% | 3.409% | 5.014% | -0.3258% | 0.02211% | 1.616% | 1.017% | 1.209% | 1.289% | 1.311% | 1.3% | 2.657% | 3.199% | 2.159% | 2.012% | 2.634% | 2.86% | 2.483% | 4.477% | -0.5093% | 2.702% | 2.351% | 2.939% | 2.566% | 1.65% | 2.566% | 1.481% | 2.679% | 0.5875% | 2.306% | 0.9267% | 1.82% | 2.15% | 1.699% | 3.373% | 0.8785% | 4.204% | 4.21% | 2.508% | 2.992% | 4.967% | 2.282% | 3.778% | 4.87% | 4.176% | 1.877% | 0.2974% | 1.115% | -13.09% | 1.324% | 2.546% | 0.3583% | 2.39% | -1.416% | 0.7334% | 1.372% | -3.667% | -1.966% | 3.293% | 0.258% | -2.306% | -0.89% | 0.2824% | -2.017% | -1.549% | -0.5032% | 1.262% | 1.274% | -0.1701% | -0.02585% | 0.4757% | -0.9988% | 2.19% | 1.474% | 1.392% | -1.121% | -9.587% | -0.8422% | -11.25% | -0.3725% | 2.789% | 2.155% | 1.333% | 0.2761% | 1.086% | -1.39% | 1.579% | 1.204% | -0.1041% | -0.4172% | -8.01% | 0.7905% | -3.146% | -0.1265% | -1.513% | 0.2761% | -1.913% | 1.532% | 1.022% | -2.792% | 2.311% | 2.406% | 2.695% | 3.51% | 3.615% | 2.533% | 3.265% | 0.6644% | -2.756% | 1.289% | 0.9752% | 1.499% | 4.529% | 4.66% | 1.777% | 4.849% | 2.518% | -0.1362% | -1.029% | -1.73% | -1.436% | -3.257% | -1.855% | -0.6902% | -2.454% | -3.042% | -0.5659% | -1.8% | -0.7128% | -0.1136% | 0.01307% | -0.2719% | -1.162% | -1.695% | -0.1922% | -1.021% | -1.293% | -0.3286% | -1.939% | -0.5442% | -1.259% | -0.8618% | -0.2832% | 0.255% | -0.1357% | 0.4518% | 1.236% | -0.6399% | -4.961% | -8.29% | 0.5711% | -0.7415% | -1.726% | -2.274% | -0.8536% | -2.394% | -7.172% | -4.197% | -1.65% | -1.426% | -0.16% | -4.074% | -1.927% | -3.068% | -2.151% | -6.948% | -0.843% | -2.19% | -1.356% | -10.83% | -1.826% | -1.368% | -12.85% | -2.71% | 0.7905% | 0.3208% | -2.945% | -0.2607% | 0.3432% | -0.5179% | 0.007699% | 0.6898% | -1.334% | 0.6166% | 0.9806% | 0.1195% | 0.239% | 0.2056% | 1.544% | -1.069% | -3.392% | -3.056% | 1.309% | -1.934% | 0.7458% | -1.112% | -1.098% | -0.0594% | -0.628% | -0.1231% | 1.388% | 0.5696% | 1.474% | 0.6166%
2025-06-01 | -7.86% | -9.669% | -6.567% | -6.567% | -7.336% | -11.78% | -3.668% | -9.773% | -6.284% | -5.489% | -5.309% | -6.361% | -5.771% | -5.438% | -4.437% | -4.565% | -6.267% | -4.322% | -5.771% | -4.258% | -1.538% | -3.026% | -1.974% | -1.743% | -2.308% | -3.565% | -1.692% | -2.154% | -0.666% | -1.102% | -2.436% | -2.41% | -7.439% | -8.157% | -7.239% | -6.375% | -5.052% | -5.16% | -7.105% | -5.322% | -7.003% | -5.196% | -3.035% | -4.003% | -3.013% | -0.6627% | -1.177% | -1.845% | -4.142% | -3.206% | -3.126% | -4.965% | -5.836% | -6.962% | -7.974% | -5.328% | -5.008% | -9.095% | -8.93% | -9.83% | -5.694% | -6.551% | -5.981% | 2.024% | 0.06083% | 0.8297% | 0.9022% | 2.328% | 0.6729% | -0.1145% | 2.258% | 2.62% | 0.5399% | -0.6519% | 0.388% | 0.1623% | -0.925% | -0.1378% | 1.638% | 1.463% | 0.5633% | 1.715% | 2.573% | 1.873% | 3.321% | 2.398% | 2.483% | 1.387% | 1.463% | 1.299% | 1.159% | -1.61% | 0.2712% | 0.8788% | 1.954% | 2.877% | 2.495% | 1.954% | 1.93% | -0.4852% | -0.9739% | 2.223% | -0.3396% | 2.748% | 6.289% | 1.358% | 3.298% | 1.183% | -0.06771% | 3.905% | 3.566% | 4.232% | 3.409% | 2.483% | 0.353% | -0.5585% | 2.258% | 2.994% | 1.276% | 2.468% | 1.51% | 2.69% | 1.445% | 2.276% | 3.298% | 3.041% | 0.6451% | 3.146% | 1.732% | 1.825% | 1.124% | 1.942% | 2.515% | 3.286% | 1.416% | 3.169% | 3.986% | 3.847% | -5.396% | 5.284% | 1.101% | 2.269% | 2.865% | 2.071% | 2.082% | 3.309% | -3.129% | 3.192% | 2.958% | 0.883% | 2.411% | 3.251% | 5.085% | 2.491% | 2.982% | 1.895% | 2.947% | 0.01408% | 2.807% | 1.475% | 2.047% | 2.106% | 0.2945% | 3.786% | 4.922% | 1.909% | -0.6993% | 1.208% | 0.5293% | 0.6829% | 0.9005% | 0.8237% | 0.9389% | 2.168% | 2.705% | 1.694% | 1.924% | 2.398% | 2.897% | 1.35% | 2.383% | -0.6074% | 2.679% | 1.848% | 2.948% | 2.347% | 1.348% | 2.475% | 1.131% | 2.334% | -0.2257% | 2.449% | 0.5805% | 1.758% | 1.672% | 1.068% | 2.022% | -0.04486% | 2.624% | 1.206% | 1.983% | 2.313% | 3.235% | 1.882% | 3.307% | 3.888% | 4.069% | 1.333% | 1.78% | -2.904% | -14.94% | 2.051% | 2.303% | 2.323% | 2.748% | 3.727% | 2.951% | 2.129% | 0.8739% | -2.3% | 1.616% | -0.1254% | -1.894% | -1.858% | 0.6825% | -1.001% | 0.439% | 0.9343% | 1.459% | 1.273% | -2.515% | 0.8423% | 2.163% | -0.2716% | 2.548% | 1.166% | 1.286% | 0.5815% | -0.8665% | -0.3729% | -1.689% | -0.4488% | 2.748% | 2.469% | 0.2227% | 0.1967% | 1.02% | -0.183% | 0.3822% | -0.1197% | 0.3233% | -0.7526% | 0.336% | 0.1714% | -1.259% | -0.2336% | -0.1577% | 1.285% | -0.4596% | 1.596% | 1.027% | 2.72% | 3.067% | 1.199% | 2.378% | 2.686% | 2.428% | 2.278% | 2.686% | 3.212% | 0.5451% | 0.607% | 2.208% | 0.9514% | 2.114% | 2.218% | 1.781% | 3.035% | 1.961% | 0.2862% | -0.1618% | -0.4049% | 0.06862% | -2.286% | -1.326% | 0.427% | -0.8401% | -1.928% | 1.63% | 1.148% | 0.4654% | 1.233% | 1.148% | -0.1688% | -0.5316% | -0.0449% | 0.5736% | 0.256% | 0.3459% | 0.256% | 2.799% | -0.386% | -0.5145% | 0.9495% | 0.05058% | 0.6971% | 0.6927% | 1.656% | 1.471% | 0.2209% | -1.199% | -1.293% | 1.229% | 0.03219% | -0.4741% | -0.9424% | -0.2225% | -1.889% | -2.626% | -1.035% | -1.638% | -0.8804% | 0.703% | -1.272% | -1.436% | -0.9804% | -1.246% | -2.398% | 1.251% | -1.611% | -0.7076% | -2.489% | 1.778% | 1.14% | -0.2558% | -0.7273% | 1.425% | 0.741% | -2.702% | 0.08282% | 0.5385% | 0.4752% | 0.5005% | 1.627% | -0.3982% | 0.7277% | 0.3423% | 1.425% | -0.1963% | 0.5549% | 1.618% | 0.8256% | 0.5385% | 0.8043% | 1.246% | 1.297% | 1.437% | 1.128% | -0.1494% | 0.8549% | -0.1096% | 0.9404% | 0.8809% | 1.751% | 1.605% | 1.751%
2025-06-02 | -6.237% | -8.571% | -5.002% | -5.198% | -5.423% | -9.934% | -2.044% | -8.09% | -4.244% | -3.767% | -3.71% | -4.496% | -4.075% | -3.767% | -2.728% | -3.289% | -4.7% | -2.454% | -3.71% | -2.391% | 0.6409% | -1.156% | 0.5005% | 0.1356% | -0.06092% | -1.717% | -0.03285% | -1.24% | 1.343% | 0.0233% | -0.7908% | -0.482% | -5.872% | -6.473% | -5.705% | -4.819% | -3.548% | -4.139% | -5.423% | -4.168% | -6.433% | -4.082% | -1.501% | -2.945% | -1.834% | 0.4965% | -0.05791% | -0.4118% | -2.694% | -1.658% | -1.628% | -3.907% | -4.873% | -5.864% | -6.925% | -4.261% | -3.55% | -8.139% | -7.626% | -8.339% | -4.861% | -5.059% | -4.752% | 4.072% | 1.795% | 3.023% | 2.793% | 4.34% | 2.773% | 1.757% | 4.123% | 4.775% | 2.844% | 1.896% | 1.463% | 2.332% | 0.2332% | -0.4806% | 3.151% | 2.55% | 2.192% | 2.897% | 4.378% | 3.468% | 5.222% | 3.829% | 3.869% | 2.94% | 3.534% | 2.512% | 2.882% | 1.642% | 3.317% | 3.905% | 4.557% | 5.887% | 5.322% | 4.609% | 4.378% | 1.931% | 1.49% | 4.008% | 1.848% | 5.222% | 8.33% | 4.161% | 5.606% | 3.637% | 2.051% | 5.951% | 5.58% | 6.591% | 5.622% | 3.816% | 1.604% | 5.005% | 3.701% | 4.276% | 2.946% | 3.33% | 2.473% | 3.394% | 2.305% | 3.228% | 4.404% | 3.905% | 1.553% | 3.841% | 2.371% | 2.396% | 1.553% | 2.448% | 2.742% | 3.931% | 1.898% | 3.803% | 4.364% | 4.992% | 3.392% | 2.026% | 2.345% | 3.164% | 3.88% | 3.292% | 3.074% | 4.161% | 3.701% | 3.682% | 3.313% | 1.075% | 2.184% | 4.263% | 5.762% | 3.049% | 3.662% | 1.949% | 3.33% | 2.831% | 3.176% | 1.335% | 1.898% | 1.872% | 0.325% | 4.171% | 5.286% | 1.583% | -1.968% | -0.06347% | -0.6937% | -0.3576% | -0.06347% | -0.007448% | 0.1746% | 2.023% | 2.415% | 1.043% | 0.4407% | 1.113% | 1.645% | -0.08097% | 0.5807% | -2.574% | 1.421% | 0.6088% | 2.219% | 1.939% | 0.2866% | 1.883% | -0.5816% | 1.379% | -2.052% | 0.7908% | -0.2595% | 0.8748% | 0.1984% | -0.2574% | 1.713% | -1.144% | 1.463% | 0.0281% | 0.9251% | 1.398% | 2.583% | 1.402% | 2.865% | 3.466% | 3.914% | 1.036% | 1.485% | -15.51% | -29.18% | 1.035% | 0.9904% | 1.41% | 1.526% | 1.225% | 1.879% | 1.059% | -0.1731% | -1.26% | 0.6757% | -1.174% | -3.636% | -2.766% | -0.27% | -1.912% | -2.415% | -1.807% | -1.237% | -0.8881% | -3.622% | -1.466% | 0.7262% | -1.771% | -0.2773% | -1.208% | -1.179% | -0.9027% | -2.533% | -2.588% | -3.447% | -1.91% | 0.2608% | 1.221% | -1.194% | -1.771% | -1.601% | -3.045% | -2.197% | -2.242% | -1.48% | -2.782% | -1.453% | -1.591% | -1.813% | -1.785% | -1.259% | 0.6786% | -0.5782% | 0.993% | 0.4032% | 2.307% | 2.578% | 1.637% | 2.108% | 2.146% | 2.346% | 2.334% | 2.252% | 3.138% | 0.2581% | -0.2572% | 1.871% | 0.2511% | 1.77% | 1.98% | 1.347% | 2.706% | 1.868% | -0.02145% | -0.9458% | -1.31% | -0.7357% | -2.864% | -1.366% | -0.5536% | -2.248% | -3.046% | 0.5527% | -1.772% | -0.5256% | -0.2315% | -0.3751% | -0.331% | -1.257% | -0.1545% | 0.3954% | -0.6498% | 0.4322% | 0.06683% | -1.235% | -0.6639% | -1.338% | 0.3479% | -0.6498% | -0.609% | -0.3969% | 0.2726% | 0.1984% | -0.9633% | -0.67% | -3.56% | -0.4045% | -1.176% | -2.145% | -2.879% | -2.493% | -4.229% | -16.9% | -3.301% | -2.721% | -1.63% | 0.02949% | -1.037% | -2.353% | -2.948% | -2.381% | -2.505% | -0.5189% | -3.579% | -1.848% | -5.353% | 0.1444% | 0.6389% | -2.139% | -0.386% | 1.47% | 1.207% | -3.198% | -0.03977% | 0.1126% | -0.4553% | -0.3168% | 0.6251% | -1.702% | -0.4955% | -1.106% | -0.02592% | -1.29% | -0.5973% | 0.9298% | 0.8769% | 0.1264% | -0.1644% | 1.817% | 0.4274% | 1.608% | 0.467% | -0.5536% | 0.5835% | -0.6409% | 0.4499% | 0.4705% | 0.8425% | 1.032% | 0.6971%
2025-06-03 | -8.216% | -10.6% | -6.81% | -7.043% | -7.11% | -11.34% | -4.235% | -8.542% | -5.478% | -5.178% | -5.811% | -6.277% | -5.544% | -5.644% | -4.512% | -5.345% | -6.393% | -4.36% | -5.578% | -4.312% | -1.181% | -3.146% | -1.415% | -1.548% | -1.415% | -3.413% | -1.748% | -2.58% | -0.2489% | -0.7818% | -2.414% | -1.981% | -7.343% | -8.251% | -7.655% | -6.568% | -5.236% | -6.007% | -6.777% | -5.937% | -8.309% | -5.926% | -3.383% | -4.938% | -3.685% | -1.352% | -1.7% | -1.732% | -5.65% | -3.022% | -3.338% | -5.027% | -5.951% | -7.673% | -8.642% | -5.858% | -5.129% | -9.76% | -9.298% | -10.6% | -6.977% | -6.717% | -6.142% | 2.188% | -0.4064% | 0.9843% | 0.5797% | 2.552% | 1.101% | -0.0575% | 2.248% | 3.068% | 0.7617% | 0.2353% | 0.6707% | 0.8851% | -0.7802% | -0.725% | 1.247% | 0.2762% | 0.3218% | 1.288% | 2.127% | 1.266% | 3.098% | 2.202% | 2.233% | 1.177% | 1.505% | 1.02% | 0.9286% | -0.9829% | 0.2156% | 0.9134% | 1.277% | 3.174% | 2.666% | 2.4% | 1.702% | -1.415% | -1.446% | 1.535% | -0.8395% | 2.415% | 5.904% | 1.808% | 3.022% | 1.793% | -0.1637% | 3.841% | 3.28% | 4.387% | 3.28% | 2.154% | 0.2307% | 3.523% | 2.218% | 2.537% | 1.035% | 1.733% | 0.8982% | 2.491% | 0.9961% | 1.932% | 3.128% | 2.688% | 0.3066% | 2.795% | 1.126% | 1.323% | 0.8527% | 1.626% | 2.43% | 3.265% | 1.293% | 3.098% | 3.962% | 3.325% | 2.275% | 0.5948% | 0.1245% | 2.021% | 2.597% | 1.899% | 1.535% | 1.338% | 2.43% | 2.598% | 2.48% | 0.07627% | 1.274% | 2.931% | 4.892% | 2.537% | 2.749% | 1.202% | 2.506% | 2.567% | 2.901% | 1.141% | 1.535% | 1.551% | -0.4216% | 1.797% | 4.949% | 1.155% | -0.608% | 1.486% | 0.8375% | 1.27% | 1.768% | 1.469% | 1.353% | 2.865% | 3.164% | 2.416% | 2.233% | 2.649% | 3.396% | 1.221% | 2.602% | -0.03475% | 3.13% | 2.316% | 3.13% | 2.748% | 1.602% | 2.914% | 1.303% | 2.682% | -0.1926% | 2.516% | 0.7877% | 1.984% | 1.937% | 1.047% | 3.14% | -1.141% | 1.371% | 0.00551% | 0.7409% | 1.32% | 2.547% | 1.153% | 2.505% | 3.015% | 3.3% | 0.9529% | 1.361% | 0.2389% | -0.3006% | 1.574% | 1.34% | 1.662% | 1.334% | 2.742% | 1.909% | 13.11% | -0.2849% | -1.069% | 0.3615% | -1.149% | -2.784% | -1.236% | -0.3312% | -1.825% | 0.05884% | 1.016% | 1.369% | 1.8% | 2.231% | 1.307% | 2.904% | 0.6497% | 2.318% | 1.593% | 1.507% | 2.042% | -1.634% | -0.4513% | -1.947% | -0.2706% | 3.698% | 6.286% | 2.318% | 1.192% | 1.248% | -0.9607% | 0.7129% | 0.2717% | 1.093% | -0.5828% | 1.06% | 0.9455% | -0.1062% | 0.04166% | 0.9948% | -0.4274% | -1.484% | 0.02952% | -0.4795% | 1.398% | 2.332% | 1.559% | 1.495% | 1.878% | 1.8% | 1.575% | 1.847% | 2.824% | -0.2511% | -2.241% | 1.26% | -0.1268% | 1.512% | 1.647% | 0.9597% | 2.363% | 1.22% | 0.4886% | -0.691% | -1.023% | -0.5083% | -2.519% | -0.9901% | -0.009827% | -0.8572% | -2.236% | 1.984% | -1.332% | 0.5385% | 1.137% | 1.5% | 0.1746% | -0.593% | -0.0945% | 0.9929% | 0.2981% | 1.048% | 0.8816% | -1.085% | -0.1187% | -0.2354% | 1.048% | 0.7149% | 0.6466% | 0.9983% | 2.117% | 1.535% | 0.4886% | 0.8855% | 0.8097% | 1.919% | 0.436% | -0.2377% | -0.8128% | 0.3491% | -1.615% | -0.2541% | -0.6% | -1.099% | 0.2298% | 3.098% | 1.57% | 1.011% | -0.2048% | 0.3539% | -2.16% | 1.817% | -0.2878% | 0.4024% | -5.447% | 3.18% | 3.525% | 1.075% | -1.043% | 0.4853% | 0.9126% | -4.198% | -0.1062% | -0.3692% | -1.404% | -0.5663% | 0.6168% | -1.93% | 0.1435% | 2.663% | 0.04166% | -1.288% | -0.3396% | 1.127% | 1.173% | -1.026% | -0.9279% | 1.334% | -0.1294% | 1.406% | 0.05884% | -0.4604% | 0.1238% | -0.3568% | 1.144% | 0.238% | 0.9027% | 1.662% | 0.7474%
2025-06-04 | -6.637% | -9.042% | -5.2% | -5.462% | -6.817% | -10.64% | -2.562% | -7.201% | -5.301% | -5.078% | -4.067% | -4.795% | -5.382% | -5.422% | -4.249% | -4.209% | -5.467% | -3.977% | -5.26% | -3.885% | -0.5091% | -2.935% | -1.5% | -1.318% | -1.176% | -3.178% | -1.864% | -2.592% | 0.5624% | -0.7517% | -2.127% | -1.601% | -8.293% | -8.957% | -7.552% | -6.893% | -4.722% | -4.977% | -7.1% | -5.765% | -7.686% | -6.595% | -4.892% | -6.009% | -4.488% | -2.752% | -2.57% | -2.792% | -5.257% | -3.214% | -3.816% | -5.327% | -5.767% | -7.359% | -8.346% | -5.446% | -5.052% | -9.533% | -8.811% | -9.694% | -4.856% | -6.148% | -6.301% | 4.272% | 4.705% | 5.123% | 4.981% | 4.88% | 3.668% | 1.334% | 3.572% | 4.392% | 2.108% | 1.7% | 1.758% | 2.494% | 0.2216% | 1.878% | 3.047% | 3.406% | 1.96% | 4.119% | 5.091% | 4.082% | 5.948% | 5.574% | 5.902% | 4.452% | 4.272% | 3.397% | 3.093% | 3.756% | 5.81% | 6.362% | 6.878% | 8.093% | 7.079% | 7.182% | 7.016% | 5.594% | 5.44% | 6.325% | 3.289% | 6.602% | 11.78% | 6.344% | 7.034% | 4.972% | 5.736% | 7.209% | 6.777% | 5.266% | 6.92% | 5.305% | 1.463% | 3.996% | 3.268% | 4.198% | 2.458% | 3.802% | 2.062% | 3.452% | 2.619% | 3.62% | 3.461% | 2.679% | 1.389% | 3.351% | 2.844% | 2.633% | 1.583% | 1.97% | 2.412% | 3.342% | 1.251% | 2.946% | 3.322% | -1.944% | -3.858% | -4.191% | -4.117% | -2.893% | -2.294% | -1.834% | -2.534% | -1.373% | -1.023% | 1.088% | -0.08167% | -2.32% | -0.2829% | -0.6365% | 2.533% | 0.4409% | 1.5% | 0.6251% | 1.822% | 2.135% | 2.273% | 0.2475% | 1.159% | -1.972% | -2.193% | 2.434% | 3.314% | 0.06756% | -3.176% | -3.317% | -3.377% | -3.579% | -3.075% | -3.176% | -2.671% | -2.57% | -2.55% | -3.176% | -2.409% | -2.137% | -2.359% | -3.163% | -2.076% | -2.763% | -1.955% | -2.57% | -1.763% | -2.409% | -3.377% | -2.046% | -3.024% | -1.774% | -2.369% | -1.501% | -2.954% | -2.459% | -2.337% | -2.729% | -2.602% | -2.985% | -0.7147% | -2.95% | -2.172% | -1.601% | -0.7198% | -2.716% | -1.209% | -0.7586% | -1.073% | -2.308% | -2.898% | -3.342% | -2.821% | 0.4338% | -0.6211% | 0.5485% | 0.02482% | 0.5208% | -0.1902% | -1.255% | -3.117% | -3.198% | -2.488% | -3.025% | -3.203% | -1.888% | -3.659% | -3.436% | -1.384% | -1.318% | -0.4675% | -0.258% | 0.36% | -0.6086% | 1.407% | -1.317% | 0.2029% | -1.106% | -0.855% | -0.3103% | -2.893% | -3.072% | -4.429% | -3.531% | 0.2029% | 3.481% | -1.347% | -1.826% | -1.232% | -2.454% | -1.923% | -2.175% | -2.145% | -3.501% | -2.394% | -1.955% | -3.621% | -3.262% | -2.973% | 2.177% | -1.353% | 2.762% | 2.114% | 1.717% | 4.153% | 2.94% | 3.776% | 4.291% | 4.082% | 3.572% | 3.681% | 3.397% | 0.5708% | -0.1479% | 1.095% | 0.854% | 1.829% | 2.294% | 2.197% | 3.117% | 2.605% | 3.158% | 2.331% | 2.059% | 2.624% | -0.2002% | 1.313% | 2.826% | 0.99% | 0.2537% | 3.461% | 0.5422% | 2.301% | 2.896% | 2.651% | 2.216% | 1.75% | 2.514% | 2.961% | 2.438% | 2.883% | 2.124% | 1.151% | 1.861% | 1.648% | 3.237% | 2.357% | 2.531% | 2.944% | 3.552% | 3.424% | 2.301% | 2.937% | -0.7448% | 4.101% | 2.563% | 2.025% | 1.187% | 1.348% | -0.5209% | -1.506% | 0.1676% | 1.041% | 1.983% | 2.803% | 1.446% | 0.5984% | 0.4188% | 1.027% | -0.5388% | 2.443% | 0.02482% | -0.03803% | -1.316% | 1.627% | 1.805% | -0.03803% | -0.3193% | 1.696% | 1.636% | -2.454% | 0.6582% | 0.5086% | 0.7779% | 0.4587% | 1.576% | -0.4889% | 0.8732% | 0.5485% | 1.666% | 0.8021% | 1.125% | 2.79% | 2.472% | 1.666% | 1.755% | 3.293% | 1.92% | 3.282% | 3.672% | 2.518% | 3.122% | 2.758% | 1.9% | 2.61% | 4.11% | 3.617% | 2.957%
2025-06-05 | -4.447% | -7.333% | -3.421% | -3.604% | -5.912% | -9.751% | -1.261% | -5.752% | -4.152% | -4.084% | -2.736% | -3.513% | -5.272% | -3.969% | -3.992% | -3.398% | -4.086% | -2.691% | -3.353% | -2.164% | 0.8515% | -0.4052% | 0.1432% | -0.1767% | 0.2117% | -0.4966% | -0.3595% | -0.7936% | 1.811% | 1.24% | -0.2224% | 0.006097% | -8.219% | -8.872% | -7.525% | -6.876% | -4.639% | -4.447% | -7.579% | -5.962% | -7.808% | -6.553% | -4.711% | -5.09% | -4.341% | -2.495% | -2.75% | -2.955% | -5.189% | -3.102% | -4.281% | -5.891% | -5.909% | -6.732% | -7.709% | -4.878% | -4.434% | -8.654% | -7.522% | -8.326% | -3.878% | -5.439% | -6.514% | 4.528% | 3.31% | 4.133% | 4.112% | 4.486% | 3.784% | 1.989% | 4.361% | 4.403% | 2.634% | 1.864% | 2.561% | 3.622% | 1.902% | 2.072% | 3.841% | 4.382% | 1.812% | 3.933% | 2.925% | 5.221% | 5.454% | 5.112% | 4.764% | 3.659% | 4.642% | 3.935% | 4.06% | 0.542% | 2.977% | 3.477% | 4.122% | 4.497% | 4.065% | 3.997% | 3.622% | 3.121% | 2.98% | 4.268% | 1.535% | 4.413% | 6.224% | 3.747% | 5.433% | 4.153% | 4.434% | 6.37% | 5.933% | 3.414% | 5.661% | 4.187% | 1.957% | 1.458% | 3.529% | 4.382% | 3.289% | 4.455% | 3.3% | 3.061% | 2.359% | 3.524% | 3.675% | 2.696% | 1.385% | 3.123% | 2.186% | 0.4692% | 0.3235% | 0.9479% | 1.427% | 1.812% | 0.02166% | 1.593% | 2.37% | 2.873% | 0.2539% | -0.8109% | -1.071% | 1.312% | 1.125% | 0.5524% | -0.09282% | 1.208% | 0.03207% | 0.8145% | -0.2064% | -1.873% | -0.5695% | 0.2922% | 2.116% | -0.3946% | 0.4796% | -0.4571% | -0.2593% | -1.134% | -2.632% | -0.9982% | -0.2281% | -0.5715% | -2.486% | 1.489% | 2.519% | -0.9263% | 3.016% | 4.327% | 2.743% | 1.979% | 0.9989% | 0.5886% | 0.08708% | 0.7026% | 1.409% | 0.9533% | 3.746% | 4.373% | 2.937% | 2.889% | 3.005% | -2.156% | 2.401% | 1.25% | 2.15% | 1.079% | 0.07568% | 0.4518% | -0.1409% | 0.5544% | -1.292% | 0.543% | -2.523% | -7.208% | -0.6413% | -1.97% | -0.4258% | -0.2026% | 3.417% | 2.41% | 3.859% | 4.388% | 6.363% | 3.688% | 5.757% | 7.248% | 7.754% | 5.668% | 6.174% | -0.5393% | 0.4458% | 4.845% | 2.366% | 2.599% | 3.558% | 4.704% | 4.186% | 3.951% | 1.972% | 3.828% | 4.809% | 3.627% | 1.433% | 2.292% | 2.565% | 0.6442% | -3.016% | -3.07% | -1.473% | -1.567% | -1.97% | -2.794% | -0.4548% | -2.67% | -0.1589% | -1.496% | -1.78% | -1.248% | -2.862% | -3.583% | -3.797% | -3.515% | -0.1944% | 0.6105% | -1.674% | -2.478% | -0.9874% | -1.565% | -1.236% | -1.238% | -2.208% | -2.715% | 0.04687% | 0.05814% | -2.704% | -1.712% | -1.171% | -5.426% | -0.9272% | 1.156% | 0.6933% | -0.33% | -13.3% | -1.143% | 1.625% | 2.569% | 2.628% | 1.938% | 2.375% | 1.416% | -1.222% | -0.504% | -0.3932% | -1.372% | 0.1371% | 0.2291% | 0.1371% | 1.096% | 1.547% | 2.23% | 1.614% | 0.4746% | 2.31% | -1.839% | 0.9077% | 1.033% | -1.474% | -2.284% | 0.5316% | -0.6652% | -0.3802% | -0.2321% | -0.006959% | 1.645% | -0.1745% | 0.589% | 0.9677% | 0.5659% | 1.103% | 0.7032% | -1.024% | -0.05169% | -0.7379% | 0.6688% | -0.1317% | 0.6454% | -0.07456% | 0.09847% | 0.4718% | -0.4139% | 2.398% | -0.7378% | 2.291% | 0.216% | -0.5055% | -1.633% | -1.072% | -2.841% | -2.039% | -2.359% | -1.84% | -0.4429% | -0.09968% | -0.7761% | -3.076% | -2.332% | -2.129% | -1.419% | 0.07459% | -2.621% | -2.266% | -0.7152% | -0.6797% | -0.5731% | -0.2062% | -3.718% | -1.204% | -1.622% | -4.97% | -2.456% | -2.94% | -1.779% | -3.234% | -1.633% | -3.808% | -2.574% | -2.23% | -1.182% | -1.994% | -1.769% | -0.05233% | -0.3472% | -0.5506% | -0.5168% | 0.6934% | -0.5731% | 0.3851% | 1.202% | 0.8946% | 0.5767% | -2.112% | -3.177% | 0.0623% | 2.055% | 0.7999% | 0.0542%
2025-06-06 | -5.904% | -8.016% | -4.435% | -4.457% | -5.934% | -9.499% | -1.97% | -6.529% | -4.655% | -4.346% | -3.068% | -4.016% | -4.324% | -4.104% | -3.509% | -3.376% | -4.302% | -3.211% | -3.156% | -2.494% | 0.7251% | -0.7082% | -0.7082% | -0.9949% | -0.0467% | -0.2672% | -0.06875% | -1.348% | 1.541% | 0.6148% | -0.3775% | -0.8846% | -6.596% | -7.622% | -6.531% | -5.602% | -3.583% | -4.349% | -5.824% | -4.79% | -6.551% | -5.166% | -3.437% | -3.937% | -3.49% | -1.393% | -2.498% | -2.94% | -6.33% | -3.643% | -3.762% | -5.379% | -5.751% | -7.157% | -8.742% | -5.838% | -5.366% | -9.375% | -8.613% | -9.868% | -4.942% | -6.679% | -6.066% | 4.131% | 3.057% | 4.829% | 4.352% | 2.816% | 2.352% | 1.45% | 4.292% | 2.715% | 1.088% | -0.4387% | 0.4354% | 1.441% | 0.08665% | -3.12% | 3.931% | 5.156% | 1.319% | 3.71% | 6.341% | 4.959% | 4.352% | 5.61% | 3.814% | 3.006% | 5.327% | 3.961% | 3.629% | 2.414% | 4.071% | 6.512% | 6.562% | 5.839% | 4.671% | 6.622% | 5.437% | 4.108% | 5.347% | 5.397% | 3.751% | 4.724% | 7.607% | 3.609% | 5.708% | 2.002% | 3.268% | 5.578% | 6.19% | 6.452% | 6.305% | 3.468% | 1.621% | 1.711% | 2.404% | 2.916% | 4.583% | 3.81% | 2.283% | 1.57% | 1.032% | 2.302% | 2.986% | 2.846% | 0.7669% | 2.966% | 1.289% | 0.8573% | 0.1843% | 2.203% | 0.6765% | 2.735% | 0.4053% | 1.811% | 1.746% | 1.169% | -1.963% | 1.239% | 0.3852% | -1.232% | 0.8372% | 1.56% | 0.7267% | 1.138% | -2.829% | 3.289% | 2.266% | 0.9477% | 3.2% | 1.118% | 4.534% | 0.1542% | 0.6062% | -1.623% | 2.896% | 2.304% | 1.309% | -4.506% | 1.952% | -4.165% | 0.576% | 0.6878% | 2.213% | 2.775% | -5.707% | -3.87% | -4.222% | -3.375% | -2.924% | -2.286% | -1.23% | 0.5517% | -0.09735% | -1.868% | -3.474% | -2.649% | -1.549% | -2.621% | -1.119% | -5.94% | -1.978% | -2.781% | -1.461% | -1.307% | -3.056% | -0.8894% | -3.276% | -1.351% | -4.145% | -1.021% | -0.2734% | -0.4384% | -0.4615% | -0.1034% | 0.09295% | -4.135% | -0.7287% | -2.069% | -2.989% | -2.913% | -1.65% | -3.17% | -1.96% | -0.975% | -1.83% | -4.087% | -2.664% | -2.142% | -3.877% | -1.009% | -3.37% | -3.143% | -0.8585% | -0.6381% | -0.2579% | -1.431% | -4.836% | -4.149% | -3.107% | -4.077% | -4.653% | -4.545% | -5.702% | -6.793% | -3.204% | -3.35% | -0.6529% | -0.6529% | 0.9464% | -1.195% | 1.7% | -1.315% | -0.6529% | -1.498% | -0.5729% | -0.4587% | -2.087% | -2.414% | -3.371% | -2.294% | -2.138% | 0.2953% | -1.795% | -4.307% | -3.463% | -2.794% | -2.675% | -2.664% | -2.087% | -4.002% | -3.752% | -3.882% | -2.827% | -2.979% | -2.381% | -1.356% | -0.2729% | 3.782% | 2.109% | -0.2928% | -1.951% | 0.3329% | 1.688% | 2.673% | 2.63% | 1.179% | 2.279% | 0.7404% | -2.424% | 0.6493% | -1.347% | 0.8664% | 3.532% | 3.659% | 0.186% | 3.939% | 1.458% | 1.839% | 1.63% | 0.9587% | 0.7827% | -1.065% | 0.001652% | 2.873% | 1.586% | -0.1413% | 3.005% | -1.583% | 1.729% | 2.268% | 3.824% | 1.687% | 0.7167% | 0.9856% | 0.8638% | 1.193% | 1.358% | -0.3414% | -3.221% | -0.3083% | -0.2531% | 0.3981% | 0.1222% | 2.207% | 0.8065% | 2.136% | 2.149% | 0.5781% | 3.597% | -3.33% | 3.893% | 2.504% | 2.341% | 1.84% | 3.558% | 2.135% | 2.961% | 1.469% | 1.712% | 1.552% | 3.787% | 1.927% | 1.383% | 2.46% | 2.254% | 3.069% | 2.904% | 2.58% | 4.876% | 5.447% | 7.229% | 7.035% | 6.727% | -0.5642% | 1.59% | 1.557% | -1.108% | 1.492% | 1.111% | 2.895% | 2.058% | 4.049% | 2.58% | 2.786% | 3.037% | 4.701% | 4.804% | 4.522% | 5.687% | 0.6899% | 1.84% | 2.123% | 3.277% | 1.822% | 2.863% | 0.7107% | 1.083% | 2.341% | 1.575% | 3.894% | 5.189% | 3.597% | 4.545% | 3.756%
2025-06-07 | -5.907% | -7.933% | -4.638% | -4.711% | -4.602% | -7.405% | -1.892% | -6.109% | -3.766% | -3.022% | -2.986% | -3.676% | -2.967% | -3.222% | -2.532% | -2.768% | -3.843% | -3.422% | -3.712% | -2.913% | 0.2282% | -1.007% | -0.2439% | -0.3528% | -0.6978% | -0.3347% | -0.2621% | -1.588% | -0.1168% | -0.06232% | -0.7705% | -0.8068% | -4.402% | -5.448% | -4.569% | -4.149% | -2.524% | -3.327% | -4.166% | -3.805% | -5.328% | -3.241% | -0.6391% | -0.8533% | -1.274% | 1.16% | -0.2902% | -0.8437% | -4.217% | -1.922% | -1.318% | -3.573% | -4.475% | -5.172% | -6.861% | -5.069% | -4.951% | -8.651% | -8.399% | -9.03% | -4.493% | -5.847% | -3.936% | 1.809% | 0.5267% | 1.835% | 1.602% | 1.263% | 0.9978% | 0.1049% | 3.19% | 1.685% | 0.6177% | -1.221% | 0.2041% | 0.9977% | 0.02933% | -2.881% | -0.35% | 2.048% | -2.409% | -0.2142% | 1.891% | 1.871% | 0.5267% | 2.372% | 0.8161% | -0.5346% | 2.115% | 1.163% | 1.651% | -3.038% | -0.2259% | 0.4853% | 1.478% | 0.7334% | -0.5306% | 0.8906% | 0.568% | 0.6259% | 0.9977% | 1.114% | -0.5317% | 0.7996% | 4.108% | 0.7417% | 2.379% | 0.6673% | 0.9733% | 3.215% | 2.892% | 1.602% | 2.99% | -0.2906% | 0.2538% | 1.668% | 0.4771% | 2.015% | 3.107% | 2.644% | 2.123% | 1.949% | 1.3% | 2.606% | 4.306% | 4.133% | 1.908% | 4.356% | 1.56% | 1.602% | 0.7583% | 3.612% | 1.734% | 3.851% | 1.552% | 3.231% | 5.589% | 1.552% | -0.9643% | -0.3831% | 1.13% | -0.3004% | 0.5019% | 2.189% | 1.304% | 1.817% | -1.781% | 3.021% | 2.639% | 1.145% | 2.994% | 1.949% | 5.354% | 1.271% | 2.172% | 0.3778% | 4.579% | 1.056% | 2.239% | 1.412% | 2.148% | 1.511% | 1.023% | 2.322% | 4% | 1.101% | -2.608% | -0.7418% | -0.6694% | -0.298% | -0.3705% | -0.1893% | 0.06432% | 1.197% | 1.423% | 0.5263% | -0.03531% | 0.5172% | 1.106% | 0.2265% | 1.556% | -2.642% | 0.9973% | 0.2636% | 1.323% | 1.133% | -0.4701% | 0.8614% | -0.769% | 0.6622% | -1.575% | 0.6984% | -0.02626% | -12.52% | 0.3596% | 0.2645% | 1.101% | -1.969% | 2.08% | 0.3009% | -0.4911% | -0.07906% | 1.704% | -0.8248% | 0.5099% | 1.537% | -0.03816% | -3.02% | -2.147% | -15.8% | -3.58% | 1.119% | 0.07669% | 1.59% | 2.295% | 2.547% | 2.798% | 1.861% | -5.356% | -5.322% | 0.001543% | -3.617% | -5.692% | -4.442% | -3.156% | -5.584% | -0.8903% | -1.07% | 1.194% | 1.59% | 2.605% | 1.213% | 3.574% | 0.5862% | 1.975% | 0.9499% | 1.232% | 1.637% | 0.425% | -0.659% | -1.188% | -1.062% | 1.881% | 4.6% | 0.3949% | -0.5784% | 0.2821% | -1.08% | 0.1598% | -0.238% | -0.6232% | -2.298% | -0.9726% | 0.07557% | -1.501% | -1.492% | -2.89% | -1.976% | -2.404% | 2.211% | 1.656% | -0.01493% | 1.637% | 1.387% | 2.076% | 2.744% | 2.931% | 1.491% | 2.676% | 2.663% | -0.8437% | 1.927% | 0.2547% | 2.24% | 4.694% | 4.746% | 1.475% | 3.768% | 2.094% | 0.8071% | 0.1368% | 0.02809% | -0.0172% | -3.287% | -1.466% | 0.9792% | -0.07155% | -1.421% | 2.012% | -2.31% | 0.3361% | 2.03% | 2.68% | -0.1825% | 0.3026% | 0.07481% | 0.6129% | -0.2849% | -0.1213% | -0.03043% | -2.105% | 0.07864% | 0.04228% | 1.333% | 0.5785% | 1.789% | 1.06% | 1.885% | 2.1% | 1.178% | 1.138% | -3.433% | 1.786% | 0.03078% | -0.04089% | -0.2201% | 1.72% | -0.2521% | -0.5605% | -0.8134% | -0.3011% | 0.7618% | 1.097% | 0.3891% | -0.5246% | -0.6322% | -0.444% | -0.5694% | 0.5135% | -0.2259% | 1.119% | 0.7524% | 3.292% | 3.471% | 2.21% | 0.7027% | 2.817% | 1.957% | -0.6501% | 1.706% | 2.584% | 1.975% | 2.369% | 2.79% | -1.868% | 2.634% | 2.812% | 1.957% | 1.194% | 2.05% | 2.982% | -0.04374% | 0.5504% | 1.106% | 2.474% | 1.273% | 2.226% | -0.2148% | 1.307% | 1.616% | 1.176% | 2.53% | 2.857% | -0.1224% | 2.427% | 1.467%
2025-06-08 | -6.374% | -8.437% | -5.477% | -6.005% | -5.854% | -8.027% | -3.014% | -7.316% | -4.874% | -4.814% | -3.879% | -4.588% | -5.191% | -4.964% | -4.497% | -4.603% | -4.898% | -4.453% | -4.301% | -3.517% | -0.487% | -1.889% | -0.9845% | -1.799% | -1.497% | -1.256% | -1.301% | -2.387% | -0.5323% | -0.8338% | -1.588% | -1.437% | -6.864% | -7.199% | -6.342% | -6.294% | -4.628% | -4.771% | -6.095% | -5.564% | -6.924% | -5.229% | -3.097% | -4.008% | -3.993% | -1.913% | -2.036% | -2.976% | -4.978% | -3.391% | -3.435% | -5.38% | -6.073% | -6.38% | -7.442% | -6.114% | -6.707% | -9.977% | -9.61% | -10.13% | -5.115% | -6.824% | -6.454% | 2.904% | 1.352% | 1.33% | 1.784% | 1.661% | 1.007% | 0.4592% | 2.808% | 2.196% | 0.418% | -1.205% | 0.4043% | 1.644% | 0.1871% | 3.11% | 3.329% | 3.378% | 1.022% | 3.025% | 4.6% | 3.827% | 3.233% | 3.669% | 2.621% | 0.9249% | 2.121% | 2.313% | 2.567% | -2.631% | -1.003% | -0.6944% | 0.6446% | 0.5485% | -1.639% | 0.3494% | 0.7476% | 0.7614% | 0.3378% | 1.599% | -0.9816% | 1.565% | 4.05% | 1.063% | 3.075% | 1.112% | 1.826% | 3.796% | 3.364% | 3.055% | 3.567% | 0.9983% | 1.901% | 2.093% | 2.43% | 3.055% | 4.586% | 3.638% | 0.8987% | 1.695% | 1.063% | 2.786% | 2.711% | 2.711% | 0.5416% | 3.082% | 0.624% | 1.791% | 0.933% | 1.414% | 1.235% | 2.519% | 0.7682% | 2.032% | 1.752% | -1.072% | -3.383% | -2.754% | -2.418% | -2.26% | -1.031% | -0.02831% | -0.4197% | 0.2876% | 0.3494% | 1.522% | 2.288% | -0.1862% | 1.898% | 0.9536% | 3.882% | 0.09529% | 1.318% | 0.1777% | 2.526% | -1.978% | 1.194% | -0.6532% | 0.3974% | 0.9536% | -1.12% | 0.7482% | 2.087% | 0.7039% | -4.315% | -4.187% | -3.819% | -3.766% | -3.736% | -3.345% | -2.736% | -1.465% | -1.277% | -1.69% | -3.728% | -3.112% | -1.615% | -3.219% | -1.537% | -3.969% | -1.111% | -1.773% | -0.5924% | -0.7428% | -1.773% | -0.2013% | -2.382% | -0.07343% | -2.803% | 0.4079% | -0.5247% | -3.886% | -0.1626% | -0.1626% | -0.1468% | -3.076% | -0.7526% | -3.353% | -3.432% | -2.628% | -1.235% | -3.808% | -2.73% | -2.233% | -3.409% | -3.761% | -4.244% | -3.991% | -3.511% | 0.3046% | -4.459% | -1.353% | 0.6225% | -0.1179% | -0.4939% | -1.587% | -4.674% | -4.327% | -2.15% | -4.124% | -4.645% | -4.731% | -4.551% | -4.358% | 0.7546% | 0.3286% | 1.817% | 2.114% | 1.896% | 1.112% | 2.833% | 0.5095% | 2.833% | 1.357% | 1.583% | 2.028% | 0.05574% | -0.3162% | -1.677% | -0.8517% | 2.887% | 3.715% | -1.221% | -0.5021% | 0.9505% | -0.7104% | 0.232% | -0.6806% | 0.3012% | -2.176% | -1.41% | -1.581% | -0.8294% | -1.216% | -3.805% | 4.802% | 2.433% | 4.259% | 3.617% | 1.747% | 3.435% | 1.68% | 3.42% | 3.751% | 3.355% | 2.411% | 2.565% | 1.667% | -0.7236% | 1.034% | -0.9842% | 0.4806% | 1.919% | 1.876% | 0.3943% | 2.301% | 1.465% | 3.348% | 2.769% | 2.484% | 2.905% | -0.9909% | 1.416% | 2.95% | 1.355% | 0.06194% | 3.431% | -2.638% | 2.499% | 3.454% | 3.699% | 2.388% | 1.851% | 2.602% | 2.224% | 2.071% | 2.335% | 1.49% | -1.246% | 1.422% | 1.188% | 2.456% | 1.754% | 2.543% | 2.328% | 3.363% | 3.257% | 2.049% | 2.833% | 0.3807% | 4.631% | 3.537% | 2.666% | 2.309% | 3.272% | 0.953% | 1.246% | 1.656% | 2.778% | 3.411% | 4.087% | 3.046% | 2.391% | 2.19% | 2.295% | 2.466% | 3.633% | 2.442% | 3.551% | 3.661% | 4.754% | 4.965% | 4.52% | 1.372% | 3.886% | 3.678% | 0.4128% | 3.507% | 3.723% | 3.827% | 4.124% | 4.972% | 2.897% | 4.262% | 4.262% | 4.325% | 3.723% | 4.262% | 5.23% | 3.161% | 3.061% | 3.767% | 5.059% | 3.864% | 4.779% | 2.934% | 3.153% | 4.228% | 3.473% | 3.879% | 4.57% | 4.84% | 5.238% | 4.527%
2025-06-09 | -6.091% | -8.333% | -5.43% | -5.844% | -5.828% | -8.21% | -3.639% | -7.783% | -5.271% | -4.413% | -4.874% | -5.526% | -4.032% | -4.365% | -3.285% | -3.444% | -5.188% | -4.669% | -5.255% | -4.349% | -0.9323% | -2.172% | -0.7415% | -1.091% | -1.266% | -0.9958% | -0.7574% | -1.536% | 0.1326% | -0.1217% | -0.8051% | -0.376% | -5.859% | -6.627% | -5.69% | -5.188% | -3.13% | -3.448% | -4.604% | -4.201% | -5.621% | -3.943% | -1.763% | -1.724% | -2.077% | 0.3617% | -0.2598% | -1.218% | -3.063% | -1.453% | -1.729% | -3.939% | -4.817% | -4.424% | -5.27% | -4.481% | -5.279% | -8.488% | -8.404% | -8.536% | -4% | -5.289% | -4.712% | 2.751% | 1.158% | 1.045% | 1.701% | 1.911% | 1.54% | 0.3544% | 2.512% | 2.056% | 0.5354% | -1.02% | 0.6585% | 1.957% | 0.67% | 3.764% | 4.09% | 3.96% | 1.911% | 3.93% | 5.046% | 10.12% | 3.714% | 4.553% | 2.865% | 1.337% | 2.07% | 2.765% | 2.461% | -0.6012% | 2.077% | 2.772% | 3.504% | 3.547% | 2.044% | 3.525% | 3.366% | 2.237% | 2.676% | 2.439% | 0.9332% | 1.752% | 7.898% | 1.65% | 3.04% | 1.759% | 2.034% | 3.714% | 3.084% | 3.496% | 3.902% | 1.767% | 3.142% | 4.604% | 3.75% | 4.944% | 5.451% | 5.755% | 1.173% | 4.228% | 3.675% | 5.4% | 5.205% | 4.278% | 2.562% | 4.358% | -1.072% | 2.903% | 1.592% | 1.375% | 2.056% | 2.07% | 1.23% | 2.787% | 2.691% | -0.6736% | -3.338% | -3.316% | -2.411% | -2.722% | -1.933% | -1.738% | -1.81% | -1.651% | -2.643% | -0.8286% | -0.7743% | -3.281% | -1.202% | -1.311% | 1.452% | -1.448% | -0.1523% | -1.557% | 0.9988% | -0.0365% | -2.194% | -2.715% | -1.846% | -5.452% | -4.467% | 1.494% | 1.491% | -2.183% | -1.284% | -0.1499% | -0.8318% | -1.331% | -1.561% | -1.331% | -1.649% | -0.5384% | -0.8556% | -1.022% | -0.2609% | 0.008659% | -0.03892% | -10.79% | -0.2887% | -4.885% | -0.4988% | -1.49% | -0.3957% | -2.885% | -2.489% | -1.379% | -3.195% | -1.641% | -4.416% | -1.855% | -3.496% | -2.56% | -2.417% | -3.033% | -1.601% | -4.171% | -0.8641% | -2.147% | -1.85% | -1.357% | 0.4159% | -1.892% | -0.3188% | 0.9815% | 0.6192% | -1.499% | 0.5219% | -21.2% | -1.378% | 1.461% | -1.426% | -1.044% | -0.3689% | 0.4906% | -0.4209% | -0.8904% | -2.812% | -5.48% | -1.675% | -3.796% | -4.398% | -4.016% | -4.255% | -6.636% | -3.273% | -3.445% | -2.296% | -1.168% | -2.46% | -3.066% | -1.695% | -3.984% | -0.01482% | -1.464% | -1.991% | -2.798% | -4.901% | -4.839% | -6.133% | -4.541% | -0.08893% | 0.6192% | -1.546% | -2.18% | -1.563% | -2.4% | -2.279% | -2.439% | -3.6% | -4.933% | -3.733% | -2.698% | -4.69% | -3.851% | -5.599% | 0.8587% | 1.341% | 2.767% | 1.863% | 2.25% | 2.472% | 0.9715% | 2.049% | 3.164% | 3.354% | 2.667% | 2.356% | 1.065% | -2.201% | -1.018% | -2.228% | -1.844% | -1.366% | -0.497% | -0.3832% | 0.5152% | 1.158% | 3.989% | 3.394% | 2.776% | 4.045% | -0.7684% | 2.189% | 2.34% | 0.3655% | -1.347% | 2.681% | 0.1083% | 2.237% | 2.475% | 2.395% | 2.711% | 2.445% | 3.28% | 3.408% | 2.92% | 3.357% | 2.968% | -3.146% | 2.307% | 2.339% | 2.856% | 2.212% | 2.974% | 2.785% | 2.673% | 2.861% | 2.029% | 3.262% | -1.536% | 3.552% | 1.756% | 1.043% | 0.4153% | 1.904% | -0.07419% | -3.662% | 0.9411% | 0.8497% | 1.681% | 1.96% | 1.325% | 0.1957% | 0.2742% | 0.5486% | 0.9878% | 2.118% | 0.4874% | 2.727% | 2.538% | 4.176% | 4.489% | 4.045% | 6.163% | 8.147% | 7.449% | 3.38% | 6.171% | 6.061% | 5.583% | 5.113% | 5.52% | 3.16% | 4.143% | 4.572% | 3.897% | 3.029% | 4.292% | 5.42% | 6.563% | 7.199% | 7.104% | 8.046% | 6.398% | 7.693% | 5.889% | 6.054% | 6.877% | 5.988% | 6.045% | 6.158% | 6.679% | 6.276% | 4.802%
2025-06-10 | -6.342% | -8.851% | -4.864% | -5.437% | -5.793% | -8.635% | -2.151% | -6.613% | -4.678% | -3.873% | -3.363% | -4.245% | -4.059% | -3.827% | -3.068% | -3.502% | -4.37% | -3.979% | -4.044% | -3.533% | -0.06543% | -1.768% | -0.8704% | -1.257% | -0.9168% | -1.056% | -1.242% | -2.96% | -0.01899% | -0.5298% | -1.49% | -1.582% | -6.195% | -7.108% | -6.163% | -5.576% | -3.653% | -4.061% | -5.251% | -5.022% | -6.474% | -4.438% | -1.875% | -2.407% | -2.885% | -0.202% | -1.192% | -2.107% | -4.268% | -3.255% | -2.585% | -4.712% | -5.591% | -5.902% | -7.263% | -6.73% | -6.034% | -9.858% | -9.342% | -10.11% | -5.05% | -6.751% | -5.611% | 3.969% | 2.862% | 3.267% | 3.954% | 3.2% | 3.064% | 1.501% | 4.413% | 3.609% | 2.065% | 0.1207% | 1.825% | 2.746% | 1.235% | 3.172% | 3.235% | 3.87% | 1.282% | 2.947% | 5.125% | 4.788% | 3.489% | 5.643% | 3.409% | 2.146% | 1.811% | 3.651% | 3.447% | 0.2035% | 2.714% | 3.503% | 4.667% | 3.813% | 1.632% | 4.265% | 3.877% | 4.124% | 4.353% | 3.891% | 1.891% | 2.84% | 6.923% | 3.623% | 5.012% | 2.481% | 3.433% | 5.238% | 5.005% | 5.301% | 5.793% | 2.414% | 2.255% | 2.093% | 2.46% | 2.453% | 4.575% | 4.201% | 2.34% | 2.453% | 1.972% | 3.623% | 3.581% | 3.327% | 1.282% | 3.475% | 0.9086% | 1.501% | 0.8733% | 1.332% | 1.177% | 2.149% | 0.8451% | 2.671% | 3.225% | 0.7887% | -1.527% | -0.6073% | 0.408% | 0.6125% | 0.2529% | 1.035% | 0.831% | 1.416% | -1.214% | 2.849% | 2.481% | 0.2545% | 1.572% | 0.8663% | 3.33% | -0.7131% | 0.2529% | -0.29% | 1.804% | 0.8522% | -1.355% | 0.2458% | -0.04325% | 0.4996% | -1.27% | 0.9541% | 1.698% | -0.7038% | -2.022% | -0.2689% | -0.8712% | -1.188% | -1.234% | -1.049% | -0.6241% | 0.8972% | 0.7041% | 0.09407% | 0.03229% | 0.2253% | 0.6578% | -0.5932% | 0.5059% | -3.497% | 0.457% | -0.6318% | 0.596% | 0.6346% | -0.9561% | 0.8817% | -1.304% | 0.2022% | -1.906% | 0.4725% | -0.2843% | 0.6732% | 0.1041% | -0.4554% | 0.8501% | -2.508% | 0.466% | -1.14% | -0.5236% | 0.1414% | 1.889% | -1.051% | 0.6295% | 1.278% | 0.1762% | -2.539% | -0.8472% | -21.57% | -2.334% | 0.2797% | -1.833% | -1.028% | -0.009588% | 0.2498% | 0.7455% | 0.7736% | -2.761% | -4.865% | -0.5754% | -2.989% | -4.906% | -3.887% | -2.801% | -5.094% | -3.435% | -3.042% | -1.188% | 0.1829% | -0.595% | -0.96% | 0.9687% | -1.227% | 0.5518% | 0.1588% | 0.223% | -0.001569% | -0.6851% | -1.38% | -1.777% | -1.609% | 0.223% | 3.447% | -1.461% | -2.297% | -1.509% | -3.03% | -1.477% | -2.625% | -0.2269% | -2.243% | -1.869% | -2.419% | -1.327% | -1.281% | -3.671% | -0.7962% | -0.3479% | 1.655% | 0.4689% | 0.9427% | 1.141% | -1.53% | -0.5925% | 3.272% | 3.279% | 1.822% | 2.266% | 0.5941% | -2.519% | -0.9314% | -2.98% | -1.051% | 0.5954% | 1.228% | -0.3119% | 1.699% | 1.486% | 3.021% | 2.503% | 2.581% | 2.951% | -0.7168% | 1.631% | 2.92% | 1.059% | 0.5806% | 3.554% | -0.5368% | 3.098% | 2.828% | 2.537% | 2.553% | 2.342% | 3.143% | 2.824% | 2.52% | 1.73% | 1.939% | -0.2765% | 1.768% | 2.078% | 2.334% | 1.985% | 3.055% | 2.923% | 2.72% | 2.82% | 1.904% | -2.167% | -1.197% | 3.769% | 2.53% | 2.08% | 1.278% | 1.483% | -0.8752% | 0.3688% | -0.4973% | 1.514% | 1.402% | 3.141% | 2.125% | 1.102% | 0.1168% | 0.9493% | 0.4299% | 1.889% | 0.1588% | -0.4105% | 0.05457% | 0.9848% | 1.041% | 1.097% | -0.8989% | 1.385% | 1.705% | -2.992% | 0.8271% | -0.6087% | 0.155% | -0.9142% | 1.056% | -5.985% | 0.5437% | 1.041% | 1.667% | 0.7117% | 0.8725% | 2.204% | 1.704% | 1.438% | 1.881% | 3.334% | 2.003% | 3.218% | 0.8732% | 0.3914% | 2.08% | 0.9928% | 1.482% | 1.843% | 1.739% | 2.019% | 0.9768%
2025-06-11 | -6.466% | -8.313% | -5.497% | -5.71% | -5.611% | -7.523% | -3.257% | -7.422% | -5.243% | -4.323% | -4.337% | -4.875% | -4.281% | -4.422% | -3.559% | -3.998% | -4.932% | -4.739% | -5.03% | -4.139% | -1.154% | -2.455% | -1.705% | -1.903% | -2.003% | -1.748% | -1.875% | -1.96% | -1.111% | -1.408% | -2.186% | -1.762% | -6.332% | -6.794% | -5.796% | -5.573% | -3.681% | -4.039% | -5.427% | -5.17% | -6.53% | -4.75% | -2.548% | -2.506% | -3.243% | -0.804% | -1.282% | -2.247% | -4.652% | -3.448% | -3.028% | -5.301% | -6.184% | -6.254% | -7.492% | -5.191% | -6.904% | -10.1% | -9.897% | -10.21% | -5.313% | -7.151% | -5.835% | 1.692% | 0.6159% | 1.369% | 1.956% | 0.9768% | 1.766% | -0.6151% | 2.833% | 0.8672% | -0.6731% | -2.474% | -0.4153% | 1.679% | 0.3382% | 1.473% | 1.235% | 2.143% | -0.8922% | 0.4443% | 3.142% | 2.535% | 0.3967% | 2.851% | 0.8098% | -0.7445% | 2.008% | 1.982% | 1.795% | -2.304% | 0.3065% | 1.363% | 2.388% | 0.7061% | -1.629% | 1.866% | 0.9832% | 1.679% | 1.975% | 1.363% | -0.2082% | 0.1067% | 4.193% | 0.6674% | 3.091% | 0.5643% | 1.724% | 3.368% | 3.033% | 2.904% | 3.959% | 7.581% | 0.6803% | 0.1776% | 0.371% | 1.963% | 3.323% | 3.265% | 1.956% | 1.376% | 0.9715% | 2.764% | 3.149% | 2.962% | 0.9252% | 3.142% | 1.686% | 1.305% | 0.5965% | 1.847% | 0.02939% | 1.873% | 0.2034% | 1.699% | 3.471% | 1.106% | -1.884% | 0.2098% | 1.363% | -0.2413% | 0.5901% | 2.15% | 1.305% | 2.736% | 1.119% | 3.539% | 2.76% | 0.8704% | 2.471% | 0.8672% | 3.542% | -1.311% | 0.0165% | 0.4676% | 2.659% | 1.196% | -0.1446% | 0.835% | 0.2872% | -2.967% | -0.6409% | -0.5007% | 0.8801% | 1.315% | 0.9798% | 2.342% | 2.025% | 1.876% | 1.587% | 2.017% | 2.264% | 3.26% | 3.352% | 2.653% | 2.384% | 2.646% | 3.253% | 1.849% | 2.764% | -1.508% | 3.104% | 2.088% | 3.373% | 3.154% | 2.081% | 3.027% | 0.6693% | 2.236% | -0.2766% | 2.145% | 0.6269% | 2.025% | 1.486% | 0.9964% | 2.76% | -1.248% | 2.709% | 0.6489% | 0.0137% | 0.8232% | 3.447% | -0.5435% | 1.104% | 3.148% | 0.8742% | -1.731% | 1.641% | -22.8% | -0.1839% | 1.868% | -0.403% | 1.257% | 2.775% | 0.1153% | 2.868% | 2.303% | -6.383% | -1.571% | 0.8713% | -2.119% | -4.09% | -1.874% | -3.274% | -6.344% | 0.1285% | -1.577% | 1.338% | 1.748% | 1.309% | 1.343% | 2.012% | 0.1564% | 2.423% | 1.243% | 1.624% | -0.06944% | -0.2904% | -0.2904% | -1.659% | -0.444% | 2.327% | 3.368% | 0.7442% | 0.5962% | 0.7442% | 0.3937% | 0.4657% | 0.31% | 0.4985% | -0.9396% | -0.1857% | 0.1913% | -0.8349% | 0.2053% | -5.198% | -0.7311% | -0.2254% | 1.939% | 1.25% | 0.5398% | 0.1896% | -0.1846% | 1.166% | 2.687% | 3.054% | 0.8678% | 2.174% | -0.08584% | -3.283% | 0.1892% | -3.76% | 0.104% | 2.091% | 2.336% | -0.5663% | 2.667% | 1.415% | 1.523% | 1.241% | 1.1% | 1.326% | -2.324% | -0.4672% | 1.756% | 0.1963% | -1.032% | 2.512% | -2.729% | 1.792% | 2.526% | 2.138% | 0.6259% | 0.9594% | 1.657% | 1.934% | 1.112% | 1.133% | 1.459% | -2.626% | 1.31% | 1.14% | 2.231% | 1.572% | 1.725% | 2.068% | 2.455% | 2.36% | 1.449% | 1.624% | -2.051% | 2.249% | 1.636% | 1.148% | 0.7707% | 1.374% | -0.8437% | 0.4775% | -0.2647% | 0.517% | 0.1944% | 2.174% | 0.3379% | 0.08658% | -0.2136% | 0.1424% | -0.6674% | 1.658% | 0.4437% | 0.5756% | 0.5976% | 2.049% | 1.814% | 0.7662% | -0.7791% | 2.404% | 1.629% | -1.358% | 1.266% | 1.769% | 1.699% | 1.706% | 2.467% | -0.793% | 1.807% | 1.888% | 2.216% | 1.062% | 1.66% | 2.672% | 0.7349% | 1.238% | 1.769% | 2.401% | 1.834% | 2.607% | 0.6682% | 0.4583% | 2.076% | 0.8541% | 1.602% | 2.235% | 1.558% | 2.298% | 0.5023%
2025-06-12 | -7.616% | -9.72% | -6.075% | -6.88% | -6.821% | -9.06% | -3.333% | -7.805% | -5.866% | -5.105% | -4.21% | -5.091% | -5.21% | -4.986% | -4.121% | -4.181% | -5.339% | -4.963% | -4.539% | -4.061% | -0.1235% | -1.958% | -1.168% | -1.749% | -0.8842% | -0.8992% | -1.347% | -1.675% | 0.1599% | -0.4517% | -1.511% | -1.526% | -7.895% | -8.024% | -7.004% | -6.8% | -4.664% | -4.633% | -6.761% | -6.093% | -7.85% | -6.12% | -3.904% | -4.16% | -5.067% | -2.496% | -3.126% | -3.858% | -5.082% | -3.644% | -3.879% | -6.153% | -7.195% | -6.705% | -7.457% | -5.041% | -6.517% | -9.95% | -9.466% | -10.13% | -4.628% | -6.776% | -6.983% | 2.915% | 1.189% | 1.211% | 1.726% | 1.597% | 1.347% | 0.8156% | 3.221% | 1.998% | 0.802% | -1.189% | 0.6798% | 1.662% | 0.1279% | 4.022% | 3.961% | 4.009% | 1.189% | 3.035% | 4.994% | 4.269% | 3.139% | 3.914% | 2.692% | 0.4417% | 2.066% | 3.18% | 3.01% | -0.747% | 2.181% | 2.752% | 4.111% | 3.173% | 1.401% | 3.37% | -0.02682% | 3.402% | 3.729% | 2.392% | 0.8097% | 1.835% | 5.911% | 2.568% | 3.744% | 1.59% | 2.453% | 3.785% | 3.234% | 3.819% | 4.085% | 1.002% | 2.467% | 2.929% | 3.139% | 4.308% | 4.002% | 5.408% | 3.391% | 2.066% | 1.904% | 4.29% | 2.799% | 1.651% | 0.5167% | 2.045% | 1.549% | 0.4963% | -0.7402% | -0.01323% | -0.6043% | 0.2314% | -1.25% | 0.4623% | -1.158% | -0.2306% | -2.149% | -1.127% | -0.3937% | -1.277% | -0.09476% | 1.176% | 0.211% | 1.726% | -0.1287% | 2.628% | 1.83% | -0.2201% | 1.281% | 0.7953% | 2.507% | -1.583% | -1.263% | -4.266% | 0.2653% | -1.46% | -3.424% | -0.8285% | -1.019% | -0.1899% | -1.786% | -1.022% | -0.1423% | 0.08528% | -1.6% | -0.5509% | -1.169% | -1.861% | -2.538% | -2.337% | -1.831% | -0.3203% | -0.1342% | -0.9379% | -0.4914% | -0.3947% | -0.3649% | -1.18% | 0.2068% | -3.068% | -0.01517% | 0.3941% | 0.3122% | 0.1188% | 0.4834% | 0.8852% | -1.042% | 0.5652% | -1.875% | 0.6545% | -0.4691% | 0.7438% | 0.2962% | -0.09442% | 1.218% | -2.51% | 0.4486% | -1.772% | -1.71% | -3.094% | 0.5659% | -2.206% | -0.4468% | 0.4845% | -0.608% | -3.031% | -0.846% | -27.49% | -4.579% | -0.05093% | -1.259% | -0.8677% | 1.018% | 0.9785% | 0.657% | -0.3105% | -3.507% | -3.554% | -1.969% | -4.106% | -6.679% | -6.663% | -4.784% | -7.66% | -1.696% | -2.391% | -0.2882% | 0.3995% | 0.4227% | 0.02678% | 1.435% | -1.048% | 0.9713% | 0.2063% | 0.4922% | -4.214% | -0.8563% | -2.026% | -1.945% | -1.497% | 0.6932% | 0.4536% | -1.038% | -1.762% | -0.7132% | -1.945% | -0.52% | -0.9078% | -1.04% | -2.615% | -0.4516% | -0.5693% | -1.224% | -1.497% | -3.601% | 3.278% | 1.093% | 3.155% | 2.274% | 1.96% | 1.767% | -1.869% | 0.2117% | 2.533% | 2.443% | 1.126% | 1.339% | 0.2736% | -1.974% | 0.4799% | -2.735% | -0.5509% | 0.3248% | 0.5481% | -1.105% | 1.243% | 0.4606% | 3.408% | 2.984% | 2.872% | 3.11% | -1.042% | 1.518% | 3.17% | 1.287% | 0.595% | 3.728% | -0.2374% | 3.043% | 3.37% | 3.437% | 2.851% | 2.898% | 3.726% | 4.049% | 3.701% | 3.805% | 3.417% | -2.734% | 2.768% | 2.924% | 2.461% | 2.14% | 3.67% | 2.992% | 3.11% | 3.023% | 1.664% | 3.73% | -0.03018% | 3.976% | 2.514% | 2.139% | 1.646% | 2.554% | 0.08759% | 1.521% | 1.037% | 1.574% | 2.061% | 3.427% | 2.338% | 1.661% | 1.543% | 1.97% | -2.387% | 2.578% | 1.628% | 2.895% | 4.008% | 5.353% | 5.476% | 5.322% | 2.639% | 5.451% | 4.729% | 1.778% | 4.95% | 4.95% | 4.685% | 4.597% | 5.612% | 2.978% | 4.449% | 4.704% | 4.98% | 3.959% | 4.719% | 5.832% | 3.685% | 4.192% | 4.84% | 5.801% | 4.872% | 5.855% | 3.39% | 3.946% | 5.244% | 4.348% | 5.082% | 5.545% | 4.789% | 5.53% | 3.745%
2025-06-13 | -7.252% | -9.114% | -5.965% | -6.29% | -5.868% | -8.077% | -3.325% | -7.361% | -4.878% | -4.229% | -4.472% | -4.959% | -4.927% | -4.018% | -3.693% | -3.352% | -4.775% | -3.801% | -4.635% | -3.612% | -0.7719% | -2.184% | -0.8368% | -1.032% | -2.362% | -2.297% | -1.811% | -1.681% | -2.005% | -2.59% | -3.044% | -2.297% | -7.247% | -7.252% | -6.227% | -6.585% | -4.672% | -4.348% | -6.387% | -5.714% | -7.004% | -5.032% | -2.467% | -3.345% | -3.267% | -1.286% | -1.255% | -2.343% | -4.093% | -2.542% | -5.512% | -5.048% | -5.883% | -5.984% | -7.132% | -4.278% | -5.626% | -9.199% | -9.225% | -9.659% | -5.625% | -6.888% | -6.109% | 2.414% | 0.8766% | 0.694% | 1.379% | 1.719% | 1.263% | 0.6031% | 2.614% | 1.431% | 0.2187% | -1.456% | -0.05486% | 1.69% | 0.1525% | 0.03385% | 1.571% | 1.061% | -1.467% | 0.669% | 2.496% | 1.984% | 1.387% | 2.726% | 1.374% | -0.3585% | 1.372% | 1.298% | 1.86% | -2.561% | -0.8976% | 0.3% | 0.6474% | 2.385% | 0.1243% | 1.579% | 1.172% | -0.1644% | 1.544% | 0.8027% | -0.5897% | -0.2101% | 6.938% | -0.2249% | 1.446% | 1.601% | 0.6031% | 3.471% | 2.274% | -1.755% | 2.209% | 0.06745% | -0.284% | 1.224% | 0.6918% | 1.845% | 2.185% | 2.17% | 1.594% | 1.86% | 1.335% | 2.571% | 3.604% | 3.331% | -0.9863% | 4.041% | 1.875% | 1.926% | 1.926% | 2.215% | 2.614% | 2.969% | 1.069% | 1.483% | 2.448% | 1.387% | -1.283% | 0.04125% | 0.3813% | 0.2408% | 1.328% | 2.067% | 0.8322% | 2.407% | 1.719% | 4.419% | 3.389% | 2.139% | 3.18% | 1.202% | 4.395% | 0.2926% | 0.2334% | 0.5735% | 1.586% | 0.7953% | -2.147% | 1.512% | 0.8027% | 2.259% | 0.6031% | -0.3512% | 0.9283% | 2.409% | -6.527% | -4.211% | -2.608% | -1.669% | -1.531% | -0.7783% | 0.02329% | 1.788% | 2.436% | 0.7925% | -4.81% | -3.183% | -0.07386% | -3.281% | -1.981% | -5.242% | -0.6811% | -1.661% | -0.4463% | 3.092% | 1.311% | 3.489% | -2.608% | 1.149% | -2.916% | 0.7763% | 1.594% | 2.825% | 1.437% | 1.505% | 3.63% | -2.732% | -1.175% | -4.025% | -5.091% | -4.758% | -3.091% | -5.209% | -4.538% | -3.915% | -5.13% | -7.422% | -5.825% | -5.8% | -6.329% | -1.777% | -2.126% | -0.796% | -0.5774% | -1.01% | -1.08% | -2.712% | -11.52% | -7.278% | -4.181% | -6.676% | -7.983% | -11.41% | -6.026% | -6.591% | 2.407% | 2.262% | 3.996% | 4.846% | 2.996% | 3.272% | 4.047% | 2.239% | 4.123% | 3.021% | 3.778% | 2.306% | 2.335% | 1.591% | 1.254% | 0.6778% | 3.114% | 3.248% | 1.306% | 0.4055% | 1.096% | -0.2911% | 0.8351% | -0.2511% | 1.27% | -1.356% | 0.2534% | -1.676% | 0.2213% | -0.9397% | -4.031% | -0.994% | -0.2281% | 1.903% | 0.8202% | 1.345% | 1.609% | 0.9929% | 1.355% | 3.111% | 3.87% | 2.583% | 3.241% | 1.42% | -1.622% | 0.9487% | -1.258% | 0.5857% | 2.277% | 2.127% | -0.2466% | 2.567% | 1.865% | 2.501% | 2.339% | 2.039% | 3.254% | -1.191% | 1.861% | 2.023% | 0.2338% | -0.2763% | 2.8% | -0.8384% | 1.95% | 2.258% | 2.406% | 2.874% | 2.16% | 3.187% | 2.803% | 2.428% | 2.347% | 1.876% | 1.384% | 2.306% | 1.957% | 2.867% | 2.225% | 2.193% | 2.469% | 2.266% | 2.585% | 1.853% | 1.752% | -0.7949% | 2.168% | 1.134% | 0.4936% | 0.05319% | 1.02% | -1.513% | 0.2133% | -0.9022% | 0.8099% | 1.525% | 2.503% | 1.711% | 0.2934% | -0.06692% | 0.4295% | -3.51% | 1.376% | 0.3222% | 0.6922% | 1.575% | 3.189% | 3.416% | 3.593% | 4.497% | 7.252% | 6.779% | 3.112% | 6.035% | 6.075% | 5.17% | 4.882% | 5.146% | 2.175% | 3.921% | 4.257% | 3.761% | 3.08% | 4.131% | 5.333% | 5.755% | 6.035% | 6.195% | 7.191% | 5.694% | 6.619% | 4.846% | 4.947% | 5.594% | 5.047% | 5.51% | 5.735% | 5.443% | 5.586% | 3.492%
2025-06-14 | -5.339% | -7.011% | -4.278% | -4.133% | -4.814% | -7.78% | -1.868% | -6.03% | -3.886% | -3.432% | -3.205% | -3.907% | -3.577% | -3.68% | -2.937% | -3.205% | -4.21% | -3.255% | -3.597% | -2.793% | -0.0504% | -0.9783% | -0.7515% | -0.7515% | -0.7103% | -0.6072% | -0.5041% | -0.6278% | 0.3002% | 0.07333% | -0.7928% | -0.4216% | -5.659% | -6.338% | -5.361% | -4.753% | -3.06% | -3.32% | -4.814% | -4.102% | -5.412% | -3.799% | -1.692% | -2.065% | -2.025% | 0.4683% | -0.04271% | -0.9082% | -3.4% | -1.93% | -5.45% | -4.327% | -5.163% | -5.041% | -6.404% | -3.922% | -4.603% | -8.301% | -8.058% | -8.915% | -4.443% | -5.75% | -4.751% | 3.346% | 2.445% | 2.914% | 3.149% | 3.619% | 3.375% | 1.562% | -3.106% | 3.59% | 2.172% | 0.8702% | 2.069% | 2.879% | 1.298% | 2.36% | 2.83% | 3.224% | 1.533% | 3.001% | 4.069% | 3.9% | 3.637% | 3.969% | 2.938% | 2.312% | 3.346% | 2.98% | 3.327% | 0.2749% | 2.773% | 2.933% | 3.891% | 3.825% | 3.115% | 3.093% | 3.252% | 2.918% | 3.095% | 3.666% | 1.131% | 3.797% | 8.738% | 3.356% | 4.858% | 3.215% | 3.797% | 5.46% | 4.868% | 5.431% | 5.113% | 2.81% | 2.163% | 3.525% | 2.999% | 3.741% | 4.361% | 4.023% | 3.327% | 2.905% | 1.897% | 3.458% | 3.882% | 3.75% | 1.336% | 3.619% | 2.106% | 2.106% | 1.28% | 2.031% | 2.106% | 3.064% | 1.59% | 3.243% | 4.165% | 2.848% | 0.8681% | 1.064% | 1.712% | 1.205% | 1.862% | 2.435% | 2.013% | 3.45% | -0.439% | 3.33% | 2.893% | 7.131% | 2.819% | 2.473% | 4.537% | 1.477% | 2.247% | 2.492% | 3.064% | -0.3075% | 1.843% | -2.533% | 1.674% | 1.984% | 2.031% | 2.857% | 3.872% | 2.368% | -1.316% | 0.5871% | -0.05073% | -3.713% | 0.1859% | 0.4431% | 0.4636% | 1.492% | 2.068% | 0.9265% | 0.7414% | 1.328% | 2.089% | 0.8098% | 1.593% | -2.139% | 1.863% | 1.595% | 0.155% | 1.554% | 1.42% | 1.575% | -0.1742% | 0.7311% | -1.347% | 0.5151% | 0.09329% | 1.143% | 0.5073% | 0.1833% | 1.652% | -0.9942% | 2.137% | -0.06299% | 0.4208% | 0.9379% | 2.394% | 0.3732% | 1.7% | 2.742% | 2.09% | -0.5728% | 0.8742% | 0.4076% | -1.134% | 2.047% | 0.6492% | 0.9946% | 2.138% | 2.691% | 2.228% | 1.344% | -1.202% | -1.589% | 0.4146% | -1.823% | -3.357% | -2.921% | -1.622% | -3.842% | -1.272% | -1.476% | 0.4391% | 0.5993% | 0.7596% | -0.0401% | 1.817% | -0.6607% | 1.155% | 0.05452% | 0.3323% | 0.2682% | -2.919% | -0.3555% | -3.387% | -0.7319% | 0.8771% | 1.593% | -0.501% | -1.068% | -0.2446% | -0.8947% | -0.5971% | -0.8947% | -0.8947% | -2.411% | -2.126% | -1.21% | -1.851% | -1.098% | -2.004% | 1.535% | -0.6867% | 1.365% | 0.8134% | 1.674% | 1.896% | 0.9527% | 1.714% | 2.632% | 2.814% | 1.858% | 2.418% | 1.966% | -1.148% | -0.07099% | -0.3991% | 0.06164% | 1.806% | 1.818% | 0.7336% | 2.419% | 1.719% | 0.6076% | 0.4122% | 0.1139% | 0.5254% | -1.841% | -0.74% | 0.6591% | -0.7605% | -1.728% | 1.379% | -0.2605% | 0.4225% | 0.9986% | 1.058% | 0.4425% | 0.3453% | 0.9446% | 1.328% | 1.085% | 1.416% | 0.951% | 0.1068% | 0.7446% | 0.311% | 1.601% | 0.8375% | 1.038% | 1.065% | 1.163% | 1.393% | 0.5506% | -7.744% | -10.57% | 1.296% | 0.06164% | -0.4979% | -0.8845% | -0.1191% | -2.079% | -16.85% | -3.661% | -1.345% | -3.108% | -0.3657% | -6.033% | -1.587% | -3.367% | -2.36% | -11.53% | 0.6279% | -1.43% | -2.445% | -12.73% | -5.949% | -5.992% | -11.7% | -2.014% | 0.2753% | -0.3148% | -3.214% | -0.8642% | -0.3657% | -0.2945% | -0.3962% | 0.5195% | -1.414% | 0.001105% | -0.3301% | 0.5093% | -0.7068% | -0.04163% | 1.166% | -1.02% | -0.3758% | 0.04129% | 0.3536% | 0.2623% | 0.4788% | -0.5243% | -0.9176% | 0.2041% | -0.4796% | 0.3109% | 0.5189% | 0.9732% | 1.016% | 0.375%
2025-06-15 | -5.306% | -6.978% | -3.971% | -4.183% | -4.959% | -8.227% | -1.536% | -6.088% | -4.394% | -3.371% | -2.7% | -3.777% | -3.212% | -3.724% | -2.7% | -2.983% | -4.025% | -3.17% | -3.124% | -2.506% | 0.723% | -0.4593% | -0.371% | -0.4063% | -0.0004592% | 0.1407% | 0.176% | -0.03575% | 0.9524% | 0.6877% | -0.124% | -0.3357% | -5.541% | -6.161% | -5.028% | -4.415% | -2.483% | -3.282% | -4.553% | -3.857% | -5.065% | -3.424% | -1.709% | -2.215% | -1.926% | 0.3673% | -0.335% | -9.115% | -2.672% | -1.417% | -1.331% | -3.688% | -4.561% | -4.611% | -5.687% | -3.162% | -4.669% | -7.826% | -7.667% | -8.336% | -3.618% | -5.179% | -4.729% | 4.037% | 3.274% | 3.337% | 3.989% | 4.222% | 3.788% | 2.438% | 4.712% | 4.134% | 2.59% | 0.8254% | 2.47% | 3.405% | 1.657% | 2.775% | 3.531% | 4.037% | 2.205% | 3.253% | 4.102% | 4.598% | 3.499% | 3.876% | 3.363% | 2.364% | 3.668% | 3.426% | 4.013% | -0.5361% | 2.59% | 2.864% | 4.166% | 3.659% | 2.051% | 2.848% | 3.507% | 3.615% | 2.926% | 4.118% | 0.9953% | 3.868% | 9.109% | 3.684% | 5.532% | 3.643% | 4.6% | 5.99% | 5.605% | 5.805% | 5.495% | 3.002% | 2.952% | 3.748% | 3.507% | 4.576% | 4.761% | 5.058% | 3.949% | 3.434% | 2.363% | 4.187% | 4.431% | 4.23% | 1.931% | 4.238% | 2.735% | 2.558% | 1.739% | 2.462% | 2.189% | 3.491% | 1.923% | 3.579% | 4.38% | 0.9026% | -1.321% | -2.537% | 0.5811% | -0.6888% | 0.1873% | 0.975% | 0.7097% | 1.755% | -0.8094% | 1.884% | 2.46% | 0.09449% | 2.599% | 1.562% | 4.544% | 0.9428% | 2.084% | 2.309% | 1.899% | 2.197% | 1.714% | -5.551% | 1.345% | -4.611% | 1.457% | 2.337% | 3.378% | 1.809% | -0.9403% | 1.023% | 0.2569% | -4.646% | -0.8258% | -0.5441% | -0.5089% | 0.2481% | 0.8467% | -0.3857% | 1.058% | 1.349% | 0.8291% | 0.1491% | 0.3596% | -3.989% | 0.1777% | -0.3769% | 0.4242% | 0.1777% | -0.1392% | 0.1865% | -1.926% | -0.9315% | -3.211% | -0.9667% | -1.011% | -0.09517% | -0.9693% | -1.108% | 0.2046% | -3.155% | 0.3701% | -1.399% | -0.6836% | -0.1426% | 1.59% | -1.218% | 1.026% | 2.458% | 1.368% | -1.346% | 0.424% | 0.3828% | -5.556% | -2.397% | -1.294% | -0.5858% | 0.4198% | 1.066% | 0.6532% | -0.01188% | -2.17% | -2.187% | -0.7637% | -3.253% | -5.695% | -4.223% | -3.612% | -6.064% | -2.152% | -2.925% | -1.034% | -1.244% | 0.1913% | -0.9057% | 1.224% | -1.393% | -0.9606% | -2.039% | -1.509% | -0.9514% | -2.159% | -1.985% | -2.934% | -4.597% | -1.262% | -1.454% | -2.268% | -3.37% | -2.487% | -2.987% | -2.752% | -3.169% | -3.021% | -4.797% | -3.021% | -2.899% | -3.735% | -3.117% | -3.648% | 1.687% | -0.3016% | 2.171% | 1.316% | 1.901% | 1.395% | 0.7943% | 1.527% | 2.709% | 3.101% | 2.322% | 3.009% | 1.24% | -3.415% | -0.6091% | -1.631% | -0.5781% | 1.837% | 1.928% | 0.4456% | 2.52% | 1.903% | 2.053% | 2.176% | 1.991% | 2.044% | -1.46% | 0.2481% | 2.528% | 0.5739% | -0.2536% | 2.678% | -1.243% | 1.841% | 2.044% | 2.062% | 1.452% | 1.6% | 2.211% | 2.22% | 2.154% | 2.604% | 2.048% | -0.5326% | 1.447% | 1.297% | 2.304% | 1.456% | 2.283% | 1.774% | 1.841% | 1.822% | 1.083% | 2.001% | -3.489% | 2.959% | 1.541% | 1.262% | 0.6701% | 1.018% | -1.002% | -10.25% | -1.363% | 0.1821% | 0.7398% | 2.02% | 0.4786% | -0.6358% | -0.01769% | -0.3311% | -2.299% | 1.943% | -0.1561% | -0.1195% | -6.445% | 1.462% | 1.297% | -4.855% | -3.474% | -0.5488% | -0.8796% | -3.796% | -1.167% | -1.367% | -0.9231% | -1.35% | 0.04326% | -1.724% | -0.3298% | 0.008433% | 0.4525% | -0.4823% | -0.4304% | 0.6392% | -1.03% | 0.3828% | 0.2957% | 0.5935% | 1.056% | 0.7049% | -0.1744% | -0.3572% | -4.841% | 0.2187% | 0.09071% | 0.5569% | 1.617% | 0.8769% | 0.2827%
2025-06-16 | -7.601% | -10.97% | -6.279% | -7.254% | -7.254% | -11.51% | -3.613% | -8.461% | -5.537% | -5.862% | -5.073% | -5.815% | -5.537% | -5.954% | -4.562% | -5.305% | -6.624% | -3.985% | -4.005% | -3.912% | -0.3378% | -1.359% | -1.591% | -2.241% | -0.5698% | -0.7555% | -0.1985% | -0.7091% | 0.6371% | 0.2193% | -0.8019% | -1.962% | -7.161% | -8.578% | -7.992% | -6.966% | -5.402% | -6.624% | -7.115% | -5.793% | -8.136% | -5.205% | -3.033% | -4.462% | -3.342% | -0.5969% | -0.6154% | -1.584% | -4.082% | -2.467% | -2.07% | -5.224% | -5.702% | -5.701% | -6.524% | -5.281% | -4.59% | -9.164% | -8.481% | -9.837% | -6.419% | -5.797% | -6.293% | 2.926% | 1.488% | 2.313% | 1.763% | 3.37% | 2.197% | 1.298% | 3.095% | 3.899% | 1.657% | 1.323% | 1.657% | 1.857% | -0.1985% | 1.319% | 2.122% | 2.376% | 1.234% | 2.832% | 2.736% | 2.874% | 3.624% | 2.83% | 2.587% | 2.175% | 2.82% | 1.657% | 2.186% | -1.937% | 0.09271% | 0.7904% | 1.425% | 2.799% | 2.356% | 2.249% | 1.996% | 0.1552% | 1.371% | 2.292% | -0.416% | 3.349% | 7.155% | 2.968% | 3.645% | 2.736% | 1.488% | 4.533% | 4.025% | 5.019% | 3.651% | 2.741% | 1.425% | 4.131% | 3.116% | 2.968% | 3.814% | 2.588% | 2.482% | 2.736% | 1.194% | 2.432% | 3.645% | 3.433% | 0.7482% | 3.412% | 1.467% | 1.742% | 1.044% | 1.869% | 2.609% | 3.306% | 1.53% | 3.095% | 4.156% | 3.666% | 2.57% | -1.704% | 1.425% | 2.799% | 3.01% | 2.503% | 1.826% | 3.751% | 3.137% | 3.493% | 3.136% | 1.504% | 2.487% | 2.968% | 4.786% | 2.778% | 2.651% | 2.545% | 2.82% | 2.884% | 2.884% | -1.239% | 1.996% | 2.44% | 2.841% | 3.966% | 4.85% | 2.388% | -2.023% | 0.8488% | -1.397% | -5.195% | -0.309% | -0.4943% | -0.4016% | 1.428% | 2.91% | 1.636% | 0.9878% | 2.076% | 3.28% | 0.931% | 2.771% | -0.1985% | 2.655% | 3.072% | 3.095% | 1.798% | 2.701% | 2.47% | 1.196% | 1.567% | -0.749% | 0.5478% | 1.405% | 1.821% | 0.4447% | 0.4447% | 3.387% | -0.6308% | 2.012% | 0.6876% | 1.034% | 1.628% | 2.551% | 1.642% | 2.757% | 3.367% | 2.966% | 0.9347% | 1.022% | 0.7025% | -0.359% | 7.274% | 2.223% | 2.323% | 1.722% | 3.24% | 2.367% | 1% | 0.09846% | -0.9309% | 1.022% | -1.153% | -3.601% | -3.665% | 0.6152% | 0.2053% | -1.077% | -0.07097% | 1.337% | 0.7117% | 1.193% | -0.8778% | 2.155% | 0.4964% | 2.034% | 0.8079% | 0.9041% | 0.9281% | -9.031% | -0.8778% | -7.634% | -5.138% | 4.126% | 5.569% | 2.732% | 0.8628% | 1.145% | -0.9694% | 0.6636% | -0.03037% | 0.5651% | -1.519% | -4.909% | 0.8399% | -1.725% | -0.2823% | -0.007466% | 1.372% | 0.128% | 1.628% | 0.9177% | 2.701% | 3.265% | 2.098% | 2.301% | 2.574% | 2.569% | 1.983% | 2.487% | 3.323% | 0.6917% | -0.04021% | 1.775% | 0.1586% | 1.775% | 4.207% | 1.23% | 2.823% | 1.94% | 1.335% | 0.5246% | -1.444% | -1.328% | -2.648% | -0.5174% | 0.7794% | -0.9111% | -2.185% | 2.192% | 1.425% | -0.1006% | 1.312% | 2.584% | 1.028% | -1.452% | -0.5355% | 0.7935% | 0.1242% | 0.6121% | 0.7051% | 1.232% | 0.5657% | -0.5032% | 0.8677% | 1.216% | -0.1384% | 0.3101% | 1.428% | 1.15% | -4.88% | 1.217% | -1.405% | 2.536% | 1.115% | -0.05327% | -0.7403% | 1.174% | -1.556% | -9.077% | 1.306% | -2.15% | 0.8319% | 4.459% | 2.489% | 2.489% | 0.4735% | 1.435% | -1.45% | 3.566% | 0.4712% | 1.217% | -14.17% | 3.405% | 4.126% | -5.829% | -2.687% | -1.038% | 0.4048% | -4.68% | -2.046% | -0.9236% | -1.931% | -1.702% | 0.4277% | -2.985% | -0.6831% | 0.03834% | 0.3819% | -1.911% | -1.525% | 1.193% | -1.142% | -4.771% | -2.733% | -1.188% | -1.164% | -2.206% | -1.317% | -2.174% | -7.016% | -2.126% | 0.4952% | -1.025% | 0.5433% | 1.313% | -1.405%
2025-06-17 | -6.581% | -9.013% | -4.886% | -5.876% | -6.678% | -11.14% | -2.13% | -7.338% | -4.792% | -5.405% | -3.754% | -4.839% | -5.169% | -5.782% | -4.273% | -4.509% | -5.837% | -3.057% | -2.811% | -2.811% | 0.9142% | -0.07612% | -1.396% | -1.302% | 0.06535% | 0.254% | 1.008% | 0.3954% | 2.14% | 1.103% | 0.4426% | -0.9721% | -7.48% | -8.865% | -7.624% | -6.879% | -5.092% | -6.383% | -7.338% | -5.34% | -7.621% | -4.855% | -3.048% | -4.538% | -3.491% | -0.8206% | -0.6232% | -1.946% | -4.158% | -1.961% | -2.478% | -5.48% | -6.092% | -5.235% | -6.158% | -4.78% | -3.535% | -8.202% | -7.476% | -8.795% | -5.216% | -5.739% | -6.676% | 4.946% | 3.937% | 4.799% | 4.409% | 2.39% | 4.163% | 3.185% | 5.118% | 5.72% | 3.421% | 2.932% | 3.185% | 3.339% | 1.273% | 3.292% | 4.001% | 4.195% | 2.927% | 5.04% | 4.86% | 4.866% | 5.913% | 10.73% | 5.248% | -3.711% | 4.667% | 5.376% | 3.701% | 2.433% | 4.366% | 5.505% | 5.977% | 7.309% | 7.004% | 6.493% | 6.235% | 3.991% | 5.113% | 6.085% | 3.28% | 6.944% | 11.41% | 5.784% | 6.987% | 4.925% | 4.839% | 7.438% | 7.03% | 8.061% | 6.825% | 5.967% | 2.906% | 5.741% | 4.624% | 4.71% | 5.333% | 4.409% | 3.937% | 3.615% | 2.082% | 3.676% | 4.109% | 3.636% | 1.23% | 3.615% | 2.047% | 1.918% | 0.758% | 1.467% | 2.304% | 2.584% | 1.188% | 2.841% | 3.586% | 1.66% | 0.6213% | -0.5737% | 0.1351% | 0.221% | 0.7365% | 0.7794% | 0.5646% | 1.896% | 1.574% | 1.341% | 1.356% | -0.5005% | 1.076% | 1.767% | 3.461% | 1.338% | 1.81% | 1.445% | 2.133% | 1.789% | 1.746% | -0.03677% | 0.6076% | 0.4787% | 0.9513% | 3.599% | 4.238% | 0.8468% | -4.89% | -1.714% | -3.855% | -3.996% | -2.937% | -2.796% | -2.679% | -1.008% | 0.403% | -1.479% | -1.855% | -0.4909% | 0.803% | -1.666% | -0.01649% | -1.062% | 0.1913% | 0.3325% | 0.5442% | -0.632% | 0.02664% | -0.2557% | -0.3262% | -0.7497% | -1.973% | -0.9143% | -0.7732% | -0.3498% | -1.864% | -1.913% | 0.7053% | -2.941% | -0.7116% | -1.085% | -1.402% | -1.157% | -0.4062% | -1.163% | 0.01185% | 0.7859% | 0.3093% | -1.794% | -1.772% | -1.933% | -3.217% | 0.7139% | -0.6741% | -0.67% | -0.9388% | -2.443% | -0.5852% | 3.174% | -2.343% | -2.242% | -0.3399% | -2.319% | -5.066% | -4.667% | -1.474% | -1.484% | -2.327% | -1.505% | -0.2303% | -1.183% | -0.5479% | -2.189% | 0.2094% | -1.259% | 0.3804% | -1.256% | -0.9143% | -1.452% | -6.4% | -2.469% | -4.958% | -6.4% | 1.822% | 1.626% | 0.01398% | -1.957% | -0.8899% | -3.027% | -1.403% | -2.748% | -1.468% | -3.399% | -1.422% | -3.19% | -4.562% | -2.562% | -1.887% | 1.16% | -0.3654% | 1.414% | 0.6059% | 2.546% | 2.929% | 1.376% | 1.903% | 1.959% | 2.242% | 2.327% | 2.226% | 2.388% | 0.1505% | -0.6654% | 1.006% | -0.837% | 0.1877% | 0.242% | 0.4367% | 1.575% | 1.471% | 2.356% | 2.309% | 0.07369% | 0.803% | -1.15% | 0.8971% | 1.72% | 0.09722% | -1.032% | 2.567% | 1.853% | 0.5912% | 1.415% | 2.657% | 2.681% | -0.011% | 0.996% | 2.322% | 2.186% | 2.445% | 2.091% | -1.32% | 1.312% | 0.4388% | 1.619% | 1.808% | 0.9248% | 0.6985% | 1.556% | 1.15% | -4.679% | -2.551% | -3.175% | 3.669% | 1.836% | 0.8818% | 0.1606% | 1.323% | -1.742% | -3.725% | 0.5159% | -1.378% | 1.358% | 4.814% | 0.3467% | 2.301% | 1.44% | -0.1186% | -3.888% | 4.319% | 0.698% | -0.6945% | -8.097% | 2.359% | 2.115% | -2.649% | -2.538% | -0.933% | 0.3699% | -4.237% | -1.98% | -1.003% | -1.119% | -1.235% | 0.8818% | -2.585% | -0.05931% | -0.328% | 0.9283% | -1.279% | -0.499% | 1.553% | -1.394% | -1.933% | -1.282% | -1.33% | -0.328% | -0.3746% | -0.639% | -1.672% | -1.189% | -1.11% | 1.602% | -0.5338% | 1.7% | 1.773% | 0.3071%
2025-06-18 | -9.058% | -10.29% | -7.098% | -7.153% | -7.08% | -10.55% | -3.862% | -8.108% | -6.377% | -5.242% | -4.521% | -5.44% | -5.332% | -5.26% | -4.323% | -4.341% | -5.378% | -3.917% | -4.341% | -3.692% | -0.3931% | -1.547% | -1.276% | -1.276% | -0.6995% | -0.7536% | -0.7536% | -0.8077% | 1.572% | 0.8687% | -0.05062% | -0.06864% | -8.414% | -8.527% | -7.066% | -6.706% | -4.562% | -4.619% | -7.549% | -5.795% | -7.819% | -7.135% | -5.768% | -5.401% | -5.001% | -3.536% | -4.142% | -5.083% | -7.082% | -3.532% | -3.833% | -5.328% | -5.737% | -5.501% | -6.816% | -4.911% | -6.442% | -9.616% | -10.11% | -9.708% | -3.277% | -4.941% | -7.043% | 2.472% | 0.8296% | 2.47% | -0.3609% | -1.847% | -2.073% | -0.9685% | 0.8952% | -1.322% | -2.11% | -0.8307% | -3.046% | -1.583% | -0.7931% | 5.271% | 4.926% | 6.24% | 1.1% | 3.426% | 5.189% | 4.477% | 3.309% | 3.602% | 2.537% | 0.9124% | 3.662% | 3.153% | 1.987% | -2.709% | -0.3609% | 1.774% | 2.701% | 1.577% | 0.1429% | 3.506% | 1.593% | 0.4258% | 2.074% | 1.265% | 0.2209% | 0.6489% | 6.954% | -0.1721% | 1.404% | -2.389% | -0.9028% | 1.002% | 1.642% | 0.9938% | 4.632% | 1.293% | 2.053% | 3.375% | 3.424% | 5.197% | 8.457% | 7.184% | 2.751% | 1.963% | 3.044% | 5.627% | 4.45% | 3.744% | 3.711% | 5.509% | 3.744% | 3.153% | 1.667% | 3.703% | 1.593% | 2.012% | -0.4266% | -0.2296% | -0.09783% | -0.3856% | -3.311% | -2.684% | -1.478% | -1.223% | -1.395% | 0.5176% | -1.74% | 0.9855% | -2.627% | 2.992% | 0.5781% | 0.9408% | 2.433% | -1.289% | 1.287% | -1.116% | -1.026% | 1.823% | 0.3534% | -2.249% | -1.609% | 1.289% | 1.634% | 1.544% | 3.153% | -1.129% | 0.02495% | 0.5888% | -4.045% | -2.336% | -2.525% | -2.912% | -1.5% | -1.464% | -1.581% | -1.042% | -0.3582% | -0.7718% | -1.797% | -0.9966% | 0.3432% | -0.01199% | 1.604% | -1.342% | 0.3342% | 0.1094% | 0.7748% | 0.1184% | 0.4781% | 0.7119% | 0.4061% | 1.045% | 0.1094% | 1.377% | -2.759% | 0.7478% | 1.168% | 0.9983% | 0.5073% | -1.594% | 1.363% | 1.261% | -1.679% | -1.967% | -0.2898% | -1.515% | -0.8631% | -0.2554% | -1.44% | -4.107% | -4.939% | -2.236% | -2.974% | -3.543% | -1.78% | -0.4945% | 1.252% | 0.8139% | 1.725% | 0.9643% | -4.192% | -4.361% | 0.8138% | -2.664% | -4.829% | -3.218% | -6.137% | -7.849% | -2.257% | -2.613% | 0.7288% | 0.1219% | 1.13% | 0.281% | 2.092% | -0.4304% | -0.1956% | -0.4571% | 0.346% | 1.121% | -0.1636% | -0.6439% | -0.7951% | -4.859% | 8.134% | 7.947% | -2.586% | -3.89% | -2.259% | -3.339% | 1.41% | -2.174% | -0.9018% | -1.391% | -0.8573% | -0.4927% | -0.9196% | -0.9907% | -0.3237% | 0.3748% | -1.62% | 3.091% | 1.758% | -1.896% | 2.259% | 1.992% | 0.9748% | 5.171% | 6.55% | 4.35% | 5.536% | 1.963% | -1.098% | 1.236% | -1.106% | 0.1576% | 3.434% | 3.62% | 1.646% | 4.428% | 4.526% | 4.048% | 3.994% | 3.886% | 4.812% | 2.42% | 3.994% | 3.733% | 2.169% | 1.602% | 3.769% | 1.043% | 3.122% | 3.023% | 4.048% | 6.39% | 6.191% | 6.399% | 6.445% | 6.352% | 6.117% | 5.558% | -8.492% | 5.08% | 4.574% | 4.674% | 4.692% | 6.037% | 4.89% | 3.427% | 5.049% | 3.028% | 4.025% | -0.4409% | 4.671% | 1.606% | 2.086% | 1.473% | 2.613% | 0.919% | 0.5834% | -0.6863% | 1.317% | 2.055% | 2.238% | 1.597% | 0.2721% | 1.215% | 1.651% | 0.281% | 1.494% | 1.233% | 0.4954% | -1.372% | 1.579% | 2.718% | 2.017% | 0.6635% | 2.495% | 1.9% | -0.9107% | 0.868% | 1.286% | 1.081% | 0.9391% | 1.259% | -1.115% | 1.037% | 1.224% | 1.197% | 2.403% | 1.382% | 2.382% | 1.054% | 2.38% | 2.38% | 7.667% | 0.8417% | 1.544% | 0.7059% | 2.036% | 1.161% | 2.045% | 1.756% | 2.443% | 1.933% | 2.624% | 1.065%
2025-06-19 | -6.322% | -7.867% | -4.937% | -5.113% | -5.945% | -9.64% | -2.664% | -7.019% | -4.959% | -4.609% | -4.083% | -5.091% | -4.477% | -5.156% | -3.995% | -4.28% | -5.284% | -4.408% | -4.587% | -3.886% | -0.7746% | -1.958% | -1.87% | -1.87% | -1.76% | -1.454% | -1.388% | -1.695% | -0.5336% | -0.8403% | -1.629% | -1.804% | -6.12% | -7.014% | -6.161% | -5.423% | -3.762% | -4.454% | -5.31% | -4.5% | -5.507% | -4.041% | -1.869% | -1.888% | -2.227% | 0.4449% | -0.758% | -2.143% | -4.738% | -3.13% | -2.576% | -5.062% | -6.042% | -6.116% | -7.449% | -5.024% | -5.758% | -9.246% | -13.98% | -10.14% | -5.397% | -6.955% | -5.862% | 2.207% | 1.449% | 2.255% | 2.477% | 2.716% | 2.746% | 0.5306% | 3.145% | 2.536% | 1.039% | -0.1411% | 1.089% | 1.939% | 0.614% | -1.256% | 1.618% | 2.107% | 0.2811% | 1.85% | 2.956% | 2.575% | 2.277% | 2.763% | 1.814% | 1.237% | 2.536% | 0.2312% | 2.017% | 0.1414% | 2.187% | 3.155% | 3.884% | 3.415% | 2.798% | 3.385% | 2.975% | 2.294% | 2.878% | 3.105% | 1.071% | 3.405% | 6.568% | 2.796% | 4.393% | 2.427% | 3.055% | 4.742% | 4.153% | 1.848% | 4.76% | 2.377% | 0.6902% | 2.337% | 1.419% | 2.496% | 3.275% | 2.936% | 1.878% | 1.528% | 0.6036% | 2.189% | 2.706% | 2.876% | 0.1913% | 2.786% | 0.8599% | 0.9297% | 0.09147% | 1.289% | 1.209% | 2.327% | 0.79% | 2.516% | 3.66% | 4.363% | 2.174% | 2.307% | 3.195% | 2.646% | 3.375% | 3.933% | 3.175% | 4.472% | 3.454% | 4.704% | 3.686% | 2.513% | 4.008% | 3.484% | 5.121% | 1.718% | 2.087% | 2.536% | 2.866% | 1.818% | 1.229% | 1.389% | 1.429% | 2.147% | 3.574% | 1.21% | 3.734% | 2.836% | 0.7819% | 2.607% | 2.05% | 2.192% | 1.908% | 2.225% | 2.389% | 3.307% | 3.886% | 2.782% | 3.044% | 3.361% | 3.831% | 3.308% | 4.394% | 1.668% | 3.624% | 3.296% | 3.864% | 3.318% | 3.121% | 3.088% | 2.946% | 3.197% | 2.29% | 3.208% | 1.93% | 2.651% | 2.665% | 2.206% | 3.044% | 0.9852% | 4.294% | 4.306% | 2.821% | 3.176% | 5.166% | 2.235% | 3.788% | 5.282% | 4.134% | 1.562% | 2.934% | 3.252% | 1.972% | 4.374% | 2.661% | 4.023% | 4.567% | 5.073% | 5.053% | 4.798% | 1.554% | 1.308% | 5.641% | 2.735% | 0.08498% | 1.824% | -34.56% | -92.09% | -1.235% | -1.338% | 0.663% | 1.128% | 0.4133% | -0.5201% | 1.696% | -0.5634% | 1.968% | 1.026% | 1.072% | 0.1863% | -2.725% | 0.6257% | -2.704% | -3.849% | 1.968% | 0.5608% | 0.7992% | 0.009542% | 0.9127% | 0.7662% | 0.9013% | 1.004% | 0.6581% | 0.55% | -0.6931% | 1.707% | -0.2499% | 0.8419% | 1.761% | 1.459% | -0.9611% | 1.054% | 0.3486% | 1.004% | 1.27% | 0.5014% | -1.455% | 1.789% | 2.081% | 1.311% | 1.727% | 1.111% | -1.42% | -0.4002% | -0.9753% | -0.6498% | 1.343% | 1.254% | -0.04122% | 1.983% | 0.9426% | 0.6836% | 0.6508% | -0.0815% | 0.2027% | -1.929% | -1.109% | 0.5087% | -0.9668% | -1.841% | 0.9022% | -0.8965% | -0.1034% | 0.3775% | 0.8519% | 0.4388% | 0.09447% | 0.6139% | 0.944% | 1.488% | 1.126% | 0.1718% | 3.607% | -0.1463% | -0.574% | 0.7311% | -0.1572% | 0.6432% | 0.01825% | 0.5743% | 0.806% | -0.1236% | -2.413% | -5.302% | 1.391% | -0.3904% | -1.028% | -1.471% | -0.4908% | -2.187% | -5.73% | -1.833% | -1.516% | -0.438% | 0.2906% | -1.244% | -1.871% | -1.309% | -1.396% | -5.752% | 0.2466% | -1.494% | -0.3926% | -10.47% | -0.9147% | -0.1202% | -7.952% | -1.212% | 0.8959% | 0.7662% | -2.758% | -0.1202% | -0.3364% | 0.06359% | -0.5958% | 0.4311% | -1.461% | -0.1202% | 0.5608% | 0.08521% | -0.3591% | 0.1068% | 1.196% | -0.4813% | 0.5933% | 1.026% | 0.9354% | 1.097% | 0.9824% | 0.07587% | 0.01603% | 0.6041% | 0.4587% | 1.367% | 1.015% | 1.571% | 1.265% | 0.7878%
2025-06-20 | -2.171% | -3.743% | -1.525% | -0.9321% | -2.382% | -5.97% | 0.6746% | -3.129% | -1.569% | -0.4488% | -0.7344% | -1.415% | -1.064% | -1.415% | -0.6685% | -1.328% | -0.8755% | -0.4592% | -1.064% | -0.2071% | 2.21% | 1.221% | 1.726% | 1.221% | 1.704% | 1.682% | 2.034% | 2.188% | 3.001% | 2.759% | 1.946% | 2.166% | -5.348% | -5.085% | -2.957% | -2.518% | -0.3667% | -1.13% | -3.876% | -1.87% | -4.557% | -3.789% | -2.797% | -3.115% | -2.161% | -0.9906% | -1.234% | -2.528% | -4.609% | -1.701% | -1.385% | -3.93% | -4.562% | -4.068% | -4.863% | -2.968% | -3.853% | -6.71% | -6.462% | -6.823% | -1.394% | -2.349% | -4.787% | 5.29% | 3.688% | 5.758% | 4.389% | 3.548% | 3.619% | 2.197% | 4.979% | 3.418% | 2.628% | 0.5561% | 2.638% | 3.128% | 2.511% | -3.287% | 1.327% | 5.86% | 2.628% | 4.787% | 6.44% | 5.556% | 5.85% | 6.34% | 5.294% | 4.671% | 7.001% | 4.969% | 4.929% | 0.636% | 3.908% | 5.189% | 6.12% | 6.2% | 5.116% | 6.44% | 6% | 4.865% | 5.001% | 5.98% | 3.932% | 5.59% | 9.082% | 4.539% | 6.36% | 3.388% | 4.799% | 6.51% | 6.56% | 6.911% | 4.345% | 5.42% | 3.248% | 2.517% | 4.269% | 5.8% | 6.701% | 6.601% | 4.639% | 3.949% | 4.028% | 5.765% | 5.77% | 4.739% | 4.089% | 5.5% | 4.439% | 3.788% | 1.817% | 3.308% | 1.887% | 1.927% | 0.4459% | 1.477% | -1.925% | -2.446% | -4.165% | -3.517% | -1.386% | -4.518% | -3.527% | -1.075% | -1.285% | -1.355% | -1.255% | -0.8265% | -1.025% | -2.72% | -0.1506% | -0.9352% | 1.309% | -2.176% | -0.4348% | -0.4148% | -1.706% | -0.6149% | -0.05451% | -3.727% | -1.195% | -1.966% | -0.8151% | 0.586% | 1.447% | -5.524% | -7.536% | -6.078% | -6.703% | -6.056% | -5.914% | -5.53% | -5.289% | -4.631% | -4.138% | -5.41% | -6.1% | -5.399% | -4.368% | -5.422% | -4.861% | -7.229% | -4.949% | -5.947% | -4.587% | -4.872% | -5.267% | -4.938% | -6.001% | -5.212% | -6.495% | -5.114% | -4.324% | -4.62% | -5.03% | -4.639% | -4.639% | -6.943% | -4.151% | -4.571% | -5.308% | -4.973% | -3.41% | -5.471% | -4.092% | -3.187% | -3.479% | -5.31% | -5.828% | -3.858% | -4.686% | 0.821% | -4.807% | -4.184% | -4.048% | -3.431% | -3.826% | -0.2158% | -8.696% | -5.817% | -2.663% | -4.411% | -7.387% | -5.819% | -5.591% | -2.797% | -5.165% | -5.683% | -3.171% | -5.3% | -1.76% | -3.826% | -1.578% | -5.766% | -4.389% | -5.71% | -4.492% | -5.949% | -8.747% | -5.495% | -9.528% | -6.883% | -4.993% | -5.391% | -8.111% | -7.435% | -6.051% | -6.568% | -6.051% | -6.731% | -6.536% | -7.067% | -8.899% | -7.977% | -9.018% | -7.511% | -7.934% | 4.913% | 0.766% | 4.707% | 3.392% | 4.39% | 3.939% | 0.3801% | 2.137% | 4.127% | 4.865% | 3.984% | 4.365% | 2.598% | -0.1339% | 1.132% | 0.4927% | 0.2015% | 2.655% | 3.098% | 1.361% | 4.022% | 3.361% | 3.754% | 3.94% | 3.063% | 3.074% | 0.5093% | 1.035% | 3.666% | 2.23% | 0.9038% | 3.973% | 1.697% | 2.833% | 3.271% | 4.579% | 2.773% | 3.164% | 3.317% | 3.758% | 4.108% | 3.888% | 2.942% | -1.189% | 2.722% | 2.579% | 3.734% | 2.744% | 4.553% | 2.678% | 3.151% | 3.475% | 2.381% | -1.976% | -4.34% | 5.374% | 3.763% | 2.635% | 2.342% | 3.659% | 2.62% | -4.053% | 0.2153% | 3.134% | 2.11% | 4.5% | -0.1291% | 2.429% | 2.95% | 0.7706% | -2.297% | 4.632% | 3.942% | 2.258% | -4.833% | 2.645% | 3.92% | -2.671% | 1.345% | 4.348% | 3.893% | 0.8465% | 3.21% | 2.581% | 4.012% | 2.418% | 4.283% | 1.66% | 4.068% | 4.375% | 5.183% | 5.639% | 5.126% | 6.697% | 2.968% | 5.161% | 5.324% | 5.456% | 4.851% | 5.02% | 4.054% | 5.001% | 5.204% | 5.559% | 5.866% | 6.61% | 7.095% | 6.435% | 5.661%
2025-06-21 | -5.871% | -7.548% | -5.94% | -5.396% | -5.517% | -9.02% | -3.946% | -7.513% | -5.336% | -4.146% | -5.557% | -5.92% | -4.227% | -4.408% | -3.924% | -4.509% | -5.192% | -5.022% | -6.061% | -5.033% | -2.795% | -3.4% | -2.533% | -2.694% | -3.501% | -2.997% | -2.714% | -2.553% | -1.585% | -2.13% | -2.694% | -2.674% | -7.009% | -7.484% | -6.041% | -5.426% | -3.834% | -4.831% | -5.92% | -4.916% | -6.082% | -5.196% | -3.968% | -2.976% | -2.918% | -1.513% | -1.55% | -2.805% | -5.725% | -3.625% | -2.887% | -5.255% | -6.329% | -6.288% | -8.171% | -5.721% | -7.08% | -9.927% | -9.462% | -10.66% | -5.719% | -6.869% | -5.931% | -0.2353% | -1.521% | -0.2654% | -1.08% | -1.448% | -1.929% | -2.43% | 0.1596% | -0.8047% | -1.246% | -3.925% | -1.181% | -1.452% | -0.5493% | 1.464% | 1.418% | 2.143% | -1.236% | 0.8797% | 2.162% | 1.323% | 0.7014% | 0.8333% | 0.01722% | -1.322% | 0.7106% | 0.1779% | -0.318% | -7.289% | -4.726% | -3.202% | -2.449% | -1.631% | -2.767% | -0.7129% | -0.8874% | -3.583% | -2.758% | -1.484% | -2.776% | -2.21% | 2.41% | -3.863% | -1.448% | -3.055% | -3.156% | -0.4833% | 0.05855% | -0.08839% | -3.629% | -0.7605% | -0.5384% | -1.466% | 1.023% | 2.162% | 3.668% | 3.558% | 0.9402% | 0.9769% | 0.6605% | 2.302% | 2.327% | 2.116% | 0.6371% | 2.235% | 0.07692% | 1.436% | -0.2721% | 0.8392% | 0.3249% | 1.142% | -0.3455% | 1.62% | 1.621% | 2.456% | 0.4608% | 1.849% | 1.308% | 1.124% | 1.216% | 2.575% | 1.611% | 2.676% | 1.813% | 2.773% | 1.839% | 0.7181% | 1.971% | 1.62% | 2.939% | -0.7864% | 0.1963% | -2.081% | -2.09% | -0.1068% | -0.5935% | -0.2261% | -0.2996% | 0.2973% | 1.803% | 1.478% | 2.391% | -1.673% | -0.4907% | 0.8672% | -0.199% | -0.5913% | -0.5611% | -0.5008% | -0.189% | 0.4145% | 1.642% | 1.249% | 1.088% | 1.139% | 2.215% | 1.401% | 3.69% | 0.939% | 2.326% | 2.587% | 2.497% | 1.571% | 2.104% | 1.783% | 2.577% | 2.205% | 1.601% | 2.527% | 0.1631% | 0.7867% | 1.718% | 0.7354% | 1.528% | 0.3396% | 4.281% | 3.953% | 2.299% | 2.592% | 4.417% | -0.5683% | 2.738% | 4.112% | 2.429% | -0.4267% | 1.14% | 0.3357% | 0.8846% | 3.714% | 1.956% | 3.284% | 4.13% | 4.816% | 5.213% | 5.116% | -5.573% | -0.1721% | 5.206% | 1.661% | -0.4684% | 1.093% | 0.6385% | 4.796% | 0.1336% | -0.5501% | 2.229% | 1.519% | 1.477% | 1.002% | 1.989% | -0.1617% | 2.605% | 0.8296% | 1.059% | 1.164% | -4.121% | -0.9476% | -3.663% | -0.8182% | 2.71% | 3.117% | 2.334% | 1.291% | 1.979% | 2.256% | 1.926% | 2.047% | -0.8083% | -0.7586% | -1.186% | 0.9127% | -1.554% | -0.3109% | 0.4054% | -1.604% | -2.248% | 2.937% | 1.895% | 0.6239% | 2.539% | 1.077% | 2.394% | 2.887% | 3.065% | 2.047% | 2.764% | 1.58% | -1.209% | 0.1642% | -0.6427% | 0.4588% | 2.829% | 2.528% | 0.5485% | 3.179% | 2.071% | 3.492% | 3.613% | 2.587% | 3.02% | 0.2335% | 1.088% | 3.583% | 1.39% | 0.6962% | 3.281% | 0.3892% | 2.376% | 2.175% | 3.249% | 2.51% | 3.038% | 2.51% | 3.259% | 2.574% | 1.978% | 1.878% | -2.007% | 1.444% | 1.686% | 1.494% | 1.1% | 3.648% | 1.555% | 1.823% | 2.087% | 0.8938% | 1.707% | -2.758% | 4.949% | 2.942% | 2.256% | 1.47% | 2.341% | 0.8588% | -3.265% | 0.07663% | 2.699% | 4.13% | 3.191% | 2.574% | 0.9823% | 1.321% | 1.699% | -2.052% | 2.384% | 1.446% | 1.289% | -2.784% | 1.947% | 2.887% | -0.9252% | 0.03729% | 2.097% | 2.176% | -1.733% | 0.5347% | 0.6541% | 1.261% | 0.6839% | 1.987% | 0.2561% | 2.344% | 2.574% | 2.355% | 2.684% | 2.198% | 3.619% | 1.881% | 3.559% | 3.599% | 3.723% | 2.622% | 2.902% | 3.229% | 3.754% | 3.36% | 4.392% | 3.316% | 4.157% | 5.029% | 2.72% | 2.898%
2025-06-22 | -8.678% | -10.41% | -8.244% | -8.078% | -7.962% | -10.58% | -5.336% | -9.457% | -7.796% | -6.102% | -6.251% | -6.716% | -5.454% | -5.753% | -4.524% | -4.358% | -6.755% | -5.881% | -6.833% | -5.703% | -3.212% | -3.909% | -2.597% | -2.63% | -4.341% | -3.677% | -3.261% | -2.713% | -2.979% | -3.029% | -3.56% | -2.879% | -7.331% | -8.363% | -7.332% | -6.562% | -4.324% | -4.499% | -6.484% | -5.234% | -6.467% | -5.448% | -3.965% | -3.675% | -3.514% | -1.573% | -1.687% | -2.867% | -5.328% | -2.582% | -2.476% | -4.761% | -5.242% | -5.125% | -7.058% | -4.595% | -6.698% | -9.391% | -9.565% | -10.18% | -5.238% | -6.641% | -5.755% | -1.698% | -2.734% | -1.467% | -1.94% | -3.09% | -2.886% | -3.423% | -0.4645% | -2.719% | -2.901% | -3.353% | -3.415% | -2.521% | -2.292% | -2.606% | -0.2224% | 0.4585% | -2.916% | -1.001% | 1.321% | -0.1798% | -1.062% | -0.4329% | -1.532% | -2.863% | -0.805% | -1.266% | -1.395% | -10.04% | -6.668% | -5.866% | -3.998% | -4.497% | -6.256% | -3.574% | -3.332% | -4.063% | -4.348% | -2.477% | -4.628% | -3.256% | -0.6537% | -3.937% | -1.652% | -4.036% | -2.984% | -0.9941% | -0.7596% | -0.9185% | 0.3475% | -2.743% | -1.917% | -0.351% | -1.418% | 0.6628% | 1.994% | 2.32% | 0.6174% | 0.7082% | 0.279% | 1.513% | 3.197% | 2.736% | 1.003% | 4.181% | 1.245% | 1.548% | 1.2% | 3.568% | 1.245% | 3.152% | 1.132% | 1.919% | 4.859% | 1.291% | -1.529% | -0.05596% | 1.563% | -0.04083% | -1.115% | 3.137% | 1.586% | 3.379% | 2.153% | 5.151% | 4.089% | 3.482% | 5.208% | 1.79% | 4.582% | 0.2618% | 1.056% | 3.137% | 4.461% | 2.827% | 1.571% | 0.3753% | 2.32% | 1.26% | 5.361% | 0.3403% | 1.904% | 4.305% | -0.4065% | 0.911% | 0.4636% | 0.9193% | 0.4801% | 0.9607% | 1.052% | 1.35% | 1.997% | 1.657% | 0.6293% | 1.367% | 2.626% | 2.407% | 4.089% | 1.307% | 2.734% | 2.676% | 2.767% | 1.831% | 2.403% | 2.195% | 2.908% | 2.991% | 2.916% | 3.662% | 2.61% | 2.452% | 3.12% | 3.068% | 2.546% | 1.33% | 5.173% | 4.13% | 0.6105% | 1.038% | 3.175% | -0.04526% | 1.008% | 2.978% | 0.6865% | -1.613% | -3.076% | 2.171% | 1.397% | 0.6846% | 1.704% | 3.493% | 5.98% | 2.668% | 5.751% | 4.073% | -2.591% | -0.6156% | 3.656% | 0.6687% | -2.731% | 0.6903% | -1.492% | -1.147% | 1.266% | 0.09229% | 3.562% | 3.889% | 3.217% | 2.326% | 4.439% | 2.121% | 4.809% | 3.76% | 3.811% | 4.069% | 2.293% | 2.441% | 1.859% | 2.015% | 3.407% | 4.293% | 1.385% | 0.2201% | 2.675% | 1.679% | 3.295% | 2.572% | 2.318% | 2.023% | 3.17% | 3.949% | 1.58% | 1.892% | 2.769% | 0.4991% | -3.383% | 3.68% | 3.091% | 2.314% | 1.891% | 1.712% | 2.802% | 3.871% | 4.196% | 1.592% | 3.738% | 2.035% | -1.784% | 2.994% | -0.8939% | 2.902% | 4.962% | 5.287% | 1.382% | 5.914% | 3.034% | 1.276% | 1.731% | 1.201% | 1.093% | -1.434% | -0.5225% | 2.419% | 0.8862% | -0.5142% | 2.411% | -1.645% | 1.707% | 2.974% | 3.338% | 1.084% | 1.093% | 1.135% | 1.385% | 1.214% | 0.3907% | 0.9478% | -1.627% | 0.8397% | 0.5986% | 1.679% | 1.197% | 2.393% | 1.472% | 2.643% | 2.763% | 1.902% | 2.288% | -2.95% | 2.676% | 1.105% | -0.3044% | 1.04% | 2.52% | 0.6881% | 1.859% | 0.9059% | 0.4897% | 0.4553% | 2.212% | 0.8511% | -0.07496% | 0.7937% | 1.212% | 1.015% | 2.153% | 1.195% | 1.583% | 4.035% | 3.846% | 4.551% | 4.25% | 0.1955% | 3.285% | 2.4% | 0.1627% | 1.9% | 2.408% | 3.179% | 2.236% | 3.375% | 0.8839% | 2.744% | 3.088% | 2.941% | 2.337% | 2.589% | 3.562% | 0.08447% | 2.818% | 3.482% | 2.434% | 2.877% | 2.285% | 0.8746% | 1.126% | 2.187% | -0.1041% | 3.114% | 3.224% | 2.925% | 3.045% | 1.557%
2025-06-23 | -5.295% | -8.68% | -5.078% | -5.914% | -6.364% | -10.34% | -2.121% | -7.651% | -5.207% | -6.3% | -3.663% | -4.885% | -4.692% | -5.721% | -4.178% | -4.435% | -6.987% | -3.129% | -3.599% | -4.114% | 0.002309% | -0.7694% | -1.991% | -3.342% | -2.699% | -1.284% | 0.002309% | -0.2549% | 1.353% | -1.477% | -0.3192% | -3.985% | -6.557% | -9.018% | -7.732% | -7.123% | -4.144% | -7.529% | -7.715% | -4.889% | -7.844% | -4.515% | -3.219% | -3.196% | -3.941% | -0.5528% | -0.5451% | -2.16% | -5.096% | -2.552% | -4.157% | -7.108% | -6.842% | -6.03% | -6.61% | -6.14% | -4.842% | -9.455% | -8.262% | -9.502% | -4.821% | -5.581% | -7.705% | 2.758% | 1.762% | 3.724% | 2.289% | 4.047% | 2.067% | 1.264% | 3.197% | 3.373% | 1.733% | 0.4621% | 1.293% | 1.488% | 1.151% | 2.025% | 2.787% | 4.047% | 1.41% | 3.529% | 3.49% | 4.121% | 4.369% | 3.264% | 2.835% | 2.654% | 4.281% | 2.201% | 2.582% | -1.109% | 2.729% | 2.582% | 3.285% | 3.783% | 3.7% | 4.105% | 2.963% | -58.81% | -19.46% | 3.9% | 1.09% | 4.193% | 8.353% | 2.816% | 4.545% | 2.523% | 4.34% | 5.218% | 4.457% | 5.218% | 5.294% | 3.907% | 1.938% | 4.427% | 3.314% | 3.812% | 5.248% | 4.31% | 2.611% | 2.67% | 1.641% | 3.386% | 4.31% | 4.281% | 1.762% | 4.31% | 2.729% | 2.699% | 1.147% | 2.67% | 2.084% | 2.992% | 1.322% | 2.67% | 4.336% | 1.82% | -0.1269% | -0.6987% | 0.473% | -0.2007% | 0.3265% | 1.293% | 0.5316% | 2.201% | 1.557% | 0.8751% | 1.704% | 0.3851% | 0.823% | 1.645% | 3.144% | 0.678% | 1.264% | 1.762% | 3.256% | 2.143% | 1.44% | 0.3265% | 1.03% | 0.5023% | 2.348% | 2.912% | 3.988% | 1.181% | -6.128% | -1.796% | -5.743% | -4.106% | -4.171% | -3.369% | -3.882% | -2.695% | -0.06404% | -1.476% | -2.887% | -0.6094% | 1.091% | -2.343% | 0.01082% | 0.6913% | -0.6736% | 0.6738% | 0.09637% | -2.246% | -0.9303% | -0.9303% | 0.4172% | -0.9303% | -1.283% | -1.379% | -0.4169% | -0.6094% | -3.051% | -2.613% | 0.7557% | -1.5% | 0.265% | 0.2481% | -1.203% | -1.413% | 0.114% | -1.551% | -0.3414% | 1.574% | 0.4408% | -1.657% | -1.475% | -1.384% | -2.746% | -2.545% | -0.0517% | 0.7146% | 0.5147% | -0.7014% | 1.702% | -1.273% | -2.467% | -2.995% | 1.44% | -1.447% | -2.572% | -2.616% | -1.132% | 1.402% | -1.263% | -0.2637% | 1.581% | -0.1183% | 0.448% | -2.812% | 2.114% | 0.2656% | 2.347% | -0.718% | 0.08156% | 2.447% | -5.636% | -2.654% | -4.018% | -2.146% | 4.613% | 3.28% | 3.347% | -1.384% | 0.3481% | -1.606% | -0.1517% | -1.67% | -0.5594% | -1.702% | 2.328% | 0.01176% | -3.003% | -1.448% | -0.4959% | 2.311% | 0.02506% | 2.237% | 1.605% | 3.271% | 3.53% | 1.433% | 3.213% | 2.129% | 2.179% | 2.295% | 2.159% | 3.465% | 0.5123% | 0.8862% | 1.679% | -0.5514% | 1.281% | 1.022% | 0.4987% | 2.298% | 1.463% | 2.984% | 3.08% | -0.5132% | -0.834% | -2.181% | 0.6738% | 2.535% | 0.3851% | -1.796% | 2.855% | 2.494% | 0.4814% | 2.374% | 3.754% | 3.013% | -0.9623% | 0.006714% | 2.946% | 2.176% | 1.372% | 3.271% | 2.079% | 2.176% | 0.0195% | 1.533% | 2.627% | 0.586% | 0.1161% | 1.412% | 1.16% | 0.3177% | 3.946% | -0.747% | 4.697% | 2.677% | -3.637% | 0.2339% | 2.844% | -1.63% | 0.2339% | 4.673% | -2.384% | 2.414% | 7.849% | 6.802% | 5.311% | 3.312% | 5.406% | -0.4642% | 6.23% | 2.214% | -2.584% | 4.546% | 6.845% | 6.278% | 8.844% | -0.2104% | 1.693% | 3.09% | -0.5594% | -0.8132% | 2.169% | 1.471% | 0.9636% | 3.629% | -0.5594% | 1.614% | 2.614% | 4.073% | 0.4393% | 0.3814% | 4.313% | -2.808% | 1.154% | 1.217% | -0.3515% | 1.523% | 1.091% | 2.159% | -0.08502% | 0.2656% | 0.4814% | 3.513% | 1.386% | 4.746% | 4.712% | 0.8145%
2025-06-24 | -7.935% | -11.6% | -7.139% | -8.281% | -8.127% | -12.37% | -3.692% | -8.96% | -6.522% | -6.399% | -4.394% | -5.628% | -6.553% | -5.628% | -5.072% | -5.072% | -6.344% | -3.616% | -3.468% | -3.777% | 0.6041% | -0.9693% | -0.63% | -1.154% | 0.203% | 0.203% | 0.3881% | 0.0796% | 2.085% | 1.036% | 0.6966% | -0.3832% | -7.88% | -9.851% | -8.942% | -8.097% | -5.922% | -6.409% | -7.541% | -5.792% | -7.541% | -6.18% | -4.49% | -4.712% | -3.492% | -1.758% | -1.823% | -2.517% | -4.54% | -2.072% | -2.641% | -4.911% | -5.597% | -4.615% | -5.449% | -4.362% | -5.089% | -9.473% | -7.528% | -9.067% | -3.808% | -5.131% | -5.776% | 4.449% | 2.819% | 3.816% | 3.241% | 3.17% | 1.6% | 2.102% | 3.367% | 3.03% | 0.9501% | 1.74% | -0.07574% | -0.08788% | -0.5286% | 4.28% | 4.758% | 5.124% | 2.777% | 4.945% | 5.138% | 5.098% | 4.983% | 5.025% | 4.084% | 3.711% | 4.379% | 3.887% | 3.859% | 1.92% | 2.96% | 4.688% | 4.294% | 4.294% | 4.251% | 5.067% | 4.07% | 2.321% | 3.923% | 4.07% | 1.775% | 4.351% | 9.353% | 3.985% | 4.983% | 2.847% | 3.03% | 5.306% | 5.025% | 6.149% | 1.884% | 4.29% | 3.03% | 4.969% | 4.646% | 4.941% | 6.768% | 4.913% | 4.154% | 3.915% | 3.056% | 4.628% | 4.8% | 3.971% | 2.369% | 4.435% | 3.03% | 3.086% | 1.99% | 3.03% | 2.664% | 3.283% | 1.217% | 2.454% | 4.231% | 3.648% | 1.6% | 1.062% | 1.807% | 2.243% | 2.088% | 2.369% | -2.563% | 2.693% | 1.484% | 2.792% | 1.632% | 0.823% | 1.807% | 1.428% | 3.516% | 1.02% | 1.358% | 1.695% | -2.465% | 2.299% | 2.215% | 0.6409% | 1.133% | -0.6097% | 2.088% | 2.481% | 3.395% | 1.352% | -1.979% | 0.2682% | -0.5783% | 0.06812% | -0.4551% | 0.1143% | 0.4067% | 1.469% | 2.238% | 1.068% | 0.7453% | 1.207% | 1.515% | 0.4983% | 1.664% | -0.8665% | 1.176% | 1.099% | 1.946% | 1.068% | 0.9762% | 0.7915% | 0.576% | 1.099% | 0.1605% | 0.4991% | -1.04% | -0.6244% | -0.2127% | -0.9723% | 1.129% | -0.1732% | 1.822% | 2.271% | 1.105% | 1.634% | 3.791% | 1.155% | 2.801% | 4% | 3.537% | 1.386% | 2.519% | 2.424% | 2.245% | 0.6604% | 0.6086% | 2.095% | 1.807% | -0.857% | -0.1695% | 2.251% | 1.101% | 1.058% | 4.537% | 2.555% | -0.5523% | 1.073% | 1.548% | 4.008% | -2.45% | -2.726% | -0.5741% | -0.67% | -0.5741% | -1.838% | 0.4647% | -1.762% | 0.6885% | -0.3344% | -0.5422% | -0.7499% | -3.513% | -2.264% | -3.65% | -2.417% | 1.104% | -0.1106% | -0.2545% | -4.624% | -0.5581% | -6.983% | -82.91% | -41.11% | -1.199% | -1.032% | -0.9706% | -0.651% | -2.341% | -1.184% | -0.1639% | -1.418% | 1.293% | 3.009% | 2.491% | -3.379% | 3.326% | -1.944% | 0.9753% | 3.58% | 4.08% | 3.44% | 3.899% | 3.184% | 0.6075% | 1.091% | 0.6874% | 0.7151% | 2.287% | 2.269% | 1.369% | 3.313% | 3.115% | 0.4375% | 0.2374% | -0.3166% | -0.4244% | -1.609% | -0.7783% | 0.853% | -0.7783% | -1.563% | 1.638% | -0.6659% | 0.2066% | 0.6376% | 1.726% | 1.387% | 0.7568% | 1.11% | 2.598% | 2.587% | 2.726% | 2.247% | -0.2014% | 1.46% | 0.3942% | 1.398% | 1.105% | 1.064% | 0.8575% | 0.8838% | 1.048% | 0.369% | -1.597% | -4.44% | 0.2559% | -0.4227% | -5.887% | -1.595% | -0.05115% | -2.121% | -1.062% | -1.84% | -1.965% | -0.2705% | 1.221% | -0.9402% | -0.6206% | -1.579% | -0.6662% | -2.067% | 0.9436% | -1.677% | -1.645% | 2.095% | 1.919% | 2.287% | 3.278% | 0.521% | 1.921% | 2.819% | -1.914% | 1.13% | 1.069% | 0.5819% | 0.8711% | 1.754% | 1.678% | 1.408% | 0.6885% | 1.526% | 0.1501% | 0.9282% | 2.59% | 0.7611% | 0.932% | 0.8711% | 1.919% | 1.429% | 1.982% | 1.081% | 0.8163% | 1.252% | 0.7524% | 2.431% | 1.9% | 1.903% | 2.542% | 3.725%
2025-06-25 | -6.152% | -8.357% | -4.962% | -4.983% | -6.473% | -9.955% | -1.881% | -6.493% | -5.647% | -4.6% | -2.867% | -3.875% | -4.499% | -4.338% | -3.875% | -3.774% | -4.434% | -2.929% | -3.19% | -2.263% | 0.3354% | -0.2287% | -0.3697% | -0.5308% | -0.551% | -0.02723% | 0.05334% | -0.1279% | 1.161% | 0.5771% | -0.1481% | 0.1138% | -6.372% | -7.488% | -6.512% | -5.516% | -3.374% | -3.756% | -6.292% | -4.434% | -5.949% | -4.983% | -3.378% | -2.894% | -2.68% | -0.8759% | -1.519% | -2.88% | -4.694% | -2.01% | -2.843% | -4.825% | -5.632% | -5.001% | -6.22% | -3.764% | -5.114% | -8.167% | -7.234% | -8.046% | -3.532% | -5.158% | -5.864% | 2.789% | 1.697% | 3.395% | 0.06415% | 1.716% | 0.7068% | 0.6881% | 2.569% | 1.973% | 0.07332% | -1.418% | 0.1742% | 0.2001% | -0.2987% | 2.064% | 2.248% | 3.542% | 1.211% | 2.226% | 3.064% | 3.72% | 3.046% | 2.896% | 2.761% | 2.012% | 3.688% | 2.78% | 2.725% | -3.321% | 0.3394% | 0.8165% | 2.652% | 1.385% | -1.787% | 0.8165% | 1.303% | -13.39% | 0.8524% | 2.752% | -0.3709% | 2.798% | 4.734% | 1.468% | 3.808% | 0.578% | 2.496% | 4.083% | 4.496% | 2.055% | 4.911% | 2.454% | 0.3486% | -0.7066% | 2.266% | 3.156% | 4.285% | 3.505% | 2.395% | 1.294% | 0.085% | 1.965% | 3.633% | 3.358% | 1.266% | 3.835% | -1.028% | 1.954% | 0.789% | 2.229% | 1.073% | 1.523% | -0.624% | 0.1651% | 3.087% | 4.285% | 0.4157% | 0.7064% | 2.174% | 2.129% | 2.074% | 3.532% | -4.138% | 4.065% | -2.734% | 0.9867% | 0.9243% | 1.716% | 2.117% | 1.092% | 2.258% | -1.028% | -0.5598% | -1.725% | -0.02761% | -0.7524% | -0.8625% | -0.2111% | 1.046% | -4% | 3.046% | -0.5793% | 0.9633% | 1.581% | 3.404% | 4.67% | -100% | 3.374% | 2.7% | 2.942% | 2.851% | 3.575% | 4.328% | 2.881% | 4.469% | 4.68% | 4.549% | 4.417% | 5.092% | 1.888% | 4.158% | 3.464% | 4.318% | 3.987% | 3.866% | 3.796% | 3.575% | 3.705% | 2.962% | 4.168% | 1.766% | 0.6002% | 3.341% | 2.317% | 3.509% | 1.07% | 4.354% | -1.406% | 3.192% | 3.538% | 6.111% | 2.181% | 4.563% | 6.859% | 5.607% | 2.704% | 3.672% | 4.524% | 4.046% | 1.116% | 3.398% | 4.532% | 4.866% | 4.507% | 3.069% | 5.746% | 2.511% | 2.528% | 7.429% | 3.761% | 1.726% | 3.308% | 2.804% | 6.572% | 0.3513% | -0.2938% | 2.038% | 1.297% | 0.7544% | 0.5681% | 1.422% | 0.04136% | 3.102% | 0.4101% | 1.881% | 0.01353% | -3.05% | 1.244% | -4.212% | 0.6277% | 2.904% | 2.998% | 2.048% | -10.02% | 0.5979% | -13.99% | -100% | -100% | 1.453% | 1.661% | 0.4588% | 2.884% | 0.01154% | 1.701% | 2.407% | -0.02821% | -2.722% | -0.2641% | -0.5505% | 0.07405% | 0.1544% | -1.493% | 1.123% | 1.442% | 1.487% | 0.3801% | 2.4% | 1.771% | -3.296% | 0.7655% | -0.7113% | 0.006574% | 2.291% | 2.349% | 0.7703% | 3.476% | 1.556% | -0.9473% | -0.2137% | -0.475% | 0.03749% | -2.796% | -3.178% | -0.3343% | -2.304% | -2.746% | -0.1534% | -0.78% | -0.7162% | 0.1782% | -0.2469% | 0.3123% | 0.1435% | 0.8947% | 1.208% | 1.599% | 1.599% | 1.508% | 0.4127% | 0.2781% | -0.2765% | 0.7016% | 0.07642% | 0.7282% | 0.0865% | 0.7309% | 0.65% | -0.4157% | -2.543% | -5.799% | -0.08862% | -2.453% | -6.598% | -2.741% | -1.83% | -3.785% | -6.22% | -3.301% | -3.472% | -2.616% | -1.976% | -4.292% | -3.815% | -3.159% | -3.586% | -5.484% | -1.064% | -3.305% | -6.279% | -0.383% | -1.354% | 1.015% | 0.08658% | -3.855% | -0.8332% | -1.668% | -4.183% | -2.026% | -1.857% | -0.8929% | -1.678% | -0.545% | -2.225% | -1.562% | -1.176% | -1.092% | -1.808% | -0.717% | 0.06571% | -2.428% | -0.7637% | -0.2767% | -0.9778% | -0.6733% | -1.41% | -1.47% | -1.719% | -1.39% | -1.969% | -0.4561% | -0.5445% | -0.2369% | -0.717% | -0.2578%
2025-06-26 | -4.541% | -12.72% | -4.314% | -4.476% | -4.282% | -8.735% | -1.94% | -5.77% | -3.359% | -2.858% | -3.068% | -3.149% | -2.647% | -2.227% | -1.434% | -1.385% | -2.702% | -3.025% | -3.634% | -2.583% | 0.6216% | -5.56% | 1.091% | 0.9938% | -0.4626% | 0.03902% | 0.5407% | 0.217% | 0.6863% | 0.7672% | 0.1523% | 0.1847% | -4.589% | -5.546% | -4.473% | -4.473% | -2.071% | -1.884% | -3.909% | -3.502% | -5.754% | -3.969% | -1.448% | -1.082% | -2.753% | -0.2449% | -5.209% | -3.016% | -5.718% | -2.901% | -3.157% | -5.728% | -7.067% | -6.656% | -6.562% | -3.212% | -4.609% | -7.952% | -7.511% | -8.467% | -3.553% | -5.714% | -8.935% | 0.8402% | 0.597% | 3.343% | 3.346% | 1.828% | 2.688% | -0.4349% | 3.472% | 1.54% | 0.07366% | -2.256% | -0.2875% | 2.326% | 2.218% | 2.513% | 2.115% | 4.961% | -0.1475% | 1.286% | 4.15% | 2.58% | -0.5013% | -0.6715% | -0.7485% | -2.044% | 2.941% | 1.563% | 1.511% | -1.791% | 1.12% | 2.911% | 4.371% | 1.386% | -0.9748% | 3.516% | 1.142% | -18.56% | 3.351% | 0.597% | -0.1689% | 1.437% | 8.196% | 2.41% | 4.57% | 1.371% | 2.838% | 2.499% | 3.442% | 2.329% | 3.364% | -1.958% | 1.142% | -0.6708% | 0.1916% | 1.29% | 4.091% | 2.285% | 1.636% | -0.08113% | -1.026% | 0.731% | 2.366% | 2.027% | -0.376% | 2.174% | -1.194% | -1.224% | -1.061% | 1.563% | -1.629% | 0.656% | -1.445% | -0.6045% | 2.727% | -2.749% | -3.409% | -3.066% | -0.8845% | -2.263% | -1.828% | 1.246% | -4.909% | 0.4643% | -3.921% | 3.652% | 1.534% | 1.432% | 2.446% | -0.6413% | 2.291% | -3.015% | -1.99% | -0.4644% | 1.341% | -1.025% | -1.747% | 0.0884% | -0.7076% | 0.8623% | 3.464% | -2.175% | -0.3391% | -0.8949% | 0.3692% | 1.298% | -100% | 1.16% | 0.7325% | 0.5872% | 0.1432% | -0.08288% | 0.9343% | 1.427% | 0.9262% | 1.136% | 2.751% | 2.345% | 3.497% | -2.259% | 2.202% | 1.249% | 2.089% | 1.661% | 1.475% | 2.323% | 0.03821% | 1.798% | -0.9063% | 1.758% | 2.299% | 2.5% | 3.302% | 3.464% | 3.302% | -5.363% | -1.24% | 0.5912% | -1.989% | -1.638% | 1.178% | -2.516% | -0.3845% | 2.042% | -0.4356% | -2.075% | 0.6453% | -2.203% | -0.1221% | -4.975% | -5.562% | -3.357% | -1.798% | -1.673% | -0.2299% | -0.1549% | -5.995% | -3.022% | 0.3184% | -3.284% | -6.615% | -2.85% | -6.242% | -1.54% | -5.208% | -5.673% | -1.169% | -2.268% | 0.566% | -1.58% | 0.5241% | -1.708% | -3.315% | -3.29% | -0.5573% | 0.5409% | -2.307% | -0.2787% | -1.788% | 1.023% | -3.567% | -2.67% | -3.575% | -11.18% | -5.629% | -12.12% | -100% | -100% | -0.8296% | -2.339% | -4.199% | -2.426% | -0.07108% | -0.9733% | -1.357% | 1.781% | -4.356% | -0.1804% | -0.6652% | -2.014% | -2.356% | -4.358% | -0.8691% | 0.9349% | 2.079% | -0.4866% | 1.171% | -2.018% | -5.133% | -1.684% | -10.01% | -3.257% | 0.1059% | 0.6555% | -2.324% | 1.879% | 0.2185% | 0.6356% | 0.3369% | -0.4219% | 0.4984% | -3.183% | -0.5269% | 0.7083% | -0.6722% | -1.932% | 1.201% | -2.101% | 0.3611% | 0.9747% | 2.319% | 1.844% | 0.7595% | 1.154% | 1.227% | 1.36% | 1.732% | 1.319% | -3.275% | 0.1042% | 0.06372% | 0.8333% | 1.125% | 1.725% | 1.173% | 0.6679% | 2.039% | 1.989% | 3.182% | -2.965% | 1.539% | 2.356% | 0.2483% | 0.3122% | 1.565% | 0.2025% | 2.356% | 0.2947% | 3.953% | 5.219% | 5.103% | 5.055% | 4.831% | 4.065% | 5.733% | 6.26% | 1.929% | 3.986% | -9.838% | 5.261% | 5.244% | 7.558% | 7.39% | 4.344% | 5.669% | 5.366% | 2.228% | 4.033% | 4.392% | 4.2% | 3.857% | 5.079% | 3.027% | 5.965% | 6.468% | 5.893% | 7.694% | 6.879% | 8.119% | 5.668% | 5.893% | 5.933% | 8.941% | 4.532% | 7.458% | 7.352% | 10.04% | 8.153% | 9.813% | 7.507% | 8.683% | 9.503% | 8.824% | 7.574%
2025-06-27 | -5.109% | -12.01% | -4.746% | -4.402% | -5.728% | -9.156% | -2.434% | -6.907% | -5.581% | -4.328% | -3.837% | -4.893% | -3.739% | -4.574% | -3.592% | -3.395% | -4.902% | -4.023% | -4.599% | -3.641% | -0.9151% | -1.652% | -1.406% | -1.455% | -2.192% | -1.578% | -0.8905% | -0.6941% | -0.3503% | -0.866% | -1.308% | -1.529% | -5.532% | -6.944% | -5.652% | -5.316% | -3.145% | -4.023% | -5.556% | -4.23% | -5.237% | -3.219% | -1.633% | -1.383% | -2.046% | 0.6207% | -0.7364% | -1.537% | -3.272% | -2.598% | -2.4% | -4.802% | -5.914% | -5.956% | -6.786% | -4.345% | -5.066% | -8.212% | -8.09% | -8.685% | -4.181% | -5.931% | -10.46% | 2.478% | 2.187% | 2.214% | 2.992% | 3.272% | 2.637% | 0.9454% | 3.473% | 2.914% | 1.717% | -0.553% | 1.807% | 1.944% | 2.248% | 1.505% | 2.042% | 2.109% | 0.9119% | 1.97% | 2.769% | 2.915% | 2.623% | 2.014% | 2.236% | 1.203% | 2.433% | 2.5% | 2.869% | -2.913% | 0.498% | 0.498% | 2.735% | 1.863% | 1.503% | 0.7217% | 1.963% | -0.3129% | 0.2133% | 2.746% | -0.234% | 2.914% | 4.827% | 1.18% | 4.144% | 2.534% | 3.496% | 4.771% | 4.525% | 4.368% | 4.091% | 2.26% | 1.348% | 3.708% | 2.142% | 3.552% | 0.4533% | 3.63% | 3.171% | 2.545% | 1.57% | 2.587% | 3.272% | 3.574% | 0.8112% | 3.563% | 2.198% | 2.142% | 1.024% | 2.086% | -0.6093% | 3.272% | 2.008% | 3.484% | 4.435% | 4.883% | 2.327% | 3.35% | 2.925% | 2.791% | 3.384% | 3.484% | 3.048% | 4.67% | 2.903% | 4.248% | 3.567% | 2.458% | 3.88% | 3.552% | 4.471% | 1.784% | 2.769% | 0.9007% | 3.708% | 2.836% | 2.142% | -0.3073% | 2.209% | 2.735% | 3.675% | 3.482% | 4.2% | 0.6928% | 0.4773% | 2.327% | -82.85% | -4.227% | 1.029% | 1.849% | 2.205% | 2.866% | 3.871% | 2.842% | 1.751% | 2.829% | 4.165% | 2.697% | 3.475% | 2.342% | 3.822% | 3.442% | 4.312% | 3.442% | 3.479% | 3.442% | 3.417% | 3.332% | 2.695% | 3.944% | 2.474% | 3.172% | 2.697% | 2.375% | 2.916% | 1.739% | 4.527% | 3.566% | 2.722% | 2.546% | 3.581% | 2.408% | 3.564% | 4.174% | 3.586% | 0.4536% | 1.772% | 1.954% | 0.2344% | -0.1078% | 3.277% | 3.222% | 4.685% | 4.595% | 4.156% | 3.157% | 1.009% | 0.2912% | 4.668% | 2.031% | -0.2993% | 0.5854% | 1.659% | 4.646% | 0.9625% | -0.275% | 2.052% | 2.103% | 1.352% | 0.3424% | 3.057% | 1.033% | 3.757% | 1.721% | 2.166% | 2.624% | 1.554% | 1.505% | 0.9966% | 1.215% | 3.299% | 3.68% | 2.103% | -5.74% | 1.53% | -4.019% | -55.5% | -58.01% | 1.348% | 0.9239% | 3.444% | 2.56% | 1.142% | 1.566% | 2.475% | 1.564% | -1.234% | 1.672% | 1.165% | 2.33% | 2.313% | 1.125% | 2.285% | 2.524% | 2.768% | 2.336% | 2.663% | 1.848% | -0.225% | 0.7685% | 0.6132% | 0.1712% | 2.125% | 1.843% | 1.208% | 2.803% | 1.622% | -0.3068% | 0.5018% | -0.4783% | -0.27% | -3.235% | -2.193% | 0.6855% | -1.434% | -2.696% | 0.465% | -0.3408% | -0.1598% | 1.176% | 0.6518% | -0.5573% | -0.6087% | 0.3391% | 1.375% | 1.349% | 0.8817% | 1.582% | -0.4119% | 0.8571% | 0.1441% | 1.705% | 0.9923% | 0.8991% | 0.9554% | 1.127% | 1.501% | 0.5103% | 1.072% | -2.73% | 0.6518% | -0.6753% | -1.148% | -1.645% | -0.7502% | -0.7857% | -3.825% | -0.8648% | -2.388% | -0.7595% | 0.4393% | -0.1059% | -2.505% | -1.172% | -0.4209% | -0.1301% | 0.8969% | -1.943% | -1.065% | 0.7161% | 0.7161% | 1.009% | 1.111% | -2.965% | 0.06371% | -0.9419% | -3.026% | -1.766% | -0.8934% | -0.00898% | -1.027% | 0.1243% | -2.044% | -1.268% | -0.8995% | 0.1849% | -0.9999% | 0.6271% | 0.4363% | -1.79% | 0.4272% | 1.057% | -0.7468% | 0.7774% | -0.3361% | -0.2634% | -0.6578% | -0.04533% | -0.2634% | 0.08007% | -0.02237% | 1.899% | 0.8688% | -0.3525%
2025-06-28 | -5.395% | -12.9% | -5.519% | -5.589% | -6.041% | -9.014% | -3.403% | -7.222% | -5.206% | -4.268% | -4.598% | -5.119% | -4.389% | -4.355% | -3.729% | -4.094% | -4.754% | -4.151% | -4.772% | -3.938% | -1.139% | -2.165% | -1.383% | -1.348% | -1.782% | -1.73% | -1.504% | -1.435% | -0.6179% | -0.9829% | -1.661% | -1.157% | -6.11% | -6.913% | -5.944% | -5.322% | -3.62% | -4.242% | -5.658% | -4.992% | -6.51% | -5.22% | -3.267% | -3.166% | -3.233% | -1.208% | -1.895% | -2.988% | -5.3% | -3.043% | -2.445% | -4.62% | -5.93% | -5.776% | -7.153% | -4.859% | -6.519% | -9.518% | -8.799% | -9.842% | -4.928% | -6.13% | -6.279% | 1.254% | 0.2877% | 1.529% | 1.309% | 1.04% | 1.332% | -0.9235% | 1.673% | 0.921% | -0.8048% | -2.215% | -0.7494% | 0.5259% | 0.6997% | -1.494% | 1.119% | 2.188% | -0.7177% | 0.6535% | 2.591% | 1.776% | 0.8894% | 1.469% | 0.6252% | -0.9439% | 1.665% | 1.238% | 1.214% | -4.692% | -2.095% | -0.4406% | 0.2798% | -0.314% | -1.748% | 0.8656% | -0.005208% | -3.472% | 0.07072% | 0.1531% | -1.295% | -0.3615% | 3.629% | -0.3931% | 1.61% | 0.549% | -0.08437% | 2.797% | 2.235% | 2.109% | 3.015% | -0.4259% | 0.169% | 1.475% | 0.7152% | 2.101% | 1.966% | 2.742% | 1.76% | 1.309% | 0.7328% | 2.239% | 3.225% | 3.003% | 0.9369% | 3.304% | 1.119% | 1.214% | 0.3827% | 1.641% | 0.7865% | 1.95% | 0.351% | 1.626% | 3.034% | 3.201% | 1.158% | 2.045% | 2.449% | 2.061% | 2.552% | 3.344% | 2.156% | 3.541% | 2.52% | 3.944% | 3.263% | 2.024% | 3.514% | 2.251% | 4.22% | 1.127% | 1.277% | -2.048% | 2.401% | 1.982% | -2.016% | 0.03438% | 1.641% | -3.441% | 3.138% | 0.9798% | 2.599% | 2.91% | -0.5571% | 0.5701% | 0.2493% | 0.4834% | 0.44% | 0.8562% | 1.29% | 2.512% | 3.059% | 2.183% | 0.6828% | 1.064% | 2.781% | 1.675% | 3.635% | 1.345% | 2.842% | 2.668% | 3.249% | 2.712% | 2.954% | 2.816% | 2.764% | 3.249% | 2.426% | 3.379% | 1.489% | 1.975% | 2.248% | 1.547% | 2.813% | 0.7359% | 3.465% | 3.376% | 1.013% | 1.104% | 2.858% | 0.7405% | 1.84% | 2.74% | 2.043% | -0.5706% | 1.304% | 0.8369% | -0.6108% | -2.137% | 1.663% | 2.7% | 3.7% | 2.532% | 4.409% | 3.837% | -1.15% | -1.54% | 2.975% | 0.4236% | -2.532% | -1.743% | 0.2404% | 2.784% | 0.2562% | -0.4969% | 1.926% | 2.034% | 2.034% | 1.3% | 3.097% | 0.8369% | 2.313% | 1.575% | 2.106% | 2.196% | 1.129% | 0.8541% | 0.7855% | 0.4596% | 2.169% | 2.106% | 1.422% | -5.131% | 0.6744% | -5.663% | 0.4854% | -2.207% | 0.7512% | 0.5368% | 1.712% | 2.278% | 0.6311% | 0.8026% | 1.917% | -3.264% | -4.433% | 1.527% | 1.384% | 1.199% | 1.356% | 1.374% | 1.671% | 2.442% | 2.764% | 1.636% | 2.229% | 2% | -0.827% | 1.091% | -0.6092% | 0.4553% | 3.367% | 2.996% | 0.7046% | 3.594% | 1.492% | -0.0889% | 0.06717% | 0.006479% | -0.01086% | -2.681% | -1.459% | 0.5007% | -1.303% | -1.892% | 0.8302% | -1.691% | 0.06717% | 0.5961% | 0.8553% | 0.3546% | 0.6824% | 0.8661% | 1.477% | 1.383% | 1.287% | 1.192% | -1.719% | 0.5131% | 0.1303% | 1.479% | 0.7654% | 1.504% | 0.7741% | 0.8302% | 1.338% | 0.7916% | 0.7105% | -2.866% | 0.9555% | -0.7666% | -1.135% | -1.641% | -0.219% | -1.96% | -0.8352% | -1.365% | -1.252% | -0.5411% | 0.5711% | -0.5522% | -1.633% | -1.324% | -0.7495% | -0.1749% | 0.1475% | -1.018% | 0.5124% | 2.079% | 1.917% | 1.926% | 2.061% | -2.027% | 0.6483% | 0.8455% | -2.687% | 0.2367% | 0.1509% | 0.5111% | 0.06517% | 1.223% | -0.5179% | 0.9806% | 1.206% | 0.7426% | 0.5801% | 0.8545% | 1.773% | -0.3496% | 0.897% | 1.403% | 1.566% | 1.189% | 1.454% | -0.8652% | 0.07117% | 0.7598% | 5.258% | 5.348% | 1.585% | 1.197% | 1.548% | 0.6294%
2025-06-29 | -7.479% | -14.52% | -7.18% | -7.015% | -7.529% | -11.04% | -4.735% | -8.76% | -6.684% | -5.802% | -5.931% | -6.592% | -5.912% | -5.931% | -5.232% | -5.526% | -6.492% | -5.583% | -6.133% | -5.324% | -2.494% | -3.431% | -2.274% | -2.678% | -3.045% | -2.917% | -2.531% | -2.898% | -2.035% | -2.145% | -2.77% | -2.421% | -7.235% | -8.524% | -7.595% | -6.937% | -5.409% | -5.873% | -6.996% | -6.415% | -7.603% | -6.294% | -3.931% | -4.532% | -4.284% | -1.954% | -2.257% | -3.347% | -5.048% | -3.886% | -3.47% | -5.945% | -7.277% | -6.571% | -8.065% | -5.756% | -6.558% | -10.42% | -9.811% | -10.44% | -6.28% | -7.588% | -6.813% | 0.7529% | -0.4692% | -0.6125% | -0.2683% | 0.3762% | -0.5994% | -0.8291% | 0.9621% | 0.8282% | -0.5361% | -2.263% | -0.6449% | -0.7667% | -0.6967% | 0.06652% | 0.6022% | 0.1753% | -0.4273% | 0.6699% | 0.845% | 1.255% | 1.255% | 0.5722% | 0.5984% | -0.4401% | -0.1093% | 0.4181% | 0.6273% | -5.131% | -2.177% | -1.834% | -0.7705% | -0.2432% | -0.9235% | -1.407% | -0.4273% | -1.222% | -1.213% | 0.1837% | -2.61% | 0.5687% | 4.746% | -0.08414% | 1.004% | -0.2683% | -0.5612% | 1.674% | 1.506% | 2.26% | 1.603% | 0.3796% | -0.02555% | 2.31% | 0.9956% | 1.941% | 1.665% | 1.615% | 1.498% | 1.356% | 0.3709% | 1.447% | 1.891% | 1.665% | -0.5027% | 1.941% | -1.281% | 0.8115% | -0.04229% | 0.5855% | 1.021% | 1.833% | 0.2339% | 1.489% | 2.322% | 3.875% | 1.957% | 1.464% | 1.816% | 2.427% | 2.645% | 2.251% | 1.925% | 3.448% | 2.452% | 3.381% | 2.579% | -0.6792% | 2.37% | 2.293% | 3.693% | 1.113% | 1.205% | 1.925% | 1.649% | 1.64% | 1.205% | 1.314% | 1.238% | 2.167% | 2.46% | 1.745% | 2.703% | 1.999% | 1.759% | 3.134% | 2.354% | 2.455% | 1.942% | 2.024% | 1.795% | 2.703% | 3.216% | 2.519% | 3.464% | 3.491% | 3.73% | 3.295% | 4.001% | 2.594% | 3.647% | 3.28% | 3.5% | 2.804% | 3.152% | 2.822% | 3.427% | 3.555% | 3.024% | 3.785% | 1.658% | 2.07% | 2.515% | 1.803% | 2.409% | 2.187% | 4.918% | 3.921% | 3.677% | 4.215% | 6.03% | 3.007% | 4.77% | 5.802% | 5.441% | 2.773% | 3.846% | 3.968% | 2.998% | 1.557% | 4.078% | 5.149% | 5.234% | 6.109% | 5.261% | 4.72% | 3.38% | 3.026% | 6.836% | 4.858% | 1.656% | 2.901% | 4.165% | 6.691% | 1.059% | 0.06414% | 1.902% | 2.74% | 1.598% | 0.9667% | 2.797% | 0.7582% | 3.854% | 2.959% | 2.702% | 2.264% | 1.221% | 1.248% | 0.7763% | 0.9214% | 3.863% | 4.72% | 3.121% | -3.512% | 2.569% | -4.111% | 1.874% | -0.8738% | 1.674% | 1.855% | 3.487% | 3.768% | 1.338% | 1.61% | 2.907% | 1.665% | -0.4557% | 1.368% | 0.9929% | 1.838% | 2.174% | 1.117% | 1.716% | 2.089% | 2.038% | 1.343% | 1.665% | 1.912% | -0.3054% | -0.1335% | -0.1148% | -0.2142% | 1.78% | 1.05% | 0.3245% | 2.095% | 0.9642% | -0.13% | -0.13% | -0.2217% | -0.24% | -2.935% | -1.89% | 0.4292% | -1.074% | -1.881% | 1.117% | -3.123% | 0.06254% | 0.8051% | 0.9362% | -0.6521% | -0.4018% | 0.09255% | 0.7664% | 0.634% | 0.6616% | 0.4684% | -2.686% | -0.09268% | -0.2215% | 0.726% | 0.1281% | 0.4556% | 0.5144% | 0.9793% | 0.9458% | 0.05062% | 0.2554% | -2.349% | 0.6089% | -0.7197% | -1.173% | -1.391% | -0.5269% | -2.435% | -0.5928% | -1.165% | -1.639% | -0.8299% | 0.468% | -0.4568% | -1.744% | -1.327% | -0.7832% | -0.6562% | 0.4161% | -1.753% | 0.1221% | 2.055% | 1.76% | 1.769% | 1.893% | -0.8376% | 1.375% | 0.9576% | -2.442% | 0.459% | 0.7491% | 0.5134% | 0.5587% | 1.175% | -0.6018% | 0.541% | 0.9123% | 0.5859% | -0.3303% | 0.4172% | 1.112% | -0.3946% | 0.5587% | 0.8216% | 0.7028% | 1.163% | 0.7491% | -0.7754% | -0.8299% | 0.2414% | -0.4205% | 0.9313% | 0.4513% | 0.6172% | 0.6743% | 0.7028%
2025-06-30 | -10.36% | -13.05% | -9.036% | -9.187% | -10.2% | -12.99% | -6.04% | -10.52% | -9.17% | -8.564% | -6.494% | -7.723% | -8.547% | -8.11% | -7.756% | -7.655% | -8.57% | -7.508% | -6.427% | -6.41% | -2.001% | -3.65% | -3.751% | -4.441% | -2.724% | -2.506% | -2.724% | -3.583% | -0.5365% | -1.344% | -2.27% | -2.657% | -10.55% | -11.64% | -10.34% | -9.563% | -8.057% | -8.464% | -9.759% | -9.403% | -10.65% | -9.206% | -7.75% | -7.632% | -7.453% | -5.754% | -6.553% | -7.287% | -9.822% | -5.496% | -6.318% | -8.046% | -8.687% | -7.889% | -9.083% | -7.268% | -9.139% | -12.68% | -11.21% | -12.62% | -6.259% | -8.433% | -9.706% | 0.482% | -0.1236% | 2.787% | 0.551% | -1.649% | -0.8512% | -3.09% | 0.2673% | -1.971% | -3.757% | -5.368% | -4.853% | -3.462% | -3.91% | -5.091% | 2.437% | 4.583% | 3.41% | 1.217% | 5.342% | 2.132% | 0.9036% | 2.998% | 0.3611% | -0.9357% | 3.663% | 0.8193% | -0.6142% | -5.099% | -2.485% | 1.003% | 1.892% | 0.1447% | -1.893% | 3.188% | -3.504% | -6.106% | -3.574% | 1.003% | 1.075% | -0.4839% | 6.285% | -1.879% | -3.098% | -2.73% | -2.14% | 1.164% | 1.249% | 1.563% | -3.86% | -0.4403% | -0.7369% | -1.051% | -0.6295% | 0.9726% | 5.143% | 3.326% | -0.1773% | -1.151% | -0.7689% | 1.764% | 1.548% | 0.8193% | -0.1696% | 1.578% | -3.175% | -1.457% | -2.776% | -0.6832% | -2.837% | -1.197% | -3.389% | -3.343% | 0.337% | 2.245% | -1.964% | -1.135% | -2.722% | -0.1389% | -0.5069% | 1.141% | -1.465% | 0.5586% | -5.367% | 1.026% | -1.831% | -1.867% | -0.9749% | -2.086% | -0.3507% | -4.278% | -3.818% | -1.787% | -0.2156% | -5.283% | -5.083% | -5.367% | -2.339% | -3.734% | -0.8442% | -5.145% | -3.182% | -4.359% | 3.872% | 6.719% | 5.913% | 5.77% | 5.35% | 5.09% | 4.888% | 4.653% | 4.502% | 5.056% | 6.282% | 6.198% | 7.18% | 6.474% | 8.118% | 2.381% | 6.5% | 5.165% | 4.636% | 2.957% | 2.974% | 1.79% | 3.226% | 2.051% | 1.648% | 1.748% | -1.736% | -0.443% | 0.2593% | -1.222% | 1.37% | -0.1673% | 5.547% | 6.647% | 4.299% | 5.716% | 9.975% | 2.684% | 5.17% | 9.095% | 5.875% | 4.394% | 8.024% | 9.407% | 8.695% | 5.282% | 1.478% | 5.644% | 4.589% | 6.605% | 6.386% | 7.85% | 4.123% | 4.908% | 10.21% | 5.597% | 3.462% | 6.457% | 3.25% | 9.596% | -5.711% | -6.75% | -2.473% | -3.022% | -1.601% | -2.708% | -0.8948% | -2.841% | -1.784% | -2.56% | -2.473% | -1.697% | -2.841% | -3.073% | -3.472% | -3.214% | -1.714% | -0.3455% | -1.383% | -7.457% | -2.944% | -6.187% | -2.935% | -3.796% | -3.156% | -2.21% | -0.2915% | 1.934% | -2.55% | -3.962% | 0.09044% | 2.896% | 1.572% | 3.843% | 2.848% | 2.285% | 1.275% | -5.494% | -1.734% | 1.034% | 1.592% | 0.1966% | -0.5436% | -2.152% | -3.818% | 0.3272% | -4.785% | -1.399% | -0.1227% | -0.01612% | -3.405% | 1.082% | -1.273% | 7.567% | 6.853% | 5.879% | 6.777% | 2.546% | 4.494% | 6.433% | 4.133% | 3.864% | 5.182% | -1.81% | 4.133% | 3.385% | 5.284% | 5.055% | 4.835% | 4.077% | 3.722% | 3.528% | 2.904% | 2.433% | 1.872% | 1.927% | 2.028% | 1.144% | 1.329% | 4.817% | 2.053% | 2.311% | 2.446% | 1.59% | 8.713% | 1.508% | 10.06% | 7.032% | 5.546% | 4.591% | 4.649% | 3.266% | -2.16% | 1.279% | 7.58% | 9.271% | 6.75% | 7.97% | 5.554% | 4.475% | 5.828% | 3.495% | 4.035% | 4.345% | 0.2648% | 4.397% | 3.56% | 5.67% | 5.496% | 1.211% | 3.453% | 4.367% | 0.1486% | 3.071% | 1.95% | 2.665% | 1.718% | 2.731% | 0.3728% | 3.212% | 3.491% | 3.578% | 5.468% | 3.377% | 5.54% | 4.18% | 5.479% | 5.886% | 7.641% | 4.006% | 5.936% | 5.013% | 7.902% | 5.753% | 7.676% | 5.383% | 6.35% | 6.237% | 6.429% | 4.049%
2025-07-01 | -4.967% | -7.244% | -4.551% | -4.551% | -5.606% | -8.652% | -2.066% | -6.321% | -5.034% | -3.996% | -3.138% | -3.907% | -4.05% | -3.853% | -3.424% | -3.585% | -4.327% | -3.179% | -3.371% | -2.602% | 0.4381% | -0.6348% | -0.4917% | -0.7242% | -0.008938% | -0.2235% | -0.3129% | -0.7242% | 1.422% | 0.7957% | -0.2772% | -0.295% | -6.464% | -7.263% | -5.87% | -5.55% | -3.781% | -3.969% | -6.267% | -5.023% | -6.607% | -5.184% | -3.198% | -3.034% | -3.586% | -1.523% | -1.585% | -2.971% | -3.554% | -2.689% | -2.94% | -5.536% | -6.712% | -5.392% | -6.615% | -4.101% | -4.985% | -8.617% | -7.944% | -8.608% | -4.265% | -5.832% | -6.245% | 4.235% | 3.453% | 4.061% | 4.544% | 4.862% | 3.475% | 2.435% | 4.08% | 4.609% | 2.654% | 1.061% | 2.589% | 2.612% | 2.476% | 4.495% | 4.21% | 4.015% | 2.972% | 4.067% | 4.178% | 4.681% | 4.691% | 3.966% | 4.17% | 3.54% | 4.577% | 3.949% | 4.259% | -0.7092% | 2.304% | 1.938% | 3.282% | 2.744% | 2.332% | 1.465% | 2.524% | 1.854% | 2.263% | 3.958% | 0.3364% | 4.666% | 3.493% | 3.738% | 5.635% | 4.3% | 4.845% | 6.662% | 6.246% | 6.425% | 3.547% | 4.357% | 2.988% | 2.972% | 4.365% | 4.625% | 4.788% | 4.226% | 3.51% | 2.72% | 1.573% | 3.327% | 2.85% | 2.337% | 0.4066% | 2.549% | 1.514% | 1.897% | 0.1541% | 0.1785% | 1.783% | 1.742% | 0.5858% | 2.011% | 1.948% | 1.368% | -0.1704% | -1.198% | -0.4893% | -0.4405% | -0.0658% | -0.245% | -0.5463% | 0.8953% | -2.493% | 0.2789% | -0.1398% | -1.262% | -0.5581% | -0.1554% | 0.3887% | -1.19% | -0.2857% | -2.159% | 0.3577% | -0.2205% | -0.04137% | -1.638% | -0.807% | -1.125% | -0.3427% | 2.334% | 1.987% | -1.313% | -2.894% | -1.074% | -1.931% | -1.565% | -1.306% | -0.6638% | -0.1911% | 0.7456% | 1.343% | 0.2371% | -1.636% | -1.217% | 0.808% | -1.111% | 0.6147% | -0.3853% | 0.9953% | 0.7902% | 1.388% | 0.7723% | 0.7812% | 0.7099% | 0.8437% | 0.6385% | 0.2014% | 0.8615% | -0.4944% | 0.2639% | -0.0992% | -0.6799% | 0.6126% | -2.525% | -0.3042% | -1.197% | -2.771% | -2.574% | -1.038% | -2.588% | -1.543% | -0.5263% | -0.4874% | -3.206% | -2.785% | -2.179% | -3.436% | -2.536% | -1.855% | -2.123% | -0.3355% | -0.8018% | -0.5213% | -1.973% | -2.58% | -4.513% | -1.233% | -3.04% | -5.79% | -4.998% | -3.374% | -2.082% | -2.196% | -3.063% | -0.7894% | -1.456% | -0.8265% | -1.711% | -0.3818% | -2.267% | -0.1688% | -1.188% | -0.8265% | -1.808% | -4.332% | -1.579% | -4.552% | -2.038% | -0.6597% | -0.141% | -2.16% | -5.355% | -1.605% | -4.817% | -1.568% | -3.299% | -1.535% | -1.667% | -2.779% | -1.676% | -3.026% | -2.505% | -0.6086% | -0.5199% | -2.229% | 1.526% | 0.6749% | 1.494% | 0.9938% | -0.2848% | 0.7166% | 0.4401% | 1.116% | 1.679% | 1.232% | 0.8382% | -1.541% | -2.131% | -0.6521% | -2.163% | -0.9438% | -1.304% | -0.5115% | 0.1808% | 0.1622% | 2.726% | 2.824% | 2.235% | 2.654% | -0.3962% | 0.6742% | 2.922% | 0.7991% | 0.2103% | 2.663% | 1.97% | 1.736% | 2.405% | 2.711% | 2.486% | 2.561% | 3.133% | 3.879% | 4.079% | 4.258% | 3.775% | 2.427% | 2.083% | 2.065% | 2.334% | 1.832% | 2.864% | 1.931% | 2.458% | 1.793% | 0.9405% | 2.212% | -0.9304% | 4.443% | 2.118% | 1.659% | 1.041% | 1.924% | -0.2287% | -4.393% | 0.8443% | 0.9428% | 2.082% | 2.709% | 0.3972% | 0.4678% | 0.7677% | 1.209% | -1.711% | 2.736% | 0.9984% | -1.975% | 3.444% | 1.443% | 2.731% | 3.814% | -1.244% | 1.782% | 0.9971% | -1.164% | 0.9706% | 1.747% | 1.985% | 1.879% | 2.497% | 0.9618% | 2.156% | 2.36% | 2.365% | 1.205% | 1.925% | 2.805% | -0.1157% | 1.182% | 2.047% | 1.202% | 2.68% | 1.165% | 0.6759% | 0.4611% | 1.271% | 1.387% | 2.314% | 2.111% | 3.064% | 2.74% | 2.657%
2025-07-02 | -10.79% | -13.4% | -10.1% | -10.48% | -12.52% | -15.98% | -7.237% | -11.92% | -11.72% | -10.22% | -8.031% | -9.434% | -9.955% | -9.494% | -8.792% | -7.81% | -9.69% | -7.664% | -7.65% | -7.309% | -3.62% | -4.422% | -4.482% | -4.341% | -4% | -3.579% | -3.359% | -3.78% | -1.855% | -2.076% | -3.379% | -3.88% | -11.82% | -13.47% | -12.27% | -11.06% | -8.551% | -8.614% | -11.28% | -9.374% | -10.82% | -9.483% | -8.14% | -7.098% | -6.905% | -5.167% | -4.903% | -5.857% | -6.851% | -5.106% | -5.099% | -7.11% | -7.846% | -7.378% | -9.014% | -6.934% | -8.614% | -11.49% | -10.79% | -11.62% | -7.068% | -8.422% | -8.708% | -1.159% | -2.136% | -2.252% | -2.154% | -1.497% | -2.688% | -2.73% | -1.305% | -1.853% | -3.186% | -5.328% | -3.597% | -3.569% | -3.903% | 0.6038% | 1.27% | 1.38% | -0.9579% | 0.4379% | 0.686% | 0.5843% | 0.3024% | -3.053% | -0.7428% | -1.673% | -1.414% | -0.3734% | -0.5652% | -4.565% | -1.597% | 0.2933% | 0.9326% | 2.102% | 1.285% | 1.389% | 1.855% | -4.4% | -0.1413% | 0.7499% | -1.173% | 1.07% | 6.476% | -1.131% | 0.6221% | -2.127% | -0.8483% | 0.686% | -0.06287% | 1.079% | 0.713% | -0.8192% | -0.6565% | 1.535% | 1.133% | 1.727% | 2.595% | 2.019% | 0.2202% | 0.06498% | -0.4469% | 0.8898% | 1.873% | 1.891% | 0.202% | 3.197% | 0.7408% | 1.17% | -0.2364% | 0.275% | 1.334% | 1.736% | -0.08114% | 0.6221% | 2.274% | 0.7317% | -1.076% | -1.195% | -0.7021% | -0.3551% | 0.3207% | 1.188% | 0.138% | 2.549% | 1.873% | 2.599% | 1.322% | 0.6129% | 1.705% | 1.188% | 2.503% | -0.05374% | 0.7773% | 1.115% | 1.462% | 1.289% | 0.5581% | 1.654% | 1.188% | -0.556% | 2.439% | 1.033% | 2.211% | 1.348% | -1.638% | -0.4073% | -1.588% | -1.678% | -1.808% | -1.318% | -1.067% | -0.7274% | 0.893% | 0.07281% | -0.7274% | -0.1772% | 0.933% | -0.2378% | 0.753% | -1.153% | 1.113% | 0.4429% | 1.563% | 0.803% | 1.053% | 1.343% | 0.5829% | 1.283% | 0.0328% | 2.213% | 1.613% | 1.633% | 1.779% | 1.569% | 1.296% | -2.417% | -0.4906% | -3.141% | -1.41% | -1.242% | -0.1852% | -1.635% | -0.02303% | 0.8701% | 0.4828% | -2.022% | -3.779% | -0.4531% | -4.539% | -3.532% | -1.28% | -1.677% | 0.06819% | -1.59% | -0.3068% | -0.989% | -1.86% | -2.513% | 0.8172% | -1.052% | -4.049% | -2.77% | -2.44% | 0.1952% | 1.254% | 0.09274% | 2.478% | 2.374% | 3.558% | 1.446% | 4.285% | 1.426% | 3.319% | 1.917% | 2.395% | 2.592% | 0.1503% | 1.07% | -0.186% | 0.8329% | 1.803% | 1.689% | -0.8355% | -4.835% | 0.7537% | -4.173% | 1.242% | -2.432% | 0.7933% | -0.3047% | -0.3245% | -0.74% | -0.1564% | -0.374% | -0.03765% | 5.824% | 2.645% | 4.349% | 4.286% | 4.398% | 3.775% | 2.078% | 3.097% | 3.001% | 2.217% | 1.512% | 2.057% | 2.662% | 0.8374% | 1.219% | 1.418% | 0.6499% | 3.131% | 1.839% | 1.35% | 3.4% | 1.698% | 3.254% | 3.043% | 2.153% | 2.603% | -0.4573% | 0.743% | 2.973% | 1.353% | -0.2473% | 2.943% | 1.453% | 1.613% | 2.973% | 3.827% | 2.367% | 2.367% | 3.095% | 3.709% | 4.007% | 3.415% | 3.666% | 1.485% | 1.117% | 1.107% | 1.277% | 1.147% | 2.269% | 1.418% | 2.823% | 2.556% | 1.579% | 3.153% | 0.4737% | 6.274% | 3.919% | 2.149% | 2.089% | 4.026% | 3.192% | 1.951% | 4.871% | 3.496% | 5.511% | 5.393% | 4.414% | 3.553% | 5.136% | 4.849% | 3.207% | 6.273% | 4.877% | 2.665% | 8.783% | 8.565% | 8.648% | 9.001% | 7.204% | 9.874% | 8.836% | 6.046% | 8.044% | 8.252% | 8.964% | 8.143% | 9.093% | 7.253% | 7.796% | 7.401% | 7.668% | 7.095% | 8.212% | 9.115% | 7.949% | 9.815% | 10.29% | 9.24% | 9.602% | 9.123% | 8.062% | 8.752% | 9.222% | 9.063% | 9.749% | 9.402% | 10.91% | 9.375% | 8.7%
2025-07-03 | -1.816% | -4.272% | -1.714% | -1.974% | -2.768% | -5.664% | -0.05623% | -4.22% | -2.457% | -1.317% | -1.628% | -2.44% | -1.023% | -1.835% | -0.7295% | -1.576% | -2.307% | -2.489% | -2.82% | -2.025% | 0.8257% | -0.3493% | 0.29% | 0.03081% | -0.2802% | -0.07287% | 0.2554% | -0.1593% | 0.7911% | 0.5146% | -0.02103% | -0.003754% | -1.956% | -3.435% | -2.853% | -2.198% | -0.1611% | -1.071% | -1.87% | -1.071% | -1.991% | -0.8578% | 0.8843% | 1.123% | 1.256% | 3.251% | 1.677% | 0.09546% | -4.15% | -1.888% | 0.1986% | -2.562% | -4.65% | -5.427% | -6.748% | -3.848% | -5.101% | -7.661% | -7.653% | -9.383% | -3.667% | -5.55% | -2.594% | -1.138% | -1.547% | 3.347% | -0.7758% | -1.398% | -0.4008% | -2.791% | 0.814% | -1.618% | -1.886% | -3.839% | -3.963% | -0.2728% | -2.322% | -2.924% | -0.9411% | 3.419% | -2.657% | -1.984% | 1.129% | -0.1412% | -0.9568% | -1.367% | -1.655% | -2.545% | 3.435% | -0.7679% | -0.7679% | -4.837% | -0.9805% | -0.1068% | 1.987% | -0.642% | -1.871% | 3.057% | -0.4453% | -0.1823% | 0.6488% | -0.7916% | -2.399% | -1.161% | 4.568% | -1.177% | 0.0742% | -1.775% | 1.995% | 0.3497% | 0.2237% | -0.1226% | 3.519% | -2.544% | -1.461% | -1.445% | -1.531% | -0.5161% | 3.435% | 1.066% | -0.9017% | -1.838% | -2.511% | -0.3222% | 0.7117% | 3.049% | -0.28% | 2.231% | -3.601% | -0.5791% | -3.279% | 1.16% | -2.224% | -0.1777% | -2.484% | -1.413% | 2.459% | 5.159% | -0.727% | -0.004505% | 6.103% | -0.3744% | 1.027% | 6.386% | -0.3115% | 6.323% | 1.019% | 1.85% | -0.2714% | 3.907% | -0.365% | 0.4835% | 0.1746% | -3.609% | -3.523% | -2.24% | 1.058% | -2.106% | -2.35% | -3.641% | -3.837% | -3.027% | 4.568% | -2.557% | -1.783% | -1.935% | 5.493% | 5.269% | 4.054% | 4.071% | 3.39% | 4.114% | 4.554% | 5.261% | 4.985% | 3.899% | 5.062% | 5.381% | 5.329% | 5.509% | 5.959% | 2.92% | 4.864% | 4.002% | 4.511% | 4.002% | 3.89% | 4.338% | 4.2% | 4.605% | 3.976% | 4.786% | 3.433% | 4.554% | 4.287% | 3.672% | 4.839% | -1.508% | 1.165% | -0.3499% | -0.5101% | -0.1459% | 2.385% | -0.778% | 1.162% | 7.678% | 7.07% | 1.992% | 4.279% | 0.8301% | 7.817% | -0.4965% | -0.6885% | 0.2857% | 1.512% | -0.4048% | 1.578% | 0.607% | 1.475% | 3.178% | 8.694% | 4.215% | 2.128% | 5.487% | 0.8349% | 7.87% | 0.3972% | -0.8235% | 2.183% | 2.076% | 0.2051% | 0.1566% | 1.825% | 0.2248% | 3.616% | 2.237% | 2.515% | 0.796% | -1.489% | 2.024% | -0.8835% | 1.623% | 3.222% | 3.75% | 1.897% | -0.2441% | 2.425% | 0.2418% | 2.201% | 1.342% | 1.802% | 1.597% | -0.09069% | 3.371% | 0.813% | 2.151% | 2.475% | -2.565% | -2.692% | -2.419% | -3.128% | -1.959% | -1.815% | -4.389% | -4.895% | -0.5468% | -0.5273% | -1.952% | -1.279% | -0.6154% | -4.659% | -3.14% | -4.331% | -3.225% | -1.8% | -2.069% | -3.104% | -0.4479% | -1.58% | -0.8684% | -0.765% | -1.093% | -0.4115% | -3.334% | -1.903% | -0.6701% | -1.989% | -3.153% | -0.4288% | -3.279% | -1.325% | -0.6701% | -0.01198% | -0.2021% | -0.8447% | -0.5105% | -0.3804% | -0.08893% | 0.05811% | -0.5041% | -2.654% | -1.456% | -1.637% | -0.8501% | -1.248% | 0.01483% | -1.196% | -0.6012% | -0.1206% | -0.6546% | -2.212% | -2.489% | 0.5763% | -1.557% | -2.06% | -2.137% | -1.125% | -2.747% | -2.597% | -3.118% | -1.728% | -0.2514% | -0.5255% | -1.932% | -2.393% | -2.12% | -1.455% | -3.092% | -0.5249% | -1.827% | -2.104% | -0.135% | -1.684% | 0.5274% | 0.2768% | 1.359% | 3.2% | -4.149% | -1.011% | 0.7533% | 1.043% | 0.796% | 0.2759% | 0.5999% | -1.83% | -0.69% | -0.4573% | -0.2441% | -0.2217% | -0.03655% | 1.485% | 1.398% | 3.226% | 2.782% | 2.649% | 1.65% | 1.725% | 1.341% | 2.783% | 1.708% | 2.604% | 1.414% | 1.795% | 2.64% | 2.336% | 0.5722%
2025-07-04 | -6.518% | -8.375% | -6.617% | -6.116% | -6.225% | -9.177% | -4.259% | -8.099% | -5.506% | -4.657% | -5.354% | -5.855% | -4.265% | -4.635% | -3.655% | -4.091% | -5.44% | -4.637% | -5.463% | -4.766% | -1.978% | -2.718% | -2.065% | -1.498% | -2.413% | -2.304% | -1.978% | -2.108% | -1.215% | -1.433% | -2.108% | -2.239% | -4.069% | -5.715% | -5.463% | -4.064% | -2.826% | -3.651% | -3.807% | -3.147% | -3.611% | -2.789% | -1.537% | -0.898% | -0.4146% | 1.032% | 0.7327% | -0.3492% | -3.916% | -1.862% | -0.4809% | -3.169% | -4.467% | -4.513% | -6.334% | -3.901% | -5.856% | -8.457% | -8.757% | -9.241% | -5.441% | -5.888% | -3.39% | 0.6463% | 0.1601% | 1.507% | 0.557% | 0.5867% | 0.04755% | -1.209% | 1.311% | 0.4577% | -0.713% | -2.416% | -3.769% | -0.4217% | -1.874% | 0.5173% | 0.557% | 1.39% | -0.9611% | 0.1514% | 1.589% | 1.248% | 0.676% | 0.7712% | -0.0379% | -0.5785% | 1.757% | 0.3982% | 0.7852% | -4.037% | -1.279% | -0.2368% | 0.9042% | -0.1971% | -2.075% | 0.547% | -0.465% | -0.8677% | 0.3666% | 0.1799% | -1.654% | 0.3883% | 5.27% | -0.3558% | 1.926% | 0.1105% | 0.5272% | 2.69% | 2.422% | -3.025% | 3.06% | -0.4113% | -0.4749% | 1.767% | 0.4478% | 1.529% | 2.779% | 2.065% | 1.44% | 1.787% | 0.6778% | 1.808% | 4.208% | 4.952% | 1.837% | 4.932% | -0.1872% | 2.641% | 2.144% | 3.99% | 2.908% | 4.684% | 2.74% | 3.791% | 3.738% | 2.045% | -0.5047% | 2.095% | 1.946% | 0.9538% | 1.599% | 3.355% | 2.482% | 3.901% | 1.341% | 4.35% | 4.307% | 4.246% | 5.235% | 3.285% | 5.798% | 2.512% | 3.335% | 2.125% | 4.744% | 1.827% | -1.656% | 3.712% | 4.129% | 4.149% | 5.379% | 3.565% | 4.397% | 4.412% | -1.276% | 0.3103% | -0.5481% | -0.3308% | -0.4721% | -0.1243% | -0.1787% | 0.3538% | 1.191% | 0.7015% | 0.1039% | 0.6581% | 1.777% | 0.8645% | 2.462% | 0.06583% | 1.799% | 1.571% | 1.995% | 1.212% | 1.506% | 1.593% | 1.408% | 1.723% | 1.017% | 2.049% | 2.179% | 1.864% | 1.891% | 2.085% | 1.88% | 0.02107% | 2.39% | 1.776% | 0.49% | 0.4626% | 2.304% | -0.02758% | 1.503% | 2.537% | 2.17% | -0.4696% | -2.142% | 1.239% | 0.6491% | -0.4561% | 0.8282% | 0.6363% | 2.543% | -0.2909% | 2.761% | 2.402% | -2.303% | -0.2196% | 2.955% | 0.8985% | -1.037% | -0.2331% | -0.0343% | 2.638% | -0.1413% | -0.9312% | 2.397% | 1.878% | 3.288% | 1.368% | 4.338% | 1.669% | 2.498% | 1.663% | 2.137% | 1.404% | 1.1% | 1.261% | 0.6696% | 1.11% | 2.036% | 1.449% | 1.031% | -1.34% | 0.9636% | -1.577% | 1.449% | -2.297% | 0.6589% | 0.05705% | 0.7019% | 1.25% | 0.2075% | 0.08929% | 0.8846% | 0.8641% | -2.385% | 0.8061% | 0.2334% | 0.5303% | 1.496% | -0.9428% | 1.684% | 2.444% | 3.161% | 1.993% | 2.977% | 2.36% | -0.7266% | 1.452% | 0.4782% | 1.712% | 5.474% | 4.245% | 1.365% | 5.327% | 2.372% | 0.2669% | 0.2886% | -0.3525% | -0.1243% | -1.906% | -1.515% | 0.4081% | -0.9067% | -1.928% | 0.7776% | -1.378% | -0.2656% | 0.2777% | 1.275% | 0.2142% | -0.04827% | 0.1549% | 1.194% | 0.8162% | 0.7726% | 0.8817% | -0.8715% | 0.03117% | -0.4813% | 1.307% | 0.4019% | 0.9679% | 0.2056% | 0.4516% | 0.7504% | 0.3625% | -0.4131% | -3.021% | 1.024% | -0.706% | -1.458% | -1.663% | -0.2194% | -1.622% | -2.748% | -1.578% | -1.169% | -0.447% | 0.5622% | -0.6845% | -1.92% | -1.018% | -0.6523% | -1.856% | 0.02961% | -1.226% | -2.602% | 1.46% | 1.359% | 2.464% | 2.182% | -2.426% | -0.3084% | -3.79% | -3.296% | -1.061% | -0.835% | -0.3406% | -0.6093% | 0.4547% | -1.05% | 0.5912% | 1.223% | 0.5084% | 0.1244% | 0.4219% | 1.562% | -1.28% | 0.01406% | 0.1645% | 0.2527% | -0.131% | -0.2439% | -1.054% | -0.8645% | -0.3406% | -0.3341% | 0.9523% | 1.158% | 0.8169% | 1.11% | 0.8169%
2025-07-05 | -5.972% | -8.949% | -5.305% | -5.541% | -7.059% | -11.18% | -1.983% | -6.981% | -5.226% | -5.279% | -2.791% | -3.576% | -5.698% | -4.729% | -4.336% | -4.022% | -4.621% | -2.581% | -2.634% | -1.796% | 0.6136% | 0.06364% | 0.4565% | -0.4339% | -0.01492% | 0.3255% | 1.347% | 0.6398% | 1.294% | 1.294% | 1.137% | 1.164% | -8.421% | -9.941% | -8.205% | -7.075% | -4.759% | -4.676% | -7.452% | -5.31% | -7.007% | -7.022% | -5.933% | -6.05% | -4.635% | -3.475% | -3.085% | -4.032% | -5.171% | -1.796% | -2.455% | -4.293% | -5.15% | -3.835% | -4.723% | -3.602% | -4.706% | -8.514% | -6.512% | -7.643% | -2.372% | -3.122% | -6.205% | 1.569% | 0.5308% | 2.268% | 1.437% | 0.9364% | 1.559% | 0.3996% | 3.095% | 1.318% | 0.6382% | -1.171% | 0.2804% | 0.8605% | 0.7981% | 2.499% | 2.881% | 4.753% | 1.068% | 2.343% | 3.453% | 3.292% | 2.01% | 2.058% | 1.596% | 0.4483% | -14.34% | 2.07% | 1.938% | -4.193% | -2.833% | -0.6858% | -0.5188% | -0.8767% | -1.948% | 0.9841% | -0.7097% | -1.359% | -0.8729% | -0.02978% | -1.611% | -0.5188% | 4.324% | -0.4353% | 1.318% | 0.1611% | -0.7455% | 2.439% | 2.129% | 2.034% | 3.22% | 0.3742% | 2.093% | 4.109% | 2.881% | 4.813% | 6.447% | 5.541% | 4.384% | 4.157% | 3.666% | 5.462% | 6.006% | 5.04% | 4.109% | 6.447% | 3.775% | 4.384% | 2.928% | 5.016% | 2.666% | 3.549% | 1.318% | 1.581% | 1.708% | -1.306% | -3.451% | -3.274% | -2.368% | -2.058% | -1.509% | 0.6621% | -1.246% | 1.151% | -1.771% | 3.005% | 2.263% | 2.482% | 3.964% | 0.02987% | 3.403% | -0.1013% | 0.3877% | -2.463% | -1.974% | 1.759% | -1.509% | -2.01% | 0.8171% | 1.736% | 4.527% | 0.343% | 1.724% | 2.556% | -0.8165% | -0.32% | -1.927% | -2.254% | -3.847% | -4.083% | -4.331% | -3.403% | -2.358% | -2.985% | -0.2939% | -0.3331% | -1.613% | -0.4663% | 0.7926% | -2.556% | -1.653% | -1.94% | -1.77% | -2.149% | -2.045% | -1.509% | -1.966% | -1.548% | -2.645% | -1.548% | -0.5029% | -1.43% | -1.303% | -0.8504% | -0.8916% | -2.426% | 1.289% | -1.072% | 0.1116% | 1.019% | 4.834% | -1.495% | 1.09% | 4.572% | 3.06% | 1.146% | -0.2849% | 4.102% | 3.52% | 0.8241% | 1.75% | 2.537% | 1.75% | 2.522% | 2.85% | 3.77% | -1.404% | 1.9% | 6.33% | 3.504% | 0.3044% | 2.405% | 0.6551% | 4.679% | -3.763% | -4.33% | -1.017% | -1.153% | -0.5019% | -2.772% | 0.7191% | -2.41% | -0.7054% | -1.438% | -1.194% | -0.6783% | -2.255% | -2.514% | -1.596% | -1.893% | -0.8275% | -1.913% | -2.062% | -4.387% | -2.591% | -4.503% | -1.329% | -2.552% | -2.346% | -3.082% | -2.449% | -0.2913% | -3.638% | -3.263% | -2.863% | 6.042% | 3.652% | 5.714% | 4.784% | 4.407% | 4.452% | 3.338% | -5.611% | 5.635% | 5.785% | 4.169% | 5.08% | 3.191% | -2.536% | 2.091% | -0.3066% | 0.7213% | 3.499% | 2.956% | 1.432% | 4.92% | 4.599% | 1.783% | 2.254% | -1.444% | 1.431% | 0.9472% | 0.5683% | 3.142% | 2.776% | 1.444% | 4.958% | 1.545% | 4.004% | 4.148% | 5.665% | 3.237% | 3.32% | 3.375% | 4.125% | 3.835% | 3.389% | 3.756% | 0.3893% | 2.996% | 2.839% | 3.324% | 2.904% | 5.342% | 3.284% | 4.2% | 4.266% | 2.84% | 2.496% | -2.284% | 2.881% | 1.169% | 0.8457% | 1.027% | 3.69% | 2.036% | 2.525% | 0.9608% | 0.4206% | 1.302% | 2.861% | 1.595% | 0.4968% | 1.065% | 0.6648% | -0.3042% | 2.428% | 1.452% | 0.8954% | 3.582% | 3.636% | 1.886% | 3.744% | -2.966% | -0.6789% | -0.6143% | -2.888% | -0.5626% | -0.6919% | -0.1492% | 0.1867% | 0.8328% | -0.1233% | 1.927% | 1.479% | 1.052% | 0.8933% | 0.7055% | 1.601% | -2.468% | -1.041% | -0.2396% | 0.05431% | -0.3835% | -0.1104% | -1.407% | -0.9496% | -0.1363% | -0.5426% | 1.425% | 1.165% | 0.9226% | 1.18% | 0.5698%
2025-07-06 | -5.63% | -8.334% | -5.352% | -5.635% | -6.058% | -9.522% | -2.7% | -7.469% | -4.647% | -4.449% | -3.913% | -4.477% | -4.308% | -4.195% | -3.348% | -3.659% | -4.947% | -3.194% | -3.856% | -3.207% | -0.7229% | -1.231% | -1.062% | -0.977% | -1.824% | -1.231% | -0.4689% | -0.6665% | -0.4971% | -0.6382% | -0.977% | -1.259% | -5.606% | -7.205% | -6.403% | -5.392% | -3.699% | -4.144% | -5.437% | -3.877% | -5.38% | -4.483% | -2.714% | -2.572% | -1.673% | 0.02682% | -0.08049% | -0.9638% | -3.318% | -1.505% | -0.8386% | -3.295% | -4.698% | -4.11% | -5.485% | -3.732% | -4.444% | -8.181% | -7.444% | -8.299% | -4.251% | -4.653% | -4.199% | 1.265% | 0.6604% | 0.6644% | 0.8789% | 1.882% | 1.306% | 0.7246% | 2.808% | 2.319% | 1.29% | -0.1977% | 1.059% | 0.8941% | 1.109% | -3.763% | -2.683% | 1.239% | -3.801% | 0.9513% | 0.8147% | 1.512% | 1.02% | 0.08762% | 0.6119% | -0.2262% | 0.6732% | 0.8404% | 1.535% | -5.344% | -3.055% | -3.274% | -1.95% | -1.795% | -2.33% | -2.631% | -2.155% | -46.45% | -2.197% | -0.7282% | -3.829% | 0.2618% | -0.1625% | -0.1754% | 1.265% | 0.9689% | -0.1111% | 2.589% | 1.933% | 2.165% | 1.361% | 0.2624% | 0.6861% | 3.502% | 1.83% | 2.808% | 2.64% | 2.19% | 3.129% | 3.296% | 1.983% | 2.803% | 4.646% | 4.53% | 2.113% | 4.865% | -0.2654% | 3.296% | 2.422% | 3.553% | 3.348% | 4.35% | 2.64% | 3.965% | 5.572% | 5.006% | 3.313% | 2.666% | 3.026% | 3.708% | 4.016% | 4.132% | 3.502% | 5.122% | 4.222% | 5.451% | 4.426% | 3.73% | 4.907% | 3.913% | 6.022% | 3.425% | 3.438% | 4.402% | 1.213% | 1.239% | 3.566% | 3.605% | 3.643% | 4.338% | 5.135% | 4.056% | 5.199% | 4.47% | 1.601% | 3.417% | 2.136% | 2.474% | 1.854% | 1.911% | 1.812% | 2.798% | 3.657% | 2.713% | 3.544% | 3.967% | 4.15% | 3.576% | 4.405% | 2.857% | 3.826% | 3.713% | 3.952% | 2.924% | 3.502% | 3.136% | 3.727% | 3.713% | 3.079% | 3.643% | 2.53% | 2.629% | 2.629% | 2.171% | 3.31% | 2.606% | 5.307% | 5.011% | 4.053% | 4.641% | 6.677% | 3.498% | 5.531% | 6.798% | 6.116% | 3.641% | 5.05% | 5.136% | 4.132% | 1.059% | 4.46% | 5.377% | 5.377% | 1.664% | 5.905% | 5.468% | 3.352% | 3.068% | 7.12% | 4.895% | 2.483% | 2.94% | 4.377% | 6.719% | 0.7692% | 0.2241% | 2.979% | 2.818% | 2.555% | 1.153% | 4.105% | 1.877% | 3.724% | 2.862% | 3.008% | 3.33% | -1.062% | 1.222% | -1.173% | 1.222% | 4.163% | 4.558% | 3.125% | 1.612% | 2.759% | 0.5539% | 2.686% | 1.919% | 1.724% | 1.71% | 1.64% | 3.437% | 1.25% | 1.501% | 2.908% | 1.514% | -0.7544% | 1.106% | 1.131% | 1.765% | 2.401% | 2.44% | 2.187% | 3.428% | 3.878% | 2.86% | 4.013% | 3.609% | 0.5555% | 1.444% | 1.787% | 1.816% | 4.639% | 3.453% | 2.415% | 5.058% | 3.401% | -2.398% | -2.187% | -7.44% | -7.257% | -3.835% | -3.905% | -1.511% | -2.567% | -3.595% | -0.2017% | -1.127% | -1.539% | -0.4692% | 0.02714% | -2.013% | -2.191% | -1.687% | -1.078% | -0.6524% | -0.3698% | -0.0589% | -4.03% | -0.3132% | -1.359% | 1.425% | 0.4498% | -0.9194% | -0.2426% | -0.1031% | 0.4707% | 0.3524% | -3.236% | -5.036% | -2.309% | -3.332% | -3.694% | -3.722% | -2.161% | -4.101% | -1.145% | -3.02% | -5.02% | -4.201% | -1.41% | -3.206% | -4.39% | -4.042% | -3.541% | -5.922% | -1.103% | -4.041% | -4.465% | -1.35% | -0.9697% | -1.584% | -1.043% | -4.627% | -3.151% | -2.691% | -6.646% | -3.791% | -8.011% | -3.777% | -3.624% | -2.663% | -4.446% | -3.163% | -1.438% | -3.332% | -4.424% | -3.646% | -2.52% | -4.309% | -3.513% | -3.22% | -3.353% | -2.993% | -3.429% | -3.937% | -4.933% | -3.736% | -4.362% | -2.739% | -3.454% | -3.002% | -3.002% | -3.192%
Formulas:
Date = Inv_SY_B20[[#This Row],[Date]]
Date = [Date, row above]+1
Note on HS86: BEHERA PRAKASH KUMAR: Same ACCB inverter with faulty inverter so deviation is there.
Note on HT86: BEHERA PRAKASH KUMAR: Inverter internal Fault (Replaced Inverter)
Note on IL87: ADMIN: Sudden changes & instability in the power grid can lead to overvoltage conditions.
Note on IP91: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Modules are under water due to heavy rain
Note on IQ91: BEHERA PRAKASH KUMAR: Isolated Inverter Due to Water Logging issue near River Area.
Note on IR91: BEHERA PRAKASH KUMAR: Isolated Inverter Due to Water Logging issue near River Area.
Note on FO92: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Isolated Inverter Due to Water Logging issue near River Area.
Note on IN92: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Water level increase upto module due to heavy rain.
Note on IP92: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Water level increase upto module due to heavy rain.
Note on IQ92: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Isolated Inverter Due to Water Logging issue near River Area.
Note on IR92: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Isolated Inverter Due to Water Logging issue near River Area.

## LB (hidden)
FY | FY24
Month | 2025-02-01
2023-10-10
Sr. No. | Particular | Budgeted | Actual | Difference | Waterfall (MWh) | Waterfall (%) | 1
1 | Egrid_Target | #REF! | #REF! | #REF! | #REF! | #REF!
2 | POA | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Irradiationce Losses (IAM+NearShadding+Soiling) | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Temperature Loss |  |  | 0 | 0 | #REF!
6 | Mismatch+DC Ohmic_Inv Conversion losses |  |  | 0 | 0 | #REF!
7 | MPPT Mismatch Loss |  |  | 0 | 0 | #REF!
8 | AC Ohmic Loss |  |  | 0 | 0 | #REF!
9 | Clipping Loss |  |  | 0 | 0 | #REF!
10 | Plant Uptime | 99.5% | #REF! | #REF! | #REF! | #REF!
11 | Grid Uptime | 99.5% | #REF! | #REF! | #REF! | #REF!
13 | DC Unbalance Load | 0 | #REF! | #REF! | #REF! | #REF!
15 | PR Related | 0 | #REF! | #REF! | #REF! | #REF!
16 | Measured |  |  | #REF! | #REF! | #REF!
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## Curtailment records
Sr. No | Month | Date | Plant Name | Categoty | Equipment Name | Inverter No. | From | To | Duration in MIN | Total Breakdown Hrs. | Avg POA During BD time | Lost POA | Total POA | Net POA | Loss of Capacity in MWp | Estimated PR % (Pvsyst) | Loss of Generation kWh | Remark | Current Load befor Load Sheeding (AC MW) | Load to be maintain (AC Mw)
1 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
2 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
3 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
4 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
5 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
6 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
7 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
8 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
9 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
10 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
11 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
12 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
13 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
14 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
15 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
16 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
17 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
18 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
19 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
20 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
21 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
22 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
23 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
24 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
25 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
26 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
27 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
28 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
29 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
30 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
31 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
32 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
33 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
34 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
35 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
36 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
37 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
38 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
39 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
40 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
41 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
42 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
43 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
44 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
45 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
46 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
47 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
48 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
49 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
50 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
51 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
52 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
53 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
54 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
55 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
56 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
57 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
58 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
59 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
60 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
61 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
62 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
63 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
64 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
65 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
66 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
67 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
68 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
69 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
70 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
71 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
72 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
73 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
74 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
75 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
76 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
77 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
78 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
79 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
80 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
81 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
82 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
83 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
84 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
85 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
86 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
87 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
88 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
89 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
90 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
91 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
92 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
93 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
94 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
95 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
96 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
97 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
98 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
99 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
100 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
101 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
102 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
103 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
104 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
105 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
106 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
107 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
108 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
109 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
110 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
111 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
112 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
113 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
114 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
115 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
116 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
117 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
118 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
119 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
120 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
121 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
122 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
123 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
124 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
125 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
126 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
127 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
128 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
129 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
130 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
131 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
132 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
133 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
134 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
135 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
136 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
137 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
138 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
139 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
140 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
141 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
142 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
143 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
144 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
145 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
146 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
147 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
148 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
149 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
150 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
151 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
152 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
153 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
154 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
155 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
156 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
157 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
158 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
159 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
160 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
161 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
162 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
163 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
164 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
165 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
166 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
167 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
168 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
169 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
170 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
171 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
172 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
173 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
174 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
175 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
176 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
177 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
178 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
179 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
180 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
181 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
182 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
183 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
184 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
185 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
186 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
187 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
188 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
189 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
190 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
191 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
192 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
193 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
194 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
195 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
196 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
197 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
198 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
199 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
200 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
201 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
202 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
203 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
204 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
205 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
206 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
207 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
208 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
209 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
210 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
211 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
212 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
213 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
214 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
215 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
216 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
217 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
218 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
219 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
220 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
221 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
222 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
223 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
224 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
225 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
226 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
227 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
228 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
228 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
229 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
230 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
231 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
232 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
233 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
234 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
235 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
236 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
237 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
238 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
239 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
240 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
241 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
242 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
243 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
244 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
245 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
246 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
247 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
248 | [8 empty] | 0:00 | 0:00 |  |  |  | 0 |  |  | 0
[13 empty] | 157479.956 | 2.6247