## O2Summary
Performance Summary CEPPL
Month | 2025-07-01
Date | 2025-07-13
Operation Year | Year-3
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks | Top Generator | Generation (MWh) | Least Generator | Generation (MWh)
1 | E_Grid Daily (MWh) | 815.9832 | 772.4777 | -5.332% |  | KUD23 | 38.7017 | KUD03 | 29.8102
| E_Grid MTD(MWh) | 10607.7819 | 11580.7004 | 9.172% |  | KUD15 | 549.4658 | KUD04 | 477.346
| E_Grid YTD (MWh) | 53800.0519 | 51581.6934 | -4.123% |  | KUD15 | 2548.3695 | KUD04 | 2108.49
2 | Wind Speed Daily | 10.3038 | 8.0652 | -21.73%
| Wind Speed MTD | 10.3038 | 9.0609 | -12.06% |  |  |  |  | Last 7 Days Performance
| Wind Speed YTD | 8.1297 | 6.7127 | -17.43% |  | Energy Loss (MWh)
3 | MA Daily | 97% | 100% | 3.093% |  | 0
| MA MTD | 97% | 99.87% | 2.958% |  | 15.1293
| MA YTD | 97% | 99.65% | 2.735% |  | 150.6611
4 | EGA Daily | 99.5% | 100% | 0.5025% |  | 0
| EGA MTD | 99.5% | 100% | 0.5025% |  | 0
| EGA YTD | 99.5% | 99.15% | -0.3563% |  | 605.885
5 | IGA Daily | 99% | 100% | 1.01% |  | 0
| IGA MTD | 99% | 99.56% | 0.5632% |  | 38.816
| IGA YTD | 99% | 97.02% | -1.999% |  | 899.619
6 | CUF Daily | 67.19% | 63.61% | -5.332%
| CUF MTD | 67.19% | 73.35% | 9.172%
| CUF YTD | 42.6% | 40.84% | -4.123%
7 | Wind PA Daily | 95.55% | 100% | 4.657% |  | 0
| Wind PA MTD | 95.55% | 99.43% | 4.058% |  | 53.9453
| Wind PA YTD | 95.55% | 95.86% | 0.3228% |  | 1656.1651
8 | Line Loss Daily | 5% | 6.671% | -33.41%
| Line Loss MTD | 5% | 1.173% | 76.53%
| Line Loss YTD | 5% | 0.8415% | 83.17%
9 | Reactive Power Daily | 5% | 7.909% | -58.19%
| Reactive Power MTD | 5% | 6.688% | -33.75%
| Reactive Power YTD | 5% | 22.86% | -357.2%
10 | Expected Energy Daily | 775.97 | 775.9812 | 0.001443%
| Expected Energy MTD | 11645.55 | 11633.223 | -0.1059%
| Expected Energy YTD | 53192 | 52738.9876 | -0.8517%
Performance Summary CEPPL Customer wise
Month | 2025-07-01
Date | 2025-07-13
Operation Year | Year-3
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | SPV | MTD WTG Generation (MWh) | MTD E_Grid (MWh) | Remarks
1 | O2R1 (KSIPL) | 5063.132 | 5040.2726
2 | O2R2 (SIL) | 1082.4412 | 1077.5541
3 | O2R5 (JK) | 4003.714 | 3985.6377
4 | O2R4 (SGDCIPL) | 500.39 | 498.1308
4 | O2R16 (Jubilant) | 983.5458 | 979.1052

## AnnualKPI
Till Date | 2025-07-13 | 2025-07-01
CEPL Performance Summary-YTD
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA(%) | Measured IGA (%) | E_Grid | 33 KV Export | Line Loss | Expected Energy | Loss (%) | Reactive Power (%)
2026 | 104 | 8.1297 | 6.7127 | 53800.0519 | 52738.9876 | 42.6% | 41.76% | 99.5% | 99.15% | 97% | 99.65% | 99% | 97.02% | 117393.6 | 119969.6626 | -2.194% | 53192 | 0.8415% | 22.86%

## MonthlyKPI
Till Date | 2025-07-13 | 0 | 0 | 0 | 0
CEPL Performance Summary
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | E_Grid | 33 KV Export | Line Loss | E_WS_Corrected | Expected Energy | Loss (%) | Reactive Power (%)
2025-07-01 | 13 | 10.3038 | 9.0609 | 10607.7819 | 11633.223 | 67.19% | 73.69% | 99.5% | 100% | 97% | 99.87% | 99% | 99.56% | 18508.8 | 18592.365 | -0.4515% | 11645.55 | 11645.55 | 1.173% | 6.688%
Start Date | 2025-07-07 | [13 empty] | 31596.72
End Date | 2025-07-13
CEPL Performance Summary
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | E_WS_Corrected
2025-07-01 | 7 | 10.3038 | 8.5124 | 5711.8826 | 5697.4657 | 67.19% | 67.02% | 99.5% | 100% | 97% | 99.82% | 99% | 99.26% | 5704.79
Formulas:
Days = [Days, row below]-6

## Analytics
Start Date | 2024-03-01 | Hours | WS Median
End Date | 2025-03-31 | 9480 | 4.5765 | [21 empty] | o2re1 | o2re2 | o2re4 | o2re5 | o2re16
WTG No. | KUD01 | KUD02 | KUD03 | KUD04 | KUD05 | KUD06 | KUD07 | KUD08 | KUD09 | KUD10 | KUD11 | KUD12 | KUD13 | KUD14 | KUD15 | KUD16 | KUD17 | KUD18 | KUD19 | KUD20 | KUD21 | KUD22 | KUD23
Machine Availability - MA(%) | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.99% | 100% | 99.98% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.98% | 100% | 99.93% | 100% |  | 100% | 100% | 100% | 99.99% | 100%
WTG BD Hours | 0.4 | 0 | 0 | 0 | 0.35 | 0 | 0.33333 | 0.35 | 0.73333 | 0.33333 | 1.8167 | 0 | 0.33333 | 0 | 0 | 0 | 0 | 0.4 | 0 | 1.4333 | 0 | 6.3167 | 0.46667 |  | 43.17% | 0% | 40% | 98.33% | 34.17%
Internal Grid Availability - IGA (%) | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100%
METERING YARD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0% | 0% | 0%
FEEDER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0% | 0% | 0%
OG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0% | 0% | 0%
TRANSFER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0% | 0% | 0%
USS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0% | 0% | 0%
ROW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 |  | 0% | 0% | 0% | 50% | 0%
Major Breakdown | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0% | 0% | 0%
Externnal Grid Availability - EGA (%) | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100%
EGA including Curtailment order (%) | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100%
EGA (Energy Availability) (%) | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100%
External Grid | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 100% | 100% | 100% | 100% | 100%
Breakdown | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0% | 0% | 0%
Curtailment Order | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0% | 0% | 0%
Curtailment Order GA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 100% | 100% | 100% | 100% | 100%
Shutdown | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0% | 0% | 0% | 0%
Generation (MWh) | 25.785 | 25.012 | 20.727 | 21.839 | 20.474 | 21.168 | 20.4 | 21.499 | 20.279 | 20.235 | 20.857 | 24.677 | 20.481 | 19.298 | 24.364 | 24.713 | 25.87 | 20.397 | 20.804 | 21.926 | 24.323 | 19.273 | 23.974 |  | 219.154 | 50.583 | 20.397 | 176.342 | 41.899
Plant Availability - PA (%) | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.98% | 99.99% | 99.97% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.97% | 99.99% | 99.88% | 99.98% |  | 99.98% | 99.99% | 99.99% | 99.97% | 99.99%
Sum of BD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9833 | 0 | 1.9833 | 0% | 0% | 0% | 24.79% | 0%
Count of BD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0% | 0% | 0% | 12.5% | 0%
MTTR WTG (Hours) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9833 | 0 | 1.9833 | 0 | 0 | 0 | 1.9833 | 0
MTBF WTG (Hours) | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9480 | 9478.0167 | 9480 |  | 94800 | 18960 | 9480 | 75838.0167 | 18960
Wind Speed (m/s) | 4.709 | 4.6976 | 4.6241 | 4.3758 | 4.4243 | 4.4857 | 4.4803 | 4.5476 | 4.5765 | 4.401 | 4.5822 | 4.5946 | 4.412 | 4.3287 | 4.8206 | 4.7144 | 4.7879 | 4.4686 | 4.4595 | 4.5278 | 4.7895 | 4.5882 | 4.6878 |  | 4.546 | 4.7511 | 4.4686 | 4.5782 | 4.5139
CUF (%) | 0.1236% | 0.1199% | 0.09938% | 0.1047% | 0.09817% | 0.1015% | 0.09781% | 0.1031% | 0.09723% | 0.09702% | 0.1% | 0.1183% | 0.0982% | 0.09253% | 0.1168% | 0.1185% | 0.124% | 0.0978% | 0.09975% | 0.1051% | 0.1166% | 0.09241% | 0.115% |  | 0.1051% | 0.1213% | 0.0978% | 0.1057% | 0.1004%
Line loss (%)
Corelation (%)
Reactive Power
Day | 36006.1 | 36763 | 29810.2 | 31260.1 | 34751 | 30854.6 | 30933 | 33129 | 30556.5 | 31685.9 | 31661.7 | 31374.6 | 33264.2 | 31963.1 | 38271.5 | 38691 | 38191.8 | 34674.4 | 34397.7 | 31745.6 | 34487 | 32807.5 | 38701.7
MTD | 536936.6 | 526309.5 | 479105.2 | 477346 | 509797.8 | 486410.9 | 478073.7 | 505472.1 | 479890.7 | 495881.8 | 489725.6 | 497012.9 | 511966.1 | 492930.9 | 549465.8 | 539524.9 | 542916.3 | 500390 | 518261.3 | 491845.8 | 498010 | 493005.1 | 532944
YTD | 2479462.9 | 2406867.7 | 2217238.2 | 2108490 | 2236706.3 | 2210841.1 | 2190939.9 | 2332876.9 | 2216614.1 | 2238397.4 | 2213820.4 | 2299634.1 | 2316975.5 | 2215247.4 | 2548369.5 | 2485759.5 | 2464453.4 | 2202533.1 | 2308124.5 | 2185558.8 | 2264697 | 2226543.5 | 2368836.4
Day Rank | 6 | 5 | 23 | 19 | 7 | 21 | 20 | 12 | 22 | 16 | 17 | 18 | 11 | 14 | 3 | 2 | 4 | 8 | 10 | 15 | 9 | 13 | 1
MTD Rank | 4 | 6 | 21 | 23 | 9 | 19 | 22 | 10 | 20 | 14 | 18 | 13 | 8 | 16 | 1 | 3 | 2 | 11 | 7 | 17 | 12 | 15 | 5
YTD Rank | 3 | 5 | 15 | 23 | 13 | 19 | 21 | 7 | 16 | 12 | 18 | 10 | 8 | 17 | 1 | 2 | 4 | 20 | 9 | 22 | 11 | 14 | 6
| Enter Correct Hours | Total Hours YTD
| 2472 | 2472
Errors | Sum of Breakdown Time | Count of Error Text | MTTR | MTBF
Pause pressed on keyboard | 1364.9858 | 354 | 3.8559 | 3.1272
Arc light detected | 1029.7419 | 49 | 21.0151 | 29.4338
Pause over RCS __0 | 615.2583 | 139 | 4.4263 | 13.3579
Manual Stop | 315.7167 | 101 | 3.1259 | 21.3493
ExEx low voltage L_: ___V | 293.9319 | 95 | 3.094 | 22.927
New SERVICE state: _, ____ | 250.4119 | 15 | 16.6941 | 148.1059
YawUntwistCCW: Code__,_______° | 226.0783 | 615 | 0.36761 | 3.6519
UPS Error | 178.9808 | 114 | 1.57 | 20.1142
High temp. Gen bearing _:___°C | 144.1644 | 19 | 7.5876 | 122.5177
GeneratorBreakerFBResponse | 61.1656 | 29 | 2.1092 | 83.1322
Manually stop | 59.3944 | 20 | 2.9697 | 120.6303
YawUntwistCW: Code__,_______° | 55.3367 | 144 | 0.38428 | 16.7824
Yaw System Stopped | 53.4519 | 31 | 1.7243 | 78.0177
Low voltage L_: ___ V | 48.4333 | 26 | 1.8628 | 93.2141
ArcNetReconfigMaxLimit 10 | 45.0333 | 4 | 11.2583 | 606.7417
Manual stopped | 43.7397 | 12 | 3.645 | 202.355
Prop Valve B Status Fault | 37.1286 | 84 | 0.44201 | 28.9866
SyncVoltMeasurementMismatch | 34.4303 | 13 | 2.6485 | 187.5054
Yaw to cable twist | 34.2 | 82 | 0.41707 | 29.7293
Pitch pos C meas. signal fault | 33.35 | 26 | 1.2827 | 93.7942
BladeCEdgePeakLoad: ___.__ kNm | 29.1519 | 18 | 1.6196 | 135.7138
Not available | 28.3667 | 3 | 9.4556 | 814.5444
Thermoerror Waterpump | 27.25 | 13 | 2.0962 | 188.0577
Tow. acc. X Fault:__.__ m/s^2 | 25.9167 | 3 | 8.6389 | 815.3611
SignalError-PAUSE _____,_____ | 25.7303 | 16 | 1.6081 | 152.8919
ArcNetReconfigMaxLimit________ | 24.8667 | 21 | 1.1841 | 116.5302
Estop button activated | 24.6333 | 2 | 12.3167 | 1223.6833
YawSignals Invalid | 22.2386 | 51 | 0.43605 | 48.0345
Grid Converter CB Open | 20.95 | 4 | 5.2375 | 612.7625
Low oil Hydraulics | 20.7167 | 2 | 10.3583 | 1225.6417
High temp gear bearing | 20.1667 | 5 | 4.0333 | 490.3667
TripHVButtonActivated__ | 19.9128 | 14 | 1.4223 | 175.1491
Extr low Voltage | 17.25 | 2 | 8.625 | 1227.375
Ch hardware error C0 | 16.9511 | 24 | 0.7063 | 102.2937
Pitch pos B meas. signal fault | 16.8194 | 14 | 1.2014 | 175.37
Ch hardware error C_ | 16.2797 | 32 | 0.50874 | 76.7413
VibrShockAct X _.__Y _.__m/s^2 | 15.8656 | 8 | 1.9832 | 307.0168
Extr. low voltage L3 | 15.5667 | 3 | 5.1889 | 818.8111
SafetySystem Reset Required | 15.4167 | 8 | 1.9271 | 307.0729
High temp. Gen bearing 1: 95Â°C | 14.4261 | 3 | 4.8087 | 819.1913
GeneratorBreakerUnexpectedFb | 13.6903 | 8 | 1.7113 | 307.2887
OutOfMemory | 13.3667 | 14 | 0.95476 | 175.6167
Grid inv. HW error L_ | 12.9 | 4 | 3.225 | 614.775
Signal Error | 12.5833 | 4 | 3.1458 | 614.8542
ExEx low voltage L3: 1V | 12.4333 | 34 | 0.36569 | 72.3402
Gear box bear c temp differ | 12.2833 | 2 | 6.1417 | 1229.8583
Yaw motor thermo error | 12.0333 | 2 | 6.0167 | 1229.9833
Leak current 2004A | 11.95 | 1 | 11.95 | 2460.05
GenBreakerOpen,US12___UL12___ | 11.9333 | 8 | 1.4917 | 307.5083
Frequency error 1 | 11.3331 | 2 | 5.6665 | 1230.3335
SafetySystem Hub Pending | 11.0167 | 4 | 2.7542 | 615.2458
GeneratorBreakerTripped | 10.6022 | 5 | 2.1204 | 492.2796
Pitch pos A meas. signal fault | 10.55 | 3 | 3.5167 | 820.4833
SafetySystem Hub Error | 10.5417 | 2 | 5.2708 | 1230.7292
Leakage Current | 10.4 | 4 | 2.6 | 615.4
Pitch valves test active | 8.8711 | 54 | 0.16428 | 45.6135
Yaw To Cable Twist Reset | 8.7975 | 30 | 0.29325 | 82.1068
Pause over RCS 13 | 8.7025 | 6 | 1.4504 | 410.5496
Internal sublogic error | 8.6147 | 35 | 0.24613 | 70.3824
HubSafty HydrPres Low DBlk | 8.3664 | 83 | 0.1008 | 29.6823
Frequency error 1: ___.__ Hz | 7.9611 | 8 | 0.99514 | 308.0049
Low voltage L3: 2 V | 7.1425 | 5 | 1.4285 | 492.9715
Overtemp charging DC, ____V | 6.1167 | 1 | 6.1167 | 2465.8833
ExEx low voltage L2: 1V | 5.95 | 15 | 0.39667 | 164.4033
YawUntwistCCW: Code 6 | 5.7667 | 15 | 0.38444 | 164.4156
HubSafetySystem Batt.Level Err | 5.75 | 3 | 1.9167 | 822.0833
Yaw To Nacelle Position Reset | 5.5889 | 17 | 0.32876 | 145.083
GearOilTempLow ___°C | 5.5558 | 3 | 1.8519 | 822.1481
Ambient temperature high: __°C | 5.3061 | 8 | 0.66326 | 308.3367
HubSafty HydrPres Low BldA | 5.0272 | 3 | 1.6757 | 822.3243
StatorFilter Thermo Fault | 4.9167 | 1 | 4.9167 | 2467.0833
Pitch C too low: __._° < __._° | 4.75 | 8 | 0.59375 | 308.4062
BladeBEdgePeakLoad: ___.__ kNm | 4.5167 | 1 | 4.5167 | 2467.4833
pitch pos Cmeans signal fault | 4.4 | 1 | 4.4 | 2467.6
HydrOilExtremeHighTemp_____°C | 4.3 | 2 | 2.15 | 1233.85
YawUntwistCCW: Code 6, 540Â° | 4.0842 | 10 | 0.40842 | 246.7916
Ch High res. load C_ Load:___% | 4.0761 | 7 | 0.5823 | 352.5606
RotorTachSpdSigErr._____,_____ | 3.9667 | 1 | 3.9667 | 2468.0333
Pitch A BL unlock alarm N= ___ | 3.8444 | 6 | 0.64074 | 411.3593
RT AGO2Sta.Cyc. Count_,____V | 3.7078 | 3 | 1.2359 | 822.7641
YawToCableTwistResetNotAvail | 3.6833 | 7 | 0.52619 | 352.6167
Blade load sensor Fault detucted | 3.4667 | 1 | 3.4667 | 2468.5333
PitAPFBsensorunavailable | 3.4467 | 1 | 3.4467 | 2468.5533
Gear HSBearB Temp:___°C | 3.2833 | 2 | 1.6417 | 1234.3583
Pitch accu. test active | 3.1847 | 50 | 0.063694 | 49.3763
EMC valves test active | 3.1803 | 9 | 0.35336 | 274.3133
Ext. low DC voltage ____V | 3.1775 | 3 | 1.0592 | 822.9408
ArcNetReconfigMaxLimit 11 | 3.1389 | 4 | 0.78472 | 617.2153
Hub BallValve B Open | 3.0833 | 1 | 3.0833 | 2468.9167
HubSafty HydrPres Draind-BldC | 3.0761 | 2 | 1.5381 | 1234.4619
Hub BallValve C Open | 3.0703 | 1 | 3.0703 | 2468.9297
Pause over RCS 14 | 3.0128 | 1 | 3.0128 | 2468.9872
PitchB pos:__._° vel:___._°/s | 3.0083 | 3 | 1.0028 | 822.9972
Frequency error 1: 0.56 Hz | 2.95 | 7 | 0.42143 | 352.7214
Low voltage L3: 1 V | 2.8961 | 4 | 0.72403 | 617.276
ExtHighIRotorInv phase: _ | 2.8906 | 10 | 0.28906 | 246.9109
Rotor:__._RPM, Gen.:____._ RPM | 2.8514 | 23 | 0.12397 | 107.3543
PrevCabTwCode:_ CabTwCode:_ | 2.8267 | 5 | 0.56533 | 493.8347
Hub panel 24V supply missing warning inspection | 2.7833 | 2 | 1.3917 | 1234.6083
HubSafetyOptiStopConfig.Err __ | 2.6333 | 2 | 1.3167 | 1234.6833
Auto reclosing RTOP inspection | 2.6167 | 1 | 2.6167 | 2469.3833
SupplyError: Min 2V phase2 | 2.5333 | 1 | 2.5333 | 2469.4667
Ext. High cur. Grid inv. L_ | 2.4128 | 2 | 1.2064 | 1234.7936
Extreme yawerror __._m/s___._° | 2.3922 | 40 | 0.059806 | 61.7402
UDC Discharge Failed | 2.3833 | 5 | 0.47667 | 493.9233
High cur.grid inv. L1:2158A | 2.3167 | 1 | 2.3167 | 2469.6833
GenerLubrErr:MissLubrTime___s | 2.3167 | 2 | 1.1583 | 1234.8417
ExEx low voltage L1: 2V | 2.2 | 2 | 1.1 | 1234.9
BrakeHotLowBrakePressure 0bar | 2.1539 | 1 | 2.1539 | 2469.8461
Pause over RCS 12 | 2.065 | 2 | 1.0325 | 1234.9675
High windspeed: __._ m/s | 2.0414 | 8 | 0.25517 | 308.7448
Gear HSBearA Temp:___°C | 2 | 2 | 1 | 1235
Extreme yawerror | 2 | 7 | 0.28571 | 352.8571
High cur.grid inv. L_:____A | 1.95 | 4 | 0.4875 | 617.5125
SupplyError: Min 1V phase1 | 1.9456 | 1 | 1.9456 | 2470.0544
Ext. low DC voltage 469V | 1.8667 | 1 | 1.8667 | 2470.1333
Thermoerror Int.Gen.Fan F___A | 1.7903 | 6 | 0.29838 | 411.7016
Safety System Fault | 1.7667 | 1 | 1.7667 | 2470.2333
Too many auto-restarts: 83 | 1.7311 | 1 | 1.7311 | 2470.2689
Too many auto-restarts: 116 | 1.6667 | 1 | 1.6667 | 2470.3333
Ext. High cur. Grid inv. L1 | 1.5333 | 1 | 1.5333 | 2470.4667
MainShaftSigError._____,_____ | 1.4333 | 1 | 1.4333 | 2470.5667
YawUntwistCCW: Code 6, 561Â° | 1.3 | 3
GearOilInletPressLow 3.4 bar | 1.2667 | 1
Too many auto-restarts: 80 | 1.1483 | 1
HubSafty HydrPres Low BldC | 1.1225 | 3
YawUntwistCCW: Code 5 | 1.1167 | 3
Too many auto-restarts: 5470 | 1.1119 | 1
SupplyError: Min 2V phase3 | 1.1 | 1
PowerSupplyLowFreq: Min___ Hz | 1.1 | 5
YawUntwistCW: Code 3 | 1.1 | 3
WatchdogReboot | 1.0667 | 3
Low voltage L3: 3 V | 1.0347 | 1
Frequency error 3: 0.47 Hz | 0.98333 | 1
Error on all wind sensors | 0.97889 | 4
DC Undervoltage: ____V | 0.93139 | 1
SaftySystem Nacelle Comm Err. | 0.85 | 1
Brake Low Pressure and Hot | 0.83333 | 1
YawUntwistCCW: Code 6, 550Â° | 0.81972 | 2
YawUntwistCCW: Code 7, 517Â° | 0.76722 | 1
YawUntwistCCW: Code 7, 112Â° | 0.75 | 1
GridInverterContactorFBError | 0.73333 | 2
ArcNetReconfigMaxLimit 12 | 0.71667 | 1
YawUntwistCCW: Code 6, 546Â° | 0.71417 | 2
YawUntwistCCW: Code 7 | 0.66667 | 1
RT Dip exc.lim.:___%:_____e-2s | 0.65 | 1
Blade loads calib. Active | 0.55306 | 4
YawUntwistCCW: Code 6, 717Â° | 0.55 | 1
Yaw To Nac Pos Reset Not Allwd | 0.51667 | 2
Incorrect Error Code | 0.50056 | 8
No space in Warning Log | 0.5 | 1
Generator FB no response | 0.5 | 1
YawUntwistCCW: Code 6, 564Â° | 0.46667 | 1
YawUntwistCCW: Code 6, 619Â° | 0.46667 | 1
Frequency error 1: 0.44 Hz | 0.45 | 1
YawUntwistCCW: Code 5, 540Â° | 0.45 | 1
Generator Bearing Temp 1 high 95 degree | 0.43333 | 1
PtchValCErr,VeloctyC___._mm/s | 0.43333 | 1
YawUntwistCCW: Code 6, 626Â° | 0.43333 | 1
ExEx low voltage L3: 2V | 0.4 | 2
YawUntwistCCW: Code 6, 547Â° | 0.38333 | 1
PowerSupplyLowFreq: Min 47 Hz | 0.37 | 1
YawUntwistCCW: Code 6, 573Â° | 0.36944 | 1
YawUntwistCCW: Code 6, 557Â° | 0.36667 | 1
YawUntwistCCW: Code 6, 555Â° | 0.36306 | 1
Prop Valve C Status Fault | 0.33333 | 1
Extr. low voltage L_: ___V | 0.26667 | 2
Pitch C ref:__._°, Act.:__._° | 0.25361 | 2
DODP Leak Failure | 0.25 | 8
ExEx low voltage L2: 4V | 0.2 | 1
Frequency error 3: 0.54 Hz | 0.2 | 1
Remote Reboot | 0.17222 | 1
HubSafetySystem Speed Err.:_ | 0.17194 | 2
HydrMainPressLow:____bar____°C | 0.15722 | 1
Max. Yaw error: ___._° | 0.15694 | 8
HighIStrikesorber | 0.15 | 1
GearOilInletPressLow 1.1 bar | 0.14194 | 1
EMC Valves Unexpected Open | 0.13694 | 1
HydPressOscBlBFilt2, 8.3bar | 0.13333 | 1
Max generator RPM: ____._ RPM | 0.11722 | 1
Slip:____ above limits _ | 0.10028 | 1
Tow. acc. X, Alarm:__.__ m/s^2 | 0.083889 | 2
ExEx low voltage L3 | 0.083333 | 1
Blade loads calib. Active | 0.083333 | 1
High cur.rotor inv. L_:____A | 0.069444 | 2
Pitch C BL unlock alarm N= ___ | 0.035 | 1
HydPressOscBlAFilt3, 15.0bar | 0.033333 | 1
Generator Disc timeout | 0.033333 | 1
Tow. acc. X, Alarm: 0.24 m/s^2 | 0.033333 | 1
Asym.currL1:____A,Others:____A | 0.016667 | 1
Extreme yawerror 15.4m/s 45.0Â° | 0.016667 | 1
Turbine OK |  | 1
Yaw system stopped | -5.3833 | 1
Gen Stator CB Open | #REF! | 114
Pitch valves test acitve | #REF! | 123
Ext. High I sum Grd inv. | #REF! | 160
Prop Valve A Status Fault | #REF! | 38
GenSpd:__._RPM, Ref:____._ RPM | #REF! | 3
Prop Valve C Status Fault | #REF! | 93
Low oil-level, hydraulic | #REF! | 6
Ext. High I sum Rotinv.ChanX | #REF! | 18
HVCB Unknown Trip Reason | #REF! | 54
HubSafetySystem Batt.Charg.Err | #REF! | 102
Grand Total | #REF! | 3703
This shape represents a slicer. Slicers are not supported in this version. Please update to the latest version of WPS Office.
This shape represents a slicer. Slicers are not supported in this version. Please update to the latest version of WPS Office.
This shape represents a slicer. Slicers are not supported in this version. Please update to the latest version of WPS Office.
This shape represents a slicer. Slicers are not supported in this version. Please update to the latest version of WPS Office.
This shape represents a slicer. Slicers are not supported in this version. Please update to the latest version of WPS Office.
This shape represents a slicer. Slicers are not supported in this version. Please update to the latest version of WPS Office.
This shape represents a slicer. Slicers are not supported in this version. Please update to the latest version of WPS Office.
This shape represents a slicer. Slicers are not supported in this version. Please update to the latest version of WPS Office.
This shape represents a slicer. Slicers are not supported in this version. Please update to the latest version of WPS Office.

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 11.4833 | [6 empty] | 4.6282 | 4.8999 | [9 empty] | 161352 |  |  |  | 50.6 | 5.9682 | 280595.0066 |  | 23.11% | 95.55% | 99.5% | 0 | [5 empty] | 0.311% | 5% | 5% | Pass@123
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 11.45 | [6 empty] | 4.394 | 4.6498 | 100% | 100% | 100% | 100% |  |  |  |  | 12.91% | 156753 | 154605 | 0 | 154605 | 50.6 | 5.9682 | 280595.0066 |  | 23.11% | 95.55% | 99.5% | 0 |  |  |  |  | 0.7463% | 0.7308% | 5% | 5% | 50.6
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 11.5333 | [6 empty] | 4.6844 | 5.0214 | 100% | 100% | 100% | 100% |  |  |  |  | 15.67% | 190270 | 186780 | 0 | 186780 | 50.6 | 5.9682 | 280595.0066 |  | 23.11% | 95.55% | 99.5% | 0 |  |  |  |  | 1.014% | 0.4708% | 5% | 5% | 50.6
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 11.6 | [6 empty] | 4.9658 | 5.2483 | 100% | 100% | 100% | 100% |  |  |  |  | 24.01% | 291613 | 287760 | 446.8323 | 287313.1677 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 292.87 |  |  |  |  | 0.9317% | 0.5258% | 5% | 5% | 50.6
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 10.9833 | [6 empty] | 4.7846 | 5.1333 | 100% | 100% | 100% | 100% |  |  |  |  | 17.3% | 210106 | 204765 | 0 | 204765 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 210.58 |  |  |  |  | 0.7562% | 0.4365% | 5% | 5% | 50.6
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 11.6 | [6 empty] | 4.1397 | 4.4785 | 92.66% | 100% | 92.66% | 100% |  |  |  |  | 10.61% | 128895 | 128535 | 248.617 | 128286.383 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 133.1 |  |  |  |  | 0.8221% | 1.079% | 5% | 5% | 50.6
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 11.4667 | [6 empty] | 4.3539 | 4.7729 | 92.96% | 100% | 92.96% | 100% |  |  |  |  | 13.71% | 166543 | 164340 | 0 | 164340 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 168.01 |  |  |  |  | 0.7612% | 1.054% | 5% | 5% | 50.6
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 11.6833 | [6 empty] | 4.7085 | 4.9534 | 100% | 100% | 100% | 100% |  |  |  |  | 14.99% | 181999 | 176880 | 0 | 176880 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 182.18 |  |  |  |  | 0.9036% | 0.4226% | 5% | 5% | 50.6
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 11.5167 | [6 empty] | 4.4631 | 4.7009 | 100% | 100% | 100% | 100% |  |  |  |  | 13.04% | 158302 | 157245 | 0 | 157245 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 159.01 |  |  |  |  | 1.003% | 0.681% | 5% | 5% | 50.6
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 11.2333 | [6 empty] | 3.92 | 4.512 | 100% | 100% | 100% | 100% |  |  |  |  | 10.89% | 132189 | 133815 | 242.4185 | 133572.5815 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 133.9 |  |  |  |  | 0.6567% | 1.16% | 5% | 5% | 50.6
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 11.6 | [6 empty] | 4.5 | 4.9 | 100% | 100% | 100% | 100% |  |  |  |  | 18.15% | 220355 | 215655 | 0 | 215655 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 228.59 |  |  |  |  | 1.017% | 0.9196% | 5% | 5% | 50.6
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 11.5833 | [6 empty] | 3.652 | 3.922 | 100% | 100% | 100% | 100% |  |  |  |  | 11.69% | 142019 | 141240 | 240.6133 | 140999.3867 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 144.28 |  |  |  |  | 1.003% | 4.081% | 5% | 5% | 50.6
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 11.8167 | [6 empty] | 6.2826 | 7 | 98.21% | 100% | 98.21% | 100% |  |  |  |  | 29.28% | 355613 | 348150 | 0 | 348150 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 380.75 |  |  |  |  | 0.7148% | 1.341% | 5% | 5% | 50.6
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 11.2833 | [6 empty] | 6.3011 | 6.7293 | 100% | 100% | 100% | 100% |  |  |  |  | 35.61% | 432425 | 419100 | 570.9809 | 418529.0191 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 432.78 |  |  |  |  | 0.6471% | 19.53% | 5% | 5% | 50.6
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 11.65 | [6 empty] | 6.4485 | 6.9491 | 100% | 100% | 100% | 100% |  |  |  |  | 33.22% | 403479 | 386430 | 0 | 386430 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 407.49 |  |  |  |  | 0.8584% | 9.23% | 5% | 5% | 50.6
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 11.5 | [6 empty] | 4.1157 | 4.4312 | 100% | 100% | 100% | 100% |  |  |  |  | 9.253% | 112367 | 109065 | 192.6943 | 108872.3057 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 113.37 |  |  |  |  | 1.064% | 11.44% | 5% | 5% | 50.6
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 11.7 | [6 empty] | 4.3424 | 5.1542 | 96.12% | 100% | 96.12% | 100% |  |  |  |  | 12.1% | 146931 | 144045 | 0 | 144045 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 151.65 |  |  |  |  | 0.5481% | 14.2% | 5% | 5% | 50.6
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 11.7 | [6 empty] | 5.1282 | 5.6831 | 96.85% | 100% | 96.85% | 100% |  |  |  |  | 20.17% | 244886 | 236115 | 0 | 236115 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 246.29 |  |  |  |  | 1.019% | 13.83% | 5% | 5% | 50.6
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 11.8167 | [6 empty] | 5.28 | 6.1219 | 90.14% | 100% | 90.14% | 100% |  |  |  |  | 17.27% | 209670 | 204270 | 0 | 204270 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 216.2 |  |  |  |  | 0.9237% | 15.61% | 5% | 5% | 50.6
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 11.8667 | [6 empty] | 5.1848 | 5.7761 | 96.45% | 100% | 96.45% | 100% |  |  |  |  | 18.09% | 219726 | 212520 | 0 | 212520 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 220.44 |  |  |  |  | 0.5859% | 18.93% | 5% | 5% | 50.6
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 10.8167 | [6 empty] | 5.4003 | 5.7738 | 97.57% | 100% | 97.57% | 100% |  |  |  |  | 21.01% | 255128 | 248160 | 0 | 248160 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 256.23 |  |  |  |  | 0.7053% | 22.07% | 5% | 5% | 50.6
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 11.8667 | [6 empty] | 5.414 | 6.0562 | 97.32% | 100% | 97.32% | 100% |  |  |  |  | 21.75% | 264166 | 254265 | 0 | 254265 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 265.03 |  |  |  |  | 1.073% | 9.707% | 5% | 5% | 50.6
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 11.3833 | [6 empty] | 5.4143 | 6.2723 | 96.32% | 100% | 96.33% | 89.66% |  |  |  |  | 18.16% | 220582 | 210210 | 0 | 210210 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 220.06 |  |  |  |  | 0.9615% | 12.39% | 5% | 5% | 50.6
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 11.7833 | [6 empty] | 4.1889 | 4.6774 | 96.27% | 100% | 96.27% | 96.81% |  |  |  |  | 9.696% | 117746 | 116160 | 0 | 116160 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 130.46 |  |  |  |  | 0.7743% | 85.66% | 5% | 5% | 50.6
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 11.7 | [6 empty] | 4.1137 | 4.603 | 96.12% | 100% | 96.13% | 98.13% |  |  |  |  | 8.451% | 102627 | 99825 | 181.1706 | 99643.8294 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 106.17 |  |  |  |  | 0.8394% | 15.98% | 5% | 5% | 50.6
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 11.7167 | [6 empty] | 4.294 | 5.387 | 96.26% | 100% | 96.27% | 100% |  |  |  |  | 10.64% | 129253 | 125235 | 0 | 125235 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 130.34 |  |  |  |  | 0.8305% | 10.97% | 5% | 5% | 50.6
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 11.7667 | [6 empty] | 4.3586 | 5.1147 | 96.61% | 100% | 96.61% | 100% |  |  |  |  | 12.07% | 146618 | 142230 | 239.8482 | 141990.1518 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 148.16 |  |  |  |  | 0.9941% | 25.66% | 5% | 5% | 50.6
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 11.7333 | [6 empty] | 4.8209 | 5.616 | 93.07% | 100% | 93.07% | 100% |  |  |  |  | 16.16% | 196249 | 189420 | 0 | 189420 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 197.44 |  |  |  |  | 0.9534% | 30.27% | 5% | 5% | 50.6
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 11.8 | [6 empty] | 3.9119 | 4.9561 | 78.17% | 100% | 78.17% | 100% |  |  |  |  | 7.071% | 85870 | 83820 | 173.1818 | 83646.8182 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 82.27 |  |  |  |  | 0.9317% | 97.47% | 5% | 5% | 50.6
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 11.4333 | [6 empty] | 4.3602 | 5.1667 | 85.79% | 100% | 85.79% | 98.72% |  |  |  |  | 12.1% | 146977 | 142065 | 0 | 142065 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 148.97 |  |  |  |  | 1.091% | 81.18% | 5% | 5% | 50.6
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 11.95 | [6 empty] | 3.2192 | 3.523 | 93.25% | 100% | 93.25% | 100% |  |  |  |  | 3.609% | 43832 | 43890 | 83.7595 | 43806.2405 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 45.94 |  |  |  |  | 0.6679% | 191.4% | 5% | 5% | 50.6
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 11.8333 | [6 empty] | 4.4261 | 5.0233 | 95.83% | 100% | 95.83% | 100% |  |  |  |  | 11.72% | 142385 | 138930 | 249.4255 | 138680.5745 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 147.48 |  |  |  |  | 1.083% | 39.44% | 5% | 5% | 50.6
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 12.0667 | [6 empty] | 5.9632 | 6.599 | 100% | 100% | 100% | 100% |  |  |  |  | 28.29% | 343576 | 333135 | 0 | 333135 | 50.6 | 5.6311 | 273284.3333 |  | 22.5% | 95.55% | 99.5% | 334.67 |  |  |  |  | 0.6693% | 3.86% | 5% | 5% | 50.6
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 12.0333 | [6 empty] | 5.3269 | 5.8546 | 100% | 100% | 100% | 100% |  |  |  |  | 26.12% | 317159 | 305745 | 0 | 305745 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 317.83 |  |  |  |  | 0.9683% | 4.779% | 5% | 5% | 50.6
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 12.1333 | [6 empty] | 4.6504 | 5.1014 | 100% | 100% | 100% | 100% |  |  |  |  | 19.03% | 231099 | 225060 | 347.8516 | 224712.1484 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 232.32 |  |  |  |  | 0.5603% | 4.137% | 5% | 5% | 50.6
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 11.0833 | [6 empty] | 5.3895 | 5.7746 | 99.77% | 100% | 99.77% | 100% |  |  |  |  | 25.62% | 311186 | 300465 | 0 | 300465 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 302.2 |  |  |  |  | 0.8333% | 6.431% | 5% | 5% | 50.6
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 11.55 | [6 empty] | 5.7047 | 6.3705 | 98.96% | 100% | 98.96% | 100% |  |  |  |  | 27.52% | 334198 | 322740 | 450.1255 | 322289.8745 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 341.49 |  |  |  |  | 1.049% | 25.1% | 5% | 5% | 50.6
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 12.15 | [6 empty] | 4.9 | 5.3055 | 99.35% | 99.35% | 100% | 100% |  |  |  |  | 20.97% | 254705 | 247665 | 0 | 247665 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 255.52 |  |  |  |  | 0.4266% | 4.266% | 5% | 5% | 50.6
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 11.6167 | [6 empty] | 5.5782 | 6.289 | 99.7% | 99.7% | 100% | 100% |  |  |  |  | 29.02% | 352361 | 330990 | 0 | 330990 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 345.81 |  |  |  |  | 0.9272% | 6.739% | 5% | 5% | 50.6
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 12.0833 | [6 empty] | 5.1478 | 5.8 | 98.66% | 98.66% | 100% | 100% |  |  |  |  | 23.76% | 288572.5 | 279840 | 0 | 279840 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 289.12 |  |  |  |  | 0.7801% | 3.003% | 5% | 5% | 50.6
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 11.9667 | [6 empty] | 5.3211 | 6.025 | 99.69% | 99.69% | 100% | 100% |  |  |  |  | 23.51% | 285510 | 277035 | 412.2545 | 276622.7455 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 287.2 |  |  |  |  | 0.9903% | 24.85% | 5% | 5% | 50.6
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 12.0833 | [6 empty] | 4.1043 | 4.6 | 81.96% | 99.49% | 82.37% | 100% |  |  |  |  | 8.537% | 103672.1 | 99660 | 0 | 99660 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 104.05 |  |  |  |  | 0.7997% | 29.03% | 5% | 5% | 50.6
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 12.0333 | [6 empty] | 4.6282 | 4.9 | 92.31% | 99.06% | 93.19% | 100% |  |  |  |  | 13.3% | 161552 | 155595 | 276.8594 | 155318.1406 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 157.98 |  |  |  |  | 0.7562% | 21.97% | 5% | 5% | 50.6
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 11.9167 | [6 empty] | 4.8743 | 5.425 | 97.09% | 97.09% | 100% | 100% |  |  |  |  | 17.86% | 216879 | 203775 | 0 | 203775 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 217.24 |  |  |  |  | 0.8348% | 20.18% | 5% | 5% | 50.6
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 11.9833 | [6 empty] | 4.8016 | 5.2602 | 82.23% | 98.65% | 83.36% | 100% |  |  |  |  | 12.28% | 149145 | 143715 | 0 | 143715 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 156.47 |  |  |  |  | 0.7828% | 45% | 5% | 5% | 50.6
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 10.85 | [6 empty] | 4.1043 | 4.6 | 74.27% | 98.31% | 75.54% | 100% |  |  |  |  | 7.886% | 95772.1 | 92070 | 200.5882 | 91869.4118 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 100.56 |  |  |  |  | 1.067% | 87.4% | 5% | 5% | 50.6
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 12.0667 | [6 empty] | 3.4739 | 4 | 60.43% | 98.67% | 61.25% | 100% |  |  |  |  | 5.7% | 69222.4 | 67485 | 0 | 67485 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 70.82 |  |  |  |  | 0.479% | 12.19% | 5% | 5% | 50.6
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 10.9667 | [6 empty] | 4.0913 | 4.4 | 99.3% | 99.3% | 100% | 100% |  |  |  |  | 10.1% | 122669 | 118965 | 0 | 118965 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 123.77 |  |  |  |  | 0.9304% | 78.57% | 5% | 5% | 50.6
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 12.2167 | [6 empty] | 4.6783 | 5 | 98.61% | 98.61% | 100% | 100% |  |  |  |  | 13.18% | 160031.5 | 153945 | 0 | 153945 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 160.18 |  |  |  |  | 1.343% | 87.75% | 5% | 5% | 50.6
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 12.15 | [6 empty] | 5.0739 | 5.4 | 99.85% | 99.85% | 100% | 100% |  |  |  |  | 19.63% | 238442 | 230670 | 413.3871 | 230256.6129 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 238.47 |  |  |  |  | 0.9185% | 44.73% | 5% | 5% | 50.6
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 12.2167 | [6 empty] | 4.3217 | 4.8 | 87.12% | 99.05% | 87.96% | 100% |  |  |  |  | 9.729% | 118148.4 | 112200 | 0 | 112200 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 120.17 |  |  |  |  | 0.9259% | 69.04% | 5% | 5% | 50.6
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 11.6167 | [6 empty] | 3.013 | 3.4 | 94.85% | 98.26% | 96.53% | 100% |  |  |  |  | 3.173% | 38536.2 | 37785 | 97.384 | 37687.616 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 41.88 |  |  |  |  | 0.9367% | 295.4% | 5% | 5% | 50.6
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 10.8333 | [6 empty] | 3.3913 | 3.8 | 96.72% | 98.86% | 97.84% | 100% |  |  |  |  | 6.833% | 82978 | 82170 | 510.3727 | 81659.6273 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 88.93 |  |  |  |  | 0.8567% | 144.4% | 5% | 5% | 50.6
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 12.1833 | [6 empty] | 6.0728 | 6.555 | 98.43% | 98.43% | 100% | 100% |  |  |  |  | 34.09% | 413940 | 398970 | 0 | 398970 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 413.94 |  |  |  |  | 1.064% | 29.92% | 5% | 5% | 50.6
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 12.3167 | [6 empty] | 7.5587 | 8.3016 | 98.23% | 100% | 98.23% | 83.71% |  |  |  |  | 43.11% | 523470 | 505560 | 0 | 505560 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 545.86 |  |  |  |  | 1.073% | 31.93% | 5% | 5% | 50.6
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 12.2167 | [6 empty] | 8.3972 | 9.1189 | 98.46% | 99.13% | 99.32% | 87.02% |  |  |  |  | 57.14% | 693942 | 673365 | 0 | 673365 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 707.87 |  |  |  |  | 0.197% | 11.96% | 5% | 5% | 50.6
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 11.85 | [6 empty] | 8.183 | 8.7875 | 99.38% | 100% | 99.38% | 100% |  |  |  |  | 64.52% | 783582 | 757020 | 0 | 757020 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 784.85 |  |  |  |  | 0.8323% | 3.712% | 5% | 5% | 50.6
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 11.6833 | [6 empty] | 9.2652 | 9.8 | 99.67% | 100% | 99.67% | 100% |  |  |  |  | 74.38% | 903221.8 | 871035 | 0 | 871035 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 907.2 |  |  |  |  | 0.9845% | 6.897% | 5% | 5% | 50.6
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 12.1833 | [6 empty] | 10.3739 | 11.3 | 100% | 100% | 100% | 100% |  |  |  |  | 91.9% | 1116056 | 1072005 | 0 | 1072005 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 1116.06 |  |  |  |  | 0.2144% | 2.589% | 5% | 5% | 50.6
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 12 | [6 empty] | 10.8217 | 11.5 | 93.31% | 100% | 93.31% | 100% |  |  |  |  | 85.73% | 1041057 | 1000395 | 0 | 1000395 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 1061.1 |  |  |  |  | 0.7742% | 7.446% | 5% | 5% | 50.6
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 12.1333 | [6 empty] | 8.8522 | 9.7 | 92.3% | 98.67% | 93.54% | 100% |  |  |  |  | 71.84% | 872420 | 839520 | 0 | 839520 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 884.82 |  |  |  |  | 0.4884% | 14.39% | 5% | 5% | 50.6
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 11.9833 | [6 empty] | 8 | 8.4 | 97.13% | 99.77% | 97.36% | 100% |  |  |  |  | 62.32% | 756821 | 728310 | 0 | 728310 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 761 |  |  |  |  | 0.8951% | 9.624% | 5% | 5% | 50.6
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 11.8 | [6 empty] | 9.5739 | 10.4 | 99.74% | 99.74% | 100% | 88.78% |  |  |  |  | 69.94% | 849349 | 818730 | 0 | 818730 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 872.37 |  |  |  |  | 0.6155% | 3.197% | 5% | 5% | 50.6
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 12.2 | [6 empty] | 9.9522 | 10.9 | 99.65% | 99.65% | 100% | 100% |  |  |  |  | 88.35% | 1072913 | 1028940 | 0 | 1028940 | 50.6 | 7.1311 | 445081.6129 |  | 36.65% | 95.55% | 99.5% | 1072.93 |  |  |  |  | 0.8762% | 9.978% | 5% | 5% | 50.6
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 12.2667 | [6 empty] | 8.8087 | 9.5 | 99.55% | 100% | 99.55% | 100% |  |  |  |  | 70.33% | 854113.6 | 821370 | 0 | 821370 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 853.95 |  |  |  |  | 0.5169% | 5.737% | 5% | 5% | 50.6
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 12.4167 | [6 empty] | 7.4348 | 8.1 | 97.56% | 99.84% | 97.72% | 100% |  |  |  |  | 51.05% | 619985.1 | 600105 | 0 | 600105 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 627.14 |  |  |  |  | 0.4726% | 18.51% | 5% | 5% | 50.6
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 0.3 | [6 empty] | 7.1435 | 7.6 | 100% | 100% | 100% | 100% |  |  |  |  | 51.01% | 619404.9 | 596970 | 0 | 596970 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 619.59 |  |  |  |  | 0.8037% | 26.44% | 5% | 5% | 50.6
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 12.4333 | [6 empty] | 7.2435 | 7.9 | 99.79% | 99.79% | 100% | 100% |  |  |  |  | 47.76% | 580032.8 | 559515 | 0 | 559515 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 580.02 |  |  |  |  | 0.7962% | 18.48% | 5% | 5% | 50.6
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 12.3 | [6 empty] | 6.0174 | 6.7 | 97.2% | 99.82% | 97.37% | 100% |  |  |  |  | 29.17% | 354273.4 | 342705 | 0 | 342705 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 358.15 |  |  |  |  | 0.7528% | 45.13% | 5% | 5% | 50.6
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 12.3 | [6 empty] | 5.587 | 5.9 | 98.27% | 98.44% | 99.82% | 100% |  |  |  |  | 24.08% | 292391 | 282315 | 0 | 282315 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 292.76 |  |  |  |  | 0.8255% | 28.49% | 5% | 5% | 50.6
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 12.3 | [6 empty] | 6.6652 | 7.2 | 99.28% | 99.28% | 100% | 100% |  |  |  |  | 36.84% | 447421.7 | 432630 | 0 | 432630 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 447.56 |  |  |  |  | 0.9556% | 10.79% | 5% | 5% | 50.6
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 12.4833 | [6 empty] | 6.6304 | 7.2 | 99.61% | 99.9% | 99.71% | 100% |  |  |  |  | 38.46% | 467011.7 | 452925 | 0 | 452925 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 468.64 |  |  |  |  | 1.941% | 4.981% | 5% | 5% | 50.6
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 12.3833 | [6 empty] | 6.7435 | 7.9 | 86.07% | 98.33% | 87.53% | 100% |  |  |  |  | 35.71% | 433658 | 421245 | 0 | 421245 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 437.12 |  |  |  |  | -0.9615% | 16.3% | 5% | 5% | 50.6
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 12.3833 | [6 empty] | 6.6391 | 7.6 | 99.41% | 99.41% | 100% | 97.69% |  |  |  |  | 37.64% | 457114.4 | 440385 | 0 | 440385 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 459.81 |  |  |  |  | 0.9328% | 16.46% | 5% | 5% | 50.6
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 11.75 | [6 empty] | 6.0261 | 6.5 | 99.41% | 99.41% | 100% | 100% |  |  |  |  | 29.22% | 354873.6 | 343530 | 0 | 343530 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 354.87 |  |  |  |  | 0.8869% | 51.73% | 5% | 5% | 50.6
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 11.5 | [6 empty] | 6.1304 | 6.6 | 98.22% | 99.62% | 98.6% | 97.54% |  |  |  |  | 30.45% | 369735.9 | 359205 | 0 | 359205 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 375.68 |  |  |  |  | 0.7557% | 73.11% | 5% | 5% | 50.6
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 11.6 | [6 empty] | 6.5 | 6.8 | 100% | 100% | 100% | 100% |  |  |  |  | 37.27% | 452635.1 | 446490 | 0 | 446490 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 452.65 |  |  |  |  | 0.5593% | 0.01239% | 5% | 5% | 50.6
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 11.6 | [6 empty] | 8.6304 | 9.2 | 99.95% | 99.95% | 100% | 100% |  |  |  |  | 74.67% | 906807.2 | 876315 | 0 | 876315 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 906.85 |  |  |  |  | 0.6711% | 8.488% | 5% | 5% | 50.6
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 11.6 | [6 empty] | 9.2261 | 9.8 | 100% | 100% | 100% | 100% |  |  |  |  | 75.34% | 914941 | 882585 | 0 | 882585 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 914.94 |  |  |  |  | 1.63% | 11.91% | 5% | 5% | 50.6
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 11.6833 | [6 empty] | 10.9261 | 11.6 | 99.71% | 100% | 99.71% | 96.74% |  |  |  |  | 90.08% | 1093971.8 | 1051380 | 0 | 1051380 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 1107.45 |  |  |  |  | -0.03823% | 16.57% | 5% | 5% | 50.6
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 11.5833 | [6 empty] | 8.1652 | 8.9 | 100% | 100% | 100% | 93.16% |  |  |  |  | 59.58% | 723527.4 | 697785 | 0 | 697785 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 742.5 |  |  |  |  | 0.8389% | 1.306% | 5% | 5% | 50.6
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 0.16667 | [6 empty] | 8.6435 | 9.6 | 99.98% | 99.98% | 100% | 97.26% |  |  |  |  | 65.72% | 798159.9 | 776160 | 0 | 776160 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 805.85 |  |  |  |  | 0.5078% | 0.03343% | 5% | 5% | 50.6
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 0.25 | [6 empty] | 10.3087 | 11.2 | 98.2% | 98.2% | 100% | 93.19% |  |  |  |  | 79.5% | 965424.1 | 929280 | 0 | 929280 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 1000.67 |  |  |  |  | 0.8663% | 4.571% | 5% | 5% | 50.6
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 12.2833 | [6 empty] | 9.4304 | 10.5 | 99.44% | 99.97% | 99.48% | 98.02% |  |  |  |  | 80.23% | 974292.9 | 939345 | 0 | 939345 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 998 |  |  |  |  | 0.5523% | 0.4387% | 5% | 5% | 50.6
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 12.25 | [6 empty] | 9.4391 | 10.2 | 100% | 100% | 100% | 100% |  |  |  |  | 74.75% | 907767 | 874665 | 0 | 874665 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 966.22 |  |  |  |  | 0.5921% | 0.8551% | 5% | 5% | 50.6
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 12.1167 | [6 empty] | 8.7957 | 9.5 | 100% | 100% | 100% | 100% |  |  |  |  | 75.06% | 911519 | 877470 | 0 | 877470 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 911.18 |  |  |  |  | 0.7344% | 3.621% | 5% | 5% | 50.6
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 12.25 | [6 empty] | 9.9348 | 10.9 | 100% | 100% | 100% | 98.1% |  |  |  |  | 87.44% | 1061869.1 | 1020855 | 0 | 1020855 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 1070.07 |  |  |  |  | 0.5405% | 6.396% | 5% | 5% | 50.6
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 12.2167 | [6 empty] | 11.1304 | 12.1 | 100% | 100% | 100% | 96.6% |  |  |  |  | 90.38% | 1097551.1 | 1052700 | 0 | 1052700 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 1107.55 |  |  |  |  | 0.8127% | 7.006% | 5% | 5% | 50.6
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 12.0833 | [6 empty] | 9.7321 | 10.7565 | 98.85% | 99.19% | 99.66% | 100% |  |  |  |  | 85.38% | 1036839 | 997425 | 0 | 997425 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 1042.72 |  |  |  |  | 0.6503% | 6.771% | 5% | 5% | 50.6
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 11.6 | [6 empty] | 9.5275 | 10.4374 | 99.69% | 100% | 99.69% | 100% |  |  |  |  | 85.3% | 1035887 | 995445 | 0 | 995445 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 1040.28 |  |  |  |  | 0.6331% | 9.905% | 5% | 5% | 50.6
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 12.3 | [6 empty] | 9.3043 | 10.1 | 78.05% | 100% | 78.05% | 100% |  |  |  |  | 63.34% | 769199.4 | 739035 | 869.4529 | 738165.5471 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 787.8 |  |  |  |  | 0.9729% | 4.218% | 5% | 5% | 50.6
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 12.4333 | [6 empty] | 8.3696 | 9.2 | 93.83% | 97.91% | 95.84% | 100% |  |  |  |  | 63.22% | 767794 | 742665 | 0 | 742665 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 771.89 |  |  |  |  | 1.09% | 1.587% | 5% | 5% | 50.6
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 12.05 | [6 empty] | 9.5043 | 10.4 | 98.27% | 98.61% | 99.65% | 100% |  |  |  |  | 76.05% | 923538.7 | 891660 | 0 | 891660 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 926.53 |  |  |  |  | 0.5208% | 0.01562% | 5% | 5% | 50.6
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 12.1167 | [6 empty] | 10.0391 | 10.9 | 100% | 100% | 100% | 100% |  |  |  |  | 82.62% | 1003287.8 | 968055 | 0 | 968055 | 50.6 | 9.453 | 706540.3333 |  | 58.18% | 95.55% | 99.5% | 1003.29 |  |  |  |  | 0.4817% | 3.522% | 5% | 5% | 50.6
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | 12.0833 | [6 empty] | 9.0609 | 9.9 | 99.97% | 99.97% | 100% | 100% |  |  |  |  | 74.62% | 906237.5 | 874005 | 0 | 874005 | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 906.23 |  |  |  |  | 1.452% | 2.657% | 5% | 5% | 50.6
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | 12.0833 | [6 empty] | 8.8 | 9.5 | 99.96% | 99.96% | 100% | 100% |  |  |  |  | 72.94% | 885797 | 856680 | 0 | 856680 | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 885.8 |  |  |  |  | 1.283% | 12.49% | 5% | 5% | 50.6
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | 12.2833 | [6 empty] | 9.2783 | 10.1 | 100% | 100% | 100% | 100% |  |  |  |  | 77.31% | 938895 | 901065 | 0 | 901065 | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 939 |  |  |  |  | 1.402% | 2.34% | 5% | 5% | 50.6
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | 12.1333 | [6 empty] | 9.9 | 10.8 | 99.4% | 100% | 99.4% | 100% |  |  |  |  | 84.97% | 1031935.8 | 994125 | 0 | 994125 | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 1036.83 |  |  |  |  | -1.09% | 4.394% | 5% | 5% | 50.6
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | 12.05 | [6 empty] | 9.8043 | 10.6 | 99.83% | 99.83% | 100% | 100% |  |  |  |  | 85.27% | 1035503 | 995940 | 0 | 995940 | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 1035.51 |  |  |  |  | 0.3927% | 7.846% | 5% | 5% | 50.6
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | 11.9833 | [6 empty] | 10.9348 | 11.6 | 99.8% | 99.8% | 100% | 100% |  |  |  |  | 93.66% | 1137389 | 1094115 | 0 | 1094115 | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 1137.39 |  |  |  |  | 0.8955% | 14.89% | 5% | 5% | 50.6
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | 12.0167 | [6 empty] | 10.4217 | 11.4 | 99.83% | 99.83% | 100% | 100% |  |  |  |  | 89.73% | 1089705 | 1047090 | 0 | 1047090 | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 1089.7 |  |  |  |  | 0.6185% | 6.122% | 5% | 5% | 50.6
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | 11.75 | [6 empty] | 9.3783 | 9.8 | 100% | 100% | 100% | 100% |  |  |  |  | 78.89% | 958084 | 922515 | 0 | 922515 | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 957.73 |  |  |  |  | 0.8333% | 1.681% | 5% | 5% | 50.6
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | 12.1833 | [6 empty] | 9.1043 | 9.9 | 99.22% | 99.22% | 100% | 100% |  |  |  |  | 76.92% | 934106 | 899415 | 0 | 899415 | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 934.11 |  |  |  |  | 0.6908% | 5.804% | 5% | 5% | 50.6
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | 12.2 | [6 empty] | 7.9565 | 8.6 | 100% | 100% | 100% | 100% |  |  |  |  | 61.37% | 745304 | 719895 | 0 | 719895 | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 745.32 |  |  |  |  | 0.7147% | 4.517% | 5% | 5% | 50.6
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | 12.1 | [6 empty] | 7.0652 | 7.6 | 99.46% | 99.84% | 99.62% | 100% |  |  |  |  | 46.23% | 561465 | 543180 | 0 | 543180 | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 562.93 |  |  |  |  | 0.5512% | 7.457% | 5% | 5% | 50.6
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | 12.25 | [6 empty] | 7.5957 | 8.2 | 95.08% | 99.84% | 95.23% | 100% |  |  |  |  | 52.11% | 632820.5 | 613305 | 0 | 613305 | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 639.03 |  |  |  |  | 0.841% | 8.829% | 5% | 5% | 50.6
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | 11.9667 | [6 empty] | 8.0652 | 8.8 | 100% | 100% | 100% | 100% |  |  |  |  | 63.9% | 775981.2 | 750585 | 0 | 750585 | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 775.97 |  |  |  |  | 6.671% | 7.909% | 5% | 5% | 50.6
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 10.3038 | 815983.2258 |  | 67.19% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [7 empty] | 0 | [8 empty] | 0% | 0 | 0 |  |  | 50.6 | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | 0 | [6 empty] | 5% | 5% | 50.6
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 8.5195 | 699874.8387 |  | 57.63% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 7.2367 | 416592.3333 |  | 34.3% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 6.0016 | 225766.129 |  | 18.59% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 6.7074 | 349937.3333 |  | 28.82% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 7.0533 | 441856.4516 |  | 36.38% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 7.4111 | 422505.1613 |  | 34.79% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.4041 | 357078.9286 |  | 29.4% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 5.9682 | 280595.1613 |  | 23.11% | 95.55% | 99.5% | [7 empty] | 5% | 5% | 50.6
2026-04-01 | 2027 | 2026 | 2026-04-01 | 30
2026-04-02 | 2027 | 2026 | 2026-04-01 | 30
2026-04-03 | 2027 | 2026 | 2026-04-01 | 30
2026-04-04 | 2027 | 2026 | 2026-04-01 | 30
2026-04-05 | 2027 | 2026 | 2026-04-01 | 30
2026-04-06 | 2027 | 2026 | 2026-04-01 | 30
2026-04-07 | 2027 | 2026 | 2026-04-01 | 30
2026-04-08 | 2027 | 2026 | 2026-04-01 | 30
2026-04-09 | 2027 | 2026 | 2026-04-01 | 30
2026-04-10 | 2027 | 2026 | 2026-04-01 | 30
2026-04-11 | 2027 | 2026 | 2026-04-01 | 30
2026-04-12 | 2027 | 2026 | 2026-04-01 | 30
2026-04-13 | 2027 | 2026 | 2026-04-01 | 30
2026-04-14 | 2027 | 2026 | 2026-04-01 | 30
2026-04-15 | 2027 | 2026 | 2026-04-01 | 30
2026-04-16 | 2027 | 2026 | 2026-04-01 | 30
2026-04-17 | 2027 | 2026 | 2026-04-01 | 30
2026-04-18 | 2027 | 2026 | 2026-04-01 | 30
2026-04-19 | 2027 | 2026 | 2026-04-01 | 30
2026-04-20 | 2027 | 2026 | 2026-04-01 | 30
2026-04-21 | 2027 | 2026 | 2026-04-01 | 30
2026-04-22 | 2027 | 2026 | 2026-04-01 | 30
2026-04-23 | 2027 | 2026 | 2026-04-01 | 30
2026-04-24 | 2027 | 2026 | 2026-04-01 | 30
2026-04-25 | 2027 | 2026 | 2026-04-01 | 30
2026-04-26 | 2027 | 2026 | 2026-04-01 | 30
2026-04-27 | 2027 | 2026 | 2026-04-01 | 30
2026-04-28 | 2027 | 2026 | 2026-04-01 | 30
2026-04-29 | 2027 | 2026 | 2026-04-01 | 30
2026-04-30 | 2027 | 2026 | 2026-04-01 | 30
2026-05-01 | 2027 | 2026 | 2026-05-01 | 31
2026-05-02 | 2027 | 2026 | 2026-05-01 | 31
2026-05-03 | 2027 | 2026 | 2026-05-01 | 31
2026-05-04 | 2027 | 2026 | 2026-05-01 | 31
2026-05-05 | 2027 | 2026 | 2026-05-01 | 31
2026-05-06 | 2027 | 2026 | 2026-05-01 | 31
2026-05-07 | 2027 | 2026 | 2026-05-01 | 31
2026-05-08 | 2027 | 2026 | 2026-05-01 | 31
2026-05-09 | 2027 | 2026 | 2026-05-01 | 31
2026-05-10 | 2027 | 2026 | 2026-05-01 | 31
2026-05-11 | 2027 | 2026 | 2026-05-01 | 31
2026-05-12 | 2027 | 2026 | 2026-05-01 | 31
2026-05-13 | 2027 | 2026 | 2026-05-01 | 31
2026-05-14 | 2027 | 2026 | 2026-05-01 | 31
2026-05-15 | 2027 | 2026 | 2026-05-01 | 31
2026-05-16 | 2027 | 2026 | 2026-05-01 | 31
2026-05-17 | 2027 | 2026 | 2026-05-01 | 31
2026-05-18 | 2027 | 2026 | 2026-05-01 | 31
2026-05-19 | 2027 | 2026 | 2026-05-01 | 31
2026-05-20 | 2027 | 2026 | 2026-05-01 | 31
2026-05-21 | 2027 | 2026 | 2026-05-01 | 31
2026-05-22 | 2027 | 2026 | 2026-05-01 | 31
2026-05-23 | 2027 | 2026 | 2026-05-01 | 31
2026-05-24 | 2027 | 2026 | 2026-05-01 | 31
2026-05-25 | 2027 | 2026 | 2026-05-01 | 31
2026-05-26 | 2027 | 2026 | 2026-05-01 | 31
2026-05-27 | 2027 | 2026 | 2026-05-01 | 31
2026-05-28 | 2027 | 2026 | 2026-05-01 | 31
2026-05-29 | 2027 | 2026 | 2026-05-01 | 31
2026-05-30 | 2027 | 2026 | 2026-05-01 | 31
2026-05-31 | 2027 | 2026 | 2026-05-01 | 31
2026-06-01 | 2027 | 2026 | 2026-06-01 | 30
2026-06-02 | 2027 | 2026 | 2026-06-01 | 30
2026-06-03 | 2027 | 2026 | 2026-06-01 | 30
2026-06-04 | 2027 | 2026 | 2026-06-01 | 30
2026-06-05 | 2027 | 2026 | 2026-06-01 | 30
2026-06-06 | 2027 | 2026 | 2026-06-01 | 30
2026-06-07 | 2027 | 2026 | 2026-06-01 | 30
2026-06-08 | 2027 | 2026 | 2026-06-01 | 30
2026-06-09 | 2027 | 2026 | 2026-06-01 | 30
2026-06-10 | 2027 | 2026 | 2026-06-01 | 30
2026-06-11 | 2027 | 2026 | 2026-06-01 | 30
2026-06-12 | 2027 | 2026 | 2026-06-01 | 30
2026-06-13 | 2027 | 2026 | 2026-06-01 | 30
2026-06-14 | 2027 | 2026 | 2026-06-01 | 30
2026-06-15 | 2027 | 2026 | 2026-06-01 | 30
2026-06-16 | 2027 | 2026 | 2026-06-01 | 30
2026-06-17 | 2027 | 2026 | 2026-06-01 | 30
2026-06-18 | 2027 | 2026 | 2026-06-01 | 30
2026-06-19 | 2027 | 2026 | 2026-06-01 | 30
2026-06-20 | 2027 | 2026 | 2026-06-01 | 30
2026-06-21 | 2027 | 2026 | 2026-06-01 | 30
2026-06-22 | 2027 | 2026 | 2026-06-01 | 30
2026-06-23 | 2027 | 2026 | 2026-06-01 | 30
2026-06-24 | 2027 | 2026 | 2026-06-01 | 30
2026-06-25 | 2027 | 2026 | 2026-06-01 | 30
2026-06-26 | 2027 | 2026 | 2026-06-01 | 30
2026-06-27 | 2027 | 2026 | 2026-06-01 | 30
2026-06-28 | 2027 | 2026 | 2026-06-01 | 30
2026-06-29 | 2027 | 2026 | 2026-06-01 | 30
2026-06-30 | 2027 | 2026 | 2026-06-01 | 30
2026-07-01 | 2027 | 2026 | 2026-07-01 | 31
2026-07-02 | 2027 | 2026 | 2026-07-01 | 31
2026-07-03 | 2027 | 2026 | 2026-07-01 | 31
2026-07-04 | 2027 | 2026 | 2026-07-01 | 31
2026-07-05 | 2027 | 2026 | 2026-07-01 | 31
2026-07-06 | 2027 | 2026 | 2026-07-01 | 31
2026-07-07 | 2027 | 2026 | 2026-07-01 | 31
2026-07-08 | 2027 | 2026 | 2026-07-01 | 31
2026-07-09 | 2027 | 2026 | 2026-07-01 | 31
2026-07-10 | 2027 | 2026 | 2026-07-01 | 31
2026-07-11 | 2027 | 2026 | 2026-07-01 | 31
2026-07-12 | 2027 | 2026 | 2026-07-01 | 31
2026-07-13 | 2027 | 2026 | 2026-07-01 | 31
2026-07-14 | 2027 | 2026 | 2026-07-01 | 31
2026-07-15 | 2027 | 2026 | 2026-07-01 | 31
2026-07-16 | 2027 | 2026 | 2026-07-01 | 31
2026-07-17 | 2027 | 2026 | 2026-07-01 | 31
2026-07-18 | 2027 | 2026 | 2026-07-01 | 31
2026-07-19 | 2027 | 2026 | 2026-07-01 | 31
2026-07-20 | 2027 | 2026 | 2026-07-01 | 31
2026-07-21 | 2027 | 2026 | 2026-07-01 | 31
2026-07-22 | 2027 | 2026 | 2026-07-01 | 31
2026-07-23 | 2027 | 2026 | 2026-07-01 | 31
2026-07-24 | 2027 | 2026 | 2026-07-01 | 31
2026-07-25 | 2027 | 2026 | 2026-07-01 | 31
2026-07-26 | 2027 | 2026 | 2026-07-01 | 31
2026-07-27 | 2027 | 2026 | 2026-07-01 | 31
2026-07-28 | 2027 | 2026 | 2026-07-01 | 31
2026-07-29 | 2027 | 2026 | 2026-07-01 | 31
2026-07-30 | 2027 | 2026 | 2026-07-01 | 31
2026-07-31 | 2027 | 2026 | 2026-07-01 | 31
2026-08-01 | 2027 | 2026 | 2026-08-01 | 31
2026-08-02 | 2027 | 2026 | 2026-08-01 | 31
2026-08-03 | 2027 | 2026 | 2026-08-01 | 31
2026-08-04 | 2027 | 2026 | 2026-08-01 | 31
2026-08-05 | 2027 | 2026 | 2026-08-01 | 31
2026-08-06 | 2027 | 2026 | 2026-08-01 | 31
2026-08-07 | 2027 | 2026 | 2026-08-01 | 31
2026-08-08 | 2027 | 2026 | 2026-08-01 | 31
2026-08-09 | 2027 | 2026 | 2026-08-01 | 31
2026-08-10 | 2027 | 2026 | 2026-08-01 | 31
2026-08-11 | 2027 | 2026 | 2026-08-01 | 31
2026-08-12 | 2027 | 2026 | 2026-08-01 | 31
2026-08-13 | 2027 | 2026 | 2026-08-01 | 31
2026-08-14 | 2027 | 2026 | 2026-08-01 | 31
2026-08-15 | 2027 | 2026 | 2026-08-01 | 31
2026-08-16 | 2027 | 2026 | 2026-08-01 | 31
2026-08-17 | 2027 | 2026 | 2026-08-01 | 31
2026-08-18 | 2027 | 2026 | 2026-08-01 | 31
2026-08-19 | 2027 | 2026 | 2026-08-01 | 31
2026-08-20 | 2027 | 2026 | 2026-08-01 | 31
2026-08-21 | 2027 | 2026 | 2026-08-01 | 31
2026-08-22 | 2027 | 2026 | 2026-08-01 | 31
2026-08-23 | 2027 | 2026 | 2026-08-01 | 31
2026-08-24 | 2027 | 2026 | 2026-08-01 | 31
2026-08-25 | 2027 | 2026 | 2026-08-01 | 31
2026-08-26 | 2027 | 2026 | 2026-08-01 | 31
2026-08-27 | 2027 | 2026 | 2026-08-01 | 31
2026-08-28 | 2027 | 2026 | 2026-08-01 | 31
2026-08-29 | 2027 | 2026 | 2026-08-01 | 31
2026-08-30 | 2027 | 2026 | 2026-08-01 | 31
2026-08-31 | 2027 | 2026 | 2026-08-01 | 31
2026-09-01 | 2027 | 2026 | 2026-09-01 | 30
2026-09-02 | 2027 | 2026 | 2026-09-01 | 30
2026-09-03 | 2027 | 2026 | 2026-09-01 | 30
2026-09-04 | 2027 | 2026 | 2026-09-01 | 30
2026-09-05 | 2027 | 2026 | 2026-09-01 | 30
2026-09-06 | 2027 | 2026 | 2026-09-01 | 30
2026-09-07 | 2027 | 2026 | 2026-09-01 | 30
2026-09-08 | 2027 | 2026 | 2026-09-01 | 30
2026-09-09 | 2027 | 2026 | 2026-09-01 | 30
2026-09-10 | 2027 | 2026 | 2026-09-01 | 30
2026-09-11 | 2027 | 2026 | 2026-09-01 | 30
2026-09-12 | 2027 | 2026 | 2026-09-01 | 30
2026-09-13 | 2027 | 2026 | 2026-09-01 | 30
2026-09-14 | 2027 | 2026 | 2026-09-01 | 30
2026-09-15 | 2027 | 2026 | 2026-09-01 | 30
2026-09-16 | 2027 | 2026 | 2026-09-01 | 30
2026-09-17 | 2027 | 2026 | 2026-09-01 | 30
2026-09-18 | 2027 | 2026 | 2026-09-01 | 30
2026-09-19 | 2027 | 2026 | 2026-09-01 | 30
2026-09-20 | 2027 | 2026 | 2026-09-01 | 30
2026-09-21 | 2027 | 2026 | 2026-09-01 | 30
2026-09-22 | 2027 | 2026 | 2026-09-01 | 30
2026-09-23 | 2027 | 2026 | 2026-09-01 | 30
2026-09-24 | 2027 | 2026 | 2026-09-01 | 30
2026-09-25 | 2027 | 2026 | 2026-09-01 | 30
2026-09-26 | 2027 | 2026 | 2026-09-01 | 30
2026-09-27 | 2027 | 2026 | 2026-09-01 | 30
2026-09-28 | 2027 | 2026 | 2026-09-01 | 30
2026-09-29 | 2027 | 2026 | 2026-09-01 | 30
2026-09-30 | 2027 | 2026 | 2026-09-01 | 30
2026-10-01 | 2027 | 2026 | 2026-10-01 | 31
2026-10-02 | 2027 | 2026 | 2026-10-01 | 31
2026-10-03 | 2027 | 2026 | 2026-10-01 | 31
2026-10-04 | 2027 | 2026 | 2026-10-01 | 31
2026-10-05 | 2027 | 2026 | 2026-10-01 | 31
2026-10-06 | 2027 | 2026 | 2026-10-01 | 31
2026-10-07 | 2027 | 2026 | 2026-10-01 | 31
2026-10-08 | 2027 | 2026 | 2026-10-01 | 31
2026-10-09 | 2027 | 2026 | 2026-10-01 | 31
2026-10-10 | 2027 | 2026 | 2026-10-01 | 31
2026-10-11 | 2027 | 2026 | 2026-10-01 | 31
2026-10-12 | 2027 | 2026 | 2026-10-01 | 31
2026-10-13 | 2027 | 2026 | 2026-10-01 | 31
2026-10-14 | 2027 | 2026 | 2026-10-01 | 31
2026-10-15 | 2027 | 2026 | 2026-10-01 | 31
2026-10-16 | 2027 | 2026 | 2026-10-01 | 31
2026-10-17 | 2027 | 2026 | 2026-10-01 | 31
2026-10-18 | 2027 | 2026 | 2026-10-01 | 31
2026-10-19 | 2027 | 2026 | 2026-10-01 | 31
2026-10-20 | 2027 | 2026 | 2026-10-01 | 31
2026-10-21 | 2027 | 2026 | 2026-10-01 | 31
2026-10-22 | 2027 | 2026 | 2026-10-01 | 31
2026-10-23 | 2027 | 2026 | 2026-10-01 | 31
2026-10-24 | 2027 | 2026 | 2026-10-01 | 31
2026-10-25 | 2027 | 2026 | 2026-10-01 | 31
2026-10-26 | 2027 | 2026 | 2026-10-01 | 31
2026-10-27 | 2027 | 2026 | 2026-10-01 | 31
2026-10-28 | 2027 | 2026 | 2026-10-01 | 31
2026-10-29 | 2027 | 2026 | 2026-10-01 | 31
2026-10-30 | 2027 | 2026 | 2026-10-01 | 31
2026-10-31 | 2027 | 2026 | 2026-10-01 | 31
2026-11-01 | 2027 | 2026 | 2026-11-01 | 30
2026-11-02 | 2027 | 2026 | 2026-11-01 | 30
2026-11-03 | 2027 | 2026 | 2026-11-01 | 30
2026-11-04 | 2027 | 2026 | 2026-11-01 | 30
2026-11-05 | 2027 | 2026 | 2026-11-01 | 30
2026-11-06 | 2027 | 2026 | 2026-11-01 | 30
2026-11-07 | 2027 | 2026 | 2026-11-01 | 30
2026-11-08 | 2027 | 2026 | 2026-11-01 | 30
2026-11-09 | 2027 | 2026 | 2026-11-01 | 30
2026-11-10 | 2027 | 2026 | 2026-11-01 | 30
2026-11-11 | 2027 | 2026 | 2026-11-01 | 30
2026-11-12 | 2027 | 2026 | 2026-11-01 | 30
2026-11-13 | 2027 | 2026 | 2026-11-01 | 30
2026-11-14 | 2027 | 2026 | 2026-11-01 | 30
2026-11-15 | 2027 | 2026 | 2026-11-01 | 30
2026-11-16 | 2027 | 2026 | 2026-11-01 | 30
2026-11-17 | 2027 | 2026 | 2026-11-01 | 30
2026-11-18 | 2027 | 2026 | 2026-11-01 | 30
2026-11-19 | 2027 | 2026 | 2026-11-01 | 30
2026-11-20 | 2027 | 2026 | 2026-11-01 | 30
2026-11-21 | 2027 | 2026 | 2026-11-01 | 30
2026-11-22 | 2027 | 2026 | 2026-11-01 | 30
2026-11-23 | 2027 | 2026 | 2026-11-01 | 30
2026-11-24 | 2027 | 2026 | 2026-11-01 | 30
2026-11-25 | 2027 | 2026 | 2026-11-01 | 30
2026-11-26 | 2027 | 2026 | 2026-11-01 | 30
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Input_Raw
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 |  | 54 | 55 | 56 | 57 | 58 |  | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107
[7 empty] | O2R1 | O2R3 | O2R1 | O2R3 | O2R3 | O2R3 | O2R3 | O2R3 | O2R3 | O2R1 | O2R1 | O2R1 | O2R1 | O2R1 | O2R1 | O2R2 | O2R2 | O2R4 | O2R1 | O2R1 | O2R3 | O2R3 | O2R3 | O2R1 | O2R3 | O2R1 | O2R3 | O2R3 | O2R3 | O2R3 | O2R3 | O2R3 | O2R1 | O2R1 | O2R1 | O2R1 | O2R1 | O2R1 | O2R2 | O2R2 | O2R4 | O2R1 | O2R1 | O2R3 | O2R3 | O2R3 | [13 empty] | 0.243 | [7 empty] | 0 | 92.547 | 0.062 | 0.088 | 0.178 | 0.35 |  | 0 | 0.1
|  |  |  | 4: Energy Generated by individual Turbine | [9 empty] | Meter Readings | [16 empty] | Calculated Energy Numbers
Finacial Year | Calendar Year | Month Year | Days | Date | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | KUD01 | KUD02 | KUD03 | KUD04 | KUD05 | KUD06 | KUD07 | KUD08 | KUD09 | KUD10 | KUD11 | KUD12 | KUD13 | KUD14 | KUD15 | KUD16 | KUD17 | KUD18 | KUD19 | KUD20 | KUD21 | KUD22 | KUD23 | WS_KUD01 | WS_KUD02 | WS_KUD03 | WS_KUD04 | WS_KUD05 | WS_KUD06 | WS_KUD07 | WS_KUD08 | WS_KUD09 | WS_KUD10 | WS_KUD11 | WS_KUD12 | WS_KUD13 | WS_KUD14 | WS_KUD15 | WS_KUD16 | WS_KUD17 | WS_KUD18 | WS_KUD19 | WS_KUD20 | WS_KUD21 | WS_KUD22 | WS_KUD23 | WTG Total Gneration (MWh) O2R1 | WTG Total Gneration (MWh) O2R2 | WTG Total Gneration (MWh) O2R5 | WTG Total Gneration (MWh) O2R4 | WTG Total Gneration (MWh) O2R16 | WTG Total Gneration (MWh) | Wind Speed Average (m/S)-O2R1 | Wind Speed Average (m/S)-O2R2 | Wind Speed Average (m/S)-O2R5 | Wind Speed Average (m/S)-O2R4 | Wind Speed Average (m/S)-O2R16 | Wind Speed Average cumulative (m/S)2 | Wind Speed Max (m/S) | 33 kV_Wind_F1_Export reading | 33 kV_Wind_F2_Export_reading | 33 kV_Wind_F3_Export_Reading | 33 kV_Wind_F4_Export Reading | 33 kV_Solar_F1_Export Reading | 33kV_Solar_F2_Export Reading | 33 kV_Solar_F3_Export reading | 32kV_Solar_F4_Export reading | 33kV_OG1_Export reading | 33kV_OG2_Export reading | 220kV_TX1_Export reading | 220kV_Tx2_Export reading | 220kV_TL_TVM Export Reading | 220kV_C&R_PQM reading | 220KV_C&R_PQM Import Reading | 33kV_Aux1 Import Reading | 33kV_Aux2_Import reading | 33 kV_Wind_F1_Energy (MWh) | 33 kV_Wind_F2_Export_reading2 | 33 kV_Wind_F3_Export_Reading3 | 33 kV_Wind_F4_Energy (MWh) | 33 kV_Solar_F1_Energy (kWh) | 32kV_Solar_F2_Energy (MWh) | 33 kV_Solar_F3_Energy (MWh) | 32kV_Solar_F4_Energy (MWh) | 33kV_OG1_Energy (MWh) | 33kV_OG2_Energy (MWh) | 220kV_TX1_Energy (MWh) | 220kV_Tx2_Energy (MWh) | 220kV_TL_TVM Energy (MWh) | 220kV_C&R_PQM xport (MWh) | 220KV_C&R_PQM Import (MWh) | 33kV_Aux1 Import (MWh) | 33kV_Aux2_Import (MWh) | 33 kV Total Export (MWH) | 220 KV Net Export (MWh) | 33 kV Line Loss (%) | Connected Wind AC Capcity(MW) | Forecasting Data count received on Forecasting Portal | Forecasting Penalties (INR) | Solar Operating Hours | Solar Export (33 KV) | Connected DC Capcity (MWp) | Wind Export (33 KV) | Expected Energy as per power curve. (MWh) | Reactive Energy (MVArH) | Remarks
2025 | 2025 | 2025-03-01 | 31 | 2025-03-29 | 6:40 | 18:09 | 8163 | 7999 | 6816 | 6903 | 6419 | 6338 | 6456 | 7033 | 6573 | 6531 | 6647 | 7902 | 6466 | 5847 | 8221 | 8004 | 8148 | 6966 | 6111 | 6391 | 7471 | 7082 | 6865 | 4.7097 | 4.7282 | 4.7628 | 4.4264 | 4.491 | 4.5442 | 4.599 | 4.6446 | 4.6692 | 4.527 | 4.7395 | 4.7118 | 4.4853 | 4.3709 | 4.8999 | 4.7251 | 4.8149 | 4.5357 | 4.3867 | 4.5678 | 4.8013 | 4.691 | 4.6155 | 69095 | 16152 | 55650 | 6966 | 13489 | 161352 | 4.6162 | 4.77 | 4.621 | 4.5357 | 4.6218 | 4.6282 | 4.8999 | 640.305 | 871.588 | 30.191 | 204.912 | 151.257 | 261.385 |  | 52.309 | 172960 | 237651 | 101.821 | 56.494 | 254.618 | 79.673 | 0.102 | 280.229 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! |  |  |  | 50.6 | 97 |  | 11.4833 | #REF! | 140 | #REF! |  | 501.8
2025 | 2025 | 2025-03-01 | 31 | 2025-03-30 | 6:41 | 18:08 | 7709 | 7920 | 6107 | 7493 | 6504 | 6204 | 5644 | 7074 | 6508 | 6334 | 6041 | 7562 | 5895 | 5797 | 7468 | 7746 | 8179 | 6312 | 7375 | 6964 | 7910 | 4719 | 7288 | 4.5045 | 4.5393 | 4.4247 | 4.3054 | 4.296 | 4.3105 | 4.25 | 4.4347 | 4.4602 | 4.2419 | 4.3499 | 4.3279 | 4.1787 | 4.1567 | 4.6498 | 4.5691 | 4.6202 | 4.2922 | 4.4718 | 4.3342 | 4.607 | 4.3097 | 4.4266 | 67252 | 15925 | 54546 | 6312 | 12718 | 156753 | 4.364 | 4.5947 | 4.3939 | 4.2922 | 4.3424 | 4.394 | 4.6498 | 640.305 | 872.079 | 31.147 | 205.358 | 151.991 | 262.144 |  | 53.017 | 173456 | 238019 | 102.43 | 56.95 | 255.154 | 80.209 | 0.102 | 280.639 | 0 |  | 81015 | 215100 | 73590 | 165150 | 170775 |  | 159300 | 496000 | 368000 | 487200 | 364800 | 857600 | 857600 | 0 | 410 |  | 864000 | 857600 | 0.7463% | 50.6 | 97 |  | 11.45 | 710325 | 140 | 154605 |  | 1145.6
2025 | 2025 | 2025-03-01 | 31 | 2025-03-31 | 6:43 | 18:15 | 9913 | 9093 | 7804 | 7443 | 7551 | 8626 | 8300 | 7392 | 7198 | 7370 | 8169 | 9213 | 8120 | 7654 | 8675 | 8963 | 9543 | 7119 | 7318 | 8571 | 8942 | 7472 | 9821 | 4.9128 | 4.8252 | 4.6849 | 4.3956 | 4.4859 | 4.6024 | 4.5918 | 4.5635 | 4.6001 | 4.4342 | 4.6572 | 4.744 | 4.572 | 4.4584 | 4.912 | 4.8489 | 4.9286 | 4.5778 | 4.5201 | 4.6815 | 4.9602 | 4.7637 | 5.0214 | 82807 | 18506 | 66146 | 7119 | 15692 | 190270 | 4.6577 | 4.8888 | 4.681 | 4.5778 | 4.5776 | 4.6844 | 5.0214 | 640.305 | 872.673 | 32.101 | 205.896 | 152.726 | 262.905 |  | 53.721 | 173951 | 238421 | 103.051 | 57.445 | 255.709 | 80.765 | 0.102 | 281.059 | 0 |  | 98010 | 214650 | 88770 | 165375 | 171225 |  | 158400 | 495000 | 402000 | 496800 | 396000 | 888000 | 889600 | 0 | 420 |  | 897000 | 888000 | 1.014% | 50.6 | 97 |  | 11.5333 | 709650 | 140 | 186780 |  | 895.8
2026 | 2025 | 2025-04-01 | 30 | 2025-04-01 | 6:38 | 18:14 | 14549 | 13503 | 12079 | 13030 | 11535 | 13133 | 12647 | 14115 | 10479 | 12412 | 12150 | 14076 | 12019 | 11832 | 13331 | 12767 | 13339 | 12206 | 11181 | 12012 | 13254 | 12545 | 13419 | 5.2326 | 5.0783 | 4.9551 | 4.8302 | 4.7406 | 4.8841 | 4.8779 | 5.2246 | 4.8301 | 4.852 | 4.9433 | 4.9768 | 4.8118 | 4.698 | 5.2483 | 5.0487 | 5.1338 | 4.8601 | 4.7953 | 4.798 | 5.1907 | 5.0869 | 5.1153 | 125641 | 26106 | 100898 | 12206 | 26762 | 291613 | 4.9311 | 5.0912 | 4.9859 | 4.8601 | 5.0513 | 4.9658 | 5.2483 | 640.305 | 873.578 | 33.113 | 206.735 | 153.501 | 263.719 |  | 54.467 | 174476 | 238936 | 103.701 | 58.079 | 256.354 | 81.409 | 0.103 | 281.509 | 0 |  | 149325 | 227700 | 138435 | 174375 | 183150 |  | 167850 | 525000 | 515000 | 520000 | 507200 | 1032000 | 1030400 | 1600 | 450 |  | 1040000 | 1030400 | 0.9317% | 50.6 | 97 |  | 11.6 | 753075 | 140 | 287760 | 292.87 | 1533.4
2026 | 2025 | 2025-04-01 | 30 | 2025-04-02 | 6:51 | 17:50 | 10125 | 8778 | 7653 | 9597 | 8538 | 9097 | 7322 | 11409 | 8056 | 8250 | 8145 | 10146 | 8814 | 8041 | 9575 | 9553 | 9367 | 7010 | 9702 | 11340 | 10084 | 8456 | 11048 | 4.8712 | 4.6717 | 4.6544 | 4.7965 | 4.6707 | 4.741 | 4.6324 | 5.0729 | 4.6749 | 4.6319 | 4.7538 | 4.7309 | 4.6183 | 4.5077 | 4.956 | 4.7868 | 4.8633 | 4.5063 | 4.8806 | 5.024 | 5.0293 | 4.839 | 5.1333 | 91791 | 18920 | 73654 | 7010 | 18731 | 210106 | 4.7629 | 4.825 | 4.8262 | 4.5063 | 4.8526 | 4.7846 | 5.1333 | 640.305 | 874.209 | 34.07 | 207.345 | 154.238 | 264.451 |  | 55.17 | 174965 | 239353 | 104.305 | 58.599 | 256.916 | 81.974 | 0.103 | 281.929 | 0 |  | 104115 | 215325 | 100650 | 165825 | 164700 |  | 158175 | 489000 | 417000 | 483200 | 416000 | 899200 | 904000 | 0 | 420 |  | 906000 | 899200 | 0.7562% | 50.6 | 97 |  | 10.9833 | 704025 | 140 | 204765 | 210.58 | 917.2
2026 | 2025 | 2025-04-01 | 30 | 2025-04-03 | 6:52 | 18:28 | 5301 | 5530 | 6629 | 5753 | 5349 | 6619 | 5174 | 6537 | 5719 | 5543 | 5937 | 5780 | 5056 | 5014 | 4958 | 5633 | 5729 | 5658 | 4437 | 5649 | 5189 | 5942 | 5759 | 4.1416 | 3.9879 | 4.4785 | 4.0059 | 3.9573 | 4.0586 | 4.0096 | 4.3733 | 4.1059 | 4.0983 | 4.4262 | 4.3141 | 4.3 | 4.1286 | 4.1699 | 3.9403 | 4.004 | 4.0062 | 4.2421 | 4.4015 | 3.9575 | 4.111 | 3.9934 | 54304 | 11362 | 45860 | 5658 | 11711 | 128895 | 4.2701 | 3.9722 | 4.0561 | 4.0062 | 4.1915 | 4.1397 | 4.4785 | 640.305 | 874.619 | 35.039 | 207.714 | 154.956 | 265.214 |  | 55.86 | 175454 | 239698 | 104.91 | 59.024 | 257.434 | 82.491 | 0.104 | 282.329 | 0 |  | 67650 | 218025 | 60885 | 161550 | 171675 |  | 155250 | 489000 | 345000 | 484000 | 340000 | 828800 | 827200 | 1600 | 400 |  | 834000 | 827200 | 0.8221% | 50.6 | 97 |  | 11.6 | 706500 | 140 | 128535 | 133.1 | 1390.2
2026 | 2025 | 2025-04-01 | 30 | 2025-04-04 | 6:41 | 18:09 | 7310 | 7976 | 7021 | 8436 | 6977 | 6854 | 7467 | 9348 | 6718 | 7320 | 6489 | 6969 | 4631 | 6580 | 8061 | 8884 | 6855 | 5890 | 6726 | 7939 | 7445 | 6305 | 8342 | 4.1968 | 4.6115 | 4.0648 | 4.5204 | 4.3289 | 4.2199 | 4.4263 | 4.4158 | 4.3346 | 4.1682 | 4.1356 | 4.2189 | 4.0887 | 4.0068 | 4.4759 | 4.7461 | 4.5338 | 4.1919 | 4.1877 | 4.3049 | 4.7304 | 4.4589 | 4.7729 | 69046 | 15739 | 59053 | 5890 | 16815 | 166543 | 4.1848 | 4.6399 | 4.482 | 4.1919 | 4.4211 | 4.3539 | 4.7729 | 640.305 | 875.145 | 36.153 | 208.184 | 155.853 | 266.109 |  | 56.697 | 176045 | 240113 | 105.642 | 59.534 | 258.058 | 83.115 | 0.104 | 282.719 | 0 |  | 86790 | 250650 | 77550 | 201825 | 201375 |  | 188325 | 591000 | 415000 | 585600 | 408000 | 998400 | 998400 | 0 | 390 |  | 1006000 | 998400 | 0.7612% | 50.6 | 97 |  | 11.4667 | 842175 | 140 | 164340 | 168.01 | 1754.9
2026 | 2025 | 2025-04-01 | 30 | 2025-04-05 | 6:30 | 18:11 | 8229 | 7721 | 7773 | 7234 | 7801 | 7678 | 7472 | 8755 | 8556 | 7947 | 7535 | 7731 | 5913 | 7268 | 7655 | 7586 | 8798 | 7531 | 8206 | 8412 | 9174 | 7589 | 9435 | 4.7235 | 4.5983 | 4.721 | 4.5653 | 4.6547 | 4.59 | 4.5 | 4.7826 | 4.9534 | 4.5816 | 4.7044 | 4.6127 | 4.7153 | 4.5259 | 4.659 | 4.6426 | 4.8123 | 4.5878 | 4.7664 | 4.8588 | 4.9453 | 4.8836 | 4.9109 | 76669 | 16384 | 65188 | 7531 | 16227 | 181999 | 4.6869 | 4.7275 | 4.7384 | 4.5878 | 4.6413 | 4.7085 | 4.9534 | 640.305 | 875.712 | 37.164 | 208.689 | 156.661 | 266.912 |  | 57.462 | 176580 | 240516 | 106.304 | 60.03 | 258.639 | 83.699 | 0.104 | 283.109 | 0 |  | 93555 | 227475 | 83325 | 181800 | 180675 |  | 172125 | 535000 | 403000 | 529600 | 396800 | 929600 | 934400 | 0 | 390 |  | 938000 | 929600 | 0.9036% | 50.6 | 97 |  | 11.6833 | 762075 | 140 | 176880 | 182.18 | 769.1
2026 | 2025 | 2025-04-01 | 30 | 2025-04-06 | 6:34 | 18:05 | 7137 | 6339 | 7704 | 6263 | 6183 | 8074 | 7553 | 8193 | 7074 | 6034 | 6955 | 7384 | 7143 | 6403 | 7757 | 6640 | 7292 | 5855 | 6050 | 7001 | 6346 | 6247 | 6675 | 4.4693 | 4.3562 | 4.5748 | 4.3978 | 4.2636 | 4.5836 | 4.5217 | 4.6128 | 4.567 | 4.1851 | 4.5401 | 4.5883 | 4.4748 | 4.3056 | 4.7009 | 4.4057 | 4.5831 | 4.2107 | 4.3157 | 4.5699 | 4.5384 | 4.4427 | 4.4429 | 69568 | 13932 | 53201 | 5855 | 15746 | 158302 | 4.4725 | 4.4944 | 4.4727 | 4.2107 | 4.5673 | 4.4631 | 4.7009 | 640.305 | 876.197 | 38.199 | 209.157 | 157.498 | 267.758 |  | 58.25 | 177136 | 240907 | 106.992 | 60.509 | 259.225 | 84.285 | 0.104 | 283.509 | 0 |  | 80025 | 232875 | 77220 | 188325 | 190350 |  | 177300 | 556000 | 391000 | 550400 | 383200 | 937600 | 937600 | 0 | 400 |  | 947000 | 937600 | 1.003% | 50.6 | 97 |  | 11.5167 | 788850 | 140 | 157245 | 159.01 | 1078
2026 | 2025 | 2025-04-01 | 30 | 2025-04-07 | 6:33 | 17:47 | 6994 | 6994 | 4730 | 3557 | 4459 | 4904 | 5075 | 5763 | 4743 | 5616 | 4858 | 4855 | 5622 | 3967 | 6654 | 6909 | 7527 | 5801 | 6680 | 5231 | 7588 | 5983 | 7679 | 4.129 | 4.187 | 3.498 | 3.411 | 3.693 | 3.551 | 3.6 | 3.835 | 3.878 | 3.78 | 3.713 | 3.705 | 3.824 | 3.456 | 4.229 | 4.252 | 4.332 | 3.91 | 4.181 | 3.815 | 4.512 | 4.222 | 4.447 | 55207 | 14436 | 45907 | 5801 | 10838 | 132189 | 3.833 | 4.292 | 3.9336 | 3.91 | 3.7175 | 3.92 | 4.512 | 640.305 | 876.632 | 39.211 | 209.533 | 158.299 | 268.546 |  | 59.026 | 177669 | 241263 | 107.65 | 60.95 | 259.778 | 84.837 | 0.105 | 283.929 | 0 |  | 71775 | 227700 | 62040 | 180225 | 177300 |  | 174600 | 533000 | 356000 | 526400 | 352800 | 884800 | 883200 | 1600 | 420 |  | 889000 | 883200 | 0.6567% | 50.6 | 97 |  | 11.2333 | 759825 | 140 | 133815 | 133.9 | 1533.4
2026 | 2025 | 2025-04-01 | 30 | 2025-04-08 | 6:31 | 18:07 | 10399 | 10405 | 9707 | 9033 | 11145 | 9282 | 9636 | 10607 | 8866 | 8819 | 9059 | 11610 | 8957 | 8357 | 8364 | 8951 | 9958 | 8543 | 8907 | 10225 | 10273 | 8376 | 10876 | 4.6 | 4.5 | 4.3 | 4.5 | 4.4 | 4.2 | 4.3 | 4.6 | 4.5 | 4.2 | 4.4 | 4.6 | 4.4 | 4.2 | 4.5 | 4.6 | 4.7 | 4.3 | 4.7 | 4.6 | 4.9 | 4.6 | 4.9 | 94404 | 18909 | 78256 | 8543 | 20243 | 220355 | 4.45 | 4.65 | 4.54 | 4.3 | 4.45 | 4.5 | 4.9 | 640.305 | 877.307 | 40.199 | 210.165 | 159.111 | 269.334 |  | 59.804 | 178204 | 241701 | 108.312 | 61.494 | 260.38 | 85.442 | 0.105 | 284.349 | 0 |  | 111375 | 222300 | 104280 | 182700 | 177300 |  | 175050 | 535000 | 438000 | 529600 | 435200 | 963200 | 968000 | 0 | 420 |  | 973000 | 963200 | 1.017% | 50.6 | 97 |  | 11.6 | 757350 | 140 | 215655 | 228.59 | 2026.3
2026 | 2025 | 2025-04-01 | 30 | 2025-04-09 | 6:31 | 18:06 | 6406 | 5773 | 7212 | 5946 | 5880 | 6510 | 6521 | 7421 | 6284 | 6493 | 5815 | 5288 | 5527 | 5696 | 5613 | 6555 | 6169 | 5911 | 6274 | 5667 | 7155 | 4808 | 7095 | 3.62 | 3.55 | 3.767 | 3.595 | 3.612 | 3.531 | 3.477 | 3.774 | 3.879 | 3.552 | 3.558 | 3.694 | 3.521 | 3.479 | 3.592 | 3.736 | 3.698 | 3.452 | 3.765 | 3.63 | 3.922 | 3.713 | 3.878 | 59991 | 12724 | 49451 | 5911 | 13942 | 142019 | 3.6178 | 3.717 | 3.6931 | 3.452 | 3.6255 | 3.652 | 3.922 | 640.305 | 877.754 | 41.25 | 210.574 | 159.999 | 270.174 |  | 60.61 | 178774 | 242078 | 109.18 | 61.951 | 260.967 | 86.029 | 0.106 | 284.769 | 0 |  | 73755 | 236475 | 67485 | 199800 | 189000 |  | 181350 | 570000 | 377000 | 694400 | 365600 | 939200 | 939200 | 1600 | 420 |  | 947000 | 937600 | 1.003% | 50.6 | 97 |  | 11.5833 | 806625 | 140 | 141240 | 144.28 | 5795.7
2026 | 2025 | 2025-04-01 | 30 | 2025-04-10 | 6:30 | 18:19 | 18091 | 18160 | 15791 | 14647 | 13620 | 16990 | 14732 | 16317 | 15895 | 14962 | 15270 | 14392 | 14848 | 14362 | 18953 | 19383 | 16956 | 15958 | 13455 | 12892 | 13976 | 10355 | 15608 | 6.5 | 6.5 | 6.4 | 6.1 | 6.3 | 6.4 | 6.1 | 6.3 | 6.2 | 6 | 6.5 | 6 | 6.2 | 6 | 7 | 6.7 | 6.5 | 6.3 | 5.9 | 6 | 6.2 | 6.2 | 6.2 | 153016 | 36339 | 119251 | 15958 | 31049 | 355613 | 6.25 | 6.6 | 6.25 | 6.3 | 6.2 | 6.2826 | 7 | 640.305 | 878.856 | 42.24 | 211.582 | 160.826 | 270.943 |  | 61.368 | 179304 | 242647 | 109.672 | 62.648 | 261.649 | 86.711 | 0.106 | 285.169 | 0 |  | 181830 | 222750 | 166320 | 186075 | 173025 |  | 170550 | 530000 | 569000 | 393600 | 557600 | 1091200 | 1091200 | 0 | 400 |  | 1099000 | 1091200 | 0.7148% | 50.6 | 97 |  | 11.8167 | 752400 | 140 | 348150 | 380.75 | 4769.9
2026 | 2025 | 2025-04-01 | 30 | 2025-04-11 | 6:28 | 17:45 | 20240 | 19245 | 20726 | 17597 | 16956 | 20457 | 19892 | 20233 | 19395 | 18548 | 20225 | 19407 | 19084 | 17670 | 19650 | 19541 | 15845 | 18466 | 17589 | 17471 | 18968 | 15788 | 19432 | 6.3587 | 6.2774 | 6.7293 | 6.0368 | 5.926 | 6.5355 | 6.4979 | 6.4988 | 6.4669 | 6.1411 | 6.6355 | 6.2297 | 6.1816 | 5.9574 | 6.4081 | 6.1938 | 6.1754 | 6.178 | 6.0685 | 6.0101 | 6.3496 | 6.7129 | 6.3566 | 190610 | 35386 | 147838 | 18466 | 40125 | 432425 | 6.272 | 6.1846 | 6.3658 | 6.178 | 6.4983 | 6.3011 | 6.7293 | 640.305 | 880.152 | 43.243 | 212.826 | 161.67 | 271.725 |  | 62.135 | 179842 | 243291 | 110.338 | 63.44 | 262.384 | 87.445 | 0.107 | 285.579 | 0 |  | 213840 | 225675 | 205260 | 189900 | 175950 |  | 172575 | 538000 | 644000 | 532800 | 633600 | 1176000 | 1174400 | 1600 | 410 |  | 1182000 | 1174400 | 0.6471% | 50.6 | 97 |  | 11.2833 | 764100 | 140 | 419100 | 432.78 | 84471.4
2026 | 2025 | 2025-04-01 | 30 | 2025-04-12 | 6:40 | 18:19 | 20467 | 19450 | 18406 | 15246 | 15683 | 17665 | 17448 | 18872 | 17354 | 16602 | 16569 | 17708 | 18146 | 16309 | 16850 | 20825 | 19950 | 15681 | 15602 | 15725 | 17772 | 17126 | 18023 | 6.7564 | 6.5984 | 6.614 | 6.0304 | 6.2253 | 6.3498 | 6.4127 | 6.6366 | 6.4263 | 6.1672 | 6.448 | 6.4024 | 6.4804 | 6.195 | 6.9491 | 6.7543 | 6.6955 | 6.2025 | 6.2299 | 6.2028 | 6.5525 | 6.5233 | 6.4628 | 172384 | 40775 | 138319 | 15681 | 36320 | 403479 | 6.4445 | 6.7249 | 6.4218 | 6.2025 | 6.5246 | 6.4485 | 6.9491 | 640.305 | 881.378 | 44.202 | 213.942 | 162.49 | 272.499 |  | 62.873 | 180367 | 243894 | 110.988 | 64.188 | 263.083 | 88.147 | 0.107 | 285.989 | 0 |  | 202290 | 215775 | 184140 | 184500 | 174150 |  | 166050 | 525000 | 603000 | 520000 | 598400 | 1118400 | 1123200 | 0 | 410 |  | 1128000 | 1118400 | 0.8584% | 50.6 | 97 |  | 11.65 | 740475 | 140 | 386430 | 407.49 | 37239.3
2026 | 2025 | 2025-04-01 | 30 | 2025-04-13 | 6:42 | 18:12 | 5946 | 5969 | 4631 | 3761 | 4457 | 4112 | 4207 | 5119 | 4790 | 4268 | 4441 | 4417 | 4799 | 4059 | 6551 | 6198 | 5838 | 4856 | 4726 | 3992 | 5037 | 4758 | 5435 | 4.2184 | 4.237 | 4.0257 | 3.94 | 4.073 | 3.8898 | 3.9454 | 4.1341 | 4.2905 | 3.8889 | 4.0788 | 3.9914 | 4.0718 | 3.9315 | 4.4312 | 4.2741 | 4.2375 | 4.0955 | 4.208 | 4.0798 | 4.2412 | 4.2055 | 4.1723 | 47830 | 12036 | 38319 | 4856 | 9326 | 112367 | 4.0925 | 4.2558 | 4.1129 | 4.0955 | 4.0398 | 4.1157 | 4.4312 | 640.305 | 881.725 | 45.252 | 214.256 | 163.376 | 273.319 |  | 63.686 | 180934 | 244239 | 111.688 | 64.612 | 263.648 | 88.713 | 0.108 | 286.409 | 0 |  | 57255 | 236250 | 51810 | 199350 | 184500 |  | 182925 | 567000 | 345000 | 560000 | 339200 | 904000 | 905600 | 1600 | 420 |  | 912000 | 902400 | 1.064% | 50.6 | 97 |  | 11.5 | 803025 | 140 | 109065 | 113.37 | 12860.3
2026 | 2025 | 2025-04-01 | 30 | 2025-04-14 | 6:29 | 18:11 | 6512 | 7623 | 7563 | 6712 | 5936 | 7444 | 7557 | 5745 | 6620 | 5726 | 5796 | 5187 | 5481 | 5339 | 7184 | 8830 | 7466 | 6716 | 4435 | 3947 | 7153 | 5602 | 6357 | 4.358 | 4.4084 | 4.6893 | 4.1294 | 4.117 | 4.3302 | 4.3735 | 5.1542 | 4.3556 | 4.1543 | 4.4115 | 4.2346 | 4.2382 | 4.1919 | 4.6157 | 4.5113 | 4.4996 | 4.2719 | 4.1092 | 3.986 | 4.3978 | 4.1826 | 4.1541 | 57170 | 16296 | 53447 | 6716 | 13302 | 146931 | 4.2989 | 4.5054 | 4.3603 | 4.2719 | 4.7638 | 4.3424 | 5.1542 | 640.305 | 882.222 | 46.289 | 214.632 | 164.29 | 274.162 |  | 64.501 | 181513 | 244614 | 112.404 | 65.072 | 264.241 | 89.305 | 0.108 | 286.839 | 0 |  | 82005 | 233325 | 62040 | 205650 | 189675 |  | 183375 | 579000 | 375000 | 572800 | 368000 | 948800 | 947200 | 0 | 430 |  | 954000 | 948800 | 0.5481% | 50.6 | 97 |  | 11.7 | 812025 | 140 | 144045 | 151.65 | 20864.4
2026 | 2025 | 2025-04-01 | 30 | 2025-04-15 | 6:27 | 18:09 | 13841 | 11740 | 11509 | 8772 | 9245 | 11248 | 11030 | 9392 | 10556 | 9559 | 11255 | 10815 | 10752 | 10492 | 12775 | 12217 | 13161 | 10364 | 9350 | 8955 | 9616 | 9465 | 8777 | 5.5261 | 5.142 | 5.3396 | 4.7129 | 4.8623 | 5.1074 | 5.1699 | 5.6603 | 5.1145 | 4.9597 | 5.3035 | 5.0659 | 5.0715 | 5.0263 | 5.6831 | 5.1848 | 5.4165 | 4.994 | 5.0572 | 4.8699 | 4.9825 | 4.9722 | 4.7276 | 109303 | 25378 | 79419 | 10364 | 20422 | 244886 | 5.1903 | 5.3006 | 5.0451 | 4.994 | 5.4151 | 5.1282 | 5.6831 | 640.305 | 882.955 | 47.165 | 215.33 | 165.109 | 274.953 |  | 65.197 | 182032 | 245047 | 113.046 | 65.607 | 264.83 | 89.897 | 0.108 | 287.269 | 0 |  | 120945 | 197100 | 115170 | 184275 | 177975 |  | 156600 | 519000 | 433000 | 513600 | 428000 | 942400 | 947200 | 0 | 430 |  | 952000 | 942400 | 1.019% | 50.6 | 97 |  | 11.7 | 715950 | 140 | 236115 | 246.29 | 33862.6
2026 | 2025 | 2025-04-01 | 30 | 2025-04-16 | 6:28 | 18:17 | 11361 | 10272 | 10945 | 6535 | 6766 | 10263 | 10292 | 9359 | 7301 | 10669 | 7405 | 9479 | 9385 | 9435 | 11916 | 11564 | 8441 | 9584 | 8857 | 7346 | 7652 | 6969 | 7874 | 5.4833 | 5.3687 | 5.6931 | 4.9092 | 4.9214 | 5.4969 | 5.5145 | 6.1219 | 5.042 | 5.3274 | 5.4621 | 5.2452 | 5.212 | 5.1626 | 5.7054 | 5.5232 | 5.1554 | 5.1883 | 5.1402 | 4.8834 | 4.9967 | 4.9658 | 4.9222 | 96798 | 20005 | 63632 | 9584 | 19651 | 209670 | 5.3315 | 5.3393 | 5.2259 | 5.1883 | 5.8182 | 5.28 | 6.1219 | 640.305 | 883.565 | 48.262 | 215.958 | 166 | 275.788 |  | 66.027 | 182608 | 245498 | 113.757 | 66.158 | 265.466 | 90.534 | 0.108 | 287.679 | 0 |  | 100650 | 246825 | 103620 | 200475 | 187875 |  | 186750 | 576000 | 451000 | 568800 | 440800 | 1017600 | 1019200 | 0 | 410 |  | 1027000 | 1017600 | 0.9237% | 50.6 | 97 |  | 11.8167 | 821925 | 140 | 204270 | 216.2 | 32720.7
2026 | 2025 | 2025-04-01 | 30 | 2025-04-17 | 6:28 | 18:20 | 9772 | 10342 | 10206 | 8098 | 8625 | 9860 | 9817 | 9374 | 9592 | 9290 | 9386 | 9380 | 8996 | 8261 | 11998 | 12620 | 11412 | 8939 | 8068 | 8041 | 9088 | 9393 | 9168 | 5.4014 | 5.1597 | 5.3432 | 4.815 | 5.0011 | 5.1464 | 5.1491 | 5.7761 | 5.1628 | 5.1372 | 5.3317 | 5.1402 | 5.0588 | 4.9449 | 5.6409 | 5.4102 | 5.3389 | 4.9691 | 5.0251 | 4.9923 | 5.0921 | 5.2181 | 4.9953 | 93398 | 24032 | 74166 | 8939 | 19191 | 219726 | 5.2016 | 5.3745 | 5.1516 | 4.9691 | 5.4626 | 5.1848 | 5.7761 | 640.305 | 884.247 | 49.346 | 216.564 | 166.895 | 276.638 |  | 66.839 | 183183 | 245953 | 114.469 | 66.717 | 266.106 | 91.174 | 0.108 | 288.079 | 0 |  | 112530 | 243900 | 99990 | 201375 | 191250 |  | 182700 | 575000 | 455000 | 569600 | 447200 | 1024000 | 1024000 | 0 | 400 |  | 1030000 | 1024000 | 0.5859% | 50.6 | 97 |  | 11.8667 | 819225 | 140 | 212520 | 220.44 | 41594.7
2026 | 2025 | 2025-04-01 | 30 | 2025-04-18 | 6:44 | 17:33 | 12808 | 11807 | 11674 | 8435 | 10493 | 11735 | 12237 | 9902 | 10463 | 11385 | 11029 | 10355 | 10391 | 9751 | 12865 | 12766 | 12559 | 10533 | 10602 | 8895 | 11405 | 10986 | 12052 | 5.5486 | 5.4299 | 5.5862 | 5.0109 | 5.2796 | 5.3825 | 5.5176 | 5.7738 | 5.2651 | 5.4275 | 5.5539 | 5.2747 | 5.2351 | 5.1376 | 5.7292 | 5.4975 | 5.5307 | 5.236 | 5.4044 | 5.1045 | 5.4726 | 5.3882 | 5.4207 | 109755 | 25325 | 87376 | 10533 | 22139 | 255128 | 5.4002 | 5.5141 | 5.3941 | 5.236 | 5.6457 | 5.4003 | 5.7738 | 640.305 | 885.043 | 50.381 | 217.272 | 167.742 | 277.439 |  | 67.622 | 183730 | 246434 | 115.145 | 67.31 | 266.744 | 91.811 | 0.108 | 288.479 | 0 |  | 131340 | 232875 | 116820 | 190575 | 180225 |  | 176175 | 547000 | 481000 | 540800 | 474400 | 1020800 | 1019200 | 0 | 400 |  | 1028000 | 1020800 | 0.7053% | 50.6 | 97 |  | 10.8167 | 779850 | 140 | 248160 | 256.23 | 56297.5
2026 | 2025 | 2025-04-01 | 30 | 2025-04-19 | 6:28 | 18:20 | 14235 | 14095 | 10954 | 8632 | 9951 | 10374 | 10202 | 11727 | 10198 | 10157 | 9254 | 10416 | 11095 | 9675 | 15781 | 15393 | 14814 | 10586 | 11387 | 8496 | 12679 | 10946 | 13119 | 5.7085 | 5.6039 | 5.4379 | 4.917 | 5.1716 | 5.2155 | 5.2399 | 6.0519 | 5.2417 | 5.2126 | 5.4825 | 5.2331 | 5.2883 | 5.1263 | 6.0562 | 5.738 | 5.697 | 5.2406 | 5.42 | 5.0011 | 5.5772 | 5.362 | 5.4985 | 111450 | 30207 | 89994 | 10586 | 21929 | 264166 | 5.3966 | 5.7175 | 5.3879 | 5.2406 | 5.6459 | 5.414 | 6.0562 | 640.305 | 885.861 | 51.067 | 217.995 | 168.604 | 278.287 |  | 68.45 | 184301 | 246843 | 115.852 | 67.816 | 267.35 | 92.42 | 0.108 | 288.909 | 0 |  | 134970 | 154350 | 119295 | 193950 | 190800 |  | 186300 | 571000 | 409000 | 565600 | 404800 | 969600 | 974400 | 0 | 430 |  | 980000 | 969600 | 1.073% | 50.6 | 97 |  | 11.8667 | 725400 | 140 | 254265 | 265.03 | 25642.7
2026 | 2025 | 2025-04-01 | 30 | 2025-04-20 | 6:27 | 17:50 | 7376 | 12342 | 9922 | 7354 | 8976 | 9264 | 8841 | 9286 | 8663 | 8678 | 9447 | 8585 | 9616 | 8478 | 11655 | 14893 | 10732 | 8714 | 9334 | 7979 | 10098 | 9165 | 11184 | 5.3279 | 5.8837 | 5.5373 | 4.9707 | 5.3031 | 5.2867 | 5.7041 | 5.2266 | 5.1818 | 5.0525 | 5.3326 | 5.0568 | 5.1719 | 4.9786 | 5.6322 | 6.0958 | 6.2723 | 5.3785 | 5.2539 | 5.0099 | 5.7485 | 5.3867 | 5.7362 | 91070 | 25625 | 77046 | 8714 | 18127 | 220582 | 5.2354 | 6.184 | 5.4428 | 5.3785 | 5.4653 | 5.4143 | 6.2723 | 640.305 | 886.546 | 52.054 | 218.584 | 169.476 | 279.115 |  | 69.208 | 184855 | 247276 | 116.536 | 68.346 | 267.961 | 93.032 | 0.108 | 289.279 | 0 |  | 113025 | 222075 | 97185 | 196200 | 186300 |  | 170550 | 554000 | 433000 | 547200 | 424000 | 977600 | 979200 | 0 | 370 |  | 987000 | 977600 | 0.9615% | 50.6 | 97 |  | 11.3833 | 775125 | 140 | 210210 | 220.06 | 27339.5
2026 | 2025 | 2025-04-01 | 30 | 2025-04-21 | 6:32 | 18:19 | 5783 | 4905 | 5957 | 3381 | 4835 | 5656 | 2096 | 5640 | 5466 | 5617 | 5250 | 4105 | 3984 | 3695 | 6573 | 6429 | 6413 | 4425 | 5329 | 4111 | 5871 | 4985 | 7240 | 4.2072 | 4.1499 | 4.0071 | 3.7903 | 4.0986 | 4.6774 | 4.037 | 4.1903 | 4.4013 | 4.0243 | 4.1272 | 3.8245 | 3.9978 | 3.7505 | 4.4705 | 4.3581 | 4.4692 | 4.1081 | 4.2639 | 3.9414 | 4.4855 | 4.3378 | 4.6273 | 50404 | 12842 | 42339 | 4425 | 7736 | 117746 | 4.0615 | 4.4136 | 4.2795 | 4.1081 | 4.1137 | 4.1889 | 4.6774 | 640.305 | 886.919 | 53.128 | 218.915 | 170.369 | 279.874 |  | 70.024 | 185410 | 247632 | 117.223 | 68.785 | 268.526 | 93.597 | 0.108 | 289.669 | 0 |  | 61545 | 241650 | 54615 | 200925 | 170775 |  | 183600 | 555000 | 356000 | 549600 | 351200 | 904000 | 904000 | 0 | 390 |  | 911000 | 904000 | 0.7743% | 50.6 | 97 |  | 11.7833 | 796950 | 140 | 116160 | 130.46 | 100864.8
2026 | 2025 | 2025-04-01 | 30 | 2025-04-22 | 6:23 | 18:05 | 4192 | 5108 | 4790 | 2836 | 3587 | 4421 | 4694 | 4847 | 4541 | 4268 | 3719 | 3889 | 3980 | 3411 | 4924 | 7253 | 5893 | 4173 | 3629 | 3295 | 5005 | 4361 | 5811 | 4.284 | 4.4805 | 4.0756 | 3.6801 | 3.8617 | 3.9126 | 4.0263 | 4.1261 | 4.1904 | 4.0197 | 4.0437 | 3.8765 | 3.9529 | 3.7904 | 4.603 | 4.4978 | 4.349 | 4.0428 | 3.9966 | 3.8932 | 4.254 | 4.1868 | 4.4719 | 40097 | 13146 | 35670 | 4173 | 9541 | 102627 | 4.0536 | 4.4234 | 4.119 | 4.0428 | 4.0762 | 4.1137 | 4.603 | 640.305 | 887.257 | 54.165 | 219.182 | 171.24 | 280.694 |  | 70.806 | 185967 | 247964 | 117.911 | 69.195 | 269.078 | 94.148 | 0.109 | 290.079 | 0 |  | 55770 | 233325 | 44055 | 195975 | 184500 |  | 175950 | 557000 | 332000 | 550400 | 328000 | 883200 | 881600 | 1600 | 410 |  | 889000 | 881600 | 0.8394% | 50.6 | 97 |  | 11.7 | 789750 | 140 | 99825 | 106.17 | 16397.6
2026 | 2025 | 2025-04-01 | 30 | 2025-04-23 | 6:27 | 18:10 | 5919 | 6384 | 6435 | 4489 | 4834 | 5720 | 5741 | 6362 | 4994 | 5517 | 5682 | 5475 | 5625 | 4787 | 7214 | 7325 | 6587 | 5239 | 4942 | 4051 | 5288 | 4837 | 5806 | 4.903 | 4.421 | 4.366 | 3.913 | 4.061 | 4.125 | 4.133 | 4.348 | 4.175 | 4.117 | 4.268 | 4.238 | 4.236 | 3.987 | 5.387 | 4.418 | 4.446 | 4.176 | 4.31 | 4.015 | 4.223 | 4.272 | 4.223 | 55647 | 13912 | 42352 | 5239 | 12103 | 129253 | 4.3827 | 4.432 | 4.1894 | 4.176 | 4.2405 | 4.294 | 5.387 | 640.305 | 887.65 | 55.257 | 219.548 | 172.134 | 281.531 |  | 71.64 | 186544 | 248334 | 118.625 | 69.651 | 269.665 | 94.736 | 0.109 | 290.479 | 0 |  | 64845 | 245700 | 60390 | 201150 | 188325 |  | 187650 | 577000 | 370000 | 571200 | 364800 | 939200 | 940800 | 0 | 400 |  | 947000 | 939200 | 0.8305% | 50.6 | 97 |  | 11.7167 | 822825 | 140 | 125235 | 130.34 | 14182.9
2026 | 2025 | 2025-04-01 | 30 | 2025-04-24 | 6:24 | 18:10 | 7103 | 7952 | 5849 | 5129 | 5831 | 5879 | 5747 | 6005 | 5974 | 5570 | 5857 | 5932 | 6457 | 5704 | 7937 | 8790 | 8226 | 6260 | 5189 | 5173 | 6596 | 6222 | 7236 | 4.903 | 4.5043 | 4.28 | 3.9862 | 4.2342 | 4.1515 | 4.1286 | 4.3537 | 4.3074 | 4.1912 | 4.3533 | 4.257 | 4.3516 | 4.1738 | 5.1147 | 4.5262 | 4.5804 | 4.2708 | 4.3647 | 4.105 | 4.3636 | 4.3592 | 4.3867 | 60771 | 17016 | 50819 | 6260 | 11752 | 146618 | 4.4094 | 4.5533 | 4.2775 | 4.2708 | 4.2412 | 4.3586 | 5.1147 | 640.305 | 888.118 | 56.319 | 219.942 | 173.029 | 282.384 |  | 72.443 | 187118 | 248715 | 119.335 | 70.121 | 270.257 | 95.329 | 0.11 | 290.889 | 0 |  | 77220 | 238950 | 65010 | 201375 | 191925 |  | 180675 | 574000 | 381000 | 568000 | 376000 | 947200 | 948800 | 1600 | 410 |  | 955000 | 945600 | 0.9941% | 50.6 | 97 |  | 11.7667 | 812925 | 140 | 142230 | 148.16 | 37616.5
2026 | 2025 | 2025-04-01 | 30 | 2025-04-25 | 6:24 | 18:08 | 8326 | 9431 | 9036 | 6719 | 8532 | 8704 | 8738 | 8362 | 7584 | 8067 | 9062 | 8275 | 8335 | 7868 | 9693 | 9344 | 10225 | 8417 | 7351 | 6822 | 9055 | 8675 | 9628 | 5.1425 | 4.85 | 4.8926 | 4.367 | 4.7628 | 4.6286 | 4.6462 | 4.8133 | 4.6296 | 4.8517 | 4.9775 | 4.7328 | 4.778 | 4.7162 | 5.616 | 4.7837 | 4.9883 | 4.7504 | 4.8802 | 4.5929 | 4.8546 | 4.7965 | 4.8297 | 82835 | 19569 | 68328 | 8417 | 17100 | 196249 | 4.918 | 4.886 | 4.7178 | 4.7504 | 4.7297 | 4.8209 | 5.616 | 640.305 | 888.729 | 57.312 | 220.479 | 173.874 | 283.186 |  | 73.199 | 187659 | 249127 | 120.003 | 70.631 | 270.847 | 95.92 | 0.11 | 291.299 | 0 |  | 100815 | 223425 | 88605 | 190125 | 180450 |  | 170100 | 541000 | 412000 | 534400 | 408000 | 944000 | 945600 | 0 | 410 |  | 953000 | 944000 | 0.9534% | 50.6 | 97 |  | 11.7333 | 764100 | 140 | 189420 | 197.44 | 59412
2026 | 2025 | 2025-04-01 | 30 | 2025-04-26 | 6:20 | 18:08 | 6642 | 1798 | 6473 | 1383 | 1236 | 1863 | 1888 | 6310 | 1673 | 4944 | 6455 | 6960 | 6484 | 5905 | 6535 | 1856 | 1723 | 1069 | 5119 | 5568 | 1546 | 1375 | 1065 | 4.7704 | 3.6542 | 4.34 | 3.2401 | 3.2679 | 3.4812 | 3.4955 | 4.286 | 3.6237 | 4.551 | 4.352 | 4.2794 | 4.2708 | 4.0802 | 4.9561 | 3.6362 | 3.6278 | 3.2408 | 4.1677 | 4.1368 | 3.6599 | 3.5113 | 3.344 | 61085 | 3579 | 11939 | 1069 | 8198 | 85870 | 4.3904 | 3.632 | 3.5564 | 3.2408 | 3.8907 | 3.9119 | 4.9561 | 640.305 | 888.838 | 58.231 | 220.878 | 174.642 | 283.9 |  | 73.897 | 188149 | 249417 | 120.61 | 70.989 | 271.331 | 96.404 | 0.111 | 291.719 | 0 |  | 17985 | 206775 | 65835 | 172800 | 160650 |  | 157050 | 490000 | 290000 | 485600 | 286400 | 774400 | 774400 | 1600 | 420 |  | 780000 | 772800 | 0.9317% | 50.6 | 97 |  | 11.8 | 697275 | 140 | 83820 | 82.27 | 83700.8
2026 | 2025 | 2025-04-01 | 30 | 2025-04-27 | 6:27 | 17:53 | 6782 | 5901 | 6955 | 5344 | 4877 | 4895 | 4864 | 7303 | 6208 | 5726 | 6252 | 6534 | 7323 | 6736 | 8022 | 7392 | 6007 | 5339 | 7472 | 6618 | 7161 | 6117 | 7149 | 4.7677 | 4.2543 | 4.4301 | 3.9238 | 3.9386 | 3.9452 | 3.9023 | 4.4648 | 4.4296 | 4.5573 | 4.3703 | 4.269 | 4.4084 | 4.3093 | 5.1667 | 4.4825 | 4.3458 | 4.0163 | 4.6276 | 4.3409 | 4.6108 | 4.3241 | 4.3988 | 68420 | 13399 | 47652 | 5339 | 12167 | 146977 | 4.5247 | 4.4141 | 4.2192 | 4.0163 | 4.1835 | 4.3602 | 5.1667 | 640.305 | 889.256 | 58.996 | 221.321 | 175.36 | 284.587 |  | 74.562 | 188615 | 249729 | 121.186 | 71.375 | 271.812 | 96.886 | 0.111 | 292.119 | 0 |  | 68970 | 172125 | 73095 | 161550 | 154575 |  | 149625 | 466000 | 312000 | 460800 | 308800 | 769600 | 771200 | 0 | 400 |  | 778000 | 769600 | 1.091% | 50.6 | 97 |  | 11.4333 | 637875 | 140 | 142065 | 148.97 | 119321.6
2026 | 2025 | 2025-04-01 | 30 | 2025-04-28 | 6:18 | 18:15 | 2016 | 1856 | 2188 | 1671 | 1586 | 2259 | 1949 | 2492 | 1917 | 1817 | 2056 | 2135 | 1913 | 1442 | 1823 | 2163 | 2068 | 1656 | 1624 | 1426 | 2048 | 1789 | 1938 | 3.523 | 3.2092 | 3.2194 | 2.8944 | 3.0124 | 3.1149 | 3.0214 | 3.3081 | 3.4388 | 3.3643 | 3.1322 | 3.19 | 3.188 | 2.9921 | 3.4303 | 3.2979 | 3.2638 | 3.0875 | 3.2929 | 3.1208 | 3.4016 | 3.2441 | 3.2958 | 18440 | 4231 | 15064 | 1656 | 4441 | 43832 | 3.2453 | 3.2808 | 3.1941 | 3.0875 | 3.1648 | 3.2192 | 3.523 | 640.305 | 889.394 | 60.053 | 221.449 | 176.242 | 285.408 |  | 75.37 | 189180 | 250008 | 121.885 | 71.721 | 272.337 | 97.41 | 0.112 | 292.529 | 0 |  | 22770 | 237825 | 21120 | 198450 | 184725 |  | 181800 | 565000 | 279000 | 559200 | 276800 | 840000 | 838400 | 1600 | 410 |  | 844000 | 838400 | 0.6679% | 50.6 | 97 |  | 11.95 | 802800 | 140 | 43890 | 45.94 | 83886.8
2026 | 2025 | 2025-04-01 | 30 | 2025-04-29 | 6:44 | 18:34 | 6461 | 7606 | 6129 | 5774 | 6443 | 6553 | 6753 | 5795 | 3484 | 5783 | 5714 | 5863 | 5835 | 5658 | 7105 | 8619 | 7690 | 6564 | 5499 | 3817 | 6509 | 6069 | 6662 | 4.4688 | 4.4705 | 4.5167 | 4.2465 | 4.3123 | 4.366 | 4.4511 | 4.3702 | 5.0233 | 4.3997 | 4.4839 | 4.2718 | 4.361 | 4.2451 | 4.6965 | 4.5445 | 4.559 | 4.3603 | 4.3313 | 4.0936 | 4.4714 | 4.4003 | 4.3564 | 57864 | 16309 | 49100 | 6564 | 12548 | 142385 | 4.3868 | 4.5518 | 4.4468 | 4.3603 | 4.4107 | 4.4261 | 5.0233 | 640.305 | 889.86 | 61.062 | 221.825 | 177.075 | 286.19 |  | 76.117 | 189712 | 250372 | 122.542 | 72.173 | 272.892 | 97.967 | 0.113 | 292.929 | 0 |  | 76890 | 227025 | 62040 | 187425 | 175950 |  | 168075 | 532000 | 364000 | 525600 | 361600 | 888000 | 891200 | 1600 | 400 |  | 896000 | 886400 | 1.083% | 50.6 | 97 |  | 11.8333 | 758475 | 140 | 138930 | 147.48 | 56151.5
2026 | 2025 | 2025-04-01 | 30 | 2025-04-30 | 6:29 | 18:33 | 17597 | 17634 | 14004 | 12995 | 14220 | 13677 | 14096 | 14725 | 14379 | 14115 | 13745 | 14532 | 14942 | 11305 | 18819 | 19672 | 17433 | 13584 | 13631 | 13622 | 14655 | 14104 | 16090 | 6.156 | 6.176 | 5.951 | 5.552 | 5.86 | 5.688 | 5.854 | 5.873 | 6.475 | 5.745 | 5.931 | 5.768 | 5.875 | 5.621 | 6.599 | 6.402 | 6.179 | 5.819 | 5.829 | 5.77 | 6.095 | 5.962 | 5.974 | 146312 | 37105 | 117754 | 13584 | 28821 | 343576 | 5.9245 | 6.2905 | 5.9509 | 5.819 | 5.8635 | 5.9632 | 6.599 | 640.305 | 890.926 | 62.072 | 222.778 | 177.935 | 287.015 |  | 76.89 | 190265 | 250932 | 123.226 | 72.865 | 273.583 | 98.658 | 0.113 | 293.329 | 0 |  | 175890 | 227250 | 157245 | 193500 | 185625 |  | 173925 | 553000 | 560000 | 547200 | 553600 | 1105600 | 1105600 | 0 | 400 |  | 1113000 | 1105600 | 0.6693% | 50.6 | 97 |  | 12.0667 | 780300 | 140 | 333135 | 334.67 | 13262.3
2026 | 2025 | 2025-05-01 | 31 | 2025-05-01 | 6:22 | 18:24 | 14828 | 14629 | 14855 | 12349 | 13455 | 13808 | 14080 | 14946 | 13244 | 13420 | 13730 | 14586 | 13997 | 13494 | 15792 | 14828 | 15483 | 12268 | 12950 | 12449 | 12701 | 12424 | 12843 | 5.4022 | 5.4347 | 5.5438 | 4.9366 | 5.2483 | 5.2449 | 5.2937 | 5.3839 | 5.3247 | 5.1284 | 5.3754 | 5.2928 | 5.2882 | 5.1956 | 5.8546 | 5.4567 | 5.5794 | 5.1316 | 5.2639 | 5.146 | 5.4618 | 5.3013 | 5.231 | 140101 | 30311 | 105453 | 12268 | 29026 | 317159 | 5.3491 | 5.5181 | 5.2861 | 5.1316 | 5.3388 | 5.3269 | 5.8546 | 640.305 | 891.868 | 63.187 | 223.689 | 178.846 | 287.874 |  | 77.741 | 190855 | 251489 | 123.955 | 73.545 | 274.293 | 99.37 | 0.113 | 293.759 | 0 |  | 155430 | 250875 | 150315 | 204975 | 193275 |  | 191475 | 590000 | 557000 | 583200 | 544000 | 1136000 | 1139200 | 0 | 430 |  | 1147000 | 1136000 | 0.9683% | 50.6 | 97 |  | 12.0333 | 840600 | 140 | 305745 | 317.83 | 15156.6
2026 | 2025 | 2025-05-01 | 31 | 2025-05-02 | 6:17 | 18:25 | 11584 | 11581 | 9836 | 8432 | 9539 | 9306 | 9821 | 10481 | 8829 | 9511 | 9514 | 9597 | 9405 | 8826 | 12231 | 12209 | 12270 | 9915 | 10073 | 8352 | 9822 | 9236 | 10729 | 4.7864 | 4.9094 | 4.6816 | 4.3501 | 4.5397 | 4.3622 | 4.5664 | 4.7148 | 4.5773 | 4.4481 | 4.5826 | 4.5089 | 4.5266 | 4.5474 | 5.1014 | 4.9435 | 4.9807 | 4.6319 | 4.7373 | 4.4385 | 4.7607 | 4.6058 | 4.6576 | 98929 | 24479 | 77474 | 9915 | 20302 | 231099 | 4.6359 | 4.9621 | 4.6044 | 4.6319 | 4.6406 | 4.6504 | 5.1014 | 640.305 | 892.581 | 64.267 | 224.34 | 179.74 | 288.709 |  | 78.569 | 191431 | 251954 | 124.667 | 74.118 | 274.941 | 100.017 | 0.114 | 294.189 | 0 |  | 117645 | 243000 | 107415 | 201150 | 187875 |  | 186300 | 576000 | 465000 | 569600 | 458400 | 1036800 | 1035200 | 1600 | 430 |  | 1041000 | 1035200 | 0.5603% | 50.6 | 97 |  | 12.1333 | 818325 | 140 | 225060 | 232.32 | 9561.7
2026 | 2025 | 2025-05-01 | 31 | 2025-05-03 | 7:18 | 18:23 | 15451 | 15572 | 14282 | 12428 | 12805 | 12956 | 12933 | 13781 | 12469 | 12513 | 12862 | 13719 | 12220 | 12474 | 15492 | 17153 | 15488 | 13003 | 12292 | 11413 | 13823 | 12029 | 14028 | 5.5536 | 5.6249 | 5.592 | 5.1438 | 5.2554 | 5.281 | 5.3061 | 5.5104 | 5.3333 | 5.1531 | 5.4136 | 5.3184 | 5.1606 | 5.1638 | 5.7602 | 5.7746 | 5.633 | 5.2665 | 5.2189 | 5.0994 | 5.6325 | 5.2694 | 5.4929 | 132718 | 32641 | 106110 | 13003 | 26714 | 311186 | 5.3434 | 5.7038 | 5.385 | 5.2665 | 5.4082 | 5.3895 | 5.7746 | 640.305 | 893.542 | 65.11 | 225.2 | 180.491 | 289.457 |  | 79.197 | 191909 | 252444 | 125.259 | 74.715 | 275.541 | 100.618 | 0.114 | 294.559 | 0 |  | 158565 | 189675 | 141900 | 168975 | 168300 |  | 141300 | 478000 | 490000 | 473600 | 477600 | 960000 | 961600 | 0 | 370 |  | 968000 | 960000 | 0.8333% | 50.6 | 96 |  | 11.0833 | 668250 | 140 | 300465 | 302.2 | 20011.7
2026 | 2025 | 2025-05-01 | 31 | 2025-05-04 | 6:48 | 18:21 | 17864 | 17151 | 11955 | 11735 | 13455 | 11870 | 11924 | 14110 | 13220 | 13607 | 13181 | 13309 | 14420 | 13809 | 15201 | 17996 | 18387 | 14694 | 15810 | 12310 | 15484 | 15232 | 17474 | 5.9703 | 5.94 | 5.4356 | 5.31 | 5.6028 | 5.4019 | 5.4627 | 5.6055 | 5.5804 | 5.4497 | 5.6289 | 5.5217 | 5.5558 | 5.4036 | 6.3705 | 5.9948 | 6.2004 | 5.6997 | 5.8227 | 5.4159 | 6.0282 | 5.8895 | 5.9169 | 141466 | 36383 | 115621 | 14694 | 26034 | 334198 | 5.6575 | 6.0976 | 5.6738 | 5.6997 | 5.5341 | 5.7047 | 6.3705 | 640.305 | 894.583 | 66.209 | 226.115 | 181.402 | 290.307 |  | 80.034 | 192494 | 253015 | 125.982 | 75.414 | 276.257 | 101.335 | 0.115 | 294.929 | 0 |  | 171765 | 247275 | 150975 | 204975 | 191250 |  | 188325 | 585000 | 571000 | 578400 | 559200 | 1145600 | 1147200 | 1600 | 370 |  | 1156000 | 1144000 | 1.049% | 50.6 | 96 |  | 11.55 | 831825 | 140 | 322740 | 341.49 | 83886.8
2026 | 2025 | 2025-05-01 | 31 | 2025-05-05 | 6:14 | 18:23 | 13856 | 11897 | 12195 | 10427 | 10758 | 11122 | 11292 | 9120 | 11132 | 10081 | 11014 | 11474 | 11375 | 11161 | 5409 | 14202 | 13120 | 11439 | 10961 | 9154 | 10379 | 12045 | 11092 | 5.1567 | 4.8761 | 4.9432 | 4.6751 | 4.7746 | 4.7746 | 4.81 | 4.7983 | 4.9877 | 4.5219 | 4.9682 | 4.8138 | 4.8626 | 4.7191 | 5.3055 | 5.1841 | 5.1286 | 4.8882 | 4.9161 | 4.6929 | 4.9473 | 5.1008 | 4.8545 | 106680 | 27322 | 88852 | 11439 | 20412 | 254705 | 4.89 | 5.1563 | 4.8599 | 4.8882 | 4.8042 | 4.9 | 5.3055 | 640.305 | 895.395 | 67.314 | 226.804 | 182.309 | 291.186 |  | 80.871 | 193084 | 253508 | 126.712 | 76.025 | 276.931 | 102.008 | 0.115 | 295.339 | 0 |  | 133980 | 248625 | 113685 | 204075 | 197775 |  | 188325 | 590000 | 493000 | 584000 | 488800 | 1078400 | 1076800 | 0 | 410 |  | 1083000 | 1078400 | 0.4266% | 50.6 | 96 |  | 12.15 | 838800 | 140 | 247665 | 255.52 | 10865.9
2026 | 2025 | 2025-05-01 | 31 | 2025-05-06 | 6:18 | 17:55 | 18672 | 18446 | 12837 | 12887 | 14149 | 13250 | 13491 | 13440 | 19257 | 15579 | 12142 | 18446 | 12887 | 14149 | 13250 | 13332 | 13582 | 18909 | 18828 | 14763 | 16484 | 16123 | 17458 | 5.921 | 5.943 | 5.382 | 5.206 | 5.417 | 5.326 | 5.36 | 5.488 | 5.493 | 5.316 | 5.505 | 5.223 | 5.361 | 5.25 | 6.289 | 6.01 | 5.987 | 5.581 | 5.681 | 5.281 | 5.834 | 5.734 | 5.71 | 151553 | 26914 | 128054 | 18909 | 26931 | 352361 | 5.5209 | 5.9985 | 5.5511 | 5.581 | 5.424 | 5.5782 | 6.289 | 640.305 | 896.484 | 68.367 | 227.721 | 183.191 | 292.004 |  | 81.673 | 193647 | 254077 | 127.408 | 76.723 | 277.632 | 102.711 | 0.115 | 295.739 | 0 |  | 179685 | 236925 | 151305 | 198450 | 184050 |  | 180450 | 563000 | 569000 | 556800 | 558400 | 1121600 | 1124800 | 0 | 400 |  | 1132000 | 1121600 | 0.9272% | 50.6 | 96 |  | 11.6167 | 799875 | 140 | 330990 | 345.81 | 23746.7
2026 | 2025 | 2025-05-01 | 31 | 2025-05-07 | 6:17 | 18:22 | 15061.9 | 14771.5 | 11602.4 | 10491.1 | 11202.7 | 10879.8 | 11509.5 | 11300.9 | 11025.5 | 11303.6 | 10290.2 | 11536.9 | 12171.7 | 10826.9 | 16555.4 | 16580.3 | 15773.8 | 13009.2 | 12714.7 | 10172.5 | 12804.2 | 12778.4 | 14209.4 | 5.4 | 5.3 | 5 | 4.9 | 5 | 4.8 | 5 | 5.1 | 5.1 | 4.9 | 5 | 5 | 5.1 | 4.9 | 5.8 | 5.5 | 5.5 | 5.2 | 5.2 | 4.9 | 5.3 | 5.3 | 5.2 | 122236.2 | 32354.1 | 98162.6 | 13009.2 | 22810.4 | 288572.5 | 5.12 | 5.5 | 5.1 | 5.2 | 5.05 | 5.1478 | 5.8 | 640.305 | 897.39 | 69.465 | 228.511 | 184.113 | 292.855 |  | 82.5 | 194232 | 254603 | 128.131 | 77.363 | 278.321 | 103.399 | 0.115 | 296.149 | 223.819 |  | 149490 | 247050 | 130350 | 207450 | 191475 |  | 186075 | 585000 | 526000 | 578400 | 512000 | 1102400 | 1100800 | 0 | 410 | 223819 | 1111000 | 1102400 | 0.7801% | 50.6 | 96 |  | 12.0833 | 832050 | 140 | 279840 | 289.12 | 8666.7
2026 | 2025 | 2025-05-01 | 31 | 2025-05-08 | 6:18 | 18:16 | 15071 | 14029 | 11404 | 11691 | 11962 | 11129 | 11155 | 10543 | 10843 | 9210 | 11003 | 12716 | 12267 | 10487 | 15924 | 14273 | 15408 | 12365 | 12187 | 10838 | 13414 | 12814 | 14777 | 5.575 | 5.462 | 5.23 | 5.175 | 5.254 | 5.082 | 5.162 | 5.164 | 5.147 | 4.97 | 5.243 | 5.297 | 5.22 | 4.969 | 6.025 | 5.488 | 5.679 | 5.27 | 5.289 | 5.107 | 5.612 | 5.476 | 5.49 | 121107 | 29681 | 100659 | 12365 | 21698 | 285510 | 5.2925 | 5.5835 | 5.3024 | 5.27 | 5.163 | 5.3211 | 6.025 | 640.305 | 898.291 | 70.508 | 229.289 | 185.012 | 293.7 |  | 83.281 | 194801 | 255115 | 128.834 | 77.988 | 278.991 | 104.071 | 0.116 | 296.419 | 223.989 |  | 148665 | 234675 | 128370 | 202275 | 190125 |  | 175725 | 569000 | 512000 | 562400 | 500000 | 1072000 | 1075200 | 1600 | 270 | 170 | 1081000 | 1070400 | 0.9903% | 50.6 | 96 |  | 11.9667 | 802800 | 140 | 277035 | 287.2 | 70953.8
2026 | 2025 | 2025-05-01 | 31 | 2025-05-09 | 6:17 | 18:22 | 5141.3 | 6008.8 | 3089.2 | 4293.5 | 3729.6 | 3314.7 | 3297.2 | 3508.5 | 4645 | 3675.9 | 3178 | 4491.9 | 4887.7 | 3832.4 | 5751.4 | 7103.6 | 5972.1 | 3607.3 | 4476.4 | 4427.8 | 4755.5 | 4670.4 | 5813.9 | 4.2 | 4.4 | 3.7 | 4 | 3.9 | 3.8 | 3.8 | 3.9 | 4.3 | 3.9 | 3.8 | 4 | 4.1 | 3.9 | 4.5 | 4.6 | 4.4 | 4.1 | 4.2 | 4 | 4.3 | 4.3 | 4.3 | 42952 | 13075.7 | 37231.4 | 3607.3 | 6805.7 | 103672.1 | 4.03 | 4.5 | 4.1 | 4.1 | 3.85 | 4.1043 | 4.6 | 640.305 | 898.623 | 71.629 | 229.561 | 185.962 | 294.599 |  | 84.124 | 195407 | 255467 | 129.58 | 78.418 | 279.585 | 104.667 | 0.116 | 296.549 | 224.219 |  | 54780 | 252225 | 44880 | 213750 | 202275 |  | 189675 | 606000 | 352000 | 596800 | 344000 | 950400 | 953600 | 0 | 130 | 230 | 958000 | 950400 | 0.7997% | 50.6 | 77 |  | 12.0833 | 857925 | 140 | 99660 | 104.05 | 30100.5
2026 | 2025 | 2025-05-01 | 31 | 2025-05-10 | 6:20 | 18:22 | 7663 | 7999 | 6816 | 6903 | 6419 | 6338 | 6456 | 7033 | 6573 | 6531 | 6647 | 7902 | 6466 | 5847 | 8221 | 8004 | 8148 | 7666 | 6111 | 6391 | 6671 | 7482 | 7265 | 4.71 | 4.728 | 4.763 | 4.426 | 4.491 | 4.544 | 4.599 | 4.645 | 4.669 | 4.527 | 4.74 | 4.712 | 4.485 | 4.371 | 4.9 | 4.725 | 4.815 | 4.536 | 4.387 | 4.568 | 4.801 | 4.691 | 4.615 | 68595 | 16152 | 55650 | 7666 | 13489 | 161552 | 4.6163 | 4.77 | 4.6209 | 4.536 | 4.622 | 4.6282 | 4.9 | 640.305 | 899.148 | 72.613 | 229.979 | 186.805 | 295.378 |  | 84.881 | 195943 | 255837 | 130.246 | 78.874 | 280.148 | 105.229 | 0.117 | 296.569 | 224.589 |  | 86625 | 221400 | 68970 | 189675 | 175275 |  | 170325 | 536000 | 370000 | 532800 | 364800 | 900800 | 899200 | 1600 | 20 | 370 | 906000 | 899200 | 0.7562% | 50.6 | 97 |  | 12.0333 | 756675 | 140 | 155595 | 157.98 | 35494.1
2026 | 2025 | 2025-05-01 | 31 | 2025-05-11 | 6:20 | 18:15 | 11432 | 11518 | 10044 | 7440 | 8012 | 8702 | 8697 | 9907 | 7301 | 8614 | 7730 | 9690 | 8949 | 7885 | 12248 | 11660 | 12222 | 9689 | 8613 | 7507 | 9828 | 8590 | 10601 | 5.08 | 5.119 | 4.967 | 4.562 | 4.72 | 4.69 | 4.724 | 4.964 | 4.684 | 4.702 | 4.735 | 4.803 | 4.702 | 4.601 | 5.425 | 5.159 | 5.218 | 4.912 | 4.84 | 4.559 | 5.069 | 4.862 | 5.011 | 92712 | 23882 | 71992 | 9689 | 18604 | 216879 | 4.8414 | 5.1885 | 4.8405 | 4.912 | 4.844 | 4.8743 | 5.425 | 640.305 | 899.779 | 73.528 | 230.583 | 187.606 | 296.122 |  | 85.571 | 196446 | 256252 | 130.868 | 79.387 | 280.717 | 105.799 | 0.117 | 0 | 224.969 |  | 104115 | 205875 | 99660 | 180225 | 167400 |  | 155250 | 503000 | 415000 | 497600 | 410400 | 910400 | 912000 | 0 |  | 380 | 918000 | 910400 | 0.8348% | 50.6 | 96 |  | 11.9167 | 708750 | 140 | 203775 | 217.24 | 43764.8
2026 | 2025 | 2025-05-01 | 31 | 2025-05-12 | 6:19 | 18:18 | 7619 | 8497 | 4967 | 5548 | 5829 | 5360 | 5181 | 5847 | 6315 | 5625 | 5799 | 4885 | 6153 | 5480 | 8503 | 8733 | 8423 | 6126 | 6457 | 5340 | 7496 | 6734 | 8228 | 4.8859 | 5.0911 | 4.6444 | 4.5513 | 4.6492 | 4.5548 | 4.5454 | 4.7102 | 4.787 | 4.5188 | 4.835 | 4.539 | 4.7466 | 4.557 | 5.2602 | 5.1763 | 5.0874 | 4.7362 | 4.789 | 4.6269 | 5.162 | 4.9292 | 5.0526 | 60828 | 17156 | 54007 | 6126 | 11028 | 149145 | 4.7403 | 5.1319 | 4.8033 | 4.7362 | 4.6278 | 4.8016 | 5.2602 | 640.305 | 900.259 | 74.31 | 230.974 | 188.429 | 296.939 |  | 86.174 | 196951 | 256571 | 131.493 | 79.781 | 281.228 | 106.311 | 0.117 | 0 | 225.329 |  | 79200 | 175950 | 64515 | 185175 | 183825 |  | 135675 | 505000 | 319000 | 500000 | 315200 | 817600 | 819200 | 0 |  | 360 | 824000 | 817600 | 0.7828% | 50.6 | 0 |  | 11.9833 | 680625 | 140 | 143715 | 156.47 | 67113.5
2026 | 2025 | 2025-05-01 | 31 | 2025-05-13 | 7:19 | 18:10 | 5141.3 | 5708.8 | 3089.2 | 3793.5 | 3729.6 | 3314.7 | 3297.2 | 3508.5 | 4645 | 3675.9 | 3178 | 4491.9 | 4287.7 | 3832.4 | 4551.4 | 3603.6 | 5172.1 | 3607.3 | 4476.4 | 4427.8 | 4755.5 | 4670.4 | 4813.9 | 4.2 | 4.4 | 3.7 | 4 | 3.9 | 3.8 | 3.8 | 3.9 | 4.3 | 3.9 | 3.8 | 4 | 4.1 | 3.9 | 4.5 | 4.6 | 4.4 | 4.1 | 4.2 | 4 | 4.3 | 4.3 | 4.3 | 41152 | 8775.7 | 35431.4 | 3607.3 | 6805.7 | 95772.1 | 4.03 | 4.5 | 4.1 | 4.1 | 3.85 | 4.1043 | 4.6 | 640.305 | 900.546 | 75.18 | 231.245 | 189.146 | 297.577 |  | 86.828 | 197403 | 256858 | 132.052 | 80.136 | 281.686 | 106.77 | 0.118 | 0 | 225.609 |  | 47355 | 195750 | 44715 | 161325 | 143550 |  | 147150 | 452000 | 287000 | 447200 | 284000 | 732800 | 734400 | 1600 |  | 280 | 739000 | 731200 | 1.067% | 50.6 | 0 |  | 10.85 | 647775 | 140 | 92070 | 100.56 | 83700.8
2026 | 2025 | 2025-05-01 | 31 | 2025-05-14 | 6:13 | 18:17 | 3681.7 | 3047.5 | 3098.3 | 2496.8 | 2901.9 | 3162.6 | 3335.4 | 3799.2 | 2264.5 | 2990.3 | 2881.7 | 2815.6 | 3010.2 | 2828.1 | 3582.6 | 3489.4 | 3382.6 | 2933.7 | 2512.6 | 2487.2 | 2540.4 | 3138.5 | 2841.6 | 3.5 | 3.5 | 3.5 | 3.3 | 3.3 | 3.5 | 3.5 | 3.7 | 3.6 | 3.3 | 3.5 | 3.3 | 3.4 | 3.2 | 3.7 | 3.5 | 3.5 | 3.3 | 4 | 3.3 | 3.5 | 3.6 | 3.4 | 29888.3 | 6872 | 22393.8 | 2933.7 | 7134.6 | 69222.4 | 3.47 | 3.5 | 3.49 | 3.3 | 3.6 | 3.4739 | 4 | 640.305 | 900.755 | 76.261 | 231.445 | 190.047 | 298.378 |  | 87.671 | 197976 | 257166 | 132.76 | 80.517 | 282.234 | 107.318 | 0.118 | 0 | 225.889 |  | 34485 | 243225 | 33000 | 202725 | 180225 |  | 189675 | 573000 | 308000 | 566400 | 304800 | 876800 | 876800 | 0 |  | 280 | 881000 | 876800 | 0.479% | 50.6 | 0 |  | 12.0667 | 815850 | 140 | 67485 | 70.82 | 8437.8
2026 | 2025 | 2025-05-01 | 31 | 2025-05-15 | 7:53 | 18:51 | 6321.6 | 6178.5 | 4742.1 | 4082.3 | 5479.2 | 4815.8 | 4731.5 | 5304.6 | 4904.9 | 4699.2 | 4875.6 | 4998.2 | 5235.1 | 5071.4 | 6502.4 | 6401.6 | 6446.6 | 5266.9 | 5862 | 4064.2 | 5097.9 | 5627.1 | 5960.3 | 4.2 | 4.2 | 3.9 | 3.8 | 4.1 | 3.9 | 4 | 4 | 4.1 | 3.9 | 4.1 | 3.9 | 4 | 4 | 4.4 | 4.2 | 4.3 | 4.1 | 4.3 | 3.9 | 4.2 | 4.3 | 4.3 | 52371.8 | 12848.2 | 42146 | 5266.9 | 10036.1 | 122669 | 4.06 | 4.25 | 4.09 | 4.1 | 4 | 4.0913 | 4.4 | 640.305 | 901.135 | 76.749 | 231.786 | 190.49 | 298.782 |  | 88.034 | 198248 | 257393 | 133.097 | 80.798 | 282.543 | 107.627 | 0.118 | 0 | 226.169 |  | 62700 | 109800 | 56265 | 99675 | 90900 |  | 81675 | 272000 | 227000 | 269600 | 224800 | 494400 | 494400 | 0 |  | 280 | 499000 | 494400 | 0.9304% | 50.6 | 94 |  | 10.9667 | 382050 | 140 | 118965 | 123.77 | 96386.2
2026 | 2025 | 2025-05-01 | 31 | 2025-05-16 | 6:15 | 18:28 | 8055.6 | 7697.7 | 7679.7 | 6191.3 | 5981.2 | 6654.5 | 7018.9 | 6924.6 | 6456.4 | 6170.5 | 6045.9 | 7229.6 | 6989.5 | 6390.9 | 8540.7 | 8076.7 | 8505.7 | 6494.8 | 6168.8 | 6203.7 | 6268.5 | 6762.7 | 7523.6 | 4.8 | 4.8 | 4.9 | 4.5 | 4.5 | 4.8 | 4.6 | 4.7 | 4.7 | 4.4 | 4.6 | 4.6 | 4.6 | 4.4 | 5 | 4.8 | 4.9 | 4.6 | 4.6 | 4.5 | 4.9 | 4.7 | 4.7 | 69474.9 | 16582.4 | 53535.9 | 6494.8 | 13943.5 | 160031.5 | 4.64 | 4.85 | 4.69 | 4.6 | 4.65 | 4.6783 | 5 | 640.305 | 901.62 | 77.313 | 232.234 | 191.186 | 299.343 |  | 88.614 | 198662 | 257673 | 133.606 | 81.144 | 282.971 | 108.057 | 0.118 | 0 | 226.449 |  | 80025 | 126900 | 73920 | 156600 | 126225 |  | 130500 | 414000 | 280000 | 407200 | 276800 | 684800 | 688000 | 0 |  | 280 | 694000 | 684800 | 1.343% | 50.6 | 96 |  | 12.2167 | 540225 | 140 | 153945 | 160.18 | 140421.6
2026 | 2025 | 2025-05-01 | 31 | 2025-05-17 | 6:18 | 18:27 | 11587.6 | 11496.8 | 10201.9 | 9808.7 | 9698.1 | 10015.9 | 10215 | 10614.2 | 10514.2 | 9954.7 | 9471.4 | 10630.8 | 10741.1 | 10295.3 | 11711.4 | 12320.9 | 11395.9 | 9831 | 9261.6 | 9821.2 | 9849.4 | 9138.5 | 9866.4 | 5.2 | 5.3 | 5.1 | 5 | 5 | 5 | 5 | 5.1 | 5.1 | 4.9 | 5 | 5 | 5 | 4.9 | 5.4 | 5.3 | 5.2 | 5 | 4.9 | 5 | 5.1 | 5.1 | 5.1 | 103677 | 23716.8 | 80388 | 9831 | 20829.2 | 238442 | 5.04 | 5.25 | 5.08 | 5 | 5.05 | 5.0739 | 5.4 | 640.305 | 902.342 | 78.235 | 232.91 | 192.014 | 300.053 |  | 89.234 | 199148 | 258088 | 134.207 | 81.653 | 283.53 | 108.615 | 0.119 | 0 | 226.779 |  | 119130 | 207450 | 111540 | 186300 | 159750 |  | 139500 | 486000 | 415000 | 480800 | 407200 | 894400 | 892800 | 1600 |  | 330 | 901000 | 892800 | 0.9185% | 50.6 | 96 |  | 12.15 | 693000 | 140 | 230670 | 238.47 | 106654.4
2026 | 2025 | 2025-05-01 | 31 | 2025-05-18 | 6:29 | 18:42 | 7152.8 | 4725.9 | 5844.7 | 3672 | 3941.2 | 4167.3 | 4120.9 | 5729 | 4088.2 | 5528.8 | 5391.4 | 5770.7 | 5598.3 | 5073.7 | 7583.2 | 4956.1 | 4621.2 | 4999.2 | 5038.7 | 4842.5 | 5082.1 | 4920.2 | 5300.3 | 4.6 | 4.2 | 4.3 | 4.2 | 4.1 | 4 | 4.1 | 4.3 | 4.3 | 4.2 | 4.4 | 4.3 | 4.2 | 4.2 | 4.8 | 4.2 | 4.5 | 4.3 | 4.5 | 4.2 | 4.6 | 4.5 | 4.4 | 57824.8 | 9577.3 | 35897.2 | 4999.2 | 9849.9 | 118148.4 | 4.37 | 4.35 | 4.27 | 4.3 | 4.2 | 4.3217 | 4.8 | 640.305 | 902.656 | 79.08 | 233.276 | 192.943 | 300.835 |  | 89.952 | 199695 | 258413 | 134.883 | 82.055 | 284.07 | 109.156 | 0.119 | 0 | 227.109 |  | 51810 | 190125 | 60390 | 209025 | 175950 |  | 161550 | 547000 | 325000 | 540800 | 321600 | 864000 | 865600 | 0 |  | 330 | 872000 | 864000 | 0.9259% | 50.6 | 96 |  | 12.2167 | 736650 | 140 | 112200 | 120.17 | 81564.1
2026 | 2025 | 2025-05-01 | 31 | 2025-05-19 | 6:17 | 17:54 | 1915.2 | 2395.7 | 1509.3 | 837.6 | 1425.9 | 1532.4 | 1455.5 | 1245.6 | 1699.4 | 1087.2 | 1621.7 | 1513.8 | 1689.9 | 1208.2 | 2344.9 | 2640.3 | 2580.9 | 1314 | 1610.6 | 1059 | 2126.4 | 1380.3 | 2342.4 | 3.2 | 3.2 | 3.1 | 2.7 | 2.8 | 2.9 | 2.9 | 3.1 | 3 | 2.8 | 3.1 | 2.9 | 3 | 2.8 | 3.4 | 3.2 | 3.2 | 2.8 | 3 | 2.9 | 3.3 | 2.9 | 3.1 | 15559.8 | 5221.2 | 13740.1 | 1314 | 2701.1 | 38536.2 | 3.02 | 3.2 | 2.99 | 2.8 | 3 | 3.013 | 3.4 | 640.305 | 902.784 | 79.854 | 233.377 | 193.648 | 301.396 |  | 90.534 | 200111 | 258622 | 135.397 | 82.313 | 284.458 | 109.544 | 0.12 | 0 | 227.439 |  | 21120 | 174150 | 16665 | 158625 | 126225 |  | 130950 | 416000 | 209000 | 411200 | 206400 | 620800 | 620800 | 1600 |  | 330 | 625000 | 619200 | 0.9367% | 50.6 | 97 |  | 11.6167 | 589950 | 140 | 37785 | 41.88 | 113831.2
2026 | 2025 | 2025-05-01 | 31 | 2025-05-20 | 6:17 | 17:07 | 3723.3 | 5084.3 | 2359.4 | 3772.1 | 3568.5 | 2996.8 | 4414.5 | 2783.2 | 4090 | 2572 | 2378.3 | 2690 | 2567.8 | 2424.3 | 4210.6 | 5784.6 | 5244.7 | 4278.5 | 2596.2 | 2278.9 | 4484.8 | 4434.1 | 4241.1 | 3.4 | 3.6 | 3.1 | 3.4 | 3.3 | 3.4 | 3.4 | 3.2 | 3.6 | 3.1 | 3.3 | 3.1 | 3.2 | 3.1 | 3.7 | 3.8 | 3.7 | 3.3 | 3.1 | 3.3 | 3.8 | 3.6 | 3.5 | 27800.8 | 11029.3 | 32671.7 | 4278.5 | 7197.7 | 82978 | 3.24 | 3.75 | 3.48 | 3.3 | 3.3 | 3.3913 | 3.8 | 640.305 | 903.096 | 80.428 | 233.563 | 194.159 | 301.818 |  | 90.975 | 200420 | 258831 | 135.776 | 82.573 | 284.781 | 109.866 | 0.122 | 0 | 227.769 |  | 51480 | 129150 | 30690 | 114975 | 94950 |  | 99225 | 309000 | 209000 | 303200 | 208000 | 516800 | 515200 | 3200 |  | 330 | 518000 | 513600 | 0.8567% | 50.6 | 97 |  | 10.8333 | 438300 | 140 | 82170 | 88.93 | 119845.6
2026 | 2025 | 2025-05-01 | 31 | 2025-05-21 | 6:15 | 18:26 | 20055 | 18674 | 18103 | 16599 | 18146 | 18708 | 18253 | 19092 | 17248 | 17623 | 17785 | 18503 | 18937 | 17832 | 20490 | 19719 | 20250 | 17350 | 17394 | 16804 | 17322 | 17676 | 11377 | 6.2395 | 6.1167 | 6.1138 | 5.7738 | 6.0408 | 6.0423 | 6.009 | 6.1672 | 5.9588 | 5.85 | 6.193 | 6.1242 | 6.0018 | 5.9411 | 6.555 | 6.1751 | 6.3888 | 5.9097 | 5.8894 | 5.8677 | 6.2454 | 6.0576 | 6.0141 | 183526 | 39969 | 135750 | 17350 | 37345 | 413940 | 6.0775 | 6.282 | 6.0426 | 5.9097 | 6.0881 | 6.0728 | 6.555 | 640.305 | 904.324 | 80.97 | 234.753 | 194.714 | 302.266 |  | 91.375 | 200736 | 259351 | 136.166 | 83.216 | 285.298 | 110.385 | 0.122 | 0 | 228.079 |  | 202620 | 121950 | 196350 | 124875 | 100800 |  | 90000 | 316000 | 520000 | 312000 | 514400 | 827200 | 830400 | 0 |  | 310 | 836000 | 827200 | 1.064% | 50.6 | 96 |  | 12.1833 | 437625 | 140 | 398970 | 413.94 | 123861
2026 | 2025 | 2025-05-01 | 31 | 2025-05-22 | 6:12 | 18:31 | 27333 | 21763 | 22850 | 20324 | 19958 | 22041 | 20889 | 24209 | 22095 | 22757 | 22926 | 24297 | 23208 | 21460 | 27362 | 24080 | 24305 | 19710 | 24374 | 21402 | 21320 | 22391 | 22416 | 8.0224 | 7.4817 | 7.5524 | 7.1228 | 7.3553 | 7.4357 | 7.5279 | 7.629 | 7.5467 | 7.3022 | 7.6659 | 7.5867 | 7.2386 | 7.2131 | 8.3016 | 7.8308 | 7.9489 | 7.2615 | 7.5969 | 7.1582 | 7.7923 | 7.7432 | 7.5367 | 237969 | 48385 | 172308 | 19710 | 45098 | 523470 | 7.5638 | 7.8898 | 7.5171 | 7.2615 | 7.5784 | 7.5587 | 8.3016 | 640.305 | 905.845 | 81.513 | 236.296 | 195.174 | 302.623 |  | 91.777 | 201010 | 259981 | 136.505 | 83.989 | 285.857 | 110.944 | 0.122 | 0 | 228.419 |  | 250965 | 122175 | 254595 | 103500 | 80325 |  | 90450 | 274000 | 630000 | 271200 | 618400 | 894400 | 894400 | 0 |  | 340 | 904000 | 894400 | 1.073% | 50.6 | 83 |  | 12.3167 | 396450 | 140 | 505560 | 545.86 | 167164.6
2026 | 2025 | 2025-05-01 | 31 | 2025-05-23 | 6:13 | 18:26 | 33684 | 31262 | 31873 | 26047 | 30308 | 31487 | 31209 | 31512 | 33593 | 31801 | 31692 | 31490 | 31733 | 30552 | 33593 | 32031 | 32621 | 23529 | 23325 | 27635 | 29939 | 29314 | 23712 | 8.7499 | 8.4718 | 8.7687 | 7.6873 | 8.3981 | 8.4849 | 8.5714 | 8.6103 | 8.7344 | 8.4352 | 8.8803 | 8.7453 | 8.4986 | 8.2823 | 9.1189 | 8.5117 | 8.7044 | 7.3711 | 8.0542 | 7.9893 | 8.6166 | 8.2656 | 7.1848 | 307378 | 64652 | 235662 | 23529 | 62721 | 693942 | 8.5523 | 8.608 | 8.3025 | 7.3711 | 8.5908 | 8.3972 | 9.1189 | 640.305 | 907.923 | 82.108 | 238.299 | 195.715 | 303.063 |  | 92.199 | 201326 | 260784 | 136.896 | 84.985 | 286.555 | 111.64 | 0.122 | 0 | 228.759 |  | 342870 | 133875 | 330495 | 121725 | 99000 |  | 94950 | 316000 | 803000 | 312800 | 796800 | 1116800 | 1113600 | 0 |  | 340 | 1119000 | 1116800 | 0.197% | 50.6 | 86 |  | 12.2167 | 449550 | 140 | 673365 | 707.87 | 82963.4
2026 | 2025 | 2025-05-01 | 31 | 2025-05-24 | 6:15 | 18:06 | 36704 | 34731 | 36152 | 30540 | 33343 | 35752 | 35541 | 36878 | 37916 | 36545 | 34821 | 34459 | 34653 | 33326 | 37650 | 36435 | 35121 | 26093 | 30488 | 30621 | 34975 | 32311 | 28527 | 8.3181 | 8.2516 | 8.5119 | 7.6936 | 8.1152 | 8.2783 | 8.4431 | 8.4881 | 8.59 | 8.2371 | 8.5008 | 8.2724 | 8.1234 | 7.9439 | 8.7875 | 8.4122 | 8.3352 | 7.3572 | 7.6628 | 7.7036 | 8.7571 | 8.0891 | 7.3359 | 345419 | 71556 | 268095 | 26093 | 72419 | 783582 | 8.2061 | 8.3737 | 8.2042 | 7.3572 | 8.4656 | 8.183 | 8.7875 | 640.305 | 910.262 | 82.775 | 240.548 | 196.292 | 303.542 |  | 92.703 | 201678 | 261692 | 137.33 | 86.11 | 287.336 | 112.424 | 0.122 | 0 | 229.129 |  | 385935 | 150075 | 371085 | 129825 | 107775 |  | 113400 | 352000 | 908000 | 347200 | 900000 | 1249600 | 1254400 | 0 |  | 370 | 1260000 | 1249600 | 0.8323% | 50.6 | 96 |  | 11.85 | 501075 | 140 | 757020 | 784.85 | 29084.9
2026 | 2025 | 2025-05-01 | 31 | 2025-05-25 | 6:10 | 17:51 | 41187 | 39712.1 | 39143.8 | 36070.1 | 39375.3 | 39404.7 | 39604.9 | 41388.5 | 41371.1 | 40245.4 | 39489.1 | 40470.3 | 39886.3 | 39601 | 41081.9 | 40756 | 41241.5 | 32939.5 | 37037.3 | 37988.2 | 38534.5 | 38145.3 | 38548 | 9.5 | 9.4 | 9.4 | 8.7 | 9.3 | 9.2 | 9.4 | 9.5 | 9.5 | 9.2 | 9.4 | 9.4 | 9.1 | 9.2 | 9.8 | 9.5 | 9.6 | 8.5 | 8.9 | 8.9 | 9.6 | 9.1 | 9 | 396130.3 | 81997.5 | 311161.1 | 32939.5 | 80993.4 | 903221.8 | 9.28 | 9.55 | 9.27 | 8.5 | 9.45 | 9.2652 | 9.8 | 640.305 | 912.968 | 83.393 | 243.121 | 196.856 | 304.021 |  | 93.165 | 202017 | 262707 | 137.748 | 87.34 | 288.174 | 113.26 | 0.122 | 0 | 229.499 |  | 446490 | 139050 | 424545 | 126900 | 107775 |  | 103950 | 339000 | 1015000 | 334400 | 984000 | 1340800 | 1337600 | 0 |  | 370 | 1354000 | 1340800 | 0.9845% | 50.6 | 96 |  | 11.6833 | 477675 | 140 | 871035 | 907.2 | 62295.4
2026 | 2025 | 2025-05-01 | 31 | 2025-05-26 | 6:18 | 18:29 | 49881 | 49078 | 46402 | 46747 | 48271 | 47761 | 47847 | 49077 | 48310 | 49126 | 46596 | 47664 | 48315 | 48155 | 50617 | 50442 | 50403 | 47222 | 49501 | 47493 | 48465 | 48893 | 49790 | 10.7 | 10.5 | 10 | 10.1 | 10.3 | 10 | 10.1 | 10.2 | 10.3 | 10 | 10.4 | 10.1 | 10.3 | 10.1 | 11.3 | 10.7 | 10.8 | 10.2 | 10.8 | 10 | 10.6 | 10.5 | 10.6 | 483750 | 100845 | 387315 | 47222 | 96924 | 1116056 | 10.37 | 10.75 | 10.32 | 10.2 | 10.15 | 10.3739 | 11.3 | 640.305 | 916.342 | 83.936 | 246.244 | 197.402 | 304.454 |  | 93.556 | 202325 | 263895 | 138.129 | 88.797 | 289.107 | 114.194 | 0.122 | 0 | 229.849 |  | 556710 | 122175 | 515295 | 122850 | 97425 |  | 87975 | 308000 | 1188000 | 304800 | 1165600 | 1492800 | 1494400 | 0 |  | 350 | 1496000 | 1492800 | 0.2144% | 50.6 | 96 |  | 12.1833 | 430425 | 140 | 1072005 | 1116.06 | 28890
2026 | 2025 | 2025-05-01 | 31 | 2025-05-27 | 6:25 | 18:25 | 50238 | 45407 | 46825 | 37424 | 40658 | 42866 | 43267 | 49203 | 40517 | 48587 | 47903 | 46818 | 48552 | 47638 | 50637 | 43448 | 46761 | 44275 | 49568 | 48290 | 40390 | 40116 | 41669 | 11 | 11.1 | 10.4 | 10.8 | 11 | 10.2 | 10.4 | 10.7 | 10.9 | 10.4 | 10.8 | 10.5 | 10.6 | 10.4 | 11.5 | 11 | 11.2 | 10.9 | 11.1 | 10.7 | 11.2 | 11 | 11.1 | 485056 | 90209 | 329047 | 44275 | 92470 | 1041057 | 10.74 | 11.1 | 10.84 | 10.9 | 10.55 | 10.8217 | 11.5 | 640.305 | 919.276 | 84.681 | 249.373 | 198.16 | 305.104 |  | 94.119 | 202769 | 265065 | 138.678 | 90.231 | 290.108 | 115.192 | 0.122 | 0 | 230.229 |  | 484110 | 167625 | 516285 | 170550 | 146250 |  | 126675 | 444000 | 1170000 | 439200 | 1147200 | 1601600 | 1596800 | 0 |  | 380 | 1614000 | 1601600 | 0.7742% | 50.6 | 96 |  | 12 | 611100 |  | 1000395 | 1061.1 | 77519.5
2026 | 2025 | 2025-05-01 | 31 | 2025-05-28 | 6:19 | 18:27 | 44303 | 39362 | 37807 | 31869 | 33421 | 34157 | 35810 | 40180 | 27448 | 39480 | 39472 | 39732 | 43377 | 39965 | 43982 | 40561 | 41110 | 36706 | 43152 | 40868 | 31682 | 32880 | 35096 | 9.3 | 9 | 8.5 | 8.4 | 8.8 | 8.3 | 8.4 | 8.7 | 8.6 | 8.4 | 8.9 | 8.7 | 9.2 | 8.7 | 9.7 | 9.2 | 9.4 | 8.8 | 9.3 | 8.8 | 8.8 | 8.8 | 8.9 | 412138 | 81671 | 265915 | 36706 | 75990 | 872420 | 8.95 | 9.3 | 8.67 | 8.8 | 8.55 | 8.8522 | 9.7 | 640.305 | 921.712 | 84.994 | 252.025 | 198.52 | 305.42 |  | 94.348 | 202973 | 265972 | 138.929 | 91.346 | 290.799 | 115.889 | 0.122 | 0 | 230.609 |  | 401940 | 70425 | 437580 | 81000 | 71100 |  | 51525 | 204000 | 907000 | 200800 | 892000 | 1105600 | 1115200 | 0 |  | 380 | 1111000 | 1105600 | 0.4884% | 50.6 | 96 |  | 12.1333 | 274050 |  | 839520 | 884.82 | 125528.2
2026 | 2025 | 2025-05-01 | 31 | 2025-05-29 | 6:21 | 18:20 | 34891 | 31960 | 30215 | 30177 | 33981 | 30820 | 30941 | 30965 | 31505 | 31273 | 31942 | 34009 | 35452 | 33205 | 35824 | 34015 | 35485 | 32002 | 35688 | 33783 | 32425 | 31182 | 35081 | 8 | 8 | 7.8 | 7.6 | 8.2 | 7.7 | 7.9 | 7.7 | 7.9 | 7.6 | 8 | 8 | 8.1 | 7.8 | 8.4 | 8.2 | 8.4 | 8.1 | 8.2 | 7.9 | 8.4 | 8 | 8.1 | 336282 | 69500 | 257131 | 32002 | 61906 | 756821 | 7.98 | 8.3 | 7.95 | 8.1 | 7.8 | 8 | 8.4 | 640.305 | 923.972 | 85.735 | 254.179 | 199.186 | 305.936 |  | 94.891 | 203361 | 266869 | 139.409 | 92.455 | 291.595 | 116.687 | 0.122 | 0 | 230.989 |  | 372900 | 166725 | 355410 | 149850 | 116100 |  | 122175 | 388000 | 897000 | 384000 | 887200 | 1273600 | 1276800 | 0 |  | 380 | 1285000 | 1273600 | 0.8951% | 50.6 | 96 |  | 11.9833 | 554850 |  | 728310 | 761 | 72839.3
2026 | 2025 | 2025-05-01 | 31 | 2025-05-30 | 6:44 | 18:32 | 39253 | 39002 | 33050 | 35001 | 37580 | 34444 | 34898 | 34441 | 35688 | 34889 | 35198 | 35412 | 36280 | 35618 | 39774 | 41087 | 39804 | 37286 | 38706 | 35402 | 38555 | 37093 | 40888 | 9.9 | 10 | 9 | 9.1 | 9.6 | 8.9 | 9.2 | 9.5 | 9.1 | 9.2 | 9.5 | 9.1 | 9.5 | 9.1 | 10.4 | 10.4 | 10.1 | 9.7 | 9.9 | 9.1 | 10.2 | 9.6 | 10.1 | 363582 | 80891 | 298251 | 37286 | 69339 | 849349 | 9.47 | 10.25 | 9.53 | 9.7 | 9.35 | 9.5739 | 10.4 | 640.305 | 926.593 | 86.347 | 256.52 | 199.723 | 306.362 |  | 95.347 | 203681 | 267824 | 139.804 | 93.637 | 292.387 | 117.479 | 0.122 | 0 | 231.369 |  | 432465 | 137700 | 386265 | 120825 | 95850 |  | 102600 | 320000 | 955000 | 316000 | 945600 | 1267200 | 1267200 | 0 |  | 380 | 1275000 | 1267200 | 0.6155% | 50.6 | 96 |  | 11.8 | 456975 |  | 818730 | 872.37 | 27151.3
2026 | 2025 | 2025-05-01 | 31 | 2025-05-31 | 6:19 | 18:31 | 50958 | 50955 | 41916 | 45753 | 46624 | 41984 | 44775 | 47508 | 45911 | 40646 | 41670 | 41860 | 46372 | 42797 | 50578 | 51331 | 51436 | 46168 | 49457 | 45231 | 49159 | 49423 | 50401 | 10.7 | 10.6 | 9.4 | 9.6 | 9.9 | 9 | 9.6 | 10 | 9.7 | 9.5 | 9.5 | 9.1 | 10 | 9.2 | 10.9 | 10.7 | 10.8 | 9.9 | 10.4 | 9.5 | 10.5 | 10.2 | 10.2 | 451485 | 102767 | 380210 | 46168 | 92283 | 1072913 | 9.82 | 10.75 | 9.93 | 9.9 | 9.8 | 9.9522 | 10.9 | 640.305 | 929.908 | 87.333 | 259.441 | 200.696 | 307.152 |  | 96.095 | 204246 | 269078 | 140.502 | 95.188 | 293.514 | 118.609 | 0.122 | 0 | 231.969 |  | 546975 | 221850 | 481965 | 218925 | 177750 |  | 168300 | 565000 | 1254000 | 558400 | 1240800 | 1803200 | 1808000 | 0 |  | 600 | 1819000 | 1803200 | 0.8762% | 50.6 | 96 |  | 12.2 | 786825 |  | 1028940 | 1072.93 | 107056.9
2026 | 2025 | 2025-06-01 | 30 | 2025-06-01 | 6:18 | 18:34 | 39781.2 | 36804.9 | 34765.1 | 33389 | 37928.8 | 35505.9 | 35601.7 | 36766.5 | 36327.9 | 36056.3 | 37122.9 | 37869.6 | 39610.7 | 38017.9 | 40717.9 | 37433.1 | 38667.9 | 36216.1 | 39444.6 | 36804 | 34743 | 36733.4 | 37805.2 | 9 | 8.9 | 8.6 | 8.2 | 8.9 | 8.4 | 8.6 | 8.8 | 8.8 | 8.5 | 9 | 8.7 | 9.1 | 8.8 | 9.5 | 8.8 | 9.1 | 8.8 | 9 | 8.6 | 8.9 | 8.8 | 8.8 | 380190.2 | 76101 | 289238.1 | 36216.1 | 72368.2 | 854113.6 | 8.88 | 8.95 | 8.71 | 8.8 | 8.7 | 8.8087 | 9.5 | 640.305 | 932.44 | 88.182 | 261.887 | 201.521 | 307.775 |  | 96.723 | 204713 | 270089 | 141.08 | 96.438 | 294.433 | 119.528 | 0.122 | 0 | 232.569 |  | 417780 | 191025 | 403590 | 185625 | 140175 |  | 141300 | 467000 | 1011000 | 462400 | 1000000 | 1470400 | 1470400 | 0 |  | 600 | 1478000 | 1470400 | 0.5169% | 50.6 | 96 |  | 12.2667 | 658125 |  | 821370 | 853.95 | 49003.1
2026 | 2025 | 2025-06-01 | 30 | 2025-06-02 | 6:12 | 18:37 | 30915.8 | 25817.2 | 28505.4 | 27088 | 24575.3 | 26022.4 | 24722.2 | 29762.7 | 26270 | 27391.2 | 26387.4 | 30128.8 | 26199.3 | 27902.8 | 31507.6 | 28380.3 | 27170.4 | 22097.9 | 26181.2 | 26132.4 | 26191.5 | 24168.7 | 26466.6 | 7.7 | 7.4 | 7.7 | 7.3 | 7.2 | 7.3 | 7.3 | 7.8 | 7.4 | 7.3 | 7.5 | 7.6 | 7.1 | 7.3 | 8.1 | 7.7 | 7.6 | 6.9 | 7.1 | 7.1 | 7.9 | 7.3 | 7.4 | 281251.9 | 55550.7 | 206599.7 | 22097.9 | 54484.9 | 619985.1 | 7.45 | 7.65 | 7.43 | 6.9 | 7.55 | 7.4348 | 8.1 | 640.305 | 934.244 | 88.986 | 263.72 | 202.315 | 308.387 |  | 97.33 | 205167 | 270868 | 141.64 | 97.404 | 295.2 | 120.294 | 0.122 | 0 | 233.169 |  | 297660 | 180900 | 302445 | 178650 | 137700 |  | 136575 | 454000 | 779000 | 448000 | 772800 | 1227200 | 1225600 | 0 |  | 600 | 1233000 | 1227200 | 0.4726% | 50.6 | 96 |  | 12.4167 | 633825 |  | 600105 | 627.14 | 114741.9
2026 | 2025 | 2025-06-01 | 30 | 2025-06-03 | 6:08 | 6:26 | 30835.7 | 26477.4 | 23953.6 | 29023.9 | 27499.1 | 25692.3 | 24763.5 | 23588.7 | 28694.7 | 23753.5 | 26152.3 | 30254.7 | 26978.8 | 25791.8 | 28170.2 | 28151.8 | 28400.9 | 25060.3 | 25926.5 | 26479.6 | 27548.2 | 28021.9 | 28185.5 | 7.5 | 7 | 7 | 7.2 | 7.2 | 6.9 | 6.9 | 6.8 | 7.4 | 6.6 | 7.3 | 7.5 | 7.1 | 6.9 | 7.4 | 7.2 | 7.3 | 6.9 | 7 | 7 | 7.6 | 7.4 | 7.2 | 268296.7 | 56552.7 | 221143 | 25060.3 | 48352.2 | 619404.9 | 7.13 | 7.25 | 7.16 | 6.9 | 6.85 | 7.1435 | 7.6 | 640.305 | 936.147 | 89.724 | 265.435 | 203.052 | 308.941 |  | 97.886 | 205583 | 271631 | 142.154 | 98.347 | 295.931 | 121.026 | 0.122 | 0 | 233.559 |  | 313995 | 166050 | 282975 | 165825 | 124650 |  | 125100 | 416000 | 763000 | 411200 | 754400 | 1169600 | 1171200 | 0 |  | 390 | 1179000 | 1169600 | 0.8037% | 50.6 | 96 |  | 0.3 | 581625 |  | 596970 | 619.59 | 163800.4
2026 | 2025 | 2025-06-01 | 30 | 2025-06-04 | 6:15 | 18:41 | 29266.2 | 26926.7 | 24919.9 | 22334.8 | 24403.4 | 24795.3 | 25103.5 | 25795.1 | 24233.5 | 24276.7 | 22210.7 | 25369.5 | 25954.2 | 22778.5 | 29479.6 | 27781.2 | 28243.9 | 25029.2 | 25881.3 | 23178.5 | 22885.2 | 24097.2 | 25088.7 | 7.6 | 7.3 | 7.4 | 6.9 | 7.1 | 7.1 | 7.2 | 7.3 | 7.1 | 7 | 7.1 | 7.2 | 7.3 | 6.9 | 7.9 | 7.4 | 7.6 | 7.2 | 7.3 | 7 | 7.3 | 7.3 | 7.1 | 253315.1 | 56025.1 | 194764.8 | 25029.2 | 50898.6 | 580032.8 | 7.27 | 7.5 | 7.17 | 7.2 | 7.25 | 7.2435 | 7.9 | 640.305 | 937.898 | 90.592 | 267.075 | 203.956 | 309.624 |  | 98.567 | 206093 | 272387 | 142.786 | 99.286 | 296.716 | 121.814 | 0.122 | 0 | 233.949 |  | 288915 | 195300 | 270600 | 203400 | 153675 |  | 153225 | 510000 | 756000 | 505600 | 751200 | 1256000 | 1260800 | 0 |  | 390 | 1266000 | 1256000 | 0.7962% | 50.6 | 96 |  | 12.4333 | 705600 |  | 559515 | 580.02 | 107193.3
2026 | 2025 | 2025-06-01 | 30 | 2025-06-05 | 6:12 | 18:30 | 18484.7 | 17250.8 | 15502.4 | 12670.6 | 13268.9 | 14650.7 | 15155.5 | 18170.2 | 14119.9 | 15486 | 14142.5 | 14002.7 | 14861.3 | 13221.3 | 19821 | 18623.7 | 17515.9 | 14577.2 | 15387.4 | 12562.5 | 15240.4 | 13662.6 | 15895.2 | 6.2 | 6.2 | 6.1 | 5.6 | 5.8 | 5.8 | 6 | 6.3 | 5.9 | 5.9 | 6 | 5.8 | 5.9 | 5.6 | 6.7 | 6.3 | 6.3 | 6 | 6 | 5.6 | 6.3 | 6.1 | 6 | 153471.8 | 36139.6 | 116759.1 | 14577.2 | 33325.7 | 354273.4 | 5.98 | 6.3 | 6 | 6 | 6.15 | 6.0174 | 6.7 | 640.305 | 938.963 | 91.567 | 268.087 | 204.978 | 310.433 |  | 99.353 | 206682 | 272949 | 143.514 | 99.982 | 297.43 | 122.529 | 0.122 | 0 | 234.339 |  | 175725 | 219375 | 166980 | 229950 | 182025 |  | 176850 | 589000 | 562000 | 582400 | 556800 | 1142400 | 1144000 | 0 |  | 390 | 1151000 | 1142400 | 0.7528% | 50.6 | 95 |  | 12.3 | 808200 |  | 342705 | 358.15 | 159881.9
2026 | 2025 | 2025-06-01 | 30 | 2025-06-06 | 6:16 | 18:34 | 12317.7 | 12868.3 | 11666.8 | 11542.5 | 12870 | 12620.1 | 13011.6 | 12427.6 | 13612.4 | 11227.3 | 11978.9 | 12249.9 | 13380 | 12100.6 | 14354.1 | 15174.2 | 13501 | 12793.9 | 13898.2 | 8501.9 | 12784.8 | 13460.9 | 14048.3 | 5.6 | 5.6 | 5.4 | 5.4 | 5.6 | 5.5 | 5.6 | 5.5 | 5.7 | 5.2 | 5.6 | 5.4 | 5.6 | 5.4 | 5.9 | 5.8 | 5.7 | 5.6 | 5.7 | 5.3 | 5.9 | 5.8 | 5.7 | 121675.4 | 28675.2 | 103807.3 | 12793.9 | 25439.2 | 292391 | 5.51 | 5.75 | 5.63 | 5.6 | 5.55 | 5.587 | 5.9 | 640.305 | 939.885 | 92.491 | 268.876 | 205.928 | 311.126 |  | 100.091 | 207219 | 273438 | 144.177 | 100.588 | 298.066 | 123.166 | 0.122 | 0 | 234.729 |  | 152130 | 207900 | 130185 | 213750 | 155925 |  | 166050 | 537000 | 489000 | 530400 | 484800 | 1017600 | 1019200 | 0 |  | 390 | 1026000 | 1017600 | 0.8255% | 50.6 | 96 |  | 12.3 | 743625 |  | 282315 | 292.76 | 83300.2
2026 | 2025 | 2025-06-01 | 30 | 2025-06-07 | 6:15 | 18:33 | 21829 | 20972.2 | 16590.9 | 16254.5 | 18932.7 | 17868 | 17873.3 | 18685.6 | 18195.7 | 18228.8 | 17172.6 | 17963.5 | 19565.2 | 18132.7 | 23271 | 23374.6 | 22786.8 | 19768.3 | 20368.2 | 17407.9 | 20737.2 | 18646.6 | 22796.4 | 6.8 | 6.8 | 6.5 | 6.2 | 6.7 | 6.4 | 6.5 | 6.6 | 6.4 | 6.5 | 6.6 | 6.4 | 6.6 | 6.4 | 7.2 | 7 | 7 | 6.7 | 6.8 | 6.4 | 7.2 | 6.6 | 7 | 190529.8 | 46161.4 | 154403.3 | 19768.3 | 36558.9 | 447421.7 | 6.62 | 7 | 6.64 | 6.7 | 6.55 | 6.6652 | 7.2 | 640.305 | 941.274 | 93.547 | 270.109 | 207.068 | 311.978 |  | 100.927 | 207855 | 274112 | 144.964 | 101.42 | 298.877 | 123.979 | 0.122 | 0 | 235.119 |  | 229185 | 237600 | 203445 | 256500 | 191700 |  | 188100 | 636000 | 674000 | 629600 | 665600 | 1297600 | 1300800 | 0 |  | 390 | 1310000 | 1297600 | 0.9556% | 50.6 | 96 |  | 12.3 | 873900 |  | 432630 | 447.56 | 48267
2026 | 2025 | 2025-06-01 | 30 | 2025-06-08 | 6:13 | 18:42 | 23216.9 | 23804.4 | 18870.7 | 17091.5 | 19478 | 18738.7 | 18877.8 | 21029.3 | 17253 | 18723.9 | 18173.4 | 18563.8 | 19900 | 18557.1 | 24662.3 | 25272.3 | 23670 | 20287 | 19876.9 | 17197.7 | 20441.3 | 20428 | 22897.7 | 6.8 | 7 | 6.6 | 6.2 | 6.6 | 6.3 | 6.5 | 6.7 | 6.2 | 6.4 | 6.6 | 6.4 | 6.5 | 6.3 | 7.2 | 7.1 | 7 | 6.7 | 6.6 | 6.3 | 7 | 6.7 | 6.8 | 197742.7 | 48942.3 | 160132.6 | 20287 | 39907.1 | 467011.7 | 6.57 | 7.05 | 6.6 | 6.7 | 6.6 | 6.6304 | 7.2 | 640.305 | 942.725 | 94.38 | 271.403 | 207.923 | 312.636 |  | 101.6 | 208348 | 274764 | 145.573 | 102.212 | 299.579 | 124.684 | 0.122 | 0 | 235.509 |  | 239415 | 187425 | 213510 | 192375 | 148050 |  | 151425 | 493000 | 652000 | 487200 | 633600 | 1123200 | 1128000 | 0 |  | 390 | 1145000 | 1123200 | 1.941% | 50.6 | 96 |  | 12.4833 | 679275 |  | 452925 | 468.64 | 23262.5
2026 | 2025 | 2025-06-01 | 30 | 2025-06-09 | 6:11 | 18:34 | 26679 | 15671 | 21441 | 11743 | 13089 | 12340 | 11897 | 23685 | 13594 | 20760 | 22275 | 24659 | 25001 | 22047 | 28909 | 17069 | 16535 | 14355 | 24412 | 21908 | 14213 | 14572 | 16804 | 7.3 | 6.5 | 6.9 | 6.2 | 6.3 | 6 | 6.1 | 7 | 6.3 | 6.6 | 7.2 | 7.2 | 7.2 | 6.7 | 7.9 | 6.7 | 6.7 | 6.5 | 7.1 | 6.8 | 6.8 | 6.5 | 6.6 | 238091 | 33604 | 112026 | 14355 | 35582 | 433658 | 7.09 | 6.7 | 6.43 | 6.5 | 6.55 | 6.7435 | 7.9 | 640.305 | 943.736 | 95.175 | 272.945 | 208.649 | 313.302 |  | 102.193 | 208795 | 275347 | 146.125 | 102.944 | 300.229 | 125.331 | 0.122 | 0 | 235.899 |  | 166815 | 178875 | 254430 | 163350 | 149850 |  | 133425 | 447000 | 583000 | 441600 | 585600 | 1040000 | 1035200 | 0 |  | 390 | 1030000 | 1040000 | -0.9615% | 50.6 | 96 |  | 12.3833 | 625500 |  | 421245 | 437.12 | 70697.9
2026 | 2025 | 2025-06-01 | 30 | 2025-06-10 | 6:09 | 18:32 | 22989.2 | 24673.1 | 17072.7 | 16443.3 | 18370.5 | 16907.3 | 15898.5 | 19051.6 | 17628.3 | 16505.7 | 16580.6 | 17991.9 | 20747.8 | 17737.4 | 26733.3 | 26523.1 | 26342.5 | 19585.9 | 20691.3 | 15891.5 | 19860.6 | 19442.5 | 23445.8 | 6.8 | 7.1 | 6.5 | 6.1 | 6.5 | 6.2 | 6.2 | 6.6 | 6.3 | 6.1 | 6.5 | 6.4 | 6.6 | 6.3 | 7.6 | 7.3 | 7.4 | 6.6 | 6.7 | 6.1 | 7.3 | 6.6 | 6.9 | 192941.4 | 52865.6 | 156771.4 | 19585.9 | 34950.1 | 457114.4 | 6.56 | 7.35 | 6.58 | 6.6 | 6.4 | 6.6391 | 7.6 | 640.305 | 945.159 | 96.029 | 274.191 | 209.354 | 313.929 |  | 102.857 | 209244 | 275980 | 146.681 | 103.726 | 300.899 | 126.002 | 0.122 | 0 | 236.279 |  | 234795 | 192150 | 205590 | 158625 | 141075 |  | 149400 | 449000 | 633000 | 444800 | 625600 | 1072000 | 1073600 | 0 |  | 380 | 1082000 | 1072000 | 0.9328% | 50.6 | 96 |  | 12.3833 | 641250 |  | 440385 | 459.81 | 75225
2026 | 2025 | 2025-06-01 | 30 | 2025-06-11 | 6:34 | 18:19 | 17917 | 17756.9 | 13494.2 | 13749.9 | 14375 | 13557 | 13572.5 | 14783.9 | 14785.3 | 11925.8 | 14151.8 | 15720.5 | 15423.4 | 13801.2 | 19032.5 | 19744.7 | 17731.7 | 15320 | 14536 | 13202.1 | 16226 | 16132.9 | 17933.3 | 6.2 | 6.3 | 5.8 | 5.8 | 5.9 | 5.7 | 5.8 | 5.9 | 5.8 | 5.6 | 6 | 6 | 6 | 5.8 | 6.5 | 6.4 | 6.2 | 6.1 | 6 | 5.8 | 6.5 | 6.2 | 6.3 | 149204.5 | 37476.4 | 124516.3 | 15320 | 28356.4 | 354873.6 | 5.97 | 6.3 | 6.02 | 6.1 | 5.85 | 6.0261 | 6.5 | 640.305 | 946.273 | 96.516 | 275.159 | 209.794 | 314.34 |  | 103.228 | 209519 | 276433 | 147.021 | 104.286 | 301.35 | 126.454 | 0.122 | 0 | 236.649 |  | 183810 | 109575 | 159720 | 99000 | 92475 |  | 83475 | 275000 | 453000 | 272000 | 448000 | 721600 | 723200 | 0 |  | 370 | 728000 | 721600 | 0.8869% | 50.6 | 96 |  | 11.75 | 384525 |  | 343530 | 354.87 | 183573.3
2026 | 2025 | 2025-06-01 | 30 | 2025-06-12 | 6:41 | 18:11 | 20532.9 | 16324.6 | 14984.8 | 15569.5 | 14702.8 | 14604.8 | 13882.1 | 16340.8 | 14455.1 | 13879.9 | 13511.2 | 18198.5 | 16526.5 | 14362.5 | 20115.6 | 18621.9 | 18317.4 | 16243.6 | 15812.3 | 15013.8 | 15807.7 | 15640 | 16287.6 | 6.4 | 6.2 | 6.1 | 5.9 | 6 | 6 | 6 | 6.1 | 6.1 | 5.7 | 6 | 6.3 | 6 | 5.9 | 6.6 | 6.4 | 6.4 | 6.2 | 6 | 5.9 | 6.5 | 6.2 | 6.1 | 162938 | 36939.3 | 123392.1 | 16243.6 | 30222.9 | 369735.9 | 6.09 | 6.4 | 6.11 | 6.2 | 6.05 | 6.1304 | 6.6 | 640.305 | 947.39 | 96.914 | 276.219 | 210.074 | 314.608 |  | 103.536 | 209712 | 276880 | 147.258 | 104.842 | 301.747 | 126.85 | 0.122 | 0 | 236.999 |  | 184305 | 89550 | 174900 | 63000 | 60300 |  | 69300 | 193000 | 447000 | 189600 | 444800 | 635200 | 633600 | 0 |  | 350 | 640000 | 635200 | 0.7557% | 50.6 | 96 |  | 11.5 | 282150 |  | 359205 | 375.68 | 270298.8
2026 | 2025 | 2025-06-01 | 30 | 2025-06-13 | 6:35 | 18:11 | 23371.3 | 19732.4 | 19238.8 | 17872.1 | 19418.9 | 19480.7 | 19875 | 21046 | 21291.3 | 19131 | 18492.5 | 21458.3 | 18799.4 | 19807.6 | 21870.3 | 21770 | 21612.6 | 16187.4 | 18305.8 | 18002.6 | 18385.9 | 18449 | 19036.2 | 6.7 | 6.5 | 6.6 | 6.2 | 6.5 | 6.4 | 6.6 | 6.6 | 6.7 | 6.3 | 6.6 | 6.7 | 6.3 | 6.5 | 6.8 | 6.6 | 6.7 | 6.1 | 6.3 | 6.3 | 6.7 | 6.5 | 6.3 | 198477.6 | 43382.6 | 153666.5 | 16187.4 | 40921 | 452635.1 | 6.51 | 6.65 | 6.5 | 6.1 | 6.6 | 6.5 | 6.8 | 640.305 | 948.78 | 97.403 | 277.535 | 210.476 | 315.032 |  | 103.918 | 209984 | 277435 | 147.595 | 105.527 | 302.261 | 127.364 | 0.122 | 0 | 237.349 |  | 229350 | 110025 | 217140 | 90450 | 95400 |  | 85950 | 272000 | 555000 | 269600 | 548000 | 822400 | 822400 | 0 |  | 350 | 827000 | 822400 | 0.5593% | 50.6 | 96 |  | 11.6 | 381825 |  | 446490 | 452.65 | 56.1
2026 | 2025 | 2025-06-01 | 30 | 2025-06-14 | 6:35 | 18:11 | 43093.2 | 40088.7 | 40092.6 | 37761.6 | 39634.7 | 40307.2 | 40842.2 | 41234.3 | 41897.5 | 40173.8 | 39416.6 | 42083.1 | 38849.9 | 40136.6 | 41977 | 42281.2 | 41938.3 | 31386.3 | 34152.8 | 36547.2 | 40056.8 | 36466.6 | 36389 | 9 | 8.6 | 8.9 | 8.2 | 8.6 | 8.6 | 8.8 | 8.9 | 8.9 | 8.6 | 8.9 | 8.9 | 8.7 | 8.6 | 9.2 | 8.8 | 8.9 | 7.7 | 8 | 8.2 | 9 | 8.3 | 8.2 | 396522.8 | 84219.5 | 312602.1 | 31386.3 | 82076.5 | 906807.2 | 8.7 | 8.85 | 8.61 | 7.7 | 8.85 | 8.6304 | 9.2 | 640.305 | 951.514 | 98.139 | 280.112 | 211.104 | 315.609 |  | 104.479 | 210381 | 278478 | 148.086 | 106.818 | 303.155 | 128.259 | 0.122 | 0 | 237.719 |  | 451110 | 165600 | 425205 | 141300 | 129825 |  | 126225 | 397000 | 1043000 | 392800 | 1032800 | 1430400 | 1432000 | 0 |  | 370 | 1440000 | 1430400 | 0.6711% | 50.6 | 96 |  | 11.6 | 562950 |  | 876315 | 906.85 | 76965.4
2026 | 2025 | 2025-06-01 | 30 | 2025-06-15 | 6:35 | 18:11 | 41893.2 | 41274.7 | 39998.5 | 38156.4 | 39986.7 | 40172.6 | 40254 | 41147.6 | 41648.8 | 39966.5 | 39057.7 | 41323.2 | 38703.3 | 38322.8 | 42107.7 | 42113.5 | 42186.1 | 33490.6 | 34968.6 | 37424.4 | 41124.9 | 39020.8 | 40598.4 | 9.6 | 9.3 | 9.4 | 9 | 9.3 | 9.2 | 9.3 | 9.5 | 9.4 | 9.1 | 9.4 | 9.5 | 9.1 | 9 | 9.8 | 9.3 | 9.5 | 8.3 | 8.6 | 8.8 | 9.6 | 9.1 | 9.1 | 393765.9 | 84299.6 | 321983.3 | 33490.6 | 81401.6 | 914941 | 9.23 | 9.4 | 9.28 | 8.3 | 9.4 | 9.2261 | 9.8 | 640.305 | 954.305 | 98.687 | 282.67 | 211.534 | 316.038 |  | 104.907 | 210671 | 279497 | 148.444 | 108.102 | 303.96 | 129.065 | 0.122 | 0 | 238.089 |  | 460515 | 123300 | 422070 | 96750 | 96525 |  | 96300 | 290000 | 1019000 | 286400 | 1027200 | 1288000 | 1289600 | 0 |  | 370 | 1309000 | 1288000 | 1.63% | 50.6 | 96 |  | 11.6 | 412875 |  | 882585 | 914.94 | 109003.4
2026 | 2025 | 2025-06-01 | 30 | 2025-06-16 | 6:30 | 18:11 | 49494.8 | 47055.2 | 47493.3 | 47820.4 | 47533.3 | 47628.7 | 47371.8 | 48160.6 | 48741.5 | 47929.9 | 47862.2 | 48744 | 47242.6 | 47951 | 48815.7 | 47246.1 | 48254.1 | 44850.4 | 46396.1 | 47247.1 | 46965.6 | 46110 | 47057.4 | 11.5 | 10.8 | 10.8 | 11 | 11 | 10.7 | 10.8 | 10.8 | 11.2 | 10.6 | 11 | 11.3 | 11 | 11 | 11.6 | 10.8 | 11.1 | 10.1 | 10.7 | 10.8 | 11.1 | 10.9 | 10.7 | 479176.7 | 95500.2 | 378912.1 | 44850.4 | 95532.4 | 1093971.8 | 11.03 | 10.95 | 10.9 | 10.1 | 10.8 | 10.9261 | 11.6 | 640.305 | 957.586 | 99.39 | 285.761 | 212.1 | 316.573 |  | 105.451 | 211042 | 280695 | 148.902 | 109.559 | 304.941 | 130.047 | 0.122 | 0 | 238.439 |  | 541365 | 158175 | 510015 | 127350 | 120375 |  | 122400 | 371000 | 1198000 | 366400 | 1165600 | 1569600 | 1571200 | 0 |  | 350 | 1569000 | 1569600 | -0.03823% | 50.6 | 95 |  | 11.6833 | 528300 |  | 1051380 | 1107.45 | 181242.9
2026 | 2025 | 2025-06-01 | 30 | 2025-06-17 | 6:38 | 18:13 | 34776.9 | 32312.6 | 29208 | 30276.9 | 30648.9 | 29652.6 | 30259.2 | 33214.6 | 32221.4 | 31688.2 | 27961.6 | 30885.6 | 30722.1 | 29211.6 | 35297.7 | 34532.9 | 34124 | 28920.2 | 33474.8 | 30764.7 | 29357.9 | 31825.8 | 32189.2 | 8.5 | 8.2 | 8.1 | 7.8 | 8 | 7.8 | 8 | 8.4 | 8.2 | 7.9 | 8 | 8.1 | 8.1 | 7.8 | 8.9 | 8.5 | 8.6 | 7.8 | 8.3 | 8 | 8.3 | 8.4 | 8.1 | 313991.2 | 68656.9 | 248485.3 | 28920.2 | 63473.8 | 723527.4 | 8.17 | 8.55 | 8.12 | 7.8 | 8.2 | 8.1652 | 8.9 | 640.305 | 959.775 | 100.097 | 287.801 | 212.644 | 317.014 |  | 105.998 | 211387 | 281552 | 149.328 | 110.622 | 305.686 | 130.795 | 0.122 | 0 | 238.789 |  | 361185 | 159075 | 336600 | 122400 | 99225 |  | 123075 | 345000 | 857000 | 340800 | 850400 | 1192000 | 1196800 | 0 |  | 350 | 1202000 | 1192000 | 0.8389% | 50.6 | 93 |  | 11.5833 | 503775 |  | 697785 | 742.5 | 9449.6
2026 | 2025 | 2025-06-01 | 30 | 2025-06-18 | 6:30 | 6:40 | 14454.3 | 37547.9 | 33242.9 | 33306.6 | 35114 | 33589 | 34105.6 | 37994.9 | 34761.9 | 35358.5 | 32387.1 | 34251.6 | 34285.9 | 33713 | 40555.4 | 39431.5 | 39066.3 | 34739.3 | 36612.7 | 33516.8 | 36272 | 36187.5 | 37665.2 | 8.4 | 8.9 | 8.5 | 8.1 | 8.6 | 8.2 | 8.4 | 9 | 8.5 | 8.5 | 8.4 | 8.4 | 8.5 | 8.4 | 9.6 | 9.1 | 9.1 | 8.6 | 8.7 | 8.3 | 9.1 | 8.8 | 8.7 | 328378.2 | 78497.8 | 284444.1 | 34739.3 | 72100.5 | 798159.9 | 8.57 | 9.1 | 8.63 | 8.6 | 8.7 | 8.6435 | 9.6 | 640.305 | 962.306 | 100.858 | 289.974 | 213.291 | 317.571 |  | 106.575 | 211787 | 282498 | 149.824 | 111.792 | 306.523 | 131.631 | 0.122 | 0 | 239.169 |  | 417615 | 171225 | 358545 | 145575 | 125325 |  | 129825 | 400000 | 946000 | 396800 | 936000 | 1339200 | 1337600 | 0 |  | 380 | 1346000 | 1339200 | 0.5078% | 50.6 | 93 |  | 0.16667 | 571950 |  | 776160 | 805.85 | 266.8
2026 | 2025 | 2025-06-01 | 30 | 2025-06-19 | 6:29 | 6:44 | 38442.5 | 43920.2 | 40780.8 | 42334.4 | 42099.2 | 42529.2 | 43175.9 | 44049.3 | 43139.5 | 41403.2 | 40048.3 | 41951.9 | 40624.2 | 37128.8 | 44135.4 | 43694.6 | 44514.8 | 41326.3 | 42011.3 | 40933.2 | 42487.1 | 41638.4 | 43055.6 | 10.6 | 10.4 | 10.3 | 9.9 | 10.2 | 9.9 | 10.2 | 10.5 | 10.4 | 10 | 10.2 | 10.2 | 10.4 | 10.2 | 11.2 | 10.5 | 10.7 | 10.1 | 10.5 | 9.9 | 10.4 | 10.3 | 10.1 | 407459.6 | 88209.4 | 341203.6 | 41326.3 | 87225.2 | 965424.1 | 10.35 | 10.6 | 10.23 | 10.1 | 10.35 | 10.3087 | 11.2 | 640.305 | 965.286 | 101.658 | 292.626 | 213.857 | 317.976 |  | 107.186 | 212144 | 283608 | 150.264 | 113.169 | 307.432 | 132.543 | 0.122 | 0 | 239.549 |  | 491700 | 180000 | 437580 | 127350 | 91125 |  | 137475 | 357000 | 1110000 | 352000 | 1101600 | 1454400 | 1459200 | 0 |  | 380 | 1467000 | 1454400 | 0.8663% | 50.6 | 93 |  | 0.25 | 535950 |  | 929280 | 1000.67 | 44129.5
2026 | 2025 | 2025-06-01 | 30 | 2025-06-20 | 6:13 | 18:30 | 46080.2 | 42513.8 | 36649.7 | 41777.2 | 42878.4 | 39298.6 | 38479.3 | 40816.6 | 42956.5 | 39688.8 | 40360.3 | 43620.6 | 44644 | 42985.2 | 46219 | 44507.1 | 44128.7 | 41586.1 | 44671.6 | 41942.5 | 40835.6 | 43752.5 | 43900.6 | 9.8 | 9.6 | 8.8 | 9.1 | 9.4 | 9 | 8.9 | 9.3 | 9.4 | 8.9 | 9.4 | 9.5 | 9.7 | 9.3 | 10.5 | 9.6 | 9.8 | 9.4 | 9.7 | 9.2 | 9.6 | 9.5 | 9.5 | 426861.9 | 88635.8 | 337913.2 | 41586.1 | 79295.9 | 974292.9 | 9.48 | 9.7 | 9.33 | 9.4 | 9.1 | 9.4304 | 10.5 | 640.305 | 968.23 | 102.404 | 295.375 | 214.465 | 318.49 |  | 107.782 | 212531 | 284714 | 150.742 | 114.539 | 308.36 | 133.472 | 0.122 | 0 | 239.929 |  | 485760 | 167850 | 453585 | 136800 | 115650 |  | 134100 | 387000 | 1106000 | 382400 | 1096000 | 1484800 | 1486400 | 0 |  | 380 | 1493000 | 1484800 | 0.5523% | 50.6 | 96 |  | 12.2833 | 554400 |  | 939345 | 998 | 4274.1
2026 | 2025 | 2025-06-01 | 30 | 2025-06-21 | 6:15 | 18:30 | 41544.8 | 40819.6 | 36063.9 | 35483.5 | 40356.1 | 37787.1 | 38251.8 | 39136.1 | 37469.8 | 37770.3 | 39026.9 | 37384.4 | 39514.9 | 38455.5 | 42956.1 | 42613.9 | 43262.7 | 39868.4 | 40031.1 | 37502 | 40456.9 | 39288.7 | 42722.5 | 9.7 | 9.6 | 9.1 | 9 | 9.6 | 9.1 | 9.2 | 9.3 | 9.2 | 9.1 | 9.6 | 9.1 | 9.8 | 9.2 | 10.2 | 9.6 | 9.8 | 9.5 | 9.5 | 9.1 | 9.7 | 9.4 | 9.7 | 390249.9 | 85876.6 | 314384.2 | 39868.4 | 77387.9 | 907767 | 9.44 | 9.7 | 9.38 | 9.5 | 9.25 | 9.4391 | 10.2 | 640.305 | 971.007 | 103.24 | 297.899 | 215.198 | 319.131 |  | 108.479 | 212997 | 285777 | 151.318 | 115.85 | 309.31 | 134.42 | 0.122 | 0 | 240.299 |  | 458205 | 188100 | 416460 | 164925 | 144225 |  | 156825 | 466000 | 1063000 | 460800 | 1048800 | 1520000 | 1516800 | 0 |  | 370 | 1529000 | 1520000 | 0.5921% | 50.6 | 96 |  | 12.25 | 654075 |  | 874665 | 966.22 | 7762
2026 | 2025 | 2025-06-01 | 30 | 2025-06-22 | 6:17 | 18:24 | 42171.6 | 41491.3 | 35504.5 | 40134.1 | 38966.4 | 37406.4 | 37083.2 | 39271.6 | 38081.1 | 37185.4 | 36355.6 | 40346.7 | 40197.7 | 37098.2 | 43001.4 | 43454.8 | 43058.6 | 38841.2 | 40088 | 39566.2 | 39503.4 | 39934.5 | 42777.1 | 9.1 | 8.9 | 8.6 | 8.7 | 8.7 | 8.4 | 8.5 | 8.8 | 8.6 | 8.4 | 8.6 | 8.8 | 8.9 | 8.4 | 9.5 | 9.1 | 9.2 | 8.7 | 8.9 | 8.7 | 9 | 8.9 | 8.9 | 391515.3 | 86513.4 | 318294.3 | 38841.2 | 76354.8 | 911519 | 8.79 | 9.15 | 8.74 | 8.7 | 8.65 | 8.7957 | 9.5 | 640.305 | 973.795 | 103.934 | 300.429 | 215.745 | 319.653 |  | 109.032 | 213362 | 286811 | 151.77 | 117.13 | 310.178 | 135.29 | 0.122 | 0 | 240.649 |  | 460020 | 156150 | 417450 | 123075 | 117450 |  | 124425 | 365000 | 1034000 | 361600 | 1024000 | 1388800 | 1392000 | 0 |  | 350 | 1399000 | 1388800 | 0.7344% | 50.6 | 96 |  | 12.1167 | 521100 |  | 877470 | 911.18 | 33002.3
2026 | 2025 | 2025-06-01 | 30 | 2025-06-23 | 6:20 | 18:35 | 47935.6 | 46595.9 | 44179.3 | 43265.7 | 45846.3 | 45806.1 | 45816.5 | 46684.2 | 47005.7 | 46225.3 | 43891.5 | 45082.2 | 47731.4 | 45269.7 | 49292.2 | 48307.8 | 48111.3 | 45424.7 | 48237 | 45531.4 | 42471.1 | 47682.1 | 45476.1 | 10.2 | 10.1 | 9.7 | 9.3 | 9.9 | 9.6 | 9.8 | 10.1 | 9.9 | 9.7 | 9.8 | 9.7 | 10.3 | 9.7 | 10.9 | 10.2 | 10.3 | 9.9 | 10.2 | 9.6 | 9.8 | 10.1 | 9.7 | 463375.6 | 96419.1 | 364149 | 45424.7 | 92500.7 | 1061869.1 | 9.98 | 10.25 | 9.83 | 9.9 | 9.95 | 9.9348 | 10.9 | 640.305 | 976.992 | 104.496 | 303.419 | 216.209 | 320.088 |  | 109.488 | 213667 | 287957 | 152.146 | 118.549 | 311.08 | 136.192 | 0.122 | 0 | 240.989 |  | 527505 | 126450 | 493350 | 104400 | 97875 |  | 102600 | 305000 | 1146000 | 300800 | 1135200 | 1443200 | 1443200 | 0 |  | 340 | 1451000 | 1443200 | 0.5405% | 50.6 | 96 |  | 12.25 | 431325 |  | 1020855 | 1070.07 | 67917.3
2026 | 2025 | 2025-06-01 | 30 | 2025-06-24 | 6:26 | 18:39 | 48094.4 | 48673.1 | 46873.2 | 45687 | 48321.5 | 47842.9 | 47510.3 | 47418.5 | 46469.7 | 47296.1 | 47767 | 47680.5 | 48297.1 | 47535.3 | 49292.2 | 48286.9 | 49086.6 | 47504.5 | 47580.6 | 47408.2 | 47906.4 | 46077.4 | 48941.7 | 11.2 | 11.6 | 10.8 | 10.5 | 11.4 | 10.7 | 10.9 | 10.9 | 10.8 | 10.7 | 11.3 | 10.9 | 11.5 | 10.9 | 12.1 | 11.5 | 11.7 | 11 | 11.1 | 10.8 | 11.4 | 10.9 | 11.4 | 477824.6 | 97373.5 | 379919.7 | 47504.5 | 94928.8 | 1097551.1 | 11.13 | 11.6 | 11.05 | 11 | 10.9 | 11.1304 | 12.1 | 640.305 | 980.298 | 105.177 | 306.493 | 216.743 | 320.579 |  | 110.042 | 214023 | 289164 | 152.586 | 120.045 | 312.049 | 137.164 | 0.122 | 0 | 241.349 |  | 545490 | 153225 | 507210 | 120150 | 110475 |  | 124650 | 356000 | 1207000 | 352000 | 1196800 | 1550400 | 1555200 | 0 |  | 360 | 1563000 | 1550400 | 0.8127% | 50.6 | 94 |  | 12.2167 | 508500 |  | 1052700 | 1107.55 | 76894
2026 | 2025 | 2025-06-01 | 30 | 2025-06-25 | 6:30 | 18:35 | 47343 | 47963 | 42126 | 41604 | 46213 | 42605 | 34994 | 46697 | 43430 | 45045 | 43873 | 43085 | 45750 | 44585 | 49611 | 48844 | 49050 | 45475 | 46507 | 44242 | 44991 | 45287 | 47519 | 9.8968 | 10.2587 | 9.3458 | 9.023 | 9.8062 | 9.0986 | 9.6031 | 9.8658 | 9.3715 | 9.3938 | 9.6978 | 9.257 | 9.8735 | 9.4948 | 10.7565 | 10.3433 | 10.3782 | 9.7342 | 9.7596 | 9.3341 | 9.9766 | 9.6848 | 9.884 | 452167 | 97894 | 359612 | 45475 | 81691 | 1036839 | 9.681 | 10.3607 | 9.6572 | 9.7342 | 9.7345 | 9.7321 | 10.7565 | 640.305 | 983.415 | 105.676 | 309.421 | 217.184 | 320.993 |  | 110.445 | 214306 | 290274 | 152.936 | 121.415 | 312.914 | 138.029 | 0.122 | 0 | 241.709 |  | 514305 | 112275 | 483120 | 99225 | 93150 |  | 90675 | 283000 | 1110000 | 280000 | 1096000 | 1384000 | 1384000 | 0 |  | 360 | 1393000 | 1384000 | 0.6503% | 50.6 | 96 |  | 12.0833 | 395325 |  | 997425 | 1042.72 | 70206.2
2026 | 2025 | 2025-06-01 | 30 | 2025-06-26 | 6:42 | 18:18 | 46509 | 46875 | 42275 | 40672 | 46671 | 44372 | 43945 | 44010 | 43578 | 44154 | 44262 | 43898 | 45974 | 44376 | 47882 | 46933 | 47836 | 45413 | 45770 | 43610 | 45202 | 44240 | 47430 | 9.7351 | 9.702 | 9.3223 | 8.6121 | 9.7857 | 9.1926 | 9.2833 | 9.3363 | 9.1375 | 9.1853 | 9.725 | 9.3608 | 9.8757 | 9.4938 | 10.4374 | 9.5923 | 9.9259 | 9.6578 | 9.7013 | 9.1124 | 9.846 | 9.3677 | 9.7434 | 448710 | 94769 | 359040 | 45413 | 87955 | 1035887 | 9.5949 | 9.7591 | 9.4007 | 9.6578 | 9.3098 | 9.5275 | 10.4374 | 640.305 | 986.561 | 106.203 | 312.308 | 217.602 | 321.264 |  | 110.879 | 214559 | 291388 | 153.248 | 122.799 | 313.763 | 138.881 | 0.122 | 0 | 242.069 |  | 519090 | 118575 | 476355 | 94050 | 60975 |  | 97650 | 253000 | 1114000 | 249600 | 1107200 | 1358400 | 1363200 | 0 |  | 360 | 1367000 | 1358400 | 0.6331% | 50.6 | 96 |  | 11.6 | 371250 |  | 995445 | 1040.28 | 102602.9
2026 | 2025 | 2025-06-01 | 30 | 2025-06-27 | 6:26 | 18:44 | 37596.7 | 31736.3 | 32681 | 32094 | 33058.4 | 32322.8 | 31946.3 | 33428.7 | 33645.8 | 33262.5 | 33945.9 | 35003.9 | 33408.8 | 34780.4 | 36535.8 | 33130.9 | 33378.4 | 31260.7 | 35543.1 | 34019.6 | 31664.3 | 32629 | 32126.1 | 10 | 9 | 9.3 | 8.8 | 9.3 | 8.9 | 9.1 | 9.4 | 9.4 | 9.1 | 9.6 | 9.4 | 9.4 | 9.5 | 10.1 | 9.2 | 9.3 | 9 | 9.6 | 9.3 | 9.2 | 9.2 | 8.9 | 346777.7 | 66509.3 | 259276.7 | 31260.7 | 65375 | 769199.4 | 9.53 | 9.25 | 9.12 | 9 | 9.25 | 9.3043 | 10.1 | 640.423 | 988.41 | 107.05 | 314.82 | 218.307 | 321.807 |  | 111.581 | 214998 | 292319 | 153.791 | 123.947 | 314.612 | 139.731 | 0.123 | 0 | 242.429 | 19470 | 305085 | 190575 | 414480 | 158625 | 122175 |  | 157950 | 439000 | 931000 | 434400 | 918400 | 1358400 | 1360000 | 1600 |  | 360 | 1370000 | 1356800 | 0.9729% | 50.6 | 68 |  | 12.3 | 629325 |  | 739035 | 787.8 | 32446.9
2026 | 2025 | 2025-06-01 | 30 | 2025-06-28 | 6:19 | 18:45 | 38746 | 35182 | 35127 | 29067 | 30776 | 33925 | 33307 | 36531 | 30251 | 35944 | 34846 | 36875 | 37908 | 35448 | 39876 | 19741 | 29400 | 32757 | 37146 | 35411 | 28221 | 30276 | 31033 | 8.6 | 8.5 | 8.4 | 7.9 | 8.3 | 8.2 | 8.3 | 8.5 | 8.2 | 8.2 | 8.5 | 8.5 | 8.6 | 8.2 | 9.2 | 8.1 | 8.5 | 8.2 | 8.5 | 8.3 | 8.3 | 8.3 | 8.2 | 367327 | 49141 | 248731 | 32757 | 69838 | 767794 | 8.5 | 8.3 | 8.27 | 8.2 | 8.4 | 8.3696 | 9.2 | 642.8 | 988.41 | 107.891 | 316.944 | 218.995 | 322.433 |  | 112.282 | 215452 | 293256 | 154.351 | 125.106 | 315.472 | 140.594 | 0.123 | 0 | 242.809 | 392205 |  | 189225 | 350460 | 154800 | 140850 |  | 157725 | 454000 | 937000 | 448000 | 927200 | 1376000 | 1380800 | 0 |  | 380 | 1391000 | 1376000 | 1.09% | 50.6 | 96 |  | 12.4333 | 642600 |  | 742665 | 771.89 | 12185.4
2026 | 2025 | 2025-06-01 | 30 | 2025-06-29 | 6:39 | 18:42 | 42796.5 | 42378.6 | 36708.9 | 36470.1 | 41153.5 | 39337.9 | 39954.1 | 39588.3 | 40391.2 | 39900.3 | 39390.4 | 38222.1 | 41034.5 | 39424.2 | 44006 | 43645.5 | 32367.3 | 41586.8 | 42444.7 | 37466.1 | 39399.8 | 42315.7 | 43556.2 | 9.7 | 9.9 | 9.2 | 8.7 | 9.5 | 9.1 | 9.4 | 9.5 | 9.4 | 9.4 | 9.6 | 9 | 9.7 | 9.3 | 10.4 | 9.9 | 9.7 | 9.5 | 9.8 | 9 | 9.7 | 9.5 | 9.7 | 401393.7 | 76012.8 | 325003 | 41586.8 | 79542.4 | 923538.7 | 9.51 | 9.8 | 9.44 | 9.5 | 9.45 | 9.5043 | 10.4 | 645.394 | 988.41 | 108.769 | 319.754 | 219.69 | 323.04 |  | 113.016 | 215910 | 294342 | 154.918 | 126.45 | 316.432 | 141.553 | 0.123 | 0 | 243.179 | 428010 |  | 197550 | 463650 | 156375 | 136575 |  | 165150 | 458000 | 1086000 | 453600 | 1075200 | 1536000 | 1534400 | 0 |  | 370 | 1544000 | 1536000 | 0.5208% | 50.6 | 96 |  | 12.05 | 655650 |  | 891660 | 926.53 | 144.3
2026 | 2025 | 2025-06-01 | 30 | 2025-06-30 | 6:19 | 18:26 | 45187.7 | 46070.8 | 40727.1 | 40271.5 | 44476.5 | 41753.7 | 42187.3 | 43193.7 | 41912.7 | 43154.2 | 42050.6 | 42865 | 43937.1 | 42592.2 | 46713.8 | 45746.9 | 46640.8 | 43966.4 | 44462.8 | 42761.1 | 44387.2 | 42358.8 | 45869.9 | 10.3 | 10.4 | 9.7 | 9.4 | 10.1 | 9.6 | 9.8 | 10 | 9.9 | 9.8 | 10.1 | 9.7 | 10.2 | 9.9 | 10.9 | 10.2 | 10.5 | 10 | 10.2 | 9.7 | 10.4 | 9.8 | 10.3 | 434451.6 | 92387.7 | 347101.1 | 43966.4 | 85381 | 1003287.8 | 10.05 | 10.35 | 9.97 | 10 | 9.9 | 10.0391 | 10.9 | 648.204 | 988.41 | 109.648 | 322.811 | 220.387 | 323.676 |  | 113.743 | 216374 | 295505 | 155.492 | 127.895 | 317.444 | 142.568 | 0.123 | 0 | 243.579 | 463650 |  | 197775 | 504405 | 156825 | 143100 |  | 163575 | 464000 | 1163000 | 459200 | 1156000 | 1619200 | 1624000 | 0 |  | 400 | 1627000 | 1619200 | 0.4817% | 50.6 | 96 |  | 12.1167 | 661275 |  | 968055 | 1003.29 | 35332.6
2026 | 2025 | 2025-07-01 | 31 | 2025-07-01 | 6:30 | 18:35 | 41556.1 | 42508.8 | 36210.5 | 38144.9 | 40843.1 | 37046.2 | 37884.5 | 38950.3 | 36278.3 | 38584.2 | 37811.8 | 36167.5 | 40161.3 | 37399.5 | 43423.2 | 42656.3 | 43440.2 | 38806 | 40545.6 | 36320.1 | 40152.4 | 38392.5 | 42954.2 | 9.4 | 9.5 | 8.7 | 8.8 | 9.2 | 8.5 | 8.8 | 9.1 | 8.5 | 9 | 9 | 8.5 | 9.2 | 8.7 | 9.9 | 9.5 | 9.6 | 9.1 | 9.2 | 8.5 | 9.4 | 9 | 9.3 | 388179.8 | 86096.5 | 316320.4 | 38806 | 76834.8 | 906237.5 | 9.01 | 9.55 | 9.01 | 9.1 | 8.95 | 9.0609 | 9.9 | 650.715 | 988.41 | 110.314 | 325.597 | 220.905 | 324.16 |  | 114.286 | 216722 | 296540 | 155.921 | 129.17 | 318.296 | 143.42 | 0.123 | 0 | 243.959 | 414315 |  | 149850 | 459690 | 116550 | 108900 |  | 122175 | 348000 | 1035000 | 343200 | 1020000 | 1363200 | 1363200 | 0 |  | 380 | 1383000 | 1363200 | 1.452% | 50.6 | 96 |  | 12.0833 | 497475 |  | 874005 | 906.23 | 24078.6
2026 | 2025 | 2025-07-01 | 31 | 2025-07-02 | 6:32 | 18:37 | 41236 | 40556 | 35781 | 36403 | 38599 | 37152 | 36901 | 38422 | 35801 | 37219 | 37380 | 36827 | 39048 | 37246 | 41913 | 41153 | 41837 | 38134 | 38996 | 36839 | 39115 | 37347 | 41892 | 9.1 | 9 | 8.6 | 8.6 | 8.9 | 8.5 | 8.6 | 8.8 | 8.4 | 8.5 | 8.9 | 8.6 | 9 | 8.6 | 9.5 | 9 | 9.1 | 8.8 | 8.8 | 8.5 | 9 | 8.7 | 8.9 | 382485 | 82990 | 306865 | 38134 | 75323 | 885797 | 8.81 | 9.05 | 8.74 | 8.8 | 8.7 | 8.8 | 9.5 | 653.196 | 988.41 | 110.944 | 328.308 | 221.439 | 324.678 |  | 114.797 | 217074 | 297546 | 156.356 | 130.394 | 319.134 | 144.258 | 0.123 | 0 | 244.319 | 409365 |  | 141750 | 447315 | 120150 | 116550 |  | 114975 | 352000 | 1006000 | 348000 | 979200 | 1340800 | 1340800 | 0 |  | 360 | 1358000 | 1340800 | 1.283% | 50.6 | 96 |  | 12.0833 | 493425 |  | 856680 | 885.8 | 110675.2
2026 | 2025 | 2025-07-01 | 31 | 2025-07-03 | 6:21 | 18:38 | 44432 | 42776 | 36434 | 38395 | 41322 | 37978 | 37552 | 41023 | 40489 | 39697 | 38215 | 39935 | 40493 | 39656 | 44382 | 44900 | 43815 | 40398 | 41907 | 39728 | 40752 | 41786 | 42830 | 9.7 | 9.6 | 8.8 | 8.9 | 9.3 | 8.7 | 8.8 | 9.4 | 9.1 | 9 | 9.1 | 9 | 9.2 | 9 | 10.1 | 9.8 | 9.8 | 9.3 | 9.4 | 9 | 9.6 | 9.4 | 9.4 | 404879 | 88715 | 326328 | 40398 | 78575 | 938895 | 9.23 | 9.8 | 9.22 | 9.3 | 9.1 | 9.2783 | 10.1 | 655.811 | 988.41 | 111.576 | 331.154 | 222.024 | 325.207 |  | 115.305 | 217439 | 298599 | 156.808 | 131.692 | 320.008 | 145.125 | 0.123 | 0 | 244.689 | 431475 |  | 142200 | 469590 | 131625 | 119025 |  | 114300 | 365000 | 1053000 | 361600 | 1038400 | 1398400 | 1387200 | 0 |  | 370 | 1418000 | 1398400 | 1.402% | 50.6 | 96 |  | 12.2833 | 507150 |  | 901065 | 939 | 21966.8
2026 | 2025 | 2025-07-01 | 31 | 2025-07-04 | 6:22 | 18:30 | 47243.5 | 45319.2 | 43034.8 | 43179.2 | 45451 | 42037.6 | 42816.7 | 45625.2 | 44130.5 | 44170.7 | 42662.2 | 44619.5 | 44506 | 44266.5 | 48201.8 | 46506.8 | 46918.4 | 43879.4 | 47108.2 | 44601 | 44391.5 | 45263 | 46003.1 | 10.2 | 10.2 | 9.6 | 9.4 | 9.9 | 9.3 | 9.6 | 10 | 9.6 | 9.6 | 9.6 | 9.8 | 9.9 | 9.6 | 10.8 | 10.3 | 10.4 | 9.8 | 10.1 | 9.7 | 10.3 | 9.9 | 10.1 | 450414.2 | 93425.2 | 355775.1 | 43879.4 | 88441.9 | 1031935.8 | 9.89 | 10.35 | 9.83 | 9.8 | 9.8 | 9.9 | 10.8 | 658.72 | 988.41 | 112.28 | 334.27 | 222.646 | 325.746 |  | 115.894 | 217837 | 299725 | 157.299 | 133.11 | 320.971 | 146.096 | 0.123 | 0 | 245.039 | 479985 |  | 158400 | 514140 | 139950 | 121275 |  | 132525 | 398000 | 1126000 | 392800 | 1134400 | 1540800 | 1553600 | 0 |  | 350 | 1524000 | 1540800 | -1.09% | 50.6 | 96 |  | 12.1333 | 552150 |  | 994125 | 1036.83 | 45338.6
2026 | 2025 | 2025-07-01 | 31 | 2025-07-05 | 6:37 | 18:40 | 47177 | 47237 | 43447 | 42247 | 45097 | 43793 | 44863 | 45197 | 43859 | 45633 | 43527 | 42497 | 45101 | 43821 | 48179 | 47902 | 47800 | 44604 | 45650 | 42258 | 44621 | 44386 | 46607 | 10.1 | 10.1 | 9.6 | 9.6 | 9.9 | 9.4 | 9.7 | 9.9 | 9.5 | 9.6 | 9.7 | 9.5 | 10 | 9.5 | 10.6 | 10.1 | 10.2 | 9.7 | 9.8 | 9.5 | 9.9 | 9.6 | 10 | 447290 | 95702 | 357847 | 44604 | 90060 | 1035503 | 9.79 | 10.15 | 9.76 | 9.7 | 9.8 | 9.8043 | 10.6 | 661.609 | 988.41 | 112.967 | 337.417 | 223.256 | 326.316 |  | 116.45 | 218224 | 300872 | 157.777 | 134.53 | 321.926 | 147.051 | 0.123 | 0 | 245.409 | 476685 |  | 154575 | 519255 | 137250 | 128250 |  | 125100 | 387000 | 1147000 | 382400 | 1136000 | 1528000 | 1528000 | 0 |  | 370 | 1534000 | 1528000 | 0.3927% | 50.6 | 96 |  | 12.05 | 545175 |  | 995940 | 1035.51 | 81244.7
2026 | 2025 | 2025-07-01 | 31 | 2025-07-06 | 6:44 | 18:43 | 49113 | 49683 | 49337 | 47434 | 50581 | 49864 | 49487 | 48172 | 48077 | 49006 | 50308 | 50025 | 50558 | 49713 | 50482 | 49901 | 49994 | 49857 | 48634 | 50572 | 49469 | 46347 | 50775 | 10.9 | 11 | 10.8 | 10.3 | 11.2 | 10.6 | 10.7 | 10.8 | 10.7 | 10.7 | 11.2 | 10.9 | 11.3 | 11 | 11.6 | 11.1 | 11 | 11.1 | 11 | 11 | 11 | 10.5 | 11.1 | 497748 | 99895 | 392230 | 49857 | 97659 | 1137389 | 11.04 | 11.05 | 10.79 | 11.1 | 10.75 | 10.9348 | 11.6 | 664.812 | 988.41 | 113.706 | 340.845 | 223.83 | 326.832 |  | 117.054 | 218606 | 302135 | 158.249 | 136.1 | 322.945 | 148.074 | 0.123 | 0 | 245.769 | 528495 |  | 166275 | 565620 | 129150 | 116100 |  | 135900 | 382000 | 1263000 | 377600 | 1256000 | 1630400 | 1636800 | 0 |  | 360 | 1645000 | 1630400 | 0.8955% | 50.6 | 96 |  | 11.9833 | 547425 |  | 1094115 | 1137.39 | 169324.9
2026 | 2025 | 2025-07-01 | 31 | 2025-07-07 | 6:30 | 18:31 | 48268 | 48727 | 46624 | 43222 | 48107 | 48161 | 47770 | 47454 | 44220 | 47491 | 47974 | 46422 | 47274 | 46500 | 49639 | 48867 | 49810 | 48146 | 47046 | 46309 | 47482 | 45587 | 48605 | 10.6 | 10.7 | 10.3 | 9.6 | 10.4 | 10.2 | 10.3 | 10.6 | 9.9 | 10.2 | 10.6 | 10.2 | 10.6 | 10.2 | 11.4 | 10.6 | 10.9 | 10.5 | 10.4 | 10.1 | 10.7 | 10.1 | 10.6 | 473547 | 98677 | 374111 | 48146 | 95224 | 1089705 | 10.46 | 10.75 | 10.31 | 10.5 | 10.45 | 10.4217 | 11.4 | 667.864 | 988.41 | 114.581 | 344.139 | 224.51 | 327.429 |  | 117.772 | 219055 | 303378 | 158.804 | 137.631 | 323.996 | 149.125 | 0.123 | 0 | 246.139 | 503580 |  | 196875 | 543510 | 153000 | 134325 |  | 161550 | 449000 | 1243000 | 444000 | 1224800 | 1681600 | 1681600 | 0 |  | 370 | 1692000 | 1681600 | 0.6185% | 50.6 | 96 |  | 12.0167 | 645750 |  | 1047090 | 1089.7 | 66715.5
2026 | 2025 | 2025-07-01 | 31 | 2025-07-08 | 6:50 | 18:35 | 42109 | 42321 | 40550 | 39834 | 43161 | 41539 | 41064 | 40168 | 39937 | 40144 | 41560 | 42161 | 42959 | 41477 | 43082 | 42579 | 43655 | 41565 | 41720 | 41560 | 41638 | 39946 | 43355 | 9.5 | 9.5 | 9.3 | 9.1 | 9.5 | 9.2 | 9.3 | 9.2 | 9.1 | 9 | 9.6 | 9.4 | 9.7 | 9.3 | 9.8 | 9.4 | 9.6 | 9.4 | 9.4 | 9.4 | 9.4 | 9.2 | 9.4 | 417322 | 86234 | 331731 | 41565 | 81232 | 958084 | 9.44 | 9.5 | 9.29 | 9.4 | 9.25 | 9.3783 | 9.8 | 670.55 | 988.41 | 115.288 | 347.044 | 225.068 | 327.928 |  | 118.351 | 219423 | 304462 | 159.259 | 138.971 | 324.896 | 150.027 | 0.123 | 0 | 246.509 | 443190 |  | 159075 | 479325 | 125550 | 112275 |  | 130275 | 368000 | 1084000 | 364000 | 1072000 | 1440000 | 1443200 | 0 |  | 370 | 1452000 | 1440000 | 0.8333% | 50.6 | 96 |  | 11.75 | 527175 |  | 922515 | 957.73 | 16106.9
2026 | 2025 | 2025-07-01 | 31 | 2025-07-09 | 6:27 | 18:38 | 43432 | 40513 | 39926 | 39711 | 40730 | 40715 | 29100 | 41249 | 41876 | 40525 | 39052 | 41573 | 41737 | 40240 | 44284 | 42437 | 43346 | 38372 | 42976 | 40788 | 38459 | 41477 | 41588 | 9.2 | 9.1 | 9.1 | 8.8 | 9.1 | 9 | 8.7 | 9.1 | 9.2 | 8.8 | 9.1 | 9.1 | 9.3 | 9 | 9.9 | 9.2 | 9.5 | 8.9 | 9.2 | 8.9 | 9.1 | 9 | 9.1 | 414533 | 85783 | 325069 | 38372 | 70349 | 934106 | 9.16 | 9.35 | 9.02 | 8.9 | 8.9 | 9.1043 | 9.9 | 673.225 | 988.41 | 116.019 | 349.82 | 225.784 | 328.62 |  | 118.953 | 219876 | 305525 | 159.818 | 140.292 | 325.837 | 150.97 | 0.123 | 0 | 246.889 | 441375 |  | 164475 | 458040 | 161100 | 155700 |  | 135450 | 453000 | 1063000 | 447200 | 1056800 | 1505600 | 1508800 | 0 |  | 380 | 1516000 | 1505600 | 0.6908% | 50.6 | 96 |  | 12.1833 | 616725 |  | 899415 | 934.11 | 54211.3
2026 | 2025 | 2025-07-01 | 31 | 2025-07-10 | 6:24 | 18:36 | 35848 | 35128 | 30025 | 30944 | 31765 | 30403 | 31071 | 32622 | 29004 | 30867 | 30654 | 31064 | 32877 | 30251 | 36311 | 36259 | 36431 | 31187 | 33611 | 29977 | 31810 | 31915 | 35280 | 8.2 | 8.2 | 7.9 | 7.6 | 7.9 | 7.7 | 7.8 | 8.1 | 7.5 | 7.8 | 8 | 7.8 | 8 | 7.6 | 8.6 | 8.4 | 8.4 | 7.9 | 8 | 7.5 | 8.1 | 7.9 | 8.1 | 321485 | 72690 | 256249 | 31187 | 63693 | 745304 | 7.94 | 8.4 | 7.89 | 7.9 | 7.95 | 7.9565 | 8.6 | 675.309 | 988.41 | 116.887 | 352.099 | 226.501 | 329.266 |  | 119.661 | 220342 | 306440 | 160.395 | 141.424 | 326.694 | 151.829 | 0.123 | 0 | 247.269 | 343860 |  | 195300 | 376035 | 161325 | 145350 |  | 159300 | 466000 | 915000 | 461600 | 905600 | 1371200 | 1374400 | 0 |  | 380 | 1381000 | 1371200 | 0.7147% | 50.6 | 96 |  | 12.2 | 661275 |  | 719895 | 745.32 | 33668.4
2026 | 2025 | 2025-07-01 | 31 | 2025-07-11 | 6:28 | 18:34 | 27846 | 25150 | 21919 | 24260 | 24206 | 22214 | 22689 | 24044 | 23343 | 22167 | 21957 | 26350 | 24966 | 22732 | 28007 | 27208 | 27411 | 22980 | 25244 | 23898 | 21833 | 23894 | 27147 | 7.2 | 7.1 | 6.9 | 6.9 | 7.1 | 6.7 | 6.9 | 7 | 6.8 | 6.8 | 7 | 7.3 | 7 | 6.8 | 7.6 | 7.3 | 7.4 | 7 | 7.1 | 7 | 7.2 | 7.1 | 7.3 | 245086 | 54619 | 192047 | 22980 | 46733 | 561465 | 7.07 | 7.35 | 7.01 | 7 | 6.95 | 7.0652 | 7.6 | 676.895 | 988.41 | 117.626 | 353.805 | 227.167 | 329.896 |  | 120.244 | 220765 | 307148 | 160.918 | 142.297 | 327.397 | 152.532 | 0.123 | 0 | 247.629 | 261690 |  | 166275 | 281490 | 149850 | 141750 |  | 131175 | 423000 | 708000 | 418400 | 698400 | 1124800 | 1124800 | 0 |  | 360 | 1131000 | 1124800 | 0.5512% | 50.6 | 96 |  | 12.1 | 589050 |  | 543180 | 562.93 | 41870.1
2026 | 2025 | 2025-07-01 | 31 | 2025-07-12 | 6:20 | 18:35 | 32669.9 | 29627.5 | 26006.7 | 22311.8 | 25184.7 | 24653.5 | 25942.5 | 29416.6 | 22319.4 | 28692 | 26962.9 | 27997.3 | 29021.6 | 27665.8 | 33290.3 | 30464.8 | 30266.9 | 27787.2 | 30425.8 | 27250.1 | 23800.1 | 23857.1 | 27206 | 7.9 | 7.8 | 7.4 | 7.1 | 7.7 | 7.2 | 7.5 | 7.6 | 7.1 | 7.6 | 7.6 | 7.4 | 7.5 | 7.3 | 8.2 | 7.9 | 8 | 7.7 | 7.7 | 7.3 | 7.8 | 7.6 | 7.8 | 289982.4 | 60731.7 | 198960.1 | 27787.2 | 55359.1 | 632820.5 | 7.59 | 7.95 | 7.52 | 7.7 | 7.55 | 7.5957 | 8.2 | 678.778 | 988.41 | 118.364 | 355.639 | 227.908 | 330.521 |  | 120.843 | 221208 | 307928 | 161.465 | 143.279 | 328.155 | 153.3 | 0.123 | 0 | 247.999 | 310695 |  | 166050 | 302610 | 166725 | 140625 |  | 134775 | 443000 | 780000 | 437600 | 785600 | 1212800 | 1228800 | 0 |  | 370 | 1223000 | 1212800 | 0.841% | 50.6 | 96 |  | 12.25 | 608175 |  | 613305 | 639.03 | 55873.6
2026 | 2025 | 2025-07-01 | 31 | 2025-07-13 | 6:22 | 18:20 | 36006.1 | 36763 | 29810.2 | 31260.1 | 34751 | 30854.6 | 30933 | 33129 | 30556.5 | 31685.9 | 31661.7 | 31374.6 | 33264.2 | 31963.1 | 38271.5 | 38691 | 38191.8 | 34674.4 | 34397.7 | 31745.6 | 34487 | 32807.5 | 38701.7 | 8.2 | 8.2 | 7.8 | 7.7 | 8.2 | 7.7 | 7.8 | 8 | 7.7 | 7.9 | 8.1 | 7.8 | 7.9 | 7.8 | 8.8 | 8.5 | 8.5 | 8.2 | 8.1 | 7.8 | 8.4 | 8 | 8.4 | 330180.6 | 76882.8 | 270181.4 | 34674.4 | 64062 | 775981.2 | 8.02 | 8.5 | 8.01 | 8.2 | 7.9 | 8.0652 | 8.8 | 680.92 | 988.41 | 119.114 | 358.046 | 228.6 | 331.085 |  | 121.457 | 221629 | 308927 | 161.985 | 144.515 | 328.987 | 154.136 | 0.123 | 0 | 248.379 | 353430 |  | 168750 | 397155 | 155700 | 126900 |  | 138150 | 421000 | 999000 | 416000 | 988800 | 1331200 | 1337600 | 0 |  | 380 | 1420000 | 1331200 | 6.671% | 50.6 | 96 |  | 11.9667 | 589500 |  | 750585 | 775.97 | 61374.5
2026 | 2025 | 2025-07-01 | 31 | 2025-07-14 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-15 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-16 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-17 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-18 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-19 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-20 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-21 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-22 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-23 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-24 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-25 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-26 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-27 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-28 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-29 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-30 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-07-01 | 31 | 2025-07-31 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-01 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-02 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-03 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-04 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-05 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-06 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-07 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-08 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-09 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-10 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-11 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-12 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-13 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-14 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-15 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-16 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-17 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-18 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-19 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-20 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-21 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-22 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-23 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-24 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-25 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-26 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-27 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0
2026 | 2025 | 2025-08-01 | 31 | 2025-08-28 | [48 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 50.6 |  |  | 0 | 0 |  | 0 |  | 0

## WTG_BD
Sr. No. | Financial Year | Calendar Year | Operating Year | Month | Date | Affected WTG | SPV | Consumer | Plant Equivalent Weightage | Error Code | Error Text | Breakdown Description | Stoppage Type | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Fault Category | Paired WTG for Enegy based MA | Paired WTG Generation for loss calculation | Estimated Energy Loss (kWh) | Special Remarks | PTW No. | Job Card No.
1 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | KUD10 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.55625 | 0.55625 | 0.57014 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.036
2 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | KUD20 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.62917 | 0.62917 | 0.68889 | 0 | 1.4333 | 1.4333 | Manual stop for Yaw claw re torquing work. | Close | 0.062319 |  | 100% |  | 0.463
3 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-30 | KUD08 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.61875 | 0.61875 | 0.63333 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.001
4 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-30 | KUD13 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.51319 | 0.51319 | 0.52708 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.003
5 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-30 | KUD09 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.59028 | 0.59028 | 0.60625 | 0 | 0.38333 | 0.38333 | Auto cable twist | Close | 0.016667 |  | 100% |  | 0.004
6 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-30 | KUD22 | O2R3 | JK | 4.348% | 5069 | Pitch pos C meas. signal fault | Pitch pos C meas. signal fault | ROW | 0.60417 | 0.60417 | 0.77083 | 0 | 4 | 4 | WTG can not attend because ROW issue. | Close | 0 |  | 100% |  | 0
7 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-30 | KUD22 | O2R3 | JK | 4.348% | 5069 | Pitch pos C meas. signal fault | Pitch pos C meas. signal fault | Breakdown | 0.77083 | 0.77083 | 0.85347 | 0 | 1.9833 | 1.9833 | Attend and HUB CT6061 Module changed. | Close | 0.086232 |  | 100% |  | 0.762
8 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | KUD01 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.55694 | 0.55694 | 0.57361 | 0 | 0.4 | 0.4 | Auto cable twist | Close | 0.017391 |  | 100% |  | 0.058
9 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | KUD11 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.49514 | 0.49514 | 0.57083 | 0 | 1.8167 | 1.8167 | Manual stop for Yearly generator Aligment work. | Close | 0.078986 |  | 100% |  | 0.05
10 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | KUD05 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.39028 | 0.39028 | 0.40486 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0
11 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | KUD07 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.54792 | 0.54792 | 0.56181 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.001
12 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | KUD09 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.52639 | 0.52639 | 0.54097 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.008
13 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | KUD18 | O2R4 | SGDCIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.61736 | 0.61736 | 0.63403 | 0 | 0.4 | 0.4 | Auto cable twist | Close | 0.017391 |  | 100% |  | 0.068
14 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | KUD22 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.42222 | 0.42222 | 0.43611 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.002
15 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | KUD23 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.67569 | 0.67569 | 0.69514 | 0 | 0.46667 | 0.46667 | Auto cable twist | Close | 0.02029 |  | 100% |  | 0.089
16 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | KUD10 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.39236 | 0.39236 | 0.40625 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.001
17 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | KUD11 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.38611 | 0.38611 | 0.4 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.001
18 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | KUD12 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.40903 | 0.40903 | 0.42431 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.001
19 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | KUD15 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.39583 | 0.39583 | 0.41042 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.001
20 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | KUD19 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.39028 | 0.39028 | 0.40417 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.002
21 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | KUD20 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.37569 | 0.37569 | 0.39028 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.002
22 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | KUD17 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.50208 | 0.50208 | 0.51597 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.001
23 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | KUD18 | O2R4 | SGDCIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.40833 | 0.54375 | 0.55764 | 3.25 | 0.33333 | 3.5833 | Auto cable twist | Close | 0.1558 |  | 100% |  | 0.001
24 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | KUD22 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.45 | 0.58542 | 0.59931 | 3.25 | 0.33333 | 3.5833 | Auto cable twist | Close | 0.1558 |  | 100% |  | 0.165
25 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | KUD04 | O2R3 | JK | 4.348% | 3487 | Gear HSBearA Temp:___°C | Gear HSBearA Temp:___°C |  | 0.098611 | 0.098611 | 0.11458 | 0 | 0.38333 | 0.38333 | Auto reset | Close | 0.016667 |  | 100%
26 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | KUD04 | O2R3 | JK | 4.348% | 3487 | Gear HSBearA Temp:___°C | Gear HSBearA Temp:___°C |  | 0.32083 | 0.32083 | 0.38819 | 0 | 1.6167 | 1.6167 | Ups reboot done. | Close | 0.07029 |  | 100%
27 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | KUD07 | O2R3 | JK | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 |  | 0.41875 | 0.41875 | 0.74722 | 0 | 7.8833 | 7.8833 | Manual stop for 2 years service Day-1 | Close | 0.34275 |  | 100%
28 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | KUD17 | O2R2 | SIL | 4.348% | 3483 | GearOilTempLow ___°C | GearOilTempLow ___°C |  | 0.25 | 0.25 | 0.35903 | 0 | 2.6167 | 2.6167 | we checked and found that PT100 sensor was malfunctioning so once rebooted system and found temp normal. | Close | 0.11377 |  | 100%
29 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD01 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 6, 540Â° |  | 0.20972 | 0.20972 | 0.22361 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100%
30 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD02 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 6, 651Â° |  | 0.84306 | 0.84306 | 0.86319 | 0 | 0.48333 | 0.48333 | Auto cable twist | Close | 0.021014 |  | 100%
31 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD05 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 5, 540Â° |  | 0.15069 | 0.15069 | 0.16528 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100%
32 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD05 | O2R3 | JK | 4.348% | 158 | Rotor:__._RPM, Gen.:____._ RPM | Rotor: 1.5RPM, Gen.:-172.4 RPM | Breakdown | 0.83125 | 0.83125 | 0.83542 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0043478 |  | 100%
33 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD05 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 5, 540Â° |  | 0.87847 | 0.87847 | 0.89375 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100%
34 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD07 | O2R3 | JK | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.43542 | 0.43542 | 0.67153 | 0 | 5.6667 | 5.6667 | Manual stop for 2 years service Day-2 | Close | 0.24638 |  | 100%
35 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD09 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 5, 540Â° |  | 0.28333 | 0.28333 | 0.29722 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100%
36 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD10 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 6, 603Â° |  | 0.84653 | 0.84653 | 0.86528 | 0 | 0.45 | 0.45 | Auto cable twist | Close | 0.019565 |  | 100%
37 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD11 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 6, 555Â° |  | 0.2125 | 0.2125 | 0.22708 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100%
38 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD12 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 6, 613Â° |  | 0.85069 | 0.85069 | 0.86944 | 0 | 0.45 | 0.45 | Auto cable twist | Close | 0.019565 |  | 100%
39 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD13 | O2R1 | KSIPL | 4.348% | 5069 | Pitch pos C meas. signal fault | Pitch pos C meas. signal fault | Breakdown | 0.52847 | 0.52847 | 0.65208 | 0 | 2.9667 | 2.9667 | Ups reboot done. | Close | 0.12899 |  | 100%
40 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD13 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 6, 550Â° |  | 0.84861 | 0.84861 | 0.86736 | 0 | 0.45 | 0.45 | Auto cable twist | Close | 0.019565 |  | 100%
41 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD14 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 6, 578Â° |  | 0.86389 | 0.86389 | 0.87986 | 0 | 0.38333 | 0.38333 | Auto cable twist | Close | 0.016667 |  | 100%
42 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD17 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 6, 664Â° |  | 0.84236 | 0.84236 | 0.8625 | 0 | 0.48333 | 0.48333 | Auto cable twist | Close | 0.021014 |  | 100%
43 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD19 | O2R1 | KSIPL | 4.348% | 2676 | UPS Error | UPS Error | Breakdown | 0.52292 | 0.52292 | 0.64792 | 0 | 3 | 3 | Ups reboot done. | Close | 0.13043 |  | 100%
44 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD19 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 6, 643Â° |  | 0.84306 | 0.84306 | 0.8625 | 0 | 0.46667 | 0.46667 | Auto cable twist | Close | 0.02029 |  | 100%
45 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD21 | O2R3 | JK | 4.348% | 158 | Rotor:__._RPM, Gen.:____._ RPM | Rotor: 1.7RPM, Gen.:-186.3 RPM | Breakdown | 0.82708 | 0.82708 | 0.83194 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0050725 |  | 100%
46 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | KUD22 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 6, 564Â° |  | 0.19444 | 0.19444 | 0.21042 | 0 | 0.38333 | 0.38333 | Auto cable twist | Close | 0.016667 |  | 100%
47 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | KUD12 | O2R1 | KSIPL | 4.348% | 4560 | BladeCEdgePeakLoad: ___.__ kNm | BladeCEdgePeakLoad: ___.__ kNm | Breakdown | 0.68056 | 0.68056 | 0.70903 | 0 | 0.68333 | 0.68333 | manual reset done. | Close | 0.02971 |  | 100%
48 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | KUD13 | O2R1 | KSIPL | 4.348% | 4500 | Pitch C too low: __._° < __._° | Pitch C too low: __._° < __._° | Breakdown | 0.25 | 0.25 | 0.3125 | 0 | 1.5 | 1.5 | remote reboot done | Close | 0.065217 |  | 100%
49 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | KUD13 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.40972 | 0.40972 | 0.71528 | 0 | 7.3333 | 7.3333 | Manual stop for 2 years service das-01 | Close | 0.31884 |  | 100%
50 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | KUD17 | O2R2 | SIL | 4.348% | 2676 | UPS Error | UPS Error | Breakdown | 0.64583 | 0.64583 | 0.6875 | 0 | 1 | 1 | UPS reboot done | Close | 0.043478 |  | 100%
51 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | KUD21 | O2R3 | JK | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L_: ___V | Breakdown | 0.64583 | 0.64583 | 0.68056 | 0 | 0.83333 | 0.83333 | Manually charge HVCB | Close | 0.036232 |  | 100%
52 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | KUD03 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.32569 | 0.32569 | 0.33958 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100%
53 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | KUD13 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.41389 | 0.41389 | 0.66042 | 0 | 5.9167 | 5.9167 | Manual stop for 2 years service das-02 | Close | 0.25725 |  | 100%
54 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | KUD04 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.31458 | 0.31458 | 0.33542 | 0 | 0.5 | 0.5 | Auto cable twist | Close | 0.021739 |  | 100%
55 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | KUD16 | O2R2 | SIL | 4.348% | 3807 | HubSafetySystem Batt.Level Err | HubSafetySystem Batt.Level Err | ROW | 0.50417 | 0.50417 | 0.59722 | 0 | 2.2333 | 2.2333 | WTG attend late because of ROW issue | Close | 0 |  | 100%
56 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | KUD16 | O2R2 | SIL | 4.348% | 3807 | HubSafetySystem Batt.Level Err | HubSafetySystem Batt.Level Err | Breakdown | 0.59722 | 0.59722 | 0.63264 | 0 | 0.85 | 0.85 | Attend and change hub battery | Close | 0.036957 |  | 100%
57 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | KUD17 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.33264 | 0.33264 | 0.35278 | 0 | 0.48333 | 0.48333 | Auto cable twist | Close | 0.021014 |  | 100%
58 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD01 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.42582 | 0.42582 | 0.43971 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.004
59 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD03 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.3389 | 0.3389 | 0.35374 | 0 | 0.35611 | 0.35611 | Auto cable twist | Close | 0.015483 |  | 100% |  | 0.001
60 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD08 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.72314 | 0.72314 | 0.74066 | 0 | 0.42056 | 0.42056 | Auto cable twist | Close | 0.018285 |  | 100% |  | 0.002
61 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD10 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.28685 | 0.28685 | 0.30238 | 0 | 0.37278 | 0.37278 | Auto cable twist | Close | 0.016208 |  | 100% |  | 0.041
62 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD11 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.2923 | 0.2923 | 0.30922 | 0 | 0.40611 | 0.40611 | Auto cable twist | Close | 0.017657 |  | 100% |  | 0.035
63 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD12 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.32485 | 0.32485 | 0.33878 | 0 | 0.33444 | 0.33444 | Auto cable twist | Close | 0.014541 |  | 100% |  | 0.019
64 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD13 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.34407 | 0.34407 | 0.35922 | 0 | 0.36361 | 0.36361 | Auto cable twist | Close | 0.015809 |  | 100% |  | 0.001
65 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD14 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.3463 | 0.3463 | 0.36146 | 0 | 0.36389 | 0.36389 | Auto cable twist | Close | 0.015821 |  | 100% |  | 0.001
66 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD19 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.7105 | 0.7105 | 0.72752 | 0 | 0.40861 | 0.40861 | Auto cable twist | Close | 0.017766 |  | 100% |  | 0.001
67 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD20 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.32745 | 0.32745 | 0.34544 | 0 | 0.43167 | 0.43167 | Auto cable twist | Close | 0.018768 |  | 100% |  | 0.001
68 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD02 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.32855 | 0.32855 | 0.34243 | 0 | 0.33306 | 0.33306 | Auto cable twist | Close | 0.014481 |  | 100% |  | 0.001
69 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD02 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.74156 | 0.74156 | 0.76333 | 0 | 0.5225 | 0.5225 | Auto cable twist | Close | 0.022717 |  | 100% |  | 0.432
70 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD04 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.66012 | 0.66012 | 0.67855 | 0 | 0.4425 | 0.4425 | Auto cable twist | Close | 0.019239 |  | 100% |  | 0.187
71 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD05 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.43784 | 0.43784 | 0.45183 | 0 | 0.33583 | 0.33583 | Auto cable twist | Close | 0.014601 |  | 100% |  | 0.061
72 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD06 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.28528 | 0.28528 | 0.30267 | 0 | 0.4175 | 0.4175 | Auto cable twist | Close | 0.018152 |  | 100% |  | 0.002
73 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD07 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.71912 | 0.71912 | 0.73738 | 0 | 0.43833 | 0.43833 | Auto cable twist | Close | 0.019058 |  | 100% |  | 0.042
74 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD09 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.32432 | 0.32432 | 0.33813 | 0 | 0.33139 | 0.33139 | Auto cable twist | Close | 0.014408 |  | 100% |  | 0.001
75 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD09 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.71404 | 0.71404 | 0.73072 | 0 | 0.40028 | 0.40028 | Auto cable twist | Close | 0.017403 |  | 100% |  | 0.003
76 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD16 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.7373 | 0.7373 | 0.75793 | 0 | 0.495 | 0.495 | Auto cable twist | Close | 0.021522 |  | 100% |  | 0.406
77 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD18 | O2R4 | SGDCIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.33313 | 0.33313 | 0.34722 | 0 | 0.33833 | 0.33833 | Auto cable twist | Close | 0.01471 |  | 100% |  | 0.005
78 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD21 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.32337 | 0.32337 | 0.3374 | 0 | 0.33667 | 0.33667 | Auto cable twist | Close | 0.014638 |  | 100% |  | 0.001
79 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD21 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.74454 | 0.74454 | 0.76515 | 0 | 0.49472 | 0.49472 | Auto cable twist | Close | 0.02151 |  | 100% |  | 0.425
80 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD22 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.30333 | 0.30333 | 0.32135 | 0 | 0.4325 | 0.4325 | Auto cable twist | Close | 0.018804 |  | 100% |  | 0.002
81 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | KUD23 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.29869 | 0.29869 | 0.31634 | 0 | 0.42361 | 0.42361 | Auto cable twist | Close | 0.018418 |  | 100% |  | 0.002
82 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | KUD03 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.60278 | 0.60278 | 0.61736 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.002
83 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | KUD08 | O2R3 | JK | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.41597 | 0.41597 | 0.77361 | 0 | 8.5833 | 8.5833 | Manual stop for 2 years service das-01 | Close | 0.37319 |  | 100% |  | 0.852
84 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | KUD10 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.49306 | 0.49306 | 0.50694 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.001
85 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | KUD12 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.71458 | 0.71458 | 0.73056 | 0 | 0.38333 | 0.38333 | Auto cable twist | Close | 0.016667 |  | 100% |  | 0.153
86 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | KUD13 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.57639 | 0.57639 | 0.59167 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.001
87 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | KUD15 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.10972 | 0.10972 | 0.12639 | 0 | 0.4 | 0.4 | Auto cable twist | Close | 0.017391 |  | 100% |  | 0.035
88 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | KUD20 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.29583 | 0.29583 | 0.31111 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.002
89 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | KUD04 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.66042 | 0.66042 | 0.675 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.144
90 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | KUD05 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.17153 | 0.17153 | 0.18542 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.001
91 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | KUD06 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.20903 | 0.20903 | 0.22292 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0
92 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | KUD07 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.52222 | 0.52222 | 0.53681 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.001
93 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | KUD17 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.11111 | 0.11111 | 0.12847 | 0 | 0.41667 | 0.41667 | Auto cable twist | Close | 0.018116 |  | 100% |  | 0
94 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | KUD22 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.16806 | 0.16806 | 0.18264 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.006
95 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | KUD23 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.20417 | 0.20417 | 0.21875 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.005
96 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | KUD08 | O2R3 | JK | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.43333 | 0.43333 | 0.72847 | 0 | 7.0833 | 7.0833 | Manual stop for 2 years service das-02 | Close | 0.30797 |  | 100% |  | 0.052
97 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | KUD03 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.15417 | 0.15417 | 0.17292 | 0 | 0.45 | 0.45 | Auto cable twist | Close | 0.019565 |  | 100% |  | 0.022
98 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | KUD11 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.55417 | 0.55417 | 0.56806 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.013
99 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | KUD14 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.63403 | 0.63403 | 0.65208 | 0 | 0.43333 | 0.43333 | Auto cable twist | Close | 0.018841 |  | 100% |  | 0.009
100 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | KUD05 | O2R3 | JK | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.42153 | 0.42153 | 0.72847 | 0 | 7.3667 | 7.3667 | Manual stop for 2 years service day-01 | Close | 0.32029 |  | 100% |  | 0.069
101 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | KUD07 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.14444 | 0.14444 | 0.15903 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.001
102 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | KUD07 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.52639 | 0.52639 | 0.54167 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0
103 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | KUD07 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.65069 | 0.65069 | 0.66667 | 0 | 0.38333 | 0.38333 | Auto cable twist | Close | 0.016667 |  | 100% |  | 0.021
104 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | KUD16 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.50417 | 0.50417 | 0.52153 | 0 | 0.41667 | 0.41667 | Auto cable twist | Close | 0.018116 |  | 100% |  | 0.011
105 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | KUD21 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.13819 | 0.13819 | 0.15347 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.015
106 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | KUD02 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C1 Load:100% | Breakdown | 0.95347 | 0.95347 | 0.975 | 0 | 0.51667 | 0.51667 | Remote reset done | Close | 0.022464 |  | 100%
107 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | KUD05 | O2R3 | JK | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.44375 | 0.44375 | 0.59375 | 0 | 3.6 | 3.6 | Manual stop for 2 years service day-02 | Close | 0.15652 |  | 100%
108 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | KUD07 | O2R3 | JK | 4.348% | 2676 | UPS Error | UPS Error | Breakdown | 0.86944 | 0.86944 | 0.87014 | 0 | 0.016667 | 0.016667 | UPS reboot done | Close | 0.00072464 |  | 100%
109 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | KUD10 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.81944 | 0.81944 | 0.82986 | 0 | 0.25 | 0.25 | Auto reset | Close | 0.01087 |  | 100%
110 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | KUD11 | O2R1 | KSIPL | 4.348% | 3298 | Yaw To Cable Twist Reset | Yaw To Cable Twist Reset | Breakdown | 0.85972 | 0.85972 | 0.87569 | 0 | 0.38333 | 0.38333 | Remote reset done | Close | 0.016667 |  | 100%
111 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | KUD12 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C1 Load:100% | Breakdown | 0.88264 | 0.88264 | 0.88889 | 0 | 0.15 | 0.15 | Remote reset done | Close | 0.0065217 |  | 100%
112 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | KUD17 | O2R2 | SIL | 4.348% | 2676 | UPS Error | UPS Error | Breakdown | 0.87569 | 0.87569 | 0.87847 | 0 | 0.066667 | 0.066667 | UPS reboot done | Close | 0.0028986 |  | 100%
113 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | KUD21 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C2 Load:100% | Breakdown | 0.94306 | 0.94306 | 0.97222 | 0 | 0.7 | 0.7 | Remote reset done | Close | 0.030435 |  | 100%
114 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | KUD22 | O2R3 | JK | 4.348% | 931 | Arc light detected | Arc light detected | Breakdown | 0.8 | 0.8 | 0.99931 | 0 | 4.7833 | 4.7833 | After feeder charged Vamp activated inspection work in progress.. | Open | 0.20797 |  | 100%
115 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | KUD22 | O2R3 | JK | 4.348% | 2676 | UPS Error | UPS Error | Breakdown | 0.83681 | 0.83681 | 0.84792 | 0 | 0.26667 | 0.26667 | UPS reboot done | Close | 0.011594 |  | 100%
116 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | KUD01 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.060417 | 0.060417 | 0.08125 | 0 | 0.5 | 0.5 | Auto cable twist | Close | 0.021739 |  | 100% |  | 0.017
117 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | KUD08 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.085417 | 0.085417 | 0.099306 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.02
118 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | KUD04 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.077083 | 0.077083 | 0.090972 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.017
119 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | KUD16 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.070139 | 0.070139 | 0.084028 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.001
120 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | KUD17 | O2R2 | SIL | 4.348% | 3483 | GearOilTempLow ___°C | GearOilTempLow ___°C | Breakdown | 0.73194 | 0.73194 | 0.82917 | 0 | 2.3333 | 2.3333 | Attend check related CT and Temp sensor found CT Malfuction so once reboot nacelle supply and restored. | Close | 0.10145 |  | 100% |  | 2.174
121 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | KUD18 | O2R4 | SGDCIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.070833 | 0.070833 | 0.086111 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.011
122 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | KUD21 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.0625 | 0.0625 | 0.075 | 0 | 0.3 | 0.3 | Auto cable twist | Close | 0.013043 |  | 100% |  | 0.037
123 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | KUD22 | O2R3 | JK | 4.348% | 931 | Arc light detected | Arc light detected | Breakdown | 0 | 0 | 0.14583 | 0 | 3.5 | 3.5 | After grid drop Trfo room arc sensor activated so attend found Y phase to B phase connecting Delta bus bar failed so replaced and Trafo inspection and magering so found all normal and then charged Trafo. | Close | 0.15217 |  | 100% |  | 0.905
124 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | KUD22 | O2R3 | JK | 4.348% | 5067 | Pitch pos A meas. signal fault | Pitch pos A meas. signal fault | Breakdown | 0.14583 | 0.14583 | 0.29653 | 0 | 3.6167 | 3.6167 | Attend found A blade all cable rubbing to hub frame so cable routing done and and restored | Close | 0.15725 |  | 100% |  | 2.273
125 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | KUD03 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.47639 | 0.47639 | 0.49653 | 0 | 0.48333 | 0.48333 | Auto cable twist | Close | 0.021014 |  | 100% |  | 0.131
126 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | KUD13 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.70972 | 0.70972 | 0.72917 | 0 | 0.46667 | 0.46667 | Auto cable twist | Close | 0.02029 |  | 100% |  | 0.59
127 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | KUD14 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.66806 | 0.66806 | 0.68889 | 0 | 0.5 | 0.5 | Auto cable twist | Close | 0.021739 |  | 100% |  | 0.081
128 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | KUD15 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.45069 | 0.45069 | 0.76806 | 0 | 7.6167 | 7.6167 | Manual stop for 2 years service day-01 | Close | 0.33116 |  | 100% |  | 3.756
129 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | KUD07 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.71389 | 0.71389 | 0.72847 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.137
130 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | KUD18 | O2R4 | SGDCIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.49375 | 0.49375 | 0.51458 | 0 | 0.5 | 0.5 | Auto cable twist | Close | 0.021739 |  | 100% |  | 0.137
131 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | KUD22 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.67917 | 0.67917 | 0.69444 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.132
132 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | KUD23 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.67917 | 0.67917 | 0.69444 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.083
133 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD01 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.66181 | 0.66181 | 0.67708 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.015
134 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD08 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.84167 | 0.84167 | 0.85764 | 0 | 0.38333 | 0.38333 | Auto cable twist | Close | 0.016667 |  | 100% |  | 0
135 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD10 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.84236 | 0.84236 | 0.85625 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0
136 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD11 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.0069444 | 0.0069444 | 0.027778 | 0 | 0.5 | 0.5 | Auto cable twist | Close | 0.021739 |  | 100% |  | 0.118
137 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD12 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.18681 | 0.18681 | 0.20903 | 0 | 0.53333 | 0.53333 | Auto cable twist | Close | 0.023188 |  | 100% |  | 0.234
138 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD15 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.66806 | 0.66806 | 0.68194 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.02
139 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD19 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.18125 | 0.18125 | 0.20556 | 0 | 0.58333 | 0.58333 | Auto cable twist | Close | 0.025362 |  | 100% |  | 0.226
140 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD20 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.18542 | 0.18542 | 0.20764 | 0 | 0.53333 | 0.53333 | Auto cable twist | Close | 0.023188 |  | 100% |  | 0.266
141 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD02 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.17917 | 0.17917 | 0.20417 | 0 | 0.6 | 0.6 | Auto cable twist | Close | 0.026087 |  | 100% |  | 0.169
142 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD04 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.32153 | 0.32153 | 0.34306 | 0 | 0.51667 | 0.51667 | Auto cable twist | Close | 0.022464 |  | 100% |  | -0.001
143 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD05 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.18125 | 0.18125 | 0.19653 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.074
144 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD06 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.5125 | 0.5125 | 0.52639 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.024
145 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD07 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.67153 | 0.67153 | 0.68542 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.017
146 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD09 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.84931 | 0.84931 | 0.86319 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.002
147 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD16 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.17778 | 0.17778 | 0.20278 | 0 | 0.6 | 0.6 | Auto cable twist | Close | 0.026087 |  | 100% |  | 0.21
148 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD17 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.17986 | 0.17986 | 0.20417 | 0 | 0.58333 | 0.58333 | Auto cable twist | Close | 0.025362 |  | 100% |  | 0.157
149 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD18 | O2R4 | SGDCIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.81667 | 0.81667 | 0.83056 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.002
150 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD21 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.17847 | 0.17847 | 0.20347 | 0 | 0.6 | 0.6 | Auto cable twist | Close | 0.026087 |  | 100% |  | 0.205
151 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | KUD22 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.52917 | 0.52917 | 0.55 | 0 | 0.5 | 0.5 | Auto cable twist | Close | 0.021739 |  | 100% |  | 0.068
152 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD01 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.52639 | 0.52639 | 0.54028 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.001
153 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD03 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.34653 | 0.34653 | 0.36389 | 0 | 0.41667 | 0.41667 | Auto cable twist | Close | 0.018116 |  | 100% |  | 0
154 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD10 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.64306 | 0.64306 | 0.65556 | 0 | 0.3 | 0.3 | Auto cable twist | Close | 0.013043 |  | 100% |  | 0.032
155 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD11 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.61806 | 0.61806 | 0.6375 | 0 | 0.46667 | 0.46667 | Auto cable twist | Close | 0.02029 |  | 100% |  | 0.006
156 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD12 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 |  | 0.43056 | 0.43056 | 0.63889 | 0 | 5 | 5 | Manual stop for CMS alert inspection work. | Close | 0.21739 |  | 100% |  | 0.372
157 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD12 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.63889 | 0.63889 | 0.64931 | 0 | 0.25 | 0.25 | Auto cable twist | Close | 0.01087 |  | 100% |  | 0.036
158 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD13 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.31736 | 0.31736 | 0.33819 | 0 | 0.5 | 0.5 | Auto cable twist | Close | 0.021739 |  | 100% |  | -0.001
159 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD14 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.31597 | 0.31597 | 0.33681 | 0 | 0.5 | 0.5 | Auto cable twist | Close | 0.021739 |  | 100% |  | 0
160 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD15 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.64097 | 0.64097 | 0.65486 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.045
161 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD19 | O2R1 | KSIPL | 4.348% | 2676 | UPS Error | UPS Error |  | 0.42361 | 0.42361 | 0.45833 | 0 | 0.83333 | 0.83333 | UPS reboot done | Close | 0.036232 |  | 100% |  | -0.002
162 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD19 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.65903 | 0.65903 | 0.67361 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.029
163 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD20 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.63125 | 0.63125 | 0.64514 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.006
164 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD20 | O2R1 | KSIPL | 4.348% | 5470 | GeneratorBreakerFBResponse | GeneratorBreakerFBResponse |  | 0.76389 | 0.76389 | 0.85556 | 0 | 2.2 | 2.2 | After grid restored generator CB not closed so checked found coil malfunctioned so once reboot and restored | Close | 0.095652 |  | 100% |  | 0.186
165 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD02 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.71111 | 0.71111 | 0.725 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.04
166 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD04 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.62986 | 0.62986 | 0.64514 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.008
167 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD05 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.36042 | 0.36042 | 0.37431 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0
168 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD06 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.42292 | 0.42292 | 0.43819 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.001
169 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD07 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.48125 | 0.48125 | 0.49653 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.005
170 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD09 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.56597 | 0.56597 | 0.57986 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.02
171 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD16 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.65 | 0.65 | 0.66458 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.042
172 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD17 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.6625 | 0.6625 | 0.67847 | 0 | 0.38333 | 0.38333 | Auto cable twist | Close | 0.016667 |  | 100% |  | 0.036
173 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD17 | O2R2 | SIL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 |  | 0.68125 | 0.68125 | 0.81667 | 0 | 3.25 | 3.25 | Manual stop for CMS alert inspection work. | Close | 0.1413 |  | 100% |  | 0.698
174 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD18 | O2R4 | SGDCIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.8375 | 0.8375 | 0.85486 | 0 | 0.41667 | 0.41667 | Auto cable twist | Close | 0.018116 |  | 100% |  | 0.156
175 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD21 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.62986 | 0.62986 | 0.64444 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.006
176 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD21 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.91042 | 0.91042 | 0.92639 | 0 | 0.38333 | 0.38333 | Auto cable twist | Close | 0.016667 |  | 100% |  | 0.032
177 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD22 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.50278 | 0.50278 | 0.51667 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.005
178 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD22 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.91944 | 0.91944 | 0.93819 | 0 | 0.45 | 0.45 | Auto cable twist | Close | 0.019565 |  | 100% |  | 0.741
179 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD23 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.37083 | 0.37083 | 0.38472 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.001
180 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD23 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.91875 | 0.91875 | 0.93819 | 0 | 0.46667 | 0.46667 | Auto cable twist | Close | 0.02029 |  | 100% |  | 0.176
181 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD14 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.72222 | 0.72222 | 0.73542 | 0 | 0.31667 | 0.31667 | Auto cable twist | Close | 0.013768 |  | 100% |  | 0.075
182 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD15 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 |  | 0.72222 | 0.72222 | 0.79097 | 0 | 1.65 | 1.65 | Manual stop for 2 years service day-02 | Close | 0.071739 |  | 100% |  | 0.045
183 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD15 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 |  | 0.60764 | 0.60764 | 0.68194 | 0 | 1.7833 | 1.7833 | Manual stop for 2 years service day-02 | Close | 0.077536 |  | 100% |  | 0.162
184 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD19 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 |  | 0.43056 | 0.43056 | 0.74306 | 0 | 7.5 | 7.5 | Manual stop for CMS alert inspection work. | Close | 0.32609 |  | 100% |  | 0.276
185 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD02 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.70347 | 0.70347 | 0.72014 | 0 | 0.4 | 0.4 | Auto cable twist | Close | 0.017391 |  | 100% |  | 0.002
186 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD04 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.71806 | 0.71806 | 0.7375 | 0 | 0.46667 | 0.46667 | Auto cable twist | Close | 0.02029 |  | 100% |  | 0.026
187 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD05 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.52569 | 0.52569 | 0.53958 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.013
188 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD05 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.79514 | 0.79514 | 0.81042 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.059
189 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD06 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.69653 | 0.69653 | 0.71528 | 0 | 0.45 | 0.45 | Auto cable twist | Close | 0.019565 |  | 100% |  | 0.037
190 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD09 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.71389 | 0.71389 | 0.73403 | 0 | 0.48333 | 0.48333 | Auto cable twist | Close | 0.021014 |  | 100% |  | 0.013
191 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD16 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.67569 | 0.67569 | 0.69028 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.073
192 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD17 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.70417 | 0.70417 | 0.71944 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.008
193 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD18 | O2R4 | SGDCIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.70694 | 0.70694 | 0.72431 | 0 | 0.41667 | 0.41667 | Auto cable twist | Close | 0.018116 |  | 100% |  | 0.006
194 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD22 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.74375 | 0.74375 | 0.75903 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.012
195 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD23 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.72986 | 0.72986 | 0.74444 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.046
196 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | KUD11 | O2R1 | KSIPL | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L_: ___V | Breakdown | 0.29861 | 0.29861 | 0.33333 | 0 | 0.83333 | 0.83333 | UPS Reboot done | Close | 0.036232 |  | 100% |  | 0.06
197 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | KUD11 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.42361 | 0.42361 | 0.75556 | 0 | 7.9667 | 7.9667 | Manual stop for 2 years service day-01 | Close | 0.34638 |  | 100% |  | 2.458
198 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | KUD12 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.12917 | 0.12917 | 0.15208 | 0 | 0.55 | 0.55 | Remote reset done | Close | 0.023913 |  | 100% |  | 0.254
199 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | KUD09 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.14028 | 0.14028 | 0.15208 | 0 | 0.28333 | 0.28333 | Remote reset done | Close | 0.012319 |  | 100% |  | 0.119
200 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | KUD17 | O2R2 | SIL | 4.348% | 2676 | UPS Error | UPS Error | Breakdown | 0.96528 | 0.96528 | 0.98611 | 0 | 0.5 | 0.5 | UPS Reboot done | Close | 0.021739 |  | 100% |  | 0.226
201 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | KUD01 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.47917 | 0.47917 | 0.74097 | 0 | 6.2833 | 6.2833 | Manual stop for 2 years service day-01 | Close | 0.27319 |  | 100% |  | 0.905
202 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | KUD01 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.77083 | 0.77083 | 0.81319 | 0 | 1.0167 | 1.0167 | Manual stop for 2 years service day-01 | Close | 0.044203 |  | 100% |  | 0.447
203 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.19097 | 0.19097 | 0.23542 | 0 | 1.0667 | 1.0667 | Remote reset done | Close | 0.046377 |  | 100% |  | 0.211
204 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | KUD05 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.21458 | 0.21458 | 0.25625 | 0 | 1 | 1 | Remote reset done | Close | 0.043478 |  | 100% |  | 0.312
205 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | KUD06 | O2R3 | JK | 4.348% | 3298 | Yaw To Cable Twist Reset | Yaw To Cable Twist Reset |  | 0.80278 | 0.80278 | 0.80625 | 0 | 0.083333 | 0.083333 | Remote reset done | Close | 0.0036232 |  | 100% |  | 0.044
206 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | KUD21 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.19097 | 0.19097 | 0.23542 | 0 | 1.0667 | 1.0667 | Remote reset done | Close | 0.046377 |  | 100% |  | 0.301
207 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | KUD23 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.22569 | 0.22569 | 0.25972 | 0 | 0.81667 | 0.81667 | Remote reset done | Close | 0.035507 |  | 100% |  | 0.213
208 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | KUD01 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.56181 | 0.56181 | 0.56458 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0028986 |  | 100%
209 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C2 Load:100% | Breakdown | 0.030556 | 0.072222 | 0.089583 | 1 | 0.41667 | 1.4167 | Remote reset done | Close | 0.061594 |  | 100%
210 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | KUD11 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.80972 | 0.80972 | 0.81319 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0036232 |  | 100%
211 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-19 | KUD11 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.44444 | 0.44444 | 0.67153 | 0 | 5.45 | 5.45 | Manual stop for 2 years service day-02 | Close | 0.23696 |  | 100% |  | 0.5
212 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-19 | KUD11 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.70833 | 0.70833 | 0.72917 | 0 | 0.5 | 0.5 | Manual stop for 2 years service day-02 | Close | 0.021739 |  | 100% |  | 0.05
213 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | KUD01 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.42292 | 0.42292 | 0.81875 | 0 | 9.5 | 9.5 | Manual stop for Oil leakage inspection found Accumulator O ring got failure so replaced and restored | Close | 0.41304 |  | 100% |  | 3.628
214 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | KUD08 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.73472 | 0.73472 | 0.75208 | 0 | 0.41667 | 0.41667 | Auto reset | Close | 0.018116 |  | 100% |  | 0.032
215 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | KUD12 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.87361 | 0.87361 | 0.89028 | 0 | 0.4 | 0.4 | Auto reset | Close | 0.017391 |  | 100% |  | 0.232
216 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | KUD15 | O2R1 | KSIPL | 4.348% | 356 | Extreme yawerror __._m/s___._° | Extreme yawerror __._m/s___._° |  | 0.86736 | 0.86736 | 0.86875 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0014493 |  | 100% |  | -0.029
217 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | KUD02 | O2R3 | JK | 4.348% | 356 | Extreme yawerror __._m/s___._° | Extreme yawerror __._m/s___._° |  | 0.86736 | 0.86736 | 0.86875 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0014493 |  | 100% |  | -0.019
218 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | KUD07 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.74028 | 0.74028 | 0.75903 | 0 | 0.45 | 0.45 | Auto reset | Close | 0.019565 |  | 100% |  | 0.018
219 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | KUD17 | O2R2 | SIL | 4.348% | 931 | Arc light detected | Arc light detected | Breakdown | 0.44444 | 0.44444 | 0.5625 | 0 | 2.8333 | 2.8333 | After grid drop Trafo room VAMP activated so trafo inspection done found all ok then charged and restored | Close | 0.12319 |  | 100% |  | 0
220 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | KUD17 | O2R2 | SIL | 4.348% | 931 | Arc light detected | Arc light detected | Breakdown | 0.69444 | 0.69444 | 0.72917 | 0 | 0.83333 | 0.83333 | After grid drop Trafo room VAMP activated so trafo inspection done found all ok then charged and restored | Close | 0.036232 |  | 100% |  | 0
221 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | KUD18 | O2R4 | SGDCIPL | 4.348% | 151 | High temp. Gen bearing _:___°C | High temp. Gen bearing _:___°C | Breakdown | 0.80069 | 0.80069 | 0.85 | 0 | 1.1833 | 1.1833 | Attend found generator high speed fan fuse 2 nos got failure so replaced and restored | Close | 0.051449 |  | 100% |  | 0.655
222 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | KUD21 | O2R3 | JK | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L_: ___V | Breakdown | 0.44444 | 0.44444 | 0.46528 | 0 | 0.5 | 0.5 | Manual charged HVCB | Close | 0.021739 |  | 100% |  | 0.065
223 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | KUD21 | O2R3 | JK | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L_: ___V | Breakdown | 0.61111 | 0.61111 | 0.65972 | 0 | 1.1667 | 1.1667 | UPS battery changed and charged HVCB | Close | 0.050725 |  | 100% |  | 0.166
224 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | KUD07 | O2R3 | JK | 4.348% | 2676 | UPS Error | UPS Error | Breakdown | 0.65903 | 0.65903 | 0.69583 | 0 | 0.88333 | 0.88333 | UPS Reboot done | Close | 0.038406 |  | 100%
225 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | KUD08 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code 3,-000540Â° |  | 0.41042 | 0.41042 | 0.42778 | 0 | 0.41667 | 0.41667 | Auto cable twist | Close | 0.018116 |  | 100%
226 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | KUD10 | O2R1 | KSIPL | 4.348% | 3298 | Yaw To Cable Twist Reset | Yaw To Cable Twist Reset | Breakdown | 0.090972 | 0.090972 | 0.11111 | 0 | 0.48333 | 0.48333 | Remote reset done | Close | 0.021014 |  | 100%
227 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | KUD12 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 5, 540Â° |  | 0.60139 | 0.60139 | 0.61944 | 0 | 0.43333 | 0.43333 | Auto cable twist | Close | 0.018841 |  | 100%
228 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | KUD13 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 6, 540Â° |  | 0.525 | 0.525 | 0.54375 | 0 | 0.45 | 0.45 | Auto cable twist | Close | 0.019565 |  | 100%
229 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | KUD15 | O2R1 | KSIPL | 4.348% | 3298 | Yaw To Cable Twist Reset | Yaw To Cable Twist Reset | Breakdown | 0.091667 | 0.091667 | 0.1125 | 0 | 0.5 | 0.5 | Remote reset done | Close | 0.021739 |  | 100%
230 | 2026 | 2025 | Year_4 | 2025-04-01 | 2025-04-21 | KUD07 | O2R3 | JK | 4.348% | 2676 | UPS Error | UPS Error | Breakdown | 0.048611 | 0.048611 | 0.24653 | 0 | 4.75 | 4.75 | UPS battery changed and charged HVCB | Close | 0.20652 |  | 100%
231 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD01 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.46528 | 0.46528 | 0.62639 | 0 | 3.8667 | 3.8667 | Manual stop for 2 years service day-02 | Close | 0.16812 |  | 100% |  | 0.243
232 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD01 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.66667 | 0.66667 | 0.71389 | 0 | 1.1333 | 1.1333 | Manual stop for 2 years service day-02 | Close | 0.049275 |  | 100% |  | 0
233 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD01 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.75 | 0.75 | 0.78472 | 0 | 0.83333 | 0.83333 | Manual stop for 2 years service day-02 | Close | 0.036232 |  | 100% |  | -0.002
234 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD10 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.65972 | 0.65972 | 0.67639 | 0 | 0.4 | 0.4 | Auto start after battery fully charged. | Close | 0.017391 |  | 100% |  | 0.112
235 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD10 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.75 | 0.75 | 0.75764 | 0 | 0.18333 | 0.18333 | Auto start after battery fully charged. | Close | 0.007971 |  | 100% |  | 0.035
236 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD11 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.0097222 | 0.0097222 | 0.045833 | 0 | 0.86667 | 0.86667 | Remote reset done | Close | 0.037681 |  | 100% |  | 0.321
237 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD12 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.0069444 | 0.0069444 | 0.045139 | 0 | 0.91667 | 0.91667 | Remote reset done | Close | 0.039855 |  | 100% |  | 0.29
238 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD13 | O2R1 | KSIPL | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L_: ___V | Breakdown | 0.46528 | 0.46528 | 0.50208 | 0 | 0.88333 | 0.88333 | HVCB Manual charged done. | Close | 0.038406 |  | 100% |  | 0.131
239 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD20 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.46528 | 0.46528 | 0.47222 | 0 | 0.16667 | 0.16667 | Auto start after battery fully charged. | Close | 0.0072464 |  | 100% |  | 0.02
240 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD20 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.66667 | 0.66667 | 0.68125 | 0 | 0.35 | 0.35 | Auto start after battery fully charged. | Close | 0.015217 |  | 100% |  | 0.191
241 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD02 | O2R3 | JK | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L_: ___V | Breakdown | 0.79167 | 0.79167 | 0.99931 | 0 | 4.9833 | 4.9833 | Rectification in progress. | Close | 0.21667 |  | 100% |  | 0
242 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.045139 | 0.045139 | 0.061111 | 0 | 0.38333 | 0.38333 | Remote reset done | Close | 0.016667 |  | 100% |  | 0.157
243 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.18403 | 0.18403 | 0.22153 | 0 | 0.9 | 0.9 | Remote reset done | Close | 0.03913 |  | 100% |  | 0.157
244 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.70417 | 0.70417 | 0.72083 | 0 | 0.4 | 0.4 | Remote reset done | Close | 0.017391 |  | 100% |  | 0.087
245 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD20 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.99722 | 0.99722 | 0.99931 | 0 | 0.05 | 0.05 | Remote reset done | Close | 0.0021739 |  | 100% |  | 0.023
246 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD17 | O2R2 | SIL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.0076389 | 0.0076389 | 0.045139 | 0 | 0.9 | 0.9 | Remote reset done | Close | 0.03913 |  | 100% |  | 0.179
247 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD17 | O2R2 | SIL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.67222 | 0.67222 | 0.67361 | 0 | 0.033333 | 0.033333 | Auto start after battery fully charged. | Close | 0.0014493 |  | 100% |  | 0.02
248 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD18 | O2R4 | SGDCIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.625 | 0.625 | 0.63194 | 0 | 0.16667 | 0.16667 | Auto cable twist | Close | 0.0072464 |  | 100% |  | 0
249 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD21 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.23056 | 0.23056 | 0.27639 | 0 | 1.1 | 1.1 | Remote reset done | Close | 0.047826 |  | 100% |  | 0.221
250 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD21 | O2R3 | JK | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.67083 | 0.67083 | 0.67361 | 0 | 0.066667 | 0.066667 | Auto start after battery fully charged. | Close | 0.0028986 |  | 100% |  | 0.112
251 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD22 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.30764 | 0.30764 | 0.32222 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.046
252 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD22 | O2R3 | JK | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.67014 | 0.67014 | 0.67361 | 0 | 0.083333 | 0.083333 | Auto start after battery fully charged. | Close | 0.0036232 |  | 100% |  | 0.058
253 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD10 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.72431 | 0.72431 | 0.73611 | 0 | 0.28333 | 0.28333 | Auto start after battery fully charged. | Close | 0.012319 |  | 100% |  | 0.001
254 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD11 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.73542 | 0.73542 | 0.73611 | 0 | 0.016667 | 0.016667 | Auto start after battery fully charged. | Close | 0.00072464 |  | 100% |  | 0
255 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD12 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.063194 | 0.063194 | 0.069444 | 0 | 0.15 | 0.15 | Remote reset done | Close | 0.0065217 |  | 100% |  | 0.061
256 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD12 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.076389 | 0.076389 | 0.093056 | 0 | 0.4 | 0.4 | Remote reset done | Close | 0.017391 |  | 100% |  | 0.028
257 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD20 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.070833 | 0.070833 | 0.094444 | 0 | 0.56667 | 0.56667 | Remote reset done | Close | 0.024638 |  | 100% |  | 0.104
258 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD20 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.44444 | 0.44444 | 0.45347 | 0 | 0.21667 | 0.21667 | Auto start after battery fully charged. | Close | 0.0094203 |  | 100% |  | 0.013
259 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD20 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.72917 | 0.72917 | 0.73611 | 0 | 0.16667 | 0.16667 | Auto start after battery fully charged. | Close | 0.0072464 |  | 100% |  | -0.001
260 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD02 | O2R3 | JK | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L_: ___V | Breakdown | 0 | 0 | 0.029861 | 0 | 0.71667 | 0.71667 |  | Close | 0.031159 |  | 100% |  | 0.371
261 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.015278 | 0.015278 | 0.034028 | 0 | 0.45 | 0.45 | Remote reset done | Close | 0.019565 |  | 100% |  | 0.193
262 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.058333 | 0.058333 | 0.06875 | 0 | 0.25 | 0.25 | Remote reset done | Close | 0.01087 |  | 100% |  | 0.056
263 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.076389 | 0.076389 | 0.09375 | 0 | 0.41667 | 0.41667 | Remote reset done | Close | 0.018116 |  | 100% |  | 0.066
264 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.11389 | 0.11389 | 0.11806 | 0 | 0.1 | 0.1 | Remote reset done | Close | 0.0043478 |  | 100% |  | 0.025
265 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.12986 | 0.12986 | 0.16806 | 0 | 0.91667 | 0.91667 | Remote reset done | Close | 0.039855 |  | 100% |  | 0.23
266 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD17 | O2R2 | SIL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.14306 | 0.14306 | 0.17292 | 0 | 0.71667 | 0.71667 | Remote reset done | Close | 0.031159 |  | 100% |  | 0.303
267 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD21 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.14375 | 0.14375 | 0.17292 | 0 | 0.7 | 0.7 | Remote reset done | Close | 0.030435 |  | 100% |  | 0.182
268 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD21 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.2 | 0.2 | 0.21181 | 0 | 0.28333 | 0.28333 | Remote reset done | Close | 0.012319 |  | 100% |  | 0.07
269 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD22 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.14861 | 0.14861 | 0.17292 | 0 | 0.58333 | 0.58333 | Remote reset done | Close | 0.025362 |  | 100% |  | 0.222
270 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD12 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.44444 | 0.44444 | 0.69722 | 0 | 6.0667 | 6.0667 | Manual stop for 2 years service day-02 | Close | 0.26377 |  | 100% |  | 0.173
271 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD12 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.72917 | 0.72917 | 0.74444 | 0 | 0.36667 | 0.36667 | Manual stop for 2 years service day-02 | Close | 0.015942 |  | 100% |  | 0.302
272 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | KUD10 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.69028 | 0.69028 | 0.70069 | 0 | 0.25 | 0.25 | Auto start after battery fully charged. | Close | 0.01087 |  | 100% |  | 0.024
273 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | KUD12 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.45833 | 0.45833 | 0.65833 | 0 | 4.8 | 4.8 | Manual stop for 2 years service day-01 | Close | 0.2087 |  | 100% |  | 0.074
274 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | KUD12 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.7 | 0.7 | 0.73403 | 0 | 0.81667 | 0.81667 | Manual stop for 2 years service day-01 | Close | 0.035507 |  | 100% |  | 0.217
275 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | KUD15 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.70139 | 0.70139 | 0.71875 | 0 | 0.41667 | 0.41667 | Auto cable twist | Close | 0.018116 |  | 100% |  | 0.05
276 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | KUD19 | O2R1 | KSIPL | 4.348% | 165 | Low oil-level, hydraulic | Low oil-level, hydraulic | Breakdown | 0.82778 | 0.82778 | 0.99931 | 0 | 4.1167 | 4.1167 | WTG Rectification work in progress | Open | 0.17899 |  | 100% |  | -0.002
277 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | KUD20 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.46458 | 0.46458 | 0.46528 | 0 | 0.016667 | 0.016667 | Auto start after battery fully charged. | Close | 0.00072464 |  | 100% |  | 0.015
278 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | KUD20 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.69444 | 0.69444 | 0.71528 | 0 | 0.5 | 0.5 | Auto start after battery fully charged. | Close | 0.021739 |  | 100% |  | 0.04
279 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | KUD07 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.65417 | 0.65417 | 0.66875 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.001
280 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | KUD01 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.29861 | 0.29861 | 0.30139 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0028986 |  | 100%
281 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.22917 | 0.22917 | 0.27708 | 0 | 1.15 | 1.15 | Remote reset done | Close | 0.05 |  | 100%
282 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | KUD03 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.68056 | 0.68056 | 0.69444 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100%
283 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | KUD06 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.52986 | 0.52986 | 0.54861 | 0 | 0.45 | 0.45 | Auto cable twist | Close | 0.019565 |  | 100%
284 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | KUD10 | O2R1 | KSIPL | 4.348% | 2676 | UPS Error | UPS Error | Breakdown | 0.65139 | 0.65139 | 0.71181 | 0 | 1.45 | 1.45 | UPS reset done. | Close | 0.063043 |  | 100%
285 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | KUD11 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.43056 | 0.43056 | 0.45208 | 0 | 0.51667 | 0.51667 | Auto cable twist | Close | 0.022464 |  | 100%
286 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | KUD16 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.71875 | 0.71875 | 0.73472 | 0 | 0.38333 | 0.38333 | Auto cable twist | Close | 0.016667 |  | 100%
287 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | KUD19 | O2R1 | KSIPL | 4.348% | 165 | Low oil-level, hydraulic | Low oil-level, hydraulic | Breakdown | 0 | 0 | 0.083333 | 0 | 2 | 2 | Found hub inside main accumulator connected oil hose pipe O-ring failure then replaced after restored | Close | 0.086957 |  | 100%
288 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | KUD19 | O2R1 | KSIPL | 4.348% | 3024 | ArcNetReconfigMaxLimit________ | ArcNetReconfigMaxLimit________ | Breakdown | 0.43611 | 0.43611 | 0.46528 | 0 | 0.7 | 0.7 | Remote reset done | Close | 0.030435 |  | 100%
289 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | KUD20 | O2R1 | KSIPL | 4.348% | 335 | ExtHighIRotorInv phase: _ | ExtHighIRotorInv phase: _ | Breakdown | 0.33403 | 0.33403 | 0.38333 | 0 | 1.1833 | 1.1833 | Remote reset done | Close | 0.051449 |  | 100%
290 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | KUD12 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.63194 | 0.63194 | 0.64583 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.104
291 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | KUD19 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.45347 | 0.45347 | 0.46806 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0
292 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | KUD17 | O2R2 | SIL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.43819 | 0.43819 | 0.49653 | 0 | 1.4 | 1.4 | Manual stop for 2 years service day-01 | Close | 0.06087 |  | 100% |  | 0.23
293 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD03 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.74792 | 0.74792 | 0.76667 | 0 | 0.45 | 0.45 | Auto cable twist | Close | 0.019565 |  | 100% |  | 0.225
294 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD08 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.68056 | 0.68056 | 0.69097 | 0 | 0.25 | 0.25 | Auto cable twist | Close | 0.01087 |  | 100% |  | 0.25
295 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD11 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.74375 | 0.74375 | 0.76181 | 0 | 0.43333 | 0.43333 | Auto cable twist | Close | 0.018841 |  | 100% |  | 0.122
296 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD12 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.94861 | 0.94861 | 0.95139 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0028986 |  | 100% |  | 0.038
297 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD12 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.95833 | 0.95833 | 0.98472 | 0 | 0.63333 | 0.63333 | Auto reset | Close | 0.027536 |  | 100% |  | 0.108
298 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD14 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.74653 | 0.74653 | 0.76458 | 0 | 0.43333 | 0.43333 | Auto cable twist | Close | 0.018841 |  | 100% |  | 0.067
299 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD15 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.98125 | 0.98125 | 0.99931 | 0 | 0.43333 | 0.43333 | Auto cable twist | Close | 0.018841 |  | 100% |  | 0.034
300 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD20 | O2R1 | KSIPL | 4.348% | 5470 | GeneratorBreakerFBResponse | GeneratorBreakerFBResponse | Breakdown | 0.68958 | 0.68958 | 0.73542 | 0 | 1.1 | 1.1 | Generator Coli supply reboot done | Close | 0.047826 |  | 100% |  | 0.608
301 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD04 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.41042 | 0.41042 | 0.42569 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.006
302 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD05 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.49236 | 0.49236 | 0.51111 | 0 | 0.45 | 0.45 | Auto cable twist | Close | 0.019565 |  | 100% |  | 0.002
303 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD06 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.31389 | 0.31389 | 0.33194 | 0 | 0.43333 | 0.43333 | Auto cable twist | Close | 0.018841 |  | 100% |  | 0.002
304 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD07 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.97153 | 0.97153 | 0.99236 | 0 | 0.5 | 0.5 | Auto cable twist | Close | 0.021739 |  | 100% |  | -0.005
305 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD17 | O2R2 | SIL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.43472 | 0.43472 | 0.60278 | 0 | 4.0333 | 4.0333 | Manual stop for 2 years service day-02 | Close | 0.17536 |  | 100% |  | 0.137
306 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD22 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.97708 | 0.97708 | 0.99792 | 0 | 0.5 | 0.5 | Auto cable twist | Close | 0.021739 |  | 100% |  | 0.076
307 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD08 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.67986 | 0.67986 | 0.6875 | 0 | 0.18333 | 0.18333 | Auto cable twist | Close | 0.007971 |  | 100% |  | 0.001
308 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD13 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.45 | 0.45 | 0.45139 | 0 | 0.033333 | 0.033333 | Auto start after battery fully charged. | Close | 0.0014493 |  | 100% |  | 0
309 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD13 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.56875 | 0.56875 | 0.58333 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.012
310 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD13 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.65625 | 0.65625 | 0.65972 | 0 | 0.083333 | 0.083333 | Auto start after battery fully charged. | Close | 0.0036232 |  | 100% |  | -0.001
311 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD13 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.74653 | 0.74653 | 0.75 | 0 | 0.083333 | 0.083333 | Auto start after battery fully charged. | Close | 0.0036232 |  | 100% |  | 0.035
312 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD19 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.55278 | 0.55278 | 0.56736 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.002
313 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD20 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.45 | 0.45 | 0.45139 | 0 | 0.033333 | 0.033333 | Auto start after battery fully charged. | Close | 0.0014493 |  | 100% |  | 0
314 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD20 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.73125 | 0.73125 | 0.73611 | 0 | 0.11667 | 0.11667 | Auto start after battery fully charged. | Close | 0.0050725 |  | 100% |  | 0
315 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.97014 | 0.97014 | 0.99931 | 0 | 0.7 | 0.7 | Remote reset done | Close | 0.030435 |  | 100% |  | 0.15
316 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD09 | O2R3 | JK | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.40833 | 0.40833 | 0.68125 | 0 | 6.55 | 6.55 | Manual stop for 2 years service day-01 | Close | 0.28478 |  | 100% |  | 0.084
317 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD09 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.77917 | 0.77917 | 0.79375 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.001
318 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD18 | O2R4 | SGDCIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.34653 | 0.34653 | 0.47361 | 0 | 3.05 | 3.05 | Manual stop for CMS alert inspection work. | Close | 0.13261 |  | 100% |  | 0
319 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD18 | O2R4 | SGDCIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.55625 | 0.55625 | 0.57222 | 0 | 0.38333 | 0.38333 | Auto cable twist | Close | 0.016667 |  | 100% |  | 0.021
320 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD21 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.55764 | 0.55764 | 0.57222 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.012
321 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | KUD01 | O2R1 | KSIPL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.46458 | 0.46458 | 0.46528 | 0 | 0.016667 | 0.016667 | Auto start after battery fully charged. | Close | 0.00072464 |  | 100% |  | 0.009
322 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | KUD10 | O2R1 | KSIPL | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L_: ___V | Breakdown | 0.70139 | 0.70139 | 0.75 | 0 | 1.1667 | 1.1667 | HVCB Manual charged done. | Close | 0.050725 |  | 100% |  | 0.491
323 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.0069444 | 0.0069444 | 0.013889 | 0 | 0.16667 | 0.16667 | Remote reset done | Close | 0.0072464 |  | 100% |  | 0.166
324 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.21875 | 0.21875 | 0.26319 | 0 | 1.0667 | 1.0667 | Remote reset done | Close | 0.046377 |  | 100% |  | 0.28
325 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | KUD05 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.97014 | 0.97014 | 0.98542 | 0 | 0.36667 | 0.36667 | Remote reset done | Close | 0.015942 |  | 100% |  | 0.149
326 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | KUD09 | O2R3 | JK | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.41319 | 0.41319 | 0.69792 | 0 | 6.8333 | 6.8333 | Manual stop for 2 years service day-02 | Close | 0.2971 |  | 100% |  | 0.107
327 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | KUD14 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __1 | Manual Stop | 0.45208 | 0.45208 | 0.72222 | 0 | 6.4833 | 6.4833 | Manual stop for 2 years service day-01 | Close | 0.28188 |  | 100% |  | 2.212
328 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | KUD01 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.56181 | 0.56181 | 0.57569 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.015
329 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | KUD15 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.68056 | 0.68056 | 0.69444 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.038
330 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | KUD20 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.60208 | 0.60208 | 0.61667 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.024
331 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | KUD02 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.68681 | 0.68681 | 0.70139 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 0.043
332 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | KUD04 | O2R3 | JK | 4.348% | 79 | Max. Yaw error: ___._° | Max. Yaw error: ___._° |  | 0.19306 | 0.19306 | 0.19444 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0014493 |  | 100% |  | 0.114
333 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.25 | 0.25 | 0.28264 | 0 | 0.78333 | 0.78333 | Remote reset done | Close | 0.034058 |  | 100% |  | 0.066
334 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | KUD22 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.58542 | 0.58542 | 0.60208 | 0 | 0.4 | 0.4 | Auto cable twist | Close | 0.017391 |  | 100% |  | 0.017
335 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | KUD23 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.27639 | 0.27639 | 0.29028 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.03
336 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-02 | KUD10 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.82431 | 0.82431 | 0.83958 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.001
337 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-02 | KUD14 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.42986 | 0.42986 | 0.68819 | 0 | 6.2 | 6.2 | Manual stop for 2 years service day-02 | Close | 0.26957 |  | 100% |  | 0.177
338 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | KUD03 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.22222 | 0.22222 | 0.24167 | 0 | 0.46667 | 0.46667 | Auto cable twist | Close | 0.02029 |  | 100% |  | 0.033
339 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | KUD08 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.079861 | 0.079861 | 0.10069 | 0 | 0.5 | 0.5 | Auto cable twist | Close | 0.021739 |  | 100% |  | 0.347
340 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | KUD11 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.34861 | 0.34861 | 0.3625 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 0.033
341 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | KUD06 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.60972 | 0.60972 | 0.63056 | 0 | 0.5 | 0.5 | Auto cable twist | Close | 0.021739 |  | 100% |  | 0.028
342 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | KUD22 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.22153 | 0.22153 | 0.23819 | 0 | 0.4 | 0.4 | Auto cable twist | Close | 0.017391 |  | 100% |  | 0.02
343 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-04 | KUD01 | O2R1 | KSIPL | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L_: ___V | Breakdown | 0.59653 | 0.59653 | 0.64931 | 0 | 1.2667 | 1.2667 | HVCB Manual charged done. | Close | 0.055072 |  | 100% |  | 0.509
344 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-04 | KUD15 | O2R1 | KSIPL | 4.348% | 3805 | HubSafetySystem DC Supply Err. | HubSafetySystem DC Supply Err. | ROW | 0.41528 | 0.41528 | 0.99931 | 0 | 14.0167 | 14.0167 | WTG Stop because of HUB power supply DC error , But cannot attend because of Local ROW issue | Close | 0 |  | 100% |  | 4.44
345 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-04 | KUD05 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.67361 | 0.67361 | 0.68889 | 0 | 0.36667 | 0.36667 | Auto cable twist | Close | 0.015942 |  | 100% |  | 0.112
346 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | KUD15 | O2R1 | KSIPL | 4.348% | 3805 | HubSafetySystem DC Supply Err. | HubSafetySystem DC Supply Err. | ROW | 0 | 0 | 0.66667 | 0 | 16 | 16 | WTG Stop because of HUB power supply DC error , But cannot attend because of Local ROW issue | Close | 0 |  | 100% |  | 0
347 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | KUD15 | O2R1 | KSIPL | 4.348% | 3805 | HubSafetySystem DC Supply Err. | HubSafetySystem DC Supply Err. | Breakdown | 0.66667 | 0.66667 | 0.88472 | 0 | 5.2333 | 5.2333 | Attend and replaced HUB 24V power supply along with C blade prop valve 'o' ring | Close | 0.22754 |  | 100% |  | 1416
348 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | KUD20 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.43681 | 0.43681 | 0.63819 | 0 | 4.8333 | 4.8333 | Manual stop for 2 years service day-02 | Close | 0.21014 |  | 100% |  | 202
349 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-06 | KUD08 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.85833 | 0.85833 | 0.875 | 0 | 0.4 | 0.4 | Auto cable twist | Close | 0.017391 |  | 100% |  | 25
350 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-06 | KUD07 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.56181 | 0.56181 | 0.57569 | 0 | 0.33333 | 0.33333 | Auto cable twist | Close | 0.014493 |  | 100% |  | 24
351 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-06 | KUD18 | O2R4 | SGDCIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.41042 | 0.41042 | 0.74167 | 0 | 7.95 | 7.95 | Manual stop for 2 years service day-01 | Close | 0.34565 |  | 100% |  | 931
352 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | KUD09 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.56528 | 0.56528 | 0.57847 | 0 | 0.31667 | 0.31667 | Auto cable twist | Close | 0.013768 |  | 100% |  | 171
353 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | KUD10 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.40486 | 0.40486 | 0.65139 | 0 | 5.9167 | 5.9167 | Manual stop for 2 years service day-01 | Close | 0.25725 |  | 100% |  | 3203
354 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | KUD11 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.66597 | 0.66597 | 0.68264 | 0 | 0.4 | 0.4 | Auto cable twist | Close | 0.017391 |  | 100% |  | 217
355 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | KUD21 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.50556 | 0.50556 | 0.52222 | 0 | 0.4 | 0.4 | Auto cable twist | Close | 0.017391 |  | 100% |  | 217
356 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | KUD10 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.43264 | 0.43264 | 0.725 | 0 | 7.0167 | 7.0167 | Manual stop for 2 years service day-02 | Close | 0.30507 |  | 100% |  | 869
357 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | KUD15 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.53194 | 0.53194 | 0.75278 | 0 | 5.3 | 5.3 | Manual stop for CMS alert inspection work. | Close | 0.23043 |  | 100% |  | 434
358 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | KUD18 | O2R4 | SGDCIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.41319 | 0.41319 | 0.66667 | 0 | 6.0833 | 6.0833 | Manual stop for 2 years service day-02 | Close | 0.26449 |  | 100% |  | 73
359 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | KUD01 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.50069 | 0.50069 | 0.64861 | 0 | 3.55 | 3.55 | Manual stop for CMS alert inspection work. | Close | 0.15435 |  | 100% |  | 583
360 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | KUD21 | O2R3 | JK | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.46181 | 0.46181 | 0.72917 | 0 | 6.4167 | 6.4167 | Manual stop for 2 years service day-02 | Close | 0.27899 |  | 100% |  | 897
361 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD01 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.76597 | 0.76597 | 0.77708 | 0 | 0.26667 | 0.26667 | Remote reset done | Close | 0.011594 |  | 100% |  | 41
362 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD01 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.78472 | 0.78472 | 0.79583 | 0 | 0.26667 | 0.26667 | Remote reset done | Close | 0.011594 |  | 100% |  | 258
363 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD11 | O2R1 | KSIPL | 4.348% | 328 | Rotor inv. HW error L_ | Rotor inv. HW error L_ | Breakdown | 0.19514 | 0.19514 | 0.43889 | 0 | 5.85 | 5.85 | Found generator slipring brush one o got failure so replaced. | Close | 0.25435 |  | 100% |  | 1702
364 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD12 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.75556 | 0.75556 | 0.77153 | 0 | 0.38333 | 0.38333 | Remote reset done | Close | 0.016667 |  | 100% |  | 89
365 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD14 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.020833 | 0.020833 | 0.040972 | 0 | 0.48333 | 0.48333 | Remote reset done | Close | 0.021014 |  | 100% |  | 154
366 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD14 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.15486 | 0.15486 | 0.19375 | 0 | 0.93333 | 0.93333 | Remote reset done | Close | 0.04058 |  | 100% |  | 101
367 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD14 | O2R1 | KSIPL | 4.348% | 336 | Ext. High cur. Grid inv. L_ | Ext. High cur. Grid inv. L_ | Breakdown | 0.29375 | 0.29375 | 0.57431 | 0 | 6.7333 | 6.7333 | Found converter L2,L3 IGBT got failure so replaced | Close | 0.29275 |  | 100% |  | 804
368 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD19 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.76042 | 0.76042 | 0.76389 | 0 | 0.083333 | 0.083333 | Remote reset done | Close | 0.0036232 |  | 100% |  | 18
369 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD19 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.78194 | 0.78194 | 0.79792 | 0 | 0.38333 | 0.38333 | Remote reset done | Close | 0.016667 |  | 100% |  | 291
370 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.060417 | 0.060417 | 0.11111 | 0 | 1.2167 | 1.2167 | Remote reset done | Close | 0.052899 |  | 100% |  | 581
371 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.17153 | 0.17153 | 0.19375 | 0 | 0.53333 | 0.53333 | Remote reset done | Close | 0.023188 |  | 100% |  | 27
372 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.21736 | 0.21736 | 0.22222 | 0 | 0.11667 | 0.11667 | Remote reset done | Close | 0.0050725 |  | 100% |  | 39
373 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.74722 | 0.74722 | 0.75 | 0 | 0.066667 | 0.066667 | Remote reset done | Close | 0.0028986 |  | 100% |  | 16
374 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.76111 | 0.76111 | 0.76389 | 0 | 0.066667 | 0.066667 | Remote reset done | Close | 0.0028986 |  | 100% |  | 22
375 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD05 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.018056 | 0.018056 | 0.040972 | 0 | 0.55 | 0.55 | Remote reset done | Close | 0.023913 |  | 100% |  | 288
376 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD05 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.15486 | 0.15486 | 0.19375 | 0 | 0.93333 | 0.93333 | Remote reset done | Close | 0.04058 |  | 100% |  | 303
377 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD05 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.74861 | 0.74861 | 0.76667 | 0 | 0.43333 | 0.43333 | Remote reset done | Close | 0.018841 |  | 100% |  | 82
378 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD05 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.82847 | 0.82847 | 0.83333 | 0 | 0.11667 | 0.11667 | Remote reset done | Close | 0.0050725 |  | 100% |  | 58
379 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD05 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.84028 | 0.84028 | 0.85347 | 0 | 0.31667 | 0.31667 | Remote reset done | Close | 0.013768 |  | 100% |  | 222
380 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD09 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.015278 | 0.015278 | 0.039583 | 0 | 0.58333 | 0.58333 | Remote reset done | Close | 0.025362 |  | 100% |  | 270
381 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD16 | O2R2 | SIL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.74583 | 0.74583 | 0.75833 | 0 | 0.3 | 0.3 | Remote reset done | Close | 0.013043 |  | 100% |  | 57
382 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD16 | O2R2 | SIL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.78472 | 0.78472 | 0.79722 | 0 | 0.3 | 0.3 | Remote reset done | Close | 0.013043 |  | 100% |  | 357
383 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD18 | O2R4 | SGDCIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.76181 | 0.76181 | 0.76389 | 0 | 0.05 | 0.05 | Remote reset done | Close | 0.0021739 |  | 100% |  | 13
384 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | KUD18 | O2R4 | SGDCIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.775 | 0.775 | 0.79444 | 0 | 0.46667 | 0.46667 | Remote reset done | Close | 0.02029 |  | 100% |  | 323
385 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | KUD03 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.1625 | 0.1625 | 0.19375 | 0 | 0.75 | 0.75 | Remote reset done | Close | 0.032609 |  | 100% |  | 266
386 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | KUD12 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.079167 | 0.079167 | 0.10347 | 0 | 0.58333 | 0.58333 | Remote reset done | Close | 0.025362 |  | 100% |  | 498
387 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | KUD12 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.11319 | 0.11319 | 0.15833 | 0 | 1.0833 | 1.0833 | Remote reset done | Close | 0.047101 |  | 100% |  | 477
388 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | KUD14 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.022917 | 0.022917 | 0.027778 | 0 | 0.11667 | 0.11667 | Remote reset done | Close | 0.0050725 |  | 100% |  | 65
389 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | KUD16 | O2R2 | SIL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.42639 | 0.42639 | 0.74931 | 0 | 7.75 | 7.75 | Manual stop for 2 years service day-01 | Close | 0.33696 |  | 100% |  | 660
390 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | KUD16 | O2R2 | SIL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.43264 | 0.43264 | 0.74861 | 0 | 7.5833 | 7.5833 | Manual stop for 2 years service day-02 | Close | 0.32971 |  | 100% |  | 1234
391 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | KUD04 | O2R3 | JK | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L_: ___V | Breakdown | 0.072917 | 0.072917 | 0.11806 | 0 | 1.0833 | 1.0833 | HVCB Manual charged done. | Close | 0.047101 |  | 100% |  | 345
392 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | KUD08 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° | Breakdown | 0.7 | 0.7 | 0.71389 | 0 | 0.33333 | 0.33333 | Remote reset done | Close | 0.014493 |  | 100% |  | 49
393 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | KUD12 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.46042 | 0.46042 | 0.475 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 10
394 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | KUD19 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.42986 | 0.42986 | 0.81806 | 0 | 9.3167 | 9.3167 | Manual stop for 2 years service day-01 | Close | 0.40507 |  | 100% |  | 386
395 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | KUD07 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.68542 | 0.68542 | 0.7 | 0 | 0.35 | 0.35 | Auto cable twist | Close | 0.015217 |  | 100% |  | 21
396 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | KUD09 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.92222 | 0.92222 | 0.93681 | 0 | 0.35 | 0.35 | Remote reset done | Close | 0.015217 |  | 100% |  | 447
397 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | KUD02 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.35833 | 0.35833 | 0.37708 | 0 | 0.45 | 0.45 | Auto reset | Close | 0.019565 |  | 100% |  | 34
398 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.95972 | 0.95972 | 0.97153 | 0 | 0.28333 | 0.28333 | Remote reset done | Close | 0.012319 |  | 100% |  | 45
399 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.98264 | 0.98264 | 0.99792 | 0 | 0.36667 | 0.36667 | Remote reset done | Close | 0.015942 |  | 100% |  | 90
400 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | KUD05 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.58264 | 0.58264 | 0.59792 | 0 | 0.36667 | 0.36667 | Auto reset | Close | 0.015942 |  | 100% |  | 25
401 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | KUD11 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.37708 | 0.37708 | 0.39097 | 0 | 0.33333 | 0.33333 | Auto reset | Close | 0.014493 |  | 100% |  | 51
402 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | KUD17 | O2R2 | SIL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.35764 | 0.35764 | 0.37639 | 0 | 0.45 | 0.45 | Auto reset | Close | 0.019565 |  | 100% |  | 20
403 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | KUD19 | O2R1 | KSIPL | 4.348% | 5197 | Prop Valve C Status Fault | Prop Valve C Status Fault | Breakdown | 0.16944 | 0.16944 | 0.17361 | 0 | 0.1 | 0.1 | Remote reset done | Close | 0.0043478 |  | 100% |  | 43
404 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | KUD20 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.42569 | 0.42569 | 0.78056 | 0 | 8.5167 | 8.5167 | Manual stop for 2 years service day-01 | Close | 0.37029 |  | 100% |  | 512
405 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | KUD22 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.59444 | 0.59444 | 0.60903 | 0 | 0.35 | 0.35 | Auto reset | Close | 0.015217 |  | 100% |  | 15
406 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.32014 | 0.32014 | 0.33958 | 0 | 0.46667 | 0.46667 | Remote reset done | Close | 0.02029 |  | 100% |  | 105
407 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.82222 | 0.82222 | 0.86736 | 0 | 1.0833 | 1.0833 | Remote reset done | Close | 0.047101 |  | 100% |  | 151
408 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | KUD05 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.30625 | 0.30625 | 0.31806 | 0 | 0.28333 | 0.28333 | Remote reset done | Close | 0.012319 |  | 100% |  | 89
409 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | KUD06 | O2R3 | JK | 4.348% | 176 | Error on all wind sensors | Error on all wind sensors | Breakdown | 0.58819 | 0.58819 | 0.59722 | 0 | 0.21667 | 0.21667 | Remote reset done | Close | 0.0094203 |  | 100% |  | 483
410 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | KUD07 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.82222 | 0.82222 | 0.86736 | 0 | 1.0833 | 1.0833 | Remote reset done | Close | 0.047101 |  | 100% |  | 248
411 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | KUD11 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.82847 | 0.82847 | 0.87431 | 0 | 1.1 | 1.1 | Remote reset done | Close | 0.047826 |  | 100% |  | 223
412 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | KUD16 | O2R2 | SIL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.58542 | 0.58542 | 0.60417 | 0 | 0.45 | 0.45 | Auto reset | Close | 0.019565 |  | 100% |  | 265
413 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | KUD21 | O2R3 | JK | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.40139 | 0.40139 | 0.70833 | 0 | 7.3667 | 7.3667 | Manual stop for 2 years service day-01 | Close | 0.32029 |  | 100% |  | 610
414 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | KUD02 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.74653 | 0.74653 | 0.75625 | 0 | 0.23333 | 0.23333 | Remote reset done | Close | 0.010145 |  | 100% |  | 127
415 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | KUD21 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.74236 | 0.74236 | 0.74861 | 0 | 0.15 | 0.15 | Remote reset done | Close | 0.0065217 |  | 100% |  | 26
416 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | KUD22 | O2R3 | JK | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.58333 | 0.58333 | 0.73403 | 0 | 3.6167 | 3.6167 | Manual stop for 2 years service day-02 | Close | 0.15725 |  | 100% |  | 159
417 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | KUD23 | O2R3 | JK | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.41806 | 0.41806 | 0.53819 | 0 | 2.8833 | 2.8833 | Manual stop for 2 years service day-02 | Close | 0.12536 |  | 100% |  | 39
418 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | KUD02 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.78264 | 0.78264 | 0.79931 | 0 | 0.4 | 0.4 | Auto reset | Close | 0.017391 |  | 100% |  | 4
419 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | KUD03 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.051389 | 0.051389 | 0.0625 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.011594 |  | 100% |  | 1
420 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | KUD03 | O2R1 | KSIPL | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.80972 | 0.80972 | 0.82361 | 0 | 0.33333 | 0.33333 | Auto reset | Close | 0.014493 |  | 100% |  | 35
421 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | KUD04 | O2R3 | JK | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L_: ___V | Breakdown | 0.375 | 0.375 | 0.44444 | 0 | 1.6667 | 1.6667 | HVCB Manual charged done. | Close | 0.072464 |  | 100% |  | 10
422 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | KUD05 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.975 | 0.975 | 0.99306 | 0 | 0.43333 | 0.43333 | Auto reset | Close | 0.018841 |  | 100% |  | 104
423 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | KUD06 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.99444 | 0.99444 | 0.99931 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0050725 |  | 100% |  | 2
424 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | KUD09 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.97569 | 0.97569 | 0.99375 | 0 | 0.43333 | 0.43333 | Auto reset | Close | 0.018841 |  | 100% |  | 6
425 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | KUD14 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.8125 | 0.8125 | 0.82639 | 0 | 0.33333 | 0.33333 | Auto reset | Close | 0.014493 |  | 100% |  | 27
426 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | KUD14 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.97778 | 0.97778 | 0.99583 | 0 | 0.43333 | 0.43333 | Auto reset | Close | 0.018841 |  | 100% |  | 81
427 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | KUD19 | O2R1 | KSIPL | 4.348% | 5196 | Prop Valve B Status Fault | Prop Valve B Status Fault | Breakdown | 0.375 | 0.375 | 0.56875 | 0 | 4.65 | 4.65 | we found Blade A proportional valve to Pitch position sensor cable was loose connection during pitching time so we retighted and restored WTG. | Close | 0.20217 |  | 100% |  | 255
428 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | KUD19 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.97431 | 0.97431 | 0.98958 | 0 | 0.36667 | 0.36667 | Auto reset | Close | 0.015942 |  | 100% |  | 103
429 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | KUD20 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.77639 | 0.77639 | 0.79167 | 0 | 0.36667 | 0.36667 | Auto reset | Close | 0.015942 |  | 100% |  | 9
430 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | KUD21 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.78264 | 0.78264 | 0.79861 | 0 | 0.38333 | 0.38333 | Auto reset | Close | 0.016667 |  | 100% |  | 16
431 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | KUD22 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.97431 | 0.97431 | 0.99167 | 0 | 0.41667 | 0.41667 | Auto reset | Close | 0.018116 |  | 100% |  | 208
432 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | KUD23 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.97431 | 0.97431 | 0.99097 | 0 | 0.4 | 0.4 | Auto reset | Close | 0.017391 |  | 100% |  | 211
433 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | KUD01 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.35 | 0.35 | 0.36389 | 0 | 0.33333 | 0.33333 | Auto reset | Close | 0.014493 |  | 100% |  | 1
434 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | KUD04 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.19444 | 0.19444 | 0.21528 | 0 | 0.5 | 0.5 | Auto reset | Close | 0.021739 |  | 100% |  | 31
435 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | KUD04 | O2R3 | JK | 4.348% | 931 | Arc light detected | Arc light detected | Breakdown | 0.70139 | 0.70139 | 0.89375 | 0 | 4.6167 | 4.6167 | we inspected the transformer room found normal then restored wtg. | Close | 0.20072 |  | 100% |  | 5
436 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | KUD06 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.0069444 | 0.0069444 | 0.015972 | 0 | 0.21667 | 0.21667 | Auto reset | Close | 0.0094203 |  | 100% |  | 45
437 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | KUD07 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.0097222 | 0.0097222 | 0.03125 | 0 | 0.51667 | 0.51667 | Auto reset | Close | 0.022464 |  | 100% |  | 98
438 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | KUD08 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.60556 | 0.60556 | 0.61944 | 0 | 0.33333 | 0.33333 | Auto reset | Close | 0.014493 |  | 100% |  | 14
439 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | KUD08 | O2R3 | JK | 4.348% | 5197 | Prop Valve C Status Fault | Prop Valve C Status Fault | Breakdown | 0.98611 | 0.98611 | 0.99931 | 0 | 0.31667 | 0.31667 | Remote reset done | Close | 0.013768 |  | 100% |  | 35
440 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | KUD11 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.57569 | 0.57569 | 0.59028 | 0 | 0.35 | 0.35 | Auto reset | Close | 0.015217 |  | 100% |  | 4
441 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | KUD16 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.73611 | 0.73611 | 0.75139 | 0 | 0.36667 | 0.36667 | Auto reset | Close | 0.015942 |  | 100% |  | 62
442 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | KUD17 | O2R2 | SIL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.68056 | 0.68056 | 0.69444 | 0 | 0.33333 | 0.33333 | Auto reset | Close | 0.014493 |  | 100% |  | 2
443 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | KUD18 | O2R4 | SGDCIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.73819 | 0.73819 | 0.75764 | 0 | 0.46667 | 0.46667 | Auto reset | Close | 0.02029 |  | 100% |  | 6
444 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | KUD22 | O2R3 | JK | 4.348% | 3272 | YawUntwistCW: Code__,_______° | YawUntwistCW: Code__,_______° |  | 0.775 | 0.775 | 0.79028 | 0 | 0.36667 | 0.36667 | Auto reset | Close | 0.015942 |  | 100% |  | 0
445 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | KUD22 | O2R3 | JK | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.42292 | 0.42292 | 0.69167 | 0 | 6.45 | 6.45 | Manual stop for 2 years service day-01 | Close | 0.28043 |  | 100% |  | 366
446 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD01 | O2R1 | KSIPL | 4.348% | 5471 | GeneratorBreakerTripped | GeneratorBreakerTripped |  | 0.75694 | 0.75694 | 0.81528 | 0 | 1.4 | 1.4 | we found ACB TUV tripped condition once rebooted and restored wtg. | Close | 0.06087 |  | 100% |  | 197
447 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD02 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.43056 | 0.43056 | 0.44444 | 0 | 0.33333 | 0.33333 | Auto reset | Close | 0.014493 |  | 100% |  | 9
448 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD03 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.5625 | 0.5625 | 0.57708 | 0 | 0.35 | 0.35 | Auto reset | Close | 0.015217 |  | 100% |  | 43
449 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD05 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° | Breakdown | 0.71181 | 0.71181 | 0.72639 | 0 | 0.35 | 0.35 | Auto reset | Close | 0.015217 |  | 100% |  | 39
450 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD06 | O2R3 | JK | 4.348% | 181 | Feedback = _, yawing CW _ | Feedback = _, yawing CW _ | Manual Stop | 0.0069444 | 0.0069444 | 0.034722 | 0 | 0.66667 | 0.66667 | Remote reset done | Close | 0.028986 |  | 100% |  | 2
451 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD06 | O2R3 | JK | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Breakdown | 0.57639 | 0.57639 | 0.64583 | 0 | 1.6667 | 1.6667 | we checked the Yaw position sensor cable found normal then restored wtg. | Close | 0.072464 |  | 100% |  | 29
452 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD06 | O2R3 | JK | 4.348% | 3298 | Yaw To Cable Twist Reset | Yaw To Cable Twist Reset |  | 0.67917 | 0.67917 | 0.69306 | 0 | 0.33333 | 0.33333 | Auto Reset | Close | 0.014493 |  | 100% |  | 102
453 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD07 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° | Breakdown | 0.49236 | 0.49236 | 0.51042 | 0 | 0.43333 | 0.43333 | Auto reset | Close | 0.018841 |  | 100% |  | 52
454 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD08 | O2R3 | JK | 4.348% | 5197 | Prop Valve C Status Fault | Prop Valve C Status Fault | Breakdown | 0.0069444 | 0.0069444 | 0.027083 | 0 | 0.48333 | 0.48333 | Remote reset done | Close | 0.021014 |  | 100% |  | 2
455 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD08 | O2R3 | JK | 4.348% | 5197 | Prop Valve C Status Fault | Prop Valve C Status Fault | Breakdown | 0.32639 | 0.32639 | 0.44722 | 0 | 2.9 | 2.9 | we checked the balde C proportional valve cable connector was loose condition due to these pitching time error was trigged so retighten done and restored wtg. | Close | 0.12609 |  | 100% |  | 5
456 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD08 | O2R3 | JK | 4.348% | 5197 | Prop Valve C Status Fault | Prop Valve C Status Fault |  | 0.52778 | 0.52778 | 0.57361 | 0 | 1.1 | 1.1 | we checked the balde C proportional valve cable connector was loose condition due to these pitching time error was trigged so retighten done and restored wtg. | Close | 0.047826 |  | 100% |  | 21
457 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD12 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° | Breakdown | 0.52778 | 0.52778 | 0.53472 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0072464 |  | 100% |  | 26
458 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD13 | O2R1 | KSIPL | 4.348% | 3298 | Yaw To Cable Twist Reset | Yaw To Cable Twist Reset |  | 0.48056 | 0.48056 | 0.49653 | 0 | 0.38333 | 0.38333 | Auto reset | Close | 0.016667 |  | 100% |  | 71
459 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD15 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° | Breakdown | 0.18889 | 0.18889 | 0.20278 | 0 | 0.33333 | 0.33333 | Auto reset | Close | 0.014493 |  | 100% |  | 2
460 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD15 | O2R1 | KSIPL | 4.348% | 3298 | Yaw To Cable Twist Reset | Yaw To Cable Twist Reset |  | 0.52778 | 0.52778 | 0.53542 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.007971 |  | 100% |  | 38
461 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD20 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.43333 | 0.43333 | 0.45139 | 0 | 0.43333 | 0.43333 | Auto reset | Close | 0.018841 |  | 100% |  | 303
462 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | KUD21 | O2R3 | JK | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code__,_______° |  | 0.48819 | 0.48819 | 0.49375 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0057971 |  | 100% |  | 4
463 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-21 | KUD23 | O2R3 | JK | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.44792 | 0.44792 | 0.71319 | 0 | 6.3667 | 6.3667 | Manual stop for 2 years service day-01 | Close | 0.27681 |  | 100% |  | 6349
464 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | KUD19 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.42708 | 0.42708 | 0.46597 | 0 | 0.93333 | 0.93333 | Manual stop for 2 years service day-02 | Close | 0.04058 |  | 100% |  | 1495 |  | KUD/2025/523
465 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | KUD19 | O2R1 | KSIPL | 4.348% | 309 | Pause over RCS __0 | Pause over RCS __0 | Manual Stop | 0.58333 | 0.58333 | 0.68403 | 0 | 2.4167 | 2.4167 | Manual stop for 2 years service day-02 | Close | 0.10507 |  | 100% |  | 4416 |  | KUD/2025/523
466 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | KUD01 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.58611 | 0.58611 | 0.59167 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0057971 |  | 100% |  | 1.951
467 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | KUD11 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.45 | 0.45 | 0.45556 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0057971 |  | 100% |  | 2.851
468 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | KUD04 | O2R3 | JK | 4.348% | 5470 | GeneratorBreakerFBResponse | GeneratorBreakerFBResponse | Breakdown | 0.93958 | 0.93958 | 0.98611 | 0 | 1.1167 | 1.1167 | we found ACB TUV tripped condition once rebooted and restored wtg. | Close | 0.048551 |  | 100% |  | 6.659
469 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | KUD16 | O2R2 | SIL | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L1: 1V | Breakdown | 0.93958 | 0.93958 | 0.98958 | 0 | 1.2 | 1.2 | HVCB Manual charged done. | Close | 0.052174 |  | 100% |  | 6.569
470 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | KUD06 | O2R3 | JK | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Breakdown | 0.6875 | 0.6875 | 0.7375 | 0 | 1.2 | 1.2 | Preventive action taken for gearoil inlet temp high checked Found GB inlet thermostat valve malfunction so replaced to new one. | Close | 0.052174 |  | 100% |  | 815.2
471 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | KUD09 | O2R3 | JK | 4.348% | 5470 | GeneratorBreakerFBResponse | GeneratorBreakerFBResponse | ROW | 0.49931 | 0.49931 | 0.54861 | 0 | 1.1833 | 1.1833 | After feeder charged generator breaker FB response error came wtg under ROW issue.. | Close | 0 |  | 100% |  | 6412.3
472 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | KUD09 | O2R3 | JK | 4.348% | 5470 | GeneratorBreakerFBResponse | GeneratorBreakerFBResponse | Breakdown | 0.54861 | 0.54861 | 0.59028 | 0 | 1 | 1 | Found ACB not closing then TU reset outside came after normalised restored done. | Close | 0.043478 |  | 100% |  | 2092.7
473 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | KUD11 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.45833 | 0.45833 | 0.46389 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0057971 |  | 100% |  | 2027.1
474 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-29 | KUD02 | O2R3 | JK | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.57153 | 0.57153 | 0.62083 | 0 | 1.1833 | 1.1833 | checked gearbox and hydraulic unit all are good condition there is no leakage then restored the wtg | Close | 0.051449 |  | 100% |  | 1664.8
475 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-30 | KUD08 | O2R3 | JK | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.58611 | 0.58611 | 0.61389 | 0 | 0.66667 | 0.66667 | Manual stop for Tower flange inspection work. | Close | 0.028986 |  | 100% |  | 2156
476 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | KUD10 | O2R1 | KSIPL | 4.348% | 3805 | HubSafetySystem DC Supply Err. | HubSafetySystem DC Supply Err. | Breakdown | 0.021528 | 0.021528 | 0.11389 | 0 | 2.2167 | 2.2167 | Found hub safety 24v cable loose condition then tighten after restored | Close | 0.096377 |  | 100% |  | 3618
477 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | KUD01 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.78056 | 0.78056 | 0.78472 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0043478 |  | 100% |  | 173
478 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | KUD18 | O2R4 | SGDCIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.73542 | 0.73542 | 0.74861 | 0 | 0.31667 | 0.31667 | Remote reset done | Close | 0.013768 |  | 100% |  | 611
479 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | KUD22 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.73264 | 0.73264 | 0.73611 | 0 | 0.083333 | 0.083333 | Remote reset done | Close | 0.0036232 |  | 100% |  | 169
480 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | KUD07 | O2R3 | JK | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.70417 | 0.70417 | 0.74028 | 0 | 0.86667 | 0.86667 | Manual stop for Stiffener plate fixing work. | Close | 0.037681 |  | 100% |  | 24
481 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | KUD11 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.36944 | 0.36944 | 0.375 | 0 | 0.13333 | 0.13333 | Auto Reset | Close | 0.0057971 |  | 100% |  | 133
482 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | KUD04 | O2R3 | JK | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.42847 | 0.42847 | 0.46319 | 0 | 0.83333 | 0.83333 | Manual stop for Tower flange inspection work. | Close | 0.036232 |  | 100% |  | 1046
483 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | KUD20 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.79653 | 0.79653 | 0.79861 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0021739 |  | 100% |  | 19
484 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | KUD22 | O2R3 | JK | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L_: ___V | Breakdown | 0.9375 | 0.9375 | 0.99931 | 0 | 1.4833 | 1.4833 | we found HUB controller communication not available then rebooted once and restored. | Close | 0.064493 |  | 100% |  | 0
485 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | KUD10 | O2R1 | KSIPL | 4.348% | 137 | Asym.currL2:____A,Others:____A | Asym.currL2:____A,Others:____A | Breakdown | 0.42014 | 0.42014 | 0.42361 | 0 | 0.083333 | 0.083333 | Auto Reset | Close | 0.0036232 |  | 100% |  | 75
486 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | KUD13 | O2R1 | KSIPL | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.65347 | 0.65347 | 0.74028 | 0 | 2.0833 | 2.0833 | Manual stop for Tower flange inspection work. | Close | 0.09058 |  | 100% |  | 9
487 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | KUD22 | O2R3 | JK | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L_: ___V | Breakdown | 0 | 0 | 0.072917 | 0 | 1.75 | 1.75 | we found HUB controller communication not available then rebooted once and restored. | Close | 0.076087 |  | 100% |  | 528
488 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-06 | KUD01 | O2R1 | KSIPL | 4.348% | 335 | ExtHighIRotorInv phase: _ | ExtHighIRotorInv phase: _ | Breakdown | 0.38333 | 0.38333 | 0.38889 | 0 | 0.13333 | 0.13333 | Auto Reset | Close | 0.0057971 |  | 100% |  | 91
489 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-06 | KUD01 | O2R1 | KSIPL | 4.348% | 5471 | GeneratorBreakerTripped | GeneratorBreakerTripped | Breakdown | 0.38889 | 0.38889 | 0.51667 | 0 | 3.0667 | 3.0667 | we found ACB TUV tripped condition once rebooted and restored wtg. | Close | 0.13333 |  | 100% |  | 1244
490 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-06 | KUD20 | O2R1 | KSIPL | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.33681 | 0.33681 | 0.65833 | 0 | 7.7167 | 7.7167 | Manual stop for Tower flange inspection work during operation Blade C Position encoder error triggered so we found blade C Encoder cable was loosen due to these signal was mismatching and alarm was triggered continuously retighten done and restored WTG. | Close | 0.33551 |  | 100% |  | 3126
491 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD01 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.75972 | 0.75972 | 0.76389 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0043478 |  | 100% |  | 105
492 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD02 | O2R3 | JK | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.58264 | 0.58264 | 0.67083 | 0 | 2.1167 | 2.1167 | Manual stop for Tower flange inspection work. | Close | 0.092029 |  | 100% |  | 1173
493 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.91667 | 0.91667 | 0.92986 | 0 | 0.31667 | 0.31667 | Remote reset done | Close | 0.013768 |  | 100% |  | 87
494 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.94236 | 0.94236 | 0.95625 | 0 | 0.33333 | 0.33333 | Remote reset done | Close | 0.014493 |  | 100% |  | 134
495 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.97917 | 0.97917 | 0.99931 | 0 | 0.48333 | 0.48333 | Remote reset done | Close | 0.021014 |  | 100% |  | 113
496 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD04 | O2R3 | JK | 4.348% | 6290 | Pitch Accu. Test active | Pitch Accu. Test active | Breakdown | 0.93472 | 0.93472 | 0.9375 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0028986 |  | 100% |  | 24
497 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD05 | O2R3 | JK | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.74097 | 0.74097 | 0.76944 | 0 | 0.68333 | 0.68333 | Manual stop for Tower flange inspection work. | Close | 0.02971 |  | 100% |  | 589
498 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD05 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.95 | 0.95 | 0.95139 | 0 | 0.033333 | 0.033333 | Remote reset done | Close | 0.0014493 |  | 100% |  | 14
499 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD05 | O2R3 | JK | 4.348% | 6293 | Pitch valves test acitve | Pitch valves test acitve | Breakdown | 0.95486 | 0.95486 | 0.95833 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0036232 |  | 100% |  | 22
500 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD08 | O2R3 | JK | 4.348% | 137 | Asym.currL2:____A,Others:____A | Asym.currL2:____A,Others:____A | Breakdown | 0.49583 | 0.49583 | 0.5 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0043478 |  | 100% |  | 63
501 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD11 | O2R1 | KSIPL | 4.348% | 137 | Asym.currL2:____A,Others:____A | Asym.currL2:____A,Others:____A | Breakdown | 0.53264 | 0.53264 | 0.53472 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0021739 |  | 100% |  | 69
502 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD11 | O2R1 | KSIPL | 4.348% | 6293 | Pitch valves test acitve | Pitch valves test acitve | Breakdown | 0.53819 | 0.53819 | 0.54167 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0036232 |  | 100% |  | 101
503 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD11 | O2R1 | KSIPL | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.66458 | 0.66458 | 0.69931 | 0 | 0.83333 | 0.83333 | Manual stop for Tower flange inspection work. | Close | 0.036232 |  | 100% |  | 457
504 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD12 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.98056 | 0.98056 | 0.98611 | 0 | 0.13333 | 0.13333 | Remote reset done | Close | 0.0057971 |  | 100% |  | 32
505 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD12 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.99653 | 0.99653 | 0.99931 | 0 | 0.066667 | 0.066667 | Remote reset done | Close | 0.0028986 |  | 100% |  | 47
506 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD12 | O2R1 | KSIPL | 4.348% | 6293 | Pitch valves test acitve | Pitch valves test acitve | Breakdown | 0.98958 | 0.98958 | 0.99306 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0036232 |  | 100% |  | 53
507 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | KUD22 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.95 | 0.95 | 0.95486 | 0 | 0.11667 | 0.11667 | Remote reset done | Close | 0.0050725 |  | 100% |  | 68
508 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | KUD03 | O2R1 | KSIPL | 4.348% | 137 | Asym.currL2:____A,Others:____A | Asym.currL2:____A,Others:____A | Breakdown | 0.53194 | 0.53194 | 0.53472 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0028986 |  | 100% |  | 120
509 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | KUD03 | O2R1 | KSIPL | 4.348% | 6293 | Pitch valves test acitve | Pitch valves test acitve | Breakdown | 0.53889 | 0.53889 | 0.54167 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0028986 |  | 100% |  | 31
510 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | KUD11 | O2R1 | KSIPL | 4.348% | 137 | Asym.currL2:____A,Others:____A | Asym.currL2:____A,Others:____A | Breakdown | 0.49722 | 0.49722 | 0.5 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0028986 |  | 100% |  | 124
511 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | KUD11 | O2R1 | KSIPL | 4.348% | 6293 | Pitch valves test acitve | Pitch valves test acitve | Breakdown | 0.50417 | 0.50417 | 0.50694 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0028986 |  | 100% |  | 32
512 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | KUD12 | O2R1 | KSIPL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.0083333 | 0.0083333 | 0.013889 | 0 | 0.13333 | 0.13333 | Remote reset done | Close | 0.0057971 |  | 100% |  | 77
513 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.0090278 | 0.0090278 | 0.013889 | 0 | 0.11667 | 0.11667 | Remote reset done | Close | 0.0050725 |  | 100% |  | 58
514 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | KUD01 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.74097 | 0.74097 | 0.74583 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0050725 |  | 100% |  | 1352.4
515 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | KUD02 | O2R3 | JK | 4.348% | 557 | RT activation no. exceeded:___ | RT activation no. exceeded: 15 | Breakdown | 0.47847 | 0.47847 | 0.48333 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0050725 |  | 100% |  | 374.9
516 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | KUD10 | O2R1 | KSIPL | 4.348% | 3273 | YawUntwistCCW: Code__,_______° | YawUntwistCCW: Code 6, 553Â° |  | 0.044444 | 0.044444 | 0.060417 | 0 | 0.38333 | 0.38333 | Auto reset | Close | 0.016667 |  | 100% |  | 870.8
517 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | KUD17 | O2R2 | SIL | 4.348% | 3298 | Yaw To Cable Twist Reset | Yaw To Cable Twist Reset | Breakdown | 0.27847 | 0.27847 | 0.28611 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.007971 |  | 100% |  | 1752
518 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | KUD18 | O2R4 | SGDCIPL | 4.348% | 3298 | Yaw To Cable Twist Reset | Yaw To Cable Twist Reset | Breakdown | 0.27847 | 0.27847 | 0.28542 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0072464 |  | 100% |  | 1255.7
519 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | KUD21 | O2R3 | JK | 4.348% | 3298 | Yaw To Cable Twist Reset | Yaw To Cable Twist Reset | Breakdown | 0.27847 | 0.27847 | 0.28681 | 0 | 0.2 | 0.2 | Auto reset | Close | 0.0086957 |  | 100% |  | 1060.8
520 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | KUD04 | O2R3 | JK | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L1: 2V | Breakdown | 0.27847 | 0.27847 | 0.32083 | 0 | 1.0167 | 1.0167 | Auto reset | Close | 0.044203 |  | 100% |  | 488.3
521 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | KUD12 | O2R1 | KSIPL | 4.348% | 138 | Asym.currL3:____A,Others:____A | Asym.currL3:____A,Others:____A | Breakdown | 0.47431 | 0.47431 | 0.47917 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0050725 |  | 100% |  | 69
522 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | KUD13 | O2R1 | KSIPL | 4.348% | 137 | Asym.currL2:____A,Others:____A | Asym.currL2:____A,Others:____A | Breakdown | 0.52014 | 0.52014 | 0.525 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0050725 |  | 100% |  | 56
523 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | KUD15 | O2R1 | KSIPL | 4.348% | 137 | Asym.currL2:____A,Others:____A | Asym.currL2:____A,Others:____A | Breakdown | 0.57292 | 0.57292 | 0.57639 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0036232 |  | 100% |  | 110
524 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | KUD19 | O2R1 | KSIPL | 4.348% | 136 | Asym.currL1:____A,Others:____A | Asym.currL1:____A,Others:____A | Breakdown | 0.48333 | 0.48333 | 0.48611 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0028986 |  | 100% |  | 58
525 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | KUD19 | O2R1 | KSIPL | 4.348% | 6293 | Pitch valves test acitve | Pitch valves test acitve | Breakdown | 0.49028 | 0.49028 | 0.49306 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0028986 |  | 100% |  | 53
526 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | KUD20 | O2R1 | KSIPL | 4.348% | 137 | Asym.currL2:____A,Others:____A | Asym.currL2:____A,Others:____A | Breakdown | 0.48889 | 0.48889 | 0.49306 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0043478 |  | 100% |  | 83
527 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | KUD04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.98819 | 0.98819 | 0.99931 | 0 | 0.26667 | 0.26667 | Remote reset done | Close | 0.011594 |  | 100% |  | 111
528 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | KUD06 | O2R3 | JK | 4.348% | 138 | Asym.currL3:____A,Others:____A | Asym.currL3:____A,Others:____A | Breakdown | 0.53264 | 0.53264 | 0.53472 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0021739 |  | 100% |  | 31
529 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | KUD06 | O2R3 | JK | 4.348% | 6293 | Pitch valves test acitve | Pitch valves test acitve | Breakdown | 0.53889 | 0.53889 | 0.54167 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0028986 |  | 100% |  | 3
530 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | KUD07 | O2R3 | JK | 4.348% | 136 | Asym.currL1:____A,Others:____A | Asym.currL1:____A,Others:____A | Breakdown | 0.52917 | 0.52917 | 0.53472 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0057971 |  | 100% |  | 63
531 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | KUD07 | O2R3 | JK | 4.348% | 136 | Asym.currL1:____A,Others:____A | Asym.currL1:____A,Others:____A | Breakdown | 0.56597 | 0.56597 | 0.56944 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0036232 |  | 100% |  | 120
532 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | KUD09 | O2R3 | JK | 4.348% | 137 | Asym.currL2:____A,Others:____A | Asym.currL2:____A,Others:____A | Breakdown | 0.52639 | 0.52639 | 0.52778 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0014493 |  | 100% |  | 71
533 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | KUD12 | O2R1 | KSIPL | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.48958 | 0.48958 | 0.53125 | 0 | 1 | 1 | Manual stop for Tower flange inspection work. | Close | 0.043478 |  | 100% |  | 528
534 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | KUD21 | O2R3 | JK | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.57014 | 0.57014 | 0.73056 | 0 | 3.85 | 3.85 | Manual stop for Generator Alignment work. | Close | 0.16739 |  | 100% |  | 1254
535 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | Kud01 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.75903 | 0.75903 | 0.76389 | 0 | 0.11667 | 0.11667 | Auto Reset | Close | 0.0050725 |  | 100% |  | 156
536 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | KUD10 | O2R1 | KSIPL | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.51597 | 0.51597 | 0.66528 | 0 | 3.5833 | 3.5833 | Manual stop for Generator Alignment work. | Close | 0.1558 |  | 100% |  | 1555
537 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | Kud04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.0069444 | 0.0069444 | 0.019444 | 0 | 0.3 | 0.3 | Remote reset done | Close | 0.013043 |  | 100% |  | 122
538 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | Kud04 | O2R3 | JK | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.24583 | 0.24583 | 0.25 | 0 | 0.1 | 0.1 | Remote reset done | Close | 0.0043478 |  | 100% |  | 37
539 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | Kud04 | O2R3 | JK | 4.348% | 6293 | Pitch valves test acitve | Pitch valves test acitve | Breakdown | 0.25347 | 0.25347 | 0.25694 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0036232 |  | 100% |  | 31
540 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | KUD17 | O2R2 | SIL | 4.348% | 704 | Ch High res. load C_ Load:___% | Ch High res. load C_ Load:___% | Breakdown | 0.44097 | 0.44097 | 0.44722 | 0 | 0.15 | 0.15 | Remote reset done | Close | 0.0065217 |  | 100% |  | 146
541 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-12 | KUD01 | O2R1 | KSIPL | 4.348% | 335 | ExtHighIRotorInv phase: _ | ExtHighIRotorInv phase: _ | Breakdown | 0.61528 | 0.61528 | 0.61806 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0028986 |  | 100% |  | 40
542 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-12 | KUD01 | O2R1 | KSIPL | 4.348% | 6293 | Pitch valves test acitve | Pitch valves test acitve | Breakdown | 0.62222 | 0.62222 | 0.625 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0028986 |  | 100% |  | 35
543 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-12 | KUD09 | O2R3 | JK | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.66042 | 0.66042 | 0.67153 | 0 | 0.26667 | 0.26667 | Manual stop for Tower flange inspection work. | Close | 0.011594 |  | 100% |  | 126
544 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-12 | KUD09 | O2R3 | JK | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.72222 | 0.72222 | 0.78264 | 0 | 1.45 | 1.45 | Manual stop for Tower flange inspection work. | Close | 0.063043 |  | 100% |  | 474
545 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-12 | KUD09 | O2R3 | JK | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.82639 | 0.82639 | 0.85625 | 0 | 0.71667 | 0.71667 | Manual stop for Tower flange inspection work. | Close | 0.031159 |  | 100% |  | 168
546 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-12 | KUD14 | O2R1 | KSIPL | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.57639 | 0.57639 | 0.64583 | 0 | 1.6667 | 1.6667 | Manual stop for Tower flange inspection work. | Close | 0.072464 |  | 100% |  | 541
547 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-14 | KUD11 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.086806 | 0.086806 | 0.090278 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0036232 |  | 100% |  | 81
548 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-14 | KUD11 | O2R1 | KSIPL | 4.348% | 6290 | Pitch Accu. Test active | Pitch Accu. Test active | Breakdown | 0.095139 | 0.095139 | 0.097222 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0021739 |  | 100% |  | 115
549 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-14 | KUD23 | O2R3 | JK | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Breakdown | 0.52708 | 0.52708 | 0.53472 | 0 | 0.18333 | 0.18333 | Remote reboot done | Close | 0.007971 |  | 100% |  | 264
550 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | KUD01 | O2R1 | KSIPL | 4.348% | 5471 | GeneratorBreakerTripped | GeneratorBreakerTripped | ROW | 0.47222 | 0.47222 | 0.98611 | 0 | 12.3333 | 12.3333 | ROW issue | Open | 0 |  | 100% |  | 143
551 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | KUD01 | O2R1 | KSIPL | 4.348% | 5471 | GeneratorBreakerTripped | GeneratorBreakerTripped | Breakdown | 0.98958 | 0.98958 | 0.99931 | 0 | 0.23333 | 0.23333 | Work under process.. | Open | 0.010145 |  | 100% |  | 0.8
552 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | KUD01 | O2R1 | KSIPL | 4.348% | 5471 | GeneratorBreakerTripped | GeneratorBreakerTripped | Breakdown | 0 | 0 | 0.055556 | 0 | 1.3333 | 1.3333 | Found ACB not closing then TU reset done. | Close | 0.057971 |  | 100% |  | 500
553 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | KUD01 | O2R1 | KSIPL | 4.348% | 5471 | GeneratorBreakerTripped | GeneratorBreakerTripped | Breakdown | 0.62639 | 0.62639 | 0.66181 | 0 | 0.85 | 0.85 | Found ACB not closing then TU reset done. | Close | 0.036957 |  | 100% |  | 4000
554 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | KUD14 | O2R1 | KSIPL | 4.348% | 5470 | GeneratorBreakerFBResponse | GeneratorBreakerFBResponse | Breakdown | 0.62639 | 0.62639 | 0.69861 | 0 | 1.7333 | 1.7333 | Found ACB closing coil malfunction then reboot done | Close | 0.075362 |  | 100% |  | 2200
555 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | KUD01 | O2R1 | KSIPL | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.60417 | 0.60417 | 0.62639 | 0 | 0.53333 | 0.53333 | Manual stop for Load Curtailment purpose | Close | 0.023188 |  | 100% |  | 1200
556 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | KUD03 | O2R1 | KSIPL | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.60417 | 0.60417 | 0.62639 | 0 | 0.53333 | 0.53333 | Manual stop for Load Curtailment purpose | Close | 0.023188 |  | 100% |  | 1200
557 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | KUD10 | O2R1 | KSIPL | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.60417 | 0.60417 | 0.62639 | 0 | 0.53333 | 0.53333 | Manual stop for Load Curtailment purpose | Close | 0.023188 |  | 100% |  | 1300
558 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | KUD11 | O2R1 | KSIPL | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.60417 | 0.60417 | 0.62639 | 0 | 0.53333 | 0.53333 | Manual stop for Load Curtailment purpose | Close | 0.023188 |  | 100% |  | 1100
559 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | KUD12 | O2R1 | KSIPL | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.60417 | 0.60417 | 0.62639 | 0 | 0.53333 | 0.53333 | Manual stop for Load Curtailment purpose | Close | 0.023188 |  | 100% |  | 1100
560 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | KUD13 | O2R1 | KSIPL | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.60417 | 0.60417 | 0.62639 | 0 | 0.53333 | 0.53333 | Manual stop for Load Curtailment purpose | Close | 0.023188 |  | 100% |  | 1100
561 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | KUD14 | O2R1 | KSIPL | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.60417 | 0.60417 | 0.62639 | 0 | 0.53333 | 0.53333 | Manual stop for Load Curtailment purpose | Close | 0.023188 |  | 100% |  | 1100
562 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | KUD15 | O2R1 | KSIPL | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.60417 | 0.60417 | 0.62639 | 0 | 0.53333 | 0.53333 | Manual stop for Load Curtailment purpose | Close | 0.023188 |  | 100% |  | 1100
563 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | KUD19 | O2R1 | KSIPL | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.60417 | 0.60417 | 0.62639 | 0 | 0.53333 | 0.53333 | Manual stop for Load Curtailment purpose | Close | 0.023188 |  | 100% |  | 1100
564 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | KUD11 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.37153 | 0.37153 | 0.375 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0036232 |  | 100% |  | 159
565 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | KUD11 | O2R1 | KSIPL | 4.348% | 6290 | Pitch Accu. Test active | Pitch Accu. Test active | Breakdown | 0.37986 | 0.37986 | 0.38194 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0021739 |  | 100% |  | 160
566 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | KUD07 | O2R3 | JK | 4.348% | 931 | Arc light detected | Arc light detected | Breakdown | 0.76389 | 0.76389 | 0.97222 | 0 | 5 | 5 | After grid restored Trafo room arc sensor activated so Trafo inspection done and found all normal and then restored. | Close | 0.21739 |  | 100% |  | 8123
567 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | KUD16 | O2R2 | SIL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | ROW | 0.36111 | 0.36111 | 0.59931 | 0 | 5.7167 | 5.7167 | Wtg pathway ROW issue.. | Close | 0 |  | 100% |  | 8176
568 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | KUD16 | O2R2 | SIL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.59931 | 0.59931 | 0.69861 | 0 | 2.3833 | 2.3833 | during running time error came checked found slipring track was damaged so we replaced 4 nos slip ring brush and 1nos slipring unit changed | Close | 0.10362 |  | 100% |  | 1767
569 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | KUD17 | O2R2 | SIL | 4.348% | 3907 | Estop Button Activated__ | Estop Button Activated 7 | Breakdown | 0.92708 | 0.92708 | 0.99931 | 0 | 1.7333 | 1.7333 | work inprogress.. | Open | 0.075362 |  | 100% |  | 5933
570 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | KUD17 | O2R2 | SIL | 4.348% | 3907 | Estop Button Activated__ | Estop Button Activated 7 | Breakdown | 0 | 0 | 0.31667 | 0 | 7.6 | 7.6 | Troubleshooting carried out safety pilz malfunction out and software update done | Close | 0.33043 |  | 100% |  | 12090
571 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | KUD01 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.029167 | 0.029167 | 0.034722 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0057971 |  | 100% |  | 490
572 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | KUD01 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.34931 | 0.34931 | 0.35417 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0050725 |  | 100% |  | 284
573 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | KUD11 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.76667 | 0.76667 | 0.77222 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0057971 |  | 100% |  | 300
574 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-05 | KUD11 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.55208 | 0.55208 | 0.55347 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0014493 |  | 100% |  | 1080
575 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-05 | KUD20 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.13542 | 0.13542 | 0.13681 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0014493 |  | 100% |  | 570
576 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-06 | KUD22 | O2R3 | JK | 4.348% | 338 | Slip:____ above limits _ | Slip:-027 above limits 1 | Breakdown | 0.58333 | 0.58333 | 0.58472 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0014493 |  | 100% |  | 2147.5
577 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | KUD01 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.24861 | 0.24861 | 0.25 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0014493 |  | 100% |  | 1295.6
578 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | KUD15 | O2R1 | KSIPL | 4.348% | 154 | Max rotor RPM: __._ RPM | Max rotor RPM: 17.3 RPM | Breakdown | 0.65069 | 0.65069 | 0.65208 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0014493 |  | 100% |  | 533.9
579 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-09 | KUD07 | O2R3 | JK | 4.348% | 598 | Circuit breaker open | Circuit breaker open | Breakdown | 0.35694 | 0.35694 | 0.59931 | 0 | 5.8167 | 5.8167 | We checked found Hydraulics motor 1 bearing was failiure so replaced new motor then restart the wtg. | Close | 0.2529 |  | 100% |  | 7068
580 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-09 | KUD11 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.29444 | 0.29444 | 0.29653 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0021739 |  | 100% |  | 30
581 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-11 | KUD01 | O2R1 | KSIPL | 4.348% | 450 | Ext. High I sum Grd inv. | Ext. High I sum Grd inv. | Breakdown | 0.28403 | 0.28403 | 0.28542 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0014493 |  | 100% |  | 110
582 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-11 | KUD21 | O2R3 | JK | 4.348% | 900 | Pause pressed on keyboard | Pause pressed on keyboard | Manual Stop | 0.47917 | 0.47917 | 0.58125 | 0 | 2.45 | 2.45 | Manual stop for VPC temp high inspection workFound VPC internal fan got failure, So replacement done. | Close | 0.10652 |  | 100% |  | 753.3
583 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-12 | KUD04 | O2R3 | JK | 4.348% | 6290 | Pitch Accu. Test active | Pitch Accu. Test active | Breakdown | 0.95694 | 0.95694 | 0.95833 | 0 | 0.033333 | 0.033333 | Remote reset done | Close | 0.0014493 |  | 100% |  | 77
584 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-12 | KUD05 | O2R3 | JK | 4.348% | 2995 | HydrHighPressPumpNotFunctional | HydrHighPressPumpNotFunctional | Breakdown | 0.95694 | 0.95694 | 0.95833 | 0 | 0.033333 | 0.033333 | Remote reset done | Close | 0.0014493 |  | 100% |  | 91
585 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-12 | KUD16 | O2R2 | SIL | 4.348% | 315 | ExEx low voltage L_: ___V | ExEx low voltage L_: ___V | Breakdown | 0.95764 | 0.95764 | 0.95833 | 0 | 0.016667 | 0.016667 | Remote reset done | Close | 0.00072464 |  | 100% |  | 1
586 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-12 | KUD17 | O2R2 | SIL | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.95694 | 0.95694 | 0.95833 | 0 | 0.033333 | 0.033333 | Remote reset done | Close | 0.0014493 |  | 100% |  | 178
587 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-12 | KUD21 | O2R3 | JK | 4.348% | 2995 | HydrHighPressPumpNotFunctional | HydrHighPressPumpNotFunctional | Breakdown | 0.95694 | 0.95694 | 0.95833 | 0 | 0.033333 | 0.033333 | Remote reset done | Close | 0.0014493 |  | 100% |  | 61
588 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-12 | KUD22 | O2R3 | JK | 4.348% | 2995 | HydrHighPressPumpNotFunctional | HydrHighPressPumpNotFunctional | Breakdown | 0.95139 | 0.95139 | 0.95833 | 0 | 0.16667 | 0.16667 | Remote reset done | Close | 0.0072464 |  | 100% |  | 335
589 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-12 | KUD22 | O2R3 | JK | 4.348% | 3806 | HubSafetySystem Batt.Charg.Err | HubSafetySystem Batt.Charg.Err | Breakdown | 0.9625 | 0.9625 | 0.96528 | 0 | 0.066667 | 0.066667 | Remote reset done | Close | 0.0028986 |  | 100% |  | 214
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
1899-12-31
Formulas:
Month = WTG_BD[[#This Row],[Date]]-DAY(WTG_BD[[#This Row],[Date]])+1

## WTG Reactive Power
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28
Date | Financial Year | Calendar Year | Month Year | Reactive Power WTG1 | Reactive Power WTG2 | Reactive Power WTG3 | Reactive Power WTG4 | Reactive Power WTG5 | Reactive Power WTG6 | Reactive Power WTG7 | Reactive Power WTG8 | Reactive Power WTG9 | Reactive Power WTG10 | Reactive Power WTG11 | Reactive Power WTG12 | Reactive Power WTG13 | Reactive Power WTG14 | Reactive Power WTG15 | Reactive Power WTG16 | Reactive Power WTG17 | Reactive Power WTG18 | Reactive Power WTG19 | Reactive Power WTG20 | Reactive Power WTG21 | Reactive Power WTG22 | Reactive Power WTG23 | Total Reactive Power (kVArh)
2025-03-29 | 2025 | 2025 | 2025-03-01 | 15 | 17.3 | 17.3 | 19.1 | 13.4 | 21.4 | 19.9 | 21.4 | 19.6 | 27.4 | 46.4 | 16.2 | 25.9 | 28 | 23.3 | 20.8 | 22.1 | 15 | 16.2 | 22 | 23.1 | 29.7 | 21.3 | 501.8
2025-03-30 | 2025 | 2025 | 2025-03-01 | 47.1 | 36.7 | 51 | 63.2 | 54.3 | 46.9 | 44.5 | 49.3 | 46.4 | 46.5 | 49.7 | 63.2 | 58.1 | 54.7 | 36.4 | 43.9 | 38.7 | 43.3 | 41.1 | 52.8 | 39.6 | 92.7 | 45.5 | 1145.6
2025-03-31 | 2026 | 2025 | 2025-04-01 | 34 | 29.3 | 55.3 | 51.2 | 51.5 | 48 | 39.9 | 37.9 | 48.6 | 33.1 | 47.9 | 40.3 | 36.1 | 40.7 | 26 | 26.9 | 33.8 | 40.2 | 27.9 | 44.4 | 33.9 | 41.2 | 27.7 | 895.8
2025-04-01 | 2026 | 2025 | 2025-04-01 | 53.7 | 48 | 72.9 | 85.7 | 80.1 | 79.9 | 68.4 | 48.5 | 76.8 | 67.2 | 72.4 | 84 | 66.5 | 66.6 | 56.7 | 41.7 | 57.4 | 73 | 74.6 | 79.2 | 56 | 67.5 | 56.6 | 1533.4
2025-04-02 | 2026 | 2025 | 2025-04-01 | 34.2 | 33.8 | 37.2 | 62.8 | 46.1 | 40.7 | 74 | 36.9 | 37.3 | 35.6 | 36.6 | 40.8 | 49.3 | 40.4 | 25.9 | 32.7 | 58.4 | 36.9 | 32.1 | 42.9 | 28.1 | 27.3 | 27.2 | 917.2
2025-04-03 | 2026 | 2025 | 2025-04-01 | 49.9 | 74.5 | 33.2 | 69.7 | 78.1 | 62.9 | 99.4 | 37.6 | 62.9 | 60.6 | 45.7 | 44.5 | 81.9 | 49.8 | 50.5 | 49.1 | 72.8 | 54.7 | 83.9 | 41.3 | 67.6 | 62.3 | 57.3 | 1390.2
2025-04-04 | 2026 | 2025 | 2025-04-01 | 91.8 | 55.9 | 93.8 | 62.6 | 65.9 | 70.4 | 69.3 | 94.5 | 73.9 | 85.4 | 90.5 | 96.6 | 90.2 | 80.8 | 78.9 | 64.4 | 78 | 73.4 | 86.3 | 82.3 | 57.7 | 53.1 | 59.2 | 1754.9
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30.3 | 29.2 | 46.8 | 44.4 | 39.3 | 38.3 | 45 | 37.7 | 16.5 | 32.2 | 31.1 | 27.4 | 57.5 | 29.3 | 22.5 | 54.4 | 36.4 | 29 | 25.9 | 30.6 | 24.8 | 21.1 | 19.4 | 769.1
2025-04-06 | 2026 | 2025 | 2025-04-01 | 40.3 | 59.6 | 59.3 | 51.1 | 58.1 | 43.7 | 54.9 | 51.2 | 48.5 | 49.3 | 49.3 | 37.7 | 31.7 | 47 | 33.1 | 54.4 | 32.3 | 48.4 | 52.3 | 41.6 | 55.2 | 38 | 41 | 1078
2025-04-07 | 2026 | 2025 | 2025-04-01 | 53.7 | 48 | 72.9 | 85.7 | 80.1 | 79.9 | 68.4 | 48.5 | 76.8 | 67.2 | 72.4 | 84 | 66.5 | 66.6 | 56.7 | 41.7 | 57.4 | 73 | 74.6 | 79.2 | 56 | 67.5 | 56.6 | 1533.4
2025-04-08 | 2026 | 2025 | 2025-04-01 | 105.3 | 71.6 | 111 | 94.7 | 83.6 | 96.1 | 99.2 | 115.1 | 85.2 | 98.7 | 87.9 | 100.8 | 78 | 90.8 | 91.4 | 63.8 | 80.9 | 84.5 | 74.3 | 94.4 | 71.8 | 80.4 | 66.8 | 2026.3
2025-04-09 | 2026 | 2025 | 2025-04-01 | 138 | 184.2 | 322.8 | 372.8 | 129.9 | 204.3 | 170.4 | 417.5 | 416.9 | 320.8 | 116 | 288.4 | 167.8 | 125.1 | 106.4 | 426.2 | 144 | 165.4 | 279.8 | 196 | 422.1 | 255.9 | 425 | 5795.7
2025-04-10 | 2026 | 2025 | 2025-04-01 | 121.7 | 65 | 105.5 | 268.9 | 155.2 | 213.3 | 360.8 | 9.2 | 240.5 | 64.6 | 157.5 | 115.6 | 87.6 | 56.3 | 179.6 | 142.3 | 324.2 | 193.7 | 105.2 | 45.7 | 456.3 | 1299.8 | 1.4 | 4769.9
2025-04-11 | 2026 | 2025 | 2025-04-01 | 4742.6 | 4102.9 | 4022.5 | 2750.8 | 3461.5 | 3296.5 | 3563.5 | 4081.6 | 3345.8 | 3444.5 | 3604.7 | 2800.7 | 3154.8 | 3229.9 | 3854.7 | 3818 | 4840.9 | 3976.5 | 3846 | 2878 | 3667 | 4434 | 3554 | 84471.4
2025-04-12 | 2026 | 2025 | 2025-04-01 | 1479.6 | 1763.5 | 479.8 | 1898.3 | 1813 | 1625.3 | 1646.4 | 1022.5 | 1809 | 1510.1 | 1735.2 | 1752.7 | 1871.1 | 1511.3 | 1482.4 | 1783 | 1529.4 | 1282.2 | 1968.9 | 1938.4 | 1638.8 | 1832.5 | 1865.9 | 37239.3
2025-04-13 | 2026 | 2025 | 2025-04-01 | 780 | 271.9 | 1306.2 | 690.6 | 411.9 | 989.8 | 1053.3 | 889.2 | 513.6 | 1073.5 | 378.9 | 527.4 | 513.4 | 813.2 | 804.9 | 101.2 | 275.6 | 214.4 | 68.8 | 228.7 | 217.8 | 498.1 | 237.9 | 12860.3
2025-04-14 | 2026 | 2025 | 2025-04-01 | 406.1 | 614.2 | 1451.1 | 1494 | 732.6 | 1379.5 | 1400.5 | 2087.7 | 917.4 | 1255.4 | 843.9 | 1624.9 | 895.6 | 657 | 306.2 | 760.7 | 231.1 | 769.7 | 499.2 | 619.2 | 574.9 | 673.8 | 669.7 | 20864.4
2025-04-15 | 2026 | 2025 | 2025-04-01 | 1560.9 | 1906.3 | 922 | 1727.8 | 1855.1 | 1446.9 | 1699.8 | 295.1 | 2305.3 | 605.9 | 907.5 | 1115.3 | 1246.6 | 1115.4 | 1219.7 | 2086.1 | 2216.6 | 2238.9 | 172.6 | 928.9 | 1873.2 | 2219.7 | 2197 | 33862.6
2025-04-16 | 2026 | 2025 | 2025-04-01 | 668.4 | 2044 | 509.6 | 2134.6 | 2219.4 | 1801.4 | 1945.6 | 2738.5 | 2262.6 | 30.3 | 3024.2 | 455.8 | 404.1 | 288.9 | 337.8 | 1968.5 | 2546.7 | 1178.3 | 297.7 | 217.7 | 2460.6 | 1393.7 | 1792.3 | 32720.7
2025-04-17 | 2026 | 2025 | 2025-04-01 | 734.3 | 2149 | 1019.1 | 2060.6 | 2358.9 | 2030.9 | 2008.2 | 1102.1 | 2035.1 | 1784.7 | 1370.3 | 1241.4 | 1656.4 | 1332.7 | 1721.9 | 1882 | 2080.2 | 2658 | 2061 | 1654.7 | 1974.6 | 2408.6 | 2270 | 41594.7
2025-04-18 | 2026 | 2025 | 2025-04-01 | 2195.6 | 2744.6 | 2387.6 | 2821 | 3000.8 | 2767.4 | 2822.4 | 136.7 | 3045.3 | 2298.5 | 2138.6 | 2331.8 | 2305.7 | 2413.7 | 2292.7 | 2568.1 | 2802.7 | 2672.6 | 2595.1 | 2349.7 | 2585.2 | 2319.7 | 2702 | 56297.5
2025-04-19 | 2026 | 2025 | 2025-04-01 | 755.1 | 1373.2 | 300.6 | 665.1 | 1483.9 | 1007.9 | 1133.2 | 2286.2 | 1461.3 | 521.1 | 1986.2 | 754.4 | 455.1 | 694.8 | 649.2 | 1225 | 1537.6 | 2024.3 | 632.5 | 340.9 | 1396.3 | 1576.8 | 1382 | 25642.7
2025-04-20 | 2026 | 2025 | 2025-04-01 | 2528.1 | 1650.6 | 1205.6 | 912.7 | 1033.2 | 1067 | 2449.5 | 1135.1 | 918.2 | 540.8 | 479.4 | 428.2 | 51 | 213.2 | 332.6 | 1396.5 | 3176.5 | 553.6 | 18.9 | 288.6 | 2869.2 | 2047 | 2044 | 27339.5
2025-04-21 | 2026 | 2025 | 2025-04-01 | 4314 | 4605.1 | 5507.4 | 4224.2 | 3959.6 | 5662.5 | 3005.7 | 5204.8 | 4091 | 4781.6 | 4938.3 | 4570.6 | 4293.1 | 3649.1 | 4895.2 | 4795.1 | 4052 | 4160.7 | 3697.4 | 4342.2 | 3557.8 | 3441.7 | 5115.7 | 100864.8
2025-04-22 | 2026 | 2025 | 2025-04-01 | 2365 | 98.8 | 1091.2 | 250.5 | 179.7 | 494.9 | 430 | 907.2 | 35.5 | 1428.6 | 612.9 | 569.4 | 1283.9 | 988 | 2295 | 280.4 | 186.2 | 12.8 | 866.8 | 1258.5 | 426.7 | 110 | 225.6 | 16397.6
2025-04-23 | 2026 | 2025 | 2025-04-01 | 411.4 | 976.2 | 70.8 | 493.5 | 1158.1 | 274.9 | 241 | 199.8 | 875.3 | 361.5 | 584.3 | 621.5 | 375.2 | 378.1 | 263 | 949.6 | 830.3 | 1425 | 69.3 | 468.3 | 914.9 | 1344.3 | 896.6 | 14182.9
2025-04-24 | 2026 | 2025 | 2025-04-01 | 3024.1 | 425.1 | 2700.8 | 1620.7 | 505.4 | 2080.2 | 2183 | 1941.2 | 582.1 | 3034.4 | 2059 | 3261.2 | 2884.9 | 2855.6 | 2816.6 | 274.8 | 517.4 | 416.5 | 911.9 | 2873 | 369.2 | 152.9 | 126.5 | 37616.5
2025-04-25 | 2026 | 2025 | 2025-04-01 | 5017.4 | 1786.6 | 3001.7 | 1641.6 | 1482.9 | 1923.8 | 2337.6 | 2655.9 | 1341 | 3852.8 | 2889.4 | 3642.3 | 3508.3 | 3650.6 | 4697.2 | 2263.2 | 2252.3 | 1309.8 | 1820 | 3929 | 1688.2 | 1022.7 | 1697.7 | 59412
2025-04-26 | 2026 | 2025 | 2025-04-01 | 6129.6 | 2178.3 | 4920.7 | 2235.1 | 1905.6 | 2417.5 | 2443.4 | 4599 | 2199.9 | 4895.2 | 4535.8 | 5590.2 | 5631 | 5169.4 | 6077.9 | 2228.7 | 2384.9 | 1960.7 | 5112.3 | 4821.1 | 2146.6 | 2032.9 | 2085 | 83700.8
2025-04-27 | 2026 | 2025 | 2025-04-01 | 7238.3 | 4102.5 | 6021.2 | 3152.3 | 3552.9 | 3873.2 | 3754.7 | 6558.8 | 3804.9 | 6823.7 | 6092.7 | 5985 | 6992.2 | 6766.3 | 7123.2 | 4392.4 | 4318.9 | 3601.3 | 6916.3 | 5817.8 | 4332 | 3713.7 | 4387.3 | 119321.6
2025-04-28 | 2026 | 2025 | 2025-04-01 | 4672.1 | 3060.6 | 4032.3 | 3158.3 | 3045.5 | 4134.3 | 3769.7 | 4429 | 4044.3 | 4130 | 4180.2 | 4328.6 | 4165.4 | 3632.5 | 4329.6 | 2838.1 | 3277.8 | 2900.7 | 3914.7 | 3288.6 | 3037.4 | 3019.7 | 2497.4 | 83886.8
2025-04-29 | 2026 | 2025 | 2025-04-01 | 3385.3 | 2482.5 | 3755.5 | 1345.5 | 1275.1 | 2202.6 | 2575.1 | 3315.2 | 2211.1 | 3078 | 2844.3 | 2272.4 | 2377.6 | 2833.4 | 3367.1 | 2571.3 | 2328.5 | 1356.2 | 2233.8 | 3284.9 | 1791.4 | 1428.3 | 1836.4 | 56151.5
2025-04-30 | 2026 | 2025 | 2025-05-01 | 618.1 | 156.4 | 688.8 | 445.4 | 46.3 | 572.3 | 563 | 456.1 | 2744.3 | 357.5 | 736.5 | 763.7 | 359.6 | 3228.2 | 452.7 | 182.6 | 28.9 | 188.9 | 29 | 401.2 | 139.4 | 94 | 9.4 | 13262.3
2025-05-01 | 2026 | 2025 | 2025-05-01 | 1285.9 | 742.6 | 850.3 | 744 | 375.9 | 773.1 | 701.9 | 773.7 | 438.5 | 815.2 | 897.4 | 347.4 | 324.1 | 449.5 | 575.7 | 598.1 | 754.7 | 576.7 | 376.6 | 828.6 | 867 | 694.9 | 364.8 | 15156.6
2025-05-02 | 2026 | 2025 | 2025-05-01 | 371.8 | 183.7 | 766.7 | 637.5 | 306.6 | 553.3 | 763.7 | 406.8 | 407.3 | 1141.7 | 655.1 | 145.8 | 137.9 | 1800.2 | 87.6 | 116.1 | 17.5 | 67.2 | 308.1 | 126.5 | 219.4 | 124.9 | 216.3 | 9561.7
2025-05-03 | 2026 | 2025 | 2025-05-01 | 465.2 | 375.3 | 1250.8 | 1548.8 | 709.8 | 1316.2 | 1031.9 | 989.2 | 762.7 | 957.6 | 1224.7 | 1436.3 | 1044 | 1029.6 | 499.4 | 447.1 | 548.2 | 523.6 | 749 | 1288.6 | 781.4 | 548.7 | 483.6 | 20011.7
2025-05-04 | 2026 | 2025 | 2025-05-01 | 4672.1 | 3060.6 | 4032.3 | 3158.3 | 3045.5 | 4134.3 | 3769.7 | 4429 | 4044.3 | 4130 | 4180.2 | 4328.6 | 4165.4 | 3632.5 | 4329.6 | 2838.1 | 3277.8 | 2900.7 | 3914.7 | 3288.6 | 3037.4 | 3019.7 | 2497.4 | 83886.8
2025-05-05 | 2026 | 2025 | 2025-05-01 | 347.7 | 460.5 | 1101.7 | 438.2 | 78.2 | 590.8 | 610 | 453.3 | 165.4 | 813.4 | 473.1 | 417.9 | 129.7 | 468.4 | 1.7 | 271.9 | 1 | 299.8 | 331.4 | 2615.7 | 444.5 | 75.8 | 275.8 | 10865.9
2025-05-06 | 2026 | 2025 | 2025-05-01 | 763.5 | 223.1 | 2403.8 | 1246.7 | 601.6 | 1329.1 | 1415.6 | 2082.1 | 402 | 1786 | 1596.9 | 1582.3 | 1030.2 | 1079.9 | 216.6 | 558.1 | 159.6 | 3398 | 510.9 | 873.4 | 322 | 44 | 121.3 | 23746.7
2025-05-07 | 2026 | 2025 | 2025-05-01 | 321.5 | 132.1 | 57 | 602.2 | 339.2 | 159.7 | 214.2 | 242.9 | 660 | 1394.2 | 327.1 | 325.3 | 432.6 | 345.7 | 524.3 | 328.7 | 282.1 | 399.1 | 343 | 331.2 | 208 | 467 | 229.6 | 8666.7
2025-05-08 | 2026 | 2025 | 2025-05-01 | 3538.6 | 3436.6 | 0 | 3605.5 | 3350.8 | 3113.1 | 2967.2 | 2915.1 | 3487.4 | 42.4 | 2841.2 | 3102 | 3394.6 | 3210.1 | 3777.8 | 3547.6 | 3592.6 | 3637.8 | 3460.5 | 3441.6 | 3418.4 | 3452.7 | 3620.2 | 70953.8
2025-05-09 | 2026 | 2025 | 2025-05-01 | 1758.5 | 1667.8 | 1088.8 | 1244.6 | 1300.3 | 1405.5 | 1313 | 1620.2 | 1496.1 | 1547.9 | 1202.9 | 1557.7 | 1384.6 | 1391.5 | 340.7 | 1654.9 | 1517.2 | 36.8 | 1580.5 | 1114 | 1333.2 | 1360.4 | 1183.4 | 30100.5
2025-05-10 | 2026 | 2025 | 2025-05-01 | 89.4 | 1554.3 | 1486.5 | 1505.7 | 1828 | 1778.4 | 1771.7 | 1396.4 | 1942.6 | 1747.6 | 1686.1 | 1538.1 | 1655.8 | 1869.9 | 1597.7 | 1481.5 | 1552.3 | 1668 | 2003.2 | 1648.3 | 392.2 | 1678.9 | 1621.5 | 35494.1
2025-05-11 | 2026 | 2025 | 2025-05-01 | 2162.1 | 2101.8 | 1599.6 | 2083.4 | 2932 | 1527.5 | 1387.5 | 1791.1 | 2057.9 | 1684 | 380.2 | 2129.1 | 1468.1 | 644.5 | 1995.3 | 2512.3 | 1896.1 | 2390 | 2597 | 1734.5 | 2230.4 | 2371.5 | 2088.9 | 43764.8
2025-05-12 | 2026 | 2025 | 2025-05-01 | 2913.2 | 3105.7 | 2690.5 | 2926.3 | 3055.9 | 2898.2 | 2810.1 | 2646.9 | 3211.4 | 2520.9 | 3077.5 | 3448.7 | 3206 | 3010.7 | 3004.2 | 890.8 | 2874.1 | 3184.8 | 3084.3 | 3172.3 | 2983.7 | 3154.4 | 3242.9 | 67113.5
2025-05-13 | 2026 | 2025 | 2025-05-01 | 6129.6 | 2178.3 | 4920.7 | 2235.1 | 1905.6 | 2417.5 | 2443.4 | 4599 | 2199.9 | 4895.2 | 4535.8 | 5590.2 | 5631 | 5169.4 | 6077.9 | 2228.7 | 2384.9 | 1960.7 | 5112.3 | 4821.1 | 2146.6 | 2032.9 | 2085 | 83700.8
2025-05-14 | 2026 | 2025 | 2025-05-01 | 358.9 | 337.5 | 1182.4 | 184.7 | 317.3 | 300.1 | 765.1 | 579.7 | 132.4 | 266.1 | 39.3 | 77.1 | 59.2 | 227.7 | 304.2 | 271.4 | 735.2 | 371.3 | 885.5 | 371.8 | 271.7 | 298.5 | 100.7 | 8437.8
2025-05-15 | 2026 | 2025 | 2025-05-01 | 4334.4 | 4106 | 4518.9 | 3680.3 | 4100.3 | 4096 | 4293.9 | 4179.4 | 3958.4 | 4346.2 | 4234.7 | 4138.8 | 4053 | 3960.2 | 4559.1 | 4434.3 | 4519.6 | 4160 | 4054.4 | 4793.3 | 3820.5 | 4061.6 | 3982.9 | 96386.2
2025-05-16 | 2026 | 2025 | 2025-05-01 | 8286.6 | 6224.6 | 6000.1 | 5316.6 | 5529.6 | 5981.4 | 5344.8 | 5811.5 | 5448.4 | 6144 | 5149.4 | 5901.2 | 5731.3 | 5624.1 | 8697.7 | 6776.6 | 6798.1 | 5908.3 | 5586 | 5533.5 | 6777.2 | 5824.4 | 6026.2 | 140421.6
2025-05-17 | 2026 | 2025 | 2025-05-01 | 4930.8 | 4753.3 | 4569.5 | 3980 | 4529.6 | 3705.3 | 4725.8 | 4757.3 | 3776.6 | 4767.7 | 4440.4 | 4102.1 | 4303.9 | 4386.2 | 5536.7 | 4914.6 | 5463.4 | 4823.4 | 4540.9 | 4112.8 | 4802.8 | 4306.7 | 6424.6 | 106654.4
2025-05-18 | 2026 | 2025 | 2025-05-01 | 6410.8 | 1989.2 | 4659 | 1070.9 | 1823.7 | 1421.7 | 1434.2 | 5284 | 1948.1 | 4610.2 | 4869.3 | 4835.3 | 5265.5 | 4824.5 | 6154.2 | 2378.6 | 2108.4 | 2181.4 | 6899.5 | 4590.3 | 2459.7 | 2338.9 | 2006.7 | 81564.1
2025-05-19 | 2026 | 2025 | 2025-05-01 | 5304.6 | 6897.6 | 4109.7 | 2849.5 | 4814 | 4320.5 | 4457.7 | 4361.8 | 5161.7 | 4249.3 | 4793.1 | 4480.4 | 4590.4 | 4378.3 | 6010.6 | 6665.2 | 6572.4 | 4520.1 | 4814.3 | 3767.3 | 5677.1 | 5230.7 | 5804.9 | 113831.2
2025-05-20 | 2026 | 2025 | 2025-05-01 | 4382.4 | 6682.1 | 4631.2 | 5708.6 | 5566 | 5238.1 | 5191.2 | 4636.3 | 5728.8 | 4459.7 | 4158.2 | 3922.4 | 3904.2 | 4116.3 | 5261.8 | 6866.7 | 6713.9 | 5755 | 4497.4 | 4212.9 | 6176.9 | 6014.8 | 6020.7 | 119845.6
2025-05-21 | 2026 | 2025 | 2025-05-01 | 6197.5 | 5626.5 | 5440.6 | 5376.4 | 5090.4 | 5492.3 | 5014.9 | 4858.5 | 5389.2 | 4870 | 5481.2 | 5749.7 | 5322.6 | 5279.9 | 5680.1 | 5939.7 | 5558.4 | 4450.8 | 4700.2 | 5437.9 | 5469.8 | 4876.4 | 6558 | 123861
2025-05-22 | 2026 | 2025 | 2025-05-01 | 8115.6 | 7163.1 | 7316.1 | 7016.1 | 7143.7 | 6963.3 | 6815.6 | 7390.3 | 6947.9 | 7540.3 | 7363.3 | 7252.6 | 7550.3 | 7372.3 | 7482.1 | 7151.2 | 7174.3 | 7113.3 | 7537.3 | 7487.6 | 7141 | 7012.1 | 7115.2 | 167164.6
2025-05-23 | 2026 | 2025 | 2025-05-01 | 4178.1 | 3543.2 | 3568.7 | 3385.6 | 3407.7 | 3603.9 | 3431.4 | 3516.1 | 3867.7 | 3705.4 | 3649.1 | 3783.4 | 3547.2 | 3579.5 | 3461.7 | 3685.1 | 3589.9 | 3170 | 4185.4 | 3478.8 | 3624.6 | 3617.2 | 3383.7 | 82963.4
2025-05-24 | 2026 | 2025 | 2025-05-01 | 1043.7 | 1043.8 | 1533.7 | 1210.2 | 1073.3 | 1514.4 | 1432.3 | 1630.9 | 844.2 | 1125.6 | 1404.9 | 1254.2 | 1657.7 | 1103.5 | 1378.6 | 1017.9 | 864.4 | 1616.9 | 1597.9 | 1376.1 | 1013.6 | 1196.8 | 1150.3 | 29084.9
2025-05-25 | 2026 | 2025 | 2025-05-01 | 2846.7 | 2895.3 | 3081.1 | 3335.9 |  | 2840 | 2670.9 | 2150.2 | 3130.3 | 2607.6 | 3077.5 | 3044.6 | 2704.6 | 2779.5 | 2477.3 | 2813.7 | 2954.3 | 2842.1 | 2092.4 | 3357.4 | 3065.7 | 2933.7 | 2594.6 | 62295.4
2025-05-26 | 2026 | 2025 | 2025-05-01 | 1624.2 | 985 | 844.9 | 434.1 | 849.9 | 1231 | 1224.9 | 2011.7 | 1262.8 | 1630.6 | 391.3 | 1226.7 | 1671 | 964.6 | 2122.9 | 1460.1 | 1517.3 | 920.9 | 1860.3 | 1107.6 | 802.2 | 1640.1 | 1105.9 | 28890
2025-05-27 | 2026 | 2025 | 2025-05-01 | 3533.8 | 4933.3 | 5105.5 | 4695.5 | 3357.5 | 4296 | 3769.8 | 3483.3 | 4613.4 | 3724 | 4593.7 | 4076.1 | 3804.7 | 4602.4 | 3968.5 | 3804.3 | 3697.8 | 3647.1 | 3812.8 |  |  |  |  | 77519.5
2025-05-28 | 2026 | 2025 | 2025-05-01 | 14348.2 | 5655.6 | 4910.1 | 6325.5 | 5915.5 | 4793.5 | 5059.4 | 4493.6 | 6671.9 | 4744.6 | 5008.8 | 4553.3 | 4017.7 | 4545.7 | 3661.2 | 5388.5 | 5268.4 | 4671.5 | 4149.3 | 4511.6 | 5919.6 | 5626.9 | 5287.8 | 125528.2
2025-05-29 | 2026 | 2025 | 2025-05-01 | 3756.5 | 3593.4 | 4025.9 | 2789 | 2568.8 | 2570.3 | 2507.2 | 3770.7 | 2809.8 | 4107.7 | 3978.3 | 3892.2 | 3864.1 | 3840.5 | 3502.9 | 1939.9 | 2524.6 | 2680.2 | 3408.5 | 3817.7 | 2473.9 | 2264.9 | 2152.3 | 72839.3
2025-05-30 | 2026 | 2025 | 2025-05-01 | 913.5 | 943.3 | 1501.3 | 1019.8 | 973.1 | 1389.3 | 1494.2 | 1171.3 | 1043.4 | 1712.1 | 1247 | 1233.3 | 1667.9 | 1273.6 | 1427.7 | 864.7 | 770.1 | 1009.1 | 1296.1 | 1194 | 1039.2 | 879.7 | 1087.6 | 27151.3
2025-05-31 | 2026 | 2025 | 2025-06-01 | 5413.6 | 4838.7 | 4742.3 | 4254.4 | 3626 | 4142.5 | 4223.2 | 5008 | 3618.8 | 4498 | 4596.4 | 4730.4 | 4761.4 | 4250 | 5616.6 | 5302.3 | 5107.8 | 4171.7 | 4610.5 | 4359.9 | 4825.2 | 5094.6 | 5264.6 | 107056.9
2025-06-01 | 2026 | 2025 | 2025-06-01 | 2021.9 | 3037.8 | 2143.2 | 2212.5 | 2097.9 | 2048.9 | 2056.9 | 2111.6 | 1752.3 | 2576.8 | 1869.7 | 1449.4 | 1586.7 | 1569.3 | 2079 | 2823 | 2705.1 | 2298.5 | 1902.1 | 1763.1 | 2593.1 | 1972.3 | 2332 | 49003.1
2025-06-02 | 2026 | 2025 | 2025-06-01 | 5126.4 | 5336 | 4788.6 | 5116.8 | 5288.7 | 5157.9 | 4815.7 | 4877 | 5331.2 | 4857.7 | 4728.7 | 4705.1 | 4479.1 | 4537.4 | 4659 | 5383.3 | 5373 | 5177.2 | 4429.1 | 4669.2 | 5251.7 | 5330.3 | 5322.8 | 114741.9
2025-06-03 | 2026 | 2025 | 2025-06-01 | 8012.8 | 7088.5 | 7519.6 | 6348.4 | 7178.5 | 7242.8 | 7250.7 | 7196.9 | 7195.1 | 7504.3 | 7539.5 | 6613.7 | 7520.7 | 7595 | 7019.5 | 6673.4 | 6777.5 | 6923.7 | 7477.1 | 7080.2 | 6660.3 | 6761.7 | 6620.5 | 163800.4
2025-06-04 | 2026 | 2025 | 2025-06-01 | 4715.5 | 4847.3 | 4263.6 | 5484.9 | 4634 | 4692.1 | 4707.4 | 4276.7 | 4879.4 | 4816 | 4586.1 | 4746.8 | 4569.4 | 4672.7 | 4815.9 | 4791.7 | 4778.4 | 4664.2 | 4641.2 | 4706 | 4688.2 | 3525.1 | 4690.7 | 107193.3
2025-06-05 | 2026 | 2025 | 2025-06-01 | 8011.7 | 7130.8 | 7526.8 | 6271.2 | 6634.4 | 6943 | 6733.1 | 7641.5 | 6281.8 | 7764.6 | 7402.6 | 7081.8 | 6553.5 | 7206.3 | 7847.2 | 7029.7 | 7021.9 | 6548.4 | 7327.9 | 6438.7 | 6710.1 | 5154.8 | 6620.1 | 159881.9
2025-06-06 | 2026 | 2025 | 2025-06-01 | 7084.3 | 3244.1 | 3215.2 | 3291 | 3392.9 | 3015.7 | 2821.3 | 3156.1 | 3096.7 | 3119.7 | 3273.9 | 2809.4 | 3215.2 | 3253.8 | 3416.2 | 3374.1 | 3808.5 | 3159 | 3178.1 | 8299.1 | 3506 | 3224.8 | 3345.1 | 83300.2
2025-06-07 | 2026 | 2025 | 2025-06-01 | 2964.9 | 153.2 | 2679.1 | 2428.1 | 2264.8 | 2286.4 | 2220.4 | 2083.3 | 2083.3 | 1701.5 | 1817 | 2495.1 | 2550.2 | 2157.5 | 2183.2 | 1835.9 | 1885.4 | 2131.1 | 2324.4 | 2040.1 | 1928.4 | 2053.9 | 1999.8 | 48267
2025-06-08 | 2026 | 2025 | 2025-06-01 | 1456.1 | 1096.5 | 1250.8 | 824.2 | 827.4 | 904.7 | 1005 | 1244 | 910.3 | 829.7 | 974.7 | 1048.2 | 1041.1 | 931.4 | 1135.7 | 1100.9 | 1007.1 | 895.2 | 988 | 836.7 | 939.9 | 957 | 1057.9 | 23262.5
2025-06-09 | 2026 | 2025 | 2025-06-01 | 4863.2 | 1378.5 | 5576.9 | 703.6 | 1106.4 | 1080 | 1163.5 | 5335.8 | 1226.1 | 5370.9 | 5372.3 | 4778.4 | 4662.1 | 5349.3 | 4615 | 1320.6 | 1199.4 | 1126.7 | 5376.5 | 5412.6 | 1200.7 | 1285.2 | 1194.2 | 70697.9
2025-06-10 | 2026 | 2025 | 2025-06-01 | 2873 | 3247 | 3393.6 | 3120.1 | 3462.9 | 3323 | 3514.8 | 2747.1 | 3264 | 3278.2 | 3600.5 | 4037.2 | 3510.5 | 3485.1 | 2998.4 | 3272.7 | 3033 | 3297.6 | 3286.4 | 3381.4 | 2852.4 | 3278.6 | 2967.5 | 75225
2025-06-11 | 2026 | 2025 | 2025-06-01 | 8918.7 | 8067.4 | 7866.2 | 7522.4 | 7902.1 | 7732.5 | 7656.4 | 7968.8 | 7936.7 | 8024.6 | 7912.3 | 7906.9 | 8125.8 | 7993.2 | 8134.9 | 8087.5 | 8064.4 | 7894.2 | 8138.1 | 7785.8 | 7949.3 | 8000.6 | 7984.5 | 183573.3
2025-06-12 | 2026 | 2025 | 2025-06-01 | 13065.6 | 11542.6 | 12377.8 | 11076 | 11297.9 | 11540.8 | 11536 | 12613.7 | 10168.2 | 12235.6 | 12073.8 | 12100.3 | 12129.2 | 11105.5 | 12403.1 | 11566.2 | 11645.1 | 11415.1 | 12194 | 11767.2 | 11569.1 | 11402.7 | 11473.3 | 270298.8
2025-06-13 | 2026 | 2025 | 2025-06-01 | 21.4 | 1.8 | 1.8 | 1.5 | 1.9 | 1.4 | 1.7 | 1.2 | 1.5 | 1.7 | 1.8 | 1.9 | 1.3 | 1.3 | 1.4 | 1.4 | 1.2 | 1.5 | 1.6 | 1.8 | 1.8 | 1.2 | 2 | 56.1
2025-06-14 | 2026 | 2025 | 2025-06-01 | 3091.2 | 3233.1 | 4022 | 3044.9 | 2993.7 | 3537.9 | 3341.3 | 3961.2 | 2916.8 | 3551 | 3517.7 | 3306.5 | 3947 | 3000.1 | 3485.6 | 2984.1 | 3089.2 | 3374 | 3120.7 | 3503.5 | 3419.5 | 3417.3 | 3107.1 | 76965.4
2025-06-15 | 2026 | 2025 | 2025-06-01 | 4740.7 | 4409.9 | 5427.3 | 4523.8 | 4386.7 | 5085.1 | 5016.5 | 5354 | 4485.7 | 4822.1 | 5158 | 4959.9 | 5343.8 | 4785.6 | 4709.8 | 4358.3 | 4230.3 | 4651.9 | 4613.7 | 4914.7 | 4301 | 4386.6 | 4338 | 109003.4
2025-06-16 | 2026 | 2025 | 2025-06-01 | 8078.7 | 7245.7 | 9019.8 | 7095.7 | 7272.1 | 8297.1 | 8298.9 | 9307.4 | 7219.6 | 8194.6 | 8423 | 7974.2 | 8823.7 | 8074.6 | 7886.9 | 7180.1 | 6959 | 8078.6 | 8188.6 | 7876.2 | 7167.3 | 7340.5 | 7240.6 | 181242.9
2025-06-17 | 2026 | 2025 | 2025-06-01 | 347.7 | 593 | 156.4 | 394.7 | 477.4 | 363.6 | 354.6 | 379.1 | 408.5 | 449.6 | 328.7 | 224.8 | 388.1 | 347.3 | 508 | 483 | 636.7 | 407.2 | 403.7 | 277.4 | 513.2 | 435.3 | 571.6 | 9449.6
2025-06-18 | 2026 | 2025 | 2025-06-01 | 183.3 | 1.8 | 9.5 | 3.2 | 4.4 | 2.6 | 3.6 | 2.9 | 2.6 | 3.9 | 4.6 | 3.8 | 3.4 | 4.2 | 4.9 | 3.2 | 2.2 | 3.5 | 5 | 3.7 | 3.5 | 1.3 | 5.7 | 266.8
2025-06-19 | 2026 | 2025 | 2025-06-01 | 1880.7 | 1824.2 | 2162.9 | 1959.1 | 1863.8 | 2025.7 | 2043.8 | 2146 | 1809.3 | 2031.9 | 2029.9 | 1995.8 | 1964.5 | 1929.7 | 1931.9 | 1754.7 | 1647.5 | 1874.7 | 1876.2 | 2003.3 | 1837.2 | 1770.6 | 1766.1 | 44129.5
2025-06-20 | 2026 | 2025 | 2025-06-01 | 186.4 | 306.3 | 354.5 | 375.2 | 190.9 | 297.4 | 42.5 | 92.9 | 340.7 | 194.6 | 131.9 | 199.7 | 94.4 | 108.6 | 323 | 31 | 81.4 | 107.9 | 152.9 | 265.2 | 87.1 | 217.2 | 92.4 | 4274.1
2025-06-21 | 2026 | 2025 | 2025-06-01 | 592.1 | 2.3 | 401.6 | 1046.9 | 293.4 | 52.9 | 16.9 | 14.1 | 602.6 | 737.4 | 405.6 | 527.5 | 66.8 | 319.3 | 305.2 | 180.5 | 206.1 | 159.1 | 420.1 | 505.3 | 246.1 | 473.1 | 187.1 | 7762
2025-06-22 | 2026 | 2025 | 2025-06-01 | 1752.2 | 1009.3 | 1177.5 | 1263.6 | 965 | 1209.1 | 1230.5 | 1634.7 | 1777.3 | 1110.1 | 1149.9 | 2115.2 | 1505.4 | 1434.8 | 1756 | 1592.5 | 1434.7 | 1210 | 1468.2 | 1427.4 | 1591.8 | 1651.7 | 1535.4 | 33002.3
2025-06-23 | 2026 | 2025 | 2025-06-01 | 3186.8 | 2621.5 | 3304.7 | 2678.3 | 2673 | 2919.1 | 3086.7 | 3464.2 | 2813.2 | 2794.2 | 3012.4 | 2976.7 | 3692.5 | 2797.7 | 3358.2 | 2927.1 | 2831.9 | 2725.9 | 3213.7 | 2874.5 | 2171 | 3102.7 | 2691.3 | 67917.3
2025-06-24 | 2026 | 2025 | 2025-06-01 | 3551.5 | 3146.9 | 3667.3 | 2559.2 | 3160.6 | 3659.1 | 3652.6 | 4073.6 | 2813.9 | 3565.9 | 3517.3 | 3390.4 | 3840.9 | 3367.1 | 3750.8 | 3114.5 | 3086.9 | 3276.5 | 3223.2 | 3177.2 | 2979.2 | 3120.2 | 3199.2 | 76894
2025-06-25 | 2026 | 2025 | 2025-06-01 | 3457.6 | 2855.7 | 3241 | 2420.3 | 2748.2 | 3113 | 2342.9 | 3508 | 2680.3 | 3134 | 2799.5 | 3013.8 | 3212.4 | 2908.5 | 3741.1 | 3304.4 | 3194.5 | 3383.1 | 3132.1 | 2661.5 | 2801.5 | 3276.1 | 3276.7 | 70206.2
2025-06-26 | 2026 | 2025 | 2025-06-01 | 4532.9 | 4088.1 | 4806.7 | 4589.1 | 4158.9 | 4391.1 | 4282.9 | 5126.2 | 3828.6 | 4420.7 | 4543.5 | 4754.7 | 4687.1 | 4325.4 | 4691.1 | 4248.2 | 4191.6 | 4529.2 | 4240.3 | 4785.8 | 4517.1 | 4443.2 | 4420.5 | 102602.9
2025-06-27 | 2026 | 2025 | 2025-06-01 | 1364 | 1463.2 | 2037 | 763.5 | 974.4 | 647.5 | 639.4 | 2039.2 | 872.1 | 1718.4 | 1622.7 | 1895.6 | 2007.9 | 1709.8 | 1863.9 | 1181.4 | 1422.2 | 1075.3 | 1557.7 | 1635 | 1489.4 | 1059 | 1408.3 | 32446.9
2025-06-28 | 2026 | 2025 | 2025-06-01 | 312.6 | 445.7 | 105.5 | 484.3 | 692.9 | 265.6 | 69.8 | 480.5 | 614.2 | 79.3 | 194.1 | 430.4 | 461.5 | 400.1 | 191.5 | 4776.2 | 431.2 | 52.7 | 271.9 | 593.2 | 219.8 | 166.2 | 446.2 | 12185.4
2025-06-29 | 2026 | 2025 | 2025-06-01 | 25.1 | 6.6 | 1.7 | 6.6 | 6.8 | 6.9 | 7.9 | 4.9 | 7.3 | 4.5 | 5.6 | 6 | 5 | 4.3 | 5.2 | 6.1 | 1.5 | 7.1 | 4.2 | 2.7 | 6.6 | 3.7 | 8 | 144.3
2025-06-30 | 2026 | 2025 | 2025-07-01 | 1293.9 | 1526.2 | 1783.2 | 852.4 | 1409.4 | 1881.5 | 1926.3 | 2105 | 1004.5 | 1748.8 | 1693.5 | 1498.8 | 2070.9 | 1570.7 | 1789.9 | 1453.1 | 1511.4 | 1409.6 | 1212.7 | 1373 | 1377 | 1303 | 1537.8 | 35332.6
2025-07-01 | 2026 | 2025 | 2025-07-01 | 401.5 | 677.3 | 1548.9 | 716.7 | 685.3 | 1556.8 | 1473 | 1519.2 | 1063 | 1036 | 1287.5 | 1729.4 | 1401.1 | 1223 | 1031.6 | 827.4 | 697.2 | 851.6 | 831 | 1317.7 | 823.8 | 795.6 | 584 | 24078.6
2025-07-02 | 2026 | 2025 | 2025-07-01 | 4666.5 | 4572.8 | 5460.9 | 4397.6 | 4500.4 | 4992 | 5155.2 | 5366.5 | 4455.9 | 5255.8 | 5095.9 | 5240.3 | 5018.6 | 4918.6 | 4812.4 | 4505.9 | 4237.7 | 4877 | 4691.8 | 4834.2 | 4559.3 | 4607.7 | 4452.2 | 110675.2
2025-07-03 | 2026 | 2025 | 2025-07-01 | 747.8 | 811.2 | 1262.4 | 1189.3 | 1139.8 | 901.7 | 860.7 | 650 | 1323.5 | 1296.2 | 1166.2 | 1106.5 | 1042.5 | 1083.6 | 271.7 | 432.1 | 631.3 | 1093.9 | 1135.9 | 1072 | 998.5 | 874.7 | 875.3 | 21966.8
2025-07-04 | 2026 | 2025 | 2025-07-01 | 2013.3 | 1925.7 | 1613.8 | 2018.4 | 1900 | 2146.5 | 2132.4 | 2105.7 | 1725.6 | 1490 | 1951 | 1882.7 | 2299.5 | 1720.8 | 2292.5 | 2083.8 | 1997.6 | 1994.6 | 2010.7 | 1843 | 1834.4 | 2132 | 2224.6 | 45338.6
2025-07-05 | 2026 | 2025 | 2025-07-01 | 3683.9 | 3465 | 3570.9 | 2943.3 | 3339.8 | 3493.4 | 3584.3 | 3736.9 | 3030.3 | 3446 | 3533.5 | 3606.7 | 3795.9 | 3573.6 | 4148.3 | 3645.3 | 3607 | 3737.8 | 3326.1 | 3388.4 | 3607 | 3340.4 | 3640.9 | 81244.7
2025-07-06 | 2026 | 2025 | 2025-07-01 | 7592.9 | 6755.8 | 8481.8 | 6861.2 | 6797.8 | 7899.8 | 7860.1 | 8720.6 | 6914 | 7817.4 | 7864.2 | 7595.8 | 8088.8 | 7555.7 | 7346.3 | 6696.5 | 6570.4 | 7099.4 | 7337.9 | 7152 | 6647.4 | 7000.9 | 6668.2 | 169324.9
2025-07-07 | 2026 | 2025 | 2025-07-01 | 3111.4 | 2443 | 3255.1 | 2451.8 | 2627.8 | 3353.6 | 3314.6 | 3516.2 | 2531.9 | 2932.9 | 3004.5 | 2946.2 | 3235.7 | 2859.8 | 3138.4 | 2786.7 | 2761.1 | 2823.6 | 2895.2 | 2839 | 2460.5 | 2859 | 2567.5 | 66715.5
2025-07-08 | 2026 | 2025 | 2025-07-01 | 26.4 | 361.5 | 699.7 | 543.3 | 606.3 | 1018.8 | 1148.1 | 1091.8 | 542.8 | 679.2 | 940.6 | 838.9 | 1189.1 | 835.6 | 698.1 | 561.6 | 198.1 | 788.3 | 881.2 | 833.2 | 494 | 613.2 | 517.1 | 16106.9
2025-07-09 | 2026 | 2025 | 2025-07-01 | 2215.7 | 2197.7 | 3028.2 | 3066.9 | 2091.9 | 2855.9 | -515.3 | 3036.2 | 2203.5 | 2416 | 2542.4 | 2901.7 | 2965.7 | 2367.1 | 2543.8 | 2313.9 | 2014.9 | 2071.7 | 2557.6 | 2611 | 2118.5 | 2451.1 | 2155.2 | 54211.3
2025-07-10 | 2026 | 2025 | 2025-07-01 | 1370.5 | 1057.7 | 1932.7 | 1573 | 1226.3 | 1555.5 | 1480.7 | 1831.9 | 1388.2 | 1681.9 | 1550.9 | 1984.2 | 1762.1 | 1500.3 | 1551.8 | 906.1 | 1010.6 | 1418.8 | 1423.2 | 1779 | 1391.3 | 1261.3 | 1030.4 | 33668.4
2025-07-11 | 2026 | 2025 | 2025-07-01 | 2483 | 1841.8 | 1687.5 | 1916.8 | 1978 | 1834 | 1880.6 | 1958.6 | 1936 | 1714.4 | 1779.3 | 1960.5 | 1870.8 | 1664.6 | 1840.9 | 1945.1 | 1957.7 | 1781.3 | 1882.8 | 1802.1 | 217.5 | 1926.8 | 2010 | 41870.1
2025-07-12 | 2026 | 2025 | 2025-07-01 | 2148.9 | 3050.6 | 2092.7 | 3102.9 | 2865.4 | 2685.3 | 2463.5 | 2035.1 | 3028.2 | 1803.5 | 1830.6 | 1694.7 | 1883.2 | 1671.3 | 2003.9 | 3102.7 | 2935 | 2636.5 | 1732 | 1652.9 | 3168.6 | 3273.6 | 3012.5 | 55873.6
2025-07-13 | 2026 | 2025 | 2025-07-01 | 3090.8 | 2810.6 | 2968.5 | 2093.2 | 2298.1 | 2584 | 2538.5 | 3327.4 | 2235.6 | 2846.6 | 2705.2 | 2671.9 | 2738 | 2510.9 | 2892.7 | 2697.1 | 2629.4 | 2560.4 | 2562.1 | 2377.5 | 2878 | 2563.3 | 2794.7 | 61374.5
2025-07-14 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-15 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-16 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-17 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-18 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-19 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-20 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-21 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-22 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-23 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-24 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-25 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-26 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-27 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-28 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-29 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-30 | 2026 | 2025 | 2025-07-01 | [23 empty] | 0
2025-07-31 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-01 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-02 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-03 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-04 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-05 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-06 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-07 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-08 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-09 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-10 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-11 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-12 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-13 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-14 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-15 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-16 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-17 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-18 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-19 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-20 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-21 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-22 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-23 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-24 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-25 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-26 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-27 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-28 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-29 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-30 | 2026 | 2025 | 2025-08-01 | [23 empty] | 0
2025-08-31 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-01 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-02 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-03 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-04 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-05 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-06 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-07 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-08 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-09 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-10 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-11 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-12 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-13 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-14 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-15 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-16 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-17 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-18 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-19 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-20 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-21 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-22 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-23 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-24 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-25 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-26 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-27 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-28 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-29 | 2026 | 2025 | 2025-09-01 | [23 empty] | 0
2025-09-30 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-01 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-02 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-03 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-04 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-05 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-06 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-07 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-08 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-09 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-10 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-11 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-12 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-13 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-14 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-15 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-16 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-17 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-18 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-19 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-20 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-21 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-22 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-23 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-24 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-25 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-26 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-27 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-28 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-29 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-30 | 2026 | 2025 | 2025-10-01 | [23 empty] | 0
2025-10-31 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-01 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-02 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-03 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-04 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-05 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-06 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-07 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-08 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-09 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-10 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-11 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-12 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-13 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-14 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-15 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-16 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-17 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-18 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-19 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-20 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-21 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-22 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-23 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-24 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-25 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-26 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-27 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-28 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-29 | 2026 | 2025 | 2025-11-01 | [23 empty] | 0
2025-11-30 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-01 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-02 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-03 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-04 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-05 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-06 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-07 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-08 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-09 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-10 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-11 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-12 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-13 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-14 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-15 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-16 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-17 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-18 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-19 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-20 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-21 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-22 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-23 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-24 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-25 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-26 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-27 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-28 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-29 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-30 | 2026 | 2025 | 2025-12-01 | [23 empty] | 0
2025-12-31 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-01 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-02 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-03 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-04 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-05 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-06 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-07 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-08 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-09 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-10 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-11 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-12 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-13 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-14 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-15 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-16 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-17 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-18 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-19 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-20 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-21 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-22 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-23 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-24 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-25 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-26 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-27 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-28 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-29 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-30 | 2026 | 2026 | 2026-01-01 | [23 empty] | 0
2026-01-31 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-01 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-02 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-03 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-04 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-05 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-06 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-07 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-08 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-09 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-10 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-11 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-12 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-13 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-14 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-15 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-16 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-17 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-18 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-19 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-20 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-21 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-22 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-23 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-24 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-25 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-26 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-27 | 2026 | 2026 | 2026-02-01 | [23 empty] | 0
2026-02-28 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-01 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-02 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-03 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-04 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-05 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-06 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-07 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-08 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-09 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-10 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-11 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-12 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-13 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-14 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-15 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-16 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-17 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-18 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-19 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-20 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-21 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-22 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-23 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-24 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-25 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-26 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-27 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-28 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-29 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-30 | 2026 | 2026 | 2026-03-01 | [23 empty] | 0
2026-03-31 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-01 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-02 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-03 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-04 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-05 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-06 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-07 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-08 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-09 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-10 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-11 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-12 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-13 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-14 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-15 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-16 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-17 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-18 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-19 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-20 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-21 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-22 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-23 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-24 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-25 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-26 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-27 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-28 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-29 | 2027 | 2026 | 2026-04-01 | [23 empty] | 0
2026-04-30 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-01 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-02 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-03 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-04 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-05 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-06 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-07 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-08 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-09 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-10 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-11 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-12 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-13 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-14 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-15 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-16 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-17 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-18 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-19 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-20 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-21 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-22 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-23 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-24 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-25 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-26 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-27 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-28 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-29 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-30 | 2027 | 2026 | 2026-05-01 | [23 empty] | 0
2026-05-31 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-01 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-02 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-03 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-04 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-05 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-06 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-07 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-08 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-09 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-10 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-11 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-12 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-13 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-14 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-15 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-16 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-17 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-18 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-19 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-20 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-21 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-22 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-23 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-24 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-25 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-26 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-27 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-28 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-29 | 2027 | 2026 | 2026-06-01 | [23 empty] | 0
2026-06-30 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-01 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-02 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-03 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-04 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-05 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-06 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-07 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-08 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-09 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-10 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-11 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-12 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-13 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-14 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-15 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-16 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-17 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-18 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-19 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-20 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-21 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-22 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-23 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-24 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-25 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-26 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-27 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-28 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-29 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-30 | 2027 | 2026 | 2026-07-01 | [23 empty] | 0
2026-07-31 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-01 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-02 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-03 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-04 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-05 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-06 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-07 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-08 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-09 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-10 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-11 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-12 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-13 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-14 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-15 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-16 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-17 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-18 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-19 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-20 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-21 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-22 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-23 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-24 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-25 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-26 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-27 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-28 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-29 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-30 | 2027 | 2026 | 2026-08-01 | [23 empty] | 0
2026-08-31 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-01 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-02 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-03 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-04 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-05 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-06 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-07 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-08 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-09 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-10 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-11 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-12 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-13 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-14 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-15 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-16 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-17 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-18 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-19 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-20 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-21 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-22 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-23 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-24 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-25 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-26 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-27 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-28 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-29 | 2027 | 2026 | 2026-09-01 | [23 empty] | 0
2026-09-30 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-01 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-02 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-03 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-04 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-05 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-06 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-07 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-08 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-09 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-10 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-11 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-12 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-13 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-14 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-15 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-16 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-17 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-18 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-19 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-20 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-21 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-22 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-23 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-24 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-25 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-26 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-27 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-28 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-29 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-30 | 2027 | 2026 | 2026-10-01 | [23 empty] | 0
2026-10-31 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-01 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-02 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-03 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-04 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-05 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-06 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-07 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-08 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-09 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-10 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-11 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-12 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-13 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-14 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-15 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-16 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-17 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-18 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-19 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-20 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-21 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-22 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-23 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-24 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
2026-11-25 | 2027 | 2026 | 2026-11-01 | [23 empty] | 0
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Date = [Date, row above]+1

## IGA_BD
Sr. No. | Finacial Year | Calendor Year | Operating Year | Month | Date | Affected Feeder | SPV | Consumer | Plant Equivalent Weightage | Breakdown Description | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Fault Category | Loss of KWH | Estimated Energy Loss (kWh) | Scope | PTW No. | Job Card No.
1 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0.30625 | 0.30625 | 0.51667 | 0 | 5.05 | 5.05 | F#4 CP-11(KUD14 to KUD19) B-Phase pin insulator & SP-02(KUD12 to KUD20) R-Phase pin insulator replacement done & charge the Feeder | Close | 2.525 |  |  | 10166
2 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0.30486 | 0.30486 | 0.30903 | 0 | 0.1 | 0.1 | Test Charge taken and line stood ok | Close | 0.05 |  |  | 1424
3 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.51597 | 0.51597 | 0.63333 | 0 | 2.8167 | 2.8167 | DCOH line F2 SP-94 R-Phase Suspension insualtor & DP-97 B-Phase pin insulator replacement done& Charge the line | Close | 1.4083 |  |  | 6635
4 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | Wind_F4 | 0 | 0 | 50% | LC taken for F2 Pin & Suspension insulator replcement work at DCOH SP-94 & DP-97 | 0.59167 | 0.59167 | 0.63333 | 0 | 1 | 1 | LC taken fo DCOH line F2 SP-94 &DP- 97 insulator replacement work | Close | 0.5 |  |  | 4379
5 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | Wind_F4 | 0 | 0 | 50% | Tripped on OCR | 0.78264 | 0.78264 | 0.79514 | 0 | 0.3 | 0.3 | Test Charge taken and line stood ok | Close | 0.15 |  |  | 2301
6 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.78333 | 0.78333 | 0.79514 | 0 | 0.28333 | 0.28333 | Test Charge taken and line stood ok | Close | 0.14167 |  |  | 2371
7 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0.79792 | 0.79792 | 0.80694 | 0 | 0.21667 | 0.21667 | Test Charge taken and line stood ok | Close | 0.10833 |  |  | 1662
8 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | Wind_F4 | 0 | 0 | 50% | LC taken for DCOH tap to KUD08 insulator replacement work(At tap jumper connection opening purpose) | 0.38194 | 0.38194 | 0.41181 | 0 | 0.71667 | 0.71667 | After jumer connection removed charge the feeder | Close | 0.35833 |  |  | 1670
9 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | KUD08 | O2R3 | JK | 4.348% | LC taken for tap to KUD08 insulator replacement work | 0.41181 | 0.41181 | 0.72917 | 0 | 7.6167 | 7.6167 | Inslator replacent work done upto 14 poles(tap to KUD08) | Close | 0.33116 |  |  | 1614
10 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | Wind_F4 | 0 | 0 | 50% | LC taken for jumper tapping connection at DCOH KUD-03 | 0.72917 | 0.72917 | 0.75347 | 0 | 0.58333 | 0.58333 | After jumper connection done charge the feeder | Close | 0.29167 |  |  | 1360
11 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | Wind_F4 | 0 | 0 | 50% | Tripped on OCR | 0.86667 | 0.86667 | 0.8875 | 0 | 0.5 | 0.5 | Test Charge taken and line stood ok | Close | 0.25 |  |  | 1165
12 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | Wind_F4 | 0 | 0 | 50% | LC taken for DCOH tap to KUD08 insulator replacement work(At tap jumper connection opening purpose) | 0.38889 | 0.38889 | 0.41319 | 0 | 0.58333 | 0.58333 | After jumer connection removed charge the feeder | Close | 0.29167 |  |  | 2681
13 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | KUD08 | O2R3 | JK | 4.348% | LC taken for tap to KUD08 insulator replacement work | 0.41319 | 0.41319 | 0.68194 | 0 | 6.45 | 6.45 | Inslator replacent work done upto 23 poles(tap to KUD08) | Close | 0.28043 |  |  | 2695
14 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | Wind_F4 | 0 | 0 | 50% | LC taken for jumper tapping connection at DCOH KUD-03 | 0.68194 | 0.68194 | 0.70278 | 0 | 0.5 | 0.5 | After jumper connection done charge the feeder | Close | 0.25 |  |  | 2298
15 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0.27083 | 0.27083 | 0.28472 | 0 | 0.33333 | 0.33333 | Test Charge taken and line stood ok | Close | 0.16667 |  |  | 1532
16 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | Wind_F4 | 0 | 0 | 50% | LC taken for DCOH tap to KUD08 insulator replacement work(At tap jumper connection opening purpose) | 0.38194 | 0.38194 | 0.40972 | 0 | 0.66667 | 0.66667 | After jumer connection removed charge the feeder | Close | 0.33333 |  |  | 3064
17 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | KUD08 | O2R3 | JK | 4.348% | LC taken for tap to KUD08 insulator replacement work | 0.40972 | 0.40972 | 0.75556 | 0 | 8.3 | 8.3 | Inslator replacent work done upto 43 poles(tap to KUD08) | Close | 0.36087 |  |  | 3468
18 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | Wind_F4 | 0 | 0 | 50% | LC taken for jumper tapping connection at DCOH KUD-03 | 0.75556 | 0.75556 | 0.76875 | 0 | 0.31667 | 0.31667 | After jumper connection done charge the feeder | Close | 0.15833 |  |  | 1455
19 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.81944 | 0.81944 | 0.825 | 0 | 0.13333 | 0.13333 | Test Charge taken and line stood ok | Close | 0.066667 |  |  | 668
20 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | KUD04 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.825 | 0.825 | 0.87847 | 0 | 1.2833 | 1.2833 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.055797 |  |  | 536
21 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | KUD05 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.825 | 0.825 | 0.87847 | 0 | 1.2833 | 1.2833 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.055797 |  |  | 536
22 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | KUD09 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.825 | 0.825 | 0.87847 | 0 | 1.2833 | 1.2833 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.055797 |  |  | 536
23 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | KUD21 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.825 | 0.825 | 0.87847 | 0 | 1.2833 | 1.2833 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.055797 |  |  | 536
24 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | KUD22 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.825 | 0.825 | 0.87847 | 0 | 1.2833 | 1.2833 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.055797 |  |  | 536
25 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | KUD23 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.825 | 0.825 | 0.87847 | 0 | 1.2833 | 1.2833 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.055797 |  |  | 536
26 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | Wind_F2 | 0 | 0 | 50% | LC taken for KUD-18 JK metering R phase fuse replacement. | 0.87847 | 0.87847 | 0.95278 | 0 | 1.7833 | 1.7833 | KUD-18 JK metering R phase fuse replacement done. | Close | 0.89167 |  |  | 8941
27 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | Wind_F4 | 0 | 0 | 50% | LC taken for DCOH tap to KUD08 insulator replacement work(At tap jumper connection opening purpose) | 0.42917 | 0.42917 | 0.46319 | 0 | 0.81667 | 0.81667 | After jumer connection removed charge the feeder | Close | 0.40833 |  |  | 3603
28 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | KUD08 | O2R3 | JK | 4.348% | LC taken for tap to KUD08 insulator replacement work | 0.46319 | 0.46319 | 0.74097 | 0 | 6.6667 | 6.6667 | Inslator replacent work done upto 51 poles(tap to KUD08) | Close | 0.28986 |  |  | 2674
29 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | Wind_F4 | 0 | 0 | 50% | LC taken for jumper tapping connection at DCOH KUD-03 | 0.74097 | 0.74097 | 0.75556 | 0 | 0.35 | 0.35 | After jumper connection done charge the feeder | Close | 0.175 |  |  | 1544
30 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | Wind_F4 | 0 | 0 | 50% | LC taken for DCOH tap to KUD08 insulator replacement work(At tap jumper connection opening purpose) | 0.44722 | 0.44722 | 0.46458 | 0 | 0.41667 | 0.41667 | After jumer connection removed charge the feeder | Close | 0.20833 |  |  | 1972
31 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | KUD08 | O2R3 | JK | 4.348% | LC taken for tap to KUD08 insulator replacement work | 0.46458 | 0.46458 | 0.71042 | 0 | 5.9 | 5.9 | Inslator replacent work done upto 67 poles(tap to KUD08) | Close | 0.25652 |  |  | 2539
32 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | Wind_F4 | 0 | 0 | 50% | LC taken for jumper tapping connection at DCOH KUD-03 | 0.71042 | 0.71042 | 0.725 | 0 | 0.35 | 0.35 | After jumper connection done charge the feeder | Close | 0.175 |  |  | 1657
33 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-19 | Wind_F4 | 0 | 0 | 50% | LC taken for DCOH tap to KUD08 insulator replacement work(At tap jumper connection opening purpose) | 0.41667 | 0.41667 | 0.43194 | 0 | 0.36667 | 0.36667 | After jumper connection removed charge the feeder | Close | 0.18333 |  |  | 1736
34 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-19 | KUD08 | O2R3 | JK | 4.348% | LC taken for tap to KUD08 insulator replacement work | 0.43194 | 0.43194 | 0.67361 | 0 | 5.8 | 5.8 | Inslator replacent work done upto 71 poles(tap to KUD08) | Close | 0.25217 |  |  | 2496
35 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-19 | Wind_F4 | 0 | 0 | 50% | LC taken for jumper tapping connection at DCOH KUD-03 | 0.67361 | 0.67361 | 0.69792 | 0 | 0.58333 | 0.58333 | After jumper connection done charge the feeder | Close | 0.29167 |  |  | 2761
36 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | Wind_F2 | 0 | 0 | 50% | LC taken for KUD06 tap KUD07 insulator replacement work(At tap jumper connection opening purpose) | 0.40903 | 0.40903 | 0.42917 | 0 | 0.48333 | 0.48333 | After jumper connection removed charge the feeder | Close | 0.24167 |  |  | 2496
37 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | KUD07 | O2R3 | JK | 4.348% | LC taken for KUD06 tap to KUD07 insulator replacement work | 0.42917 | 0.42917 | 0.56389 | 0 | 3.2333 | 3.2333 | Inslator replacent work done upto 12 poles(tap to KUD07) | Close | 0.14058 |  |  | 1391
38 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.56389 | 0.56389 | 0.59722 | 0 | 0.8 | 0.8 | After jumper connection done & at KUD06 metering point R Phase pin insulator replacement done & charge the feeder | Close | 0.4 |  |  | 4131
39 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | Wind_F2 | 0 | 0 | 50% | LC taken for DCOH tap.to KUD06 jumper connection opening purpose | 0.39583 | 0.39583 | 0.41667 | 0 | 0.5 | 0.5 | After jumper connection removed charge the feeder | Close | 0.25 |  |  | 1197
40 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | KUD07 | O2R3 | JK | 4.348% | LC taken for DCOH tap to KUD06 insulator replacement work | 0.41667 | 0.41667 | 0.65278 | 0 | 5.6667 | 5.6667 | Inslator replacent work done upto 12 poles(tap to KUD06) | Close | 0.24638 |  |  | 1131
41 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | KUD06 | O2R3 | JK | 4.348% | LC taken for DCOH tap to KUD06 insulator replacement work | 0.41667 | 0.41667 | 0.65278 | 0 | 5.6667 | 5.6667 | Inslator replacent work done upto 12 poles(tap to KUD06) | Close | 0.24638 |  |  | 1131
42 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | Wind_F2 | 0 | 0 | 50% | LC taken for DCOH tap.to KUD06 jumper connection Closeing purpose | 0.63472 | 0.63472 | 0.65278 | 0 | 0.43333 | 0.43333 | After jumper connection removed charge the feeder | Close | 0.21667 |  |  | 1037
43 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | Wind_F4 | 0 | 0 | 50% | LC taken for KUD-01 tap.to KUD-15 jumper connection opening purpose | 0.41458 | 0.41458 | 0.45278 | 0 | 0.91667 | 0.91667 | After jumper connection removed charge the feeder | Close | 0.45833 |  |  | 1845
44 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | KUD15 | O2R1 | KSIPL | 4.348% | LC taken for KUD-01 tap to KUD-15 insulator replacement work | 0.45278 | 0.45278 | 0.71597 | 0 | 6.3167 | 6.3167 | Inslator replacent work done upto 16 poles(tap to KUD-15) | Close | 0.27464 |  |  | 1156
45 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | Wind_F4 | 0 | 0 | 50% | LC taken for KUD-01 tap.to KUD-15 jumper connection Closeing purpose | 0.71597 | 0.71597 | 0.73194 | 0 | 0.38333 | 0.38333 | After jumper connection removed charge the feeder | Close | 0.19167 |  |  | 772
46 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0.50208 | 0.50208 | 0.50625 | 0 | 0.1 | 0.1 | Test Charge taken and line stood ok | Close | 0.05 |  |  | 243
47 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | Wind_F4 | 0 | 0 | 50% | LC taken for KUD-10 tap.to KUD-01 jumper connection opening purpose | 0.4125 | 0.4125 | 0.43125 | 0 | 0.45 | 0.45 | Afterjumper connection removed charge the feeder | Close | 0.225 |  |  | 1049
48 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD01 | O2R1 | KSIPL | 4.348% | LC taken for KUD-10 tap to KUD-01 insulator replacement work | 0.43125 | 0.43125 | 0.69861 | 0 | 6.4167 | 6.4167 | Inslator replacent work done upto 11 poles(tap to KUD-01) | Close | 0.27899 |  |  | 1360
49 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | KUD15 | O2R1 | KSIPL | 4.348% | LC taken for KUD-10 tap to KUD-01 insulator replacement work | 0.43125 | 0.43125 | 0.69861 | 0 | 6.4167 | 6.4167 | Inslator replacent work done (tap to KUD-01) | Close | 0.27899 |  |  | 1360
50 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | Wind_F4 | 0 | 0 | 50% | LC taken for KUD-10 tap.to KUD-01 jumper connection Closeing purpose | 0.69861 | 0.69861 | 0.71806 | 0 | 0.46667 | 0.46667 | Afte jumper connection closeing charge the feeder | Close | 0.23333 |  |  | 1088
51 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | Wind_F4 | 0 | 0 | 50% | LC taken for KUD-10 tap.to KUD-01 jumper connection opening purpose | 0.42431 | 0.42431 | 0.44444 | 0 | 0.48333 | 0.48333 | After jumper connection removed charge the feeder | Close | 0.24167 |  |  | 1176
52 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | KUD01 | O2R1 | KSIPL | 4.348% | LC taken for KUD-10 tap to KUD-01 insulator replacement work | 0.44444 | 0.44444 | 0.65833 | 0 | 5.1333 | 5.1333 | Inslator replacent work done upto 16 poles(KUD-10 tap to KUD-01) | Close | 0.22319 |  |  | 1135
53 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | KUD15 | O2R1 | KSIPL | 4.348% | LC taken for KUD-10 tap to KUD-01 insulator replacement work | 0.45 | 0.45 | 0.65833 | 0 | 5 | 5 | Inslator replacent work done (KUD-10 tap to KUD-01) | Close | 0.21739 |  |  | 1135
54 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | Wind_F4 | 0 | 0 | 50% | LC taken for KUD-10 tap.to KUD-01 jumper connection Closeing purpose | 0.65833 | 0.65833 | 0.68472 | 0 | 0.63333 | 0.63333 | After jumper connection closeing charge the feeder | Close | 0.31667 |  |  | 1541
55 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | Wind_F4 | 0 | 0 | 50% | LC taken for KUD-10 tap.to KUD-01 jumper connection opening purpose | 0.39028 | 0.39028 | 0.42222 | 0 | 0.76667 | 0.76667 | After jumper connection removed charge the feeder | Close | 0.38333 |  |  | 4215
56 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | KUD01 | O2R1 | KSIPL | 4.348% | LC taken for KUD-10 tap to KUD-01 insulator replacement work | 0.42222 | 0.42222 | 0.59375 | 0 | 4.1167 | 4.1167 | Inslator replacent work done upto 19 poles(KUD-10 tap to KUD-01) | Close | 0.17899 |  |  | 2057
57 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | KUD15 | O2R1 | KSIPL | 4.348% | LC taken for KUD-10 tap to KUD-01 insulator replacement work | 0.42222 | 0.42222 | 0.59375 | 0 | 4.1167 | 4.1167 | Inslator replacent work done (KUD-10 tap to KUD-01) | Close | 0.17899 |  |  | 2057
58 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | Wind_F4 | 0 | 0 | 50% | LC taken for KUD-10 tap.to KUD-01 jumper connection Closeing purpose | 0.59375 | 0.59375 | 0.6375 | 0 | 1.05 | 1.05 | After jumper connection closeing charge the feeder | Close | 0.525 |  |  | 5772
59 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | Wind_F4 | 0 | 0 | 50% | LC taken for DCOH tap.to KUD-10 jumper connection opening purpose | 0.36458 | 0.36458 | 0.39583 | 0 | 0.75 | 0.75 | After jumper connection removed charge the feeder | Close | 0.375 |  |  | 1132
60 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | KUD10 | O2R1 | KSIPL | 4.348% | LC taken for DCOH tap.to KUD-10 insulator replacement work | 0.39583 | 0.39583 | 0.6875 | 0 | 7 | 7 | Inslator replacent work done upto 25 poles(DCOH tap.to KUD-10) | Close | 0.30435 |  |  | 961
61 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | KUD01 | O2R1 | KSIPL | 4.348% | LC taken for DCOH tap.to KUD-10 insulator replacement work | 0.39583 | 0.39583 | 0.6875 | 0 | 7 | 7 | Inslator replacent work done (DCOH tap.to KUD-10) | Close | 0.30435 |  |  | 961
62 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | KUD15 | O2R1 | KSIPL | 4.348% | LC taken for DCOH tap.to KUD-10 insulator replacement work | 0.39583 | 0.39583 | 0.6875 | 0 | 7 | 7 | Inslator replacent work done (DCOH tap.to KUD-10) | Close | 0.30435 |  |  | 961
63 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | Wind_F2 | 0 | 0 | 50% | Tripped on OCR due to 33kv Outdoor B-phase UG cable puncher | 0.52083 | 0.52083 | 0.99931 | 0 | 11.4833 | 11.4833 | Cable Jointing Work in Progress | Open | 5.7417 |  |  | 18916
64 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | Wind_F4 | 0 | 0 | 50% | LC taken for DCOH tap.to KUD-10 jumper connection Closeing purpose | 0.6875 | 0.6875 | 0.69931 | 0 | 0.28333 | 0.28333 | After jumper connection closeing charge the feeder | Close | 0.14167 |  |  | 428
65 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | Wind_F2 | 0 | 0 | 50% | Tripped on OCR due to 33kv Outdoor B-phase UG cable puncher | 0 | 0 | 0.10069 | 0 | 2.4167 | 2.4167 | Cable Jointing Work done,chagre the feeder | Close | 1.2083 |  |  | 11631
66 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | Wind_F4 | 0 | 0 | 50% | LC taken for DCOH tap.to KUD-10 jumper connection opening purpose | 0.41667 | 0.41667 | 0.45486 | 0 | 0.91667 | 0.91667 | Afterjumper connection removed charge the feeder | Close | 0.45833 |  |  | 4044
67 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD10 | O2R1 | KSIPL | 4.348% | LC taken for DCOH tap.to KUD-10 insulator replacement work | 0.45486 | 0.45486 | 0.64792 | 0 | 4.6333 | 4.6333 | Inslator replacent work done upto 16 poles(DCOH tap.to KUD-10) | Close | 0.20145 |  |  | 1858
68 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD01 | O2R1 | KSIPL | 4.348% | LC taken for DCOH tap.to KUD-10 insulator replacement work | 0.45486 | 0.45486 | 0.64792 | 0 | 4.6333 | 4.6333 | Inslator replacent work done (DCOH tap.to KUD-10) | Close | 0.20145 |  |  | 1858
69 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | KUD15 | O2R1 | KSIPL | 4.348% | LC taken for DCOH tap.to KUD-10 insulator replacement work | 0.45486 | 0.45486 | 0.64792 | 0 | 4.6333 | 4.6333 | Inslator replacent work done (DCOH tap.to KUD-10) | Close | 0.20145 |  |  | 1858
70 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | Wind_F4 | 0 | 0 | 50% | LC taken for DCOH tap.to KUD-10 jumper connection Closeing purpose | 0.64792 | 0.64792 | 0.66944 | 0 | 0.51667 | 0.51667 | After jumper connection closeing charge the feeder | Close | 0.25833 |  |  | 2279
71 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | Wind_F4 | 0 | 0 | 50% | LC taken for DCOH tap.to KUD-10 jumper connection opening purpose | 0.40278 | 0.40278 | 0.43056 | 0 | 0.66667 | 0.66667 | After jumper connection removed charge the feeder | Close | 0.33333 |  |  | 631
72 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD10 | O2R1 | KSIPL | 4.348% | LC taken for DCOH tap.to KUD-10 insulator replacement work | 0.43056 | 0.43056 | 0.61181 | 0 | 4.35 | 4.35 | Insulator replacent work done (DCOH tap.to KUD-10) | Close | 0.18913 |  |  | 374
73 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD01 | O2R1 | KSIPL | 4.348% | LC taken for DCOH tap.to KUD-10 insulator replacement work | 0.43056 | 0.43056 | 0.61181 | 0 | 4.35 | 4.35 | Insulator replacent work done (DCOH tap.to KUD-10) | Close | 0.18913 |  |  | 374
74 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD15 | O2R1 | KSIPL | 4.348% | LC taken for DCOH tap.to KUD-10 insulator replacement work | 0.43056 | 0.43056 | 0.61181 | 0 | 4.35 | 4.35 | Insulator replacent work done (DCOH tap.to KUD-10) | Close | 0.18913 |  |  | 374
75 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | Wind_F4 | 0 | 0 | 50% | LC taken for DCOH tap.to KUD-10 jumper connection Closeing purpose & At the same time DCOH tap to KUD-11 jumper connection removing purpose | 0.61181 | 0.61181 | 0.64306 | 0 | 0.75 | 0.75 | After jumper connection closeing charge the feeder | Close | 0.375 |  |  | 662
76 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | KUD11 | O2R1 | KSIPL | 4.348% | LC taken for DCOH tap.to KUD-11 insulator replacement work | 0.64306 | 0.64306 | 0.68958 | 0 | 1.1167 | 1.1167 | Insulator replacent work done (DCOH tap.to KUD-11) | Close | 0.048551 |  |  | 96
77 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | Wind_F4 | 0 | 0 | 50% | LC taken for DCOH tap.to KUD-11 jumper connection Closeing purpose | 0.68958 | 0.68958 | 0.71875 | 0 | 0.7 | 0.7 | After jumper connection closeing charge the feeder | Close | 0.35 |  |  | 662
78 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | Wind_F4 | 0 | 0 | 50% | LC taken for KUD-12 tap.to KUD-20 insulator replacement work(At tap jumper connection opening purpose) | 0.42014 | 0.42014 | 0.44444 | 0 | 0.58333 | 0.58333 | After jumper connection removed charge the feeder | Close | 0.29167 |  |  | 2239
79 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | KUD20 | O2R1 | KSIPL | 4.348% | LC taken for KUD-12 tap.to KUD-20 insulator replacement work | 0.44444 | 0.44444 | 0.66806 | 0 | 5.3667 | 5.3667 | Inslator replacent work done (KUD-12 tap. to KUD-20) | Close | 0.23333 |  |  | 1873
80 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | Wind_F4 | 0 | 0 | 50% | LC taken for KUD-12 tap.to KUD-20 jumper connection Closeing purpose | 0.66806 | 0.66806 | 0.68889 | 0 | 0.5 | 0.5 | After jumper connection done charge the feeder | Close | 0.25 |  |  | 1920
81 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.69444 | 0.69444 | 0.7 | 0 | 0.13333 | 0.13333 | Test Charge taken and line stood ok | Close | 0.066667 |  |  | 689
82 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-04 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.12431 | 0.12431 | 0.14236 | 0 | 0.43333 | 0.43333 | Test Charge taken and line stood ok | Close | 0.21667 |  |  | 2723
83 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-04 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0.57778 | 0.57778 | 0.58264 | 0 | 0.11667 | 0.11667 | Test Charge taken and line stood ok | Close | 0.058333 |  |  | 672
84 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | TX2 | 0 | 0 | 100% | PTR-02 manually shutdown taken for PSS equipments annual testing | 0.78819 | 0.78819 | 0.99931 | 0 | 5.0667 | 5.0667 | Annual testing work in progress | Open | 5.0667 |  |  | 21326
85 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | TX2 | 0 | 0 | 100% | PTR-02 manually shutdown taken for PSS equipments annual testing | 0 | 0 | 0.075 | 0 | 1.8 | 1.8 | Annual testing work done and TRF-02 charged | Close | 1.8 |  |  | 11344
86 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | Line1 | 0 | 0 | 100% | Manually shutdown taken for PSS equipments annual testing | 0.80903 | 0.80903 | 0.99931 | 0 | 4.5667 | 4.5667 | Annual testing work in progress | Open | 4.5667 |  |  | 28697
87 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | Line1 | 0 | 0 | 100% | Manually shutdown taken for PSS equipments annual testing | 0 | 0 | 0.055556 | 0 | 1.3333 | 1.3333 | Annual testing work done and Line1 charged | Close | 1.3333 |  |  | 5612
88 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | Line1 | 0 | 0 | 100% | Manually shutdown taken for PSS equipments annual testing | 0.76042 | 0.76042 | 0.99931 | 0 | 5.7333 | 5.7333 | Annual testing work in progress | Open | 5.7333 |  |  | 24132
89 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | Line1 | 0 | 0 | 100% | Manually shutdown taken for PSS equipments annual testing | 0 | 0 | 0.23819 | 0 | 5.7167 | 5.7167 | Annual testing work done and Line1 charged | Close | 5.7167 |  |  | 42693
90 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.0041667 | 0.0041667 | 0.020833 | 0 | 0.4 | 0.4 | Test Charge taken and line stood ok | Close | 0.2 |  |  | 958
91 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | Wind_F4 | 0 | 0 | 50% | Tripped on OCR | 0.061806 | 0.061806 | 0.077778 | 0 | 0.38333 | 0.38333 | Test Charge taken and line stood ok | Close | 0.19167 |  |  | 841
92 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.11389 | 0.11389 | 0.31944 | 0 | 4.9333 | 4.9333 | DCOH line F2 SP-98 B-Phase Suspension insualtor replacement done& Charge the line | Close | 2.4667 |  |  | 11810
93 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | Wind_F4 | 0 | 0 | 50% | LC taken for DCOH line F2 SP-98 B-Ph suspension insulator replacement work | 0.28611 | 0.28611 | 0.31944 | 0 | 0.8 | 0.8 | DCOH line F2 SP-98 B-Phase Suspension insualtor replacement done& Charge the line | Close | 0.4 |  |  | 1756
94 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0.63611 | 0.63611 | 0.72083 | 0 | 2.0333 | 2.0333 | DCOH line DP -140 F-4 Y-Phase tension insualtor replacement done& Charge the line | Close | 1.0167 |  |  | 604
95 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | Wind_F2 | 0 | 0 | 50% | LC taken for DCOH line F4 DP-140 Y-Ph Tension insulator replacement work | 0.69444 | 0.69444 | 0.72083 | 0 | 0.63333 | 0.63333 | DCOH line DP -140 F-4 Y-Phase tension insualtor replacement done& Charge the line | Close | 0.31667 |  |  | 205
96 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0.72569 | 0.72569 | 0.80208 | 0 | 1.8333 | 1.8333 | After rain stop,Test Charge taken and line stood ok | Close | 0.91667 |  |  | 545
97 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0.47014 | 0.47014 | 0.51389 | 0 | 1.05 | 1.05 | After rain stop,Test Charge taken and line stood ok | Close | 0.525 |  |  | 778
98 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0.62986 | 0.62986 | 0.68056 | 0 | 1.2167 | 1.2167 | SP-36 Y-Phase (KUD14-KUD19 Line)pin insulator replacement work done and test charge taken line stood ok | Close | 0.60833 |  |  | 901
99 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0.74306 | 0.74306 | 0.75 | 0 | 0.16667 | 0.16667 | After rain stop,Test Charge taken and line stood ok | Close | 0.083333 |  |  | 123
100 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | Wind_F2 | 0 | 0 | 50% | Tripped on OCR | 0.64444 | 0.64444 | 0.64722 | 0 | 0.066667 | 0.066667 | Test Charge taken and line stood ok | Close | 0.033333 |  |  | 1011
101 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | Wind_F2 | 0 | 0 | 50% | Tripped on OCR | 0.69861 | 0.69861 | 0.70486 | 0 | 0.15 | 0.15 | Test Charge taken and line stood ok | Close | 0.075 |  |  | 2276
102 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | Wind_F2 | 0 | 0 | 50% | Tripped on OCR | 0.71319 | 0.71319 | 0.72917 | 0 | 0.38333 | 0.38333 | Test Charge taken and line stood ok | Close | 0.19167 |  |  | 5816
103 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.25694 | 0.25694 | 0.26181 | 0 | 0.11667 | 0.11667 | Test Charge taken and line stood ok | Close | 0.058333 |  |  | 2293
104 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0.26181 | 0.26181 | 0.26667 | 0 | 0.11667 | 0.11667 | Test Charge taken and line stood ok | Close | 0.058333 |  |  | 2293
105 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-24 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.095139 | 0.095139 | 0.10417 | 0 | 0.21667 | 0.21667 | Test Charge taken and line stood ok | Close | 0.10833 |  |  | 4715
106 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.88889 | 0.88889 | 0.89375 | 0 | 0.11667 | 0.11667 | Test Charge taken and line stood ok | Close | 0.058333 |  |  | 2866
107 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | Wind_F2 | 0 | 0 | 50% | Tripped on OCR | 0.13194 | 0.13194 | 0.13889 | 0 | 0.16667 | 0.16667 | Test Charge taken and line stood ok | Close | 0.083333 |  |  | 4397
108 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | Wind_F2 | 0 | 0 | 50% | Tripped on OCR | 0.75625 | 0.75625 | 0.76111 | 0 | 0.11667 | 0.11667 | Test Charge taken and line stood ok | Close | 0.058333 |  |  | 3078
109 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | Wind_F2 | 0 | 0 | 50% | Tripped on OCR | 0.77083 | 0.77083 | 0.78264 | 0 | 0.28333 | 0.28333 | Test Charge taken and line stood ok | Close | 0.14167 |  |  | 7476
110 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | KUD04 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.78264 | 0.78264 | 0.88958 | 0 | 2.5667 | 2.5667 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.11159 |  |  | 5643
111 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | KUD05 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.78264 | 0.78264 | 0.88958 | 0 | 2.5667 | 2.5667 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.11159 |  |  | 5643
112 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | KUD09 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.78264 | 0.78264 | 0.88958 | 0 | 2.5667 | 2.5667 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.11159 |  |  | 5643
113 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | KUD21 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.78264 | 0.78264 | 0.88958 | 0 | 2.5667 | 2.5667 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.11159 |  |  | 5643
114 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | KUD22 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.78264 | 0.78264 | 0.88958 | 0 | 2.5667 | 2.5667 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.11159 |  |  | 5643
115 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | KUD23 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.78264 | 0.78264 | 0.88958 | 0 | 2.5667 | 2.5667 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.11159 |  |  | 5643
116 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | Wind_F2 | 0 | 0 | 50% | LC taken for KUD-18 JK metering R phase fuse replacement. | 0.88958 | 0.88958 | 0.92569 | 0 | 0.86667 | 0.86667 | KUD-18 JK metering R phase fuse replacement done. | Close | 0.43333 |  |  | 22867
117 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | Wind_F2 | 0 | 0 | 50% | Tripped on OCR | 0.33194 | 0.33194 | 0.33958 | 0 | 0.18333 | 0.18333 | Test Charge taken and line stood ok | Close | 0.091667 |  |  | 4152
118 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | KUD04 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.33958 | 0.33958 | 0.45417 | 0 | 2.75 | 2.75 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.11957 |  |  | 5189
119 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | KUD05 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.33958 | 0.33958 | 0.45417 | 0 | 2.75 | 2.75 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.11957 |  |  | 5189
120 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | KUD09 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.33958 | 0.33958 | 0.45417 | 0 | 2.75 | 2.75 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.11957 |  |  | 5189
121 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | KUD21 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.33958 | 0.33958 | 0.45417 | 0 | 2.75 | 2.75 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.11957 |  |  | 5189
122 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | KUD22 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.33958 | 0.33958 | 0.45417 | 0 | 2.75 | 2.75 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.11957 |  |  | 5189
123 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | KUD23 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.33958 | 0.33958 | 0.45417 | 0 | 2.75 | 2.75 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.11957 |  |  | 5189
124 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | Wind_F2 | 0 | 0 | 50% | LC taken for KUD-18 JK metering R phase fuse replacement. | 0.45417 | 0.45417 | 0.48542 | 0 | 0.75 | 0.75 | KUD-18 JK metering R phase fuse replacement done. | Close | 0.375 |  |  | 16984
125 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | Wind_F2 | 0 | 0 | 50% | Tripped on OCR | 0.92361 | 0.92361 | 0.93403 | 0 | 0.25 | 0.25 | Test Charge taken and line stood ok | Close | 0.125 |  |  | 5661
126 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-29 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR due to heavy rain and Lighting | 0.77569 | 0.77569 | 0.82292 | 0 | 1.1333 | 1.1333 | Test Charge taken and line stood ok | Close | 0.56667 |  |  | 19774
127 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-01 | Wind_F2 | 0 | 0 | 50% | Tripped on OCR | 0.68056 | 0.68056 | 0.68611 | 0 | 0.13333 | 0.13333 | Test Charge taken and line stood ok | Close | 0.066667 |  |  | 1862
128 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-01 | Wind_F2 | 0 | 0 | 50% | Tripped on OCR | 0.69653 | 0.69653 | 0.70833 | 0 | 0.28333 | 0.28333 | Test Charge taken and line stood ok | Close | 0.14167 |  |  | 1862
129 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | Wind_F2 | 0 | 0 | 50% | Tap to KUD-18 line SP 74 B phase Suspension insulator replacement work | 0.56528 | 0.56528 | 0.59792 | 0 | 0.78333 | 0.78333 | Tap to KUD-18 line SP 74 B phase Suspension insulator replacement work done | Close | 0.39167 |  |  | 10611
130 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | Wind_F2 | 0 | 0 | 50% | Tripped on OCR | 0.67569 | 0.67569 | 0.68611 | 0 | 0.25 | 0.25 | Test Charge taken and line stood ok | Close | 0.125 |  |  | 3387
131 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.58681 | 0.58681 | 0.60625 | 0 | 0.46667 | 0.46667 | Test Charge taken and line stood ok | Close | 0.23333 |  |  | 3332
132 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0.58681 | 0.58681 | 0.60625 | 0 | 0.46667 | 0.46667 | Test Charge taken and line stood ok | Close | 0.23333 |  |  | 3054
133 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | Wind_F2 | 0 | 0 | 50% | F#02 LC taken for tree trimming work | 0.74722 | 0.74722 | 0.76389 | 0 | 0.4 | 0.4 | Tree trimming work completed & charge the feeder | Close | 0.2 |  |  | 2856
134 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-06 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.67361 | 0.67361 | 0.67708 | 0 | 0.083333 | 0.083333 | Test Charge taken and line stood ok | Close | 0.041667 |  |  | 500
135 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.33542 | 0.33542 | 0.34097 | 0 | 0.13333 | 0.13333 | Test Charge taken and line stood ok | Close | 0.066667 |  |  | 1316
136 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | Wind_F2 | 0 | 0 | 50% | KUD-17 to KUD-16 CP-19 B phase Tension insulator Replacement work | 0.022222 | 0.022222 | 0.26458 | 0 | 5.8167 | 5.8167 | KUD-17 to KUD-16 CP=19 B phase Tension insulator Replacement work done & after feeder charger line stood ok | Close | 2.9083 |  |  | 60024
137 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-12 | Wind_F2 | 0 | 0 | 50% | LC taken for KUD17 to KUD02 line TP-47 Y & B Phase tension insulator replacement work | 0.67361 | 0.67361 | 0.70139 | 0 | 0.66667 | 0.66667 | KUD-17 to KUD-02 TP=47 Y & B Tension insulator Replacement work completed | Close | 0.33333 |  |  | 5114
138 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-16 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.66875 | 0.66875 | 0.67361 | 0 | 0.11667 | 0.11667 | Test Charge taken and line stood ok | Close | 0.058333 |  |  | 3077
139 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR | 0.26875 | 0.26875 | 0.27708 | 0 | 0.2 | 0.2 | Test Charge taken and line stood ok | Close | 0.1 |  |  | 4951
140 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | Wind_F2 | 0 | 0 | 50% | Tripped on OCR | 0.75 | 0.75 | 0.75556 | 0 | 0.13333 | 0.13333 | Test Charge taken and line stood ok | Close | 0.066667 |  |  | 3421
141 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0.68889 | 0.68889 | 0.69444 | 0 | 0.13333 | 0.13333 | Test Charge taken and line stood ok | Close | 0.066667 |  |  | 3093
142 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-27 | Wind_F2 | 0 | 0 | 50% | Tripped on EFR found 33kv B-phase UG cable insulation faliure and cable puncher | 0.64167 | 0.64167 | 0.84097 | 0 | 4.7833 | 4.7833 | Spare feeder cable connected to the H pole and chrged | Close | 2.3917 |  |  | 117521
143 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-27 | Wind_F1 | 0 | 0 | 50% | Feeder #04 Shutdown for f#02 cable replacement work | 0.76944 | 0.76944 | 0.93611 | 0 | 4 | 4 | F#01 cable connected to the DP yard F#01 and F#4 cable conneted to DP yard F#02 | Close | 2 |  |  | 90086
144 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | Wind_F4 | 0 | 0 | 50% | Tripped on OCR found fuse failure at jk metering point | 0.80347 | 0.80347 | 0.81042 | 0 | 0.16667 | 0.16667 | Test Charge taken and line stood ok | Close | 0.083333 |  |  | 3276
145 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | KUD04 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.81042 | 0.81042 | 0.89583 | 0 | 2.05 | 2.05 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.08913 |  |  | 3358
146 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | KUD05 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.81042 | 0.81042 | 0.89583 | 0 | 2.05 | 2.05 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.08913 |  |  | 3358
147 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | KUD09 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.81042 | 0.81042 | 0.89583 | 0 | 2.05 | 2.05 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.08913 |  |  | 3358
148 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | KUD21 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.81042 | 0.81042 | 0.89583 | 0 | 2.05 | 2.05 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.08913 |  |  | 3358
149 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | KUD22 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.81042 | 0.81042 | 0.89583 | 0 | 2.05 | 2.05 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.08913 |  |  | 3358
150 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | KUD23 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.81042 | 0.81042 | 0.89583 | 0 | 2.05 | 2.05 | During the Line inspection Found R-phase fuse failure at JK metering point | Close | 0.08913 |  |  | 3358
151 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | Wind_F4 | 0 | 0 | 50% | LC taken for KUD-18 JK metering R phase fuse replacement. | 0.89583 | 0.89583 | 0.91458 | 0 | 0.45 | 0.45 | KUD-18 JK metering R phase fuse replacement done. | Close | 0.225 |  |  | 8845
152 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | Wind_F1 | 0 | 0 | 50% | Tripped on EFR | 0.77708 | 0.77708 | 0.78264 | 0 | 0.13333 | 0.13333 | Test Charge taken and line stood ok | Close | 0.066667 |  |  | 3093
153 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-04 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0 | 0 | 0.0097222 | 0 | 0.23333 | 0.23333 | Test Charge taken and line stood ok | Close | 0.11667 |  |  | 6032
154 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-11 | Wind_F4 | 0 | 0 | 50% | Tripped on EFR | 0.26597 | 0.26597 | 0.27292 | 0 | 0.16667 | 0.16667 | Test Charge taken and line stood ok | Close | 0.083333 |  |  | 2060
155 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-12 | Wind_F4 | 0 | 0 | 50% | Tripped on OCR found fuse failure at jk metering point | 0.80833 | 0.80833 | 0.82639 | 0 | 0.43333 | 0.43333 | Test Charge taken and line stood ok | Close | 0.21667 |  |  | 6574
156 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-12 | KUD04 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.82639 | 0.82639 | 0.92014 | 0 | 2.25 | 2.25 | During the Line inspection Found R & B-phase fuse failure at JK metering point | Close | 0.097826 |  |  | 2845
157 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-12 | KUD05 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.82639 | 0.82639 | 0.92014 | 0 | 2.25 | 2.25 | During the Line inspection Found R & B-phase fuse failure at JK metering point | Close | 0.097826 |  |  | 2845
158 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-12 | KUD09 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.82639 | 0.82639 | 0.92014 | 0 | 2.25 | 2.25 | During the Line inspection Found R & B-phase fuse failure at JK metering point | Close | 0.097826 |  |  | 2845
159 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-12 | KUD21 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.82639 | 0.82639 | 0.92014 | 0 | 2.25 | 2.25 | During the Line inspection Found R & B-phase fuse failure at JK metering point | Close | 0.097826 |  |  | 2845
160 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-12 | KUD22 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.82639 | 0.82639 | 0.92014 | 0 | 2.25 | 2.25 | During the Line inspection Found R & B-phase fuse failure at JK metering point | Close | 0.097826 |  |  | 2845
161 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-12 | KUD23 | O2R3 | JK | 4.348% | F#02 Line inspection and Metering points inspection under progress | 0.82639 | 0.82639 | 0.92014 | 0 | 2.25 | 2.25 | During the Line inspection Found R & B-phase fuse failure at JK metering point | Close | 0.097826 |  |  | 2845
162 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-12 | Wind_F4 | 0 | 0 | 50% | LC taken for KUD-18 JK metering point fuse replacement. | 0.92014 | 0.92014 | 0.93958 | 0 | 0.46667 | 0.46667 | KUD-18 JK metering point R & B- phase fuse replacement done. | Close | 0.23333 |  |  | 7080
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
|  |  |  | 1899-12-31 | [9 empty] | 0 | 0 | 0
Formulas:
Month = IGA_BD[[#This Row],[Date]]-DAY(IGA_BD[[#This Row],[Date]])+1

## Grid_BD
Sr. No. | Finacial Year | Calendor Year | Operating Year | Month | Date | Affected Feeder | SPV | Concumaer | Plant Equivalent Weightage | Breakdown Description | Breakdown Type | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Fault Category | Paired WTG for Enegy based MA | Loss of KWH | Estimated Energy Loss (kWh) | Curtailment Order imit. | EGA_Including_CurtailmentOrder | PTW No. | Job Card No.
1 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | Line1 |  |  | 100% | 220 KV Grid failure from GSS due to DC failure at GSS | Breakdown | 0.89722 | 0.89722 | 0.99931 | 0 | 2.45 | 2.45 | Rectification work in progress | Open | 2.45 |  |  |  | 24250 |  | 100%
2 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-21 | Line1 |  |  | 100% | 220 KV Grid failure from GSS due to DC failure at GSS | Breakdown | 0 | 0 | 0.034722 | 0 | 0.83333 | 0.83333 | After the rectification work done grid resumed and charged the line | Close | 0.83333 |  |  |  | 3824 |  | 100%
3 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-22 | Line1 |  |  | 100% | 220 KV Grid failure from GSS due to DC failure at GSS | Breakdown | 0.62639 | 0.62639 | 0.65208 | 0 | 0.61667 | 0.61667 | After the rectification work done grid resumed and charged the line | Close | 0.61667 |  |  |  | 1685 |  | 100% |  |  | [
4 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-22 | Line1 |  |  | 100% | 220 KV Grid failure from GSS due to DC failure at GSS | Breakdown | 0.72917 | 0.72917 | 0.73194 | 0 | 0.066667 | 0.066667 | After the rectification work done grid resumed and charged the line | Close | 0.066667 |  |  |  | 210 |  | 100%
5 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-27 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.49653 | 0.49653 | 0.52083 | 0 | 0.58333 | 0.58333 | Charged after Grid Resume | Close | 0.58333 |  |  |  | 1842 |  | 100%
6 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-22 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.47361 | 0.47361 | 0.61458 | 0 | 3.3833 | 3.3833 | Charged after Grid Resume | Close | 3.3833 |  |  |  | 98380 |  | 100%
7 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-23 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.46597 | 0.46597 | 0.57708 | 0 | 2.6667 | 2.6667 | Charged after Grid Resume | Close | 2.6667 |  |  |  | 100457 |  | 100%
8 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.46667 | 0.46667 | 0.52361 | 0 | 1.3667 | 1.3667 | Charged after Grid Resume | Close | 1.3667 |  |  |  | 66812 |  | 100%
9 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.54097 | 0.54097 | 0.57222 | 0 | 0.75 | 0.75 | Charged after Grid Resume | Close | 0.75 |  |  |  | 36665 |  | 100%
10 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.42153 | 0.42153 | 0.44444 | 0 | 0.55 | 0.55 | Charged after Grid Resume | Close | 0.55 |  |  |  | 10401 |  | 100%
11 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-12 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.78681 | 0.78681 | 0.8125 | 0 | 0.61667 | 0.61667 | Charged after Grid Resume | Close | 0.61667 |  |  |  | 9067 |  | 100%
12 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-16 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.54375 | 0.54375 | 0.57292 | 0 | 0.7 | 0.7 | Charged after Grid Resume | Close | 0.7 |  |  |  | 35384 |  | 100%
13 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-17 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.47222 | 0.47222 | 0.50347 | 0 | 0.75 | 0.75 | Charged after Grid Resume | Close | 0.75 |  |  |  | 27112 |  | 100%
14 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-17 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.57431 | 0.57431 | 0.60208 | 0 | 0.66667 | 0.66667 | Charged after Grid Resume | Close | 0.66667 |  |  |  | 24099 |  | 100%
15 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-18 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.44167 | 0.44167 | 0.46389 | 0 | 0.53333 | 0.53333 | Charged after Grid Resume | Close | 0.53333 |  |  |  | 21871 |  | 100%
16 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.49653 | 0.49653 | 0.51389 | 0 | 0.41667 | 0.41667 | Charged after Grid Resume | Close | 0.41667 |  |  |  | 20966 |  | 100%
17 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.53472 | 0.53472 | 0.55139 | 0 | 0.4 | 0.4 | Charged after Grid Resume | Close | 0.4 |  |  |  | 20127 |  | 100%
18 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.56736 | 0.56736 | 0.58958 | 0 | 0.53333 | 0.53333 | Charged after Grid Resume | Close | 0.53333 |  |  |  | 26836 |  | 100%
19 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | Line1 | Line2 | Line3 | 100% | Grid failure from GSS | Breakdown | 0.45833 | 0.45833 | 0.475 | 0 | 0.4 | 0.4 | Charged after Grid Resume | Close | 0.4 |  |  |  | 18978 |  | 100%
20 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-23 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.50694 | 0.50694 | 0.52361 | 0 | 0.4 | 0.4 | Charged after Grid Resume | Close | 0.4 |  |  |  | 19818 |  | 100%
21 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | Line1 |  |  | 100% | Grid failure from GSS | Breakdown | 0.42431 | 0.42431 | 0.45486 | 0 | 0.73333 | 0.73333 | Charged after Grid Resume | Close | 0.73333 |  |  |  | 37101 |  | 100%
b
Formulas:
Month = Grid_BD[[#This Row],[Date]]-DAY(Grid_BD[[#This Row],[Date]])+1

## PM
Sr. No. | Location No. | Location Type | FY | CY | Cycle No. | Frequency | PM Title | Planned Maintenance Date | Actual Maintenance Date | Delay | Remark
1 | KUD01 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-05-23 | 2023-06-05 | 13
2 | KUD02 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-09-01 | 2023-08-25 | -7
3 | KUD03 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-08-16 | 2023-08-21 | 5
4 | KUD04 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-08-18 | 2023-08-17 | -1
5 | KUD05 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-08-20 | 2023-06-12 | -69
6 | KUD06 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-08-21 | 2023-08-23 | 2
7 | KUD07 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-08-23 | 2023-09-27 | 35
8 | KUD08 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-08-25 | 2023-09-28 | 34
9 | KUD09 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-08-28 | 2023-08-28 | 0
10 | KUD10 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-05-11 | 2023-05-11 | 0
11 | KUD11 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-05-13 | 2023-05-16 | 3
12 | KUD12 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-05-15 | 2023-05-19 | 4
13 | KUD13 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-05-16 | 2023-05-25 | 9
14 | KUD14 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-05-18 | 2023-06-24 | 37
15 | KUD15 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-05-27 | 2023-06-14 | 18
16 | KUD16 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-05-30 | 2023-06-17 | 18
17 | KUD17 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-06-01 | 2023-07-08 | 37
18 | KUD18 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-08-30 | 2023-09-06 | 7
19 | KUD19 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-09-01 | 2023-05-30 | -94
20 | KUD20 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-09-04 | 2023-06-22 | -74
21 | KUD21 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-09-08 | 2023-09-01 | -7
22 | KUD22 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-09-06 | 2023-09-04 | -2
23 | KUD23 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | A-Service | 2023-09-04 | 2023-08-30 | -5
24 | KUD01 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-05-24 | 2023-06-07 | 14
25 | KUD02 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-09-02 | 2023-08-26 | -7
26 | KUD03 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-08-17 | 2023-08-22 | 5
27 | KUD04 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-08-19 | 2023-08-19 | 0
28 | KUD05 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-08-21 | 2023-06-13 | -69
29 | KUD06 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-08-22 | 2023-08-24 | 2
30 | KUD07 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-08-24 | 2023-09-30 | 37
31 | KUD08 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-08-26 | 2023-09-29 | 34
32 | KUD09 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-08-29 | 2023-08-29 | 0
33 | KUD10 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-05-12 | 2023-05-15 | 3
34 | KUD11 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-05-14 | 2023-05-18 | 4
35 | KUD12 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-05-16 | 2023-05-20 | 4
36 | KUD13 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-05-17 | 2023-05-27 | 10
37 | KUD14 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-05-19 | 2023-06-24 | 36
38 | KUD15 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-05-28 | 2023-06-15 | 18
39 | KUD16 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-05-31 | 2023-06-19 | 19
40 | KUD17 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-06-02 | 2023-07-09 | 37
41 | KUD18 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-08-31 | 2023-09-07 | 7
42 | KUD19 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-09-02 | 2023-06-02 | -92
43 | KUD20 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-09-05 | 2023-06-22 | -75
44 | KUD21 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-09-09 | 2023-09-02 | -7
45 | KUD22 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-09-07 | 2023-09-05 | -2
46 | KUD23 | V120 2.2MW | 2023-24 | 2023 | Day-2 | 50Hz | A-Service | 2023-09-05 | 2023-08-31 | -5
47 | KUD01 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-13 | 2023-10-05 | -8
48 | KUD02 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-14 | 2023-12-15 | 62
49 | KUD03 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-11-13 | 2023-12-01 | 18
50 | KUD04 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-11-14 | 2023-12-07 | 23
51 | KUD05 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-14 | 2023-10-05 | -9
52 | KUD06 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-15 | 2023-11-15 | 31
53 | KUD07 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-16 | 2023-11-16 | 31
54 | KUD08 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-17 | 2023-11-17 | 31
55 | KUD09 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-18 | 2023-11-18 | 31
56 | KUD10 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-03 | 2023-10-10 | 7
57 | KUD11 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-06 | 2023-10-03 | -3
58 | KUD12 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-04 | 2023-10-03 | -1
59 | KUD13 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-05 | 2023-10-07 | 2
60 | KUD14 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-12 | 2023-10-12 | 0
61 | KUD15 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-09 | 2023-10-04 | -5
62 | KUD16 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-10 | 2023-10-04 | -6
63 | KUD17 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-11 | 2023-10-09 | -2
64 | KUD18 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-13 | 2023-12-13 | 61
65 | KUD19 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-07 | 2023-10-06 | -1
66 | KUD20 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-15 | 2023-10-07 | -8
67 | KUD21 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-16 | 2023-12-19 | 64
68 | KUD22 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-17 | 2023-12-21 | 65
69 | KUD23 | V120 2.2MW | 2023-24 | 2023 | Day-1 | 50Hz | B-Service | 2023-10-18 | 2023-12-05 | 48
70 | KUD01 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-04-01 | 2024-04-02 | 1
71 | KUD02 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-04-03 | 2024-03-28 | -6
72 | KUD03 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-04-29 | 2024-03-22 | -38
73 | KUD04 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-05-01 | 2024-03-25 | -37
74 | KUD05 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-04-04 | 2024-04-05 | 1
75 | KUD06 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-04-08 | 2024-04-08 | 0
76 | KUD07 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-04-11 | 2024-04-12 | 1
77 | KUD08 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-04-15 | 2024-04-15 | 0
78 | KUD09 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-04-18 | 2024-04-18 | 0
79 | KUD10 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-04-25 | 2024-05-04 | 9
80 | KUD11 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-04-28 | 2024-03-30 | -29
81 | KUD12 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-04-29 | 2024-04-24 | -5
82 | KUD13 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-05-01 | 2024-04-26 | -5
83 | KUD14 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-05-03 | 2024-04-27 | -6
84 | KUD15 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-05-05 | 2024-04-22 | -13
85 | KUD16 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-05-07 | 2024-03-18 | -50
86 | KUD17 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-05-10 | 2024-05-04 | -6
87 | KUD18 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-05-13 | 2024-04-30 | -13
88 | KUD19 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-05-15 | 2024-05-11 | -4
89 | KUD20 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-05-17 | 2024-05-09 | -8
90 | KUD21 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-05-19 | 2024-05-16 | -3
91 | KUD22 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-05-22 | 2024-05-16 | -6
92 | KUD23 | V120 2.2MW | 2023-24 | 2024 | Day-1 | 50Hz | C-Service | 2024-05-24 | 2024-05-11 | -13
93 | KUD01 | V120 2.2MW | 2023-24 | 2024 | Day-2 | 50Hz | C-Service | 2024-04-02 | 2024-04-03 | 1
94 | KUD02 | V120 2.2MW | 2023-24 | 2024 | Day-2 | 50Hz | C-Service | 2024-04-04 | 2024-04-01 | -3
95 | KUD03 | V120 2.2MW | 2023-24 | 2024 | Day-2 | 50Hz | C-Service | 2024-04-30 | 2024-03-23 | -38
96 | KUD04 | V120 2.2MW | 2023-24 | 2024 | Day-2 | 50Hz | C-Service | 2024-05-02 | 2024-03-27 | -36
97 | KUD05 | V120 2.2MW | 2023-24 | 2024 | Day-2 | 50Hz | C-Service | 2024-04-05 | 2024-04-06 | 1
98 | KUD06 | V120 2.2MW | 2023-24 | 2024 | Day-2 | 50Hz | C-Service | 2024-04-09 | 2024-04-10 | 1
99 | KUD07 | V120 2.2MW | 2023-24 | 2024 | Day-2 | 50Hz | C-Service | 2024-04-12 | 2024-04-13 | 1
100 | KUD08 | V120 2.2MW | 2023-24 | 2024 | Day-2 | 50Hz | C-Service | 2024-04-16 | 2024-04-17 | 1
101 | KUD09 | V120 2.2MW | 2023-24 | 2024 | Day-2 | 50Hz | C-Service | 2024-04-19 | 2024-04-19 | 0
102 | KUD10 | V120 2.2MW | 2023-24 | 2024 | Day-2 | 50Hz | C-Service | 2024-04-26 | 2024-05-06 | 10
103 | KUD11 | V120 2.2MW | 2023-24 | 2024 | Day-2 | 50Hz | C-Service | 2024-04-29 | 2024-04-16 | -13
104 | KUD12 | V120 2.2MW | 2023-24 | 2024 | Day-2 | 50Hz | C-Service | 2024-04-30 | 2024-04-23 | -7
105 | KUD13 | V120 2.2MW | 2023-24 | 2024 | Day-2 | 50Hz | C-Service | 2024-05-02 | 2024-04-27 | -5
106 | KUD14 | V120 2.2MW | 2024-25 | 2024 | Day-2 | 50Hz | C-Service | 2024-05-04 | 2024-04-29 | -5
107 | KUD15 | V120 2.2MW | 2024-25 | 2024 | Day-2 | 50Hz | C-Service | 2024-05-06 | 2024-04-23 | -13
108 | KUD16 | V120 2.2MW | 2024-25 | 2024 | Day-2 | 50Hz | C-Service | 2024-05-08 | 2024-03-19 | -50
109 | KUD17 | V120 2.2MW | 2024-25 | 2024 | Day-2 | 50Hz | C-Service | 2024-05-11 | 2024-05-06 | -5
110 | KUD18 | V120 2.2MW | 2024-25 | 2024 | Day-2 | 50Hz | C-Service | 2024-05-14 | 2024-05-02 | -12
111 | KUD19 | V120 2.2MW | 2024-25 | 2024 | Day-2 | 50Hz | C-Service | 2024-05-16 | 2024-05-14 | -2
112 | KUD20 | V120 2.2MW | 2024-25 | 2024 | Day-2 | 50Hz | C-Service | 2024-05-18 | 2024-05-10 | -8
113 | KUD21 | V120 2.2MW | 2024-25 | 2024 | Day-2 | 50Hz | C-Service | 2024-05-20 | 2024-05-18 | -2
114 | KUD22 | V120 2.2MW | 2024-25 | 2024 | Day-2 | 50Hz | C-Service | 2024-05-23 | 2024-05-17 | -6
115 | KUD23 | V120 2.2MW | 2024-25 | 2024 | Day-2 | 50Hz | C-Service | 2024-05-25 | 2024-05-15 | -10
116 | KUD01 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-09-28 | 2024-09-28 | 0
117 | KUD02 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-09-23 | 2024-09-23 | 0
118 | KUD03 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-09-28 | 2024-09-28 | 0
119 | KUD04 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-09-29 | 2024-09-29 | 0
120 | KUD05 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-09-29 | 2024-09-29 | 0
121 | KUD06 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-10-03 | 2024-10-09 | 6
122 | KUD07 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-10-04 | 2024-10-10 | 6
123 | KUD08 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-10-14 | 2024-10-12 | -2
124 | KUD09 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-10-15 | 2024-10-03 | -12
125 | KUD10 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-10-17 | 2024-10-14 | -3
126 | KUD11 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-10-18 | 2024-11-13 | 26
127 | KUD12 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-10-21 | 2024-10-22 | 1
128 | KUD13 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-10-13 | 2024-10-24 | 11
129 | KUD14 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-10-28 | 2024-11-12 | 15
130 | KUD15 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-10-29 | 2024-10-25 | -4
131 | KUD16 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-11-02 | 2024-11-04 | 2
132 | KUD17 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-11-04 | 2024-11-14 | 10
133 | KUD18 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-11-05 | 2024-11-05 | 0
134 | KUD19 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-11-06 | 2024-11-06 | 0
135 | KUD20 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-11-08 | 2024-11-09 | 1
136 | KUD21 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-11-11 | 2024-12-19 | 38
137 | KUD22 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-11-12 | 2024-11-11 | -1
138 | KUD23 | V120 2.2MW | 2024-25 | 2024 | Day-1 | 50Hz | B-Service | 2024-11-13 | 2024-12-05 | 22
139 | KUD01 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-03-04 | 2025-04-17 | 44
140 | KUD02 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-03-06 | 2025-03-12 | 6
141 | KUD03 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-03-09 | 2025-03-25 | 16
142 | KUD04 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-03-12 | 2025-04-09 | 28
143 | KUD05 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-03-14 | 2025-03-15 | 1
144 | KUD06 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-03-17 | 2025-03-27 | 10
145 | KUD07 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-03-20 | 2025-04-02 | 13
146 | KUD08 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-03-22 | 2025-04-07 | 16
147 | KUD09 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-03-26 | 2025-04-28 | 33
148 | KUD10 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-04-02 | 2025-05-07 | 35
149 | KUD11 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-04-07 | 2025-04-16 | 9
150 | KUD12 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-04-10 | 2025-04-23 | 13
151 | KUD13 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-04-14 | 2025-04-04 | -10
152 | KUD14 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-04-17 | 2025-04-30 | 13
153 | KUD15 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-04-21 | 2025-04-12 | -9
154 | KUD16 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-04-24 | 2025-05-12 | 18
155 | KUD17 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-04-28 | 2025-04-26 | -2
156 | KUD18 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-05-02 | 2025-05-06 | 4
157 | KUD19 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-05-05 | 2025-05-14 | 9
158 | KUD20 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-05-08 | 2025-05-05 | -3
159 | KUD21 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-05-12 | 2025-05-10 | -2
160 | KUD22 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-05-15 | 2025-05-17 | 2
161 | KUD23 | V120 2.2MW | 2025-26 | 2025 | Day-1 | 50Hz | C-Service | 2025-05-18 | 2025-05-17 | -1
162 | KUD01 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-03-05 | 2025-04-22 | 48
163 | KUD02 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-03-07 | 2025-03-21 | 14
164 | KUD03 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-03-10 | 2025-03-26 | 16
165 | KUD04 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-03-13 | 2025-04-10 | 28
166 | KUD05 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-03-15 | 2025-03-20 | 5
167 | KUD06 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-03-18 | 2025-03-28 | 10
168 | KUD07 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-03-21 | 2025-04-03 | 13
169 | KUD08 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-03-23 | 2025-04-08 | 16
170 | KUD09 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-03-27 | 2025-04-29 | 33
171 | KUD10 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-04-03 | 2025-05-08 | 35
172 | KUD11 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-04-08 | 2025-04-19 | 11
173 | KUD12 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-04-11 | 2025-04-24 | 13
174 | KUD13 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-04-15 | 2025-04-05 | -10
175 | KUD14 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-04-18 | 2025-05-02 | 14
176 | KUD15 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-04-22 | 2025-05-09 | 17
177 | KUD16 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-04-25 | 2025-05-13 | 18
178 | KUD17 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-04-29 | 2025-04-27 | -2
179 | KUD18 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-05-03 | 2025-05-09 | 6
180 | KUD19 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-05-06 | 2025-05-23 | 17
181 | KUD20 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-05-09 | 2025-05-15 | 6
182 | KUD21 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-05-13 | 2025-05-16 | 3
183 | KUD22 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-05-16 | 2025-05-19 | 3
184 | KUD23 | V120 2.2MW | 2025-26 | 2025 | Day-2 | 50Hz | C-Service | 2025-05-19 | 2025-05-21 | 2

## Modelling New (hidden)
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | Bugt Capacity | CC*Bugt | Capacity | 50.6
1 | February | 2 | 2023-02-01 | 2023 | FY23 | 28 |  |  | 6.4041 |  |  | 5226.9829 |  |  |  | 0 |  |  | 186.678 | 0 | 0 | [6 empty] | 6.4041 | 6.4041 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5% |  |  | Hourly reactive power bugt | 2.53
2 | March | 3 | 2023-03-01 | 2023 | FY23 | 31 |  |  | 5.9682 |  |  | 2550.8419 |  |  |  | 0 |  |  | 82.2852 | 0 | 0 | [6 empty] | 5.9682 | 6.1861 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5% |  |  | Day | 60.72
3 | April | 4 | 2023-04-01 | 2023 | FY23 | 30 |  |  | 5.6311 |  |  | 5913.5255 | 26.4 |  |  | 0 |  |  | 197.1175 | 0 | 0 | 31.11% | [5 empty] | 5.6311 | 6.0011 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
4 | May | 5 | 2023-05-01 | 2023 | FY23 | 31 |  |  | 7.1311 |  |  | 11097.9571 | 50.6 |  |  | 0 |  |  | 357.9986 | 0 | 0 | 29.48% | [5 empty] | 7.1311 | 6.2836 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
5 | June | 6 | 2023-06-01 | 2023 | FY23 | 30 |  |  | 9.453 |  |  | 19352.4784 | 50.6 |  |  | 0 |  |  | 645.0826 | 0 | 0 | 53.12% | [5 empty] | 9.453 | 6.9175 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
6 | July | 7 | 2023-07-01 | 2023 | FY23 | 31 |  |  | 10.3038 |  |  | 23096.4358 | 50.6 |  |  | 0 |  |  | 745.0463 | 0 | 0 | 61.35% | [5 empty] | 10.3038 | 7.4819 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
7 | August | 8 | 2023-08-01 | 2023 | FY23 | 31 |  |  | 8.5195 |  |  | 19809.7697 | 50.6 |  |  | 0 |  |  | 639.0248 | 0 | 0 | 52.62% | [5 empty] | 8.5195 | 7.6301 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
8 | September | 9 | 2023-09-01 | 2023 | FY23 | 30 |  |  | 7.2367 |  |  | 11411.0191 | 50.6 |  |  | 0 |  |  | 380.3673 | 0 | 0 | 31.32% | [5 empty] | 7.2367 | 7.5809 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
9 | October | 10 | 2023-10-01 | 2023 | FY23 | 31 |  |  | 6.0016 |  |  | 6390.1646 | 50.6 |  |  | 0 |  |  | 206.1343 | 0 | 0 | 16.97% | [5 empty] | 6.0016 | 7.4054 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
10 | November | 11 | 2023-11-01 | 2023 | FY23 | 30 |  |  | 6.7074 |  |  | 9585.0871 | 50.6 |  |  | 0 |  |  | 319.5029 | 0 | 0 | 26.31% | [5 empty] | 6.7074 | 7.3356 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
11 | December | 12 | 2023-12-01 | 2023 | FY23 | 31 |  |  | 7.0533 |  |  | 12506.529 | 50.6 |  |  | 0 |  |  | 403.4364 | 0 | 0 | 33.22% | [5 empty] | 7.0533 | 7.31 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
12 | January | 2 | 2024-01-01 | 2024 | FY23 | 31 |  |  | 7.4111 |  |  | 11958.6075 | 50.6 |  |  | 0 |  |  | 385.7615 | 0 | 0 | 31.77% | [5 empty] | 7.4111 | 7.3184 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
13 | February | 3 | 2024-02-01 | 2024 | FY24 | 29 |  |  | 6.4041 |  |  | 9128.6623 | 50.6 |  |  | 0 |  |  | 314.7815 | 0 | 0 | 25.92% | [5 empty] | 6.4041 | 6.4041 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
14 | March | 4 | 2024-03-01 | 2024 | FY24 | 31 |  |  | 5.9682 |  |  | 7942.2128 | 50.6 |  |  | 0 |  |  | 256.2004 | 0 | 0 | 21.1% | [5 empty] | 5.9682 | 6.1861 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
15 | April | 5 | 2024-04-01 | 2024 | FY24 | 30 |  |  | 5.6311 |  |  | 8198.5346 | 50.6 |  |  | 0 |  |  | 273.2845 | 0 | 0 | 22.5% | [5 empty] | 5.6311 | 6.0011 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
16 | May | 6 | 2024-05-01 | 2024 | FY24 | 31 |  |  | 7.1311 |  |  | 13797.5338 | 50.6 |  |  | 0 |  |  | 445.0817 | 0 | 0 | 36.65% | [5 empty] | 7.1311 | 6.2836 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
17 | June | 7 | 2024-06-01 | 2024 | FY24 | 30 |  |  | 9.453 |  |  | 21196.2113 | 50.6 |  |  | 0 |  |  | 706.5404 | 0 | 0 | 58.18% | [5 empty] | 9.453 | 6.9175 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
18 | July | 8 | 2024-07-01 | 2024 | FY24 | 31 |  |  | 10.3038 |  |  | 25295.4786 | 50.6 |  |  | 0 |  |  | 815.9832 | 0 | 0 | 67.19% | [5 empty] | 10.3038 | 7.4819 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
19 | August | 9 | 2024-08-01 | 2024 | FY24 | 31 |  |  | 8.5195 |  |  | 21696.1219 | 50.6 |  |  | 0 |  |  | 699.8749 | 0 | 0 | 57.63% | [5 empty] | 8.5195 | 7.6301 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
20 | September | 10 | 2024-09-01 | 2024 | FY24 | 30 |  |  | 7.2367 |  |  | 12497.7661 | 50.6 |  |  | 0 |  |  | 416.5922 | 0 | 0 | 34.3% | [5 empty] | 7.2367 | 7.5809 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
21 | October | 11 | 2024-10-01 | 2024 | FY24 | 31 |  |  | 6.0016 |  |  | 6998.749 | 50.6 |  |  | 0 |  |  | 225.7661 | 0 | 0 | 18.59% | [5 empty] | 6.0016 | 7.4054 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
22 | November | 12 | 2024-11-01 | 2024 | FY24 | 30 |  |  | 6.7074 |  |  | 10498.1235 | 50.6 |  |  | 0 |  |  | 349.9375 | 0 | 0 | 28.82% | [5 empty] | 6.7074 | 7.3356 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
23 | December | 2 | 2024-12-01 | 2024 | FY24 | 31 |  |  | 7.0533 |  |  | 13697.5516 | 50.6 |  |  | 0 |  |  | 441.8565 | 0 | 0 | 36.38% | [5 empty] | 7.0533 | 7.31 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
24 | January | 3 | 2025-01-01 | 2025 | FY24 | 31 |  |  | 7.4111 |  |  | 13097.6589 | 50.6 |  |  | 0 |  |  | 422.5051 | 0 | 0 | 34.79% | [5 empty] | 7.4111 | 7.3184 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
25 | February | 4 | 2025-02-01 | 2025 | FY24 | 28 |  |  | 6.4041 |  |  | 9998.2129 | 50.6 |  |  | 0 |  |  | 357.079 | 0 | 841.785 | 29.4% | [5 empty] | 6.4041 | 7.2481 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
26 | March | 5 | 2025-03-01 | 2025 | FY24 | 31 |  |  | 5.9682 |  |  | 8698.4452 | 50.6 |  |  | 3 |  |  | 280.595 | 841.785 | 841.785 | 23.11% | 23.11% | 23.11% | 50.6 | 50.6 |  | 5.9682 | 7.1567 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
27 | April | 6 | 2025-04-01 | 2025 | FY25 | 30 |  |  | 5.6311 |  |  | 8198.53 | 50.6 |  |  | 30 |  |  | 273.2843 | 8198.53 | 8198.53 | 22.5% | 22.5% | 22.5% | 50.6 | 50.6 |  | 5.6311 | 5.6311 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
28 | May | 7 | 2025-05-01 | 2025 | FY25 | 31 |  |  | 7.1311 |  |  | 13797.53 | 50.6 |  |  | 31 |  |  | 445.0816 | 13797.53 | 21996.06 | 36.65% | 36.65% | 29.69% | 50.6 | 50.6 |  | 7.1311 | 6.3811 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
29 | June | 8 | 2025-06-01 | 2025 | FY25 | 30 |  |  | 9.453 |  |  | 21196.21 | 50.6 |  |  | 30 |  |  | 706.5403 | 21196.21 | 43192.27 | 58.18% | 58.18% | 39.08% | 50.6 | 50.6 |  | 9.453 | 7.4051 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
30 | July | 9 | 2025-07-01 | 2025 | FY25 | 31 |  |  | 10.3038 |  |  | 25295.48 | 50.6 |  |  | 13 |  |  | 815.9832 | 10607.7819 | 53800.0519 | 67.19% | 67.19% | 42.6% | 50.6 | 50.6 |  | 10.3038 | 8.1297 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
31 | August | 10 | 2025-08-01 | 2025 | FY25 | 31 |  |  | 8.5195 |  |  | 21696.12 | 50.6 |  |  | 0 |  |  | 699.8748 | 0 | 53800.0519 | 57.63% |  | 42.6% | 50.6 | 50.6 |  | 8.5195 | 8.2077 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
32 | September | 11 | 2025-09-01 | 2025 | FY25 | 30 |  |  | 7.2367 |  |  | 12497.77 | 50.6 |  |  | 0 |  |  | 416.5923 | 0 | 53800.0519 | 34.3% |  | 42.6% |  | 50.6 |  | 7.2367 | 8.0459 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
33 | October | 12 | 2025-10-01 | 2025 | FY25 | 31 |  |  | 6.0016 |  |  | 6998.75 | 50.6 |  |  | 0 |  |  | 225.7661 | 0 | 53800.0519 | 18.59% |  | 42.6% |  | 50.6 |  | 6.0016 | 7.7538 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
34 | November | 2 | 2025-11-01 | 2025 | FY25 | 30 |  |  | 6.7074 |  |  | 10498.12 | 50.6 |  |  | 0 |  |  | 349.9373 | 0 | 53800.0519 | 28.82% |  | 42.6% |  | 50.6 |  | 6.7074 | 7.623 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
35 | December | 3 | 2025-12-01 | 2025 | FY25 | 31 |  |  | 7.0533 |  |  | 13697.55 | 50.6 |  |  | 0 |  |  | 441.8565 | 0 | 53800.0519 | 36.38% |  | 42.6% |  | 50.6 |  | 7.0533 | 7.5597 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
36 | January | 4 | 2026-01-01 | 2026 | FY25 | 31 |  |  | 7.4111 |  |  | 13097.66 | 50.6 |  |  | 0 |  |  | 422.5052 | 0 | 53800.0519 | 34.79% |  | 42.6% |  | 50.6 |  | 7.4111 | 7.5449 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
37 | February | 5 | 2026-02-01 | 2026 | FY25 | 28 |  |  | 6.4041 |  |  | 9998.21 | 50.6 |  |  | 0 |  |  | 357.0789 | 0 | 53800.0519 | 29.4% |  | 42.6% |  | 50.6 |  | 6.4041 | 7.4411 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
38 | March | 6 | 2026-03-01 | 2026 | FY25 | 31 |  |  | 5.9682 |  |  | 8698.45 | 50.6 |  |  | 0 |  |  | 280.5952 | 0 | 53800.0519 | 23.11% |  | 42.6% |  | 50.6 |  | 5.9682 | 7.3184 | 95.55% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## Basic Data (hidden)
[5 empty] | IGA | [7 empty] | No | Description |  |  | Major Breakdown | Breakdown | [8 empty] | Inverter Station | Inverter | Module | SCB | String Type | Equipment | WTG NO. | Generator | Consumer | Capacity | % Plant Equiva. Weightage | USS YARD | METERING YARD | FEEDER | OG | TRANSFER | Fault Category Plant BD sheet | Status | Fault Category
WTG NO. | Generator | Consumer | Capacity | % Plant Equiva. Weightage | USS YARD | METERING YARD | FEEDER | OG | TRANSFER |  |  |  | 0 | Turbine OK | 0 | 45 | Breakdown | Curtailment Order | Last 7 Days Performance | [7 empty] | IS1 | Inv1 | M1 | SCB1 | Str_Typ1(540*29) | Tx | IS1Inv1M1 | O2R4_Solar | SGDCIPL | 2011.44 | 47.66% | NA | MY1_Solar | Solar_F1 | Line1 | TX1 | Module | Open | WTG | IG | EG
KUD01 | O2R1 | KSIPL | 2.2 | 4.348% | KUD01 | MY1 | Wind_F1 | Line1 | TX2 | Total WInd Capacity | 50.6 | Open | 1 | Illegal InitVal data in PROM | 0 | 45 | Manual Stop | Shutdown | Date | 2025-07-13 | 2025-07-12 | 2025-07-11 | 2025-07-10 | 2025-07-09 | 2025-07-08 | 2025-07-07 | IS2 | Inv2 | M2 | SCB2 | Str_Typ2(545*29) | MVP | IS1Inv1M2 | O2R4_Solar | SGDCIPL | 2046.53 | 48.5% | NA | MY1_Solar | Solar_F1 | Line1 | TX1 | Cables | Close | WTG Unscheduled Maintenance | IG Unscheduled Maintenance | EG Unscheduled Maintenance
KUD02 | O2R3 | JK | 2.2 | 4.348% | KUD02 | MY6 | Wind_F2 | Line1 | TX2 | Total Solar Capacity | 4220 | Close | 2 | Conflict: Rack/Turbinetype | 0 | 45 | ROW |  | Energy (MWh) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | IS3 | Inv3 |  | SCB3 | Str_Typ3(550*29) | Aux_Tx | IS2Inv2M1 | [9 empty] | String Fuses |  | WTG Breakdown Maintenance | IG Breakdown Maintenance | EG Breakdown Maintenance
KUD03 | O2R1 | KSIPL | 2.2 | 4.348% | KUD03 | MY1 | Wind_F1 | Line1 | TX2 |  |  |  | 3 | Hub CT____ missing (pos.__) | 0 | 45 |  |  | Wind (m/s) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | IS4 | Inv4 |  | SCB4 | Str_Typ4(540*58) | MCR_MVP_SolarF1 | IS2Inv2M2 | [9 empty] | SCB |  | WTG Scheduled Maintenance | IG Scheduled Maintenance | EG Scheduled Maintenance
KUD04 | O2R3 | JK | 2.2 | 4.348% | KUD04 | MY3 | Wind_F2 | Line1 | TX2 |  |  |  | 4 | Top CT____ missing (pos.__) | 0 | 45 | [10 empty] | IS5 | Inv5 |  | SCB5 | Str_Typ5(545*58) | MCR_MVP_SolarF2 | IS2Inv3M1 | [9 empty] | Inverter |  | WTG Environmental | IG Force Majeure | EG Force Majeure
KUD05 | O2R3 | JK | 2.2 | 4.348% | KUD05 | MY3 | Wind_F2 | Line1 | TX2 |  |  |  | 5 | Wrong ARCNet node no. | 0 | 45 | [11 empty] | Inv6 |  | SCB6 | Str_Typ6(550*58) | MCR_MVP_SolarF3 | IS2Inv3M2 | [9 empty] | IDT |  | WTG Force Majeure
KUD06 | O2R3 | JK | 2.2 | 4.348% | KUD06 | MY7 | Wind_F2 | Line1 | TX2 |  |  |  | 6 | Serial communication not init. | 0 | 45 | [11 empty] | Inv7 |  | SCB7 |  | MCR_MVP_SolarF4 | IS3Inv4M1 | [9 empty] | PTR
KUD07 | O2R3 | JK | 2.2 | 4.348% | KUD07 | MY4 | Wind_F2 | Line1 | TX2 |  |  |  | 7 | CT3218 initialization error | 0 | 45 | [11 empty] | Inv8 |  | SCB8 |  | Power_Tx1 | IS3Inv4M2 | [9 empty] | MV Panel
KUD08 | O2R3 | JK | 2.2 | 4.348% | KUD08 | MY5 | Wind_F1 | Line1 | TX2 |  |  |  | 8 | CT3220 initial. error pos.__ | 0 | 45 | [13 empty] | SCB9 |  | Power_Tx2 | IS4Inv5M1 | [9 empty] | Metering System Plant
KUD09 | O2R3 | JK | 2.2 | 4.348% | KUD09 | MY3 | Wind_F2 | Line1 | TX2 |  |  |  | 9 | Initialisation of ArcNet | 0 | 45 | [13 empty] | SCB10 |  | Line_Bay1 | IS4Inv5M2 | [9 empty] | Grid System
KUD10 | O2R1 | KSIPL | 2.2 | 4.348% | KUD10 | MY1 | Wind_F1 | Line1 | TX2 |  |  |  | 10 | CT3232 initialization error | 0 | 45 | [13 empty] | SCB11 |  |  | IS4Inv6M1 | [9 empty] | Metering System Grid
KUD11 | O2R1 | KSIPL | 2.2 | 4.348% | KUD11 | MY1 | Wind_F1 | Line1 | TX2 |  |  |  | 11 | Unexpected interrupt | 0 | 45 | [13 empty] | SCB12 |  |  | IS4Inv6M2 | [9 empty] | WMS
KUD12 | O2R1 | KSIPL | 2.2 | 4.348% | KUD12 | MY1 | Wind_F1 | Line1 | TX2 |  |  |  | 12 | Too many digital filters | 0 | 45 | [13 empty] | SCB13 |  |  | IS5Inv7M1 | [9 empty] | MMS
KUD13 | O2R1 | KSIPL | 2.2 | 4.348% | KUD13 | MY1 | Wind_F1 | Line1 | TX2 |  |  |  | 13 | Too many subLogics | 0 | 45 | [13 empty] | SCB14 |  |  | IS5Inv7M2 | [9 empty] | Battery Charger_MCR
KUD14 | O2R1 | KSIPL | 2.2 | 4.348% | KUD14 | MY1 | Wind_F1 | Line1 | TX2 |  |  |  | 14 | Too many DecOpState routines | 0 | 45 | [13 empty] | SCB15 |  |  | IS5Inv8M1 | [9 empty] | IC_UPS
KUD15 | O2R1 | KSIPL | 2.2 | 4.348% | KUD15 | MY1 | Wind_F1 | Line1 | TX2 |  |  |  | 15 | Too many IncOpState routines | 0 | 45 | [13 empty] | SCB16 |  |  | IS5Inv8M2 | [9 empty] | IC_Auxiliary Tranformer
KUD16 | O2R2 | SIL | 2.2 | 4.348% | KUD16 | MY2 | Wind_F2 | Line1 | TX2 |  |  |  | 16 | Too many WriteProLog routines | 0 | 45 | [13 empty] | SCB17 |  |  | IS1INV1M1SCB1 | O2R4_Solar | SGDCIPL | 219.24 | 5.195% | NA | MY1_Solar | Solar_F1 | Line1 | TX1 | IC_Auxiliary DB
KUD17 | O2R2 | SIL | 2.2 | 4.348% | KUD17 | MY2 | Wind_F2 | Line1 | TX2 |  |  |  | 17 | Too many interval timers | 0 | 45 | [13 empty] | SCB18 |  |  | IS1INV1M1SCB2 | O2R4_Solar | SGDCIPL | 219.24 | 5.195% | NA | MY1_Solar | Solar_F1 | Line1 | TX1 | IC_SCADA Panel
KUD18 | O2R4 | SGDCIPL | 2.2 | 4.348% | KUD18 | MY8 | Wind_F2 | Line1 | TX2 |  |  |  | 18 | Too many sec timers | 0 | 45 | [13 empty] | SCB19 |  |  | IS1INV1M1SCB3 | O2R4_Solar | SGDCIPL | 219.24 | 5.195% | NA | MY1_Solar | Solar_F1 | Line1 | TX1 | Connectors
KUD19 | O2R1 | KSIPL | 2.2 | 4.348% | KUD19 | MY1 | Wind_F1 | Line1 | TX2 |  |  |  | 19 | Too many msec timers | 0 | 45 | [13 empty] | SCB20 |  |  | IS1INV1M1SCB4 | O2R4_Solar | SGDCIPL | 219.24 | 5.195% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
KUD20 | O2R1 | KSIPL | 2.2 | 4.348% | KUD20 | MY1 | Wind_F1 | Line1 | TX2 |  |  |  | 20 | Too many event timers | 0 | 45 | [13 empty] | SCB21 |  |  | IS1INV1M1SCB5 | O2R4_Solar | SGDCIPL | 156.6 | 3.711% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
KUD21 | O2R3 | JK | 2.2 | 4.348% | KUD21 | MY3 | Wind_F2 | Line1 | TX2 |  |  |  | 21 | Interval timer not initialized | 0 | 45 | [13 empty] | SCB22 |  |  | IS1INV1M1SCB6 | O2R4_Solar | SGDCIPL | 219.24 | 5.195% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
KUD22 | O2R3 | JK | 2.2 | 4.348% | KUD22 | MY3 | Wind_F2 | Line1 | TX2 |  |  |  | 22 | Sec timer not initialized | 0 | 45 | [16 empty] | IS1INV1M1SCB7 | O2R4_Solar | SGDCIPL | 252.88 | 5.992% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
KUD23 | O2R3 | JK | 2.2 | 4.348% | KUD23 | MY3 | Wind_F2 | Line1 | TX2 |  |  |  | 23 | mSec timer not initialized | 0 | 45 | [16 empty] | IS1INV1M1SCB8 | O2R4_Solar | SGDCIPL | 252.88 | 5.992% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
Wind_F1 |  |  | 25.3 | 50% | [8 empty] | 24 | Event timer not initialized | 0 | 45 | [16 empty] | IS1INV1M1SCB9 | O2R4_Solar | SGDCIPL | 252.88 | 5.992% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
Wind_F2 |  |  | 25.3 | 50% | [8 empty] | 25 | Error Parameter Checksum | 0 | 45 | [16 empty] | IS1INV1M1SCB10 | O2R4_Solar | SGDCIPL | 0 | 0% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
Wind_F3 |  |  | 25.3 | 50% | [8 empty] | 26 | Illegal parameter group | 0 | 45 | [16 empty] | IS1INV1M2SCB1 | O2R4_Solar | SGDCIPL | 252.88 | 5.992% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
Wind_F4 |  |  | 25.3 | 50% | [8 empty] | 27 | Illegal text no.:______,__ | 0 | 45 | [16 empty] | IS1INV1M2SCB2 | O2R4_Solar | SGDCIPL | 252.88 | 5.992% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
Solar_F1 |  |  | 0 | 0% | [8 empty] | 28 | Q16 breaker open | 0 | 45 | [16 empty] | IS1INV1M2SCB3 | O2R4_Solar | SGDCIPL | 219.24 | 5.195% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
Solar_F2 |  |  | 0 | 0% | [8 empty] | 29 | Too many square filters | 0 | 45 | [16 empty] | IS1INV1M2SCB4 | O2R4_Solar | SGDCIPL | 219.24 | 5.195% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
Solar_F3 |  |  | 0 | 0% | [8 empty] | 30 | Internal subLogic error | 0 | 45 | [16 empty] | IS1INV1M2SCB5 | O2R4_Solar | SGDCIPL | 187.92 | 4.453% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
Solar_F4 |  |  | 0 | 0% | [8 empty] | 31 | OpSt change: Run -> Run | 0 | 45 | [16 empty] | IS1INV1M2SCB6 | O2R4_Solar | SGDCIPL | 221.27 | 5.243% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
BC |  |  | 0 | 0% | [8 empty] | 32 | Out of ArcNet xmit pools | 0 | 45 | [16 empty] | IS1INV1M2SCB7 | O2R4_Solar | SGDCIPL | 250.56 | 5.937% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
OG1 |  |  | 50.6 | 100% | [8 empty] | 33 | TelegramRcv resource too small | 0 | 45 | [16 empty] | IS1INV1M2SCB8 | O2R4_Solar | SGDCIPL | 221.27 | 5.243% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
OG2 |  |  | 50.6 | 100% | [8 empty] | 34 | Bad telegram xmit format | 0 | 45 | [16 empty] | IS1INV1M2SCB9 | O2R4_Solar | SGDCIPL | 221.27 | 5.243% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
TX1 |  |  | 50.6 | 100% | [8 empty] | 35 | Bad ArcNet sub address | 0 | 45 | [16 empty] | IS1INV1M2SCB10 | O2R4_Solar | SGDCIPL | 0 | 0% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
TX2 |  |  | 50.6 | 100% | [8 empty] | 36 | No communication with Top _ | 0 | 45 | [16 empty] | IS1Tx | O2R4_Solar | SGDCIPL | 4220 | 100% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
Line1 |  |  | 50.6 | 100% | [8 empty] | 37 | No communication with VCPM _ | 0 | 45 | [16 empty] | IS2Tx
MY1 | [12 empty] | 38 | No comm. with Hub _ | 0 | 45 | [16 empty] | IS3Tx
MY6 | [12 empty] | 39 | Too many Log slaves | 0 | 45 | [16 empty] | IS4Tx
MY1 | [12 empty] | 40 | SW versionconflict GND/HUB | 0 | 45 | [16 empty] | IS5Tx
MY3 | [12 empty] | 41 | BladeLubr Oil Low | 0 | 45 | [16 empty] | IS1MVP | O2R4_Solar | SGDCIPL | 4220 | 100% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
MY3 | [12 empty] | 42 | Aviation light error | 0 | 45 | [16 empty] | IS2MVP
MY7 | [12 empty] | 43 | Ground:ServiceHandler called | 0 | 45 | [16 empty] | IS3MVP
MY4 | [12 empty] | 44 | SW versionconflict GND/TOP | 0 | 45 | [16 empty] | IS4MVP
MY5 | [12 empty] | 45 | SW versionconflict GND/VCPM | 0 | 45 | [16 empty] | IS5MVP
MY3 | [12 empty] | 46 | CT____ illegal version __.__ | 0 | 45 | [16 empty] | IS1AuxTx | O2R4_Solar | SGDCIPL | 4220 | 100% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
MY1 | [12 empty] | 47 | CT 3218 data error _,__ | 0 | 45 | [16 empty] | IS2AuxTx
MY1 | [12 empty] | 48 | Too many ArcNet retransmiss. | 0 | 45 | [16 empty] | IS3AuxTx
MY1 | [12 empty] | 49 | Too many ArcNet reconf._____ | 0 | 45 | [16 empty] | IS4AuxTx
MY1 | [12 empty] | 50 | No communication with CT3251 | 0 | 45 | [16 empty] | IS5AuxTx
MY1 | [12 empty] | 51 | Feedback table full | 0 | 45 | [16 empty] | MCR_MVP_SolarF1 |  |  | 4220 | 100% | NA | MY1_Solar | Solar_F1 | Line1 | TX1
MY1 | [12 empty] | 52 | ZeroCross interrupt missing _ | 0 | 45 | [16 empty] | MCR_MVP_SolarF2
MY2 | [12 empty] | 53 | Error in CT3232 | 0 | 45 | [16 empty] | MCR_MVP_SolarF3
MY2 | [12 empty] | 54 | VDI telegram xmit error | 0 | 45 | [16 empty] | MCR_MVP_SolarF4
MY8 | [12 empty] | 55 | Telegram lost during reception | 0 | 45 | [16 empty] | Power_Tx1
MY1 | [12 empty] | 56 | Telegram lost during xmission | 0 | 45 | [16 empty] | Power_Tx2
MY1 | [12 empty] | 57 | ArcNet reconfiguration | 0 | 45 | [16 empty] | Line_Bay1
MY3 | [12 empty] | 58 | Time constant (thau) is zero | 0 | 45 | [16 empty] | Str_Typ1(540*29) |  |  | 15.66 | 0.3711%
MY3 | [12 empty] | 59 | Top fan__, Temp:___°C | 0 | 45 | [16 empty] | Str_Typ2(545*29) |  |  | 15.805 | 0.3745%
MY3 | [12 empty] | 60 | VDI telegram format error | 0 | 45 | [16 empty] | Str_Typ3(550*29) |  |  | 15.95 | 0.378%
[13 empty] | 61 | Illegal VDI subscription | 0 | 45 | [16 empty] | Str_Typ4(540*58) |  |  | 31.32 | 0.7422%
[13 empty] | 62 | Ground status report timeout | 0 | 45 | [16 empty] | Str_Typ5(545*58) |  |  | 31.61 | 0.7491%
[13 empty] | 63 | Power telegraph timeout | 0 | 45 | [16 empty] | Str_Typ6(550*58) |  |  | 31.9 | 0.7559%
[13 empty] | 64 | VCPMstate queue overflow | 0 | 45
[13 empty] | 65 | Unused Opcode | 0 | 45
[13 empty] | 66 | Hub fan__, Temp:___°C | 0 | 45
[13 empty] | 67 | Gen. ext. vent. _, temp:___°C | 0 | 45
[13 empty] | 68 | HV Trafo. vent. _, temp:___°C | 0 | 45
[13 empty] | 69 | Gen. int. vent. _, temp:___°C | 0 | 45
[13 empty] | 70 | Nacelle position reset: ___._° | 0 | 45
[13 empty] | 71 | Feedback=_, Int.Gen.Fan S___A | 0 | 45
[13 empty] | 72 | Feedback=_, Int.Gen.Fan S___B | 0 | 45
[13 empty] | 73 | Feedback=_, Ext.Gen.Fan S____ | 0 | 45
[13 empty] | 74 | PitchA pos:__._° vel:___._°/s | 0 | 45
[13 empty] | 75 | PitchB pos:__._° vel:___._°/s | 0 | 45
[13 empty] | 76 | PitchC pos:__._° vel:___._°/s | 0 | 45
[13 empty] | 77 | Low processor temp. in Nacelle | 0 | 45
[13 empty] | 78 | Low processor temp. in Hub | 0 | 45
[13 empty] | 79 | Max. Yaw error: ___._° | 1 | 28
[13 empty] | 80 | Low oil pressure:____RPM/___°C | 0 | 45
[13 empty] | 81 | Pitch B ref:__._°, Act.:__._° | 0 | 45
[13 empty] | 82 | Pitch C ref:__._°, Act.:__._° | 0 | 45
[13 empty] | 83 | B Ctrl:___.__V P.Vel:___._°/s | 0 | 45
[13 empty] | 84 | C Ctrl:___.__V P.Vel:___._°/s | 0 | 45
[13 empty] | 85 | B CtrlV.STD__._V B CtrlV__._V | 0 | 45
[13 empty] | 86 | C CtrlV.STD__._V C CtrlV__._V | 0 | 45
[13 empty] | 87 | Pitch dev. min:__._° max:__._° | 0 | 45
[13 empty] | 88 | Hydr. temperature low: ___°C | 0 | 45
[13 empty] | 89 | Trip F60 L_: ___ °C | 0 | 45
[13 empty] | 90 | System error (1) | 0 | 45
[13 empty] | 91 | System error (2) | 0 | 45
[13 empty] | 92 | System error (3) | 0 | 45
[13 empty] | 93 | Low supply voltage CT3503 | 0 | 45
[13 empty] | 94 | Frequency reg: __.__Hz _____kW | 0 | 45
[13 empty] | 95 | Com.err: Address ____:____ | 0 | 45
[13 empty] | 96 | Crash no. 0 | 0 | 45
[13 empty] | 97 | Gnd.err. Address______:______ | 0 | 45
[13 empty] | 98 | Top.err. Address______:______ | 0 | 45
[13 empty] | 99 | VCPM.err. Address______:______ | 0 | 45
[13 empty] | 100 | Too many auto-restarts:_____ | 0 | 45
[13 empty] | 101 | Emerg.-> Stop, EMC not conn. | 0 | 45
[13 empty] | 102 | Emergency circuit open | 0 | 45
[13 empty] | 103 | PhaseSequence error | 0 | 45
[13 empty] | 104 | Phasesequence not measured | 0 | 45
[13 empty] | 105 | Phase sequence check timed out | 0 | 45
[13 empty] | 106 | Top OpSt.change timeout (_) | 0 | 45
[13 empty] | 107 | VCPM OpSt.change timeout (_) | 0 | 45
[13 empty] | 108 | Illegal gen.cmd.: _ in state _ | 0 | 45
[13 empty] | 109 | Thermerr. offlin:____RPM/___°C | 0 | 45
[13 empty] | 110 | High pres offlin:____RPM/___°C | 0 | 45
[13 empty] | 111 | No offline filtrat. For__days | 0 | 45
[13 empty] | 112 | Max DP filt. A: ____RPM/___°C | 0 | 45
[13 empty] | 113 | Error Smoke Detector | 0 | 45
[13 empty] | 114 | Gen _ in,LastProdCtrlState __ | 0 | 45
[13 empty] | 115 | Generator out | 0 | 45
[13 empty] | 116 | Emerg. --> Stop, Output active | 0 | 45
[13 empty] | 117 | Anemom.error:__._m/s,____._RPM | 0 | 45
[13 empty] | 118 | Anemom.error:__._m/s,____._kW | 0 | 45
[13 empty] | 119 | Extrem frequency: ___.__ Hz | 0 | 45
[13 empty] | 120 | Low curr.L1:____A,Others:____A | 0 | 45
[13 empty] | 121 | Low curr.L2:____A,Others:____A | 0 | 45
[13 empty] | 122 | Low curr.L3:____A,Others:____A | 0 | 45
[13 empty] | 123 | High curr Gen0 L_: ____ A | 0 | 45
[13 empty] | 124 | Extr.high curr.Gen1 L_: ____ A | 0 | 45
[13 empty] | 125 | Extr.high curr.Gen2 L_: ____ A | 0 | 45
[13 empty] | 126 | Extr. high volt. L_: ___ V | 0 | 45
[13 empty] | 127 | Extr. low voltage L_: ___V | 0 | 45
[13 empty] | 128 | Trip Q8 L_: ___ V | 0 | 45
[13 empty] | 129 | Frequency error: ___.__ Hz | 0 | 45
[13 empty] | 130 | Max power Gen_: ____._ kW | 0 | 45
[13 empty] | 131 | Negative power Gen_: ____._ kW | 0 | 45
[13 empty] | 132 | Leak current ____A | 0 | 45
[13 empty] | 133 | Power: ____._ kW, OpSt<Run | 0 | 45
[13 empty] | 134 | High voltage L_: ___ V | 0 | 45
[13 empty] | 135 | Low voltage L_: ___ V | 0 | 45
[13 empty] | 136 | Asym.currL1:____A,Others:____A | 3 | 17
[13 empty] | 137 | Asym.currL2:____A,Others:____A | 9 | 11
[13 empty] | 138 | Asym.currL3:____A,Others:____A | 2 | 20
[13 empty] | 139 | Asym.voltL1:____V,Others:____V | 0 | 45
[13 empty] | 140 | Asym.voltL2:____V,Others:____V | 0 | 45
[13 empty] | 141 | Asym.voltL3:____V,Others:____V | 0 | 45
[13 empty] | 142 | High curr Gen1 L_: ____ A | 0 | 45
[13 empty] | 143 | High curr Gen2 L_: ____ A | 0 | 45
[13 empty] | 144 | High windspeed: __._ m/s | 0 | 45
[13 empty] | 145 | Low processor temp. in top | 0 | 45
[13 empty] | 146 | Ambient temperature low: ___°C | 0 | 45
[13 empty] | 147 | High gear temp:___°C/air:___°C | 0 | 45
[13 empty] | 148 | High temperature Gen_: ___°C | 0 | 45
[13 empty] | 149 | High temperature T53: ___°C L_ | 0 | 45
[13 empty] | 150 | High temp.Gear bearing _:___°C | 0 | 45
[13 empty] | 151 | High temp. Gen bearing _:___°C | 1 | 28
[13 empty] | 152 | Emerg. --> Stop,Rot:___._ RPM | 0 | 45
[13 empty] | 153 | Max generator RPM: ____._ RPM | 0 | 45
[13 empty] | 154 | Max rotor RPM: __._ RPM | 1 | 28
[13 empty] | 155 | High Gen.SlipRTemp:___°C ____A | 0 | 45
[13 empty] | 156 | Chock sensor trigged:____._RPM | 0 | 45
[13 empty] | 157 | Gen.RPM: ____._ RPM, OpSt<Run | 0 | 45
[13 empty] | 158 | Rotor:__._RPM, Gen.:____._ RPM | 2 | 20
[13 empty] | 159 | Ext. RPM guard, ____ RPM S_ | 0 | 45
[13 empty] | 160 | High temperature brake disc | 0 | 45
[13 empty] | 161 | Hydr max time:___sec, ___bar | 0 | 45
[13 empty] | 162 | Safety-pressostat brake | 0 | 45
[13 empty] | 163 | Low workingpressure: ___._ bar | 0 | 45
[13 empty] | 164 | Press.drop hydr. filter ___°C | 0 | 45
[13 empty] | 165 | Low oil-level, hydraulic | 2 | 20
[13 empty] | 166 | Thermoerror hydraulicmotor | 0 | 45
[13 empty] | 167 | Hydr. temperature high: ___°C | 0 | 45
[13 empty] | 168 | High temp top ctrl.: ___°C | 0 | 45
[13 empty] | 169 | Thermoerr. Nac. fan F___/___°C | 0 | 45
[13 empty] | 170 | Thermoerr. oil pump F___/___°C | 0 | 45
[13 empty] | 171 | Max no of pitchconnect cmd | 0 | 45
[13 empty] | 172 | Feedback=_, Nacelle fan S___ | 0 | 45
[13 empty] | 173 | Feedback=_, Gearoil cool S___ | 0 | 45
[13 empty] | 174 | Feedback = _,:Hydraulicmotor | 0 | 45
[13 empty] | 175 | High temp. bus bar section | 0 | 45
[13 empty] | 176 | Error on all wind sensors | 1 | 28
[13 empty] | 177 | Low processor temp. in ground | 0 | 45
[13 empty] | 178 | Def. fuse,lightn. prot.(F9-11) | 0 | 45
[13 empty] | 179 | Error, yawcontrol: _____ (_) | 0 | 45
[13 empty] | 180 | No yawpulses _____, ____ s | 0 | 45
[13 empty] | 181 | Feedback = _, yawing CW _ | 1 | 28
[13 empty] | 182 | Feedback = _, yawing CCW _ | 0 | 45
[13 empty] | 183 | Max autoyawtime ____ sec. | 0 | 45
[13 empty] | 184 | Max outyawtime superceeded | 0 | 45
[13 empty] | 185 | Outyawing too much, S___ activ | 0 | 45
[13 empty] | 186 | Thermoerror yawmotor F___ | 0 | 45
[13 empty] | 187 | External 24 V power supply | 0 | 45
[13 empty] | 188 | External 24 V power supply eq. | 0 | 45
[13 empty] | 189 | Feedback = _, Brake | 0 | 45
[13 empty] | 190 | Pitch A ref:__._°, Act.:__._° | 0 | 45
[13 empty] | 191 | A Ctrl:___.__V P.Vel:___._°/s | 0 | 45
[13 empty] | 192 | A CtrlV.STD__._V A CtrlV__._V | 0 | 45
[13 empty] | 193 | PowerSTD____._kW MEAN____._kW | 0 | 45
[13 empty] | 194 | Pitch A too low:__._° < __._° | 0 | 45
[13 empty] | 195 | PowerError ____._ kW | 0 | 45
[13 empty] | 196 | Max generator RPM: ____._ RPM | 0 | 45
[13 empty] | 197 | Yaw activity not detected | 0 | 45
[13 empty] | 198 | Yaw position is changed | 0 | 45
[13 empty] | 199 | Thermo table full | 0 | 45
[13 empty] | 200 | Yaw speed error ___._° in __ s | 0 | 45
[13 empty] | 201 | Low temperature Gen_:___°C | 0 | 45
[13 empty] | 202 | Frequency error 1: ___.__ Hz | 0 | 45
[13 empty] | 203 | Frequency error 2: ___.__ Hz | 0 | 45
[13 empty] | 204 | Frequency error 3: ___.__ Hz | 0 | 45
[13 empty] | 205 | Frequency error 4: ___.__ Hz | 0 | 45
[13 empty] | 206 | Feedback=_, Hydroilcool S___ | 0 | 45
[13 empty] | 207 | Division by zero | 0 | 45
[13 empty] | 208 | Lubr Error Blade _ | 0 | 45
[13 empty] | 209 | Missing VAMS permission _ | 0 | 45
[13 empty] | 210 | Low gear temp:___°C/nac:___°C | 0 | 45
[13 empty] | 211 | Metal chip detec:____RPM/___°C | 0 | 45
[13 empty] | 212 | Error temp.sensor R___, ____°C | 0 | 45
[13 empty] | 213 | Error temp.sensor R___ blade _ | 0 | 45
[13 empty] | 214 | Low oil level, ____RPM/___°C | 0 | 45
[13 empty] | 215 | Press.drop hydr.filt.Hub ___°C | 0 | 45
[13 empty] | 216 | Oil leakage in Hub | 0 | 45
[13 empty] | 217 | Thermoerror Int.Gen.Fan F___A | 0 | 45
[13 empty] | 218 | Thermoerror Int.Gen.Fan F___B | 0 | 45
[13 empty] | 219 | Thermoerror Ext.Gen.Fan F____ | 0 | 45
[13 empty] | 220 | New SERVICE state: _, ____ | 0 | 45
[13 empty] | 221 | ERROR: | 0 | 45
[13 empty] | 222 | Emergency ____._kW ____RPM | 0 | 45
[13 empty] | 223 | Stop ____._kW ____RPM | 0 | 45
[13 empty] | 224 | Pause ____._kW ____RPM | 0 | 45
[13 empty] | 225 | Run | 0 | 45
[13 empty] | 226 | Power cutout | 0 | 45
[13 empty] | 227 | Power cutin | 0 | 45
[13 empty] | 228 | SysState _.___ set to ______ | 0 | 45
[13 empty] | 229 | Parameter __.___ set to ______ | 0 | 45
[13 empty] | 230 | Auto-restart after ____ sec | 0 | 45
[13 empty] | 231 | Restart not possible | 0 | 45
[13 empty] | 232 | WatchdogReboot | 0 | 45
[13 empty] | 233 | WATCHDOG trigging disabled | 0 | 45
[13 empty] | 234 | Miss. error ack.before restart | 0 | 45
[13 empty] | 235 | Error ___ ackd. over RCS | 0 | 45
[13 empty] | 236 | Error ___ acknowledged manual. | 0 | 45
[13 empty] | 237 | WATCHDOG was not trigged | 0 | 45
[13 empty] | 238 | Busbarvent._, Power: ____._kW | 0 | 45
[13 empty] | 239 | Lightning blade _: ___ kA | 0 | 45
[13 empty] | 240 | Lightning blade _: ___ kA | 0 | 45
[13 empty] | 241 | GPS reciever out of order | 0 | 45
[13 empty] | 242 | Light. det. error ___ ___ | 0 | 45
[13 empty] | 243 | Hot generator ___°C ______kW | 0 | 45
[13 empty] | 244 | Hot gear___°C ______kW | 0 | 45
[13 empty] | 245 | Hot HV trafo ___°C ______kW | 0 | 45
[13 empty] | 246 | High voltage ___V ______kW | 0 | 45
[13 empty] | 247 | Wind:__._m/s derate to:_____kW | 0 | 45
[13 empty] | 248 | User power setpoint _____kW | 0 | 45
[13 empty] | 249 | Too many Warnings in queue _ | 0 | 45
[13 empty] | 250 | No space in Warning Log | 0 | 45
[13 empty] | 251 | Low oil flow: _.__bar/ ____RPM | 0 | 45
[13 empty] | 252 | Low oil flow: ____RPM/ ___°C | 0 | 45
[13 empty] | 253 | Max DP filt. A:_.__bar/____RPM | 0 | 45
[13 empty] | 254 | Max DP filt. A: ____RPM/ ___°C | 0 | 45
[13 empty] | 255 | Manual, signal:___,chg.:_ | 0 | 45
[13 empty] | 256 | Too low nacel temp ____°C | 0 | 45
[13 empty] | 257 | Start hydr. motor, ___._ bar | 0 | 45
[13 empty] | 258 | Stop hydr. motor, ___._ bar | 0 | 45
[13 empty] | 259 | SW versionconflict GND/GRID | 0 | 45
[13 empty] | 260 | Log reset by user | 0 | 45
[13 empty] | 261 | AlarmLog reset by user | 0 | 45
[13 empty] | 262 | GndSystemState reset by user | 0 | 45
[13 empty] | 263 | TopSystemState reset by user | 0 | 45
[13 empty] | 264 | VCPMSystemState reset by user | 0 | 45
[13 empty] | 265 | Wind:___._ m/s Gen:____._ RPM | 0 | 45
[13 empty] | 266 | Pitch: __._° Power: ____._ kW | 0 | 45
[13 empty] | 267 | ComSystemState reset by user | 0 | 45
[13 empty] | 268 | Pitchtest nr. __ param.:______ | 0 | 45
[13 empty] | 269 | Pitchtest nr. __ | 0 | 45
[13 empty] | 270 | Nac.vent.0, nac/gear:___/___°C | 0 | 45
[13 empty] | 271 | Nac.vent.1, nac/gear:___/___°C | 0 | 45
[13 empty] | 272 | Nac.vent.2, nac/gear:___/___°C | 0 | 45
[13 empty] | 273 | E.Wind:__._m/s Nac.Dir:____._° | 0 | 45
[13 empty] | 274 | Nac.vent.3, nac/gear:___/___°C | 0 | 45
[13 empty] | 275 | Start auto-outyawing CW | 0 | 45
[13 empty] | 276 | Start auto-outyawing CCW | 0 | 45
[13 empty] | 277 | Start autoyawing CW | 0 | 45
[13 empty] | 278 | Start autoyawing CCW | 0 | 45
[13 empty] | 279 | Stop autoyawing | 0 | 45
[13 empty] | 280 | Yawcontr. from:_____ to:_____ | 0 | 45
[13 empty] | 281 | Start manual yawing CCW | 0 | 45
[13 empty] | 282 | Yawing manually stopped | 0 | 45
[13 empty] | 283 | Start manual yawing CW | 0 | 45
[13 empty] | 284 | Stop auto-outyawing | 0 | 45
[13 empty] | 285 | Stop yawing at twiststop(S104) | 0 | 45
[13 empty] | 286 | Max DP filt. B:_.__bar/____RPM | 0 | 45
[13 empty] | 287 | Max DP filt. B: ____RPM/ ___°C | 0 | 45
[13 empty] | 288 | Standby heating _, gen: ___°C | 0 | 45
[13 empty] | 289 | Gearoilheater _, gear: ___°C | 0 | 45
[13 empty] | 290 | VDF data lost. Code_____,_____ | 0 | 45
[13 empty] | 291 | CT3251 OpSt.change timeout (_) | 0 | 45
[13 empty] | 292 | GearoilCooler _, gear: ___°C | 0 | 45
[13 empty] | 293 | Frequency controller started | 0 | 45
[13 empty] | 294 | Frequency controller stopped | 0 | 45
[13 empty] | 295 | VMP halted: Program upload | 0 | 45
[13 empty] | 296 | Tow. acc. X, Alarm:__.__ m/s^2 | 0 | 45
[13 empty] | 297 | Tow. acc. Y, Alarm:__.__ m/s^2 | 0 | 45
[13 empty] | 298 | Tow. acc. X, Warn.:__.__ m/s^2 | 0 | 45
[13 empty] | 299 | Tow. acc. Y, Warn.:__.__ m/s^2 | 0 | 45
[13 empty] | 300 | Aviation Lamp error | 0 | 45
[13 empty] | 301 | Aviation Lamp shift | 0 | 45
[13 empty] | 302 | Thermo error, hydr. oilcooler | 0 | 45
[13 empty] | 303 | Marine Lamp error | 0 | 45
[13 empty] | 304 | Marine Lamp shift | 0 | 45
[13 empty] | 305 | Timeout comm. Tower acc. | 0 | 45
[13 empty] | 306 | Operation Log reestablished | 0 | 45
[13 empty] | 307 | Alarm Log reestablished | 0 | 45
[13 empty] | 308 | System Log reestablished | 0 | 45
[13 empty] | 309 | Pause over RCS __0 | 54 | 3
[13 empty] | 309 | Pause over RCS __1 | 0 | 45
[13 empty] | 309 | Pause over RCS __2 | 0 | 45
[13 empty] | 309 | Pause over RCS __3 | 0 | 45
[13 empty] | 309 | Pause over RCS __4 (Power Manager) | 0 | 45
[13 empty] | 309 | Pause over RCS __5 (Curtailment) | 0 | 45
[13 empty] | 309 | Pause over RCS __6 | 0 | 45
[13 empty] | 309 | Pause over RCS __10 | 0 | 45
[13 empty] | 309 | Pause over RCS __12 (Remote – VOB Client) | 0 | 45
[13 empty] | 309 | Pause over RCS __13 (Remote – VOB Client) | 0 | 45
[13 empty] | 309 | Pause over RCS __14 (Remote – VOB Client) | 0 | 45
[13 empty] | 309 | Pause over RCS __15 (Remote – VOB Client) | 0 | 45
[13 empty] | 310 | Run over RCS __ | 0 | 45
[13 empty] | 311 | Trip Q8 Feedback error | 0 | 45
[13 empty] | 312 | Transformer Thermo Fault | 0 | 45
[13 empty] | 313 | Ambient temperature high: __°C | 0 | 45
[13 empty] | 314 | Trip Q8 high current L_ ____ A | 0 | 45
[13 empty] | 315 | ExEx low voltage L_: ___V | 16 | 8
[13 empty] | 316 | Cont.=___ Feedback s.failed: _ | 0 | 45
[13 empty] | 317 | Cont.=___ Feedback r.failed: _ | 0 | 45
[13 empty] | 318 | Cannot syncronize____ RPM,st__ | 0 | 45
[13 empty] | 319 | Long DC charge time ___s ____V | 0 | 45
[13 empty] | 320 | High temp. Rotor Inv.L_:___°C | 0 | 45
[13 empty] | 321 | Ext. high temp. RInv.L_:___°C | 0 | 45
[13 empty] | 322 | High temp. Grid Inv.L_:___°C | 0 | 45
[13 empty] | 323 | Ext. high temp. GInv.L_:___°C | 0 | 45
[13 empty] | 324 | High temp. VCP Board ___°C | 0 | 45
[13 empty] | 325 | High temp. VCS System ___°C | 0 | 45
[13 empty] | 326 | High temp. Aux. ___°C | 0 | 45
[13 empty] | 327 | Grid inv. HW error L_ | 0 | 45
[13 empty] | 328 | Rotor inv. HW error L_ | 1 | 28
[13 empty] | 329 | DC Overvolt: ____V state __ | 0 | 45
[13 empty] | 330 | Ext. high DC voltage ____V | 0 | 45
[13 empty] | 331 | DC Undervoltage: ____V | 0 | 45
[13 empty] | 332 | Ext. low DC voltage ____V | 0 | 45
[13 empty] | 333 | High cur.rotor inv. L_:____A | 0 | 45
[13 empty] | 334 | High cur.grid inv. L_:____A | 0 | 45
[13 empty] | 335 | ExtHighIRotorInv phase: _ | 3 | 17
[13 empty] | 336 | Ext. High cur. Grid inv. L_ | 1 | 28
[13 empty] | 337 | Overtemp charging DC, ____V | 0 | 45
[13 empty] | 338 | Slip:____ above limits _ | 1 | 28
[13 empty] | 339 | Phase L:_ failure | 0 | 45
[13 empty] | 340 | OVP active UDC_____V state __ | 0 | 45
[13 empty] | 341 | OVPHwErr UDC _____V state __ | 0 | 45
[13 empty] | 342 | Encoder hardware error | 0 | 45
[13 empty] | 343 | Encoder signal error _:_____ | 0 | 45
[13 empty] | 344 | MDSP to VCPM Comm. timeout | 0 | 45
[13 empty] | 345 | VCPM to MDSP Comm. timeout | 0 | 45
[13 empty] | 346 | DSP _ checksum err. | 0 | 45
[13 empty] | 347 | DSP _mat. overflow | 0 | 45
[13 empty] | 348 | DSP _internal error ____ | 0 | 45
[13 empty] | 349 | Error in Cal Val on VCPM | 0 | 45
[13 empty] | 350 | PFC breaker open | 0 | 45
[13 empty] | 351 | VCS Low water level | 0 | 45
[13 empty] | 352 | Q7 breaker open | 0 | 45
[13 empty] | 353 | Q8 breaker open | 0 | 45
[13 empty] | 354 | Par. __.___ set to ______ rem. | 0 | 45
[13 empty] | 355 | WS1 Dir Frozen __._m/s ___._° | 0 | 45
[13 empty] | 356 | Extreme yawerror __._m/s___._° | 2 | 20
[13 empty] | 357 | Lightning detected | 0 | 45
[13 empty] | 358 | Lightn. detect. power supplied | 0 | 45
[13 empty] | 359 | Lightn. det. emergency suppl. | 0 | 45
[13 empty] | 360 | Warning Log reestablished | 0 | 45
[13 empty] | 361 | Pending Warning in Log | 0 | 45
[13 empty] | 362 | De-Ice System overtemp _-_ | 0 | 45
[13 empty] | 363 | De-Ice System timeout | 0 | 45
[13 empty] | 364 | De-Ice curr.dev. _, ____A | 0 | 45
[13 empty] | 365 | De-Ice feedback=0 _-_ | 0 | 45
[13 empty] | 366 | De-Ice feedback=1 _-_ | 0 | 45
[13 empty] | 367 | De-Ice temp. feedback _-_ | 0 | 45
[13 empty] | 368 | Ice sensor error | 0 | 45
[13 empty] | 369 | De-ice event: System ON | 0 | 45
[13 empty] | 370 | De-ice event: System OFF | 0 | 45
[13 empty] | 371 | De-ice event: Ice detected | 0 | 45
[13 empty] | 372 | De-ice event: Mass unbalance | 0 | 45
[13 empty] | 373 | De-ice event: Power loss | 0 | 45
[13 empty] | 374 | De-ice event: Ice climate | 0 | 45
[13 empty] | 375 | Ice safety stop | 0 | 45
[13 empty] | 376 | Lightning detected (stopped) | 0 | 45
[13 empty] | 377 | Error on US, change to 0/90° | 0 | 45
[13 empty] | 378 | De-Ice: Feedback = _, K1064 | 0 | 45
[13 empty] | 379 | No comm. with DeIce | 0 | 45
[13 empty] | 380 | WS1 invalid data: _ | 0 | 45
[13 empty] | 381 | WS1 timeout err. | 0 | 45
[13 empty] | 382 | SlipR ext. fan__, Temp:___°C | 0 | 45
[13 empty] | 383 | Gen SlipR. Fan: __, Temp:___°C | 0 | 45
[13 empty] | 384 | Thermo error Gen.Slip Ring Fan | 0 | 45
[13 empty] | 385 | Feedback = _,:SlipR fan S____ | 0 | 45
[13 empty] | 386 | Feedback = _,:VCS fan S____ | 0 | 45
[13 empty] | 387 | VCS water pump ON | 0 | 45
[13 empty] | 388 | VCS water pump OFF | 0 | 45
[13 empty] | 389 | IGBT pump ON Top:___ Wa:___ | 0 | 45
[13 empty] | 390 | IGBT pump OFF Top:___ Wa:___ | 0 | 45
[13 empty] | 391 | VCS int.fan ON Nac:___ Wa:___ | 0 | 45
[13 empty] | 392 | VCS int.fan OFF Nac:___ Wa:___ | 0 | 45
[13 empty] | 393 | VCS external vent. ON | 0 | 45
[13 empty] | 394 | VCS external vent. OFF | 0 | 45
[13 empty] | 395 | IGBT fan ON Nac:___ Am:___ | 0 | 45
[13 empty] | 396 | IGBT fan OFF Nac:___ Am:___ | 0 | 45
[13 empty] | 397 | Thermoerror Int. VCS Fan F____ | 0 | 45
[13 empty] | 398 | Thermoerror ext. VCS Fan F____ | 0 | 45
[13 empty] | 399 | Thermoerror IGBT pump F___ | 0 | 45
[13 empty] | 400 | Thermoerror IGBT fan F____ | 0 | 45
[13 empty] | 401 | Smoke detected | 0 | 45
[13 empty] | 402 | NRMS sector __, wind: __._m/s | 0 | 45
[13 empty] | 403 | RCS disconnected due to ___ | 0 | 45
[13 empty] | 404 | RCS reconnected | 0 | 45
[13 empty] | 405 | Gen SlipR. Heat: __, t:____°C | 0 | 45
[13 empty] | 406 | Low temp. slipring: ___°C | 0 | 45
[13 empty] | 407 | Low delta temp. slipr: ___°C | 0 | 45
[13 empty] | 408 | User defined alarm 1 | 0 | 45
[13 empty] | 409 | User defined alarm 2 | 0 | 45
[13 empty] | 410 | CT3234 init error P__ S___ | 0 | 45
[13 empty] | 411 | Feedback = _, SlipR heat S___ | 0 | 45
[13 empty] | 412 | WS2 invalid data: _ | 0 | 45
[13 empty] | 413 | WS2 timeout err. | 0 | 45
[13 empty] | 414 | PistonAVel:__._m/s,Ang:__._° | 0 | 45
[13 empty] | 415 | PistonBVel:__._m/s,Ang:__._° | 0 | 45
[13 empty] | 416 | PistonCVel:__._m/s,Ang:__._° | 0 | 45
[13 empty] | 417 | EMCV. Pitch min:__._°max:__._° | 0 | 45
[13 empty] | 418 | Timeout generator reconnecting | 0 | 45
[13 empty] | 419 | VDI Transmit resource Low | 0 | 45
[13 empty] | 420 | High hydr. pressure ___._ bar | 0 | 45
[13 empty] | 421 | Yaw Curve Error point _._=_._ | 0 | 45
[13 empty] | 422 | Too low nacelle temp. ___°C | 0 | 45
[13 empty] | 423 | Blocking run, nacelle ___°C | 0 | 45
[13 empty] | 424 | CT3223 init error | 0 | 45
[13 empty] | 425 | Event __ in ConvCtrl state __ | 0 | 45
[13 empty] | 426 | Event __ in KxxCtrl state __ | 0 | 45
[13 empty] | 427 | Event __ in StDlCtrl state __ | 0 | 45
[13 empty] | 428 | Event __ in ConvCtrl state __ | 0 | 45
[13 empty] | 429 | Max Warnings gen-_ reconnects | 0 | 45
[13 empty] | 430 | Transm. osc. ____ RPM, __ m/s | 0 | 45
[13 empty] | 431 | MDSP-SDSP Comm. timeout | 0 | 45
[13 empty] | 432 | Wrong LSI Version: _____ | 0 | 45
[13 empty] | 433 | Noise setting changed to: _ | 0 | 45
[13 empty] | 434 | WarningLog reset by user | 0 | 45
[13 empty] | 435 | Start yawing to reset CW | 0 | 45
[13 empty] | 436 | Start yawing to reset CCW | 0 | 45
[13 empty] | 437 | Hot bearing ___°C ______kW | 0 | 45
[13 empty] | 438 | Hot top ctrl. ___°C ______kW | 0 | 45
[13 empty] | 439 | Hot IGBTs ___°C ______kW | 0 | 45
[13 empty] | 440 | Hot VRCC water ___°C ______kW | 0 | 45
[13 empty] | 441 | Derated at __°C ambi by __ | 0 | 45
[13 empty] | 442 | Remote power setpoint _____kW | 0 | 45
[13 empty] | 443 | Frequency error 1: ___.__ Hz | 0 | 45
[13 empty] | 444 | EMF Acc _ Press Low, ___._ bar | 0 | 45
[13 empty] | 446 | Hydr Pilot Press Diff | 0 | 45
[13 empty] | 447 | Trafo Temp Diff | 0 | 45
[13 empty] | 448 | Remote Stop | 0 | 45
[13 empty] | 450 | Ext. High I sum Grd inv. | 24 | 6
[13 empty] | 453 | Ext. High I sum Rotinv.ChanX | 0 | 45
[13 empty] | 454 | Ext. High I sum Rotinv.ChanY | 0 | 45
[13 empty] | 455 | RInv GInv PWM out of Sync | 0 | 45
[13 empty] | 456 | VPC Signal error, auto __,__ | 0 | 45
[13 empty] | 457 | Nom DCVolt failed ____V | 0 | 45
[13 empty] | 460 | Generator Disc timeout | 0 | 45
[13 empty] | 461 | VPC board IntSW Warning __:__ | 0 | 45
[13 empty] | 462 | VPC board IntSW Disc __:__ | 0 | 45
[13 empty] | 463 | VPC board IntSW Q8Stop __:__ | 0 | 45
[13 empty] | 464 | VPC board IntSW DCharge __:__ | 0 | 45
[13 empty] | 467 | VPC board IntSW Stop __:__ | 0 | 45
[13 empty] | 469 | StopCmd failed. __:__ | 0 | 45
[13 empty] | 470 | VPC board crashed | 0 | 45
[13 empty] | 471 | Loadcal.A Offset ___Gain ____ | 0 | 45
[13 empty] | 472 | Loadcal.B Offset ___Gain ____ | 0 | 45
[13 empty] | 474 | Loadcal.C Offset ___Gain ____ | 0 | 45
[13 empty] | 475 | Feedback error, Preheater S557 | 0 | 45
[13 empty] | 478 | VCMS: Net error | 0 | 45
[13 empty] | 479 | VCMS:Node___ Initialize error | 0 | 45
[13 empty] | 480 | VCMS:Node___ Comm. error | 0 | 45
[13 empty] | 481 | VCMS:Node___ Selftest error | 0 | 45
[13 empty] | 482 | VCMS:Node___ Acc. Low level | 0 | 45
[13 empty] | 483 | VCMS:Node___ Ping error | 0 | 45
[13 empty] | 484 | VCMS:Node___ Warn. :Temp=___°C | 0 | 45
[13 empty] | 485 | VCMS:Node___ Alarm :Temp=___°C | 0 | 45
[13 empty] | 486 | VCMS:SEW11 V=_____um/s, ____kW | 0 | 45
[13 empty] | 487 | VCMS:SEW11 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 488 | VCMS:SEA11 V=_____um/s, ____kW | 0 | 45
[13 empty] | 489 | VCMS:SEA11 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 490 | VCMS:FEW11 V=_____um/s, ____kW | 0 | 45
[13 empty] | 491 | VCMS:FEW11 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 492 | VCMS:FEA11 V=_____um/s, ____kW | 0 | 45
[13 empty] | 493 | VCMS:FEA11 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 494 | VCMS:AMA11 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 495 | VCMS:SEW12 V=_____um/s, ____kW | 0 | 45
[13 empty] | 496 | VCMS:SEW12 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 497 | VCMS:SEA12 V=_____um/s, ____kW | 0 | 45
[13 empty] | 498 | VCMS:SEA12 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 499 | VCMS:FEW12 V=_____um/s, ____kW | 0 | 45
[13 empty] | 500 | VCMS:FEW12 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 501 | VCMS:FEA12 V=_____um/s, ____kW | 0 | 45
[13 empty] | 502 | VCMS:FEA12 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 503 | VCMS:AMA12 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 504 | VCMS:SEW13 V=_____um/s, ____kW | 0 | 45
[13 empty] | 505 | VCMS:SEW13 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 506 | VCMS:SEA13 V=_____um/s, ____kW | 0 | 45
[13 empty] | 507 | VCMS:SEA13 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 508 | VCMS:FEW13 V=_____um/s, ____kW | 0 | 45
[13 empty] | 509 | VCMS:FEW13 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 510 | VCMS:FEA13 V=_____um/s, ____kW | 0 | 45
[13 empty] | 511 | VCMS:FEA13 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 512 | VCMS:AMA13 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 513 | VCMS:SEW14 V=_____um/s, ____kW | 0 | 45
[13 empty] | 514 | VCMS:SEW14 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 515 | VCMS:SEA14 V=_____um/s, ____kW | 0 | 45
[13 empty] | 516 | VCMS:SEA14 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 517 | VCMS:FEW14 V=_____um/s, ____kW | 0 | 45
[13 empty] | 518 | VCMS:FEW14 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 519 | VCMS:FEA14 V=_____um/s, ____kW | 0 | 45
[13 empty] | 520 | VCMS:FEA14 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 521 | VCMS:AMA14 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 522 | VCMS:SEW15 V=_____um/s, ____kW | 0 | 45
[13 empty] | 523 | VCMS:SEW15 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 524 | VCMS:SEA15 V=_____um/s, ____kW | 0 | 45
[13 empty] | 525 | VCMS:SEA15 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 526 | VCMS:FEW15 V=_____um/s, ____kW | 0 | 45
[13 empty] | 527 | VCMS:FEW15 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 528 | VCMS:FEA15 V=_____um/s, ____kW | 0 | 45
[13 empty] | 529 | VCMS:FEA15 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 530 | VCMS:AMA15 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 531 | VCMS:SEW31 V=_____um/s, ____kW | 0 | 45
[13 empty] | 532 | VCMS:SEW31 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 533 | VCMS:SEA31 V=_____um/s, ____kW | 0 | 45
[13 empty] | 534 | VCMS:SEA31 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 535 | VCMS:FEW31 V=_____um/s, ____kW | 0 | 45
[13 empty] | 536 | VCMS:FEW31 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 537 | VCMS:FEA31 V=_____um/s, ____kW | 0 | 45
[13 empty] | 538 | VCMS:FEA31 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 539 | VCMS:AMA31 V=_____um/s, ____kW | 0 | 45
[13 empty] | 540 | VCMS:SEW32 V=_____um/s, ____kW | 0 | 45
[13 empty] | 541 | VCMS:SEW32 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 542 | VCMS:SEA32 V=_____um/s, ____kW | 0 | 45
[13 empty] | 543 | VCMS:SEA32 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 544 | VCMS:FEW32 V=_____um/s, ____kW | 0 | 45
[13 empty] | 545 | VCMS:FEW32 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 546 | VCMS:FEA32 V=_____um/s, ____kW | 0 | 45
[13 empty] | 547 | VCMS:FEA32 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 548 | VCMS:AMA32 V=_____um/s, ____kW | 0 | 45
[13 empty] | 549 | VCMS:Element warn. bearing #__ | 0 | 45
[13 empty] | 550 | VCMS:Element alarm bearing #__ | 0 | 45
[13 empty] | 551 | VCMS:Undefined error code | 0 | 45
[13 empty] | 552 | VCMS:Unknown Command received | 0 | 45
[13 empty] | 553 | VCMS:Error in INI file | 0 | 45
[13 empty] | 554 | VCMS:Timer is inactive | 0 | 45
[13 empty] | 555 | VCMS:Element alarm bearing #__ | 0 | 45
[13 empty] | 556 | Grid inverter Filter: Overload | 0 | 45
[13 empty] | 557 | RT activation no. exceeded:___ | 1 | 28
[13 empty] | 558 | VCMS:Unknown Command received | 0 | 45
[13 empty] | 559 | VCMS:Error in INI file | 0 | 45
[13 empty] | 560 | VCMS:File open error | 0 | 45
[13 empty] | 561 | Memory allocation failed | 0 | 45
[13 empty] | 562 | SW versionconflict GND/VCMS | 0 | 45
[13 empty] | 563 | No communication with VCMS | 0 | 45
[13 empty] | 564 | Shortcircuitindicator1 Active | 0 | 45
[13 empty] | 565 | Shortcircuitindicator2 Active | 0 | 45
[13 empty] | 566 | SF6 Pressure low | 0 | 45
[13 empty] | 567 | Close Gridbreaker 1 | 0 | 45
[13 empty] | 568 | Gridbreaker 1 closed | 0 | 45
[13 empty] | 569 | Open Gridbreaker 1 | 0 | 45
[13 empty] | 570 | Gridbreaker 1 open | 0 | 45
[13 empty] | 571 | Gridbreaker 1 grounded | 0 | 45
[13 empty] | 572 | Close Gridbreaker 2 | 0 | 45
[13 empty] | 573 | Gridbreaker 2 closed | 0 | 45
[13 empty] | 574 | Open Gridbreaker 2 | 0 | 45
[13 empty] | 575 | Gridbreaker 2 open | 0 | 45
[13 empty] | 576 | Gridbreaker 2 grounded | 0 | 45
[13 empty] | 577 | Current Limiter Feedback error | 0 | 45
[13 empty] | 578 | CL.active ____ms ____kJ/O | 0 | 45
[13 empty] | 579 | CL.time exceeded____ms____kJ/O | 0 | 45
[13 empty] | 580 | Current Limiter Voltage inval. | 0 | 45
[13 empty] | 581 | Current Limiter temp. high R | 0 | 45
[13 empty] | 582 | Current Limiter Run Error | 0 | 45
[13 empty] | 583 | Current Limiter Timeout | 0 | 45
[13 empty] | 584 | CL Capacitor under voltage | 0 | 45
[13 empty] | 585 | Q7 Close via RCS | 0 | 45
[13 empty] | 586 | Q8 Close via RCS | 0 | 45
[13 empty] | 587 | Q16 Close via RCS | 0 | 45
[13 empty] | 588 | User ____ primary access | 0 | 45
[13 empty] | 589 | Obsolete | 0 | 45
[13 empty] | 590 | Obsolete | 0 | 45
[13 empty] | 591 | User ____ Access denied | 0 | 45
[13 empty] | 592 | New global account | 0 | 45
[13 empty] | 593 | New local account | 0 | 45
[13 empty] | 594 | Hoist mode failure | 0 | 45
[13 empty] | 595 | Help button activated | 0 | 45
[13 empty] | 596 | Hoist mode active | 0 | 45
[13 empty] | 597 | Reverse Yaw | 0 | 45
[13 empty] | 598 | Circuit breaker open | 1 | 28
[13 empty] | 599 | Error in UPS | 0 | 45
[13 empty] | 600 | UPS battery activated | 0 | 45
[13 empty] | 601 | Wind estimate dev. __._m/s | 0 | 45
[13 empty] | 602 | Error in ColdBoot file | 0 | 45
[13 empty] | 603 | 3218.bin File missing | 0 | 45
[13 empty] | 604 | Remote Reboot | 0 | 45
[13 empty] | 605 | Brush on gen.slip ring is worn | 0 | 45
[13 empty] | 606 | Item_____ Updated by user_____ | 0 | 45
[13 empty] | 607 | Control of LT blocked | 0 | 45
[13 empty] | 608 | STOP through RCS | 0 | 45
[13 empty] | 609 | Auto Yaw blocked | 0 | 45
[13 empty] | 610 | Error Slip Ring Fan Diff:___°C | 0 | 45
[13 empty] | 611 | External error : __, ___ | 0 | 45
[13 empty] | 614 | Contactor switching, max | 0 | 45
[13 empty] | 615 | Err_____ Rem. Ack by user_____ | 0 | 45
[13 empty] | 616 | Bypass miss. before phasecomp_ | 0 | 45
[13 empty] | 617 | Feedback = _, Phasecomp__ | 0 | 45
[13 empty] | 618 | Fuse phasecomp + Gen2 cut | 0 | 45
[13 empty] | 619 | Logic error phase compensation | 0 | 45
[13 empty] | 620 | Phasecomp.:__ in | 0 | 45
[13 empty] | 621 | Phasecomp.:__ out | 0 | 45
[13 empty] | 622 | Phasecomp temp.disconn.:____ V | 0 | 45
[13 empty] | 623 | Awaiting delay in phasecomp:_ | 0 | 45
[13 empty] | 624 | PComp. dis. avr____ step ____V | 0 | 45
[13 empty] | 625 | Command to VCMS failed | 0 | 45
[13 empty] | 626 | RCC CRC error | 0 | 45
[13 empty] | 627 | RCC Timeout | 0 | 45
[13 empty] | 628 | CRC/Timeout error to RCC | 0 | 45
[13 empty] | 629 | RCC status error:______ | 0 | 45
[13 empty] | 630 | RCC header error | 0 | 45
[13 empty] | 631 | RCC IVCE error _ | 0 | 45
[13 empty] | 632 | RCC ILIM error _ | 0 | 45
[13 empty] | 633 | RCC temperature error _ | 0 | 45
[13 empty] | 634 | RCC voltage error ___ | 0 | 45
[13 empty] | 635 | RCC RAM error | 0 | 45
[13 empty] | 636 | RCC communication error | 0 | 45
[13 empty] | 637 | RCC error in master prom _ | 0 | 45
[13 empty] | 638 | RCC NAK during upload. | 0 | 45
[13 empty] | 639 | RCC NAK start appl._____,_____ | 0 | 45
[13 empty] | 640 | Unknown RCC Log message ___ | 0 | 45
[13 empty] | 641 | RCC upload _. Result: _ | 0 | 45
[13 empty] | 642 | RCC CE overvoltage: ____ V | 0 | 45
[13 empty] | 643 | RCC OVP active: ____ V | 0 | 45
[13 empty] | 644 | RCC high temperature _ | 0 | 45
[13 empty] | 645 | RCC low temperature _ | 0 | 45
[13 empty] | 646 | RCC high voltage ___ | 0 | 45
[13 empty] | 647 | RCC low voltage ___ | 0 | 45
[13 empty] | 648 | Illegal RCCState | 0 | 45
[13 empty] | 649 | VRCC.bin File missing | 0 | 45
[13 empty] | 650 | No satelites tracked | 0 | 45
[13 empty] | 651 | One satelite tracked | 0 | 45
[13 empty] | 652 | Current Limiter temp. high Thy | 0 | 45
[13 empty] | 653 | CL VMP Timeout | 0 | 45
[13 empty] | 654 | VCMS:theApp is suspended | 0 | 45
[13 empty] | 655 | FeedBack = _, VRCC Pump S___ | 0 | 45
[13 empty] | 656 | FeedBack = _, VRCC Fan S___A | 0 | 45
[13 empty] | 657 | FeedBack = _, VRCC Fan S___B | 0 | 45
[13 empty] | 658 | Low level VRCC cool water | 0 | 45
[13 empty] | 659 | High temp.VRCC coolwater:___°C | 0 | 45
[13 empty] | 660 | Thermoerror VRCC Pump F___ | 0 | 45
[13 empty] | 661 | Thermoerror VRCC fan low F___A | 0 | 45
[13 empty] | 662 | Thermoerr. VRCC fan High F___B | 0 | 45
[13 empty] | 663 | VCMS, error in historic DB | 0 | 45
[13 empty] | 664 | VCMS, historic DB disabled | 0 | 45
[13 empty] | 665 | Feedback = _, Bypass contactor | 0 | 45
[13 empty] | 666 | Feedback = _, Generator_ | 0 | 45
[13 empty] | 667 | Stop error during thyr. firing | 0 | 45
[13 empty] | 668 | Commencing thyristor-in | 0 | 45
[13 empty] | 669 | Commencing thyristor-out | 0 | 45
[13 empty] | 670 | Thyristors stopped | 0 | 45
[13 empty] | 671 | Thyristor firing interrupted | 0 | 45
[13 empty] | 672 | Commence thyristor test Gen_ | 0 | 45
[13 empty] | 673 | End thyristor test Gen_ | 0 | 45
[13 empty] | 674 | Commence motorstart Gen_ | 0 | 45
[13 empty] | 675 | End motorstart Gen_ | 0 | 45
[13 empty] | 676 | Bypass missing before gen_ | 0 | 45
[13 empty] | 677 | Generatorbreaker open | 0 | 45
[13 empty] | 678 | Illegal GenLogicState | 0 | 45
[13 empty] | 679 | CT316 driver fail | 0 | 45
[13 empty] | 680 | VCMS: No top communication | 0 | 45
[13 empty] | 681 | VCMS: No gnd communication | 0 | 45
[13 empty] | 682 | VCMS: No hub communication | 0 | 45
[13 empty] | 683 | VCMS: No VCPM communication | 0 | 45
[13 empty] | 684 | VCMS: Parameter mismatch | 0 | 45
[13 empty] | 685 | RCCPRM.bin File missing | 0 | 45
[13 empty] | 686 | RCC.bin File missing | 0 | 45
[13 empty] | 687 | Hub Top Sync timeout | 0 | 45
[13 empty] | 688 | VCMS:Error in RS INI file | 0 | 45
[13 empty] | 689 | Remote AP Crash | 0 | 45
[13 empty] | 690 | Signal operatinal. | 0 | 45
[13 empty] | 691 | SignalError. _____,_____ | 0 | 45
[13 empty] | 692 | SignalError-PAU(a) _____,_____ | 0 | 45
[13 empty] | 693 | SignalError-PAUSE _____,_____ | 0 | 45
[13 empty] | 694 | SignalError-STOP _____,_____ | 0 | 45
[13 empty] | 695 | SignalError-EMERG _____,_____ | 0 | 45
[13 empty] | 696 | CAN API error. | 0 | 45
[13 empty] | 697 | CAN SDO error. | 0 | 45
[13 empty] | 698 | CAN emergency error. | 0 | 45
[13 empty] | 699 | Low Battery Ground | 0 | 45
[13 empty] | 700 | Low Battery Nacelle | 0 | 45
[13 empty] | 701 | Low Battery Hub | 0 | 45
[13 empty] | 702 | VCP detects Q8 feedback missin | 0 | 45
[13 empty] | 703 | RT Dip exc.lim.:___%:_____e-2s | 0 | 45
[13 empty] | 704 | Ch High res. load C_ Load:___% | 89 | 2
[13 empty] | 705 | Ch High IGBT load C_ Load:___% | 0 | 45
[13 empty] | 706 | Ch High res. dev. C_ R:_.__Ohm | 0 | 45
[13 empty] | 707 | Ch hardware error C_ | 0 | 45
[13 empty] | 708 | RT High Rotor Current L_:____A | 0 | 45
[13 empty] | 709 | RT Ext. High Rot.Cur. L_:____A | 0 | 45
[13 empty] | 710 | RT Rotor HW Error L_:____A | 0 | 45
[13 empty] | 711 | RT Number:__,LastRT time_____s | 0 | 45
[13 empty] | 712 | Ch active D Load C1___% C2___% | 0 | 45
[13 empty] | 713 | Preheater, thermal cutout | 0 | 45
[13 empty] | 714 | Preheating timeout in run mode | 0 | 45
[13 empty] | 715 | Possible Humidity sensor err. | 0 | 45
[13 empty] | 716 | Hoist failure -low brake press | 0 | 45
[13 empty] | 717 | SMTP client failed | 0 | 45
[13 empty] | 718 | Hoist failure - max gen. rpm | 0 | 45
[13 empty] | 719 | Close Gridbreaker 3 | 0 | 45
[13 empty] | 720 | Gridbreaker 3 closed | 0 | 45
[13 empty] | 721 | Open Gridbreaker 3 | 0 | 45
[13 empty] | 722 | Gridbreaker 3 open | 0 | 45
[13 empty] | 723 | Obsolete | 0 | 45
[13 empty] | 724 | Obsolete | 0 | 45
[13 empty] | 725 | No RT, High Rotor Cur L_:____A | 0 | 45
[13 empty] | 726 | No RT, Ex.Hig.Rot.Cur L_:____A | 0 | 45
[13 empty] | 727 | No RT, Rotor HW.Error L_:____A | 0 | 45
[13 empty] | 728 | Dip detec. V:___%,t:_____e-2s | 0 | 45
[13 empty] | 729 | Timeout EMCPitchSelfTest ___s | 0 | 45
[13 empty] | 730 | High wind EMC Pitchtest ___m/s | 0 | 45
[13 empty] | 731 | _ EMC pitchAccu failed __° | 0 | 45
[13 empty] | 732 | EMC pitchtest deviation __° | 0 | 45
[13 empty] | 733 | Blade _ EMC pitchSystem Err. _ | 0 | 45
[13 empty] | 734 | Error EMC pitch blade _ ___° | 0 | 45
[13 empty] | 735 | Long EMCpitch time bladeX_ __s | 0 | 45
[13 empty] | 736 | Blade _ pitch react. time___s | 0 | 45
[13 empty] | 737 | Close F60 | 0 | 45
[13 empty] | 738 | F60 closed | 0 | 45
[13 empty] | 739 | Fog horn inactive | 0 | 45
[13 empty] | 740 | Fog horn active | 0 | 45
[13 empty] | 741 | Ext. 24V persistent in Hub | 0 | 45
[13 empty] | 742 | Test:__________, __________ | 0 | 45
[13 empty] | 743 | EMC Pitch Accu Test Started | 0 | 45
[13 empty] | 744 | EMC Pitch Accu Test Stopped | 0 | 45
[13 empty] | 745 | EMC Pitch Accu Test Blade _ | 0 | 45
[13 empty] | 746 | EMC Pitch Accu Test Aborted | 0 | 45
[13 empty] | 747 | EMC Pitch Accu Test Failed | 0 | 45
[13 empty] | 748 | Too many contactor supervis. | 0 | 45
[13 empty] | 749 | Extra info. Err:___ P:____._kW | 0 | 45
[13 empty] | 750 | Coldboot parameters lost | 0 | 45
[13 empty] | 751 | Parameters not recovered | 0 | 45
[13 empty] | 752 | Automatic reestablish failed | 0 | 45
[13 empty] | 753 | Automatic reestablish OK | 0 | 45
[13 empty] | 754 | no RT, Dip no __,___e-2 | 0 | 45
[13 empty] | 755 | VCMS:AMA11 V=_____um/s, ____kW | 0 | 45
[13 empty] | 756 | VCMS:AMA12 V=_____um/s, ____kW | 0 | 45
[13 empty] | 757 | VCMS:AMA13 V=_____um/s, ____kW | 0 | 45
[13 empty] | 758 | VCMS:AMA14 V=_____um/s, ____kW | 0 | 45
[13 empty] | 759 | VCMS:AMA15 V=_____um/s, ____kW | 0 | 45
[13 empty] | 760 | VCMS:AMA31 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 761 | VCMS:AMA32 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 762 | VCMS:SEW51 V=_____um/s, ____kW | 0 | 45
[13 empty] | 763 | VCMS:SEW51 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 764 | VCMS:SEA51 V=_____um/s, ____kW | 0 | 45
[13 empty] | 765 | VCMS:SEA51 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 766 | VCMS:FEW51 V=_____um/s, ____kW | 0 | 45
[13 empty] | 767 | VCMS:FEW51 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 768 | VCMS:FEA51 V=_____um/s, ____kW | 0 | 45
[13 empty] | 769 | VCMS:FEA51 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 770 | VCMS:AMA51 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 771 | VCMS:AMA51 V=_____um/s, ____kW | 0 | 45
[13 empty] | 772 | VCMS:SEW52 V=_____um/s, ____kW | 0 | 45
[13 empty] | 773 | VCMS:SEW52 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 774 | VCMS:SEA52 V=_____um/s, ____kW | 0 | 45
[13 empty] | 775 | VCMS:SEA52 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 776 | VCMS:FEW52 V=_____um/s, ____kW | 0 | 45
[13 empty] | 777 | VCMS:FEW52 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 778 | VCMS:FEA52 V=_____um/s, ____kW | 0 | 45
[13 empty] | 779 | VCMS:FEA52 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 780 | VCMS:AMA52 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 781 | VCMS:AMA52 V=_____um/s, ____kW | 0 | 45
[13 empty] | 782 | VCMS:SEW53 V=_____um/s, ____kW | 0 | 45
[13 empty] | 783 | VCMS:SEW53 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 784 | VCMS:SEA53 V=_____um/s, ____kW | 0 | 45
[13 empty] | 785 | VCMS:SEA53 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 786 | VCMS:FEW53 V=_____um/s, ____kW | 0 | 45
[13 empty] | 787 | VCMS:FEW53 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 788 | VCMS:FEA53 V=_____um/s, ____kW | 0 | 45
[13 empty] | 789 | VCMS:FEA53 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 790 | VCMS:AMA53 A=_____mm/s2,____kW | 0 | 45
[13 empty] | 791 | VCMS:AMA53 V=_____um/s, ____kW | 0 | 45
[13 empty] | 792 | VCMS:Node __ overload error | 0 | 45
[13 empty] | 793 | VCMS:Node __ reset error | 0 | 45
[13 empty] | 794 | VCMS:Assertion failure | 0 | 45
[13 empty] | 795 | VCMS:Socket error | 0 | 45
[13 empty] | 796 | VCMS:Start client __ error | 0 | 45
[13 empty] | 797 | RT,NotReady during next __min. | 0 | 45
[13 empty] | 798 | Phasecomp temp.disc.:___.__ Hz | 0 | 45
[13 empty] | 799 | PComp. dis. avr____ step ____A | 0 | 45
[13 empty] | 800 | PComp. dis. step__.__/__.__Hz | 0 | 45
[13 empty] | 801 | Thermoerror Hydr. cool F___ | 0 | 45
[13 empty] | 802 | Pitch Lubricate Motion ___._ ° | 0 | 45
[13 empty] | 803 | GenRpm error measurem. ____rpm | 0 | 45
[13 empty] | 804 | Invalid Turbine ID-number | 0 | 45
[13 empty] | 805 | VCMS:Node __ defect | 0 | 45
[13 empty] | 806 | Time changed more than __sec,_ | 0 | 45
[13 empty] | 807 | Too many interval usec timers | 0 | 45
[13 empty] | 808 | Interval usec timer not init. | 0 | 45
[13 empty] | 809 | VCMS:__ nodes not responding | 0 | 45
[13 empty] | 810 | VCMS:Net jammed | 0 | 45
[13 empty] | 811 | RT not allowed. Dip no __ | 0 | 45
[13 empty] | 812 | Feedback = _, Phasecomp. 1 | 0 | 45
[13 empty] | 813 | Feedback = _, Phasecomp. 2 | 0 | 45
[13 empty] | 814 | Feedback = _, Phasecomp. 3 | 0 | 45
[13 empty] | 815 | Feedback = _, Phasecomp. 4 | 0 | 45
[13 empty] | 816 | Feedback = _, Phasecomp. 5 | 0 | 45
[13 empty] | 817 | Feedback = _, Phasecomp. 6 | 0 | 45
[13 empty] | 818 | Feedback = _, Phasecomp. 7 | 0 | 45
[13 empty] | 819 | Feedback = _, Phasecomp. 8 | 0 | 45
[13 empty] | 820 | Feedback = _, Phasecomp. 9 | 0 | 45
[13 empty] | 821 | Feedback = _, Phasecomp. 10 | 0 | 45
[13 empty] | 822 | Feedback = _, Phasecomp. 11 | 0 | 45
[13 empty] | 823 | Feedback = _, Phasecomp. 12 | 0 | 45
[13 empty] | 824 | Max. Ph. Comp. FB. Warnings | 0 | 45
[13 empty] | 825 | Ph. C. low reac. pow _____hVAr | 0 | 45
[13 empty] | 826 | Gridstate queue overflow | 0 | 45
[13 empty] | 827 | Nac Heaters __, Temp:___°C | 0 | 45
[13 empty] | 828 | Start Frequency error:___.__Hz | 0 | 45
[13 empty] | 829 | Timeout Start Frequency error | 0 | 45
[13 empty] | 830 | External power ref.:____kW | 0 | 45
[13 empty] | 831 | SWDS High Wind:__._m/s dir:___ | 0 | 45
[13 empty] | 832 | Remote service panel taken _ _ | 0 | 45
[13 empty] | 833 | Main WS switch from WS_ to WS_ | 0 | 45
[13 empty] | 834 | Remote service panel free _ _ | 0 | 45
[13 empty] | 835 | RT, UnexpAGO2Event C__ S __ | 0 | 45
[13 empty] | 836 | RT, IntAGO2CtrlErr C__ S __ | 0 | 45
[13 empty] | 837 | RT AGO2Sta.Cyc. Count_,____V | 0 | 45
[13 empty] | 838 | Q8 contactor in state: ___ | 0 | 45
[13 empty] | 839 | VCS/VCRS dummy alarm1 ____ ___ | 0 | 45
[13 empty] | 840 | VCS/VCRS dummy alarm2 ____ ___ | 0 | 45
[13 empty] | 841 | VCS/VCRS dummy alarm3 ____ ___ | 0 | 45
[13 empty] | 842 | VCS/VCRS dummy alarm4 ____ ___ | 0 | 45
[13 empty] | 843 | VCS/VCRS dummy alarm5 ____ ___ | 0 | 45
[13 empty] | 844 | VCS/VCRS dummy warn1 ____ ____ | 0 | 45
[13 empty] | 845 | VCS/VCRS dummy warn2 ____ ____ | 0 | 45
[13 empty] | 846 | VCS/VCRS dummy warn3 ____ ____ | 0 | 45
[13 empty] | 847 | VCS/VCRS dummy warn4 ____ ____ | 0 | 45
[13 empty] | 848 | VCS/VCRS dummy warn5 ____ ____ | 0 | 45
[13 empty] | 849 | RT DC Undervoltage: ____V | 0 | 45
[13 empty] | 850 | No RT, DC Undervoltage: ____V | 0 | 45
[13 empty] | 851 | Low temp. Gen bearing _:___°C | 0 | 45
[13 empty] | 852 | Extr Extr high volt. L_: ___ V | 0 | 45
[13 empty] | 853 | Puls Pause on:___°C/air:___°C | 0 | 45
[13 empty] | 854 | Puls Pause off:___°C/air:___°C | 0 | 45
[13 empty] | 855 | Nacelle reset not found | 0 | 45
[13 empty] | 856 | No ParameterDefinition file | 0 | 45
[13 empty] | 857 | SW/Param def. vers. conflict | 0 | 45
[13 empty] | 858 | Error in ParameterDef. file | 0 | 45
[13 empty] | 859 | Error in Param. def. parser | 0 | 45
[13 empty] | 860 | No ParameterValues file | 0 | 45
[13 empty] | 861 | SW/Param value vers. conflict | 0 | 45
[13 empty] | 862 | Error in ParameterValue. file | 0 | 45
[13 empty] | 863 | Error in Param. Value parser | 0 | 45
[13 empty] | 864 | Cmd scan suspended ____ ____ | 0 | 45
[13 empty] | 865 | WS2 Dir Frozen __._m/s ___._° | 0 | 45
[13 empty] | 866 | WS1 checksum err. | 0 | 45
[13 empty] | 867 | WS2 checksum err. | 0 | 45
[13 empty] | 868 | Gear temp. diff. ___°C ___°C | 0 | 45
[13 empty] | 869 | PrepReconTimeout,__m/s____rpm | 0 | 45
[13 empty] | 870 | Gen_ Speed Control Connect | 0 | 45
[13 empty] | 871 | LSO Timeout State __ | 0 | 45
[13 empty] | 872 | RunningUpTimeout,__m/s____rpm | 0 | 45
[13 empty] | 873 | Instable CtrlState operation | 0 | 45
[13 empty] | 874 | RCC not ready at gen. connect | 0 | 45
[13 empty] | 875 | Timeout comm. Tower acc. | 0 | 45
[13 empty] | 876 | AGO timeout state:__ * ______ | 0 | 45
[13 empty] | 877 | Power drop: _____ -> _____ kW | 0 | 45
[13 empty] | 878 | SSL Time to Gen. Disc. ___._s | 0 | 45
[13 empty] | 879 | SSL Power ____kW Min: _____kW | 0 | 45
[13 empty] | 880 | SSL RPM ____ to <200 in ___._s | 0 | 45
[13 empty] | 881 | SSL Max. pitch vel. ___._°/s | 0 | 45
[13 empty] | 882 | Hub heating | 0 | 45
[13 empty] | 883 | Power Curve __._m/s ______kW | 0 | 45
[13 empty] | 884 | P Curve Ice __._m/s ______kW | 0 | 45
[13 empty] | 885 | Feedback = _, Bypass L1 | 0 | 45
[13 empty] | 886 | Feedback = _, Bypass L2 | 0 | 45
[13 empty] | 887 | Feedback = _, Bypass L3 | 0 | 45
[13 empty] | 888 | UTC time changed _____ min | 0 | 45
[13 empty] | 889 | External RPM not Reset | 0 | 45
[13 empty] | 890 | Peak Gen.:____RPM Rot.:__._RPM | 0 | 45
[13 empty] | 891 | Yaw prot.__.__m/s2 Wdir____._° | 0 | 45
[13 empty] | 892 | Yaw gear protection stop | 0 | 45
[13 empty] | 893 | Heating slipring (H=0/PH=1) _ | 0 | 45
[13 empty] | 894 | Heating nacelle and gear oil | 0 | 45
[13 empty] | 895 | Heating nacelle ___°C | 0 | 45
[13 empty] | 896 | Heating Hydraulic oil ___°C | 0 | 45
[13 empty] | 897 | Heating valve block (pause) | 0 | 45
[13 empty] | 898 | Heating valve block (stop) | 0 | 45
[13 empty] | 899 | Grid volt above stop lim ___% | 0 | 45
[13 empty] | 900 | Pause pressed on keyboard | 28 | 5
[13 empty] | 901 | DC Overvolt stop:____V state__ | 0 | 45
[13 empty] | 902 | Max DP filt. A: ____RPM/___°C | 0 | 45
[13 empty] | 903 | Low oil level, ____RPM/___°C | 0 | 45
[13 empty] | 904 | Accumulator test done -> OK | 0 | 45
[13 empty] | 905 | Pitch accu fail _ 1Z14/ _ 3Z2 | 0 | 45
[13 empty] | 906 | EMF accu fail: 5Z01 axis _ | 0 | 45
[13 empty] | 907 | Brake accu fail:_ 2Z01/_ 2Z05 | 0 | 45
[13 empty] | 908 | Accumulator fail Solenoid | 0 | 45
[13 empty] | 909 | Heating slipring time ____ Sec | 0 | 45
[13 empty] | 910 | Tow. acc. X Fault:__.__ m/s^2 | 0 | 45
[13 empty] | 911 | Tow. acc. Y Fault:__.__ m/s^2 | 0 | 45
[13 empty] | 912 | Supply error: ___.__ Hz ___ V | 0 | 45
[13 empty] | 913 | Shutdown timeout Pause Slow | 0 | 45
[13 empty] | 914 | Shutdown timeout Pause Fast | 0 | 45
[13 empty] | 915 | Shutdown timeout Stop Slow | 0 | 45
[13 empty] | 916 | Shutdown timeout Stop Fast | 0 | 45
[13 empty] | 917 | High temp. Gen bear. DE:___°C | 0 | 45
[13 empty] | 918 | Low temp. Gen bear. DE:___°C | 0 | 45
[13 empty] | 919 | High temp. Gen bear. NDE:___°C | 0 | 45
[13 empty] | 920 | Low temp. Gen bear. NDE:___°C | 0 | 45
[13 empty] | 921 | Too many Tow. acc. X Warnings | 0 | 45
[13 empty] | 922 | Tow. acc. X-dead | 0 | 45
[13 empty] | 923 | Accumulator fail Mechanical | 0 | 45
[13 empty] | 924 | Accu test not completed | 0 | 45
[13 empty] | 925 | EMF accumulator failures: _ | 0 | 45
[13 empty] | 926 | Disc brake accumulator failure | 0 | 45
[13 empty] | 927 | High Delta Gearbear :___°C | 0 | 45
[13 empty] | 928 | Disconnect High Freq ___.__ Hz | 0 | 45
[13 empty] | 929 | No Pitch Hydraulic Power | 0 | 45
[13 empty] | 930 | High temp. main bear. :___°C | 0 | 45
[13 empty] | 931 | Arc light detected | 6 | 12
[13 empty] | 932 | Gear oil bypass:____RPM/___°C | 0 | 45
[13 empty] | 933 | Hi Gear sys pres:____RPM/___°C | 0 | 45
[13 empty] | 934 | DP Gear oil fltr:____RPM/___°C | 0 | 45
[13 empty] | 935 | Hi DP inlin fltr:____RPM/___°C | 0 | 45
[13 empty] | 936 | Lo DP inlin fltr:____RPM/___°C | 0 | 45
[13 empty] | 937 | Insp inline fltr:____RPM/___°C | 0 | 45
[13 empty] | 938 | Yaw direction incorrect | 0 | 45
[13 empty] | 939 | Blade bearing Act.:__._° St.:_ | 0 | 45
[13 empty] | 940 | Blade bearing Act.:__._° St.:_ | 0 | 45
[13 empty] | 941 | BBCM: Err:__._° Windsp:__._m/s | 0 | 45
[13 empty] | 942 | TripQ8 extr high HydTemp:___°C | 0 | 45
[13 empty] | 943 | Failure in Anemometer | 0 | 45
[13 empty] | 944 | WS1 Anemometer Frozen | 0 | 45
[13 empty] | 945 | Failure in Wind Vane Sensor | 0 | 45
[13 empty] | 946 | VOG Test timed out | 0 | 45
[13 empty] | 947 | NRMS NoiseMode:__,HourPeriod:_ | 0 | 45
[13 empty] | 948 | NRMS NoiseMode:__,Wind:__._m/s | 0 | 45
[13 empty] | 949 | NRMS NoiseMode:__,Dir.:___deg | 0 | 45
[13 empty] | 950 | NRMS NoiseMode:0,Deactivated | 0 | 45
[13 empty] | 951 | WS1 Vane Frozen __._m/s ___._° | 0 | 45
[13 empty] | 952 | WS1 Vane in Turbulence/Frozen | 0 | 45
[13 empty] | 953 | WS1 Wind Speed Out of Range | 0 | 45
[13 empty] | 954 | Key switch: Remote control | 0 | 45
[13 empty] | 955 | Key switch: Local/Remote | 0 | 45
[13 empty] | 956 | Key switch: Local control | 0 | 45
[13 empty] | 957 | pause after power cut out | 0 | 45
[13 empty] | 958 | Yaw Lubrication Failed | 0 | 45
[13 empty] | 959 | pause after grid drop | 0 | 45
[13 empty] | 960 | Transformer Hatch Fb _ | 0 | 45
[13 empty] | 961 | WaterCoolLiquidLow | 0 | 45
[13 empty] | 962 | SWDS Low Wind:__._m/s dir:___ | 0 | 45
[13 empty] | 963 | OptiStop Internal Fault | 0 | 45
[13 empty] | 964 | OptiStop Communication Fault | 0 | 45
[13 empty] | 965 | OptiStop Alive Fault | 0 | 45
[13 empty] | 966 | OptiStop Rotor Speed Fault | 0 | 45
[13 empty] | 967 | OptiStop Rotor Speed Std Dev | 0 | 45
[13 empty] | 968 | OptiStop Plug Mounted Fault | 0 | 45
[13 empty] | 969 | OptiStop Int Battery Fault | 0 | 45
[13 empty] | 970 | OptiStop Ups1 Battery Fault | 0 | 45
[13 empty] | 971 | OptiStop Ups2 Battery Fault | 0 | 45
[13 empty] | 972 | VCP upload failed | 0 | 45
[13 empty] | 973 | High temp RE main bear:___°C | 0 | 45
[13 empty] | 974 | High temp NRE main bear:___°C | 0 | 45
[13 empty] | 975 | SlipRTemp Diff T___°C B___°C | 0 | 45
[13 empty] | 976 | Yaw activity is not dectected | 0 | 45
[13 empty] | 977 | YawSpeedFault:__ Pos:___° | 0 | 45
[13 empty] | 978 | Yaw Speed Exc:___° Rate:__sec | 0 | 45
[13 empty] | 979 | Yaw direction incorrect | 0 | 45
[13 empty] | 980 | Yaw Position is changed:___° | 0 | 45
[13 empty] | 981 | Load sensor not calibrated | 0 | 45
[13 empty] | 982 | Loadsensor A error | 0 | 45
[13 empty] | 983 | Loadsensor B error | 0 | 45
[13 empty] | 984 | Loadsensor C error | 0 | 45
[13 empty] | 985 | TowerAccY SignalDead __m/s^2 | 0 | 45
[13 empty] | 986 | TowerAccY NoZeroCross __m/s^2 | 0 | 45
[13 empty] | 987 | Thermoerror Waterpump | 0 | 45
[13 empty] | 988 | NRMS NoiseMode:__,ClockHour:_ | 0 | 45
[13 empty] | 989 | OverFreq:__.__ Hz Ref:__.__ Hz | 0 | 45
[13 empty] | 990 | WS1 ConstSpeed:__._m/s ActWS_ | 0 | 45
[13 empty] | 991 | WS1 ConstDir.: ___._° ActWS_ | 0 | 45
[13 empty] | 992 | WS2 ConstSpeed:__._m/s ActWS_ | 0 | 45
[13 empty] | 993 | WS2 ConstDir.: ___._° ActWS_ | 0 | 45
[13 empty] | 994 | Pitch error on all blades | 0 | 45
[13 empty] | 995 | Last ArcNet reconfig count:__ | 0 | 45
[13 empty] | 996 | Curtailed 1. ____kW 2. __% | 0 | 45
[13 empty] | 997 | Curtailed 1. __% 2. ____kW | 0 | 45
[13 empty] | 998 | Grid volt under stop lim ___% | 0 | 45
[13 empty] | 999 | Extended Yaw Status _ | 0 | 45
[13 empty] | 1000 | Power Backup Status _ | 0 | 45
[13 empty] | 1001 | Alarms Ignored Dur Ext Yaw _ | 0 | 45
[13 empty] | 1002 | Extended Yaw Current Status _ | 0 | 45
[13 empty] | 1003 | Failure in Anemometer | 0 | 45
[13 empty] | 1004 | WS2 Anemometer Frozen | 0 | 45
[13 empty] | 1005 | Failure in Wind Vane Sensor | 0 | 45
[13 empty] | 1006 | WS2 Vane Frozen __._m/s ___._° | 0 | 45
[13 empty] | 1007 | WS2 Vane in Turbulence/Frozen | 0 | 45
[13 empty] | 1008 | High Q7 current ____A L_ | 0 | 45
[13 empty] | 1009 | Extr High Q7 current ____A L_ | 0 | 45
[13 empty] | 1010 | Asym. Q7 current ____A L_ | 0 | 45
[13 empty] | 1011 | Ground Q7 current ____A | 0 | 45
[13 empty] | 1709 | TYC Const Load Sig A Detected | 0 | 45
[13 empty] | 1710 | TYC Const Load Sig B Detected | 0 | 45
[13 empty] | 1711 | TYC Const Load Sig C Detected | 0 | 45
[13 empty] | 1712 | TYC Gain Hyst Err Detected | 0 | 45
[13 empty] | 1715 | TYC Load Sensor Status A Err | 0 | 45
[13 empty] | 1716 | TYC Load Sensor Status B Err | 0 | 45
[13 empty] | 1717 | TYC Load Sensor Status C Err | 0 | 45
[13 empty] | 1718 | TYC Azim Sensor Status Err | 0 | 45
[13 empty] | 1719 | TYC Load Sensor Calib Err | 0 | 45
[13 empty] | 1721 | TYC Rotor Azim Err Detected | 0 | 45
[13 empty] | 2001 | VCS/VCRS dummy alarm1 ____ ___ | 0 | 45
[13 empty] | 2002 | VCS/VCRS dummy alarm2 ____ ___ | 0 | 45
[13 empty] | 2003 | VCS/VCRS dummy alarm3 ____ ___ | 0 | 45
[13 empty] | 2004 | VCS/VCRS dummy alarm4 ____ ___ | 0 | 45
[13 empty] | 2005 | VCS/VCRS dummy alarm5 ____ ___ | 0 | 45
[13 empty] | 2006 | Thermoerror hydraulicmotor | 0 | 45
[13 empty] | 2007 | Thermoerror Int. VCS Fan F____ | 0 | 45
[13 empty] | 2008 | Thermoerror ext. VCS Fan F____ | 0 | 45
[13 empty] | 2009 | Safety System Fault | 0 | 45
[13 empty] | 2648 | Grid Breaker Trip Q8 | 0 | 45
[13 empty] | 2649 | Grid Breaker Trip F60 | 0 | 45
[13 empty] | 2657 | Write Access Taken: _ | 0 | 45
[13 empty] | 2658 | Write Access Release: _ | 0 | 45
[13 empty] | 2659 | Session Login: _ | 0 | 45
[13 empty] | 2660 | Session Logout: _ | 0 | 45
[13 empty] | 2661 | TransTempExtHigh:Ph_Temp___°C | 0 | 45
[13 empty] | 2667 | Hot gear derate active_,___°C | 0 | 45
[13 empty] | 2668 | AuxTransformer Temp High ___°C | 0 | 45
[13 empty] | 2669 | OfflineFilt High Press __._bar | 0 | 45
[13 empty] | 2670 | OfflineFilt Low Press __._bar | 0 | 45
[13 empty] | 2671 | OfflineFilt Sensors | 0 | 45
[13 empty] | 2672 | OfflineFiltPressTooHigh__._bar | 0 | 45
[13 empty] | 2673 | Overspeed Guard Activated | 0 | 45
[13 empty] | 2674 | UPS Battery Error | 0 | 45
[13 empty] | 2675 | UPS On Battery | 0 | 45
[13 empty] | 2676 | UPS Error | 10 | 9
[13 empty] | 2677 | YawCW Pos Fb | 0 | 45
[13 empty] | 2678 | YawCW Neg Fb | 0 | 45
[13 empty] | 2679 | YawCW Signal Err | 0 | 45
[13 empty] | 2680 | YawCCW Pos Fb | 0 | 45
[13 empty] | 2681 | YawCCW Neg Fb | 0 | 45
[13 empty] | 2682 | YawCCW Signal Err | 0 | 45
[13 empty] | 2683 | Yaw Thermo 1 Fault | 0 | 45
[13 empty] | 2684 | Yaw Thermo 2 Fault | 0 | 45
[13 empty] | 2685 | Yaw Thermo 3 Fault | 0 | 45
[13 empty] | 2686 | Yaw Thermo 4 Fault | 0 | 45
[13 empty] | 2687 | Yaw Thermo 5 Fault | 0 | 45
[13 empty] | 2688 | Yaw Thermo 6 Fault | 0 | 45
[13 empty] | 2689 | Yaw Thermo 7 Fault | 0 | 45
[13 empty] | 2690 | Yaw Thermo 8 Fault | 0 | 45
[13 empty] | 2691 | Yaw Thermo 1 Signal Err | 0 | 45
[13 empty] | 2692 | Yaw Thermo 2 Signal Err | 0 | 45
[13 empty] | 2693 | Yaw Thermo 3 Signal Err | 0 | 45
[13 empty] | 2694 | Yaw Thermo 4 Signal Err | 0 | 45
[13 empty] | 2695 | Yaw Thermo 5 Signal Err | 0 | 45
[13 empty] | 2696 | Yaw Thermo 6 Signal Err | 0 | 45
[13 empty] | 2697 | Yaw Thermo 7 Signal Err | 0 | 45
[13 empty] | 2698 | Yaw Thermo 8 Signal Err | 0 | 45
[13 empty] | 2699 | Yaw Ciruitbreaker Fb Err | 0 | 45
[13 empty] | 2787 | Nacellle Hatch Fb _ | 0 | 45
[13 empty] | 2803 | YawLubr Completed Req:__ | 0 | 45
[13 empty] | 2857 | BypsPressHigh:___°C,___l/min | 0 | 45
[13 empty] | 2858 | BypsPressTooHigh___°C,___l/min | 0 | 45
[13 empty] | 2859 | DiffPressHigh___°C,___l/min | 0 | 45
[13 empty] | 2860 | DiffPressTooHigh___°C,___l/min | 0 | 45
[13 empty] | 2861 | InlDiffPressLow:___°C,___l/min | 0 | 45
[13 empty] | 2862 | PreSensorErr:Bef___After___bar | 0 | 45
[13 empty] | 2863 | ConvWaterCoolPressLow__.__bar | 0 | 45
[13 empty] | 2864 | ConvWaterCoolWatLevelLow_____l | 0 | 45
[13 empty] | 2865 | ConvWatCoolTempSlopeExceeded | 0 | 45
[13 empty] | 2869 | BrakeApplyPressureLow___bar | 0 | 45
[13 empty] | 2870 | BrakeReleasedPressHigh___bar | 0 | 45
[13 empty] | 2871 | BrakeReleasedPressTooHigh__bar | 0 | 45
[13 empty] | 2872 | BrakeApplyValve1CBActivated | 0 | 45
[13 empty] | 2873 | BrakeApplyValve2CBActivated | 0 | 45
[13 empty] | 2874 | BrakeDrainValveCBActivated | 0 | 45
[13 empty] | 2875 | BrakeAccumulatorPressLow___bar | 0 | 45
[13 empty] | 2876 | BrakeAccPressLowManInNac___bar | 0 | 45
[13 empty] | 2877 | BrakeHotLowBrakePressure___bar | 0 | 45
[13 empty] | 2878 | BrakeHotHighBrakePress___bar | 0 | 45
[13 empty] | 2879 | Brake Worn | 0 | 45
[13 empty] | 2887 | PitA Sys: ___bar Aside: ___bar | 0 | 45
[13 empty] | 2888 | PitB Sys: ___bar Aside: ___bar | 0 | 45
[13 empty] | 2889 | PitC Sys: ___bar Aside: ___bar | 0 | 45
[13 empty] | 2890 | VibrShockAct X _.__Y _.__m/s^2 | 0 | 45
[13 empty] | 2891 | HighCyclicPitch | 0 | 45
[13 empty] | 2892 | PB OilDiffHigh Main___ A___bar | 0 | 45
[13 empty] | 2893 | PB OilDiffHigh Main___ B___bar | 0 | 45
[13 empty] | 2894 | PB OilDiffHigh Main___ C___bar | 0 | 45
[13 empty] | 2896 | PitA: PFB max: ___ min:__ | 0 | 45
[13 empty] | 2897 | PitB: PFB max: ___ min:__ | 0 | 45
[13 empty] | 2898 | PitC: PFB max: ___ min:__ | 0 | 45
[13 empty] | 2899 | Pitch A: PFB indi open : ___ | 0 | 45
[13 empty] | 2900 | Pitch B: PFB indi open : ___ | 0 | 45
[13 empty] | 2901 | Pitch C: PFB indi open : ___ | 0 | 45
[13 empty] | 2902 | PitA Not lock C: __.__ W:__.__ | 0 | 45
[13 empty] | 2903 | PitB Not lock C: __.__ W:__.__ | 0 | 45
[13 empty] | 2904 | PitC Not lock C: __.__ W:__.__ | 0 | 45
[13 empty] | 2905 | Pitch A BL unlock WarningN= __ | 0 | 45
[13 empty] | 2906 | Pitch B BL unlock WarningN= __ | 0 | 45
[13 empty] | 2907 | Pitch C BL unlock WarningN= __ | 0 | 45
[13 empty] | 2908 | Pitch A BL unlock alarm N= ___ | 0 | 45
[13 empty] | 2909 | Pitch B BL unlock alarm N= ___ | 0 | 45
[13 empty] | 2910 | Pitch C BL unlock alarm N= ___ | 0 | 45
[13 empty] | 2911 | NegFB = _,:SupplyContHydrMotor | 0 | 45
[13 empty] | 2912 | PosFB = _,:SupplyContHydrMotor | 0 | 45
[13 empty] | 2913 | InvFB = _,:SupplyContHydrMotor | 0 | 45
[13 empty] | 2914 | NegFB = _,:SupplyContYawMotor | 0 | 45
[13 empty] | 2915 | PosFB = _,:SupplyContYawMotor | 0 | 45
[13 empty] | 2916 | InvFB = _,:SupplyContYawMotor | 0 | 45
[13 empty] | 2917 | NegFB = _,:SupplyContOtherMot | 0 | 45
[13 empty] | 2918 | PosFB = _,:SupplyContOtherMot | 0 | 45
[13 empty] | 2919 | InvFB = _,:SupplyContOtherMot | 0 | 45
[13 empty] | 2920 | GearLubrGravityTankFault | 0 | 45
[13 empty] | 2921 | SpareCanBeUsed | 0 | 45
[13 empty] | 2922 | DrySump Lev G:___l M:____l | 0 | 45
[13 empty] | 2923 | WetSump Lev G:___l M:____l | 0 | 45
[13 empty] | 2924 | GearLeak:MainTankVol____.__m^3 | 0 | 45
[13 empty] | 2925 | Gear Leak: Flow __.__ l/min | 0 | 45
[13 empty] | 2926 | Gear Oil Contaminated Drain A | 0 | 45
[13 empty] | 2927 | Gear Oil Contaminated Drain B | 0 | 45
[13 empty] | 2928 | Gear Oil Contaminated Drain C | 0 | 45
[13 empty] | 2929 | GearboxOilLevelHigh M:____l | 0 | 45
[13 empty] | 2930 | Gear Oil Level High M:____l | 0 | 45
[13 empty] | 2931 | GearOilLevelTooLow M:____l | 0 | 45
[13 empty] | 2932 | GearOilLevelTooHigh M:____l | 0 | 45
[13 empty] | 2933 | GearOilTempHigh ___°C | 0 | 45
[13 empty] | 2934 | GearOilInletPressLow _._ bar | 0 | 45
[13 empty] | 2936 | Thermoerror gear oil pump | 0 | 45
[13 empty] | 2939 | Feedback = _,:GearOilHeater | 0 | 45
[13 empty] | 2942 | GearOilSumpWet: MainTank___°C | 0 | 45
[13 empty] | 2943 | GearOilSumpDry: MainTank___°C | 0 | 45
[13 empty] | 2944 | SpareCanBeUsed | 0 | 45
[13 empty] | 2945 | GearOilPressMissing: Derate | 0 | 45
[13 empty] | 2946 | GearOilPressMissing: No Derate | 0 | 45
[13 empty] | 2948 | GenWarmPhaseTmp:Min___Max___°C | 0 | 45
[13 empty] | 2949 | GenLowPhaseTemp:Min___Max__°C | 0 | 45
[13 empty] | 2950 | GenHighPhaseTemp:Min___Max__°C | 0 | 45
[13 empty] | 2951 | GenLowBearTemp:DE__NonDE__°C | 0 | 45
[13 empty] | 2952 | GenHighBearTemp:DE__NonDE__°C | 0 | 45
[13 empty] | 2953 | PowerSupplyLowFreq: Min___ Hz | 0 | 45
[13 empty] | 2954 | PowerSupplyHighFreq: Max___ Hz | 0 | 45
[13 empty] | 2955 | UPS Battery Low | 0 | 45
[13 empty] | 2956 | SupplyError: Min ____V phase_ | 0 | 45
[13 empty] | 2957 | UPS DC1 Battery Error | 0 | 45
[13 empty] | 2958 | UPS DC2 Battery Error | 0 | 45
[13 empty] | 2959 | UPS DC Power Supply Missing | 0 | 45
[13 empty] | 2960 | UPS DC1 Error | 0 | 45
[13 empty] | 2961 | UPS DC2 Error | 0 | 45
[13 empty] | 2962 | GenCold:MinTemp___EnvTemp___°C | 0 | 45
[13 empty] | 2963 | GenColdDeratePowerNotActive | 0 | 45
[13 empty] | 2964 | GenWarm:MaxTemp___EnvTemp___°C | 0 | 45
[13 empty] | 2965 | GenWarmDeratePowerNotActive | 0 | 45
[13 empty] | 2967 | SupplyError: Max ____V phase_ | 0 | 45
[13 empty] | 2968 | Supply Aux Main CB Opened | 0 | 45
[13 empty] | 2969 | Supply CommonCB Nacelle Opened | 0 | 45
[13 empty] | 2970 | PanelPowerSupplyHub24VError | 0 | 45
[13 empty] | 2971 | PanelPowerSupplyNacelle24VErr | 0 | 45
[13 empty] | 2972 | PanelPowerSupplyTower24VError | 0 | 45
[13 empty] | 2973 | YawMotorLowVol:____V, phase_ | 0 | 45
[13 empty] | 2979 | HV TrafoFanState __ | 0 | 45
[13 empty] | 2980 | MainBearLubrErr: NacTemp___°C | 0 | 45
[13 empty] | 2981 | MainBearLubrReservoirLevelLow | 0 | 45
[13 empty] | 2982 | MainBearingLubrCompleted | 0 | 45
[13 empty] | 2983 | MainBearLubrErr: NacTemp___°C | 0 | 45
[13 empty] | 2984 | GearHydrWatPumpPressLow___bar | 0 | 45
[13 empty] | 2985 | GearHydrWatPumpLevelLow___m^3 | 0 | 45
[13 empty] | 2986 | GearHydWaterPumpSignalInvalid | 0 | 45
[13 empty] | 2987 | GearHydWaterPumpThermoError | 0 | 45
[13 empty] | 2988 | GearHydWaterPumpThermoInvalid | 0 | 45
[13 empty] | 2989 | GearHydWaterPumpPositiveFB | 0 | 45
[13 empty] | 2990 | GearHydWaterPumpNegativeFB | 0 | 45
[13 empty] | 2991 | GearHydWaterPumpFBInvalid | 0 | 45
[13 empty] | 2992 | KeySwitchCommRights______ | 0 | 45
[13 empty] | 2993 | HydrHighPressPump1ThermoErr__ | 0 | 45
[13 empty] | 2994 | HydrHighPressPump2ThermoErr__ | 0 | 45
[13 empty] | 2995 | HydrHighPressPumpNotFunctional | 3 | 17
[13 empty] | 2996 | NacelleTemp:___PanelTemp:___°C | 0 | 45
[13 empty] | 2997 | NacelleTemp:___PanelTemp:___°C | 0 | 45
[13 empty] | 2998 | NacelleCtrlPanelFan__Temp___°C | 0 | 45
[13 empty] | 2999 | HubPanelTempHigh:___Hub:___°C | 0 | 45
[13 empty] | 3000 | HubPanelTempLow:___Hub:___°C | 0 | 45
[13 empty] | 3001 | GndPanelTempHigh:___Env:___°C | 0 | 45
[13 empty] | 3002 | GndPanelTempLow:___Env:___°C | 0 | 45
[13 empty] | 3003 | HydrMainPressLow:____bar____°C | 0 | 45
[13 empty] | 3004 | HydrMainPressHigh:____bar___°C | 0 | 45
[13 empty] | 3005 | HydrInitPressMissing___bar__°C | 0 | 45
[13 empty] | 3006 | HydrFiltOilPressDiffHigh___bar | 0 | 45
[13 empty] | 3007 | HydrFiltOilPressDiffTooH___bar | 0 | 45
[13 empty] | 3009 | HydrOilTempHigh___°C | 0 | 45
[13 empty] | 3011 | HydrStartupProcedure___ | 0 | 45
[13 empty] | 3012 | HydrHighPressPump1NegFBError | 0 | 45
[13 empty] | 3013 | HydrHighPressPump1PosFBError | 0 | 45
[13 empty] | 3014 | HydrHighPressPump2NegFBError | 0 | 45
[13 empty] | 3015 | HydrHighPressPump2PosFBError | 0 | 45
[13 empty] | 3016 | HydrHighPressPump__NewState__ | 0 | 45
[13 empty] | 3017 | Load/PowerMode invalid winddir | 0 | 45
[13 empty] | 3018 | Load/PowerMode invalid config. | 0 | 45
[13 empty] | 3019 | Load/PowerMode windsector __ | 0 | 45
[13 empty] | 3020 | GndControllerProcessorBattLow | 0 | 45
[13 empty] | 3021 | HubControllerProcessorBattLow | 0 | 45
[13 empty] | 3022 | NacelleControllerProcBattLow | 0 | 45
[13 empty] | 3023 | ConvControllerProcessorBattLow | 0 | 45
[13 empty] | 3024 | ArcNetReconfigMaxLimit________ | 1 | 28
[13 empty] | 3025 | GndArcNetRec1LightErr___.__dBm | 0 | 45
[13 empty] | 3026 | GndArcNetRec2LightErr___.__dBm | 0 | 45
[13 empty] | 3027 | GndArcNetRec3LightErr___.__dBm | 0 | 45
[13 empty] | 3028 | GndArcNetRec4LightErr___.__dBm | 0 | 45
[13 empty] | 3029 | GndArcNetRec5LightErr___.__dBm | 0 | 45
[13 empty] | 3030 | NacArcNetRec1LightErr___.__dBm | 0 | 45
[13 empty] | 3031 | NacArcNetRec2LightErr___.__dBm | 0 | 45
[13 empty] | 3032 | NacArcNetRec3LightErr___.__dBm | 0 | 45
[13 empty] | 3033 | NacArcNetRec4LightErr___.__dBm | 0 | 45
[13 empty] | 3034 | NacArcNetRec5LightErr___.__dBm | 0 | 45
[13 empty] | 3035 | HubArcNetRec1LightErr___.__dBm | 0 | 45
[13 empty] | 3036 | HubArcNetRec2LightErr___.__dBm | 0 | 45
[13 empty] | 3037 | HubArcNetRec3LightErr___.__dBm | 0 | 45
[13 empty] | 3038 | HubArcNetRec4LightErr___.__dBm | 0 | 45
[13 empty] | 3039 | HubArcNetRec5LightErr___.__dBm | 0 | 45
[13 empty] | 3040 | ConvArcNetRc3LightErr___.__dBm | 0 | 45
[13 empty] | 3041 | ConvArcNetRc4LightErr___.__dBm | 0 | 45
[13 empty] | 3042 | AccTestInitPressMissing____bar | 0 | 45
[13 empty] | 3043 | BrakeAccTestMinTimeErr____sec | 0 | 45
[13 empty] | 3044 | BrakeAccTestMaxTimeErr____sec | 0 | 45
[13 empty] | 3045 | BrakeApplyValve1ErrPress___bar | 0 | 45
[13 empty] | 3046 | BrakeDrainValveFailed | 0 | 45
[13 empty] | 3047 | DrainTestInitialPressMissing | 0 | 45
[13 empty] | 3048 | BrakeApplyValve2ErrPress___bar | 0 | 45
[13 empty] | 3049 | BrakeAccTestNotPerformed | 0 | 45
[13 empty] | 3050 | BrakeAccumulatorTestPerformed | 0 | 45
[13 empty] | 3051 | BrakeApplyValve1TestNotPerform | 0 | 45
[13 empty] | 3052 | BrakeApplyValve1TestPerformed | 0 | 45
[13 empty] | 3053 | BrakeDrainValveTestNotPerform | 0 | 45
[13 empty] | 3054 | BrakeDrainValveTestPerformed | 0 | 45
[13 empty] | 3055 | BrakeApplyValve2TestNotPerform | 0 | 45
[13 empty] | 3056 | BrakeApplyValve2TestPerformed | 0 | 45
[13 empty] | 3057 | FRBPowerReference___kW | 0 | 45
[13 empty] | 3059 | PowerStop1Error | 0 | 45
[13 empty] | 3060 | PowerStop2Error | 0 | 45
[13 empty] | 3061 | PowerStop3Error | 0 | 45
[13 empty] | 3062 | PowerStop4Error | 0 | 45
[13 empty] | 3069 | SafetySystemErr:Nacelle__Hub__ | 0 | 45
[13 empty] | 3070 | EmergStopButtonActivated__ | 0 | 45
[13 empty] | 3071 | HVCBTripError | 0 | 45
[13 empty] | 3072 | HVCBNotReconnected | 0 | 45
[13 empty] | 3073 | TripHVButtonActivated__ | 0 | 45
[13 empty] | 3074 | HVCBTripCircuitError | 0 | 45
[13 empty] | 3075 | ProtectionSystemActivated | 0 | 45
[13 empty] | 3076 | HVCBOpened | 0 | 45
[13 empty] | 3077 | HVCBReconnected | 0 | 45
[13 empty] | 3078 | YawLubrUntwistRequested | 0 | 45
[13 empty] | 3079 | YawLubrUntwistRequired | 0 | 45
[13 empty] | 3080 | ModeSelectorTowerSignalError | 0 | 45
[13 empty] | 3081 | ModeSelectorNacelleSignalError | 0 | 45
[13 empty] | 3082 | ModeSelectorOperationErr__ | 0 | 45
[13 empty] | 3083 | TowerModeSelPos__Tow__Nacelle | 0 | 45
[13 empty] | 3084 | NacelleModeSelPos__Tower__Nac | 0 | 45
[13 empty] | 3085 | ModeSelector__Pos__CommRights | 0 | 45
[13 empty] | 3086 | ManBladeSelectorSignalMismatch | 0 | 45
[13 empty] | 3087 | Hub In Safe Mode Enter | 0 | 45
[13 empty] | 3088 | Hub In Safe Mode Leave | 0 | 45
[13 empty] | 3089 | Hub In SafeMode While Rotating | 0 | 45
[13 empty] | 3091 | StatorFilter Thermo Fault | 0 | 45
[13 empty] | 3092 | StatorFilter Fuse,Contac Fail | 0 | 45
[13 empty] | 3093 | StatorFilterSignal Err | 0 | 45
[13 empty] | 3094 | StatorFilterFuseSig Err | 0 | 45
[13 empty] | 3095 | BrakeAccPressTooHigh___bar | 0 | 45
[13 empty] | 3096 | BrakePressureTooHigh___bar | 0 | 45
[13 empty] | 3097 | BrakeApplied:_Safety_Control | 0 | 45
[13 empty] | 3098 | BrakeReleased:_Safety_Control | 0 | 45
[13 empty] | 3099 | BrakeAppliedInProduction | 0 | 45
[13 empty] | 3100 | CMSGearVibrSignal1High____mm/s | 0 | 45
[13 empty] | 3101 | CMSGearVibrSignal2High____mm/s | 0 | 45
[13 empty] | 3102 | CMSGearVibrSignal3High____mm/s | 0 | 45
[13 empty] | 3103 | CMSGearVibrSignal4High____mm/s | 0 | 45
[13 empty] | 3104 | CMSGearVibrSignal5High____mm/s | 0 | 45
[13 empty] | 3105 | CMSGearVibrSignal6High____mm/s | 0 | 45
[13 empty] | 3106 | CMSGearVibrSignal7High____mm/s | 0 | 45
[13 empty] | 3107 | CMSGearVibr1TooHigh_____mm/s | 0 | 45
[13 empty] | 3108 | CMSGearVibr2TooHigh_____mm/s | 0 | 45
[13 empty] | 3109 | CMSGearVibr3TooHigh_____mm/s | 0 | 45
[13 empty] | 3110 | CMSGearVibr4TooHigh_____mm/s | 0 | 45
[13 empty] | 3111 | CMSGearVibr5TooHigh_____mm/s | 0 | 45
[13 empty] | 3112 | CMSGearVibr6TooHigh_____mm/s | 0 | 45
[13 empty] | 3113 | CMSGearVibr7TooHigh_____mm/s | 0 | 45
[13 empty] | 3114 | CMSGenVibrSignal1High____mm/s | 0 | 45
[13 empty] | 3115 | CMSGenVibrSignal2High____mm/s | 0 | 45
[13 empty] | 3116 | CMSGenerVibr1TooHigh____mm/s | 0 | 45
[13 empty] | 3117 | CMSGenerVibr2TooHigh____mm/s | 0 | 45
[13 empty] | 3118 | CMSMainBearingVibrHigh____mm/s | 0 | 45
[13 empty] | 3119 | CMSMainBearVibrTooHigh____mm/s | 0 | 45
[13 empty] | 3120 | PtchValAErr,VeloctyA___._mm/s | 0 | 45
[13 empty] | 3121 | PtchValBErr,VeloctyB___._mm/s | 0 | 45
[13 empty] | 3122 | PtchValCErr,VeloctyC___._mm/s | 0 | 45
[13 empty] | 3123 | PitchVelocityDiffExceed___mm/s | 0 | 45
[13 empty] | 3124 | EMCPitchValvesTestPerformed | 0 | 45
[13 empty] | 3125 | Pitch Valves Test Failure | 0 | 45
[13 empty] | 3126 | FlushTestErr;EMCPilot___bar | 0 | 45
[13 empty] | 3127 | HydrPress___bar;EMCPilot___bar | 0 | 45
[13 empty] | 3128 | HydrPress___bar;EMCPilot___bar | 0 | 45
[13 empty] | 3129 | DODP Valve Failure | 0 | 45
[13 empty] | 3130 | MSCHWErr, ConvModID __ Par2___ | 0 | 45
[13 empty] | 3131 | MSCHWErrInfo,ModID__, Phase _ | 0 | 45
[13 empty] | 3132 | HighIMSC L__,MaxCurr____A | 0 | 45
[13 empty] | 3134 | GenSpeedOutLimLw/Hi:_, ____rpm | 0 | 45
[13 empty] | 3135 | Sync time out___s,SyncState___ | 0 | 45
[13 empty] | 3136 | ConnTransTimeOut__s,MSCState__ | 0 | 45
[13 empty] | 3137 | LckMSCTimeOut___ms,MSCState_ | 0 | 45
[13 empty] | 3138 | DiscTransPrm___s,MainMSCState_ | 0 | 45
[13 empty] | 3139 | LSCHWErr, ConvModule_,Par2____ | 0 | 45
[13 empty] | 3140 | LSCHWErrInfo, ConvModule_, L_ | 0 | 45
[13 empty] | 3141 | HighILSC,L_,MaxLSCCurr____A | 0 | 45
[13 empty] | 3143 | PreChTimeOut DCLink____V, ___s | 0 | 45
[13 empty] | 3144 | ChargeTrnsTimeout__s,LSC__ | 0 | 45
[13 empty] | 3145 | PreDisTimeout DC:____V,_.__s | 0 | 45
[13 empty] | 3146 | DischTrnsTime_.___s,LSCState__ | 0 | 45
[13 empty] | 3147 | LockLSCTimeOut_.___s,LSCState_ | 0 | 45
[13 empty] | 3148 | DCChopperHWErr, ConvModule__ | 0 | 45
[13 empty] | 3149 | DCChopperHWErrInfo,ConvMod__ | 0 | 45
[13 empty] | 3150 | GridPhaseSeqErr,Par1___ Par2__ | 0 | 45
[13 empty] | 3151 | GridFilterContErr,Par1__Par2__ | 0 | 45
[13 empty] | 3152 | GridFiltFuseErr,___kVar,Val:_ | 0 | 45
[13 empty] | 3153 | GridFiltNotCon,Time___s,Par2__ | 0 | 45
[13 empty] | 3154 | DischargeSupvTimeout___s | 0 | 45
[13 empty] | 3155 | RundownTimeout___s,____RPM | 0 | 45
[13 empty] | 3156 | FrtDetect: Volt___%,Time__.__s | 0 | 45
[13 empty] | 3157 | DisconnPowHi:____kW Lim:__kW | 0 | 45
[13 empty] | 3158 | UnexpContFB:Substate_,EvntNr__ | 0 | 45
[13 empty] | 3159 | VPCIntSWErr:Par1____Par2____ | 0 | 45
[13 empty] | 3160 | ExtHighIMSC,ConvMod_,Par2___ | 0 | 45
[13 empty] | 3161 | ExtMSCInfo:ConvMod_, L___ | 0 | 45
[13 empty] | 3162 | ExtHighILSC,ConvMod_,Par2___ | 0 | 45
[13 empty] | 3163 | ExtLSCInfo:ConvMod_, L___ | 0 | 45
[13 empty] | 3164 | PwrStopActive,Par1____Par2____ | 0 | 45
[13 empty] | 3165 | PSCCHWErr,ConvMod_,ErrCode____ | 0 | 45
[13 empty] | 3166 | PSCCCANErr,ConvMod_,ErrCod____ | 0 | 45
[13 empty] | 3172 | PowerStopHighTemp | 0 | 45
[13 empty] | 3173 | PowerStopOverTemp | 0 | 45
[13 empty] | 3174 | TransformerHighCoreTemp | 0 | 45
[13 empty] | 3175 | HydrOilExtremeHighTemp_____°C | 0 | 45
[13 empty] | 3178 | ModeSelectorInStop:Tow__Nac__ | 0 | 45
[13 empty] | 3179 | LIDARExtremeGustDetec__._m/s^2 | 0 | 45
[13 empty] | 3180 | Nac Temp:___Panel2Temp:___°C | 0 | 45
[13 empty] | 3181 | Nac Temp:___Panel2Temp:___°C | 0 | 45
[13 empty] | 3182 | Nac PanelFan2__Temp___°C | 0 | 45
[13 empty] | 3184 | GrayCodeInvShift:Prev__Act__ | 0 | 45
[13 empty] | 3185 | CamPulsMiss:Time___s,CT______° | 0 | 45
[13 empty] | 3186 | CTStopReached:Code__,CT______° | 0 | 45
[13 empty] | 3187 | Common EMC Valve Fail | 0 | 45
[13 empty] | 3188 | EMC valve err in pitch blockA | 0 | 45
[13 empty] | 3189 | EMC valve err in pitch blockB | 0 | 45
[13 empty] | 3190 | EMC valve err in pitch blockC | 0 | 45
[13 empty] | 3191 | Common accu failed test:____ | 0 | 45
[13 empty] | 3192 | Leakage pitch accum.A:___bar | 0 | 45
[13 empty] | 3193 | Leakage pitch accum.B:___bar | 0 | 45
[13 empty] | 3194 | Leakage pitch accum.C:___bar | 0 | 45
[13 empty] | 3195 | Low flow tank block A:___bar | 0 | 45
[13 empty] | 3196 | Low flow tank block B:___bar | 0 | 45
[13 empty] | 3197 | Low flow tank block C:___bar | 0 | 45
[13 empty] | 3198 | Accu A failed in test:___bar | 0 | 45
[13 empty] | 3199 | Accu B failed in test:___bar | 0 | 45
[13 empty] | 3200 | Accu C failed in test:___bar | 0 | 45
[13 empty] | 3201 | PitchPress Diff Hi.A___,___ | 0 | 45
[13 empty] | 3202 | PitchPress Diff Hi.B___,___ | 0 | 45
[13 empty] | 3203 | PitchPress Diff Hi.C___,___ | 0 | 45
[13 empty] | 3204 | Nacelle position err ___° | 0 | 45
[13 empty] | 3205 | GrayCodeShiftUnexp.Err: ___ | 0 | 45
[13 empty] | 3206 | Nacelle pos ResetUnexp: ___._° | 0 | 45
[13 empty] | 3207 | Nacelle pos reset missing | 0 | 45
[13 empty] | 3208 | CT Est.Twist fault | 0 | 45
[13 empty] | 3209 | YawSignals Invalid | 0 | 45
[13 empty] | 3210 | GrayCodeResetShiftUnexp.____ | 0 | 45
[13 empty] | 3211 | GrayCodeResetShiftMiss.____ | 0 | 45
[13 empty] | 3212 | CableTwistCodeShift:New__Old__ | 0 | 45
[13 empty] | 3213 | NacReset Err___._ Est___._ | 0 | 45
[13 empty] | 3214 | NacPosNoise:Est___._Nac___._ | 0 | 45
[13 empty] | 3215 | NacPosHiFreq:Est___._Nac___._ | 0 | 45
[13 empty] | 3216 | CableTwReset:Err___._Est:___._ | 0 | 45
[13 empty] | 3217 | CableTwRstPa:Err___._Est:___._ | 0 | 45
[13 empty] | 3218 | Low Battery VPC | 0 | 45
[13 empty] | 3219 | GrayCodeShiftMiss ____ | 0 | 45
[13 empty] | 3220 | Yaw Speed Low ___ | 0 | 45
[13 empty] | 3221 | NacPosSigInvalidShift Err:___ | 0 | 45
[13 empty] | 3222 | HighTempMSC.IGBT:Mod__; ____°C | 0 | 45
[13 empty] | 3223 | HighTempLSC.IGBT:Mod__; ____°C | 0 | 45
[13 empty] | 3224 | HighTempDCChop:Mod__; ____°C | 0 | 45
[13 empty] | 3225 | HighTempGridChoke1:Mod__,___°C | 0 | 45
[13 empty] | 3226 | HighTempGridChoke2:Mod__,___°C | 0 | 45
[13 empty] | 3228 | HydHighPressPump1SignalInvalid | 0 | 45
[13 empty] | 3229 | HighPressPump1ThermoInvalid | 0 | 45
[13 empty] | 3230 | HighPressPump1FeedbackInvalid | 0 | 45
[13 empty] | 3231 | HydHighPressPump2SignalInvalid | 0 | 45
[13 empty] | 3232 | HighPressPump2ThermoInvalid | 0 | 45
[13 empty] | 3233 | HighPressPump2FeedbackInvalid | 0 | 45
[13 empty] | 3234 | PitchAccumulatorTestAccFailed | 0 | 45
[13 empty] | 3235 | PitchAccTestSysAccFail,Time__s | 0 | 45
[13 empty] | 3236 | PitchSystDrainValveFail____bar | 0 | 45
[13 empty] | 3237 | PitchManifAAccFailed,Time___s | 0 | 45
[13 empty] | 3238 | PitchManifADrainVlvFail____bar | 0 | 45
[13 empty] | 3239 | PitchManifBAccFailed,Time___s | 0 | 45
[13 empty] | 3240 | PitchManifBDrainVlvFail____bar | 0 | 45
[13 empty] | 3241 | PitchManifCAccFailed,Time___s | 0 | 45
[13 empty] | 3242 | PitchManifCDrainVlvFail____bar | 0 | 45
[13 empty] | 3243 | ConvGenWatCoolPumpSignInvalid | 0 | 45
[13 empty] | 3244 | ConvGenWatCoolPumpThermoFault | 0 | 45
[13 empty] | 3245 | ConvGenWatCoolPumpThermInvalid | 0 | 45
[13 empty] | 3246 | ConvGenWatCoolPumpPosFeedback | 0 | 45
[13 empty] | 3247 | ConvGenWatCoolPumpNegFeedback | 0 | 45
[13 empty] | 3248 | ConvGenWatCoolPumpFeedBInvalid | 0 | 45
[13 empty] | 3249 | ConvGenWatCooHeaterSignInvalid | 0 | 45
[13 empty] | 3250 | ConvGenWatCoolHeatPosFeedback | 0 | 45
[13 empty] | 3251 | ConvGenWatCoolHeatNegFeedback | 0 | 45
[13 empty] | 3252 | ConvGenWatCoolHeatFeedBInvalid | 0 | 45
[13 empty] | 3253 | HighTempPwrStopRes:Mod__,___°C | 0 | 45
[13 empty] | 3254 | Software Err On PSC Controller | 0 | 45
[13 empty] | 3255 | MSCCurrLoadShare:PSC__,Phase__ | 0 | 45
[13 empty] | 3256 | TempSwitchdvdtFilter: Mod__ | 0 | 45
[13 empty] | 3257 | Boot Failure PSC Module __ | 0 | 45
[13 empty] | 3258 | LSCCurrLoadShare:Mod__,Phase__ | 0 | 45
[13 empty] | 3259 | DCLinkFuseBlownOnPSC Module __ | 0 | 45
[13 empty] | 3260 | TmpSwitchDCChopper:Mod_; ___°C | 0 | 45
[13 empty] | 3261 | TmpSwitchGridChoke1:Mod_;___°C | 0 | 45
[13 empty] | 3262 | TmpSwitchGridChoke2:Mod_;___°C | 0 | 45
[13 empty] | 3263 | WeldedContactor: ID __, PSC __ | 0 | 45
[13 empty] | 3264 | BreakerTrip:Subst___,EvntNr___ | 0 | 45
[13 empty] | 3265 | PitchSystemAccTestComplete | 0 | 45
[13 empty] | 3266 | PitchManifoldAccTestComplete | 0 | 45
[13 empty] | 3267 | PilotLine:EMCFlushTestComplete | 0 | 45
[13 empty] | 3268 | PilotValves: EMC Test Complete | 0 | 45
[13 empty] | 3269 | DODPValves:DODPTestComplete | 0 | 45
[13 empty] | 3270 | YawToCableTwistResetNotAvail | 0 | 45
[13 empty] | 3271 | YawToCableTwistResetFailed | 0 | 45
[13 empty] | 3272 | YawUntwistCW: Code__,_______° | 37 | 4
[13 empty] | 3273 | YawUntwistCCW: Code__,_______° | 193 | 1
[13 empty] | 3274 | CTCodeResetShiftUnexp:Old_New_ | 0 | 45
[13 empty] | 3275 | CodeResShiftMiss:Code_,______° | 0 | 45
[13 empty] | 3276 | Yaw Wrong Direction | 0 | 45
[13 empty] | 3277 | Yaw Move Unexpected | 0 | 45
[13 empty] | 3278 | CableTwistCodeShift:New__Old__ | 0 | 45
[13 empty] | 3279 | NacellePosReset:Pos___°,Code_ | 0 | 45
[13 empty] | 3280 | NacPosNoise:EstPos___,Pos___° | 0 | 45
[13 empty] | 3281 | NacPosHighFr:EstPos___,Pos___° | 0 | 45
[13 empty] | 3282 | NacPosShift:EstPos___,Pos___° | 0 | 45
[13 empty] | 3283 | CableTwistReset:Err______,___° | 0 | 45
[13 empty] | 3284 | Cable Twist Reset Passed | 0 | 45
[13 empty] | 3285 | Yaw Control Auto Yawing | 0 | 45
[13 empty] | 3286 | Yaw Control Manual Yawing | 0 | 45
[13 empty] | 3287 | StartManYawCW:CableTwist___._ | 0 | 45
[13 empty] | 3288 | StartManYawCCW:CableTwist___._ | 0 | 45
[13 empty] | 3289 | StopManYaw:CableTwist___._ | 0 | 45
[13 empty] | 3290 | CableUntwistCW:CableTw___._ | 0 | 45
[13 empty] | 3291 | CableUntwistCCW:CableTw___._ | 0 | 45
[13 empty] | 3292 | CableUntwistPerf:CableTw___._ | 0 | 45
[13 empty] | 3293 | StopYawDirection:Allow CW_CCW_ | 0 | 45
[13 empty] | 3294 | YawMovUnxpSt:Slip___._Nac___._ | 0 | 45
[13 empty] | 3295 | YawMovUnxpEn:Slip___._Nac___._ | 0 | 45
[13 empty] | 3296 | Yaw To Nacelle Position Reset | 0 | 45
[13 empty] | 3297 | YawToNacPositResetErr_______° | 0 | 45
[13 empty] | 3298 | Yaw To Cable Twist Reset | 10 | 9
[13 empty] | 3312 | Transf Fan Pos Feedback Error | 0 | 45
[13 empty] | 3313 | Transf Fan Neg Feedback Error | 0 | 45
[13 empty] | 3315 | PitchA step:__._°, SwHist:___ | 0 | 45
[13 empty] | 3316 | PitchB step:__._°, SwHist:___ | 0 | 45
[13 empty] | 3317 | PitchC step:__._°, SwHist:___ | 0 | 45
[13 empty] | 3318 | CollPi step:__._°, SwHist:___ | 0 | 45
[13 empty] | 3323 | OverspeedGuardConfErr:Setting_ | 0 | 45
[13 empty] | 3324 | Max time hydr. pumping:___ sec | 0 | 45
[13 empty] | 3325 | GenerLubrErr:MissLubrTime___s | 0 | 45
[13 empty] | 3326 | GeneratorLubricationCompleted | 0 | 45
[13 empty] | 3327 | SafetySysCommErr:LinkEstabl___ | 0 | 45
[13 empty] | 3328 | SafetySysCheckSumErr:_____ | 0 | 45
[13 empty] | 3329 | DODP Leak Failure | 0 | 45
[13 empty] | 3330 | Brake Warning | 0 | 45
[13 empty] | 3331 | DCLink Contactor Feedback | 0 | 45
[13 empty] | 3332 | ChargeCont Fb timeout act:__ | 0 | 45
[13 empty] | 3333 | GridFiltContFb timeout act:__ | 0 | 45
[13 empty] | 3334 | LSCBreakerFbTimeout PSC__,act_ | 0 | 45
[13 empty] | 3335 | StatVoltSensFbTimeout act:__ | 0 | 45
[13 empty] | 3336 | GenBreakerFbTimeout PSC__,act_ | 0 | 45
[13 empty] | 3337 | DischangeTimeout.____V, ____ms | 0 | 45
[13 empty] | 3338 | PSC Low DCVolt. PSC:__, ____V | 0 | 45
[13 empty] | 3339 | PSC High DCVolt. PSC:__, ____V | 0 | 45
[13 empty] | 3340 | Unexp DCLink Fb. PSC__,act_ | 0 | 45
[13 empty] | 3341 | Unexp GridFilter Fb.ID:__,act_ | 0 | 45
[13 empty] | 3342 | Unexp ChargeContFb. Act:__ | 0 | 45
[13 empty] | 3343 | UnexpLSCBreaker Fb.PSC__,act_ | 0 | 45
[13 empty] | 3344 | UnexpGenBreakerFb.PSC__,act _ | 0 | 45
[13 empty] | 3345 | UnexpStatVoltContFb.act _ | 0 | 45
[13 empty] | 3347 | ManualBladeBearingLubrDone | 0 | 45
[13 empty] | 3348 | PressureControlSuppressed | 0 | 45
[13 empty] | 3349 | GearHeat Pos Fb Err | 0 | 45
[13 empty] | 3350 | GearHeat Neg Fb Err | 0 | 45
[13 empty] | 3351 | GearHeat Signal Err | 0 | 45
[13 empty] | 3352 | GearLubr StartPressLow __._bar | 0 | 45
[13 empty] | 3353 | GearLubr StartPressLow __._bar | 0 | 45
[13 empty] | 3354 | GearLubrPress Derate Active | 0 | 45
[13 empty] | 3355 | GearLubrPress Derate Inactive | 0 | 45
[13 empty] | 3356 | Inv. WindSig->SafeModePitch | 0 | 45
[13 empty] | 3361 | GenPhase Derate time ___ °C | 0 | 45
[13 empty] | 3362 | GenBearTempDerate __°C En:__°C | 0 | 45
[13 empty] | 3363 | GearDerate Time __°C | 0 | 45
[13 empty] | 3364 | GearHS A Temp High Derate __°C | 0 | 45
[13 empty] | 3365 | GearHS B Temp High Derate __°C | 0 | 45
[13 empty] | 3366 | GearHS C Temp High Derate __°C | 0 | 45
[13 empty] | 3368 | BladeLoadGainErr in VTL | 0 | 45
[13 empty] | 3369 | Sensor StatusOrDeadErr in VTL | 0 | 45
[13 empty] | 3370 | Yaw Pulse Missing | 0 | 45
[13 empty] | 3371 | CableTwistSens Fail | 0 | 45
[13 empty] | 3372 | Man Untwist Req | 0 | 45
[13 empty] | 3375 | WS1 Abrupt Dir Change | 0 | 45
[13 empty] | 3376 | WS2 Abrupt Dir Change | 0 | 45
[13 empty] | 3377 | WS1 Abrupt Speed Change | 0 | 45
[13 empty] | 3378 | WS2 Abrupt Speed Change | 0 | 45
[13 empty] | 3379 | WS1 Dir IO Err | 0 | 45
[13 empty] | 3380 | WS2 Dir IO Err | 0 | 45
[13 empty] | 3381 | WS1 Speed IO Err | 0 | 45
[13 empty] | 3382 | WS2 Speed IO Err | 0 | 45
[13 empty] | 3383 | WE Speed IO Err | 0 | 45
[13 empty] | 3384 | WE Speed Disagree ___ | 0 | 45
[13 empty] | 3385 | WS2 Speed Disagree ___ | 0 | 45
[13 empty] | 3386 | WS1 Speed Disagree ___ | 0 | 45
[13 empty] | 3387 | Wind Speed Unresolved | 0 | 45
[13 empty] | 3388 | Wind Dir Unresolved ___ | 0 | 45
[13 empty] | 3411 | WS1 Dir Disagree ___ | 0 | 45
[13 empty] | 3412 | WS2 Dir Disagree ___ | 0 | 45
[13 empty] | 3415 | TestEmergencyPitchValveFailed | 0 | 45
[13 empty] | 3416 | Hydr Startup Testing | 0 | 45
[13 empty] | 3417 | EMC Valve Testing | 0 | 45
[13 empty] | 3419 | Shadow Detected | 0 | 45
[13 empty] | 3420 | Shadow Ctrl Error | 0 | 45
[13 empty] | 3421 | SWDS derate: Wind __, Dir _ | 0 | 45
[13 empty] | 3422 | SWDS OFF Wind __ m/s Dir ___d | 0 | 45
[13 empty] | 3423 | SWDS Low Wind:__._m/s dir:___ | 0 | 45
[13 empty] | 3424 | SWDS High Wind:__._m/s dir:___ | 0 | 45
[13 empty] | 3425 | SwGear Conf Error | 0 | 45
[13 empty] | 3426 | SwGear Insul Gas Press | 0 | 45
[13 empty] | 3427 | SwGear WaterSys1 | 0 | 45
[13 empty] | 3428 | SwGear WaterSys2 | 0 | 45
[13 empty] | 3429 | SwGear ShortCiruit Fault | 0 | 45
[13 empty] | 3430 | SwGear OverCurr Fault | 0 | 45
[13 empty] | 3431 | SwGear Earth Fault | 0 | 45
[13 empty] | 3432 | SwGear BreakerFailProtect | 0 | 45
[13 empty] | 3433 | SwGear Suprv Signal | 0 | 45
[13 empty] | 3434 | NRMS Deactivated,dir:__ | 0 | 45
[13 empty] | 3435 | Ext.SupplyVoltLow V:___ Ph_ | 0 | 45
[13 empty] | 3436 | Ext.SupplyVoltHi V:___ Ph_ | 0 | 45
[13 empty] | 3437 | Ext.SupplyFreqLow __Hz | 0 | 45
[13 empty] | 3438 | Ext.SupplyFreqHi __Hz | 0 | 45
[13 empty] | 3439 | Supply MainMotor Err | 0 | 45
[13 empty] | 3440 | Supply Coil Volt Err | 0 | 45
[13 empty] | 3441 | Supply YawMotor Err | 0 | 45
[13 empty] | 3442 | Supply Main Hydr Err | 0 | 45
[13 empty] | 3443 | Supply Aux Main CB Closed | 0 | 45
[13 empty] | 3444 | Supply Yaw Voltage Ok | 0 | 45
[13 empty] | 3445 | Supply Yaw Voltage Low | 0 | 45
[13 empty] | 3446 | Supply OtherMotor Err | 0 | 45
[13 empty] | 3450 | HighVoltageRoom SPDFuseL1Blown | 0 | 45
[13 empty] | 3451 | HighVoltageRoom SPDFuseL2Blown | 0 | 45
[13 empty] | 3452 | HighVoltageRoom SPDFuseL3Blown | 0 | 45
[13 empty] | 3453 | PowerBackupSupplyActive__ | 0 | 45
[13 empty] | 3455 | DeIce Heater Group Fault | 0 | 45
[13 empty] | 3456 | DeIce Relay Contact Err | 0 | 45
[13 empty] | 3457 | DeIce Bl.Outside Shed Angles | 0 | 45
[13 empty] | 3458 | DeIce Safety Stop | 0 | 45
[13 empty] | 3459 | Gear Oil Pump Fault | 0 | 45
[13 empty] | 3460 | ConvPanel Humidity Err | 0 | 45
[13 empty] | 3461 | LineSideBreakerOpenFail Mod:__ | 0 | 45
[13 empty] | 3462 | GenSideBreakerOpenFail Mod:__ | 0 | 45
[13 empty] | 3463 | ChargeContactorOpenFailed | 0 | 45
[13 empty] | 3464 | StatVoltSensContOpenFailed | 0 | 45
[13 empty] | 3465 | GridFiltContOpenFail.Filter__ | 0 | 45
[13 empty] | 3466 | LineSideBreakerTripped. Mod:__ | 0 | 45
[13 empty] | 3467 | GenSideBreakerTripped. Mod:__ | 0 | 45
[13 empty] | 3468 | DCChopperResistorLoad. ___°C | 0 | 45
[13 empty] | 3469 | LineSideBreakResetErr Module__ | 0 | 45
[13 empty] | 3470 | GenSideBreakResetErr Module__ | 0 | 45
[13 empty] | 3471 | DCLinkContOpenFailed Module__ | 0 | 45
[13 empty] | 3472 | SafetySystem Reset Required | 0 | 45
[13 empty] | 3473 | SafetySys Not Ready For Reset | 0 | 45
[13 empty] | 3475 | SafetySys Converter Stopped | 0 | 45
[13 empty] | 3476 | GearHSBearA Diff A___°C S___°C | 0 | 45
[13 empty] | 3477 | GearHSBearB Diff B___°C S___°C | 0 | 45
[13 empty] | 3478 | GearHSBearC Diff C___°C S___°C | 0 | 45
[13 empty] | 3479 | GearIMBearA Diff A___°C S___°C | 0 | 45
[13 empty] | 3480 | GearIMBearB Diff B___°C S___°C | 0 | 45
[13 empty] | 3481 | GearIMBearC Diff C___°C S___°C | 0 | 45
[13 empty] | 3482 | GearOilDerate Time __°C | 0 | 45
[13 empty] | 3483 | GearOilTempLow ___°C | 2 | 20
[13 empty] | 3484 | GearOilTempHigh ___°C | 0 | 45
[13 empty] | 3485 | GearInletTempLow ___°C | 0 | 45
[13 empty] | 3486 | GearInletTempHigh ___°C | 0 | 45
[13 empty] | 3487 | Gear HSBearA Temp:___°C | 2 | 20
[13 empty] | 3488 | Gear HSBearB Temp:___°C | 0 | 45
[13 empty] | 3489 | Gear HSBearC Temp:___°C | 0 | 45
[13 empty] | 3490 | Gear HSBearA Derate:___°C | 0 | 45
[13 empty] | 3491 | Gear HSBearB Derate:___°C | 0 | 45
[13 empty] | 3492 | Gear HSBearC Derate:___°C | 0 | 45
[13 empty] | 3493 | Gear IMBearA Temp:___°C | 0 | 45
[13 empty] | 3494 | Gear IMBearB Temp:___°C | 0 | 45
[13 empty] | 3495 | Gear IMBearC Temp:___°C | 0 | 45
[13 empty] | 3496 | Gear IMBearA Derate:___°C | 0 | 45
[13 empty] | 3497 | Gear IMBearB Derate:___°C | 0 | 45
[13 empty] | 3498 | Gear IMBearC Derate:___°C | 0 | 45
[13 empty] | 3501 | SafetySystem pending | 0 | 45
[13 empty] | 3502 | SafetySystem error | 0 | 45
[13 empty] | 3510 | NacelleHeater Pos Fb Err | 0 | 45
[13 empty] | 3511 | NacelleHeater Neg Fb Err | 0 | 45
[13 empty] | 3512 | NacelleHeater Signal Err | 0 | 45
[13 empty] | 3513 | Min generator RPM: ____._ | 0 | 45
[13 empty] | 3514 | Pitch Calib Not Complete | 0 | 45
[13 empty] | 3515 | Fire Evolution | 0 | 45
[13 empty] | 3516 | FireProtection Service Done | 0 | 45
[13 empty] | 3517 | FireProtection Inspection Done | 0 | 45
[13 empty] | 3518 | FireProtection Enter Service | 0 | 45
[13 empty] | 3519 | FireProtection Leave Service | 0 | 45
[13 empty] | 3520 | FireProtection System Error | 0 | 45
[13 empty] | 3521 | FireProtection Config Error | 0 | 45
[13 empty] | 3522 | FireProtection LockForInsp _ | 0 | 45
[13 empty] | 3523 | Fire Detected Node_ | 0 | 45
[13 empty] | 3524 | Fire Prot Gas Low Amb:__ | 0 | 45
[13 empty] | 3525 | Fire Prot Sensor Err | 0 | 45
[13 empty] | 3526 | Fire Prot Sensor Soiled | 0 | 45
[13 empty] | 3527 | PSCCTempExc. Mod:_ Temp:__._°C | 0 | 45
[13 empty] | 3537 | PitchAngleAOffset:__._° | 0 | 45
[13 empty] | 3538 | PitchAngleBOffset:__._° | 0 | 45
[13 empty] | 3539 | PitchAngleCOffset:__._° | 0 | 45
[13 empty] | 3540 | Drain Time___s | 0 | 45
[13 empty] | 3541 | Drain Time___s | 0 | 45
[13 empty] | 3542 | Fail Reason:___ | 0 | 45
[13 empty] | 3543 | Test Pitch Axis:___ | 0 | 45
[13 empty] | 3544 | Fail Reason:___ | 0 | 45
[13 empty] | 3545 | GearInl Be__._bar Af__._bar | 0 | 45
[13 empty] | 3546 | GearInlHi Be__._bar Af__._bar | 0 | 45
[13 empty] | 3547 | GearInlLo Be__._bar Af__._bar | 0 | 45
[13 empty] | 3548 | GearInline Sensor Fail | 0 | 45
[13 empty] | 3549 | GearBeforeInlinePres SensFail | 0 | 45
[13 empty] | 3550 | GearAfterInlinePres SensFail | 0 | 45
[13 empty] | 3551 | GearOilInletPressLow _._ bar | 0 | 45
[13 empty] | 3552 | GearOilLevelLow | 0 | 45
[13 empty] | 3555 | GearOil Heater Postive Fb | 0 | 45
[13 empty] | 3556 | GearOil Heater Negative Fb | 0 | 45
[13 empty] | 3557 | GearOil Heater Sig Err | 0 | 45
[13 empty] | 3558 | GearOil Pump Sig Err | 0 | 45
[13 empty] | 3559 | GearLubr Pump Sig Err | 0 | 45
[13 empty] | 3562 | Overspeed Guard Error | 0 | 45
[13 empty] | 3563 | CableUntwistAbort:CableTw___._ | 0 | 45
[13 empty] | 3564 | CableCalibrAbort:CableTw___._ | 0 | 45
[13 empty] | 3565 | Extended Yaw Active | 0 | 45
[13 empty] | 3566 | FireProtection In Maintenence | 0 | 45
[13 empty] | 3567 | FireProt Prod Not Allowed | 0 | 45
[13 empty] | 3568 | FireProt Commis Err | 0 | 45
[13 empty] | 3569 | BladeAPeakLoad: ___.__ kNm | 0 | 45
[13 empty] | 3570 | BladeBPeakLoad: ___.__ kNm | 0 | 45
[13 empty] | 3571 | BladeCPeakLoad: ___.__ kNm | 0 | 45
[13 empty] | 3572 | MBrngTiltPeakLoad: ___.__ kNm | 0 | 45
[13 empty] | 3573 | MBrngYawPeakLoad: ___.__ kNm | 0 | 45
[13 empty] | 3574 | BlAEdgeVibration: ___.__ kNm | 0 | 45
[13 empty] | 3575 | BlBEdgeVibration: ___.__ kNm | 0 | 45
[13 empty] | 3576 | BlCEdgeVibration: ___.__ kNm | 0 | 45
[13 empty] | 3577 | Yaw Motors Trip Power | 0 | 45
[13 empty] | 3578 | High NacTilt: __._deg | 0 | 45
[13 empty] | 3579 | High NacRoll: __._deg | 0 | 45
[13 empty] | 3580 | Low PlatStat: _ | 0 | 45
[13 empty] | 3581 | HubBallValveOpen | 0 | 45
[13 empty] | 3582 | ArcLightDetected __ | 0 | 45
[13 empty] | 3583 | ArcLightDetectorError __ | 0 | 45
[13 empty] | 3584 | Nacellle Fan Hatches Bad Fb | 0 | 45
[13 empty] | 3585 | Blade Load Dev Too High | 0 | 45
[13 empty] | 3586 | Blade Load Signal Fluctuation | 0 | 45
[13 empty] | 3587 | Blade Load Out Of Range | 0 | 45
[13 empty] | 3588 | Blade Load Common Strain High | 0 | 45
[13 empty] | 3589 | Blade Load Dev Too High | 0 | 45
[13 empty] | 3590 | Blade Load Dev Upper Blade | 0 | 45
[13 empty] | 3591 | Blade Load Signal Fluctuation | 0 | 45
[13 empty] | 3592 | Blade Load Out Of Range | 0 | 45
[13 empty] | 3593 | Blade Load Common Strain High | 0 | 45
[13 empty] | 3595 | FireProtectnDiscoveryBusFail | 0 | 45
[13 empty] | 3596 | FireProtection Gas Valve Error | 0 | 45
[13 empty] | 3599 | SWDS Conf Invalid | 0 | 45
[13 empty] | 3600 | Tilt Roll Signal Fault | 0 | 45
[13 empty] | 3601 | OutOfMemory | 0 | 45
[13 empty] | 3604 | HubBallValveError | 0 | 45
[13 empty] | 3605 | LowWind,TimePro_____s __._m/s | 0 | 45
[13 empty] | 3606 | Brake Worn | 0 | 45
[13 empty] | 3608 | PS Power Restriction Activated | 0 | 45
[13 empty] | 3609 | Power Restriction De Activated | 0 | 45
[13 empty] | 3610 | Power Save Activated | 0 | 45
[13 empty] | 3611 | Power Save DeActivated | 0 | 45
[13 empty] | 3612 | PowSuppOp:________ RiskFa:___ | 0 | 45
[13 empty] | 3613 | PSRiskFa:________ NeedPow:___ | 0 | 45
[13 empty] | 3614 | PowerGrantedStatus:_ | 0 | 45
[13 empty] | 3615 | PowSupp Yaw motor Cont Opened | 0 | 45
[13 empty] | 3616 | PowSupp Yaw Main Cont Opened | 0 | 45
[13 empty] | 3617 | PowSupp Pow Back Up Mode:_ | 0 | 45
[13 empty] | 3618 | Power Supply Contactor Error | 0 | 45
[13 empty] | 3619 | TNF Freq:_.___Hz Zero Cross:__ | 0 | 45
[13 empty] | 3620 | TNF failed _.___ Hz Error:_ | 0 | 45
[13 empty] | 3621 | Converter Disconnected In Prod | 0 | 45
[13 empty] | 3622 | CutIn Grid Voltage ___._V | 0 | 45
[13 empty] | 3623 | CutIn Grid Frequency __.___Hz | 0 | 45
[13 empty] | 3624 | Tower nat freq test not done | 0 | 45
[13 empty] | 3625 | Tow Freq _.___Hz OutsideBounds | 0 | 45
[13 empty] | 3626 | Yaw Motors Contactor Opened | 0 | 45
[13 empty] | 3627 | Main Supply Contactor Opened | 0 | 45
[13 empty] | 3628 | Yaw CW Signal Invalid | 0 | 45
[13 empty] | 3629 | Yaw CCW Signal Invalid | 0 | 45
[13 empty] | 3630 | PrevCabTwCode:_ CabTwCode:_ | 0 | 45
[13 empty] | 3631 | Yaw To Reset Too Frequent | 0 | 45
[13 empty] | 3632 | Yaw To Nac Pos Reset Not Allwd | 0 | 45
[13 empty] | 3633 | Yaw System Stopped | 0 | 45
[13 empty] | 3634 | Automatic Test Activated: ___ | 0 | 45
[13 empty] | 3635 | SafetySys Closed Timeout | 0 | 45
[13 empty] | 3636 | Power Supply Trip Request | 0 | 45
[13 empty] | 3637 | TYC 1P Fault Detected | 0 | 45
[13 empty] | 3638 | TYC 2P Fault Detected | 0 | 45
[13 empty] | 3639 | TYC Gain Hysteresis Error | 0 | 45
[13 empty] | 3640 | PBOilDiffHiEMC:___ EMC ___bar | 0 | 45
[13 empty] | 3641 | Warning Limit Reached | 0 | 45
[13 empty] | 3642 | Blade Loads New Calib Data | 0 | 45
[13 empty] | 3643 | Blade Loads Calib Failed | 0 | 45
[13 empty] | 3644 | Calib Values | 0 | 45
[13 empty] | 3645 | Blade Loads Calib Ended | 0 | 45
[13 empty] | 3646 | Blade Loads Calib Started | 0 | 45
[13 empty] | 3647 | BrakePressRebuild Fail:Test _ | 0 | 45
[13 empty] | 3648 | Brake SupplyValve Leak:___bar | 0 | 45
[13 empty] | 3649 | Rundown Stop Timeout | 0 | 45
[13 empty] | 3650 | Azim Ang Invalid Speed:___ RPM | 0 | 45
[13 empty] | 3651 | PowSavMode:___ PowResAct:__ | 0 | 45
[13 empty] | 3652 | CabTwstInconstnt:Code_,______° | 0 | 45
[13 empty] | 3653 | LDO Power Speed Derate | 0 | 45
[13 empty] | 3654 | PSCC module lost, module id __ | 0 | 45
[13 empty] | 3655 | Derate HiTemp.GearBear_:___°C | 0 | 45
[13 empty] | 3656 | Conv Charge Failed | 0 | 45
[13 empty] | 3657 | Conv Charge Command Failed | 0 | 45
[13 empty] | 3658 | Hub BallValve A Open | 0 | 45
[13 empty] | 3659 | Hub BallValve B Open | 0 | 45
[13 empty] | 3660 | Hub BallValve C Open | 0 | 45
[13 empty] | 3661 | GenBreakerOpen,US12___UL12___ | 0 | 45
[13 empty] | 3662 | TSDManEmergency:____RPM,____kW | 0 | 45
[13 empty] | 3663 | TSDManStopFast:____RPM,____kW | 0 | 45
[13 empty] | 3664 | TSDManStopSlow:____RPM,____kW | 0 | 45
[13 empty] | 3665 | TSDManPauseFast:____RPM,____kW | 0 | 45
[13 empty] | 3666 | TSDManPauseSlow:____RPM,____kW | 0 | 45
[13 empty] | 3667 | VPC Err Causing Rundown Stop | 0 | 45
[13 empty] | 3668 | Reactive pow. derated by:_.__ | 0 | 45
[13 empty] | 3669 | Grid resonance filter temp Sw | 0 | 45
[13 empty] | 3670 | Grid curr harmonics exceed L1 | 0 | 45
[13 empty] | 3671 | Grid curr harmonics exceed L2 | 0 | 45
[13 empty] | 3672 | Grid curr harmonics exceed L3 | 0 | 45
[13 empty] | 3673 | Gear Oil Pump Reset | 0 | 45
[13 empty] | 3674 | PilotPressLow:____bar____bar | 0 | 45
[13 empty] | 3675 | ConvArcNetRc1LightErr___.__dBm | 0 | 45
[13 empty] | 3676 | ConvArcNetRc2LightErr___.__dBm | 0 | 45
[13 empty] | 3677 | ConvArcNetRc5LightErr___.__dBm | 0 | 45
[13 empty] | 3678 | Missing Grid Choke Fan feedb. | 0 | 45
[13 empty] | 3679 | Yaw Lubrication Pump2 Failed | 0 | 45
[13 empty] | 3680 | YawLubr Pump2 Completed | 0 | 45
[13 empty] | 3681 | YawLubr Untwist Pump2 Request | 0 | 45
[13 empty] | 3682 | YawLubr Untwist Pump2 Required | 0 | 45
[13 empty] | 3683 | Generator Speed Step Detected | 0 | 45
[13 empty] | 3684 | Grid Voltage Low | 0 | 45
[13 empty] | 3685 | GenPhase Derate time ___ °C | 0 | 45
[13 empty] | 3686 | GenNDETempDerate __°C En:__°C | 0 | 45
[13 empty] | 3687 | GenDETempDerate __°C En:__°C | 0 | 45
[13 empty] | 3688 | BrakeActivationTestFailed | 0 | 45
[13 empty] | 3690 | High Chopper IGBT Temp ___°C | 0 | 45
[13 empty] | 3691 | High Chopper Wire Temp ___°C | 0 | 45
[13 empty] | 3692 | HVCBMotorError | 0 | 45
[13 empty] | 3693 | Grid Failure Detected | 0 | 45
[13 empty] | 3694 | Startup After Grid Failure | 0 | 45
[13 empty] | 3695 | UDC____ Low to close LSBreak | 0 | 45
[13 empty] | 3696 | NRMS Auto cycle new setting: _ | 0 | 45
[13 empty] | 3699 | Pitch Pos A ___° ;Ref ___° | 0 | 45
[13 empty] | 3700 | Pitch Pos B ___° ;Ref ___° | 0 | 45
[13 empty] | 3701 | Pitch Pos C ___° ;Ref ___° | 0 | 45
[13 empty] | 3702 | Blade Load Not Calibrated | 0 | 45
[13 empty] | 3703 | GearPmpTrafoContCloseInvalid | 0 | 45
[13 empty] | 3704 | GearPmpTrafoContThermoFault | 0 | 45
[13 empty] | 3705 | GearPmpTrafoContThermoInvalid | 0 | 45
[13 empty] | 3706 | GearPmpTrafoContPosFBFault | 0 | 45
[13 empty] | 3707 | GearPmpTrafoContNegFBFault | 0 | 45
[13 empty] | 3708 | GearPmpTrafoContFBInvalid | 0 | 45
[13 empty] | 3709 | EMC Valves Unexpected Open | 0 | 45
[13 empty] | 3710 | RawTemp___°C,ActiveFaults___ | 0 | 45
[13 empty] | 3711 | Temp___°C,TDPDPowRef___% | 0 | 45
[13 empty] | 3712 | RawTemp___°C,ActiveFaults___ | 0 | 45
[13 empty] | 3713 | RawPh1Temp___°C,ActivFault___ | 0 | 45
[13 empty] | 3714 | RawPh2Temp___°C,ActivFault___ | 0 | 45
[13 empty] | 3715 | RawPh3Temp___°C,ActivFault___ | 0 | 45
[13 empty] | 3716 | GenMaxPhTmp___°C,TDPD Ref___% | 0 | 45
[13 empty] | 3717 | RawEnvTemp___°C,ActivFault___ | 0 | 45
[13 empty] | 3718 | TowAcc X, Extreme:__.__ m/s^2 | 0 | 45
[13 empty] | 3719 | TowAcc Y, Extreme:__.__ m/s^2 | 0 | 45
[13 empty] | 3720 | Tow. Damp. Estimate OK: _.____ | 0 | 45
[13 empty] | 3721 | Tower Damping estimate failed | 0 | 45
[13 empty] | 3722 | TimeSpentInRunningUp _____sec | 0 | 45
[13 empty] | 3723 | NewGenConnectionStatus___ | 0 | 45
[13 empty] | 3724 | TimeSpentInProductionSD____ | 0 | 45
[13 empty] | 3725 | FireProtection Pollution | 0 | 45
[13 empty] | 3726 | Conv Panel Temp Low:___°C | 0 | 45
[13 empty] | 3727 | Conv Panel Temp High:___°C | 0 | 45
[13 empty] | 3728 | Conv Panel Supply Volt | 0 | 45
[13 empty] | 3729 | Delay Start After Err:____ | 0 | 45
[13 empty] | 3730 | AirInlet hatch state: _, ___°C | 0 | 45
[13 empty] | 3731 | NacAirInletHatches Pos Fb Err | 0 | 45
[13 empty] | 3732 | NacAirInletHatches Neg Fb Err | 0 | 45
[13 empty] | 3733 | Grid QU Protection | 0 | 45
[13 empty] | 3734 | LowWindDiscHighPow____kW__m/s | 0 | 45
[13 empty] | 3735 | Blade Load Signal Frozen | 0 | 45
[13 empty] | 3739 | HVCBDisconnectError | 0 | 45
[13 empty] | 3740 | HVCBNotHealthy | 0 | 45
[13 empty] | 3741 | HVCBError | 0 | 45
[13 empty] | 3742 | TripHVButtonActivated__ | 0 | 45
[13 empty] | 3746 | GenLowPh Temp:Min___Max___°C | 0 | 45
[13 empty] | 3747 | GenHighPh Temp:Min___Max___°C | 0 | 45
[13 empty] | 3748 | GenLowBearTemp:DE___NDE___°C | 0 | 45
[13 empty] | 3749 | GenHighBearTemp:DE___NDE___°C | 0 | 45
[13 empty] | 3750 | GenStatorPhaseSensorFailed | 0 | 45
[13 empty] | 3751 | GenGroundBrushWorn | 0 | 45
[13 empty] | 3752 | Yaw motors demand CW_ CCW_ | 0 | 45
[13 empty] | 3753 | Yaw motor error | 0 | 45
[13 empty] | 3754 | Yaw system error | 0 | 45
[13 empty] | 3755 | BLCalibFailedGainRatioInvalid | 0 | 45
[13 empty] | 3756 | BLCalibFailGainInval:___blade | 0 | 45
[13 empty] | 3757 | BLCalibFailOffsInval:___blade | 0 | 45
[13 empty] | 3758 | BLSensorsCalibActivated | 0 | 45
[13 empty] | 3759 | BLCalibAbortedWindSpdExceed | 0 | 45
[13 empty] | 3760 | BLCalibAbortedEnviroTempExceed | 0 | 45
[13 empty] | 3761 | BLCalibAbortNoSensorASignal | 0 | 45
[13 empty] | 3762 | High temp. in Grid Panel: __ | 0 | 45
[13 empty] | 3763 | H temp in Harm Filt Panel: __ | 0 | 45
[13 empty] | 3764 | HydrBuildPressMiss___bar__°C | 0 | 45
[13 empty] | 3765 | HydrOffFilterPressDropHigh | 0 | 45
[13 empty] | 3766 | HydrOffFilterPressDropTooHigh | 0 | 45
[13 empty] | 3767 | HydraulicOilLevelLow | 0 | 45
[13 empty] | 3768 | HydraulicOilLevelTooLow | 0 | 45
[13 empty] | 3769 | HydrOilTempHigh___°C | 0 | 45
[13 empty] | 3770 | HydrOilTempLow___°C | 0 | 45
[13 empty] | 3771 | HydrSysPressHigh:____bar____°C | 0 | 45
[13 empty] | 3772 | HydrSysPressLow:____bar____°C | 0 | 45
[13 empty] | 3773 | HydrPumpsNotFunctional | 0 | 45
[13 empty] | 3774 | HydrPump1NegFBError | 0 | 45
[13 empty] | 3775 | HydrPump2NegFBError | 0 | 45
[13 empty] | 3776 | HydrPump3NegFBError | 0 | 45
[13 empty] | 3777 | HydrPump1PosFBError | 0 | 45
[13 empty] | 3778 | HydrPump2PosFBError | 0 | 45
[13 empty] | 3779 | HydrPump3PosFBError | 0 | 45
[13 empty] | 3780 | HydrPump1ThermoFault | 0 | 45
[13 empty] | 3781 | HydrPump2ThermoFault | 0 | 45
[13 empty] | 3782 | HydrPump3ThermoFault | 0 | 45
[13 empty] | 3783 | HydrPump1SignalInvalid | 0 | 45
[13 empty] | 3784 | HydrPump2SignalInvalid | 0 | 45
[13 empty] | 3785 | HydrPump3SignalInvalid | 0 | 45
[13 empty] | 3786 | HydrPump1FeedbackInvalid | 0 | 45
[13 empty] | 3787 | HydrPump2FeedbackInvalid | 0 | 45
[13 empty] | 3788 | HydrPump3FeedbackInvalid | 0 | 45
[13 empty] | 3789 | HydrPump1ThermoInvalid | 0 | 45
[13 empty] | 3790 | HydrPump2ThermoInvalid | 0 | 45
[13 empty] | 3791 | HydrPump3ThermoInvalid | 0 | 45
[13 empty] | 3792 | PitchBlockPilotPressLow____bar | 0 | 45
[13 empty] | 3793 | PitchBlockAPressDiffHigh___bar | 0 | 45
[13 empty] | 3794 | PitchBlockBPressDiffHigh___bar | 0 | 45
[13 empty] | 3795 | PitchBlockCPressDiffHigh___bar | 0 | 45
[13 empty] | 3796 | HubSafetySystem EncoderA,EC:_ | 0 | 45
[13 empty] | 3797 | HubSafetySystem EncoderB,EC:_ | 0 | 45
[13 empty] | 3798 | HubSafetySystem EncoderC,EC:_ | 0 | 45
[13 empty] | 3799 | HubSafetySystem Speed Err.:_ | 0 | 45
[13 empty] | 3800 | HubSafety FastPitchValveA Err. | 0 | 45
[13 empty] | 3801 | HubSafety FastPitchValveB Err. | 0 | 45
[13 empty] | 3802 | HubSafety FastPitchValveC Err. | 0 | 45
[13 empty] | 3803 | HubSafety PilotValve1 Err. | 0 | 45
[13 empty] | 3804 | HubSafety PilotValve2 Err. | 0 | 45
[13 empty] | 3805 | HubSafetySystem DC Supply Err. | 4 | 16
[13 empty] | 3806 | HubSafetySystem Batt.Charg.Err | 23 | 7
[13 empty] | 3807 | HubSafetySystem Batt.Level Err | 2 | 20
[13 empty] | 3808 | HubSafetySystem Logic state:__ | 0 | 45
[13 empty] | 3809 | CyclicPitchLevel:__ | 0 | 45
[13 empty] | 3810 | RawTemp:___°C,ActFaults:____ | 0 | 45
[13 empty] | 3811 | Temp:___°C,PowRef:__% | 0 | 45
[13 empty] | 3812 | Temp:___°C,PowRef:__% | 0 | 45
[13 empty] | 3813 | RawPh1Tmp:___°C,ActFaults:____ | 0 | 45
[13 empty] | 3814 | RawPh2Tmp:___°C,ActFaults:____ | 0 | 45
[13 empty] | 3815 | RawPh3Tmp:___°C,ActFaults:____ | 0 | 45
[13 empty] | 3816 | RawPh1Tmp:___°C,ActFaults:____ | 0 | 45
[13 empty] | 3817 | RawPh2Tmp:___°C,ActFaults:____ | 0 | 45
[13 empty] | 3818 | RawPh3Tmp:___°C,ActFaults:____ | 0 | 45
[13 empty] | 3819 | GenMaxPhTemp:___°C,PowRef:__% | 0 | 45
[13 empty] | 3820 | RawEnvTmp:___°C,ActFaults:____ | 0 | 45
[13 empty] | 3821 | RawTemp:___°C,ActFaults:____ | 0 | 45
[13 empty] | 3822 | RawTemp:___°C,ActFaults:____ | 0 | 45
[13 empty] | 3823 | BLSigFrozen:__,Speed:___RPM | 0 | 45
[13 empty] | 3824 | CableTwistProtectionStop:___° | 0 | 45
[13 empty] | 3825 | YawSensorOutOfRange:___°,___° | 0 | 45
[13 empty] | 3828 | YawSensorCalibrationPerformed | 0 | 45
[13 empty] | 3833 | Gbx A1 NRE bearing hot ___ºC | 0 | 45
[13 empty] | 3834 | Gbx A2 RE bearing hot ___ºC | 0 | 45
[13 empty] | 3835 | Gbx A2 NRE bearing hot ___ºC | 0 | 45
[13 empty] | 3836 | Gbx A1 RE carr. bearing ___ºC | 0 | 45
[13 empty] | 3837 | Gbx A2B NRE carr.bearing ___ºC | 0 | 45
[13 empty] | 3838 | Gbx A2B RE carr. bearing ___ºC | 0 | 45
[13 empty] | 3839 | Gbx B NRE carr. bearing ___ºC | 0 | 45
[13 empty] | 3840 | Gbx A1 low press___bar | 0 | 45
[13 empty] | 3841 | ExtHighPwrAct:___kW,Ref:___kW | 0 | 45
[13 empty] | 3842 | PitA:PFBOpen:___Bar,___s | 0 | 45
[13 empty] | 3843 | PitB:PFBOpen:___Bar,___s | 0 | 45
[13 empty] | 3844 | PitC:PFBOpen:___Bar,___s | 0 | 45
[13 empty] | 3845 | PitA:PBLOpen:___Bar,___s | 0 | 45
[13 empty] | 3846 | PitB:PBLOpen:___Bar,___s | 0 | 45
[13 empty] | 3847 | PitC:PBLOpen:___Bar,___s | 0 | 45
[13 empty] | 3848 | PitAPFBsensorunavailable | 0 | 45
[13 empty] | 3849 | PitBPFBsensorunavailable | 0 | 45
[13 empty] | 3850 | PitCPFBsensorunavailable | 0 | 45
[13 empty] | 3851 | PitchValAErr,FastVel.A____mm/s | 0 | 45
[13 empty] | 3852 | PitchValAErr,FastVel.B____mm/s | 0 | 45
[13 empty] | 3853 | PitchValAErr,FastVel.C____mm/s | 0 | 45
[13 empty] | 3854 | PitchVelocityDiffExceed___mm/s | 0 | 45
[13 empty] | 3855 | EMCPitchValv.FastTestPerformed | 0 | 45
[13 empty] | 3856 | EMCPitchValv.FastTestFailed | 0 | 45
[13 empty] | 3857 | SafetySysNaceleChksumErr_____ | 0 | 45
[13 empty] | 3858 | SafetySysHub checksum err_____ | 0 | 45
[13 empty] | 3859 | SafetySystem Nacelle Pending | 0 | 45
[13 empty] | 3860 | SafetySystem Nacelle Error | 0 | 45
[13 empty] | 3861 | SafetySystem Converter Stopped | 0 | 45
[13 empty] | 3862 | SafetySystem Reset Required | 0 | 45
[13 empty] | 3863 | SafetySystNotReadyForReset | 0 | 45
[13 empty] | 3864 | Hub controller 24V error | 0 | 45
[13 empty] | 3865 | HubCtrl 24V PSU1 AC error | 0 | 45
[13 empty] | 3866 | HubCtrl 24V PSU2 AC error | 0 | 45
[13 empty] | 3867 | HubCtrl 24V PSU1 DC error | 0 | 45
[13 empty] | 3868 | HubCtrl 24V PSU2 DC error | 0 | 45
[13 empty] | 3869 | Nacelle controller 24V error | 0 | 45
[13 empty] | 3870 | NacelleCtrl 24V PSU1 AC error | 0 | 45
[13 empty] | 3871 | NacelleCtrl 24V PSU2 AC error | 0 | 45
[13 empty] | 3872 | NacelleCtrl 24V PSU1 DC error | 0 | 45
[13 empty] | 3873 | NacelleCtrl 24V PSU2 DC error | 0 | 45
[13 empty] | 3874 | Tower controller 24V error | 0 | 45
[13 empty] | 3875 | TowerCtrl 24V PSU AC error | 0 | 45
[13 empty] | 3876 | TowerCtrl 24V PSU1 DC error | 0 | 45
[13 empty] | 3877 | TowerCtrl 24V PSU2 DC error | 0 | 45
[13 empty] | 3878 | Tower controller 24V error | 0 | 45
[13 empty] | 3879 | NacActuators 24V PSU1 DC error | 0 | 45
[13 empty] | 3880 | NacActuators 24V PSU2 DC error | 0 | 45
[13 empty] | 3881 | NacActuators 24V PSU3 DC error | 0 | 45
[13 empty] | 3882 | TwrConvModule1 24V error | 0 | 45
[13 empty] | 3883 | TwrConvModule1 24V PSU1DC err | 0 | 45
[13 empty] | 3884 | TwrConvModule1 24V PSU2DC err | 0 | 45
[13 empty] | 3885 | TwrConvModule1 24V PSU1AC err | 0 | 45
[13 empty] | 3886 | TwrConvModule2 24V error | 0 | 45
[13 empty] | 3887 | TwrConvModule2 24V PSU1DC err | 0 | 45
[13 empty] | 3888 | TwrConvModule2 24V PSU2DC err | 0 | 45
[13 empty] | 3889 | TwrConvModule2 24V PSU1AC err | 0 | 45
[13 empty] | 3890 | NacConvModule1 24V error | 0 | 45
[13 empty] | 3891 | NacConvModule1 24V PSU1DC err | 0 | 45
[13 empty] | 3892 | NacConvModule1 24V PSU2DC err | 0 | 45
[13 empty] | 3893 | NacConvModule1 24V PSU1AC err | 0 | 45
[13 empty] | 3894 | NacConvModule2 24V error | 0 | 45
[13 empty] | 3895 | NacConvModule2 24V PSU1DC err | 0 | 45
[13 empty] | 3896 | NacConvModule2 24V PSU2DC err | 0 | 45
[13 empty] | 3897 | NacConvModule2 24V PSU1AC err | 0 | 45
[13 empty] | 3898 | Tower 110V error | 0 | 45
[13 empty] | 3899 | Tower 110V PSU1 AC error | 0 | 45
[13 empty] | 3900 | Tower 110V PSU2 AC error | 0 | 45
[13 empty] | 3901 | Tower 110V PSU1 DC error | 0 | 45
[13 empty] | 3902 | Tower 110V PSU2 DC error | 0 | 45
[13 empty] | 3903 | Tower 110V PSU3 DC error | 0 | 45
[13 empty] | 3904 | Tower 24V error | 0 | 45
[13 empty] | 3905 | Tower 24V PSU1 error | 0 | 45
[13 empty] | 3906 | Tower 24V PSU2 error | 0 | 45
[13 empty] | 3907 | Estop Button Activated__ | 2 | 20
[13 empty] | 3908 | Tower AC Aux CB Opened | 0 | 45
[13 empty] | 3909 | Tower AC Aux Contactor Opened | 0 | 45
[13 empty] | 3910 | Tower DC CB Opened | 0 | 45
[13 empty] | 3911 | Nacelle Main AC CB Opened | 0 | 45
[13 empty] | 3912 | Nacelle Main AC Disc Opened | 0 | 45
[13 empty] | 3913 | Nacelle AC Aux CB Opened | 0 | 45
[13 empty] | 3914 | Nacelle AC Aux Cont Opened | 0 | 45
[13 empty] | 3915 | Nacelle AC Hydr CB Opened | 0 | 45
[13 empty] | 3916 | Nacelle DC Cabinet CB Opened | 0 | 45
[13 empty] | 3917 | Main DC CB 1 Opened | 0 | 45
[13 empty] | 3918 | Main DC CB 2 Opened | 0 | 45
[13 empty] | 3919 | Main DC Rectifier 1 Error | 0 | 45
[13 empty] | 3920 | Main DC Rectifier 2 Error | 0 | 45
[13 empty] | 3921 | Yaw VFD Disc Opened | 0 | 45
[13 empty] | 3922 | Other VFD Disc Opened | 0 | 45
[13 empty] | 3923 | TwrMain DC Nac CB Opened | 0 | 45
[13 empty] | 3924 | TwrMain DC Nac Disc Opened | 0 | 45
[13 empty] | 3925 | TwrMain DC Twr CB Opened | 0 | 45
[13 empty] | 3926 | TwrMain DC Twr Disc Opened | 0 | 45
[13 empty] | 3927 | Nacelle AC CB Opened | 0 | 45
[13 empty] | 3928 | Tower AC CB Opened | 0 | 45
[13 empty] | 3929 | Aux Power Main CB Closed | 0 | 45
[13 empty] | 3930 | Aux Trafo Main CB Opened | 0 | 45
[13 empty] | 3931 | Service Gen Main CB Closed | 0 | 45
[13 empty] | 3932 | Service Gen Main CB Opened | 0 | 45
[13 empty] | 3933 | Nacelle Pwr Outlet CB Opened | 0 | 45
[13 empty] | 3934 | Aux Power Main CB Opened | 0 | 45
[13 empty] | 3935 | Aux Main Disc Opened | 0 | 45
[13 empty] | 3936 | Nacelle Rear Fan : ___°C | 0 | 45
[13 empty] | 3937 | Nacelle Rear Hatch : ___°C | 0 | 45
[13 empty] | 3938 | Nacelle Rear Fan Thermo Fault | 0 | 45
[13 empty] | 3939 | Nacelle Rear Fan Therm Sig Inv | 0 | 45
[13 empty] | 3940 | NacelleRearFanSignalInvalid | 0 | 45
[13 empty] | 3941 | Battery error in Tower UPS DC1 | 0 | 45
[13 empty] | 3942 | Error in Tower UPS DC1 | 0 | 45
[13 empty] | 3944 | HubInSafeModeWhileRotating | 0 | 45
[13 empty] | 3945 | Nacelle Rear Hatch Pos FB Err | 0 | 45
[13 empty] | 3946 | Nacelle Rear Hatch Neg FB Err | 0 | 45
[13 empty] | 3947 | Confirm leave hub in safe mode | 0 | 45
[13 empty] | 3948 | ManBladeSelectorSignalMismatch | 0 | 45
[13 empty] | 3949 | Hub ball valve A closed | 0 | 45
[13 empty] | 3950 | Hub ball valve B closed | 0 | 45
[13 empty] | 3951 | Hub ball valve C closed | 0 | 45
[13 empty] | 3952 | Hub ball valve A Hw error | 0 | 45
[13 empty] | 3953 | Hub ball valve B Hw error | 0 | 45
[13 empty] | 3954 | Hub ball valve C Hw error | 0 | 45
[13 empty] | 3955 | Hub service switch Hw error | 0 | 45
[13 empty] | 3956 | Hold To Run button Hw error | 0 | 45
[13 empty] | 3957 | Hub switch while rotating | 0 | 45
[13 empty] | 3958 | LubrInletPressValidationFailed | 0 | 45
[13 empty] | 3959 | LubrDrySumpValidationFailed | 0 | 45
[13 empty] | 3960 | GearOilInletPressLow _._ bar | 0 | 45
[13 empty] | 3961 | GearOilInletTempHigh ___ °C | 0 | 45
[13 empty] | 3962 | GearOilInletTempTooHigh ___ °C | 0 | 45
[13 empty] | 3963 | GearOilWetSumpLevelLow | 0 | 45
[13 empty] | 3964 | GearFiltPressHigh __._bar | 0 | 45
[13 empty] | 3965 | GearFiltPressTooHigh __._bar | 0 | 45
[13 empty] | 3966 | GearOilPumpFault P1: _ P2: _ | 0 | 45
[13 empty] | 3967 | GearOilPumpsAllFailed | 0 | 45
[13 empty] | 3968 | MBADistOilPressLow _._ bar | 0 | 45
[13 empty] | 3969 | MBADistOilTempHigh ___ °C | 0 | 45
[13 empty] | 3970 | MBADistOilTempTooHigh ___ °C | 0 | 45
[13 empty] | 3971 | GenOilInletPressLow _._ bar | 0 | 45
[13 empty] | 3972 | GenOilInletTempHigh ___ °C | 0 | 45
[13 empty] | 3973 | GenOilInletTempTooHigh ___ °C | 0 | 45
[13 empty] | 3974 | MBGFiltPressHigh __._bar | 0 | 45
[13 empty] | 3975 | MBGFiltPressTooHigh __._bar | 0 | 45
[13 empty] | 3976 | MBGOilPumpFault P1: _ P2: _ | 0 | 45
[13 empty] | 3977 | MBGOilPumpsAllFailed | 0 | 45
[13 empty] | 3978 | MainTankOilLevelLow: ____mm | 0 | 45
[13 empty] | 3979 | MainTankOilTempLow ___°C | 0 | 45
[13 empty] | 3980 | MainTankOilTempHigh ___°C | 0 | 45
[13 empty] | 3981 | GearboxA1A2ValveCannotClose | 0 | 45
[13 empty] | 3982 | GearboxA1A2ValveCannotOpen | 0 | 45
[13 empty] | 3983 | GearboxBValveCannotClose | 0 | 45
[13 empty] | 3984 | GearboxBValveCannotOpen | 0 | 45
[13 empty] | 3985 | MainBearREValveCannotClose | 0 | 45
[13 empty] | 3986 | MainBearREValveCannotOpen | 0 | 45
[13 empty] | 3987 | MainBearNREValveCannotClose | 0 | 45
[13 empty] | 3988 | MainBearNREValveCannotOpen | 0 | 45
[13 empty] | 3989 | GeneratorDEValveCannotClose | 0 | 45
[13 empty] | 3990 | GeneratorDEValveCannotOpen | 0 | 45
[13 empty] | 3991 | GeneratorNDEValveCannotClose | 0 | 45
[13 empty] | 3992 | GeneratorNDEValveCannotOpen | 0 | 45
[13 empty] | 3993 | StatLubrOilLeak G:____ M:____ | 0 | 45
[13 empty] | 3994 | DynLubrOilLeak M:____ l | 0 | 45
[13 empty] | 4004 | NacWaterCoolPumpPressLow:__bar | 0 | 45
[13 empty] | 4005 | NacWaterCoolPump1CBOpen | 0 | 45
[13 empty] | 4006 | NacWaterCoolPump2CBOpen | 0 | 45
[13 empty] | 4007 | NacWaterCoolHeaterCBOpen | 0 | 45
[13 empty] | 4008 | NacWaterCoolPump1SignalInvalid | 0 | 45
[13 empty] | 4009 | NacWaterCoolPump2SignalInvalid | 0 | 45
[13 empty] | 4010 | NacWaterCoolPump1FBInvalid | 0 | 45
[13 empty] | 4011 | NacWaterCoolPump2FBInvalid | 0 | 45
[13 empty] | 4012 | NacWaterCoolPump1ThermoInvalid | 0 | 45
[13 empty] | 4013 | NacWaterCoolPump2ThermoInvalid | 0 | 45
[13 empty] | 4014 | NacWaterCoolPump1NegFBError | 0 | 45
[13 empty] | 4015 | NacWaterCoolPump2NegFBError | 0 | 45
[13 empty] | 4016 | NacWaterCoolPump1PosFBError | 0 | 45
[13 empty] | 4017 | NacWaterCoolPump2PosFBError | 0 | 45
[13 empty] | 4018 | NacWaterCoolPump1ThermoFault | 0 | 45
[13 empty] | 4019 | NacWaterCoolPump2ThermoFault | 0 | 45
[13 empty] | 4025 | GenAirFlowReduced Fan1 | 0 | 45
[13 empty] | 4026 | GenAirFlowReduced Fan2 | 0 | 45
[13 empty] | 4027 | GenAirflowFault | 0 | 45
[13 empty] | 4028 | GenAirFan1Fault | 0 | 45
[13 empty] | 4029 | GenAirFan2Fault | 0 | 45
[13 empty] | 4030 | GenAirFansBothFailed | 0 | 45
[13 empty] | 4033 | SafetySystem Hub Pending | 0 | 45
[13 empty] | 4034 | SafetySystem Hub Error | 0 | 45
[13 empty] | 4035 | ExtrHighAgo2Chopper R Loading | 0 | 45
[13 empty] | 4036 | TestEmgPitchValvesActivated | 0 | 45
[13 empty] | 4039 | NacelleACHydr contactor error | 0 | 45
[13 empty] | 4040 | PowerTrainLubr enabler error | 0 | 45
[13 empty] | 4041 | YawActuators enabler error | 0 | 45
[13 empty] | 4042 | GenFans enabler error | 0 | 45
[13 empty] | 4043 | NacelleACAux contactor error | 0 | 45
[13 empty] | 4044 | TowerACAux contactor error | 0 | 45
[13 empty] | 4045 | Nacelle PSU CB Opened | 0 | 45
[13 empty] | 4046 | TYC SafeMode _ PowDerate:____ | 0 | 45
[13 empty] | 4047 | PSA SafeMode _ PowDerate:____ | 0 | 45
[13 empty] | 4048 | SupplyError: Max ____V DC | 0 | 45
[13 empty] | 4049 | SupplyError: Min ____V DC | 0 | 45
[13 empty] | 4050 | Nac AC Hydr contactor: __ | 0 | 45
[13 empty] | 4051 | Yaw enabler: __ | 0 | 45
[13 empty] | 4052 | Nac AC Aux contactor: __ | 0 | 45
[13 empty] | 4053 | Tower AC Aux contactor: __ | 0 | 45
[13 empty] | 4054 | Power Train Lubr enabler: __ | 0 | 45
[13 empty] | 4055 | Gen Fans enabler: __ | 0 | 45
[13 empty] | 4056 | HubSafety Variant Select. Err. | 0 | 45
[13 empty] | 4057 | TowWaterCoolPumpPressLow:__bar | 0 | 45
[13 empty] | 4058 | TowerWaterCoolPumpCBOpen | 0 | 45
[13 empty] | 4059 | TowerWaterCoolFan1CBOpen | 0 | 45
[13 empty] | 4060 | TowerWaterCoolFan2CBOpen | 0 | 45
[13 empty] | 4061 | TowerWaterCoolHeaterCBOpen | 0 | 45
[13 empty] | 4062 | TowerWaterCoolPumpSigInvalid | 0 | 45
[13 empty] | 4063 | TowerWaterCoolFan1SigInvalid | 0 | 45
[13 empty] | 4064 | TowerWaterCoolFan2SigInvalid | 0 | 45
[13 empty] | 4065 | TowerWaterCoolPumpFBInvalid | 0 | 45
[13 empty] | 4066 | TowerWaterCoolFan1FBInvalid | 0 | 45
[13 empty] | 4067 | TowerWaterCoolFan2FBInvalid | 0 | 45
[13 empty] | 4068 | TowWaterCoolPumpThermoInvalid | 0 | 45
[13 empty] | 4069 | TowWaterCoolFan1ThermoInvalid | 0 | 45
[13 empty] | 4070 | TowWaterCoolFan2ThermoInvalid | 0 | 45
[13 empty] | 4071 | TowerWaterCoolPumpNegFBError | 0 | 45
[13 empty] | 4072 | TowerWaterCoolFan1NegFBError | 0 | 45
[13 empty] | 4073 | TowerWaterCoolFan2NegFBError | 0 | 45
[13 empty] | 4074 | TowerWaterCoolPumpPosFBError | 0 | 45
[13 empty] | 4075 | TowerWaterCoolFan1PosFBError | 0 | 45
[13 empty] | 4076 | TowerWaterCoolFan2PosFBError | 0 | 45
[13 empty] | 4077 | TowerWaterCoolPumpThermoFault | 0 | 45
[13 empty] | 4078 | TowerWaterCoolFan1ThermoFault | 0 | 45
[13 empty] | 4079 | TowerWaterCoolFan2ThermoFault | 0 | 45
[13 empty] | 4080 | UPS On Grid | 0 | 45
[13 empty] | 4081 | UPS Battery OK | 0 | 45
[13 empty] | 4085 | Trafo high core temp.: ___ °C | 0 | 45
[13 empty] | 4086 | Trafo extreme low liquid level | 0 | 45
[13 empty] | 4087 | Trafo high liquid temp:___ °C | 0 | 45
[13 empty] | 4088 | Trafo high press relief valves | 0 | 45
[13 empty] | 4089 | Trafo low liquid level: ___ mA | 0 | 45
[13 empty] | 4090 | TrafoRapidPressRiseDetected | 0 | 45
[13 empty] | 4092 | Safety waiting for reset | 0 | 45
[13 empty] | 4093 | Safety Hub unknown reset | 0 | 45
[13 empty] | 4094 | Safety Nac unknown reset | 0 | 45
[13 empty] | 4095 | Safety Twr unknown reset | 0 | 45
[13 empty] | 4096 | Safety TPiece unknown reset | 0 | 45
[13 empty] | 4097 | Safety Hub unknown pending | 0 | 45
[13 empty] | 4098 | Safety Nac unknown pending | 0 | 45
[13 empty] | 4099 | Safety Twr unknown pending | 0 | 45
[13 empty] | 4100 | Safety TPiece unknown pending | 0 | 45
[13 empty] | 4101 | Safety Hub Error, code: ___ | 0 | 45
[13 empty] | 4102 | Safety Nac Error, code: ___ | 0 | 45
[13 empty] | 4103 | Safety Twr Error, code: ___ | 0 | 45
[13 empty] | 4104 | Safety TPiese Error, code: ___ | 0 | 45
[13 empty] | 4105 | EmergStopButtonActivated __ | 0 | 45
[13 empty] | 4106 | Yaw motor manual control | 0 | 45
[13 empty] | 4107 | Converter MSI error | 0 | 45
[13 empty] | 4108 | Converter LSI error | 0 | 45
[13 empty] | 4109 | ExtrHigh Grid Inv Brk Current | 0 | 45
[13 empty] | 4110 | High Grid Inv Breaker Current | 0 | 45
[13 empty] | 4111 | Asym Grid Inv Break Current | 0 | 45
[13 empty] | 4112 | OverSpdGuardActivatedReconfirm | 0 | 45
[13 empty] | 4113 | HighRotSpd SlopeToRefDisabled | 0 | 45
[13 empty] | 4114 | BladeA Heaters temp dif. error | 0 | 45
[13 empty] | 4115 | BladeA Fan1 pos feedback error | 0 | 45
[13 empty] | 4116 | BladeA Fan1 neg feedback error | 0 | 45
[13 empty] | 4117 | BladeA Fan2 pos feedback error | 0 | 45
[13 empty] | 4118 | BladeA Fan2 neg feedback error | 0 | 45
[13 empty] | 4119 | BladeA Fan3 pos feedback error | 0 | 45
[13 empty] | 4120 | BladeA Fan3 neg feedback error | 0 | 45
[13 empty] | 4121 | BladeA Fan1 is overloaded | 0 | 45
[13 empty] | 4122 | BladeA Fan2 is overloaded | 0 | 45
[13 empty] | 4123 | BladeA Fan3 is overloaded | 0 | 45
[13 empty] | 4124 | BladeA Heat/Out temp dif. err | 0 | 45
[13 empty] | 4125 | BldAFanPreheat pos feedbck err | 0 | 45
[13 empty] | 4126 | BldAFanPreheat neg feedbck err | 0 | 45
[13 empty] | 4127 | BladeA Heaters has high temp | 0 | 45
[13 empty] | 4128 | BladeA Heaters too high temp | 0 | 45
[13 empty] | 4129 | BladeA Heater1 pos feedbck err | 0 | 45
[13 empty] | 4130 | BladeA Heater1 neg feedbck err | 0 | 45
[13 empty] | 4131 | BladeA Heater2 pos feedbck err | 0 | 45
[13 empty] | 4132 | BladeA Heater2 neg feedbck err | 0 | 45
[13 empty] | 4133 | BladeA Root temperature high | 0 | 45
[13 empty] | 4134 | BladeB Heaters temp dif. error | 0 | 45
[13 empty] | 4135 | BladeB Fan1 pos feedback error | 0 | 45
[13 empty] | 4136 | BladeB Fan1 neg feedback error | 0 | 45
[13 empty] | 4137 | BladeB Fan2 pos feedback error | 0 | 45
[13 empty] | 4138 | BladeB Fan2 neg feedback error | 0 | 45
[13 empty] | 4139 | BladeB Fan3 pos feedback error | 0 | 45
[13 empty] | 4140 | BladeB Fan3 neg feedback error | 0 | 45
[13 empty] | 4141 | BladeB Fan1 is overloaded | 0 | 45
[13 empty] | 4142 | BladeB Fan2 is overloaded | 0 | 45
[13 empty] | 4143 | BladeB Fan3 is overloaded | 0 | 45
[13 empty] | 4144 | BladeB Heat/Out temp dif. err | 0 | 45
[13 empty] | 4145 | BldBFanPreheat pos feedbck err | 0 | 45
[13 empty] | 4146 | BldBFanPreheat neg feedbck err | 0 | 45
[13 empty] | 4147 | BladeB Heaters has high temp | 0 | 45
[13 empty] | 4148 | BladeB Heaters too high temp | 0 | 45
[13 empty] | 4149 | BladeB Heater1 pos feedbck err | 0 | 45
[13 empty] | 4150 | BladeB Heater1 neg feedbck err | 0 | 45
[13 empty] | 4151 | BladeB Heater2 pos feedbck err | 0 | 45
[13 empty] | 4152 | BladeB Heater2 neg feedbck err | 0 | 45
[13 empty] | 4153 | BladeB Root temperature high | 0 | 45
[13 empty] | 4154 | BladeC Heaters temp dif. error | 0 | 45
[13 empty] | 4155 | BladeC Fan1 pos feedback error | 0 | 45
[13 empty] | 4156 | BladeC Fan1 neg feedback error | 0 | 45
[13 empty] | 4157 | BladeC Fan2 pos feedback error | 0 | 45
[13 empty] | 4158 | BladeC Fan2 neg feedback error | 0 | 45
[13 empty] | 4159 | BladeC Fan3 pos feedback error | 0 | 45
[13 empty] | 4160 | BladeC Fan3 neg feedback error | 0 | 45
[13 empty] | 4161 | BladeC Fan1 is overloaded | 0 | 45
[13 empty] | 4162 | BladeC Fan2 is overloaded | 0 | 45
[13 empty] | 4163 | BladeC Fan3 is overloaded | 0 | 45
[13 empty] | 4164 | BladeC Heat/Out temp dif. err | 0 | 45
[13 empty] | 4165 | BldCFanPreheat pos feedbck err | 0 | 45
[13 empty] | 4166 | BldCFanPreheat neg feedbck err | 0 | 45
[13 empty] | 4167 | BladeC Heaters has high temp | 0 | 45
[13 empty] | 4168 | BladeC Heaters too high temp | 0 | 45
[13 empty] | 4169 | BladeC Heater1 pos feedbck err | 0 | 45
[13 empty] | 4170 | BladeC Heater1 neg feedbck err | 0 | 45
[13 empty] | 4171 | BladeC Heater2 pos feedbck err | 0 | 45
[13 empty] | 4172 | BladeC Heater2 neg feedbck err | 0 | 45
[13 empty] | 4173 | BladeC Root temperature high | 0 | 45
[13 empty] | 4174 | Trafo liquid pump state:___ | 0 | 45
[13 empty] | 4175 | Trafo liquid pump CB open | 0 | 45
[13 empty] | 4176 | TrafoLiquidPump signal invalid | 0 | 45
[13 empty] | 4177 | Trafo liquid pump positive FB | 0 | 45
[13 empty] | 4178 | Trafo liquid pump negative FB | 0 | 45
[13 empty] | 4179 | TrafoLiquidPump FB Sig Invalid | 0 | 45
[13 empty] | 4180 | Trafo liquid pump thermo fault | 0 | 45
[13 empty] | 4181 | TrafoLiquidPump thermo Sig Inv | 0 | 45
[13 empty] | 4182 | SafetyPitchSpdNotOk | 0 | 45
[13 empty] | 4183 | SafetyPitchSpdNotOkForProd | 0 | 45
[13 empty] | 4184 | A Ctrl:__._V P.Vel:___._mm/s | 0 | 45
[13 empty] | 4185 | B Ctrl:__._V P.Vel:___._mm/s | 0 | 45
[13 empty] | 4186 | C Ctrl:__._V P.Vel:___._mm/s | 0 | 45
[13 empty] | 4187 | StarToDelta, TimeProd _____s | 0 | 45
[13 empty] | 4188 | DeltaToStar,TimeProd_____s, _ | 0 | 45
[13 empty] | 4189 | Yaw and return completed | 0 | 45
[13 empty] | 4190 | Yaw and return failed | 0 | 45
[13 empty] | 4191 | BladeA Unexpected airflow err | 0 | 45
[13 empty] | 4192 | BladeB Unexpected airflow err | 0 | 45
[13 empty] | 4193 | BladeC Unexpected airflow err | 0 | 45
[13 empty] | 4194 | BladeA Missing airflow error | 0 | 45
[13 empty] | 4195 | BladeB Missing airflow error | 0 | 45
[13 empty] | 4196 | BladeC Missing airflow error | 0 | 45
[13 empty] | 4197 | BladeA Heaters low temperature | 0 | 45
[13 empty] | 4198 | BladeB Heaters low temperature | 0 | 45
[13 empty] | 4199 | BladeC Heaters low temperature | 0 | 45
[13 empty] | 4200 | EMCPitchValv.FuncTestPerformed | 0 | 45
[13 empty] | 4201 | TurbineNotUpwind | 0 | 45
[13 empty] | 4202 | Blade A : FlowTestSeq.started | 0 | 45
[13 empty] | 4203 | Blade B : FlowTestSeq.started | 0 | 45
[13 empty] | 4204 | Blade C : FlowTestSeq.started | 0 | 45
[13 empty] | 4205 | Ctrl:___._V,PitchRate:___._°/s | 0 | 45
[13 empty] | 4206 | PistV Meas:___._,Exp:___._mm/s | 0 | 45
[13 empty] | 4207 | TestStepFailed, Ctrl:___._V | 0 | 45
[13 empty] | 4208 | Blade A: Seq. TestPassed,___s | 0 | 45
[13 empty] | 4209 | Blade B: Seq. TestPassed,___s | 0 | 45
[13 empty] | 4210 | Blade C: Seq. TestPassed,___s | 0 | 45
[13 empty] | 4211 | Blade A: SequenceTestFailed | 0 | 45
[13 empty] | 4212 | Blade B: SequenceTestFailed | 0 | 45
[13 empty] | 4213 | Blade C: SequenceTestFailed | 0 | 45
[13 empty] | 4214 | PASS:_ FlowTestSeq,in__.__min | 0 | 45
[13 empty] | 4215 | FAIL:_ FlowTestSeq,in__.__min | 0 | 45
[13 empty] | 4216 | Yaw CB Feedback Fault | 0 | 45
[13 empty] | 4217 | Yaw Motor CB Signal Invalid | 0 | 45
[13 empty] | 4218 | HVCBOpened | 0 | 45
[13 empty] | 4219 | HVCBConnected | 0 | 45
[13 empty] | 4220 | WaterPumpPressureLow__.__bar | 0 | 45
[13 empty] | 4221 | All blades deicing started | 0 | 45
[13 empty] | 4222 | Blade A deicing started | 0 | 45
[13 empty] | 4223 | Blade B deicing started | 0 | 45
[13 empty] | 4224 | Blade C deicing started | 0 | 45
[13 empty] | 4225 | TowerAccX SignalDead __m/s^2 | 0 | 45
[13 empty] | 4226 | TowerAccX NoZeroCross __m/s^2 | 0 | 45
[13 empty] | 4227 | All blades deicing stopped | 0 | 45
[13 empty] | 4228 | Blade A deicing stopped | 0 | 45
[13 empty] | 4229 | Blade B deicing stopped | 0 | 45
[13 empty] | 4230 | Blade C deicing stopped | 0 | 45
[13 empty] | 4231 | NoiseReductionPauseModeActive | 0 | 45
[13 empty] | 4232 | ECD_Detected | 0 | 45
[13 empty] | 4234 | Grid Converter CB Open | 0 | 45
[13 empty] | 4235 | Gen Stator CB Open | 0 | 45
[13 empty] | 4236 | ControllerCabinetSupplyCBOpen | 0 | 45
[13 empty] | 4239 | HVCB Unknown Trip Reason | 0 | 45
[13 empty] | 4240 | ManPitchAllBldHighWind__._m/s | 0 | 45
[13 empty] | 4241 | Grid Fast Link Is Stopped | 0 | 45
[13 empty] | 4242 | Machine Fast Link Is Stopped | 0 | 45
[13 empty] | 4243 | Missing OK Status Fan feedb. | 0 | 45
[13 empty] | 4244 | Ext.ConverterStopSignalActive | 0 | 45
[13 empty] | 4245 | ExtConverterStopArcDetected | 0 | 45
[13 empty] | 4246 | LSI ExtHighI X | 0 | 45
[13 empty] | 4247 | LSI ExtHighI Y | 0 | 45
[13 empty] | 4248 | LSI ExtHighI Info X | 0 | 45
[13 empty] | 4249 | LSI ExtHighI Info Y | 0 | 45
[13 empty] | 4250 | LSI HW Err X | 0 | 45
[13 empty] | 4251 | LSI HW Err Y | 0 | 45
[13 empty] | 4252 | LSI HW Err Info X | 0 | 45
[13 empty] | 4253 | LSI HW Err Info Y | 0 | 45
[13 empty] | 4254 | MoistureLevelTooHigh | 0 | 45
[13 empty] | 4255 | TempSwitch_GridChoke | 0 | 45
[13 empty] | 4256 | LSI High Temp PWR Sect Air1 | 0 | 45
[13 empty] | 4257 | LSI High Temp PWR Sect Air2 | 0 | 45
[13 empty] | 4258 | High Temp Grid Choke | 0 | 45
[13 empty] | 4259 | High Temp Fil Sect Air | 0 | 45
[13 empty] | 4260 | High Temp LSI X IGBT | 0 | 45
[13 empty] | 4261 | High Temp LSI Y IGBT | 0 | 45
[13 empty] | 4262 | HighDCCurrentDiff | 0 | 45
[13 empty] | 4263 | IDC Estimate To IDC Deviation | 0 | 45
[13 empty] | 4264 | LSI Inv Current Load Share | 0 | 45
[13 empty] | 4265 | HighICenterLine | 0 | 45
[13 empty] | 4266 | HighIDCLeak | 0 | 45
[13 empty] | 4267 | Invt.PosToNegOutOffPWMSync | 0 | 45
[13 empty] | 4268 | AsymStatorVoltage | 0 | 45
[13 empty] | 4269 | MachineInvNegLoadShareError | 0 | 45
[13 empty] | 4270 | TooLowStatorVoltage | 0 | 45
[13 empty] | 4271 | StatorPhaseSequenceErr | 0 | 45
[13 empty] | 4272 | LSI HighTemp CabinetAir | 0 | 45
[13 empty] | 4273 | MSI HighTemp Inv IGBT X | 0 | 45
[13 empty] | 4274 | MSI HighTemp Inv IGBT Y | 0 | 45
[13 empty] | 4275 | WrongRotationDir.OrSpeedDiff | 0 | 45
[13 empty] | 4276 | HPC Contactor opened | 0 | 45
[13 empty] | 4277 | HPC Contactor closed | 0 | 45
[13 empty] | 4278 | HPC disconnected | 0 | 45
[13 empty] | 4279 | HPC ready for power | 0 | 45
[13 empty] | 4280 | HPC heater pos feedback err | 0 | 45
[13 empty] | 4281 | HPC heater neg feedback err | 0 | 45
[13 empty] | 4282 | HPC actuator extend error | 0 | 45
[13 empty] | 4283 | HPC actuator retract error | 0 | 45
[13 empty] | 4284 | HPC CB opened err | 0 | 45
[13 empty] | 4285 | HPC CB closed err | 0 | 45
[13 empty] | 4286 | HPC pos sensor off | 0 | 45
[13 empty] | 4287 | HPC rotor position error | 0 | 45
[13 empty] | 4288 | CabinetFanContactorFBError | 0 | 45
[13 empty] | 4289 | BLCalibAbortedAutoYawDisabled | 0 | 45
[13 empty] | 4290 | ResFilterContOpenFailed | 0 | 45
[13 empty] | 4291 | ResFilterContFeedBackResponse | 0 | 45
[13 empty] | 4292 | UnexpecGridResFiltContFeedb | 0 | 45
[13 empty] | 4293 | GridResFilterNotPresent | 0 | 45
[13 empty] | 4294 | DCChopperX_HWErr, ConvModule__ | 0 | 45
[13 empty] | 4295 | DCChopperY_HWErr, ConvModule__ | 0 | 45
[13 empty] | 4296 | MSI HW Err Info X | 0 | 45
[13 empty] | 4297 | MSI HW Err Info Y | 0 | 45
[13 empty] | 4298 | TempSwitch_GridFilter | 0 | 45
[13 empty] | 4299 | HighTemp_DCChopperRes_X | 0 | 45
[13 empty] | 4300 | HighTemp_DCChopperRes_Y | 0 | 45
[13 empty] | 4301 | HighTempDVDTFilter_X | 0 | 45
[13 empty] | 4302 | HighTempDVDTFilter_Y | 0 | 45
[13 empty] | 4305 | MSIStringLoadShareError | 0 | 45
[13 empty] | 4306 | CabinetFanContactorFBError | 0 | 45
[13 empty] | 4307 | Missing OK Status Fan feedb. | 0 | 45
[13 empty] | 4308 | DCChopperX_HWErr, ConvModule__ | 0 | 45
[13 empty] | 4309 | DCChopperY_HWErr, ConvModule__ | 0 | 45
[13 empty] | 4310 | Ext.ConverterStopSignalActive | 0 | 45
[13 empty] | 4311 | ExtConverterStopArcDetected | 0 | 45
[13 empty] | 4312 | HighDCCurrentDiff | 0 | 45
[13 empty] | 4313 | HighTemp_DCChopperRes_X | 0 | 45
[13 empty] | 4314 | HighTemp_DCChopperRes_Y | 0 | 45
[13 empty] | 4315 | MSI High Temp PWR Sect Air1 | 0 | 45
[13 empty] | 4316 | MSI High Temp PWR Sect Air2 | 0 | 45
[13 empty] | 4317 | Invt.PosToNegOutOffPWMSync | 0 | 45
[13 empty] | 4318 | MSI HW Err X | 0 | 45
[13 empty] | 4319 | MSI HW Err Y | 0 | 45
[13 empty] | 4320 | MoistureLevelTooHigh | 0 | 45
[13 empty] | 4321 | BLCalibCompletedSuccessfully | 0 | 45
[13 empty] | 4322 | Rotor positioning started | 0 | 45
[13 empty] | 4323 | Rotor positioning stopped | 0 | 45
[13 empty] | 4324 | RotorStoppedAtPosition __.__° | 0 | 45
[13 empty] | 4325 | Rotor positioning succeeded | 0 | 45
[13 empty] | 4326 | Rotor positioning failed: __ | 0 | 45
[13 empty] | 4327 | MSI ExtHighI Info X | 0 | 45
[13 empty] | 4328 | MSI ExtHighI Info Y | 0 | 45
[13 empty] | 4329 | MSI ExtHighI X | 0 | 45
[13 empty] | 4330 | MSI ExtHighI Y | 0 | 45
[13 empty] | 4331 | GenSpeedOutLimLw/Hi:_, ____rpm | 0 | 45
[13 empty] | 4332 | MSI HighTemp CabinetAir | 0 | 45
[13 empty] | 4333 | PitchOffsetCycle test started | 0 | 45
[13 empty] | 4334 | PitchOffsetCycleTest next step | 0 | 45
[13 empty] | 4335 | PitchOffsetCycleTest finalized | 0 | 45
[13 empty] | 4336 | PanelPowerSupplyNacelle24VErr | 0 | 45
[13 empty] | 4337 | PanelPowerSupplyTower24VError | 0 | 45
[13 empty] | 4338 | Watchdog Application Reboot | 0 | 45
[13 empty] | 4339 | De-icing TestFunctionSucceeded | 0 | 45
[13 empty] | 4340 | De-icing aborted: __ | 0 | 45
[13 empty] | 4341 | PwrBkup voltage sensor 1 error | 0 | 45
[13 empty] | 4342 | PwrBkup voltage sensor 2 error | 0 | 45
[13 empty] | 4343 | PwrBkup voltage deviation err | 0 | 45
[13 empty] | 4344 | PwrBkup state | 0 | 45
[13 empty] | 4345 | PwrBkup draining batteries | 0 | 45
[13 empty] | 4346 | PwrBkup system error | 0 | 45
[13 empty] | 4347 | PwrBkup charger 1 error | 0 | 45
[13 empty] | 4348 | PwrBkup charger 2 error | 0 | 45
[13 empty] | 4349 | PwrBkup charging system ok | 0 | 45
[13 empty] | 4350 | PwrBkup charging system error | 0 | 45
[13 empty] | 4351 | PwrBkup battery test | 0 | 45
[13 empty] | 4352 | PwrBkup battery bank ok | 0 | 45
[13 empty] | 4353 | PwrBkup battery bank error | 0 | 45
[13 empty] | 4354 | PwrBkup string 1 status | 0 | 45
[13 empty] | 4355 | PwrBkup string 2 status | 0 | 45
[13 empty] | 4356 | PwrBkup string 3 status | 0 | 45
[13 empty] | 4357 | PwrBkup string 4 status | 0 | 45
[13 empty] | 4358 | PwrBkup recharge time | 0 | 45
[13 empty] | 4359 | PwrBkup converter 1 error | 0 | 45
[13 empty] | 4360 | PwrBkup converter 2 error | 0 | 45
[13 empty] | 4361 | PwrBkup converter 3 error | 0 | 45
[13 empty] | 4362 | PwrBkup converter 4 error | 0 | 45
[13 empty] | 4363 | PwrBkup converter 5 error | 0 | 45
[13 empty] | 4364 | PwrBkup converter 6 error | 0 | 45
[13 empty] | 4365 | PwrBkup DCDC converter error | 0 | 45
[13 empty] | 4366 | Pitch Common A accu failed | 0 | 45
[13 empty] | 4367 | Pitch EMF A accu 1 failed | 0 | 45
[13 empty] | 4368 | Pitch EMF A accu 2 one failed | 0 | 45
[13 empty] | 4369 | Pitch EMF A accu 2 two failed | 0 | 45
[13 empty] | 4370 | Pitch Com. A accu drain failed | 0 | 45
[13 empty] | 4371 | PitchEMF A accu 1 drain failed | 0 | 45
[13 empty] | 4372 | PitchEMF A accu 2 drain failed | 0 | 45
[13 empty] | 4373 | Pitch Common B accu failed | 0 | 45
[13 empty] | 4374 | Pitch EMF B accu 1 failed | 0 | 45
[13 empty] | 4375 | Pitch EMF B accu 2 one failed | 0 | 45
[13 empty] | 4376 | Pitch EMF B accu 2 two failed | 0 | 45
[13 empty] | 4377 | Pitch Com. B accu drain failed | 0 | 45
[13 empty] | 4378 | PitchEMF B accu 1 drain failed | 0 | 45
[13 empty] | 4379 | PitchEMF B accu 2 drain failed | 0 | 45
[13 empty] | 4380 | Pitch Common C accu failed | 0 | 45
[13 empty] | 4381 | Pitch EMF C accu 1 failed | 0 | 45
[13 empty] | 4382 | Pitch EMF C accu 2 one failed | 0 | 45
[13 empty] | 4383 | Pitch EMF C accu 2 two failed | 0 | 45
[13 empty] | 4384 | Pitch Com. C accu drain failed | 0 | 45
[13 empty] | 4385 | PitchEMF C accu 1 drain failed | 0 | 45
[13 empty] | 4386 | PitchEMF C accu 2 drain failed | 0 | 45
[13 empty] | 4387 | Pitch accumulator failure | 0 | 45
[13 empty] | 4388 | Accu Test Initial Press Failed | 0 | 45
[13 empty] | 4392 | GearOilQualityErr:___RPM___°C | 0 | 45
[13 empty] | 4393 | Act Pwr Remote tmt P=____ M=__ | 0 | 45
[13 empty] | 4395 | DeIcing Requested | 0 | 45
[13 empty] | 4396 | DeIcing In Progress | 0 | 45
[13 empty] | 4397 | DeIcing Cooling | 0 | 45
[13 empty] | 4398 | DeIce Finished-Turbine paused | 0 | 45
[13 empty] | 4400 | Rct Pwr Remote tmt P=____ M=__ | 0 | 45
[13 empty] | 4401 | MSI InvCurrentLoadShare | 0 | 45
[13 empty] | 4402 | StringStateTransitionTimeout | 0 | 45
[13 empty] | 4403 | MSIStateTransitionTimeout | 0 | 45
[13 empty] | 4407 | Pitch Calib Not Complete | 0 | 45
[13 empty] | 4408 | TempSwitchdvdtFilterX: Mod__ | 0 | 45
[13 empty] | 4409 | TempSwitchdvdtFilterY: Mod__ | 0 | 45
[13 empty] | 4410 | PowerError ____._ kW | 0 | 45
[13 empty] | 4411 | PowerDev(SlowFilt):____._ kW | 0 | 45
[13 empty] | 4412 | SafetySystemNotReadyForReset | 0 | 45
[13 empty] | 4413 | SafetySystem Hub Pending | 0 | 45
[13 empty] | 4414 | SafetySystem Hub Error | 0 | 45
[13 empty] | 4415 | SafetySystem Nacelle Pending | 0 | 45
[13 empty] | 4416 | SafetySystem Nacelle Error | 0 | 45
[13 empty] | 4417 | Grid Inv Breaker Open | 0 | 45
[13 empty] | 4418 | MSI, arc detected __ | 0 | 45
[13 empty] | 4419 | MSI, arc detector error __ | 0 | 45
[13 empty] | 4420 | MSI, arc detected | 0 | 45
[13 empty] | 4421 | MSI, arc detector error | 0 | 45
[13 empty] | 4422 | LSI, arc detected __ | 0 | 45
[13 empty] | 4423 | LSI, arc detector error __ | 0 | 45
[13 empty] | 4424 | LSI, arc detected | 0 | 45
[13 empty] | 4425 | LSI, arc detector error | 0 | 45
[13 empty] | 4426 | Switchgear, arc detected __ | 0 | 45
[13 empty] | 4427 | Switchgear arc detector err__ | 0 | 45
[13 empty] | 4428 | Switchgear, arc detected | 0 | 45
[13 empty] | 4429 | Switchgear, arc detector error | 0 | 45
[13 empty] | 4430 | HVCBOpened | 0 | 45
[13 empty] | 4431 | HVCBReconnected | 0 | 45
[13 empty] | 4432 | TripHVButtonActivated __ | 0 | 45
[13 empty] | 4433 | HVCBNotHealthy | 0 | 45
[13 empty] | 4434 | PilotValvesTestP1V1Failure | 0 | 45
[13 empty] | 4435 | PilotValvesTestP1V2Failure | 0 | 45
[13 empty] | 4436 | PilotValvesTestPilotSystemFail | 0 | 45
[13 empty] | 4437 | DODP InitialPressFailure | 0 | 45
[13 empty] | 4438 | DODP Valve A Failure | 0 | 45
[13 empty] | 4439 | DODP Valve B Failure | 0 | 45
[13 empty] | 4440 | DODP Valve C Failure | 0 | 45
[13 empty] | 4441 | EMF Accu A Leakage Fail | 0 | 45
[13 empty] | 4442 | EMF Accu B Leakage Fail | 0 | 45
[13 empty] | 4443 | EMF Accu C Leakage Fail | 0 | 45
[13 empty] | 4444 | PilotValvesTestCompleted | 0 | 45
[13 empty] | 4445 | DODPValvesTestCompleted | 0 | 45
[13 empty] | 4446 | Blade Locking Timeout Error | 0 | 45
[13 empty] | 4447 | Accu Test Blade Locking Failed | 0 | 45
[13 empty] | 4448 | Active pow. derated by:_.__ | 0 | 45
[13 empty] | 4449 | Grid volt harmonics exceed L1 | 0 | 45
[13 empty] | 4450 | Grid volt harmonics exceed L2 | 0 | 45
[13 empty] | 4451 | Grid volt harmonics exceed L3 | 0 | 45
[13 empty] | 4452 | Hydr Mode Selector In Manual | 0 | 45
[13 empty] | 4453 | VTL ConstLoad Signal Detected | 0 | 45
[13 empty] | 4454 | VTL Wind Sensor Status Error | 0 | 45
[13 empty] | 4455 | VTL Load Sensor Status Error | 0 | 45
[13 empty] | 4456 | VTL Gain Hyst Err Detected | 0 | 45
[13 empty] | 4457 | High wind TYCNotOk : __._ m/s | 0 | 45
[13 empty] | 4458 | High windspeed fast: __._ m/s | 0 | 45
[13 empty] | 4459 | HighWindSpd,FlowTestSeqAborted | 0 | 45
[13 empty] | 4460 | BladeB: HighWindSpdTestAborted | 0 | 45
[13 empty] | 4461 | BladeC: HighWindSpdTestAborted | 0 | 45
[13 empty] | 4462 | Nacelle temp too low: ___ °C | 0 | 45
[13 empty] | 4463 | NacelleHeating fan1 neg FB err | 0 | 45
[13 empty] | 4464 | NacelleHeating fan2 neg FB err | 0 | 45
[13 empty] | 4465 | NacelleHeating fan1 pos FB err | 0 | 45
[13 empty] | 4466 | NacelleHeating fan2 pos FB err | 0 | 45
[13 empty] | 4467 | Tower cooling fan 1 error | 0 | 45
[13 empty] | 4468 | Tower cooling fan 2 error | 0 | 45
[13 empty] | 4469 | Tower cooling fan 3 error | 0 | 45
[13 empty] | 4470 | Tower cooling fan 4 error | 0 | 45
[13 empty] | 4471 | Tower cooling fan 5 error | 0 | 45
[13 empty] | 4472 | Tower cooling fan 6 error | 0 | 45
[13 empty] | 4473 | TowerAirFilter1 PartialCLogged | 0 | 45
[13 empty] | 4474 | TowerAirFilter2 PartialCLogged | 0 | 45
[13 empty] | 4475 | TowerAirFilter1 cLogged | 0 | 45
[13 empty] | 4476 | TowerAirFilter2 cLogged | 0 | 45
[13 empty] | 4477 | TowerAirFilter1 fully cLogged | 0 | 45
[13 empty] | 4478 | TowerAirFilter2 fully cLogged | 0 | 45
[13 empty] | 4479 | Nacelle hatch open error | 0 | 45
[13 empty] | 4480 | Nacelle hatch close error | 0 | 45
[13 empty] | 4481 | Tower hatch1 open error | 0 | 45
[13 empty] | 4482 | Tower hatch1 close error | 0 | 45
[13 empty] | 4483 | Tower hatch2 open error | 0 | 45
[13 empty] | 4484 | Tower hatch2 close error | 0 | 45
[13 empty] | 4485 | Nacelle heating fan1 CB opened | 0 | 45
[13 empty] | 4486 | Nacelle heating fan2 CB opened | 0 | 45
[13 empty] | 4487 | Tower cooling fan1 CB opened | 0 | 45
[13 empty] | 4488 | Tower cooling fan2 CB opened | 0 | 45
[13 empty] | 4489 | Tower cooling fan3 CB opened | 0 | 45
[13 empty] | 4490 | Tower cooling fan4 CB opened | 0 | 45
[13 empty] | 4491 | Tower cooling fan5 CB opened | 0 | 45
[13 empty] | 4492 | Tower cooling fan6 CB opened | 0 | 45
[13 empty] | 4493 | TurbineHeatingState: __ | 0 | 45
[13 empty] | 4494 | TurbineCoolingState: __ | 0 | 45
[13 empty] | 4495 | SafetyCircuit Unexpected Open | 0 | 45
[13 empty] | 4496 | PitA: PBL max: ___ min:__ | 0 | 45
[13 empty] | 4497 | PitB: PBL max: ___ min:__ | 0 | 45
[13 empty] | 4498 | PitC: PBL max: ___ min:__ | 0 | 45
[13 empty] | 4499 | Pitch B too low: __._° < __._° | 0 | 45
[13 empty] | 4500 | Pitch C too low: __._° < __._° | 1 | 28
[13 empty] | 4502 | PitA:PFBOpen:_CountEnabl,__._° | 0 | 45
[13 empty] | 4503 | PitB:PFBOpen:_CountEnabl,__._° | 0 | 45
[13 empty] | 4504 | PitC:PFBOpen:_CountEnabl,__._° | 0 | 45
[13 empty] | 4505 | PitA:PBLOpen:_CountEnabl,__._° | 0 | 45
[13 empty] | 4506 | PitB:PBLOpen:_CountEnabl,__._° | 0 | 45
[13 empty] | 4507 | PitC:PBLOpen:_CountEnabl,__._° | 0 | 45
[13 empty] | 4508 | HubSafty Saf Pitch Req I/P Err | 0 | 45
[13 empty] | 4509 | HubSafty EmgStpHubIO I/P Err. | 0 | 45
[13 empty] | 4510 | HubSafty EmgStpHubPnl I/P Err. | 0 | 45
[13 empty] | 4511 | HubSafty HubServ Req I/P Err. | 0 | 45
[13 empty] | 4512 | HubSafty HydrPres Draind-BldA | 0 | 45
[13 empty] | 4513 | HubSafty HydrPres Draind-BldB | 0 | 45
[13 empty] | 4514 | HubSafty HydrPres Draind-BldC | 0 | 45
[13 empty] | 4515 | HubSafty HydrPres Draind DBlk | 0 | 45
[13 empty] | 4516 | HubSafty HydrPres Low BldA | 0 | 45
[13 empty] | 4517 | HubSafty HydrPres Low BldB | 0 | 45
[13 empty] | 4518 | HubSafty HydrPres Low BldC | 0 | 45
[13 empty] | 4519 | HubSafty HydrPres Low DBlk | 0 | 45
[13 empty] | 4520 | HubSafty Ball Vlv A Open Err. | 0 | 45
[13 empty] | 4521 | HubSafty Ball Vlv A Close Err. | 0 | 45
[13 empty] | 4522 | HubSafty Ball Vlv B Open Err. | 0 | 45
[13 empty] | 4523 | HubSafty Ball Vlv B Close Err. | 0 | 45
[13 empty] | 4524 | HubSafty Ball Vlv C Open Err. | 0 | 45
[13 empty] | 4525 | HubSafty Ball Vlv C Close Err. | 0 | 45
[13 empty] | 4526 | FEXLowPressure or bypassed | 0 | 45
[13 empty] | 4527 | OvrspdGuardRotorSpeedExtrHigh | 0 | 45
[13 empty] | 4528 | OvrspdGuardExpectedActivated | 0 | 45
[13 empty] | 4530 | SafetySysProt. Stop SignalFail | 0 | 45
[13 empty] | 4531 | Converter LSI insulation error | 0 | 45
[13 empty] | 4532 | Conv. LSI Pos SPD fuse L1 trip | 0 | 45
[13 empty] | 4533 | Conv. LSI Neg SPD fuse L1 trip | 0 | 45
[13 empty] | 4534 | Conv. LSI Pos SPD fuse L2 trip | 0 | 45
[13 empty] | 4535 | Conv. LSI Neg SPD fuse L2 trip | 0 | 45
[13 empty] | 4536 | Conv. LSI Pos SPD fuse L3 trip | 0 | 45
[13 empty] | 4537 | Conv. LSI Neg SPD fuse L3 trip | 0 | 45
[13 empty] | 4538 | SafetySystem waiting for reset | 0 | 45
[13 empty] | 4539 | SafetySysHubUnknownResetRsn | 0 | 45
[13 empty] | 4540 | SafetySysNaceleUnknwnResetRsn | 0 | 45
[13 empty] | 4541 | LSI High Chopper IGBT Temp. | 0 | 45
[13 empty] | 4542 | MSI High Chopper IGBT Temp. | 0 | 45
[13 empty] | 4543 | LSITmpSwitchDCChopX:Mod_;___°C | 0 | 45
[13 empty] | 4544 | LSITmpSwitchDCChopY:Mod_;___°C | 0 | 45
[13 empty] | 4545 | LSI High Chopper Resistor Load | 0 | 45
[13 empty] | 4546 | MSI High Chopper Resistor Load | 0 | 45
[13 empty] | 4547 | Safety nac1 checksum:_____ | 0 | 45
[13 empty] | 4548 | Safety nac2 checksum:_____ | 0 | 45
[13 empty] | 4549 | Safety hub checksum:_____ | 0 | 45
[13 empty] | 4550 | SafetySysNac1 comm link error | 0 | 45
[13 empty] | 4551 | SafetySysNac2 comm link error | 0 | 45
[13 empty] | 4552 | SafetySysHub comm link error | 0 | 45
[13 empty] | 4553 | Conv Disconnect Failed | 0 | 45
[13 empty] | 4558 | BladeAEdgePeakLoad: ___.__ kNm | 0 | 45
[13 empty] | 4559 | BladeBEdgePeakLoad: ___.__ kNm | 0 | 45
[13 empty] | 4560 | BladeCEdgePeakLoad: ___.__ kNm | 1 | 28
[13 empty] | 4561 | MSI Hi Chopper Wire Temp ___°C | 0 | 45
[13 empty] | 4562 | LSI Hi Chopper Wire Temp ___°C | 0 | 45
[13 empty] | 4563 | Deicing cycle aborted by SCADA | 0 | 45
[13 empty] | 4564 | Lubr offline pump neg. FB err | 0 | 45
[13 empty] | 4565 | Lubr offline pump pos. FB err | 0 | 45
[13 empty] | 4566 | PTR ODM pump1 neg. FB err | 0 | 45
[13 empty] | 4567 | PTR ODM pump1 pos. FB err | 0 | 45
[13 empty] | 4568 | PTR ODM pump2 neg. FB err | 0 | 45
[13 empty] | 4569 | PTR ODM pump2 pos. FB err | 0 | 45
[13 empty] | 4570 | Lubr. oil heater neg. FB err | 0 | 45
[13 empty] | 4571 | Lubr. oil heater pos. FB err | 0 | 45
[13 empty] | 4572 | Lubr offline pump thermo fault | 0 | 45
[13 empty] | 4573 | PTR ODM pump1 thermo fault | 0 | 45
[13 empty] | 4574 | PTR ODM pump2 thermo fault | 0 | 45
[13 empty] | 4575 | Lubr. offline pump CB opened | 0 | 45
[13 empty] | 4576 | PTR ODM pump1 CB opened | 0 | 45
[13 empty] | 4577 | PTR ODM pump2 CB opened | 0 | 45
[13 empty] | 4578 | Lubr. oil heater CB opened | 0 | 45
[13 empty] | 4592 | Conv MSI Neutral SPD fuse trip | 0 | 45
[13 empty] | 4593 | ValidateEMCPitchValvesTestFail | 0 | 45
[13 empty] | 4594 | ConnTransTimeOut__s,MSCState__ | 0 | 45
[13 empty] | 4595 | ConnTransTimeOut__s,MSCState__ | 0 | 45
[13 empty] | 4596 | RundownTimeout___s,____RPM | 0 | 45
[13 empty] | 4597 | GenSideBreakResetErr Module__ | 0 | 45
[13 empty] | 4598 | GenSideBreakerWindUpFailed | 0 | 45
[13 empty] | 4599 | LineSideBreakerWindUpFailed | 0 | 45
[13 empty] | 4600 | Missing Grid Choke Fan feedb. | 0 | 45
[13 empty] | 4601 | UDC ____ LowToClose GenBreaker | 0 | 45
[13 empty] | 4602 | YawBrakesCBOpen | 0 | 45
[13 empty] | 4603 | Yaw Brake Resistor Overheated | 0 | 45
[13 empty] | 4604 | Remote Pow=0,Reactive possible | 0 | 45
[13 empty] | 4605 | PrepReconLSOtime,__m/s____rpm | 0 | 45
[13 empty] | 4606 | RunUpLSOtimeout,__m/s ____rpm | 0 | 45
[13 empty] | 4607 | PrepProdEntry, Derate ____rpm | 0 | 45
[13 empty] | 4608 | PrepProdExit, InState _____s | 0 | 45
[13 empty] | 4609 | FrtDetect: Volt___%,Time__.__s | 0 | 45
[13 empty] | 4610 | FrtDetect: Volt___%,Time__.__s | 0 | 45
[13 empty] | 4611 | Reactive pow. derated by:_.__ | 0 | 45
[13 empty] | 4612 | Reactive pow. derated by:_.__ | 0 | 45
[13 empty] | 4615 | VPC board IntSW Warning __:__ | 0 | 45
[13 empty] | 4616 | VPC board IntSW Warning __:__ | 0 | 45
[13 empty] | 4617 | UDC Discharge Failed | 0 | 45
[13 empty] | 4618 | TNF Test Interrupted | 0 | 45
[13 empty] | 4619 | Tower Frequency Test Activated | 0 | 45
[13 empty] | 4620 | GenMainContactorFBError | 0 | 45
[13 empty] | 4621 | GenDeltaModeContactFBError | 0 | 45
[13 empty] | 4622 | GenStarModeContactFBError | 0 | 45
[13 empty] | 4623 | ChargeContactorFBError | 0 | 45
[13 empty] | 4624 | GridInverterContactorFBError | 0 | 45
[13 empty] | 4625 | EMCPitchValvesTestFailed | 0 | 45
[13 empty] | 4626 | YawLubr bearing pump 1 | 0 | 45
[13 empty] | 4627 | YawLubr bearing pump 2 | 0 | 45
[13 empty] | 4628 | YawLubr bearing error | 0 | 45
[13 empty] | 4629 | YawLubrBearing Req:_ OkPumps:_ | 0 | 45
[13 empty] | 4630 | YawLubr ring pump 1 | 0 | 45
[13 empty] | 4631 | YawLubr ring pump 2 | 0 | 45
[13 empty] | 4632 | YawLubr ring error | 0 | 45
[13 empty] | 4633 | YawLubrRing Req:_ OkPumps:_ | 0 | 45
[13 empty] | 4634 | LSI_InverterRI_GIOutOffPWMSync | 0 | 45
[13 empty] | 4635 | MSI_InverterRI_GIOutOffPWMSync | 0 | 45
[13 empty] | 4636 | TempSwitch_GridFilter | 0 | 45
[13 empty] | 4637 | MSI HighTempGradient InvIGBT X | 0 | 45
[13 empty] | 4638 | MSI HighTempGradient InvIGBT Y | 0 | 45
[13 empty] | 4639 | LSI HighTempGradient InvIGBT X | 0 | 45
[13 empty] | 4640 | LSI HighTempGradient InvIGBT Y | 0 | 45
[13 empty] | 4641 | MSI Low Rotor Flux | 0 | 45
[13 empty] | 4642 | LSI High DC Cable Impedance | 0 | 45
[13 empty] | 4643 | MSI High Current Generator | 0 | 45
[13 empty] | 4644 | PowerBackupChargerDisconnected | 0 | 45
[13 empty] | 4645 | PowerBackupCharger CapacityLow | 0 | 45
[13 empty] | 4646 | PowerBackupCharger Error | 0 | 45
[13 empty] | 4647 | PowerBackupCharger State | 0 | 45
[13 empty] | 4648 | SmokeDetectorErrDuringService | 0 | 45
[13 empty] | 4649 | ConvLSI InsulationDetectorErr | 0 | 45
[13 empty] | 4650 | TowerWaterCoolLiquidLo___l | 0 | 45
[13 empty] | 4651 | BladeVibrSigStatus Low_ High_ | 0 | 45
[13 empty] | 4652 | BladeVibrationHigh | 0 | 45
[13 empty] | 4656 | NacWaterCoolPumpsNotFunctional | 0 | 45
[13 empty] | 4657 | NacWaterCoolLiquidLo___l | 0 | 45
[13 empty] | 4658 | MFun TerminateTimeout, Seq:__ | 0 | 45
[13 empty] | 4659 | SafetySysNac checksum err_____ | 0 | 45
[13 empty] | 4660 | SafetySysHub checksum err_____ | 0 | 45
[13 empty] | 4661 | SafetySysNac checksum err_____ | 0 | 45
[13 empty] | 4662 | SafetSysTransPieceCsumErr_____ | 0 | 45
[13 empty] | 4663 | SafetySysNac comm error | 0 | 45
[13 empty] | 4664 | SafetySysHub comm error | 0 | 45
[13 empty] | 4665 | SafetySysTower comm error | 0 | 45
[13 empty] | 4666 | SafetySysTransPiece comm error | 0 | 45
[13 empty] | 4667 | HighMSCPowerDeviation | 0 | 45
[13 empty] | 4668 | HydrPilotPressDiffHigh:___ bar | 0 | 45
[13 empty] | 4669 | PitchBlockACommonLow: ___ bar | 0 | 45
[13 empty] | 4670 | PitchBlockBCommonLow: ___ bar | 0 | 45
[13 empty] | 4671 | PitchBlockCCommonLow: ___ bar | 0 | 45
[13 empty] | 4672 | PitchBlockACylinderLeak:___bar | 0 | 45
[13 empty] | 4673 | PitchBlockBCylinderLeak:___bar | 0 | 45
[13 empty] | 4674 | PitchBlockCCylinderLeak:___bar | 0 | 45
[13 empty] | 4675 | FastRelTrans:__MaxRotSpd__RPM | 0 | 45
[13 empty] | 4676 | PitchAlignTrans___,Monitor___ | 0 | 45
[13 empty] | 4677 | CabinetTowerAuxPowerTemp High | 0 | 45
[13 empty] | 4678 | CabinetTowerAuxPowerTemp Low | 0 | 45
[13 empty] | 4679 | CabinetNacAuxDCPowerTempHigh | 0 | 45
[13 empty] | 4680 | CabinetNacAuxDCPowerTempLow | 0 | 45
[13 empty] | 4681 | CabinetTowerControllerTempHigh | 0 | 45
[13 empty] | 4682 | CabinetTowerControllerTemp Low | 0 | 45
[13 empty] | 4683 | CabinetTowTransPieceCtrTmpHigh | 0 | 45
[13 empty] | 4684 | CabinetTowTransPieceCtrlTmpLow | 0 | 45
[13 empty] | 4685 | CabinetNacControllerTemp High | 0 | 45
[13 empty] | 4686 | CabinetNacControllerTemp Low | 0 | 45
[13 empty] | 4687 | CabinetHubControllerTemp High | 0 | 45
[13 empty] | 4688 | CabinetHubControllerTemp Low | 0 | 45
[13 empty] | 4692 | PistonPosAPreset:___mm | 0 | 45
[13 empty] | 4693 | PistonPosBPreset:___mm | 0 | 45
[13 empty] | 4694 | PistonPosCPreset:___mm | 0 | 45
[13 empty] | 4696 | LowTemp_DCChopperRes_X | 0 | 45
[13 empty] | 4697 | LowTemp_DCChopperRes_Y | 0 | 45
[13 empty] | 4698 | LSI_LowTemp_GridChoke | 0 | 45
[13 empty] | 4699 | LSI_LowTemp_GridFilSectAir | 0 | 45
[13 empty] | 4700 | LowTemp_DCChopperRes_X | 0 | 45
[13 empty] | 4701 | Tower cooling M1 fan CB opened | 0 | 45
[13 empty] | 4702 | Tower cooling M2 fan CB opened | 0 | 45
[13 empty] | 4703 | Tower cooling M3 fan CB opened | 0 | 45
[13 empty] | 4704 | Tower cooling M4 fan CB opened | 0 | 45
[13 empty] | 4705 | Tower cooling M1 fan error | 0 | 45
[13 empty] | 4706 | Tower cooling M2 fan error | 0 | 45
[13 empty] | 4707 | Tower cooling M3 fan error | 0 | 45
[13 empty] | 4708 | Tower cooling M4 fan error | 0 | 45
[13 empty] | 4709 | TwrCool M1 filter cLogged | 0 | 45
[13 empty] | 4710 | TwrCool M2 filter cLogged | 0 | 45
[13 empty] | 4711 | TwrCool M3 filter cLogged | 0 | 45
[13 empty] | 4712 | TwrCool M4 filter cLogged | 0 | 45
[13 empty] | 4713 | TwrCool M1 filter PartialCLog | 0 | 45
[13 empty] | 4714 | TwrCool M2 filter PartialCLog | 0 | 45
[13 empty] | 4715 | TwrCool M3 filter PartialCLog | 0 | 45
[13 empty] | 4716 | TwrCool M4 filter PartialCLog | 0 | 45
[13 empty] | 4717 | Twr cooling M1 hatch close err | 0 | 45
[13 empty] | 4718 | Twr cooling M2 hatch close err | 0 | 45
[13 empty] | 4719 | Twr cooling M3 hatch close err | 0 | 45
[13 empty] | 4720 | Twr cooling M4 hatch close err | 0 | 45
[13 empty] | 4721 | Twr cooling M1 hatch open err | 0 | 45
[13 empty] | 4722 | Twr cooling M2 hatch open err | 0 | 45
[13 empty] | 4723 | Twr cooling M3 hatch open err | 0 | 45
[13 empty] | 4724 | Twr cooling M4 hatch open err | 0 | 45
[13 empty] | 4725 | AutoTNFReachedMaxRetry | 0 | 45
[13 empty] | 4726 | BladeLoads calibrated manually | 0 | 45
[13 empty] | 4727 | BladeLoads calib pitching fail | 0 | 45
[13 empty] | 4728 | BladeLoads calibration started | 0 | 45
[13 empty] | 4729 | BladeLoads calibration stopped | 0 | 45
[13 empty] | 4730 | IceDetectPostCycleRun | 0 | 45
[13 empty] | 4731 | OperatorPostCycleRun | 0 | 45
[13 empty] | 4732 | IceDetectPostCyclePause | 0 | 45
[13 empty] | 4733 | OperatorPostCyclePause | 0 | 45
[13 empty] | 4734 | PilotValvesTestP2V1Failure | 0 | 45
[13 empty] | 4735 | PilotValvesTestP2V2Failure | 0 | 45
[13 empty] | 4736 | PilotValvesTestPilot1Fail | 0 | 45
[13 empty] | 4737 | PilotValvesTestPilot2Fail | 0 | 45
[13 empty] | 4738 | HydrSystemPressSensorFail | 0 | 45
[13 empty] | 4739 | HydrPilotPressSensor1Fail | 0 | 45
[13 empty] | 4740 | HydrPilotPressSensor2Fail | 0 | 45
[13 empty] | 4742 | LSI FanThermoRelayError | 0 | 45
[13 empty] | 4743 | MSI FanThermoRelayError | 0 | 45
[13 empty] | 4749 | Pwr backup charger module err | 0 | 45
[13 empty] | 4750 | Pwr backup charger err | 0 | 45
[13 empty] | 4751 | PwrBkup charger test started | 0 | 45
[13 empty] | 4752 | PwrBkup charger test finish | 0 | 45
[13 empty] | 4757 | Aviation equipment error | 0 | 45
[13 empty] | 4758 | Marine equipment error | 0 | 45
[13 empty] | 4759 | Quantification b__ PitchDist__ | 0 | 45
[13 empty] | 4761 | ExternFastGridDisconnectAlarm | 0 | 45
[13 empty] | 4762 | OutOfMemory | 0 | 45
[13 empty] | 4763 | NtpSyncError | 0 | 45
[13 empty] | 4764 | SafetySysHub chksum error_____ | 0 | 45
[13 empty] | 4765 | SafetySysTower chksum err_____ | 0 | 45
[13 empty] | 4766 | SafetSysTransPieceCsumErr_____ | 0 | 45
[13 empty] | 4767 | SafetySystemNac comm error | 0 | 45
[13 empty] | 4768 | Trafo leakage ___ °C ___mbar | 0 | 45
[13 empty] | 4769 | Estop Button Hub Activated__ | 0 | 45
[13 empty] | 4770 | Nac1ControllerProcessorBattLow | 0 | 45
[13 empty] | 4771 | Nac2ControllerProcessorBattLow | 0 | 45
[13 empty] | 4772 | Hub1ControllerProcessorBattLow | 0 | 45
[13 empty] | 4773 | Hub2ControllerProcessorBattLow | 0 | 45
[13 empty] | 4774 | ConMSINegContrProcessorBattLow | 0 | 45
[13 empty] | 4775 | ConMSIPosContrProcessorBattLow | 0 | 45
[13 empty] | 4776 | ConLSINegContrProcessorBattLow | 0 | 45
[13 empty] | 4777 | ConLSIPosContrProcessorBattLow | 0 | 45
[13 empty] | 4778 | Smoke Detector Version | 0 | 45
[13 empty] | 4779 | Smoke Detector Evolution | 0 | 45
[13 empty] | 4780 | SmokeDetectServiceInspPrformed | 0 | 45
[13 empty] | 4781 | SmokeDetectSmokeInspPerformed | 0 | 45
[13 empty] | 4782 | SmokeDetectMaintenancModeEnter | 0 | 45
[13 empty] | 4783 | SmokeDetectMaintenancModeLeave | 0 | 45
[13 empty] | 4784 | Smoke Detector System Error | 0 | 45
[13 empty] | 4785 | SmokeDetectorConfigurationErr | 0 | 45
[13 empty] | 4786 | Smoke Detector In Maintenance | 0 | 45
[13 empty] | 4787 | SmokeDetectCommissioningErr | 0 | 45
[13 empty] | 4788 | SmokeDetectLockedForInspect _ | 0 | 45
[13 empty] | 4789 | SmokeDetectProdNotAllowed | 0 | 45
[13 empty] | 4790 | Smoke Detected | 0 | 45
[13 empty] | 4791 | SmokeDetectorDiscoveryBusFail | 0 | 45
[13 empty] | 4792 | Smoke Detector Sensor Error | 0 | 45
[13 empty] | 4793 | Smoke Detector Sensor Soiled | 0 | 45
[13 empty] | 4794 | Smoke Detector Pollution | 0 | 45
[13 empty] | 4795 | StringStateTransitionTimeout | 0 | 45
[13 empty] | 4796 | MSIStateTransitionTimeout | 0 | 45
[13 empty] | 4797 | SafetySysHubChecksumError_____ | 0 | 45
[13 empty] | 4798 | SafetySysTowChecksumError_____ | 0 | 45
[13 empty] | 4799 | HydrPump1Failing | 0 | 45
[13 empty] | 4800 | HydrPump2Failing | 0 | 45
[13 empty] | 4801 | HydrPump3Failing | 0 | 45
[13 empty] | 4802 | HydrPump1Leakage | 0 | 45
[13 empty] | 4803 | HydrPump2Leakage | 0 | 45
[13 empty] | 4804 | HydrPump3Leakage | 0 | 45
[13 empty] | 4805 | SafetySysHub comm error | 0 | 45
[13 empty] | 4806 | SafetySysHubChecksumError_____ | 0 | 45
[13 empty] | 4807 | SafetySysHubChecksumError_____ | 0 | 45
[13 empty] | 4808 | SafetySysNac1 comm error | 0 | 45
[13 empty] | 4809 | SafetySysNac1 ChksumError_____ | 0 | 45
[13 empty] | 4810 | SafetySysNac1 ChksumError_____ | 0 | 45
[13 empty] | 4811 | SafetySysNac2 comm error | 0 | 45
[13 empty] | 4812 | SafetySysNac2 ChksumError_____ | 0 | 45
[13 empty] | 4813 | SafetySysNac2 ChksumError_____ | 0 | 45
[13 empty] | 4814 | SubSyncResonance | 0 | 45
[13 empty] | 4815 | PFB A azim state _, count ___ | 0 | 45
[13 empty] | 4816 | PFB B azim state _, count ___ | 0 | 45
[13 empty] | 4817 | PFB C azim state _, count ___ | 0 | 45
[13 empty] | 4818 | Prop valves unavailable A | 0 | 45
[13 empty] | 4819 | Prop valves unavailable B | 0 | 45
[13 empty] | 4820 | Prop valves unavailable C | 0 | 45
[13 empty] | 4821 | Prop Valve Status Error A1 | 0 | 45
[13 empty] | 4822 | Prop Valve Status Error A2 | 0 | 45
[13 empty] | 4823 | Prop Valve Status Error B1 | 0 | 45
[13 empty] | 4824 | Prop Valve Status Error B2 | 0 | 45
[13 empty] | 4825 | Prop Valve Status Error C1 | 0 | 45
[13 empty] | 4826 | Prop Valve Status Error C2 | 0 | 45
[13 empty] | 4827 | PValve A1 Act:_.___Ref:_.___ | 0 | 45
[13 empty] | 4828 | PValve A2 Act:_.___Ref:_.___ | 0 | 45
[13 empty] | 4829 | PValve B1 Act:_.___Ref:_.___ | 0 | 45
[13 empty] | 4830 | PValve B2 Act:_.___Ref:_.___ | 0 | 45
[13 empty] | 4831 | PValve C1 Act:_.___Ref:_.___ | 0 | 45
[13 empty] | 4832 | PValve C2 Act:_.___Ref:_.___ | 0 | 45
[13 empty] | 4833 | High OVRT VoltageLimitDetected | 0 | 45
[13 empty] | 4834 | WarnRiseDetected | 0 | 45
[13 empty] | 4835 | ConvLSIPos InsulationLevel2Err | 0 | 45
[13 empty] | 4836 | ConvLSINeg InsulationLevel2Err | 0 | 45
[13 empty] | 4837 | RotorAzimuthAngle Invalid | 0 | 45
[13 empty] | 4838 | BLCalibAbortNoSensorBSignal | 0 | 45
[13 empty] | 4839 | BLCalibAbortNoSensorCSignal | 0 | 45
[13 empty] | 4840 | BLCalibCompletedWithFailure | 0 | 45
[13 empty] | 4841 | DCOnTimeOut | 0 | 45
[13 empty] | 4842 | Towr cool ducted fan CB opened | 0 | 45
[13 empty] | 4843 | Tower cooling ducted fan error | 0 | 45
[13 empty] | 4844 | Tower cool M1 fan neg. FB err. | 0 | 45
[13 empty] | 4845 | Tower cool M1 fan pos. FB err. | 0 | 45
[13 empty] | 4846 | Tower cool M2 fan neg. FB err. | 0 | 45
[13 empty] | 4847 | Tower cool M2 fan pos. FB err. | 0 | 45
[13 empty] | 4848 | Tower cool M3 fan neg. FB err. | 0 | 45
[13 empty] | 4849 | Tower cool M3 fan pos. FB err. | 0 | 45
[13 empty] | 4850 | Tower cool M4 fan neg. FB err. | 0 | 45
[13 empty] | 4851 | Tower cool M4 fan pos. FB err. | 0 | 45
[13 empty] | 4852 | TowerCool DuctedFan neg FB err | 0 | 45
[13 empty] | 4853 | TowerCool DuctedFan pos FB err | 0 | 45
[13 empty] | 4854 | BLS Frozen IO Signal | 0 | 45
[13 empty] | 4855 | BLS IO Signal Out of Range | 0 | 45
[13 empty] | 4856 | BLS High IO Signal Fluctuation | 0 | 45
[13 empty] | 4857 | BLS Axial Force Deviation | 0 | 45
[13 empty] | 4858 | BLS All Sensors Not Calibrated | 0 | 45
[13 empty] | 4859 | BLS BladeA Edge Not Calibrated | 0 | 45
[13 empty] | 4860 | BLS BladeA Flap Not Calibrated | 0 | 45
[13 empty] | 4861 | BLS BladeB Edge Not Calibrated | 0 | 45
[13 empty] | 4862 | BLS BladeB Flap Not Calibrated | 0 | 45
[13 empty] | 4863 | BLS BladeC Edge Not Calibrated | 0 | 45
[13 empty] | 4864 | BLS BladeC Flap Not Calibrated | 0 | 45
[13 empty] | 4865 | BLS Azimuth Error | 0 | 45
[13 empty] | 4866 | BladeRingPosAOffset:___mm | 0 | 45
[13 empty] | 4867 | BladeRingPosBOffset:___mm | 0 | 45
[13 empty] | 4868 | BladeRingPosCOffset:___mm | 0 | 45
[13 empty] | 4869 | PitchRingAngleAOffset:__._° | 0 | 45
[13 empty] | 4870 | PitchRingAngleBOffset:__._° | 0 | 45
[13 empty] | 4871 | PitchRingAngleCOffset:__._° | 0 | 45
[13 empty] | 4872 | BladeRingPosAPreset:___mm | 0 | 45
[13 empty] | 4873 | BladeRingPosBPreset:___mm | 0 | 45
[13 empty] | 4874 | BladeRingPosCPreset:___mm | 0 | 45
[13 empty] | 4875 | HVCB tripped by SCADA | 0 | 45
[13 empty] | 4876 | HubSafetySystem EncoderA,EC:_ | 0 | 45
[13 empty] | 4877 | HubSafetySystem EncoderB,EC:_ | 0 | 45
[13 empty] | 4878 | HubSafetySystem EncoderC,EC:_ | 0 | 45
[13 empty] | 4879 | SaftySystem Nacelle Comm Err. | 0 | 45
[13 empty] | 4880 | SaftySystem Hub Comm Err. | 0 | 45
[13 empty] | 4882 | Derate<MinStatSpd: ____rpm, _ | 0 | 45
[13 empty] | 4885 | TurnerGearEngaged:Pos1:_Pos2:_ | 0 | 45
[13 empty] | 4886 | TurnerGearPosSensorMismatch | 0 | 45
[13 empty] | 4887 | NacWaterCoolPump1Failing:__bar | 0 | 45
[13 empty] | 4888 | NacWaterCoolPump2Failing:__bar | 0 | 45
[13 empty] | 4889 | Pitch A Pist:__._°,Ring:__._° | 0 | 45
[13 empty] | 4890 | Pitch B Pist:__._°,Ring:__._° | 0 | 45
[13 empty] | 4891 | Pitch C Pist:__._°,Ring:__._° | 0 | 45
[13 empty] | 4892 | SafetSysBladeEncCalibActiveEC_ | 0 | 45
[13 empty] | 4893 | Yaw lubr bear pump1 completed | 0 | 45
[13 empty] | 4894 | Yaw lubr bear pump2 completed | 0 | 45
[13 empty] | 4895 | Yaw lubr ring pump1 completed | 0 | 45
[13 empty] | 4896 | Yaw lubr ring pump2 completed | 0 | 45
[13 empty] | 4897 | StarDeltaTimeout,__m/s____rpm | 0 | 45
[13 empty] | 4898 | BladeA Heaters are Over Heated | 0 | 45
[13 empty] | 4899 | BladeB Heaters are Over Heated | 0 | 45
[13 empty] | 4900 | BladeC Heaters are Over Heated | 0 | 45
[13 empty] | 4901 | Yaw SignalError. _____,_____ | 0 | 45
[13 empty] | 4902 | Gen SignalError. _____,_____ | 0 | 45
[13 empty] | 4903 | Gear SignalError. _____,_____ | 0 | 45
[13 empty] | 4904 | Conv SignalError. _____,_____ | 0 | 45
[13 empty] | 4905 | Hydr SignalError. _____,_____ | 0 | 45
[13 empty] | 4906 | WatrCoolingSigErr._____,_____ | 0 | 45
[13 empty] | 4907 | NacelleSignalError._____,_____ | 0 | 45
[13 empty] | 4908 | Wind SignalError. _____,_____ | 0 | 45
[13 empty] | 4909 | Trafo SignalError. _____,_____ | 0 | 45
[13 empty] | 4910 | SafetySignalError. _____,_____ | 0 | 45
[13 empty] | 4911 | ArcLightDetSigErr._____,_____ | 0 | 45
[13 empty] | 4912 | GenRPM SigError._____,_____ | 0 | 45
[13 empty] | 4913 | GenSlipRingSigError_____,_____ | 0 | 45
[13 empty] | 4914 | MainShaftSigError._____,_____ | 0 | 45
[13 empty] | 4915 | HydrPressSigError._____,_____ | 0 | 45
[13 empty] | 4916 | Yaw Lubr SigError._____,_____ | 0 | 45
[13 empty] | 4917 | RotorTachSpdSigErr._____,_____ | 0 | 45
[13 empty] | 4918 | ShockSensorSigErr._____,_____ | 0 | 45
[13 empty] | 4919 | ProdCtrlPwrSigErr._____,_____ | 0 | 45
[13 empty] | 4920 | Helihoist active | 0 | 45
[13 empty] | 4921 | Helihoist mode inactive | 0 | 45
[13 empty] | 4922 | Helihoist mode prepare | 0 | 45
[13 empty] | 4923 | Helihoist mode active | 0 | 45
[13 empty] | 4924 | User defined alarm 2__ | 0 | 45
[13 empty] | 4925 | User defined alarm 2__ | 0 | 45
[13 empty] | 4926 | User defined alarm 2__ | 0 | 45
[13 empty] | 4927 | User defined alarm 2__ | 0 | 45
[13 empty] | 4928 | User defined alarm 1__ | 0 | 45
[13 empty] | 4929 | User defined alarm 1__ | 0 | 45
[13 empty] | 4930 | User defined alarm 1__ | 0 | 45
[13 empty] | 4931 | User defined alarm 1__ | 0 | 45
[13 empty] | 4932 | CPR Node ____ disconnected | 0 | 45
[13 empty] | 4933 | User defined alarm 2__ | 0 | 45
[13 empty] | 4934 | User defined alarm 2__ | 0 | 45
[13 empty] | 4935 | User defined alarm 2__ | 0 | 45
[13 empty] | 4936 | User defined alarm 2__ | 0 | 45
[13 empty] | 4937 | User defined alarm 1__ | 0 | 45
[13 empty] | 4938 | User defined alarm 1__ | 0 | 45
[13 empty] | 4939 | User defined alarm 1__ | 0 | 45
[13 empty] | 4940 | User defined alarm 1__ | 0 | 45
[13 empty] | 4941 | User defined alarm 2__ | 0 | 45
[13 empty] | 4942 | User defined alarm 2__ | 0 | 45
[13 empty] | 4943 | User defined alarm 2__ | 0 | 45
[13 empty] | 4944 | User defined alarm 2__ | 0 | 45
[13 empty] | 4945 | User defined alarm 1__ | 0 | 45
[13 empty] | 4946 | User defined alarm 1__ | 0 | 45
[13 empty] | 4947 | User defined alarm 1__ | 0 | 45
[13 empty] | 4948 | User defined alarm 1__ | 0 | 45
[13 empty] | 4949 | Grid QU Protection | 0 | 45
[13 empty] | 4950 | HighRotSpd FreezeInact Valves | 0 | 45
[13 empty] | 4951 | UserDefined IO invalid conf __ | 0 | 45
[13 empty] | 4952 | Yaw speed high __.__ °/sec | 0 | 45
[13 empty] | 4953 | Yaw speed too high | 0 | 45
[13 empty] | 4954 | NoCcommunicationToVID Alarm | 0 | 45
[13 empty] | 4955 | NoCcommunicationToVID Warning | 0 | 45
[13 empty] | 4956 | AliveSignal Alarm Error | 0 | 45
[13 empty] | 4957 | AliveSignal Warning Error | 0 | 45
[13 empty] | 4958 | EvaluationSignal Alarm Error | 0 | 45
[13 empty] | 4959 | EvaluationSignal Warning Error | 0 | 45
[13 empty] | 4960 | WrongCommissioningInVID Alarm | 0 | 45
[13 empty] | 4961 | WrongCommissioningInVIDWarning | 0 | 45
[13 empty] | 4962 | Calibration Warning | 0 | 45
[13 empty] | 4963 | IceDetectedInBladeAutoAckAlarm | 0 | 45
[13 empty] | 4964 | IceDetectedInBlade Warning | 0 | 45
[13 empty] | 4965 | IceDetectedByVID | 0 | 45
[13 empty] | 4966 | IceDetectedBySCADA | 0 | 45
[13 empty] | 4967 | PitchCommonAccuPressLow | 0 | 45
[13 empty] | 4968 | EMFAccuPressLow: Blade _ | 0 | 45
[13 empty] | 4969 | Yaw movement while stopped | 0 | 45
[13 empty] | 4978 | Gen. magnet temp high___°C | 0 | 45
[13 empty] | 4979 | MPC max number of lost samples | 0 | 45
[13 empty] | 4980 | Yaw position sensor not moving | 0 | 45
[13 empty] | 4981 | Yaw direction wrong | 0 | 45
[13 empty] | 4982 | Cable twist signal error | 0 | 45
[13 empty] | 4983 | LSI_LOW_TEMP_IGBTX:Mod__,___°C | 0 | 45
[13 empty] | 4984 | LSI_LOW_TEMP_IGBTY:Mod__,___°C | 0 | 45
[13 empty] | 4985 | MSI_LOW_TEMP_IGBTX:Mod__,___°C | 0 | 45
[13 empty] | 4986 | MSI_LOW_TEMP_IGBTY:Mod__,___°C | 0 | 45
[13 empty] | 4987 | GenSpd:__._RPM, Ref:____._ RPM | 0 | 45
[13 empty] | 5000 | GenLubrRetValve Error | 0 | 45
[13 empty] | 5001 | Slip:____ above limits _ | 1 | 28
[13 empty] | 5002 | GeneratorLubrCompleted | 0 | 45
[13 empty] | 5003 | GridFilterCap thermo sw open | 0 | 45
[13 empty] | 5004 | GridDrossel thermo sw open | 0 | 45
[13 empty] | 5005 | Blade loads calibration failed | 0 | 45
[13 empty] | 5006 | BladeLoadsCalib attempt failed | 0 | 45
[13 empty] | 5007 | ReplacePowerSurgeProtectorWarn | 0 | 45
[13 empty] | 5008 | IceDetected | 0 | 45
[13 empty] | 5009 | PowerDerateTimeExceeded | 0 | 45
[13 empty] | 5010 | SpeedDerateTimeExceeded | 0 | 45
[13 empty] | 5011 | BladeLoads auto calib. failed | 0 | 45
[13 empty] | 5012 | Active pow. derated by:_.__ | 0 | 45
[13 empty] | 5013 | BladeLoadSensorFaultDetected | 0 | 45
[13 empty] | 5014 | BladeLoadFaultDetected | 0 | 45
[13 empty] | 5015 | BladeLoadSystemNotCalibrated | 0 | 45
[13 empty] | 5016 | BladeLoadCalibrationExpired | 0 | 45
[13 empty] | 5017 | BladeLoadSensorSaturaDetected | 0 | 45
[13 empty] | 5018 | BladeLoadFrozenSensorDetected | 0 | 45
[13 empty] | 5019 | BladeLoadHighSensFluctuaDetect | 0 | 45
[13 empty] | 5020 | BladeALoadSensorNotCalibrated | 0 | 45
[13 empty] | 5021 | BladeBLoadSensorNotCalibrated | 0 | 45
[13 empty] | 5022 | BladeCLoadSensorNotCalibrated | 0 | 45
[13 empty] | 5023 | BladeLoadSensorCalibraExpired | 0 | 45
[13 empty] | 5024 | BladeLoadHardwareChangeDetect | 0 | 45
[13 empty] | 5025 | BladeLoadEstimatorDeviatDetect | 0 | 45
[13 empty] | 5027 | BladeLoadCalibratStateChange | 0 | 45
[13 empty] | 5028 | BladeLoadCalibrationFailReason | 0 | 45
[13 empty] | 5029 | BladeLoadCalibratManuallyReset | 0 | 45
[13 empty] | 5030 | BladeLoadCalibratManuallySet | 0 | 45
[13 empty] | 5031 | SideSideTwrDampTwrAccSenErr | 0 | 45
[13 empty] | 5032 | Aviation Equipment UPS Error | 0 | 45
[13 empty] | 5033 | SAR Light Feedback Error | 0 | 45
[13 empty] | 5035 | Test Pitch Axis:___ | 0 | 45
[13 empty] | 5036 | NacelleInletHatch open error | 0 | 45
[13 empty] | 5037 | NacelleInletHatch close error | 0 | 45
[13 empty] | 5038 | NacelleOutletHatch open error | 0 | 45
[13 empty] | 5039 | NacelleOutletHatch close error | 0 | 45
[13 empty] | 5040 | Nacelle fan error | 0 | 45
[13 empty] | 5041 | SideSideTwrDampRotPosSenErr | 0 | 45
[13 empty] | 5042 | Tower Conv 24V DC error | 0 | 45
[13 empty] | 5043 | Tower Conv 24V AC error | 0 | 45
[13 empty] | 5044 | Nacelle Conv 24V DC error | 0 | 45
[13 empty] | 5045 | Nacelle Conv 24V AC error | 0 | 45
[13 empty] | 5046 | External Noise Mode: __ | 0 | 45
[13 empty] | 5047 | Noise Mode Not Supported: __ | 0 | 45
[13 empty] | 5048 | External Noise Comm Status : _ | 0 | 45
[13 empty] | 5050 | NacSafeSysHydrPressReq I/P Err | 0 | 45
[13 empty] | 5051 | Pwr backup battery string err | 0 | 45
[13 empty] | 5052 | Pwr backup battery bank err | 0 | 45
[13 empty] | 5053 | TowAcc Whirl Frq P _.__ N _.__ | 0 | 45
[13 empty] | 5054 | TowAcc Whirl Frq P _.__ N _.__ | 0 | 45
[13 empty] | 5055 | Commanded pause slow | 0 | 45
[13 empty] | 5056 | Commanded pause fast | 0 | 45
[13 empty] | 5057 | Commanded stop slow | 0 | 45
[13 empty] | 5058 | Commanded stop fast | 0 | 45
[13 empty] | 5059 | Commanded emc alarm | 0 | 45
[13 empty] | 5060 | SideSideTowerDampingTestStart | 0 | 45
[13 empty] | 5061 | SideSideTowerDampingTestStop | 0 | 45
[13 empty] | 5062 | PowerBackupChargerStartError | 0 | 45
[13 empty] | 5063 | PowerBackupChargerStopError | 0 | 45
[13 empty] | 5064 | SafetySysTowerChksumErr_____ | 0 | 45
[13 empty] | 5065 | SafetySysTowerChksumError_____ | 0 | 45
[13 empty] | 5066 | Rotor Left Locked | 0 | 45
[13 empty] | 5067 | Pitch pos A meas. signal fault | 1 | 28
[13 empty] | 5068 | Pitch pos B meas. signal fault | 0 | 45
[13 empty] | 5069 | Pitch pos C meas. signal fault | 1 | 28
[13 empty] | 5070 | SaftySystem Tower Comm Err. | 0 | 45
[13 empty] | 5072 | BladeLoadCalibrationDataSaved | 0 | 45
[13 empty] | 5076 | Azimuth Reset Miss: Rev __ | 0 | 45
[13 empty] | 5077 | SSTD TestState:__ TestSeq:__ | 0 | 45
[13 empty] | 5079 | Transformer fan error | 0 | 45
[13 empty] | 5080 | TransfHatchActuator1OpenErr | 0 | 45
[13 empty] | 5081 | TransfHatchActuator1CloseErr | 0 | 45
[13 empty] | 5084 | BladeLoadHighTxCurrent | 0 | 45
[13 empty] | 5085 | BladeLoadHighTxCurrentDetected | 0 | 45
[13 empty] | 5086 | ConvGenWaterCoolingPumpState | 0 | 45
[13 empty] | 5087 | ConvGenWaterCoolingHeaterState | 0 | 45
[13 empty] | 5088 | WaterLevelTooLowAlarm Error | 0 | 45
[13 empty] | 5089 | AliveSignal Alarm Error | 0 | 45
[13 empty] | 5090 | PumpCBOpened Warning Error | 0 | 45
[13 empty] | 5091 | HeaterCBOpened Warning Error | 0 | 45
[13 empty] | 5092 | SSTDpitchDisabledOnLowPress | 0 | 45
[13 empty] | 5093 | VCS Fan Reset | 0 | 45
[13 empty] | 5094 | BladeLoadDeviationDetected | 0 | 45
[13 empty] | 5095 | ConvChargeTrafo_Temp_switch | 0 | 45
[13 empty] | 5096 | ConvChargeSupervTimeout | 0 | 45
[13 empty] | 5097 | ConvConnectMMSupervTimeout | 0 | 45
[13 empty] | 5098 | ConvConnectSupervTimeout | 0 | 45
[13 empty] | 5099 | ConvCoolWaterHighTemp: ____°C | 0 | 45
[13 empty] | 5100 | ConvChargetrafoHiTemp: ____°C | 0 | 45
[13 empty] | 5101 | HiTempChokeWind:Mod__; ____°C | 0 | 45
[13 empty] | 5102 | LSCCircuitBreakHiTemp: ____°C | 0 | 45
[13 empty] | 5103 | LSCControlCabAirHiTemp: ____°C | 0 | 45
[13 empty] | 5104 | LSCControlCabAirLoTemp: ____°C | 0 | 45
[13 empty] | 5105 | LSC_DVDTFilt_TempSwitch:Mod__ | 0 | 45
[13 empty] | 5106 | LSC_Choke_TempSwitch:Mod__ | 0 | 45
[13 empty] | 5107 | MSC_DVDTFilt_TempSwitch:Mod__ | 0 | 45
[13 empty] | 5108 | MSC_Chopper_TempSwitch:Mod__ | 0 | 45
[13 empty] | 5109 | ConvDisconnectSupervTimeout | 0 | 45
[13 empty] | 5110 | DisableLSCCTRL__s,LSCState_ | 0 | 45
[13 empty] | 5111 | EnableLSCCTRL__s,LSCState_ | 0 | 45
[13 empty] | 5112 | ConvPrechargeSupervTimeout | 0 | 45
[13 empty] | 5113 | ConvPreconnectSupervTimeout | 0 | 45
[13 empty] | 5114 | ConvRundownStopSupervTimeout | 0 | 45
[13 empty] | 5115 | ConvRundownSupervTimeout | 0 | 45
[13 empty] | 5116 | SyncGridFilt__s,ScanLSCState_ | 0 | 45
[13 empty] | 5117 | DCLinkPrechargeErr___v,__s | 0 | 45
[13 empty] | 5118 | PrechargeVoltTimeout___v,__s | 0 | 45
[13 empty] | 5119 | Ext_SumCurrentILSC,Mod__ | 0 | 45
[13 empty] | 5120 | Ext_SumCurrentIMSC,Mod__ | 0 | 45
[13 empty] | 5121 | HiTempPrevCharge,Trafo___°C | 0 | 45
[13 empty] | 5122 | LowCurrGridFiltCheck:Mod__L_ | 0 | 45
[13 empty] | 5123 | LSCHarmFilterHiTemp:___°C | 0 | 45
[13 empty] | 5124 | LSCWTGAmbientHiTemp:___°C | 0 | 45
[13 empty] | 5125 | MSCChopResHiTemp:___°C | 0 | 45
[13 empty] | 5126 | LSCChopIGBTHiTemp:Mod_,__°C | 0 | 45
[13 empty] | 5127 | LSCIGBTGradHiTemp:Mod_,__°C | 0 | 45
[13 empty] | 5128 | LSCIGBTHiTemp:Mod_,___°C | 0 | 45
[13 empty] | 5129 | LSCIGBTLowTemp:Mod_,___°C | 0 | 45
[13 empty] | 5130 | LSCStackAirHiTemp:Mod_,___°C | 0 | 45
[13 empty] | 5131 | LSCTempSensorFail:id__,Mod_ | 0 | 45
[13 empty] | 5132 | LSC_ChopIGBT_HWError:Mod_ | 0 | 45
[13 empty] | 5133 | LSC_IGBT_HWError:Mod_ | 0 | 45
[13 empty] | 5134 | MSCChopIGBTHiTemp:Mod_,__°C | 0 | 45
[13 empty] | 5135 | MSCIGBTGradHiTemp:Mod_,__°C | 0 | 45
[13 empty] | 5136 | MSCIGBTHiTemp:Mod_,___°C | 0 | 45
[13 empty] | 5137 | MSCIGBTLowTemp:Mod_,___°C | 0 | 45
[13 empty] | 5138 | MSCStackAirHiTemp:Mod_,___°C | 0 | 45
[13 empty] | 5139 | MSCTempSensorFail:id__,Mod_ | 0 | 45
[13 empty] | 5140 | MSC_ChopIGBT_HWError:Mod_ | 0 | 45
[13 empty] | 5141 | MSC_IGBT_HWError:Mod_ | 0 | 45
[13 empty] | 5142 | WaterLevelTooLowAlarm Error | 0 | 45
[13 empty] | 5143 | AliveSignal Alarm Error | 0 | 45
[13 empty] | 5144 | PumpCBOpened Warning Error | 0 | 45
[13 empty] | 5145 | GearHydrWaterCoolingPumpState | 0 | 45
[13 empty] | 5146 | GenBearingTempSensorsFailed | 0 | 45
[13 empty] | 5147 | BladeLoadsCalibrAttemptFinish | 0 | 45
[13 empty] | 5148 | BladeLoadsCalibrAttemptStart | 0 | 45
[13 empty] | 5149 | NacelleHeater Pos Fb Err | 0 | 45
[13 empty] | 5150 | NacelleHeater Neg Fb Err | 0 | 45
[13 empty] | 5151 | NacelleHeater Signal Err | 0 | 45
[13 empty] | 5153 | GearOilHeaterCBOpened | 0 | 45
[13 empty] | 5154 | RI/GI Cheksum error once | 0 | 45
[13 empty] | 5155 | RI/GI Cheksum error persistent | 0 | 45
[13 empty] | 5156 | RI/GI Frozen communication | 0 | 45
[13 empty] | 5157 | NacelleFan1 Pos Fb Err | 0 | 45
[13 empty] | 5158 | NacelleFan1 Neg Fb Err | 0 | 45
[13 empty] | 5159 | NacelleFan2 Pos Fb Err | 0 | 45
[13 empty] | 5160 | NacelleFan2 Neg Fb Err | 0 | 45
[13 empty] | 5161 | NacelleFan1 Thermo Err | 0 | 45
[13 empty] | 5162 | NacelleFan2 Thermo Err | 0 | 45
[13 empty] | 5163 | HydrHighPressPmp1CB open err | 0 | 45
[13 empty] | 5164 | HydrHighPressPmp2CB open err | 0 | 45
[13 empty] | 5165 | Invalid Tower Sticker Checksum | 0 | 45
[13 empty] | 5166 | Max generator RPM: ____._ RPM | 0 | 45
[13 empty] | 5167 | Wind Direction Change Detected | 0 | 45
[13 empty] | 5168 | Low Press A TYC Off, ___._ bar | 0 | 45
[13 empty] | 5169 | Low Press B TYC Off, ___._ bar | 0 | 45
[13 empty] | 5170 | Low Press C TYC Off, ___._ bar | 0 | 45
[13 empty] | 5171 | PitchDevAtStop __._deg __._deg | 0 | 45
[13 empty] | 5172 | HubSafetyOptiStopConfig.Err __ | 0 | 45
[13 empty] | 5173 | Ext.ConverterRundownActive | 0 | 45
[13 empty] | 5174 | Rotor positioning released | 0 | 45
[13 empty] | 5175 | AutoDeicingMaxCountReached | 0 | 45
[13 empty] | 5176 | Fire Suppress prepare active | 0 | 45
[13 empty] | 5177 | Fire Suppress agent ignore | 0 | 45
[13 empty] | 5178 | Fire suppress agent release | 0 | 45
[13 empty] | 5179 | Fire cylinder1 gas level low | 0 | 45
[13 empty] | 5180 | Fire cylinder2 gas level low | 0 | 45
[13 empty] | 5181 | Fire cylinder3 gas level low | 0 | 45
[13 empty] | 5182 | Fire cylinder4 gas level low | 0 | 45
[13 empty] | 5183 | Fire cylinder5 gas level low | 0 | 45
[13 empty] | 5184 | Fire suppression cylinder1 err | 0 | 45
[13 empty] | 5185 | Fire suppression cylinder2 err | 0 | 45
[13 empty] | 5186 | Fire suppression cylinder3 err | 0 | 45
[13 empty] | 5187 | Fire suppression cylinder4 err | 0 | 45
[13 empty] | 5188 | Fire suppression cylinder5 err | 0 | 45
[13 empty] | 5189 | Fire suppression C1 discharged | 0 | 45
[13 empty] | 5190 | Fire suppression C2 discharged | 0 | 45
[13 empty] | 5191 | Fire suppression C3 discharged | 0 | 45
[13 empty] | 5192 | Fire suppression C4 discharged | 0 | 45
[13 empty] | 5193 | Fire suppression C5 discharged | 0 | 45
[13 empty] | 5194 | Auto Yaw Disabled | 0 | 45
[13 empty] | 5195 | Prop Valve A Status Fault | 0 | 45
[13 empty] | 5196 | Prop Valve B Status Fault | 1 | 28
[13 empty] | 5197 | Prop Valve C Status Fault | 5 | 15
[13 empty] | 5198 | Chopper capacity error | 0 | 45
[13 empty] | 5199 | Nacelle Temperature___°C | 0 | 45
[13 empty] | 5200 | Nacelle Temperature___°C | 0 | 45
[13 empty] | 5201 | Nacelle Temperature___°C | 0 | 45
[13 empty] | 5202 | VID calibrating | 0 | 45
[13 empty] | 5203 | Ice detected | 0 | 45
[13 empty] | 5204 | IceDetected | 0 | 45
[13 empty] | 5205 | Ice detector system error | 0 | 45
[13 empty] | 5206 | Ice detector sensor error | 0 | 45
[13 empty] | 5207 | VID MkVersion Mismatch | 0 | 45
[13 empty] | 5208 | VID MaxPower Mismatch | 0 | 45
[13 empty] | 5209 | VID TurbineType Mismatch | 0 | 45
[13 empty] | 5210 | Blade loads rotor speed low | 0 | 45
[13 empty] | 5211 | Yaw Cont Feedback Error | 0 | 45
[13 empty] | 5212 | Other Cont Feedback Error | 0 | 45
[13 empty] | 5213 | Hydr Cont Feedback Error | 0 | 45
[13 empty] | 5214 | Conv Gen WCool Cont Fb Err | 0 | 45
[13 empty] | 5215 | Yaw Main Switch Opened | 0 | 45
[13 empty] | 5216 | Yaw Cabinet CB Opened | 0 | 45
[13 empty] | 5217 | Tower Cabinet CB Opened | 0 | 45
[13 empty] | 5218 | Other CB Opened | 0 | 45
[13 empty] | 5219 | Nacelle Cabinet Main CB Opened | 0 | 45
[13 empty] | 5220 | Hydr CB Opened | 0 | 45
[13 empty] | 5221 | DeIcing Main Supply CB Opened | 0 | 45
[13 empty] | 5222 | Conv Gen WCool CB Opened | 0 | 45
[13 empty] | 5223 | Nacelle 24V Error | 0 | 45
[13 empty] | 5224 | Aux Trafo Main CB Opened | 0 | 45
[13 empty] | 5225 | Aux Trafo Main CB Closed | 0 | 45
[13 empty] | 5226 | BLS Calibration Status | 0 | 45
[13 empty] | 5227 | Edge Vib. Detected In Service | 0 | 45
[13 empty] | 5228 | Edge Vibrations In Service | 0 | 45
[13 empty] | 5229 | NacelleRearHatch open error | 0 | 45
[13 empty] | 5230 | NacelleRearHatch close error | 0 | 45
[13 empty] | 5231 | NacelleRearFanOverloaded error | 0 | 45
[13 empty] | 5232 | Tower Sticker Data Updated | 0 | 45
[13 empty] | 5233 | ConverterPanelExternalFanError | 0 | 45
[13 empty] | 5234 | ConverterAirFilterCLogged | 0 | 45
[13 empty] | 5236 | High env. temp NRMS enabled | 0 | 45
[13 empty] | 5237 | Low env. temp. NRMS disabled | 0 | 45
[13 empty] | 5238 | ExtrHigh Generator Brk Current | 0 | 45
[13 empty] | 5239 | High Generator Breaker Current | 0 | 45
[13 empty] | 5240 | Pitch Sys Disabled Man In Turb | 0 | 45
[13 empty] | 5244 | Trafo Temp Sensor Fault | 0 | 45
[13 empty] | 5245 | Generator SlipRing Suction Fan | 0 | 45
[13 empty] | 5246 | Generator SlipRing Heater | 0 | 45
[13 empty] | 5247 | Generator SlipRing Fan | 0 | 45
[13 empty] | 5248 | Gen SlipR Conditioning State | 0 | 45
[13 empty] | 5249 | Gen SlipR CondensationTime | 0 | 45
[13 empty] | 5250 | Gen SlipRingPreheatTime | 0 | 45
[13 empty] | 5251 | GenSlipR SuctionFanFB pos err | 0 | 45
[13 empty] | 5252 | GenSlipR SuctionFanFB neg err | 0 | 45
[13 empty] | 5253 | GenSlipR SuctionFanOverloaded | 0 | 45
[13 empty] | 5254 | GenSlipR Fan Overloaded | 0 | 45
[13 empty] | 5255 | HydrSysPressUnex:____bar____°C | 0 | 45
[13 empty] | 5256 | HydrOilTempLow___°C | 0 | 45
[13 empty] | 5257 | Nacelle heater | 0 | 45
[13 empty] | 5258 | Nacelle fan 1 | 0 | 45
[13 empty] | 5259 | Nacelle fan 2 | 0 | 45
[13 empty] | 5260 | Nacelle hatch right side | 0 | 45
[13 empty] | 5261 | Nacelle hatch left side | 0 | 45
[13 empty] | 5262 | Nac inlet hatch right open err | 0 | 45
[13 empty] | 5263 | Nac inlet hatch right clos err | 0 | 45
[13 empty] | 5264 | Nac inlet hatch left open err | 0 | 45
[13 empty] | 5265 | Nac inlet hatch left clos err | 0 | 45
[13 empty] | 5266 | Nac HeatRightSpeed PosFB Err | 0 | 45
[13 empty] | 5267 | Nac HeatRightSpeed NegFB Err | 0 | 45
[13 empty] | 5268 | Nac HeatingLeftSpeed PosFB Err | 0 | 45
[13 empty] | 5269 | Nac HeatingLeftSpeed NegFB Err | 0 | 45
[13 empty] | 5270 | Nac Fan2LowSpeed PosFB Err | 0 | 45
[13 empty] | 5271 | Nac. Fan2LowSpeed Overloaded | 0 | 45
[13 empty] | 5272 | Nac Fan2LowSpeed NegFB Err | 0 | 45
[13 empty] | 5273 | Nac Fan2HighSpeed PosFB Err | 0 | 45
[13 empty] | 5274 | Nac. Fan2HighSpeed Overloaded | 0 | 45
[13 empty] | 5275 | Nac Fan2HighSpeed NegFB Err | 0 | 45
[13 empty] | 5276 | Nac Fan1LowSpeed PosFB Err | 0 | 45
[13 empty] | 5277 | Nac. Fan1LowSpeed Overloaded | 0 | 45
[13 empty] | 5278 | Nac Fan1LowSpeed NegFB Err | 0 | 45
[13 empty] | 5279 | Nac Fan1HighSpeed PosFB Err | 0 | 45
[13 empty] | 5280 | Nac. Fan1HighSpeed Overloaded | 0 | 45
[13 empty] | 5281 | Nac Fan1HighSpeed NegFB Err | 0 | 45
[13 empty] | 5282 | TrafoFan HighSpeed PosFB Error | 0 | 45
[13 empty] | 5283 | Trafo Fan LowSpeed PosFB Error | 0 | 45
[13 empty] | 5284 | TrafoFan HighSpeed NegFB Error | 0 | 45
[13 empty] | 5285 | Trafo Fan LowSpeed NegFB Error | 0 | 45
[13 empty] | 5286 | TrafoFan HighSpeed ThermoFault | 0 | 45
[13 empty] | 5287 | TrafoFan LowSpeed ThermoFault | 0 | 45
[13 empty] | 5288 | Transformer Fan | 0 | 45
[13 empty] | 5289 | SSR detect Freq:___Hz,Ind:___ | 0 | 45
[13 empty] | 5290 | TooFrequentAccuRechargLevel1 | 0 | 45
[13 empty] | 5291 | TooFrequentAccuRechargLevel2 | 0 | 45
[13 empty] | 5292 | Grid volt harmonics exceeded | 0 | 45
[13 empty] | 5293 | BladeA heating, fuse blown | 0 | 45
[13 empty] | 5294 | BladeB heating, fuse blown | 0 | 45
[13 empty] | 5295 | BladeC heating, fuse blown | 0 | 45
[13 empty] | 5296 | BladeAHeatingLWE1E2FuseBlown | 0 | 45
[13 empty] | 5297 | BladeAHeatingLWE3E4FuseBlown | 0 | 45
[13 empty] | 5298 | BladeAHeatingLWE5E6FuseBlown | 0 | 45
[13 empty] | 5299 | BladeA heating, fuse blown | 0 | 45
[13 empty] | 5300 | BladeB heating, fuse blown | 0 | 45
[13 empty] | 5301 | BladeC heating, fuse blown | 0 | 45
[13 empty] | 5302 | BladeAHeatingLWE1E2FuseBlown | 0 | 45
[13 empty] | 5303 | BladeAHeatingLWE3E4FuseBlown | 0 | 45
[13 empty] | 5304 | BladeAHeatingLWE5E6FuseBlown | 0 | 45
[13 empty] | 5305 | BladeAHeatingLWE7E8FuseBlown | 0 | 45
[13 empty] | 5306 | BladeAHeatingLWE9E10FuseBlown | 0 | 45
[13 empty] | 5307 | BladeAHeatingLWE11E12FuseBlown | 0 | 45
[13 empty] | 5308 | BladeBHeatingLWE1E2FuseBlown | 0 | 45
[13 empty] | 5309 | BladeBHeatingLWE3E4FuseBlown | 0 | 45
[13 empty] | 5310 | BladeBHeatingLWE5E6FuseBlown | 0 | 45
[13 empty] | 5311 | BladeBHeatingLWE7E8FuseBlown | 0 | 45
[13 empty] | 5312 | BladeBHeatingLWE9E10FuseBlown | 0 | 45
[13 empty] | 5313 | BladeBHeatingLWE11E12FuseBlown | 0 | 45
[13 empty] | 5314 | BladeCHeatingLWE1E2FuseBlown | 0 | 45
[13 empty] | 5315 | BladeCHeatingLWE3E4FuseBlown | 0 | 45
[13 empty] | 5316 | BladeCHeatingLWE5E6FuseBlown | 0 | 45
[13 empty] | 5317 | BladeCHeatingLWE7E8FuseBlown | 0 | 45
[13 empty] | 5318 | BladeCHeatingLWE9E10FuseBlown | 0 | 45
[13 empty] | 5319 | BladeCHeatingLWE11E12FuseBlown | 0 | 45
[13 empty] | 5320 | BladeAHeatingWWE1E2FuseBlown | 0 | 45
[13 empty] | 5321 | BladeAHeatingWWE3E4FuseBlown | 0 | 45
[13 empty] | 5322 | BladeAHeatingWWE5E6FuseBlown | 0 | 45
[13 empty] | 5323 | BladeAHeatingWWE7E8FuseBlown | 0 | 45
[13 empty] | 5324 | BladeAHeatingWWE9E10FuseBlown | 0 | 45
[13 empty] | 5325 | BladeAHeatingWWE11E12FuseBlown | 0 | 45
[13 empty] | 5326 | BladeBHeatingWWE1E2FuseBlown | 0 | 45
[13 empty] | 5327 | BladeBHeatingWWE3E4FuseBlown | 0 | 45
[13 empty] | 5328 | BladeBHeatingWWE5E6FuseBlown | 0 | 45
[13 empty] | 5329 | BladeBHeatingWWE7E8FuseBlown | 0 | 45
[13 empty] | 5330 | BladeBHeatingWWE9E10FuseBlown | 0 | 45
[13 empty] | 5331 | BladeBHeatingWWE11E12FuseBlown | 0 | 45
[13 empty] | 5332 | BladeCHeatingWWE1E2FuseBlown | 0 | 45
[13 empty] | 5333 | BladeCHeatingWWE3E4FuseBlown | 0 | 45
[13 empty] | 5334 | BladeCHeatingWWE5E6FuseBlown | 0 | 45
[13 empty] | 5335 | BladeCHeatingWWE7E8FuseBlown | 0 | 45
[13 empty] | 5336 | BladeCHeatingWWE9E10FuseBlown | 0 | 45
[13 empty] | 5337 | BladeCHeatingWWE11E12FuseBlown | 0 | 45
[13 empty] | 5338 | BladeA heating current error | 0 | 45
[13 empty] | 5339 | BladeB heating current error | 0 | 45
[13 empty] | 5340 | BladeC heating current error | 0 | 45
[13 empty] | 5341 | AntiIcing heating level | 0 | 45
[13 empty] | 5342 | DeIcing heating level | 0 | 45
[13 empty] | 5343 | DeIcingStarted - ByOwner | 0 | 45
[13 empty] | 5344 | DeIcingStarted - ByManufact | 0 | 45
[13 empty] | 5345 | DeIce finished-turbine idling | 0 | 45
[13 empty] | 5346 | Bld heat SCADA Comm timeout | 0 | 45
[13 empty] | 5347 | Blade heating info | 0 | 45
[13 empty] | 5348 | De-icing started | 0 | 45
[13 empty] | 5349 | De-icing stopped | 0 | 45
[13 empty] | 5350 | De-icing succeeded | 0 | 45
[13 empty] | 5351 | De-icing failed | 0 | 45
[13 empty] | 5352 | Anti-icing started | 0 | 45
[13 empty] | 5353 | Anti-icing stopped | 0 | 45
[13 empty] | 5354 | Anti-icing failed | 0 | 45
[13 empty] | 5355 | PitchAccTestSysAccLowPress | 0 | 45
[13 empty] | 5356 | LORC testbench shutdown | 0 | 45
[13 empty] | 5357 | Awaiting safety reset pressed | 0 | 45
[13 empty] | 5358 | HubSafty EmgStpNacPnl I/P Err. | 0 | 45
[13 empty] | 5359 | HubSafty HoldToRunErr. | 0 | 45
[13 empty] | 5360 | Safety AbnormalCableTwist Err | 0 | 45
[13 empty] | 5361 | Safety ExcessiveVibration Err | 0 | 45
[13 empty] | 5362 | Safety TripHVButtonNac Err | 0 | 45
[13 empty] | 5363 | Safety TripHVButtonTow Err | 0 | 45
[13 empty] | 5364 | GearODMSensorCommFault | 0 | 45
[13 empty] | 5365 | GearODMSensorBITFault | 0 | 45
[13 empty] | 5366 | ConverterNotReady ____°C ___% | 0 | 45
[13 empty] | 5367 | ModeSelTowerSignalMismatch | 0 | 45
[13 empty] | 5368 | ModeSelNacelleSignalMismatch | 0 | 45
[13 empty] | 5369 | ModeSelectorInStopMode | 0 | 45
[13 empty] | 5370 | ModeSelectorOperationErr__ | 0 | 45
[13 empty] | 5371 | ModeSelectorHWError | 0 | 45
[13 empty] | 5372 | TowerModeSelPos__Tow__Nacelle | 0 | 45
[13 empty] | 5373 | NacelleModeSelPos__Tower__Nac | 0 | 45
[13 empty] | 5374 | ModeSelector__Pos__CommRights | 0 | 45
[13 empty] | 5375 | ModeSel - PointOfOpr changed | 0 | 45
[13 empty] | 5376 | Brake hydraulic leakage | 0 | 45
[13 empty] | 5377 | Brake hydraulic leakage high | 0 | 45
[13 empty] | 5378 | ArcLightDetected 2 | 0 | 45
[13 empty] | 5379 | ArcLightDetectorError | 0 | 45
[13 empty] | 5380 | ArcDetectorTestStart | 0 | 45
[13 empty] | 5381 | ArcDetectorTestStop | 0 | 45
[13 empty] | 5382 | ArcLightDetectorError | 0 | 45
[13 empty] | 5383 | ArcLightDetector2Error | 0 | 45
[13 empty] | 5384 | McpGracePeriod | 0 | 45
[13 empty] | 5385 | BrakeApplied | 0 | 45
[13 empty] | 5386 | BrakeReleased | 0 | 45
[13 empty] | 5387 | BrakeHydrPump | 0 | 45
[13 empty] | 5388 | BrakeDrainValve | 0 | 45
[13 empty] | 5389 | LowBrakeHydraulicPressure | 0 | 45
[13 empty] | 5390 | Brake worn | 0 | 45
[13 empty] | 5391 | High temperature brake disc | 0 | 45
[13 empty] | 5392 | BrakeHydraulicPressLeak | 0 | 45
[13 empty] | 5393 | BrakeNotApplied | 0 | 45
[13 empty] | 5394 | BrakeNotReleased | 0 | 45
[13 empty] | 5395 | BrakeHydrPumpPosFbErr | 0 | 45
[13 empty] | 5396 | BrakeHydrPumpNegFbErr | 0 | 45
[13 empty] | 5397 | BrakeHydrPumpThermoErr | 0 | 45
[13 empty] | 5398 | YawCam1StateErr:_ CTwist:___° | 0 | 45
[13 empty] | 5399 | YawCam2StateErr:_ CTwist:___° | 0 | 45
[13 empty] | 5400 | YawCam3StateErr:_ CTwist:___° | 0 | 45
[13 empty] | 5401 | YawCam1RequiresActivation | 0 | 45
[13 empty] | 5402 | YawCam2RequiresActivation | 0 | 45
[13 empty] | 5403 | YawCam3RequiresActivation | 0 | 45
[13 empty] | 5404 | YawCam1Act.State_.CTwist___° | 0 | 45
[13 empty] | 5405 | YawCam2Act.State_.CTwist___° | 0 | 45
[13 empty] | 5406 | YawCam3Act.State_.CTwist___° | 0 | 45
[13 empty] | 5407 | GearOilCold | 0 | 45
[13 empty] | 5408 | GearOilTooCold | 0 | 45
[13 empty] | 5409 | GearBearingsCold | 0 | 45
[13 empty] | 5410 | HSSBearRETempHigh ___°C | 0 | 45
[13 empty] | 5411 | HSSBearRETempTooHigh ___°C | 0 | 45
[13 empty] | 5412 | HSSBrNREInnerTempHigh ___°C | 0 | 45
[13 empty] | 5413 | HSSBrNREInnerTempTooHigh___°C | 0 | 45
[13 empty] | 5414 | HSBrNREOuterTempHigh ___°C | 0 | 45
[13 empty] | 5415 | HSBrNREOuterTempTooHigh ___°C | 0 | 45
[13 empty] | 5416 | LSSBearRETempHigh ___°C | 0 | 45
[13 empty] | 5417 | LSSBearRETempTooHigh ___°C | 0 | 45
[13 empty] | 5418 | LSBearNRETempHigh ___°C | 0 | 45
[13 empty] | 5419 | LSSBearNRETempTooHigh ___°C | 0 | 45
[13 empty] | 5420 | YawCW1StartSignalInvalid | 0 | 45
[13 empty] | 5421 | YawCW2StartSignalInvalid | 0 | 45
[13 empty] | 5422 | YawCW3StartSignalInvalid | 0 | 45
[13 empty] | 5423 | YawCCW1StartSignalInvalid | 0 | 45
[13 empty] | 5424 | YawCCW2StartSignalInvalid | 0 | 45
[13 empty] | 5425 | YawCCW3StartSignalInvalid | 0 | 45
[13 empty] | 5426 | SwitchgearActiveCoilTripTest | 0 | 45
[13 empty] | 5427 | SwitchgearUVoltageCoilTripTest | 0 | 45
[13 empty] | 5428 | Switchgear SC/OC/EF fault | 0 | 45
[13 empty] | 5429 | Awaiting safety reset pressed | 0 | 45
[13 empty] | 5430 | McpAlarm | 0 | 45
[13 empty] | 5431 | Q8 Close not possible | 0 | 45
[13 empty] | 5432 | Q7 breaker closed | 0 | 45
[13 empty] | 5433 | Q7 breaker open | 0 | 45
[13 empty] | 5434 | Q8 breaker open | 0 | 45
[13 empty] | 5435 | Q7 Tripped | 0 | 45
[13 empty] | 5436 | Over Voltage Fuse Open | 0 | 45
[13 empty] | 5437 | Other motors CB Opened | 0 | 45
[13 empty] | 5438 | Grid Breaker Q8 Reconnected | 0 | 45
[13 empty] | 5439 | Grid Breaker Q8 Reconnecting | 0 | 45
[13 empty] | 5440 | Grid Breaker Trip F60 | 0 | 45
[13 empty] | 5441 | Grid Breaker Trip Q8 | 0 | 45
[13 empty] | 5442 | Trip Nacelle Common Contactor | 0 | 45
[13 empty] | 5443 | Frequency error 5: ___.__ Hz | 0 | 45
[13 empty] | 5444 | High temp. grid choke ___°C | 0 | 45
[13 empty] | 5445 | High temp. polygon trans ___°C | 0 | 45
[13 empty] | 5446 | HydrInitPressMissing___bar__°C | 0 | 45
[13 empty] | 5447 | HydrHPFilterPresDrpHigh____°C | 0 | 45
[13 empty] | 5448 | HydrHPFltrPresDrpTooHgh____°C | 0 | 45
[13 empty] | 5449 | HydraulicOilLevelLow | 0 | 45
[13 empty] | 5450 | HydraulicOilLevelTooLow | 0 | 45
[13 empty] | 5451 | HydrMainPressHigh:____bar___°C | 0 | 45
[13 empty] | 5452 | HydrMainPressLow:____bar____°C | 0 | 45
[13 empty] | 5453 | HydrOilTempHigh___°C | 0 | 45
[13 empty] | 5454 | HydrOilTempTooHigh___°C | 0 | 45
[13 empty] | 5455 | HydrOilTempLow___°C | 0 | 45
[13 empty] | 5456 | HydraulicOilUnderSludge | 0 | 45
[13 empty] | 5457 | HydrOffFltrPresDrpHigh____°C | 0 | 45
[13 empty] | 5458 | HydrHPPumpNegativeFeedbackErr | 0 | 45
[13 empty] | 5459 | HydrHPPumpPositiveFeedbackErr | 0 | 45
[13 empty] | 5460 | HydrHighPressPumpThermoError | 0 | 45
[13 empty] | 5461 | HydrOLPumpNegativeFeedbackErr | 0 | 45
[13 empty] | 5462 | HydrOLPumpPositiveFeedbackErr | 0 | 45
[13 empty] | 5463 | HydrOfflinePumpThermoError | 0 | 45
[13 empty] | 5464 | HydrHighPressPumpState | 0 | 45
[13 empty] | 5465 | HydrHeatingValveState | 0 | 45
[13 empty] | 5466 | HydrCoolingValveState | 0 | 45
[13 empty] | 5467 | HydrOfflinePumpState | 0 | 45
[13 empty] | 5468 | YawCableTwistDetMuteStart | 0 | 45
[13 empty] | 5469 | YawCableTwistDetMuteStop | 0 | 45
[13 empty] | 5470 | GeneratorBreakerFBResponse | 6 | 12
[13 empty] | 5471 | GeneratorBreakerTripped | 6 | 12
[13 empty] | 5472 | GeneratorBreakerUnexpectedFb | 0 | 45
[13 empty] | 5473 | GeneratorBreakerOpenFail | 0 | 45
[13 empty] | 5474 | Power supply on grid | 0 | 45
[13 empty] | 5475 | Power supply off grid | 0 | 45
[13 empty] | 5476 | Converter requests a reboot | 0 | 45
[13 empty] | 5477 | Smoke Detector Sensor Info | 0 | 45
[13 empty] | 5478 | WindSensor WindDirRelDisagree | 0 | 45
[13 empty] | 5479 | Ext.ConverterStopSignalActive | 0 | 45
[13 empty] | 5480 | ConvGen WCool liquid temp high | 0 | 45
[13 empty] | 5481 | ConvGen WCool liquid level low | 0 | 45
[13 empty] | 5482 | ConvGen WCool Pump NegFB | 0 | 45
[13 empty] | 5483 | ConvGen WCool pump Overloaded | 0 | 45
[13 empty] | 5484 | ConvGen WCool Pump PosFB | 0 | 45
[13 empty] | 5485 | ConvGen WCool Preheat NegFB | 0 | 45
[13 empty] | 5486 | ConvGen WCool preheat OLoaded | 0 | 45
[13 empty] | 5487 | ConvGen WCool Preheat PosFB | 0 | 45
[13 empty] | 5488 | ConvGen WCool Fan1Low NegFB | 0 | 45
[13 empty] | 5489 | ConvGen WCool Fan1Low OLoaded | 0 | 45
[13 empty] | 5490 | ConvGen WCool Fan1Low PosFB | 0 | 45
[13 empty] | 5491 | ConvGen WCool Fan1High NegFB | 0 | 45
[13 empty] | 5492 | ConvGen WCool Fan1High OLoaded | 0 | 45
[13 empty] | 5493 | ConvGen WCool Fan1High PosFB | 0 | 45
[13 empty] | 5494 | ConvGen WCool Fan2Low NegFB | 0 | 45
[13 empty] | 5495 | ConvGen WCool Fan2Low OLoaded | 0 | 45
[13 empty] | 5496 | ConvGen WCool Fan2Low PosFB | 0 | 45
[13 empty] | 5497 | ConvGen WCool Fan2High NegFB | 0 | 45
[13 empty] | 5498 | ConvGen WCool Fan2High OLoaded | 0 | 45
[13 empty] | 5499 | ConvGen WCool Fan2High PosFB | 0 | 45
[13 empty] | 5500 | ConvGen WCool State | 0 | 45
[13 empty] | 5501 | ConvGen WCool Fan1 State | 0 | 45
[13 empty] | 5502 | ConvGen WCool Fan2 State | 0 | 45
[13 empty] | 5503 | ConvGen WCool Pump State | 0 | 45
[13 empty] | 5504 | ConvGen WCool Preheater State | 0 | 45
[13 empty] | 5505 | UPS AC Grd Mismatch | 0 | 45
[13 empty] | 5506 | UPS AC Await disconn pwr | 0 | 45
[13 empty] | 5507 | LDO Validation Toggling Active | 0 | 45
[13 empty] | 5508 | ConvCheckHumidityAndTemp | 0 | 45
[13 empty] | 5509 | ConvCoolingWaterTooCold | 0 | 45
[13 empty] | 5510 | Conv Est. DryOut time:__.__ | 0 | 45
[13 empty] | 5511 | ConvHeaterTurnOffFailed | 0 | 45
[13 empty] | 5512 | HighTempPreventCharging:___ | 0 | 45
[13 empty] | 5513 | StartingConverterafterPreCond | 0 | 45
[13 empty] | 5514 | TimeWithoutPowerNotAcc : __ | 0 | 45
[13 empty] | 5515 | ConvUnableToReachAcptCond : _ | 0 | 45
[13 empty] | 5516 | GenHeater: _, temp:___°C | 0 | 45
[13 empty] | 5517 | UPS DC Error | 0 | 45
[13 empty] | 5518 | UPS DC Battery Error | 0 | 45
[13 empty] | 5519 | UPS DC battery level low | 0 | 45
[13 empty] | 5520 | UPS DC OnGrid signal mismatch | 0 | 45
[13 empty] | 5521 | ConvGen WCool Fan Error | 0 | 45
[13 empty] | 5522 | ConvGen WCool Fan Error | 0 | 45
[13 empty] | 5523 | Safety, waiting for reset | 0 | 45
[13 empty] | 5524 | SftyNac, UnknownResetReason | 0 | 45
[13 empty] | 5525 | SftyHub, UnknownResetReason | 0 | 45
[13 empty] | 5526 | SftyTow, UnknownResetReason | 0 | 45
[13 empty] | 5527 | SftyNac, UnknownPendingReason | 0 | 45
[13 empty] | 5528 | SftyHub, UnknownPendingReason | 0 | 45
[13 empty] | 5529 | SftyTow, UnknownPendingReason | 0 | 45
[13 empty] | 5530 | EmergStopButtonActivated: __ | 0 | 45
[13 empty] | 5531 | Awaiting safety reset pressed | 0 | 45
[13 empty] | 5532 | EStopButtonIOCabinet HwError | 0 | 45
[13 empty] | 5533 | EStopButtonHubCabinet HwError | 0 | 45
[13 empty] | 5534 | EStopBtnHighSpeedShaft HwError | 0 | 45
[13 empty] | 5535 | EStopBtnLowSpeedShaft HwError | 0 | 45
[13 empty] | 5536 | EStopBtnNacelleCabinet HwError | 0 | 45
[13 empty] | 5537 | EStopBtnTowerCabinet HwError | 0 | 45
[13 empty] | 5538 | EStopBtnTowerTop HwError | 0 | 45
[13 empty] | 5539 | EStopBtnYaw HwError | 0 | 45
[13 empty] | 5540 | EStopBtnConvCabinet HwError | 0 | 45
[13 empty] | 5541 | HubServiceSwitch HwError | 0 | 45
[13 empty] | 5542 | BallValveAOpen HwError | 0 | 45
[13 empty] | 5543 | BallValveAClosed HwError | 0 | 45
[13 empty] | 5544 | BallValveBOpen HwError | 0 | 45
[13 empty] | 5545 | BallValveBClosed HwError | 0 | 45
[13 empty] | 5546 | BallValveCOpen HwError | 0 | 45
[13 empty] | 5547 | BallValveCClosed HwError | 0 | 45
[13 empty] | 5548 | HoldToRun HwError | 0 | 45
[13 empty] | 5549 | ExcessiveVibration HwError | 0 | 45
[13 empty] | 5550 | AbnormalCableTwist HwError | 0 | 45
[13 empty] | 5551 | SafetySystem Converter Stopped | 0 | 45
[13 empty] | 5552 | SafetyNac1 SwVers Error | 0 | 45
[13 empty] | 5553 | SafetyNac1 SwVers Temp Error | 0 | 45
[13 empty] | 5554 | SafetyNac2 SwVers Error | 0 | 45
[13 empty] | 5555 | SafetyNac2 SwVers Temp Error | 0 | 45
[13 empty] | 5556 | SafetyNac3 SwVers Error | 0 | 45
[13 empty] | 5557 | SafetyNac3 SwVers Temp Error | 0 | 45
[13 empty] | 5558 | SafetyHub1 SwVers Error | 0 | 45
[13 empty] | 5559 | SafetyHub1 SwVers Temp Error | 0 | 45
[13 empty] | 5560 | SafetyTow1 SwVers Error | 0 | 45
[13 empty] | 5561 | SafetyTow1 SwVers Temp Error | 0 | 45
[13 empty] | 5562 | SafetyNac1 Communication Error | 0 | 45
[13 empty] | 5563 | SafetyNac2 Communication Error | 0 | 45
[13 empty] | 5564 | SafetyNac3 Communication Error | 0 | 45
[13 empty] | 5565 | SafetyHub1 Communication Error | 0 | 45
[13 empty] | 5566 | SafetyTow1 Communication Error | 0 | 45
[13 empty] | 5567 | SafetySystemCriticalCommError | 0 | 45
[13 empty] | 5568 | SafetyNac1 EKey Error | 0 | 45
[13 empty] | 5569 | SafetyNac2 EKey Error | 0 | 45
[13 empty] | 5570 | SafetyNac3 EKey Error | 0 | 45
[13 empty] | 5571 | SafetyHub1 EKey Error | 0 | 45
[13 empty] | 5572 | SafetyTow1 EKey Error | 0 | 45
[13 empty] | 5573 | SafetyNac1 Operational Error | 0 | 45
[13 empty] | 5574 | SafetyNac2 Operational Error | 0 | 45
[13 empty] | 5575 | SafetyNac3 Operational Error | 0 | 45
[13 empty] | 5576 | SafetyHub1 Operational Error | 0 | 45
[13 empty] | 5577 | SafetyTow1 Operational Error | 0 | 45
[13 empty] | 5578 | Protection System Activated | 0 | 45
[13 empty] | 5579 | TripHVButtonNacelle HwError | 0 | 45
[13 empty] | 5580 | TripHVButtonTower HwError | 0 | 45
[13 empty] | 5581 | ConvGen WCool Fans State | 0 | 45
[13 empty] | 5582 | GearHydr WCool liquid level lo | 0 | 45
[13 empty] | 5583 | GearHydr WCool Pump NegFB | 0 | 45
[13 empty] | 5584 | GearHydr WCool pump Overloaded | 0 | 45
[13 empty] | 5585 | GearHydr WCool Pump PosFB | 0 | 45
[13 empty] | 5586 | GearHydr WCool Fan1Low NegFB | 0 | 45
[13 empty] | 5587 | GearHydr WCool Fan1Low OLoaded | 0 | 45
[13 empty] | 5588 | GearHydr WCool Fan1Low PosFB | 0 | 45
[13 empty] | 5589 | GearHydr WCool Fan1High NegFB | 0 | 45
[13 empty] | 5590 | GearHydr WCool Fan1High OLoad | 0 | 45
[13 empty] | 5591 | GearHydr WCool Fan1High PosFB | 0 | 45
[13 empty] | 5592 | GearHydr WCool Fan2Low NegFB | 0 | 45
[13 empty] | 5593 | GearHydr WCool Fan2Low OLoaded | 0 | 45
[13 empty] | 5594 | GearHydr WCool Fan2Low PosFB | 0 | 45
[13 empty] | 5595 | GearHydr WCool Fan2High NegFB | 0 | 45
[13 empty] | 5596 | GearHydr WCool Fan2High OLoad | 0 | 45
[13 empty] | 5597 | GearHydr WCool Fan2High PosFB | 0 | 45
[13 empty] | 5598 | GearHydr WCool State | 0 | 45
[13 empty] | 5599 | GearHydr WCool Fan1 State | 0 | 45
[13 empty] | 5600 | GearHydr WCool Fan2 State | 0 | 45
[13 empty] | 5601 | GearHydr WCool Pump State | 0 | 45
[13 empty] | 5602 | GearHydr WCool Fan Error | 0 | 45
[13 empty] | 5603 | GearHydr WCool Fan Error | 0 | 45
[13 empty] | 5604 | GearHydr WCool Fans State | 0 | 45
[13 empty] | 5605 | GenShaftCurrent1High: __,_A | 0 | 45
[13 empty] | 5606 | GenShaftCurrent2High: __,_A | 0 | 45
[13 empty] | 5607 | GenShaftCurrent1TooHigh: __,_A | 0 | 45
[13 empty] | 5608 | GenShaftCurrent2TooHigh: __,_A | 0 | 45
[13 empty] | 5609 | ShaftCurrent1ChargeHigh: __._C | 0 | 45
[13 empty] | 5610 | ShaftCurrent2ChargeHigh: __._C | 0 | 45
[13 empty] | 5611 | GenShaftCurrentSystemFault | 0 | 45
[13 empty] | 5612 | ConvPanelAirCoolingExtFanNegFB | 0 | 45
[13 empty] | 5613 | ConvPanelAirCoolingExtFanPosFB | 0 | 45
[13 empty] | 5614 | ConvAirCoolingIntFanOverloaded | 0 | 45
[13 empty] | 5615 | ConvAirCoolingHumiditySnsrErr | 0 | 45
[13 empty] | 5616 | ConvAirCoolingIntFanState | 0 | 45
[13 empty] | 5617 | ConvAirCoolingExtFanState | 0 | 45
[13 empty] | 5618 | ConvAirCoolingHeaterState | 0 | 45
[13 empty] | 5619 | ConvChopper FanLow NegFB | 0 | 45
[13 empty] | 5620 | ConvChopper FanLow Overloaded | 0 | 45
[13 empty] | 5621 | ConvChopper FanLow PosFB | 0 | 45
[13 empty] | 5622 | ConvChopper FanHigh NegFB | 0 | 45
[13 empty] | 5623 | ConvChopper FanHigh Overloaded | 0 | 45
[13 empty] | 5624 | ConvChopper FanHigh PosFB | 0 | 45
[13 empty] | 5625 | ConvChopper Temp High | 0 | 45
[13 empty] | 5626 | ConvChopper Cooling State | 0 | 45
[13 empty] | 5627 | ConvChopper Cooling Fan State | 0 | 45
[13 empty] | 5628 | CtrlPwr DCNHub1 RailA Err | 0 | 45
[13 empty] | 5629 | CtrlPwr DCNHub1 RailB Err | 0 | 45
[13 empty] | 5630 | CtrlPwr DCNHub1 Test Err | 0 | 45
[13 empty] | 5631 | CtrlPwr DCNHub1 Test Missing | 0 | 45
[13 empty] | 5635 | HubInSafeMode BallValvePosErr | 0 | 45
[13 empty] | 5636 | Load/PowerMode setmode__.__.__ | 0 | 45
[13 empty] | 5637 | GearOilInitialPressLow___._bar | 0 | 45
[13 empty] | 5638 | GearOilLevelHigh:___._ mm | 0 | 45
[13 empty] | 5639 | GearOilLevelLow: ___._ mm | 0 | 45
[13 empty] | 5640 | GearOilLevelTooLow: ___._ mm | 0 | 45
[13 empty] | 5641 | GearFiltPressHigh __._bar | 0 | 45
[13 empty] | 5642 | GearFiltPressTooHigh __._bar | 0 | 45
[13 empty] | 5643 | GearFiltPressLow __._bar | 0 | 45
[13 empty] | 5644 | GearOilInletPressLow __._ bar | 0 | 45
[13 empty] | 5645 | Warm gearoil temp :____°C | 0 | 45
[13 empty] | 5646 | GearOilInletPressSensorFailed | 0 | 45
[13 empty] | 5647 | BeforeInlinePressSensorFailed | 0 | 45
[13 empty] | 5648 | AfterInlinePressSensorFailed | 0 | 45
[13 empty] | 5649 | GearOilMainBearSwarfErr | 0 | 45
[13 empty] | 5650 | GearOilStage1SwarfErr | 0 | 45
[13 empty] | 5651 | GearOilStage2SwarfErr | 0 | 45
[13 empty] | 5652 | GearOilStage3SwarfErr | 0 | 45
[13 empty] | 5653 | GenInitialOilPressLow | 0 | 45
[13 empty] | 5654 | GenOilPressLow | 0 | 45
[13 empty] | 5655 | GearboxOfflinePumpThermoError | 0 | 45
[13 empty] | 5656 | OfflineFiltDiffPressHigh | 0 | 45
[13 empty] | 5657 | OfflineFiltDiffPressLow | 0 | 45
[13 empty] | 5658 | GenLeakageDetected | 0 | 45
[13 empty] | 5659 | OfflinePumpPositiveFeedback | 0 | 45
[13 empty] | 5660 | OfflinePumpNegativeFeedback | 0 | 45
[13 empty] | 5661 | GearOilHeaterPositiveFeedback | 0 | 45
[13 empty] | 5662 | GearOilHeaterNegativeFeedback | 0 | 45
[13 empty] | 5663 | Emergency lubrication active | 0 | 45
[13 empty] | 5664 | EmergencyLubrSystemError | 0 | 45
[13 empty] | 5665 | KeySwitchPosErr Nac: _, Twr: _ | 0 | 45
[13 empty] | 5666 | Hub cabinet cooling state _ | 0 | 45
[13 empty] | 5667 | Nac cabinet cooling state _ | 0 | 45
[13 empty] | 5668 | EmcLubrSystemActive: _ | 0 | 45
[13 empty] | 5669 | GearOilPumpStart: _ | 0 | 45
[13 empty] | 5670 | OfflineOilPumpStart: _ | 0 | 45
[13 empty] | 5671 | GearboxOilHeater: _ | 0 | 45
[13 empty] | 5672 | EmergStopButtonActivated __ | 0 | 45
[13 empty] | 5673 | No Deicing - Temp out of range | 0 | 45
[13 empty] | 5674 | No Deicing - Wind out of range | 0 | 45
[13 empty] | 5675 | Deicing started cooling phase | 0 | 45
[13 empty] | 5676 | Cold generator ___°C ______kW | 0 | 45
[13 empty] | 5677 | ColdGeneratorDerateNotActive | 0 | 45
[13 empty] | 5678 | MKversionMismatchK500Feedback | 0 | 45
[13 empty] | 5679 | StatorStrikesorbFuses | 0 | 45
[13 empty] | 5680 | HighUStrikesorber____V | 0 | 45
[13 empty] | 5681 | HighIStrikesorber____A | 0 | 45
[13 empty] | 5682 | Yaw Lubrication Error | 0 | 45
[13 empty] | 5683 | Yaw lubrication _ | 0 | 45
[13 empty] | 5684 | Fast Pause Activated. Src: __ | 0 | 45
[13 empty] | 5685 | SyncVoltMeasurementMismatch | 0 | 45
[13 empty] | 5686 | ConvPanelAirCoolingIntFanNegFB | 0 | 45
[13 empty] | 5687 | ConvPanelAirCoolingIntFanPosFB | 0 | 45
[13 empty] | 5688 | ConvAirCoolingIntFanThermoErr | 0 | 45
[13 empty] | 5689 | ConvAirCoolingExtFanThermoErr | 0 | 45
[13 empty] | 5690 | ConvAirCoolingIntFanState | 0 | 45
[13 empty] | 5691 | ConvAirCoolingExtFanState | 0 | 45
[13 empty] | 5692 | PowerSupply VDS Sensor Error | 0 | 45
[13 empty] | 5693 | Grid Filter Thermo Fault | 0 | 45
[13 empty] | 5694 | DCLinkPrechargeEstErr___v | 0 | 45
[13 empty] | 5695 | BrakeApplyValve1Faulty | 0 | 45
[13 empty] | 5696 | BrakeApplyValve2Faulty | 0 | 45
[13 empty] | 5697 | BrakeDrainValveFaulty | 0 | 45
[13 empty] | 5698 | BldAFanSpaceHeater pos fb err | 0 | 45
[13 empty] | 5699 | BldAFanSpaceHeater neg fb err | 0 | 45
[13 empty] | 5700 | BladeA short circuit error | 0 | 45
[13 empty] | 5701 | BldBFanSpaceHeater pos fb err | 0 | 45
[13 empty] | 5702 | BldBFanSpaceHeater neg fb err | 0 | 45
[13 empty] | 5703 | BladeB short circuit error | 0 | 45
[13 empty] | 5704 | BldCFanSpaceHeater pos fb err | 0 | 45
[13 empty] | 5705 | BldCFanSpaceHeater neg fb err | 0 | 45
[13 empty] | 5706 | BladeC short circuit error | 0 | 45
[13 empty] | 5707 | DeIcing switch opened err | 0 | 45
[13 empty] | 5708 | DeIcing switch closed err | 0 | 45
[13 empty] | 5709 | YawSensorCommunicationError | 0 | 45
[13 empty] | 5710 | DeIcing Start Cmd: __ : __ | 0 | 45
[13 empty] | 5711 | WaterCoolingRequestTimeout | 0 | 45
[13 empty] | 5712 | WaterCoolingTripped | 0 | 45
[13 empty] | 5713 | HydraulicOilLeakage | 0 | 45
[13 empty] | 5714 | Brake release error | 0 | 45
[13 empty] | 5715 | Brake apply error | 0 | 45
[13 empty] | 5716 | Safety Nac EStop HSS I/P Err | 0 | 45
[13 empty] | 5717 | Safety Nac EStop Yaw I/P Err | 0 | 45
[13 empty] | 5718 | Safety Nac EStop LSS I/P Err | 0 | 45
[13 empty] | 5719 | Safty Nac EStop TwrTop I/P Err | 0 | 45
[13 empty] | 5720 | Safty Nac EStop TwrCab I/P Err | 0 | 45
[13 empty] | 5721 | Safty Nac EStop NacCab I/P Err | 0 | 45
[13 empty] | 5722 | Safety Nac EStop Hub I/P Err | 0 | 45
[13 empty] | 5723 | Safety Nac HVCB Trip I/P Err | 0 | 45
[13 empty] | 5724 | Safety Tower HVCB Trip I/P Err | 0 | 45
[13 empty] | 5725 | Safty Nac HydrPressReq I/P Err | 0 | 45
[13 empty] | 5726 | Safety Hub EPitch I/P Err | 0 | 45
[13 empty] | 5727 | SaftyHub HydrMainPress I/P Err | 0 | 45
[13 empty] | 5728 | SafetyHub PitchBlockA I/P Err | 0 | 45
[13 empty] | 5729 | SafetyHub PitchBlockB I/P Err | 0 | 45
[13 empty] | 5730 | SafetyHub PitchBlockC I/P Err | 0 | 45
[13 empty] | 5731 | WaterCoolLiquidLo___ l | 0 | 45
[13 empty] | 5732 | AviationLightLampShortLifetime | 0 | 45
[13 empty] | 5733 | Tower Door Opened | 0 | 45
[13 empty] | 5734 | Tower Door Closed | 0 | 45
[13 empty] | 5735 | Tower/SwG DC supply error | 0 | 45
[13 empty] | 5736 | Converter Off | 0 | 45
[13 empty] | 5737 | Converter Standby | 0 | 45
[13 empty] | 5738 | Converter Q Production | 0 | 45
[13 empty] | 5739 | Converter Q and P Production | 0 | 45
[13 empty] | 5740 | Lightning detected | 0 | 45
[13 empty] | 5741 | Lightning detected | 0 | 45
[13 empty] | 5742 | Lightning detected | 0 | 45
[13 empty] | 5743 | Lightning data blade A ___ kA | 0 | 45
[13 empty] | 5744 | Lightning data blade B ___ kA | 0 | 45
[13 empty] | 5745 | Lightning data blade C ___ kA | 0 | 45
[13 empty] | 5746 | ExtExt High Volt L_: ___ V | 0 | 45
[13 empty] | 5747 | Lightning blade A | 0 | 45
[13 empty] | 5748 | Lightning blade B | 0 | 45
[13 empty] | 5749 | Lightning blade C | 0 | 45
[13 empty] | 5750 | Lightning data blade A missing | 0 | 45
[13 empty] | 5751 | Lightning data blade B missing | 0 | 45
[13 empty] | 5752 | Lightning data blade C missing | 0 | 45
[13 empty] | 5753 | LowWindInHWO,T:_____s __._m/s | 0 | 45
[13 empty] | 5754 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5755 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5756 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5757 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5758 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5759 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5760 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5761 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5762 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5763 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5764 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5765 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5766 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5767 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5768 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5769 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5770 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5771 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5772 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5773 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5774 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5775 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5776 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5777 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5778 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5779 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5780 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5781 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5782 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5783 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5784 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5785 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5786 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5787 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5788 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5789 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5790 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5791 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5792 | Blade Load Calibration Data | 0 | 45
[13 empty] | 5793 | BladeLoadCalibrationSuccessful | 0 | 45
[13 empty] | 5794 | BladeLoadCalibrationSuccessful | 0 | 45
[13 empty] | 5795 | BladeLoadCalibrationSuccessful | 0 | 45
[13 empty] | 5796 | BladeLoadCalibrationSuccessful | 0 | 45
[13 empty] | 5797 | BladeLoadCalibrationSuccessful | 0 | 45
[13 empty] | 5798 | BladeLoadCalibrationSuccessful | 0 | 45
[13 empty] | 5799 | ConverterEstAirHumidityHigh | 0 | 45
[13 empty] | 5800 | PSCStateChange From __ To __ | 0 | 45
[13 empty] | 5801 | BladeLoadHardwareChange | 0 | 45
[13 empty] | 5802 | Lightning det. BldA sensor err | 0 | 45
[13 empty] | 5803 | Lightning det. BldB sensor err | 0 | 45
[13 empty] | 5804 | Lightning det. BldC sensor err | 0 | 45
[13 empty] | 5805 | Lightning det. system error | 0 | 45
[13 empty] | 5806 | Lightning det. comm. error | 0 | 45
[13 empty] | 5807 | Illegal picture no. | 0 | 45
[13 empty] | 5808 | VCMSCrashErrorLx | 0 | 45
[13 empty] | 5809 | Hub crash error | 0 | 45
[13 empty] | 5810 | Ground crash error | 0 | 45
[13 empty] | 5811 | Nacelle crash error | 0 | 45
[13 empty] | 5812 | Invalid data US. ID:3 | 0 | 45
[13 empty] | 5813 | Timeout/Checksum err. US.ID:3 | 0 | 45
[13 empty] | 5814 | High gen speed at low gear tmp | 0 | 45
[13 empty] | 5815 | CPS DltPRefA | 0 | 45
[13 empty] | 5816 | CPS DltPRefB | 0 | 45
[13 empty] | 5817 | CPS DltPRefC | 0 | 45
[13 empty] | 5818 | CPS DltPRefM | 0 | 45
[13 empty] | 5819 | HighGridFreq | 0 | 45
[13 empty] | 5820 | B407 open loop | 0 | 45
[13 empty] | 5821 | B549 open loop | 0 | 45
[13 empty] | 5822 | All US in error,Turb. in stop | 0 | 45
[13 empty] | 5823 | Pin Rotation AB | 0 | 45
[13 empty] | 5824 | Pin Rotation BC | 0 | 45
[13 empty] | 5825 | Pin Rotation CA | 0 | 45
[13 empty] | 5826 | Pin Rotation AB | 0 | 45
[13 empty] | 5827 | Pin Rotation BC | 0 | 45
[13 empty] | 5828 | Pin Rotation CA | 0 | 45
[13 empty] | 5829 | Remote timeout p | 0 | 45
[13 empty] | 5830 | Remote timeout q | 0 | 45
[13 empty] | 5831 | Signal error, swarf | 0 | 45
[13 empty] | 5832 | Yaw in stop Diesel Supply | 0 | 45
[13 empty] | 5833 | CAN node fault. PAUSE | 0 | 45
[13 empty] | 5834 | Extd. High Wind Op | 0 | 45
[13 empty] | 5835 | LaPM, derate | 0 | 45
[13 empty] | 5836 | CT6234 | 0 | 45
[13 empty] | 5837 | EMC Push button FB Error | 0 | 45
[13 empty] | 5838 | NRMS power derate | 0 | 45
[13 empty] | 5839 | VDF System Corrupted | 0 | 45
[13 empty] | 5840 | Windvaneerror | 0 | 45
[13 empty] | 5841 | High voltage THD | 0 | 45
[13 empty] | 5842 | Hub OpSt.change timeout | 0 | 45
[13 empty] | 5843 | CT6118 init. error | 0 | 45
[13 empty] | 5844 | Blade is not ready for lock | 0 | 45
[13 empty] | 5845 | Blade realese not detected | 0 | 45
[13 empty] | 5846 | Actuator do not run, blade | 0 | 45
[13 empty] | 5847 | Reser. full with oil and water | 0 | 45
[13 empty] | 5848 | Feedback,gear oil pump | 0 | 45
[13 empty] | 5849 | Disconnect Timeout | 0 | 45
[13 empty] | 5850 | High hub slipring temp | 0 | 45
[13 empty] | 5851 | Thermo error, oil vent. F | 0 | 45
[13 empty] | 5852 | Data error from blade | 0 | 45
[13 empty] | 5853 | Yaw CW to absolute yaw stop | 0 | 45
[13 empty] | 5854 | Yaw CCW to absolute yaw stop | 0 | 45
[13 empty] | 5855 | Error, Yawcontrol: | 0 | 45
[13 empty] | 5856 | Schnorkel is displaced | 0 | 45
[13 empty] | 5857 | S248 Error no signal 2 rounds | 0 | 45
[13 empty] | 5858 | Feedback=_,Hydr ventilator | 0 | 45
[13 empty] | 5859 | Thermoerror hydr. Vent. motor | 0 | 45
[13 empty] | 5860 | CAN InitError node | 0 | 45
[13 empty] | 5861 | SignalManager error in node | 0 | 45
[13 empty] | 5862 | Rotor counter error | 0 | 45
[13 empty] | 5863 | Generator tacho ch. is lost | 0 | 45
[13 empty] | 5864 | Generator counter error | 0 | 45
[13 empty] | 5865 | Feedback, GearGen | 0 | 45
[13 empty] | 5866 | GearGenTest fail, S561 | 0 | 45
[13 empty] | 5867 | User, Logged on | 0 | 45
[13 empty] | 5868 | User, Logged off | 0 | 45
[13 empty] | 5869 | High OutLet Temp Diff Error | 0 | 45
[13 empty] | 5870 | Signal error EMC-valve | 0 | 45
[13 empty] | 5871 | Signal not ready | 0 | 45
[13 empty] | 5872 | OS supervision error | 0 | 45
[13 empty] | 5873 | Thermoerror gen. slipring fan | 0 | 45
[13 empty] | 5874 | Warm gear bearing: | 0 | 45
[13 empty] | 5875 | ArcNet event | 0 | 45
[13 empty] | 5876 | Active Tower Damp. Active | 0 | 45
[13 empty] | 5877 | Active Tower Damp. deactivated | 0 | 45
[13 empty] | 5878 | Active Tower Damp. Max.Contrib | 0 | 45
[13 empty] | 5879 | Max flapwise load, blade | 0 | 45
[13 empty] | 5880 | Max edgewise load, blade | 0 | 45
[13 empty] | 5881 | Low rpm setpoint | 0 | 45
[13 empty] | 5882 | Pitch com error | 0 | 45
[13 empty] | 5883 | Error azimuth orientation | 0 | 45
[13 empty] | 5884 | Individual pitch enabled | 0 | 45
[13 empty] | 5885 | Individual pitch disabled | 0 | 45
[13 empty] | 5886 | No signal loadsensor | 0 | 45
[13 empty] | 5887 | Signal error PosTransducer | 0 | 45
[13 empty] | 5888 | Signal error PropValve | 0 | 45
[13 empty] | 5889 | Manual, signal:B | 0 | 45
[13 empty] | 5890 | Manual, signal:S | 0 | 45
[13 empty] | 5891 | Manual, signal:F | 0 | 45
[13 empty] | 5892 | Manual, signal:K | 0 | 45
[13 empty] | 5893 | Manual, unknown signal chg | 0 | 45
[13 empty] | 5894 | Manual control canceled | 0 | 45
[13 empty] | 5895 | Blade load gain level | 0 | 45
[13 empty] | 5896 | IPC sync error | 0 | 45
[13 empty] | 5897 | Frequency error 5 | 0 | 45
[13 empty] | 5898 | Error on press. sensor S439 | 0 | 45
[13 empty] | 5899 | IPC derate | 0 | 45
[13 empty] | 5900 | PC max wind derate | 0 | 45
[13 empty] | 5901 | Pitch data error | 0 | 45
[13 empty] | 5902 | EMERGENCY after signal error | 0 | 45
[13 empty] | 5903 | GearOil pressure not stable | 0 | 45
[13 empty] | 5904 | Turbine cold, test not allowed | 0 | 45
[13 empty] | 5905 | Gen. slipring heater | 0 | 45
[13 empty] | 5906 | Startup without VCP board | 0 | 45
[13 empty] | 5907 | Reboot to enable VCP board | 0 | 45
[13 empty] | 5908 | Coil supply active in EMC | 0 | 45
[13 empty] | 5909 | 1P RBM Level | 0 | 45
[13 empty] | 5910 | 2P RBM Level | 0 | 45
[13 empty] | 5911 | RCPL FiltError | 0 | 45
[13 empty] | 5912 | RCPL Max Error | 0 | 45
[13 empty] | 5913 | Accu _ low prechg. press | 0 | 45
[13 empty] | 5914 | User Def Input __ Pause Slow | 0 | 45
[13 empty] | 5915 | User Def Input __ Pause Fast | 0 | 45
[13 empty] | 5916 | Extreme tilt moment: | 0 | 45
[13 empty] | 5917 | Extreme yaw moment: | 0 | 45
[13 empty] | 5918 | TYCOutOfOrder,deactivated | 0 | 45
[13 empty] | 5919 | RT activation no. exceeded: | 0 | 45
[13 empty] | 5920 | BldA Fan_ Press Diff NotOk | 0 | 45
[13 empty] | 5921 | BldB Fan_ Press Diff NotOk | 0 | 45
[13 empty] | 5922 | BldB Fan_ Press Diff NotOk | 0 | 45
[13 empty] | 5923 | Ch.high res.loadC_Load: | 0 | 45
[13 empty] | 5924 | Lightning detected ____ _ | 0 | 45
[13 empty] | 5925 | ModeSel Enter OverrideStopMode | 0 | 45
[13 empty] | 5926 | ModeSel Leave OverrideStopMode | 0 | 45
[13 empty] | 5930 | Lightning det. SN:__________ | 0 | 45
[13 empty] | 5931 | Cabinet conv. DC voltage fail | 0 | 45
[13 empty] | 5933 | BladeAAzimOffs: ___._ r2:_.__ | 0 | 45
[13 empty] | 5934 | BladeBAzimOffs: ___._ r2:_.__ | 0 | 45
[13 empty] | 5935 | BladeCAzimOffs: ___._ r2:_.__ | 0 | 45
[13 empty] | 5936 | GenSpdHighReverse: _____ RPM | 0 | 45
[13 empty] | 5937 | DcLinkCupper_HighTemp: ____ ¸°C | 0 | 45
[13 empty] | 5938 | ExtAirOutlet_HighTemp: ____ ¸°C | 0 | 45
[13 empty] | 5939 | WindSensor1 Failure | 0 | 45
[13 empty] | 5940 | WindSensor2 Failure | 0 | 45
[13 empty] | 5941 | Swg VDS Low voltage detected | 0 | 45
[13 empty] | 5942 | Swg VDS or HV fault | 0 | 45
[13 empty] | 5943 | Swg VDS fault | 0 | 45
[13 empty] | 5944 | Switchgear is open | 0 | 45
[13 empty] | 5945 | Swg open due to voltage fault | 0 | 45
[13 empty] | 5946 | Swg opened manually by pendant | 0 | 45
[13 empty] | 5947 | Conv. grid CBs safety FB error | 0 | 45
[13 empty] | 5948 | BrakeDrainingDurationError | 0 | 45
[13 empty] | 5949 | BrakeAccDrainingTooOfte:___ | 0 | 45
[13 empty] | 5950 | AGOStateTimeOut | 0 | 45
[13 empty] | 5951 | DeIcing safety swversion error | 0 | 45
[13 empty] | 5952 | SmokeDetector LockForInspect | 0 | 45
[13 empty] | 5954 | SmokeDetector Com. Error | 0 | 45
[13 empty] | 5955 | Deicing maincontactor fb error | 0 | 45
[13 empty] | 5956 | Deicing power unavailable | 0 | 45
[13 empty] | 5957 | Deicing mode selector no power | 0 | 45
[13 empty] | 5958 | Deicing cooling active | 0 | 45
[13 empty] | 5959 | Deicing main contactor test | 0 | 45
[13 empty] | 5960 | Pitch Oscillation in Blade A | 0 | 45
[13 empty] | 5961 | Pitch Oscillation in Blade B | 0 | 45
[13 empty] | 5962 | Pitch Oscillation in Blade C | 0 | 45
[13 empty] | 5963 | Diagnostics Available | 0 | 45
[13 empty] | 5964 | High Energy in Harm Filt ___J | 0 | 45
[13 empty] | 5965 | Modulation idx ___ Avg ___ | 0 | 45
[13 empty] | 5967 | MSI, arc detector no protocol | 0 | 45
[13 empty] | 5968 | LSI, arc detector no protocol | 0 | 45
[13 empty] | 5969 | Sw.gear, arc det. no protocol | 0 | 45
[13 empty] | 5970 | MSI, arc det. internal fault | 0 | 45
[13 empty] | 5972 | Sw.gear, arc det. int. fault | 0 | 45
[13 empty] | 5973 | Pitch Osc High in Blade A | 0 | 45
[13 empty] | 5974 | Pitch Osc High in Blade B | 0 | 45
[13 empty] | 5975 | Pitch Osc High in Blade C | 0 | 45
[13 empty] | 5984 | HubSafetySystem Batt.Serv.Req | 0 | 45
[13 empty] | 5990 | Converter MotorMode | 0 | 45
[13 empty] | 5991 | BladeLoadCalibrationNegAxial | 0 | 45
[13 empty] | 5993 | ConvIntFanMissingFB | 0 | 45
[13 empty] | 5994 | ConvExtLiquidCoolingNotOK | 0 | 45
[13 empty] | 5995 | ConvExtFanCoolingNotOK | 0 | 45
[13 empty] | 5996 | PowerBackupChargerNotStarted | 0 | 45
[13 empty] | 6002 | Backup power volt low | 0 | 45
[13 empty] | 6003 | Backup power volt very low | 0 | 45
[13 empty] | 6004 | Backup power volt critical low | 0 | 45
[13 empty] | 6005 | SafetyNac4 SwVers Error | 0 | 45
[13 empty] | 6006 | SafetyNac4 SwVers Temp Error | 0 | 45
[13 empty] | 6007 | SafetyNac4 Communication Error | 0 | 45
[13 empty] | 6008 | SafetyNac4 EKey Error | 0 | 45
[13 empty] | 6009 | SafetyNac4 Operational Error | 0 | 45
[13 empty] | 6011 | Pwr backup charger fuse error | 0 | 45
[13 empty] | 6012 | Pwr backup charger err on Ext | 0 | 45
[13 empty] | 6013 | GearHydrWaterCoolTempLow ___°C | 0 | 45
[13 empty] | 6026 | Smoke Detector Hub Error | 0 | 45
[13 empty] | 6027 | SmokeDetectorHubSmokeDetected | 0 | 45
[13 empty] | 6028 | SmokeDetetorHubMaintenanceMode | 0 | 45
[13 empty] | 6030 | SmokeDetector SwG HVCB blocked | 0 | 45
[13 empty] | 6031 | Power Backup AUX CB mismatch | 0 | 45
[13 empty] | 6032 | Power Backup Ext CB mismatch | 0 | 45
[13 empty] | 6033 | HubSafetyPowerSupply HwError | 0 | 45
[13 empty] | 6037 | AzimuthOffsetCorrectionChanged | 0 | 45
[13 empty] | 6039 | RtoP Reboot | 0 | 45
[13 empty] | 6056 | BladeA heat cont.secondary err | 0 | 45
[13 empty] | 6057 | BladeB heat cont.secondary err | 0 | 45
[13 empty] | 6058 | BladeC heat cont.secondary err | 0 | 45
[13 empty] | 6059 | Blade Heating Imbalance Error | 0 | 45
[13 empty] | 6060 | Cold Climate Trafo Temp High | 0 | 45
[13 empty] | 6065 | BldA heat elm.__ current:__._A | 0 | 45
[13 empty] | 6066 | BldB heat elm.__ current:__._A | 0 | 45
[13 empty] | 6067 | BldC heat elm.__ current:__._A | 0 | 45
[13 empty] | 6068 | Blade heat.pow.avg:___._ kW | 0 | 45
[13 empty] | 6069 | BladeA Heat Safety Err: _____ | 0 | 45
[13 empty] | 6070 | BladeB Heat Safety Err: _____ | 0 | 45
[13 empty] | 6071 | BladeC Heat Safety Err: _____ | 0 | 45
[13 empty] | 6072 | Bld.Heat Env.Temp.Err:___Â°C | 0 | 45
[13 empty] | 6073 | Awaiting safety reset pressed | 0 | 45
[13 empty] | 6074 | Awaiting safety reset pressed | 0 | 45
[13 empty] | 6075 | BladeA Heat. Leak Curr. Error | 0 | 45
[13 empty] | 6076 | BladeB Heat. Leak Curr. Error | 0 | 45
[13 empty] | 6077 | BladeC Heat. Leak Curr. Error | 0 | 45
[13 empty] | 6078 | Hub in safe mode pending | 0 | 45
[13 empty] | 6079 | IceDetectedInBladeAutoAckWarn | 0 | 45
[13 empty] | 6081 | SwappedWindSensors | 0 | 45
[13 empty] | 6082 | SafetySystemConvProtectionStop | 0 | 45
[13 empty] | 6083 | Safety Sw Version Acknowledged | 0 | 45
[13 empty] | 9999 | Unknown Log Number | 0 | 45
[13 empty] | 6293 | Pitch valves test acitve
[13 empty] | 6290 | Pitch Accu. Test active
[13 empty] | CE100001 | Manual Stop
[13 empty] | CE100002 | Major BD - Blade
[13 empty] | CE100003 | Major BD - Transformer
[13 empty] | CE100004 | Major BD - Generator
[13 empty] | CE100005 | Major BD - Gearbox
[13 empty] | CE100006 | Major BD - Main Bearing
[13 empty] | CE100007 | Transmission Line Related work
[13 empty] | CE100008 | General Work Stoppage
[13 empty] | CE100009 | Major BD - Power Cable
[13 empty] | CE100011 | Major BD - DFIG
[13 empty] | CE100012 | Major BD - Foundation
[13 empty] | CE100013 | Theft
[13 empty] | CE100010 | Manual Stop - Preventive Maintenance Activity
[13 empty] | CE100014 | Manual Stop - Audit
[13 empty] | CE100015 | Manual Stop - Safety Related
[13 empty] | CE100016 | Manual Stop - Blade Cleaning
[13 empty] | CE100017 | UPS breakdown