## O2Summary
Performance Summary Ghatodi Solar
Month | 2025-07-01
Date | 2025-07-13
Operation Year | 2026
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks | CC*Bugt (Daily) | CC*Bugt (MTD) | CC*Bugt (YTD)
1 | E_Grid Daily (MWh) | 171.307 | 150 | -12.44% |  | 123.5386 | 3829.6954 | 18028.8941
| E_Grid MTD(MWh) | 2226.9905 | 1328.3528 | -40.35%
| E_Grid YTD (MWh) | 18494.0042 | 15877 | -14.15%
2 | POA Daily | 3.8097 | 4.2805 | 12.36%
| POA MTD | 49.5258 | 38.3255 | -22.62%
| POA YTD | 586.6338 | 526.6732 | -10.22%
3 | PR Daily | 82.7% | 89.23% | 7.898%
| PR MTD | 82.7% | 88.4% | 6.884%
| PR YTD | 82.7% | 78.54% | -5.035%
4 | PA Daily | 99.5% | 100% | 0.5025%
| PA MTD | 99.5% | 96.62% | -2.891%
| PA YTD | 99.5% | 100% | 0.5025%
5 | GA Daily | 99.5% | 100% | 0.5025%
| GA MTD | 99.5% | 100% | 0.5025%
| GA YTD | 99.5% | 100% | 0.5025%
6 | CUF Daily | 13.13% | 11.5% | -12.44%
| CUF MTD | 13.13% | 7.831% | -40.35%
| CUF YTD | 13.63% | 11.7% | -14.15%
Performance Summary Ghatodi
Month | 2025-07-01
Date | 2025-07-13
Operation Year | 2026
Year Start Date | 2025-02-01
Year End Date | 2025-03-31
SPV | Particular | Target | Measured | Deviation | Remarks
O2RE7 | E_Grid MTD(MWh) | 1649706.7253 | 1000760.3 | -39.34%
O2RE27 | E_Grid MTD(MWh) | 577283.7768 | 354274.8 | -38.63%

## DGR
Name of the Project: Ghatodi
DC Capacity (In MWp): & AC Capacity (In MW):
DATE | Plant DC Capacity (KW) | Estimated IR (kWh/ M2) | Estimated Gen. (Kwh) | Estimated PR (%) | Estimated CUF (%) | Actual IR (kwh/m2) | Expected Gen. on Actual IR (kwh) | Actual Gen. (Export) (kwh) | Import (kwh) | Net Gen. (kwh) | Gen. loss due to BD (kwh) | Actual PR (%) | Actual PR Including BD loss (%) | Actual CUF (%) | Actual CUF Including BD loss (%) | Short / Excess Actual Power Gen. with Expected based on IR in kWh | PR Var. with Estimated PR (%) | Remark (Reasons for deviation) | Loss of Generation due to Breakdowns
[19 empty] | Duration |  | Downtime in Min. | IR during BD Period (Kwh/m2) | Actual/ Guaranteed PR (%) | BD Plant capacity (DC) in KWp | Gen. Loss = (IRxPRxDC Capacity) | Reason for Breakdown
[19 empty] | From | To
2025-07-01 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 1.747 | 78556.0637 | 53000 |  | 53000 | 0 | 77.37% | 77.37% | 5.632% | 5.632% | -25556.0637 | -37.31% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-02 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 2.929 | 131706.1881 | 100000 |  | 100000 | 0 | 87.07% | 87.07% | 10.63% | 10.63% | -31706.1881 | -27.61% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-03 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 3.92 | 176267.756 | 142000 |  | 142000 | 0 | 92.39% | 92.39% | 15.09% | 15.09% | -34267.756 | -22.29% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-04 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 2.71 | 121858.5762 | 100000 |  | 100000 | 0 | 94.11% | 94.11% | 10.63% | 10.63% | -21858.5762 | -20.57% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-05 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 2.95 | 132650.4797 | 107000 |  | 107000 | 0 | 92.5% | 92.5% | 11.37% | 11.37% | -25650.4797 | -22.18% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-06 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 2.06 | 92630.5044 | 75000 |  | 75000 | 0 | 92.85% | 92.85% | 7.97% | 7.97% | -17630.5044 | -21.83% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-07 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 1.39 | 62503.1074 | 57000 |  | 57000 | 0 | 104.6% | 104.6% | 6.057% | 6.057% | -5503.1074 | -10.1% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-08 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 1.72 | 77341.9746 | 66000 |  | 66000 | 0 | 97.86% | 97.86% | 7.014% | 7.014% | -11341.9746 | -16.82% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-09 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 1.45 | 65201.0832 | 55000 |  | 55000 | 0 | 96.74% | 96.74% | 5.845% | 5.845% | -10201.0832 | -17.94% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-10 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 1.66 | 74643.9987 | 59000 |  | 59000 | 0 | 90.65% | 90.65% | 6.27% | 6.27% | -15643.9987 | -24.03% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-11 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 5.579 | 250866.7885 | 191000 |  | 191000 | 0 | 87.31% | 87.31% | 20.3% | 20.3% | -59866.7885 | -27.37% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-12 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 5.93 | 266649.9472 | 189000 |  | 189000 | 0 | 81.28% | 81.28% | 20.08% | 20.08% | -77649.9472 | -33.4% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-13 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 4.2805 | 192478.0943 | 150000 |  | 150000 | 0 | 89.37% | 89.37% | 15.94% | 15.94% | -42478.0943 | -25.31% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-14 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-15 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-16 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-17 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-18 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-19 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-20 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-21 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-22 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-23 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-24 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-25 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-26 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-27 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-28 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-29 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-30 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
2025-07-31 | 39.21 | 3.8097 | 171306.9617 | 114.7% | 18.2% | 0 | 0 | 0 |  | 0 | 0 | 0% | 0% | 0% | 0% | 0 | -114.7% |  |  |  | 0 |  | 114.7% |  | 0
Month to date | 39.21 | 118.1 | 5310515.8128 | 114.7% | 18.2% | 38.3255 | 1723354.5621 | 1344000 | 0 | 1344000 | 0 | 91.08% | 91.08% | 10.99% | 10.99% | -379354.5621 | -23.6% |  |  |  | 0 |  |  |  | 0
Formulas:
DATE = [DATE, row above]+1

## AnnualKPI
Till Date | 2025-07-13 | 2025-07-01
Ghatodi Solar Performance Summary-YTD
Year | Days | Estimated POA(kWh/M2) | Measured POA(kWh/M2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Budgeted PR (MWh) | Measured PR(MWh)
2026 | 104 | 586.6338 | 526.6732 | 18494.0042 | 15877 | 13.63% | 11.7% | 99.5% | 100% | 99.5% | 100% | 82.7% | 78.54%

## MonthlyKPI
Till Date | 2025-07-13 | 0 | 0 | 0 | 0
Ghatodi Performance Summary Solar
Month | Days | Estimated POA(m/s) | Measured POA (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target PR (%) | Measured PR (%) | Measured WPR (%)
2025-07-01 | 13 | 49.5258 | 38.3255 | 2226.9905 | 1328.3528 | 13.13% | 7.831% | 99.5% | 100% | 99.5% | 96.62% | 82.7% | 88.4%
Start Date | 2025-07-07
End Date | 2025-07-13
Ghatodi Performance Summary Solar
Month | Days | Estimated POA(m/s) | Measured POA (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target PR (%) | Measured PR (%) | Measured WPR (%)
2025-07-01 | 7 | 26.6677 | 22.0095 | 1199.1487 | 757.5845 | 13.13% | 8.294% | 99.5% | 100% | 99.5% | 98.41% | 82.7% | 63.31%
Formulas:
Days = [Days, row below]-6

## SPV_Summary
Row Labels | Sum of O2RE7 | Sum of O2RE27
2025 | 8349710.65 | 1715597.49
Feb | 1263514 | 99126.39
Mar | 2993651.26 | 577993.2
Apr | 4092545.39 | 1038477.9
May | 0 | 0
Jun | 0 | 0
Jul | 0 | 0
Aug | 0 | 0
Sep | 0 | 0
Oct | 0 | 0
Nov | 0 | 0
Dec | 0 | 0
Grand Total | 8349710.65 | 1715597.49

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 11.5667 | 5.73 |  | 6.29 |  | 35.94 | 44.76 | 2.76 | 7.89 | [9 empty] | 147871.1 |  |  |  | 30.72 | 6.871 | 214258.0645 | 79.53% | 22.77% | 99.5% | 99.5% | [9 empty] | 39.21 | 167865.5379
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 11.5667 | 5.68 |  | 5.81 |  | 36.33 | 44.98 | 2.06 | 7.88 | 100% |  |  | 100% |  |  | 77.89% |  | 14.77% | 141377.1 | 140000 |  | 139023.2324 | 30.72 | 6.871 | 214258.0645 | 79.53% | 22.77% | 99.5% | 99.5% | [9 empty] | 39.21 | 167865.5379
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 11.4333 | 5.15 |  | 5.26 |  | 36.3 | 45.84 | 1.74 | 4.8 | 100% |  |  | 100% |  |  | 78.6% |  | 13.5% | 129252.4 | 128000 |  | 127012.439 | 30.72 | 6.871 | 214258.0645 | 79.53% | 22.77% | 99.5% | 99.5% | [9 empty] | 39.21 | 167865.5379
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 10.7667 | 4.28 |  | 4.29 |  | 35 | 43.05 | 1.88 | 5.22 | 100% |  |  | 100% |  |  | 74.38% |  | 11.41% | 109008 | 108000 |  | 107335.9419 | 33.64 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 143025.5546
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 11.65 | 5.4 |  | 5.47 |  | 33.62 | 41.29 | 3.31 | 7.96 | 100% |  |  | 100% |  |  | 76.16% |  | 14.9% | 142503.7 | 141000 |  | 140144.8448 | 33.64 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 143025.5546
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 10.95 | 4.86 |  | 4.93 |  | 31.69 | 39.79 | 3.55 | 9.87 | 100% |  |  | 100% |  |  | 74.66% |  | 13.17% | 125939.3 | 125000 |  | 123818.9453 | 33.64 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 143025.5546
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 11.65 | 6.38 |  | 6.45 |  | 32.73 | 45.1 | 2.19 | 6.83 | 100% |  |  | 100% |  |  | 77.42% |  | 17.86% | 170766.2 | 169000 |  | 167973.8064 | 33.64 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 143025.5546
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 11.75 | 6.44 |  | 6.5 |  | 35.47 | 47.05 | 2.18 | 6.22 | 100% |  |  | 100% |  |  | 77.18% |  | 17.95% | 171536.5 | 170000 |  | 168771.1814 | 33.64 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 143025.5546
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 11.8 | 7.08 |  | 7.13 |  | 36.69 | 46.52 | 2.38 | 9.06 | 85.22% |  |  | 100% |  |  | 65.83% |  | 16.79% | 160533.8 | 159000 |  | 157902.4761 | 33.64 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 143025.5546
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 11.8 | 6.77 |  | 6.82 |  | 37.89 | 46.46 | 2.52 | 9.18 | 96.94% |  |  | 100% |  |  | 76.35% |  | 18.63% | 178266.9 | 176000 |  | 175176.1617 | 33.64 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 143025.5546
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 11.8 | 6.36 |  | 6.4 |  | 37.07 | 47.88 | 2.45 | 6.44 | 100% |  |  | 100% |  |  | 78.32% |  | 17.93% | 171545.1 | 169000 |  | 168609.0979 | 33.64 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 143025.5546
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 11.5333 | 6.17 |  | 6.21 |  | 36.2 | 46.92 | 2.91 | 6.66 | 100% |  |  | 100% |  |  | 75.8% |  | 17.67% | 169153.5 | 168000 |  | 166200.9385 | 35.31 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 150125.8125
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 11.8333 | 6.25 |  | 6.27 |  | 36.95 | 46.54 | 2.86 | 8.27 | 100% |  |  | 100% |  |  | 79.27% |  | 18.66% | 178601 | 176000 |  | 175488.5179 | 35.31 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 150125.8125
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 11.7 | 6.52 |  | 6.52 |  | 36.73 | 45.41 | 3.15 | 7.42 | 92.99% |  |  | 100% |  |  | 74.07% |  | 18.13% | 173429.4 | 172000 |  | 170527.5009 | 35.31 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 150125.8125
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 11.3833 | 6.66 |  | 6.67 |  | 36.52 | 48.68 | 3.66 | 8.68 | 100% |  |  | 100% |  |  | 77.51% |  | 19.41% | 185766.6 | 184000 |  | 182538.4826 | 35.31 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 150125.8125
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 11.95 | 6.24 |  | 6.15 |  | 36.53 | 44.93 | 2.98 | 7.7 | 100% |  |  | 100% |  |  | 74.93% |  | 17.3% | 165703.6 | 163000 |  | 162709.4831 | 35.31 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 150125.8125
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 11.85 | 6.7 |  | 6.68 |  | 36.76 | 45.63 | 3.14 | 9.32 | 100% |  |  | 100% |  |  | 74.74% |  | 18.75% | 179771 | 178000 |  | 176283.6075 | 35.31 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 150125.8125
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 11.9167 | 6.3 |  | 6.23 |  | 37.45 | 46.26 | 3.09 | 10.7 | 100% |  |  | 100% |  |  | 77.02% |  | 18.02% | 171919.8 | 170000 |  | 169428.0824 | 35.31 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 150125.8125
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 11.8333 | 6.1 |  | 6.05 |  | 36.22 | 47 | 2.37 | 6.75 | 100% |  |  | 100% |  |  | 77.28% |  | 17.56% | 167880.4 | 166000 |  | 165095.0939 | 35.31 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 150125.8125
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 11.8833 | 6.45 |  | 6.39 |  | 37.65 | 48.8 | 2.2 | 9.02 | 100% |  |  | 100% |  |  | 75.01% |  | 18% | 173337.6 | 171000 |  | 169242.1127 | 35.31 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 150125.8125
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 11.6833 | 4.45 |  | 4.41 |  | 36.84 | 44.34 | 2.73 | 9.4 | 100% |  |  | 100% |  |  | 77.98% |  | 12.91% | 123455.7 | 122000 |  | 121427.3244 | 35.31 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 150125.8125
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 12.0333 | 7.01 |  | 6.92 |  | 38.5 | 47.72 | 3.12 | 7.92 | 100% |  |  | 100% |  |  | 76.74% |  | 19.94% | 190763.1 | 188000 |  | 187498.6667 | 35.31 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 150125.8125
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 12.15 | 7.17 |  | 7.05 |  | 38.97 | 49.7 | 2.77 | 7.35 | 100% |  |  | 100% |  |  | 76.66% |  | 20.29% | 194360.7 | 193000 |  | 190836.0054 | 35.31 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 150125.8125
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 12.0667 | 7.28 |  | 7.16 |  | 38.88 | 50.19 | 2.91 | 7.53 | 97.04% |  |  | 100% |  |  | 72.01% |  | 19.36% | 185473 | 183000 |  | 182045.0426 | 35.31 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 150125.8125
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 12.0667 | 7.03 |  | 6.85 |  | 39.34 | 50.33 | 2.3 | 6.44 | 98.7% |  |  | 100% |  |  | 76.45% |  | 19.66% | 188205.19 | 186000 |  | 184923.809 | 35.31 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 150125.8125
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 6.09 |  | 6.01 |  | 39.86 | 50.62 | 2.97 | 7.13 | 98.9% |  |  | 100% |  |  | 78.95% |  | 19.78% | 189521.8 | 187000 |  | 186045.1492 | 39.21 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 166707.2531
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 12.0667 | 7 |  | 6.83 |  | 39.48 | 50.97 | 2.22 | 6.45 | 97.42% |  |  | 100% |  |  | 67.74% |  | 19.29% | 181268.3 | 182000 |  | 181418.1457 | 39.21 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 166707.2531
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 11.8667 | 6.45 |  | 6.25 |  | 39.48 | 48.98 | 2.29 | 7.53 | 100% |  |  | 100% |  |  | 69.13% |  | 18.01% | 172704.4 | 171000 |  | 169405.265 | 39.21 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 166707.2531
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 12.05 | 5.92 |  | 5.75 |  | 37.77 | 46.78 | 3.31 | 11.44 | 99.79% |  |  | 100% |  |  | 71.95% |  | 17.25% | 165110.1 | 163000 |  | 162216.2495 | 39.21 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 166707.2531
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 12.1833 | 6.96 |  | 6.9 |  | 35.22 | 46.45 | 2.92 | 8.41 | 99.44% |  |  | 100% |  |  | 69.66% |  | 20.04% | 191696.8 | 190000 |  | 188457.5795 | 39.21 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 166707.2531
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 12.1167 | 6.52 |  | 6.28 |  | 37.8 | 47.71 | 3.28 | 8.31 | 99.1% |  |  | 100% |  |  | 69.06% |  | 18.08% | 173178 | 171000 |  | 170054.8042 | 39.21 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 166707.2531
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 12.0167 | 6.81 |  | 6.54 |  | 38.44 | 49.35 | 2.64 | 8.23 | 100% |  |  | 100% |  |  | 72.18% |  | 19.68% | 188809.2 | 187000 |  | 185090.7028 | 39.21 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 166707.2531
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 12.1667 | 6.76 |  | 6.45 |  | 38.89 | 48.04 | 3.72 | 9.53 | 100% |  |  | 100% |  |  | 74.32% |  | 19.99% | 190814.6 | 188000 |  | 187969.9952 | 39.21 | 6.0635 | 166595.6473 | 70.12% | 17.72% | 99.5% | 99.5% | [9 empty] | 39.1838 | 166707.2531
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 6.24 |  | 6.12 |  | 37.42 | 49.2 | 2.08 | 5.61 | 100% |  |  | 100% |  |  | 72.4% |  | 15.76% | 177267.9 | 175000 |  | 173730.8622 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 12.2167 | 6.52 |  | 6.39 |  | 38.17 | 47.52 | 3.04 | 8.62 | 99.93% |  |  | 100% |  |  | 71.76% |  | 16.31% | 182791.8 | 181000 |  | 179802.1245 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 12.2667 | 6.65 |  | 6.42 |  | 38.62 | 48.41 | 2.78 | 7.26 | 93.79% |  |  | 100% |  |  | 70.47% |  | 16.09% | 180735.1 | 179000 |  | 177395.75 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 12.3 | 7.03 |  | 6.79 |  | 35.28 | 48.06 | 2.25 | 5.72 | 94.5% |  |  | 100% |  |  | 72.77% |  | 17.57% | 197226.4 | 195000 |  | 193731.8055 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 11.15 | 6.02 |  | 5.79 |  | 34.85 | 47.54 | 2.63 | 13.16 | 95.01% |  |  | 100% |  |  | 79.27% |  | 16.33% | 183079.5 | 181000 |  | 179974.2194 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 11.1833 | 7.3 |  | 7.04 |  | 35.07 | 35.07 | 3.03 | 7.66 | 93.84% |  |  | 100% |  |  | 72.44% |  | 18.14% | 203662.5 | 201000 |  | 199964.6947 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 11.95 | 7.43 |  | 7.12 |  | 33.29 | 46.34 | 3.49 | 15.01 | 89.15% |  |  | 100% |  |  | 65.27% |  | 16.53% | 185564.6 | 183000 |  | 182226.7464 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 11.8833 | 6.83 |  | 6.57 |  | 33.46 | 46.01 | 3.02 | 8.76 | 87.52% |  |  | 100% |  |  | 65.89% |  | 15.4% | 172861.4 | 171000 |  | 169730.6469 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 12.0333 | 7.28 |  | 7.02 |  | 35.61 | 49.14 | 2.34 | 6.85 | 97.23% |  |  | 100% |  |  | 73.11% |  | 18.26% | 204806 | 203000 |  | 201244.9568 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 12.4333 | 6.27 |  | 6.01 |  | 35.81 | 46.41 | 2.59 | 8.49 | 94.64% |  |  | 100% |  |  | 73.45% |  | 15.7% | 176198.1 | 174000 |  | 173095.3206 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 11.9667 | 6.7 |  | 6.45 |  | 35.93 | 47.43 | 2.3 | 6.74 | 94.79% |  |  | 100% |  |  | 75.72% |  | 17.37% | 194866.3 | 193000 |  | 191488.2507 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 11.5167 | 2.67 |  | 2.62 |  | 30.36 | 34.92 | 1.9 | 5.8 | 95.24% |  |  | 100% |  |  | 84.25% |  | 7.851% | 88349 | 87000 |  | 86547.6603 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 11.3833 | 3.23 |  | 3.18 |  | 28.47 | 34.35 | 2.59 | 6.84 | 96.48% |  |  | 100% |  |  | 114.2% |  | 12.91% | 145288.6 | 144000 |  | 142361.5676 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 12.25 | 4.31 |  | 4.15 |  | 33.94 | 41.83 | 2.26 | 6.66 | 100% |  |  | 100% |  |  | 74.42% |  | 10.98% | 122942.7 | 122000 |  | 121093.3113 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 12.3333 | 4.91 |  | 4.77 |  | 33.31 | 41.68 | 2.82 | 10.69 | 95.05% |  |  | 100% |  |  | 79.37% |  | 13.47% | 150653.1 | 150000 |  | 148454.2332 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 12.25 | 5.55 |  | 5.39 |  | 33.82 | 43.71 | 2.93 | 9.26 | 97.22% |  |  | 100% |  |  | 79.4% |  | 15.22% | 170690.3 | 169000 |  | 167811.703 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 11.4833 | 5.46 |  | 5.34 |  | 33.51 | 44.31 | 2.57 | 8.06 | 99.97% |  |  | 100% |  |  | 81.07% |  | 15.4% | 172444 | 170000 |  | 169749.6318 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 12.2833 | 6.07 |  | 5.82 |  | 35.43 | 46.81 | 2.04 | 6.31 | 99.84% |  |  | 100% |  |  | 80.05% |  | 16.57% | 185854.7 | 185000 |  | 182671.0454 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 12.3167 | 5.53 |  | 5.31 |  | 33.41 | 43.82 | 1.7 | 11.93 | 99.81% |  |  | 100% |  |  | 83.52% |  | 15.77% | 176960.2 | 175000 |  | 173903.1683 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 5.15 |  | 4.91 |  | 34.88 | 43.35 | 2.46 | 14.53 | 100% |  |  | 100% |  |  | 83.93% |  | 14.66% | 164452.7 | 162000 |  | 161578.9083 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 12.2667 | 4.5 |  | 4.36 |  | 30.53 | 39.47 | 2.39 | 14.28 | 100% |  |  | 100% |  |  | 88.06% |  | 13.66% | 152923.9 | 152000 |  | 150536.0345 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 12.3 | 3.4 |  | 3.32 |  | 28.46 | 34.88 | 1.94 | 5.2 | 98.72% |  |  | 100% |  |  | 87.25% |  | 10.3% | 115421.3 | 115000 |  | 113582.7465 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 11.0833 | 3.8 |  | 3.67 |  | 30.01 | 38.16 | 1.98 | 5.6 | 99.97% |  |  | 100% |  |  | 87.72% |  | 11.45% | 128400.8 | 127000 |  | 126235.4246 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 11.35 | 3.39 |  | 3.33 |  | 28.12 | 35.05 | 1.92 | 7.93 | 89.92% |  |  | 100% |  |  | 73.87% |  | 8.75% | 98383.4 | 98000 |  | 96456.0531 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 12.1667 | 5.29 |  | 5.06 |  | 30.16 | 39.49 | 1.97 | 7.16 | 98.26% |  |  | 100% |  |  | 79.11% |  | 14.24% | 159255.7 | 158000 |  | 156953.1091 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 12.6667 | 5.99 |  | 5.58 |  | 32.11 | 40.13 | 2.73 | 8.16 | 100% |  |  | 100% |  |  | 83.14% |  | 16.5% | 184885.9 | 183000 |  | 181903.4687 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 12.15 | 3.82 |  | 3.71 |  | 30.66 | 37.84 | 2.56 | 6.52 | 100% |  |  | 100% |  |  | 87% |  | 11.48% | 128758.7 | 127000 |  | 126558.4703 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 12.0833 | 2.87 |  | 2.79 |  | 28.48 | 32.9711 | 2.444 | 6.14 | 100% |  |  | 100% |  |  | 90.23% |  | 8.953% | 100304.2 | 100000 |  | 98703.4036 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 12.25 | 5.59 |  | 5.38 |  | 32.35 | 39.62 | 3.94 | 10.17 | 100% |  |  | 100% |  |  | 86.69% |  | 16.59% | 184742.9 | 183000 |  | 182869.9076 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 12.4 | 3.504 |  | 3.368 |  | 31.092 | 35.154 | 3.29 | 7.67 | 99.95% |  |  | 100% |  |  | 90.97% |  | 10.9% | 123069.8 | 122000 |  | 120131.8242 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 12.4833 | 7.06 |  | 6.71 |  | 33.61 | 42.51 | 4.68 | 8.79 | 100% |  |  | 100% |  |  | 81.85% |  | 19.53% | 219098.9 | 217000 |  | 215347.5111 | 39.21 | 6.8323 | 200698.5782 | 63.95% | 18.21% | 99.5% | 99.5% | [9 empty] | 45.9338 | 171320.4616
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 6.96 |  | 6.58 |  | 33.58 | 45.55 | 4.62 | 9.42 | 100% |  |  | 44.57% |  |  | 36.4% |  | 8.518% | 95299.6 | 94000 |  | 93899.8935 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 12.4833 | 6.49 |  | 6.1 |  | 32.75 | 43.67 | 3.97 | 8.55 | 100% |  |  | 100% |  |  | 82.07% |  | 17.81% | 199668.5 | 198000 |  | 196295.4511 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 12.5667 | 6.54 |  | 6.08 |  | 33.88 | 42.48 | 4.46 | 9.18 | 99.93% |  |  | 100% |  |  | 82.27% |  | 17.79% | 199550.7 | 197000 |  | 196126.1408 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 12.55 | 6.81 |  | 6.32 |  | 33.85 | 45.19 | 3.2 | 8.39 | 100% |  |  | 100% |  |  | 80.72% |  | 18.14% | 203656.4 | 202000 |  | 200020.7958 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 12.25 | 5.42 |  | 5.25 |  | 32.74 | 43.09 | 1.96 | 6.64 | 99.93% |  |  | 100% |  |  | 80.56% |  | 15.04% | 168885.5 | 167000 |  | 165831.8862 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 7.22 |  | 6.77 |  | 35.74 | 36.48 | 2.27 | 6.36 | 100% |  |  | 100% |  |  | 80.26% |  | 19.33% | 217073 | 214000 |  | 213045.7639 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 12.3167 | 5.54 |  | 5.23 |  | 34.45 | 40.98 | 3.45 | 10.47 | 100% |  |  | 100% |  |  | 82.58% |  | 15.36% | 172414.9 | 171000 |  | 169344.119 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 12.55 | 5.95 |  | 5.65 |  | 35.87 | 42.72 | 4.45 | 9.21 | 100% |  |  | 100% |  |  | 84.47% |  | 16.98% | 190546.7 | 188000 |  | 187136.0479 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 12.15 | 6.56 |  | 6.21 |  | 36.05 | 44.68 | 4.65 | 9.27 | 99.93% |  |  | 100% |  |  | 82.88% |  | 18.31% | 205464 | 204000 |  | 201816.8847 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 10.35 | 4.93 |  | 4.76 |  | 33.84 | 40.71 | 4.86 | 22.74 | 100% |  |  | 100% |  |  | 86.72% |  | 14.68% | 164762 | 163000 |  | 161851.9708 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 10.6 | 4.65 |  | 4.53 |  | 31.42 | 41.11 | 2.13 | 9.66 | 100% |  |  | 100% |  |  | 85.09% |  | 13.71% | 154046 | 152000 |  | 151135.1065 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 12.35 | 3.62 |  | 3.5 |  | 31.05 | 36.9 | 2.04 | 7.18 | 99.93% |  |  | 100% |  |  | 84.69% |  | 10.54% | 118676 | 118000 |  | 116223.6559 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 12.3167 | 5.05 |  | 4.83 |  | 32.37 | 41.61 | 1.86 | 3.14 | 99.88% |  |  | 100% |  |  | 83.27% |  | 14.3% | 160770 | 159000 |  | 157699.4484 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 12.4833 | 6.42 |  | 6 |  | 34.28 | 45.49 | 2.42 | 7.64 | 100% |  |  | 100% |  |  | 81.91% |  | 17.48% | 195698.6 | 194000 |  | 192711.4985 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 5.38 |  | 5.21 |  | 32.48 | 41.41 | 3.51 | 7.84 | 100% |  |  | 100% |  |  | 79.96% |  | 14.82% | 166318.4 | 164000 |  | 163337.3332 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 12.0333 | 3.72 |  | 3.63 |  | 29.49 | 36.21 | 3.05 | 7.5 | 100% |  |  | 100% |  |  | 85.46% |  | 11.03% | 123833.3 | 123000 |  | 121635.0185 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 12.6667 | 6.82 |  | 6.38 |  | 32.42 | 42.24 | 5.16 | 10.17 | 100% |  |  | 100% |  |  | 83.11% |  | 18.86% | 211561.3 | 210000 |  | 207919.5922 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 12.8333 | 4.51 |  | 4.21 |  | 30.68 | 36.66 | 5.1 | 13.52 | 100% |  |  | 100% |  |  | 85.84% |  | 12.85% | 144313.8 | 143000 |  | 141698.257 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 11 | 4.03 |  | 3.91 |  | 29.64 | 36.14 | 5.14 | 14.85 | 100% |  |  | 100% |  |  | 83.35% |  | 11.59% | 130305.8 | 128000 |  | 127779.6212 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 6.46 |  | 6.13 |  | 31.83 | 39.69 | 5.37 | 11.97 | 100% |  |  | 100% |  |  | 82.84% |  | 18.06% | 202592.2 | 201000 |  | 199102.2499 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 12.4833 | 5.11 |  | 4.85 |  | 30.4 | 37.59 | 4.09 | 13.91 | 100% |  |  | 100% |  |  | 83.67% |  | 14.43% | 161985 | 161000 |  | 159118.2607 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 12.1667 | 4.5 |  | 4.4 |  | 30.53 | 36.64 | 4.75 | 10.61 | 100% |  |  | 100% |  |  | 85.37% |  | 13.36% | 149880 | 148000 |  | 147286.5775 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 12.3833 | 3 |  | 2.87 |  | 29.43 | 32.99 | 4.05 | 8.89 | 100% |  |  | 100% |  |  | 90.8% |  | 9.269% | 103942 | 103000 |  | 102183.5796 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 12.2167 | 4.222 |  | 4.112 |  | 28.766 | 34.624 | 4.596 | 11.02 | 100% |  |  | 100% |  |  | 85.49% |  | 12.5% | 140669.2 | 140000 |  | 137837.0929 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 11.7167 | 2.84 |  | 2.79 |  | 28.997 | 33.98 | 2.891 | 10.85 | 100% |  |  | 100% |  |  | 96.48% |  | 9.574% | 106920.5 | 106000 |  | 105548.0815 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 9.9833 | 0.94666 |  | 0.9487 |  | 25.18 | 25.71 | 2.33 | 5.3 | 81.68% |  |  | 100% |  |  | 69.41% |  | 2.342% | 27160 | 27000 |  | 25820.6417 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 12.6333 | 4.32 |  | 4.18 |  | 29.35 | 36.57 | 3.197 | 8.59 | 100% |  |  | 100% |  |  | 87.95% |  | 13.08% | 146718.2 | 145000 |  | 144155.1054 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 11.9833 | 4.9455 |  | 4.749 |  | 30.309 | 37.622 | 4.7416 | 10.52 | 99.94% |  |  | 100% |  |  | 86.52% |  | 14.61% | 163808.7 | 163000 |  | 161108.2976 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 11.4167 | 1.406 |  | 1.4 |  | 25.0888 | 26.024 | 2.861 | 8.32 | 56.98% |  |  | 100% |  |  | 49.31% |  | 2.456% | 28102.4 | 28000 |  | 27070.1107 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 11.3833 | 1.73 |  | 1.72 |  | 25.98 | 28.19 | 2.83 | 7.2 | 100% |  |  | 100% |  |  | 93.59% |  | 5.725% | 64726.1 | 64000 |  | 63118.0105 | 39.21 | 4.78 | 168249.611 | 76.63% | 15.26% | 99.5% | 99.5% | [9 empty] | 45.9338 | 143621.3514
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | 11.8 | 1.749 |  | 1.747 |  | 26.297 | 28.05 | 3.21 | 7.29 | 83.36% |  |  | 100% |  |  | 76.49% |  | 4.015% | 53579.8 | 53000 |  | 52393.1298 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | 11.45 | 2.955 |  | 2.929 |  | 28.278 | 33.41 | 4.26 | 12.1 | 94.81% |  |  | 100% |  |  | 85.57% |  | 7.531% | 100110.1 | 100000 |  | 98270.6002 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | 12.3333 | 3.99 |  | 3.92 |  | 29.07 | 35.27 | 3.9 | 8.73 | 99.93% |  |  | 100% |  |  | 91.94% |  | 10.83% | 143810.7 | 142000 |  | 141316.728 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | 11.6167 | 2.74 |  | 2.71 |  | 28.22 | 32.41 | 3.62 | 11.91 | 100% |  |  | 100% |  |  | 92.44% |  | 7.528% | 100157.1 | 100000 |  | 98229.1879 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | 11.5333 | 3 |  | 2.95 |  | 28.56 | 33.66 | 3.87 | 9.07 | 100% |  |  | 100% |  |  | 91.75% |  | 8.133% | 107921.5 | 107000 |  | 106122.8682 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | 11.4167 | 2.09 |  | 2.06 |  | 26.86 | 30 | 3.47 | 7.6 | 89.15% |  |  | 100% |  |  | 92.15% |  | 5.704% | 76070.5 | 75000 |  | 74435.7872 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | 11.95 | 1.39 |  | 1.39 |  | 25.01 | 25.15 | 3.9 | 8.42 | 100% |  |  | 100% |  |  | 101.2% |  | 4.227% | 56879.6 | 57000 |  | 55162.6222 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | 11.65 | 1.7 |  | 1.72 |  | 25.64 | 26.104 | 3.26 | 6.65 | 99.93% |  |  | 100% |  |  | 95.31% |  | 4.926% | 66352.1 | 66000 |  | 64276.1194 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | 11.9833 | 1.445 |  | 1.45 |  | 25.149 | 26.08 | 2.99 | 5.35 | 100% |  |  | 100% |  |  | 96.08% |  | 4.186% | 56192 | 55000 |  | 54627.4941 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | 10.6 | 1.67 |  | 1.66 |  | 25.05 | 26.89 | 2.62 | 6.32 | 91.16% |  |  | 100% |  |  | 87.71% |  | 4.375% | 58523.4 | 59000 |  | 57090.1137 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | 12.65 | 5.842 |  | 5.579 |  | 29.898 | 37.64 | 3.77 | 7.67 | 100% |  |  | 100% |  |  | 87.05% |  | 14.59% | 193454.2 | 191000 |  | 190418.2334 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | 12.6167 | 6.17 |  | 5.93 |  | 30.19 | 37.99 | 4.29 | 9.12 | 97.75% |  |  | 100% |  |  | 80.1% |  | 14.27% | 190586.4 | 189000 |  | 186240.2834 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | 12.5 | 4.395 |  | 4.2805 |  | 29.503 | 35.71 | 4.06 | 10.17 | 100% |  |  | 100% |  |  | 89.23% |  | 11.48% | 151397.7 | 150000 |  | 149769.6468 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 39.21 | 3.8097 | 171306.9617 | 82.7% | 13.13% | 99.5% | 99.5% | [9 empty] | 54.3713 | 123538.5607
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 3.9097 | 185476.6696 | 87.25% | 14.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 4.91 | 224556.0795 | 84.12% | 17.21% | 99.5% | 99.5% | [9 empty] | 54.3713 | 0
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.7677 | 551238.5395 | 70.79% | 17.01% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.6467 | 573694.3848 | 75.26% | 17.71% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 |  | 0 | 0 | 5.5258 | 589943.4924 | 79.08% | 18.21% | 99.5% | 99.5% | [9 empty] | 135 | 0
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.6323 | 661640.3462 | 87.02% | 20.42% | 99.5% | 99.5% | [9 empty] | 135
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3607 | 737121.348 | 85.84% | 22.75% | 99.5% | 99.5% | [9 empty] | 135
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.871 | 762147.6224 | 82.17% | 23.52% | 99.5% | 99.5% | [9 empty] | 135
Formulas:
Month Year = Daily_KPI[[#This Row],[Date]]-DAY(Daily_KPI[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Input_Raw
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
[7 empty] | O2RE7 | O2RE7 | O2RE7 | O2RE7 | O2RE7 | O2RE27 | O2RE27 | O2R4_P3 | O2R4_P3 | [11 empty] | 0 | 0.178 |  | 0.1
[7 empty] | 1 | 1 | 2 | 2 | 3 | 4 | 4 | [17 empty] | Calculated Energy Numbers
Date | Finacial Year | Calendor Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | IS1Inv1 | IS1Inv2 | IS2Inv1 | IS2Inv2 | IS3Inv1 | IS4Inv1 | IS4Inv2 | IS15_Inv1_M1 | IS15_Inv1_M2 | POA_UP_IS1 (KWh/m2) | GHI_UP_IS1 (KWh/m2) | AT_IS1 (°C) | MT_IS1 (°C) | RH_IS1 (%) | Rain_IS1 (mm) | WS_Avg_IS1 (m/s) | WS_Max_IS1 (m/s) | O2RE7 | O2RE27 | Inv Total Gneration (MWh) | 33 kV_F1_Ex | 33kV_OG1_Ex | 220kV_TX1_Ex | 220kV_TL_TVM_Ex | 220kV_C&R_PQM_Ex | 220kV_C&R_PQM_Imp | 33kV_Aux1_Im | 33 kV_Solar_F1_Energy (kWh) | 33kV_OG1_Energy (KWh) | 220kV_TL_TVM Energy (KWh) | 220kV_C&R_PQM_Ex (KWh) | 220kV_C&R_PQM_Imp (KWh)2 | 33kV_Aux1_Im(KWh) | 33 kV Total Export (KWH) | 220 KV Net Export (KWh) | 33 kV Line Loss (%) | Operating Hours | Export (33 kV) | Net Export | Connected DC Capcity (MWp) | E_AC (WPR) | E_DC (WPR) | WPR (%)
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 6:36 | 18:10 | 21911.1 | 21381.1 | 29468.8 | 29598.8 | 10397.8 | 20540.7 | 14572.8 |  |  | 6.29 | 5.73 | 35.94 | 44.76 | 17.07 | 0 | 2.76 | 7.89 | 112757.6 | 35113.5 | 147871.1 |  | 5633 |  | 3964 | 5417.35 | 0.04 | 0.68 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | 11.5667 | #REF! | #REF! | 30.72
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 6:35 | 18:09 | 21251.8 | 20537.2 | 27288.8 | 28301.4 | 9591.5 | 20442.5 | 13963.9 |  |  | 5.81 | 5.68 | 36.33 | 44.98 | 16.32 | 0 | 2.06 | 7.88 | 106970.7 | 34406.4 | 141377.1 |  | 5773 |  | 4050.9 | 5556.0215 | 0.04 | 0.69 |  | 140000 | 139040 | 138671.5 | 10 | 10 | 140000 | 139030 | 0.6977% | 11.5667 | 140000 | 139023.2324 | 30.72
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 6:37 | 18:03 | 19012.1 | 18444.5 | 24547.8 | 26020.4 | 8594.9 | 18677.4 | 13955.3 |  |  | 5.26 | 5.15 | 36.3 | 45.84 | 22.59 | 0 | 1.74 | 4.8 | 96619.7 | 32632.7 | 129252.4 |  | 5901 |  | 4130.3 | 5682.814 | 0.04 | 0.71 |  | 128000 | 127040 | 126792.5 | 20 | 20 | 128000 | 127020 | 0.7715% | 11.4333 | 128000 | 127012.439 | 30.72
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 6:34 | 17:20 | 15477.5 | 15003.3 | 21701.9 | 21077.5 | 7020.8 | 16212.1 | 12514.9 |  |  | 4.29 | 4.28 | 35 | 43.05 | 29.12 | 0 | 1.88 | 5.22 | 80281 | 28727 | 109008 |  | 6009 |  | 4197.4 | 5789.535 | 0.04 | 0.73 |  | 108000 | 107360 | 106721 | 20 | 20 | 108000 | 107340 | 0.6149% | 10.7667 | 108000 | 107335.9419 | 33.64
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 6:34 | 18:13 | 19849.7 | 19221 | 28054.5 | 27826.8 | 10420.3 | 20997 | 16134.4 |  |  | 5.47 | 5.4 | 33.62 | 41.29 | 33.81 | 0 | 3.31 | 7.96 | 105372.3 | 37131.4 | 142503.7 |  | 6150 |  | 4285 | 5929.448 | 0.04 | 0.74 |  | 141000 | 140160 | 139913 | 10 | 10 | 141000 | 140150 | 0.6065% | 11.65 | 141000 | 140144.8448 | 33.64
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 6:35 | 17:32 | 17770.2 | 17182.5 | 25413.9 | 25418 | 10899.5 | 19071 | 10184.2 |  |  | 4.93 | 4.86 | 31.69 | 39.79 | 38.84 | 0 | 3.55 | 9.87 | 96684.1 | 29255.2 | 125939.3 |  | 6275 |  | 4362.4 | 6053 | 0.04 | 0.75 |  | 125000 | 123840 | 123552 | 10 | 10 | 125000 | 123830 | 0.9448% | 10.95 | 125000 | 123818.9453 | 33.64
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 6:33 | 18:12 | 23201.2 | 22190.3 | 32311.6 | 32744 | 16878.2 | 24438.7 | 19002.2 |  |  | 6.45 | 6.38 | 32.73 | 45.1 | 41.09 | 0 | 2.19 | 6.83 | 127325.3 | 43440.9 | 170766.2 |  | 6444 |  | 4467.4 | 6220.714 | 0.04 | 0.77 |  | 169000 | 168000 | 167714 | 20 | 20 | 169000 | 167980 | 0.6072% | 11.65 | 169000 | 167973.8064 | 33.64
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 6:30 | 18:15 | 23433.3 | 22152.5 | 31686.8 | 32557.8 | 18545.6 | 18955.2 | 24205.3 |  |  | 6.5 | 6.44 | 35.47 | 47.05 | 26.42 | 0 | 2.18 | 6.22 | 128376 | 43160.5 | 171536.5 |  | 6614 |  | 4572.9 | 6389.29 | 0.04 | 0.79 |  | 170000 | 168800 | 168576 | 20 | 20 | 170000 | 168780 | 0.7228% | 11.75 | 170000 | 168771.1814 | 33.64
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 6:27 | 18:15 | 25208 | 24960.8 | 19613 | 20543.6 | 22565.7 | 20954.5 | 26688.2 |  |  | 7.13 | 7.08 | 36.69 | 46.52 | 15.91 | 0 | 2.38 | 9.06 | 112891.1 | 47642.7 | 160533.8 |  | 6773 |  | 4671.6 | 6546.8025 | 0.04 | 0.8 |  | 159000 | 157920 | 157512.5 | 10 | 10 | 159000 | 157910 | 0.6903% | 11.8 | 159000 | 157902.4761 | 33.64
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 6:27 | 18:15 | 24405.8 | 24592.3 | 29357.6 | 31048.7 | 22264.4 | 20182.4 | 26415.7 |  |  | 6.82 | 6.77 | 37.89 | 46.46 | 13.4 | 0 | 2.52 | 9.18 | 131668.8 | 46598.1 | 178266.9 |  | 6949 |  | 4781.1 | 6721.693 | 0.04 | 0.82 |  | 176000 | 175200 | 174890.5 | 20 | 20 | 176000 | 175180 | 0.4681% | 11.8 | 176000 | 175176.1617 | 33.64
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 6:30 | 18:18 | 22513.7 | 22701.5 | 29676.8 | 31873.1 | 21144.1 | 24655.7 | 18980.2 |  |  | 6.4 | 6.36 | 37.07 | 47.88 | 26.68 | 0 | 2.45 | 6.44 | 127909.2 | 43635.9 | 171545.1 |  | 7118 |  | 4886.5 | 6890.02 | 0.04 | 0.85 |  | 169000 | 168640 | 168327 | 30 | 30 | 169000 | 168610 | 0.2313% | 11.8 | 169000 | 168609.0979 | 33.64
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 6:40 | 18:12 | 21961 | 22001.2 | 29252.2 | 31249.9 | 22253.1 | 23913.3 | 18522.8 |  |  | 6.21 | 6.17 | 36.2 | 46.92 | 30.68 | 0 | 2.91 | 6.66 | 126717.4 | 42436.1 | 169153.5 |  | 7286 |  | 4990.4 | 7055.816 | 0.04 | 0.87 |  | 168000 | 166240 | 165796 | 20 | 20 | 168000 | 166220 | 1.071% | 11.5333 | 168000 | 166200.9385 | 35.31
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 6:26 | 18:16 | 22575.7 | 22790.9 | 31219.4 | 32792.6 | 26225.8 | 24214.4 | 18782.2 |  |  | 6.27 | 6.25 | 36.95 | 46.54 | 22.4 | 0 | 2.86 | 8.27 | 135604.4 | 42996.6 | 178601 |  | 7462 |  | 5100.1 | 7231.088 | 0.04 | 0.9 |  | 176000 | 175520 | 175272 | 30 | 30 | 176000 | 175490 | 0.2906% | 11.8333 | 176000 | 175488.5179 | 35.31
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 6:26 | 18:08 | 21754.1 | 22114.9 | 30514.2 | 31302.8 | 27999.8 | 21607.5 | 18136.1 |  |  | 6.52 | 6.52 | 36.73 | 45.41 | 19.94 | 0 | 3.15 | 7.42 | 133685.8 | 39743.6 | 173429.4 |  | 7634 |  | 5206.7 | 7401.211 | 0.04 | 0.92 |  | 172000 | 170560 | 170123 | 20 | 20 | 172000 | 170540 | 0.8561% | 11.7 | 172000 | 170527.5009 | 35.31
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 6:41 | 18:04 | 24760.6 | 25063.8 | 34600 | 35287.9 | 34363.4 | 11140.3 | 20550.6 |  |  | 6.67 | 6.66 | 36.52 | 48.68 | 19.73 | 0 | 3.66 | 8.68 | 154075.7 | 31690.9 | 185766.6 |  | 7818 |  | 5320.8 | 7583.549 | 0.04 | 0.93 |  | 184000 | 182560 | 182338 | 10 | 10 | 184000 | 182550 | 0.7943% | 11.3833 | 184000 | 182538.4826 | 35.31
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 6:25 | 18:22 | 22476.9 | 22664.1 | 30536.8 | 31302.9 | 29720.7 | 10781.1 | 18221.1 |  |  | 6.15 | 6.24 | 36.53 | 44.93 | 23 | 0 | 2.98 | 7.7 | 136701.4 | 29002.2 | 165703.6 |  | 7981 |  | 5422.5 | 7746.0725 | 0.04 | 0.94 |  | 163000 | 162720 | 162523.5 | 10 | 10 | 163000 | 162710 | 0.1782% | 11.95 | 163000 | 162709.4831 | 35.31
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 6:28 | 18:19 | 24357.7 | 24544.9 | 33021.3 | 33926.9 | 33170.8 | 10819.1 | 19930.3 |  |  | 6.68 | 6.7 | 36.76 | 45.63 | 18.65 | 0 | 3.14 | 9.32 | 149021.6 | 30749.4 | 179771 |  | 8159 |  | 5532.7 | 7922.316 | 0.04 | 0.96 |  | 178000 | 176320 | 176243.5 | 20 | 20 | 178000 | 176300 | 0.9643% | 11.85 | 178000 | 176283.6075 | 35.31
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 6:21 | 18:16 | 22930.4 | 23567.9 | 30886.7 | 32230 | 31994 | 10943.5 | 19367.3 |  |  | 6.23 | 6.3 | 37.45 | 46.26 | 19.19 | 0 | 3.09 | 10.7 | 141609 | 30310.8 | 171919.8 |  | 8329 |  | 5638.6 | 8091.1935 | 0.04 | 0.97 |  | 170000 | 169440 | 168877.5 | 10 | 10 | 170000 | 169430 | 0.3364% | 11.9167 | 170000 | 169428.0824 | 35.31
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 6:21 | 18:11 | 22169.3 | 23172.1 | 30132.2 | 31530 | 31360.8 | 10772 | 18744 |  |  | 6.05 | 6.1 | 36.22 | 47 | 29.36 | 0 | 2.37 | 6.75 | 138364.4 | 29516 | 167880.4 |  | 8495 |  | 5741.8 | 8255.9205 | 0.04 | 0.99 |  | 166000 | 165120 | 164727 | 20 | 20 | 166000 | 165100 | 0.5451% | 11.8333 | 166000 | 165095.0939 | 35.31
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 6:23 | 18:16 | 23143.2 | 25126.4 | 29397.1 | 32741.7 | 32372.1 | 10762.1 | 19795 |  |  | 6.39 | 6.45 | 37.65 | 48.8 | 24.52 | 0 | 2.2 | 9.02 | 142780.5 | 30557.1 | 173337.6 |  | 8666 |  | 5847.6 | 8425.04 | 0.04 | 1.01 |  | 171000 | 169280 | 169119.5 | 20 | 20 | 171000 | 169260 | 1.028% | 11.8833 | 171000 | 169242.1127 | 35.31
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 6:24 | 18:05 | 16310.8 | 17006 | 19632.3 | 23109.4 | 23455.5 | 9900.9 | 14040.8 |  |  | 4.41 | 4.45 | 36.84 | 44.34 | 25.13 | 0 | 2.73 | 9.4 | 99514 | 23941.7 | 123455.7 |  | 8788 |  | 5923.5 | 8546.142 | 0.04 | 1.02 |  | 122000 | 121440 | 121102 | 10 | 10 | 122000 | 121430 | 0.4694% | 11.6833 | 122000 | 121427.3244 | 35.31
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 6:19 | 18:21 | 25795.1 | 26189.5 | 35078.4 | 36032.6 | 34929.5 | 11004.8 | 21733.2 |  |  | 6.92 | 7.01 | 38.5 | 47.72 | 20.21 | 0 | 3.12 | 7.92 | 158025.1 | 32738 | 190763.1 |  | 8976 |  | 6040.7 | 8733.297 | 0.04 | 1.04 |  | 188000 | 187520 | 187155 | 20 | 20 | 188000 | 187500 | 0.2667% | 12.0333 | 188000 | 187498.6667 | 35.31
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 6:15 | 18:24 | 26169.2 | 26546.3 | 36215.1 | 36779.1 | 35644 | 11019 | 21988 |  |  | 7.05 | 7.17 | 38.97 | 49.7 | 17.43 | 0 | 2.77 | 7.35 | 161353.7 | 33007 | 194360.7 |  | 9169 |  | 6160 | 8924.017 | 0.04 | 1.06 |  | 193000 | 190880 | 190720 | 20 | 20 | 193000 | 190860 | 1.121% | 12.15 | 193000 | 190836.0054 | 35.31
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 6:16 | 18:20 | 25428 | 25626 | 35665 | 34826 | 34797 | 7790 | 21341 |  |  | 7.16 | 7.28 | 38.88 | 50.19 | 15.15 | 0 | 2.91 | 7.53 | 156342 | 29131 | 185473 |  | 9352 |  | 6273.8 | 9105.894 | 0.04 | 1.09 |  | 183000 | 182080 | 181877 | 30 | 30 | 183000 | 182050 | 0.5218% | 12.0667 | 183000 | 182045.0426 | 35.31
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 6:14 | 18:18 | 25865 | 26250.3 | 34910.99 | 33995.4 | 34849.5 | 10787 | 21547 |  |  | 6.85 | 7.03 | 39.34 | 50.33 | 14.77 | 0 | 2.3 | 6.44 | 155871.19 | 32334 | 188205.19 |  | 9538 |  | 6389.4 | 9290.495 | 0.04 | 1.12 |  | 186000 | 184960 | 184601 | 30 | 30 | 186000 | 184930 | 0.5786% | 12.0667 | 186000 | 184923.809 | 35.31
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 6:16 | 18:16 | 25913.8 | 26467.7 | 35218.8 | 34229.6 | 35121.9 | 10882.8 | 21687.2 |  |  | 6.01 | 6.09 | 39.86 | 50.62 | 12.58 | 0 | 2.97 | 7.13 | 156951.8 | 32570 | 189521.8 |  | 9725 |  | 6505.7 | 9476.46 | 0.04 | 1.15 |  | 187000 | 186080 | 185965 | 30 | 30 | 187000 | 186050 | 0.5106% | 12 | 187000 | 186045.1492 | 39.21
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 6:14 | 18:18 | 25653.2 | 26065 | 35868 | 34817 | 26315 | 10943.7 | 21606.4 |  |  | 6.83 | 7 | 39.48 | 50.97 | 10.25 | 0 | 2.22 | 6.45 | 148718.2 | 32550.1 | 181268.3 |  | 9907 |  | 6619.1 | 9657.61 | 0.04 | 1.17 |  | 182000 | 181440 | 181150 | 20 | 20 | 182000 | 181420 | 0.3197% | 12.0667 | 182000 | 181418.1457 | 39.21
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 6:15 | 18:07 | 23021.7 | 23755.9 | 32869.4 | 31816.8 | 31382.3 | 10318.5 | 19539.8 |  |  | 6.25 | 6.45 | 39.48 | 48.98 | 14.69 | 0 | 2.29 | 7.53 | 142846.1 | 29858.3 | 172704.4 |  | 10078 |  | 6725 | 9826.87 | 0.04 | 1.19 |  | 171000 | 169440 | 169260 | 20 | 20 | 171000 | 169420 | 0.9326% | 11.8667 | 171000 | 169405.265 | 39.21
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 6:17 | 18:20 | 21553.6 | 22298.5 | 31441.1 | 30901.1 | 30618.6 | 10192.5 | 18104.7 |  |  | 5.75 | 5.92 | 37.77 | 46.78 | 24.39 | 0 | 3.31 | 11.44 | 136812.9 | 28297.2 | 165110.1 |  | 10241 |  | 6826.4 | 9988.701 | 0.04 | 1.21 |  | 163000 | 162240 | 161831 | 20 | 20 | 163000 | 162220 | 0.4808% | 12.05 | 163000 | 162216.2495 | 39.21
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 6:12 | 18:23 | 25493.3 | 26016.6 | 36288.5 | 35895.1 | 35637.8 | 10870.4 | 21495.1 |  |  | 6.9 | 6.96 | 35.22 | 46.45 | 33.43 | 0 | 2.92 | 8.41 | 159331.3 | 32365.5 | 191696.8 |  | 10431 |  | 6944.2 | 10176.25 | 0.04 | 1.22 |  | 190000 | 188480 | 187549 | 10 | 10 | 190000 | 188470 | 0.8118% | 12.1833 | 190000 | 188457.5795 | 39.21
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 6:15 | 18:22 | 23209.9 | 23586.8 | 32906.6 | 32381.1 | 31544.9 | 11231 | 18317.7 |  |  | 6.28 | 6.52 | 37.8 | 47.71 | 24.58 | 0 | 3.28 | 8.31 | 143629.3 | 29548.7 | 173178 |  | 10602 |  | 7050.5 | 10346.735 | 0.04 | 1.24 |  | 171000 | 170080 | 170485 | 20 | 20 | 171000 | 170060 | 0.5527% | 12.1167 | 171000 | 170054.8042 | 39.21
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 6:23 | 18:24 | 24414.7 | 25061.7 | 34468.7 | 33788.2 | 33164.9 | 10793 | 27118 |  |  | 6.54 | 6.81 | 38.44 | 49.35 | 18.72 | 0 | 2.64 | 8.23 | 150898.2 | 37911 | 188809.2 |  | 10789 |  | 7166.2 | 10531.945 | 0.04 | 1.25 |  | 187000 | 185120 | 185210 | 10 | 10 | 187000 | 185110 | 1.021% | 12.0167 | 187000 | 185090.7028 | 39.21
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 6:15 | 18:25 | 24922.3 | 25428.1 | 34960.8 | 34304.6 | 33567.8 | 9538.1 | 28092.9 |  |  | 6.45 | 6.76 | 38.89 | 48.04 | 17.93 | 0 | 3.72 | 9.53 | 153183.6 | 37631 | 190814.6 |  | 10977 |  | 7283.7 | 10719.214 | 0.04 | 1.28 |  | 188000 | 188000 | 187269 | 30 | 30 | 188000 | 187970 | 0.01596% | 12.1667 | 188000 | 187969.9952 | 39.21
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 6:12 | 18:12 | 23671.8 | 24003.1 | 32992.2 | 32428.2 | 32113.6 | 5975.2 | 26083.8 |  |  | 6.12 | 6.24 | 37.42 | 49.2 | 29.42 | 0 | 2.08 | 5.61 | 145208.9 | 32059 | 177267.9 |  | 11152 |  | 7392.3 | 10893.017 | 0.04 | 1.3 |  | 175000 | 173760 | 173803 | 20 | 20 | 175000 | 173740 | 0.7252% | 12 | 175000 | 173730.8622 | 39.21
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 6:12 | 18:25 | 24585.4 | 24919.3 | 34493.7 | 33793.7 | 33801.9 | 3655.9 | 27541.9 |  |  | 6.39 | 6.52 | 38.17 | 47.52 | 25.83 | 0 | 3.04 | 8.62 | 151594 | 31197.8 | 182791.8 |  | 11333 |  | 7504.7 | 11072.181 | 0.04 | 1.33 |  | 181000 | 179840 | 179164 | 30 | 30 | 181000 | 179810 | 0.6618% | 12.2167 | 181000 | 179802.1245 | 39.21
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 6:11 | 18:27 | 24474.1 | 24650.9 | 34572.6 | 33993.5 | 33395.8 | 3052.7 | 26595.5 |  |  | 6.42 | 6.65 | 38.62 | 48.41 | 20.25 | 0 | 2.78 | 7.26 | 151086.9 | 29648.2 | 180735.1 |  | 11512 |  | 7615.6 | 11249.369 | 0.04 | 1.36 |  | 179000 | 177440 | 177188 | 30 | 30 | 179000 | 177410 | 0.8962% | 12.2667 | 179000 | 177395.75 | 39.21
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 6:10 | 18:28 | 25619 | 25750.4 | 35895.1 | 35308.8 | 35069.4 | 11532.7 | 28051 |  |  | 6.79 | 7.03 | 35.28 | 48.06 | 32.01 | 0 | 2.25 | 5.72 | 157642.7 | 39583.7 | 197226.4 |  | 11707 |  | 7736.7 | 11442.973 | 0.04 | 1.38 |  | 195000 | 193760 | 193604 | 20 | 20 | 195000 | 193740 | 0.6504% | 12.3 | 195000 | 193731.8055 | 39.21
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 6:10 | 17:19 | 23621 | 23869.7 | 32720.1 | 32278.7 | 32440.4 | 11962.3 | 26187.3 |  |  | 5.79 | 6.02 | 34.85 | 47.54 | 30.28 | 0 | 2.63 | 13.16 | 144929.9 | 38149.6 | 183079.5 |  | 11888 |  | 7849.2 | 11622.492 | 0.04 | 1.4 |  | 181000 | 180000 | 179519 | 20 | 20 | 181000 | 179980 | 0.5667% | 11.15 | 181000 | 179974.2194 | 39.21
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 7:13 | 18:24 | 22272 | 24284 | 37212 | 36769.1 | 36873.7 | 17012.8 | 29238.9 |  |  | 7.04 | 7.3 | 35.07 | 35.07 | 27.11 | 0 | 3.03 | 7.66 | 157410.8 | 46251.7 | 203662.5 |  | 12089 |  | 7974.2 | 11822.399 | 0.04 | 1.43 |  | 201000 | 200000 | 199907 | 30 | 30 | 201000 | 199970 | 0.5151% | 11.1833 | 201000 | 199964.6947 | 39.21
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 6:07 | 18:04 | 16102.4 | 21594.9 | 36989 | 36498.6 | 37049.1 | 7483.9 | 29846.7 |  |  | 7.12 | 7.43 | 33.29 | 46.34 | 30.21 | 0 | 3.49 | 15.01 | 148234 | 37330.6 | 185564.6 |  | 12272 |  | 8088.1 | 12004.75 | 0.04 | 1.44 |  | 183000 | 182240 | 182351 | 10 | 10 | 183000 | 182230 | 0.4225% | 11.95 | 183000 | 182226.7464 | 39.21
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 6:11 | 18:04 | 19692.1 | 22374 | 33547 | 33179 | 34230.3 | 2276 | 27563 |  |  | 6.57 | 6.83 | 33.46 | 46.01 | 33.7 | 0 | 3.02 | 8.76 | 143022.4 | 29839 | 172861.4 |  | 12443 |  | 8194.2 | 12173.583 | 0.04 | 1.46 |  | 171000 | 169760 | 168833 | 20 | 20 | 171000 | 169740 | 0.7423% | 11.8833 | 171000 | 169730.6469 | 39.21
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 6:23 | 18:25 | 25317.8 | 26237.1 | 36189.8 | 35948 | 35673 | 16612.2 | 28828.1 |  |  | 7.02 | 7.28 | 35.61 | 49.14 | 29.75 | 0 | 2.34 | 6.85 | 159365.7 | 45440.3 | 204806 |  | 12646 |  | 8320 | 12374.585 | 0.04 | 1.48 |  | 203000 | 201280 | 201002 | 20 | 20 | 203000 | 201260 | 0.8646% | 12.0333 | 203000 | 201244.9568 | 39.21
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 6:07 | 18:33 | 22173.6 | 22506.9 | 31522.3 | 30791.9 | 31226.1 | 12720.5 | 25256.8 |  |  | 6.01 | 6.27 | 35.81 | 46.41 | 34.58 | 0 | 2.59 | 8.49 | 138220.8 | 37977.3 | 176198.1 |  | 12820 |  | 8428.2 | 12547.379 | 0.04 | 1.5 |  | 174000 | 173120 | 172794 | 20 | 20 | 174000 | 173100 | 0.5199% | 12.4333 | 174000 | 173095.3206 | 39.21
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 6:17 | 18:15 | 24551.4 | 24981.4 | 34045.1 | 35166.7 | 34677.6 | 13979.4 | 27464.7 |  |  | 6.45 | 6.7 | 35.93 | 47.43 | 36.04 | 0 | 2.3 | 6.74 | 153422.2 | 41444.1 | 194866.3 |  | 13013 |  | 8547.9 | 12738.581 | 0.04 | 1.52 |  | 193000 | 191520 | 191202 | 20 | 20 | 193000 | 191500 | 0.7833% | 11.9667 | 193000 | 191488.2507 | 39.21
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 6:15 | 17:46 | 11076.1 | 11228.3 | 15665.3 | 15949.4 | 16018.1 | 6168.1 | 12243.7 |  |  | 2.62 | 2.67 | 30.36 | 34.92 | 63.8 | 0 | 1.9 | 5.8 | 69937.2 | 18411.8 | 88349 |  | 13100 |  | 8602 | 12824.814 | 0.04 | 1.53 |  | 87000 | 86560 | 86233 | 10 | 10 | 87000 | 86550 | 0.5199% | 11.5167 | 87000 | 86547.6603 | 39.21
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 7:05 | 18:28 | 18729.3 | 18736.7 | 25635.7 | 25850.1 | 25852.4 | 10154 | 20330.4 |  |  | 3.18 | 3.23 | 28.47 | 34.35 | 39.83 | 0 | 2.59 | 6.84 | 114804.2 | 30484.4 | 145288.6 |  | 13244 |  | 8691 | 12967.318 | 0.04 | 1.55 |  | 144000 | 142400 | 142504 | 20 | 20 | 144000 | 142380 | 1.138% | 11.3833 | 144000 | 142361.5676 | 39.21
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 6:06 | 18:21 | 16720 | 16929 | 23244.2 | 23814.4 | 24052.9 | 0 | 18182.2 |  |  | 4.15 | 4.31 | 33.94 | 41.83 | 46.98 | 0 | 2.26 | 6.66 | 104760.5 | 18182.2 | 122942.7 |  | 13366 |  | 8766.7 | 13087.72 | 0.04 | 1.57 |  | 122000 | 121120 | 120402 | 20 | 20 | 122000 | 121100 | 0.7432% | 12.25 | 122000 | 121093.3113 | 39.21
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 6:08 | 18:28 | 19114.8 | 19206.5 | 26275.2 | 26685.1 | 26939.6 | 12234.9 | 20197 |  |  | 4.77 | 4.91 | 33.31 | 41.68 | 47.67 | 0 | 2.82 | 10.69 | 118221.2 | 32431.9 | 150653.1 |  | 13516 |  | 8859.5 | 13235.612 | 0.04 | 1.58 |  | 150000 | 148480 | 147892 | 10 | 10 | 150000 | 148470 | 1.031% | 12.3333 | 150000 | 148454.2332 | 39.21
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 6:08 | 18:23 | 21102.9 | 21223 | 28779.4 | 29171.3 | 29403.4 | 19923.8 | 21086.5 |  |  | 5.39 | 5.55 | 33.82 | 43.71 | 48.47 | 0 | 2.93 | 9.26 | 129680 | 41010.3 | 170690.3 |  | 13685 |  | 8964.4 | 13403.179 | 0.04 | 1.6 |  | 169000 | 167840 | 167567 | 20 | 20 | 169000 | 167820 | 0.7031% | 12.25 | 169000 | 167811.703 | 39.21
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 6:20 | 17:49 | 20715.8 | 20682.8 | 28200.4 | 28484.2 | 28599.3 | 23023.9 | 22737.6 |  |  | 5.34 | 5.46 | 33.51 | 44.31 | 51.02 | 0 | 2.57 | 8.06 | 126682.5 | 45761.5 | 172444 |  | 13855 |  | 9070.5 | 13572.088 | 0.04 | 1.61 |  | 170000 | 169760 | 168909 | 10 | 10 | 170000 | 169750 | 0.1473% | 11.4833 | 170000 | 169749.6318 | 39.21
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 6:07 | 18:24 | 22068.6 | 22340.7 | 30505.3 | 31243.7 | 31750.1 | 23252.6 | 24693.7 |  |  | 5.82 | 6.07 | 35.43 | 46.81 | 44.93 | 0 | 2.04 | 6.31 | 137908.4 | 47946.3 | 185854.7 |  | 14040 |  | 9184.7 | 13754.648 | 0.04 | 1.63 |  | 185000 | 182720 | 182560 | 20 | 20 | 185000 | 182700 | 1.259% | 12.2833 | 185000 | 182671.0454 | 39.21
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 6:06 | 18:25 | 20965.3 | 21214.6 | 28712.6 | 29429.4 | 30190.1 | 22791.4 | 23656.8 |  |  | 5.31 | 5.53 | 33.41 | 43.82 | 54.35 | 0 | 1.7 | 11.93 | 130512 | 46448.2 | 176960.2 |  | 14215 |  | 9293.4 | 13928.355 | 0.04 | 1.64 |  | 175000 | 173920 | 173707 | 10 | 10 | 175000 | 173910 | 0.6268% | 12.3167 | 175000 | 173903.1683 | 39.21
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 6:06 | 18:06 | 19414.9 | 19566.4 | 26970.6 | 27568.2 | 27760 | 21593 | 21579.6 |  |  | 4.91 | 5.15 | 34.88 | 43.35 | 46.07 | 0 | 2.46 | 14.53 | 121280.1 | 43172.6 | 164452.7 |  | 14377 |  | 9394.4 | 14089.439 | 0.04 | 1.66 |  | 162000 | 161600 | 161084 | 20 | 20 | 162000 | 161580 | 0.2599% | 12 | 162000 | 161578.9083 | 39.21
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 5:58 | 18:14 | 17943.4 | 18204.4 | 25313.4 | 25764.6 | 25850.2 | 19971.8 | 19876.1 |  |  | 4.36 | 4.5 | 30.53 | 39.47 | 66.83 | 0 | 2.39 | 14.28 | 113076 | 39847.9 | 152923.9 |  | 14529 |  | 9488.5 | 14239.595 | 0.04 | 1.67 |  | 152000 | 150560 | 150156 | 10 | 10 | 152000 | 150550 | 0.9631% | 12.2667 | 152000 | 150536.0345 | 39.21
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 6:02 | 18:20 | 12059 | 13560.3 | 19069.2 | 19626.8 | 20071.4 | 15518.9 | 15515.7 |  |  | 3.32 | 3.4 | 28.46 | 34.88 | 71.85 | 0 | 1.94 | 5.2 | 84386.7 | 31034.6 | 115421.3 |  | 14644 |  | 9559.5 | 14352.875 | 0.04 | 1.67 |  | 115000 | 113600 | 113280 | 0 | 0 | 115000 | 113600 | 1.232% | 12.3 | 115000 | 113582.7465 | 39.21
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 6:08 | 17:13 | 14926.4 | 15213 | 21054 | 21594.4 | 21923.2 | 16839.1 | 16850.7 |  |  | 3.67 | 3.8 | 30.01 | 38.16 | 67.59 | 0 | 1.98 | 5.6 | 94711 | 33689.8 | 128400.8 |  | 14771 |  | 9638.4 | 14478.651 | 0.04 | 1.67 |  | 127000 | 126240 | 125776 | 0 | 0 | 127000 | 126240 | 0.602% | 11.0833 | 127000 | 126235.4246 | 39.21
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 6:19 | 17:40 | 10691.2 | 11547.6 | 16137.1 | 16450.8 | 16668.7 | 13429.4 | 13458.6 |  |  | 3.33 | 3.39 | 28.12 | 35.05 | 80.78 | 0 | 1.92 | 7.93 | 71495.4 | 26888 | 98383.4 |  | 14869 |  | 9698.7 | 14574.142 | 0.04 | 1.67 |  | 98000 | 96480 | 95491 | 0 | 0 | 98000 | 96480 | 1.575% | 11.35 | 98000 | 96456.0531 | 39.21
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 6:04 | 18:14 | 19513.2 | 19459.4 | 26739.1 | 26828.4 | 27268 | 19846.5 | 19601.1 |  |  | 5.06 | 5.29 | 30.16 | 39.49 | 70.54 | 0 | 1.97 | 7.16 | 119808.1 | 39447.6 | 159255.7 |  | 15027 |  | 9796.8 | 14730.711 | 0.04 | 1.67 |  | 158000 | 156960 | 156569 | 0 | 0 | 158000 | 156960 | 0.6626% | 12.1667 | 158000 | 156953.1091 | 39.21
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 6:00 | 18:40 | 21898.9 | 21972.4 | 29889.5 | 30427.5 | 30775 | 24945.4 | 24977.2 |  |  | 5.58 | 5.99 | 32.11 | 40.13 | 62.24 | 0 | 2.73 | 8.16 | 134963.3 | 49922.6 | 184885.9 |  | 15210 |  | 9910.5 | 14912.501 | 0.04 | 1.68 |  | 183000 | 181920 | 181790 | 10 | 10 | 183000 | 181910 | 0.5992% | 12.6667 | 183000 | 181903.4687 | 39.21
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 6:01 | 18:10 | 15474.9 | 15423.5 | 21061.2 | 21195.5 | 21372.4 | 17148.3 | 17082.9 |  |  | 3.71 | 3.82 | 30.66 | 37.84 | 71.31 | 0 | 2.56 | 6.52 | 94527.5 | 34231.2 | 128758.7 |  | 15337 |  | 9989.6 | 15038.584 | 0.04 | 1.68 |  | 127000 | 126560 | 126083 | 0 | 0 | 127000 | 126560 | 0.3477% | 12.15 | 127000 | 126558.4703 | 39.21
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 6:24 | 18:29 | 11802.5 | 11973.3 | 16441.1 | 16782.4 | 16913 | 13148.3 | 13243.6 |  |  | 2.79 | 2.87 | 28.48 | 32.9711 | 76.489 | 0 | 2.444 | 6.14 | 73912.3 | 26391.9 | 100304.2 |  | 15437 |  | 10051.3 | 15136.995 | 0.04 | 1.68 |  | 100000 | 98720 | 98411 | 0 | 0 | 100000 | 98720 | 1.297% | 12.0833 | 100000 | 98703.4036 | 39.21
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 6:16 | 18:31 | 21769.6 | 22020.3 | 30285 | 30780 | 31272 | 24255 | 24361 |  |  | 5.38 | 5.59 | 32.35 | 39.62 | 62.78 | 0 | 3.94 | 10.17 | 136126.9 | 48616 | 184742.9 |  | 15620 |  | 10165.6 | 15318.507 | 0.04 | 1.69 |  | 183000 | 182880 | 181512 | 10 | 10 | 183000 | 182870 | 0.07109% | 12.25 | 183000 | 182869.9076 | 39.21
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 6:06 | 18:30 | 14512.2 | 14615.6 | 20360.5 | 20693.2 | 20855 | 15955.4 | 16077.9 |  |  | 3.368 | 3.504 | 31.092 | 35.154 | 64.828 | 0 | 3.29 | 7.67 | 91036.5 | 32033.3 | 123069.8 |  | 15742 |  | 10240.7 | 15439.433 | 0.04 | 1.69 |  | 122000 | 120160 | 120926 | 0 | 0 | 122000 | 120160 | 1.531% | 12.4 | 122000 | 120131.8242 | 39.21
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 6:01 | 18:30 | 25992 | 26047.9 | 35462.8 | 35762.1 | 36111.6 | 29920.8 | 29801.7 |  |  | 6.71 | 7.06 | 33.61 | 42.51 | 47.66 | 0 | 4.68 | 8.79 | 159376.4 | 59722.5 | 219098.9 |  | 15959 |  | 10375.3 | 15654.553 | 0.04 | 1.69 |  | 217000 | 215360 | 215120 | 0 | 0 | 217000 | 215360 | 0.7615% | 12.4833 | 217000 | 215347.5111 | 39.21
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 5:58 | 18:33 | 11350.2 | 11384.9 | 15664.4 | 15955.7 | 16152.7 | 12499.8 | 12291.9 |  |  | 6.58 | 6.96 | 33.58 | 45.55 | 43.63 | 0 | 4.62 | 9.42 | 70507.9 | 24791.7 | 95299.6 |  | 16053 |  | 10434 | 15748.129 | 0.04 | 1.71 |  | 94000 | 93920 | 93576 | 20 | 20 | 94000 | 93900 | 0.1065% | 12.5833 | 94000 | 93899.8935 | 39.21
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 6:00 | 18:29 | 23622.7 | 23664.5 | 32476.8 | 32801.3 | 33594.9 | 26777.1 | 26731.2 |  |  | 6.1 | 6.49 | 32.75 | 43.67 | 46 | 0 | 3.97 | 8.55 | 146160.2 | 53508.3 | 199668.5 |  | 16251 |  | 10556.7 | 15944.245 | 0.04 | 1.72 |  | 198000 | 196320 | 196116 | 10 | 10 | 198000 | 196310 | 0.8609% | 12.4833 | 198000 | 196295.4511 | 39.21
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 6:01 | 18:35 | 23648.3 | 23720.3 | 32407.4 | 32783.7 | 33084.1 | 27005.6 | 26901.3 |  |  | 6.08 | 6.54 | 33.88 | 42.48 | 40.86 | 0 | 4.46 | 9.18 | 145643.8 | 53906.9 | 199550.7 |  | 16448 |  | 10679.3 | 16140.189 | 0.04 | 1.75 |  | 197000 | 196160 | 195944 | 30 | 30 | 197000 | 196130 | 0.4436% | 12.5667 | 197000 | 196126.1408 | 39.21
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 5:59 | 18:32 | 24183.7 | 24204 | 33292.3 | 33623.5 | 33784.5 | 27278.4 | 27290 |  |  | 6.32 | 6.81 | 33.85 | 45.19 | 41.91 | 0 | 3.2 | 8.39 | 149088 | 54568.4 | 203656.4 |  | 16650 |  | 10804.5 | 16340.052 | 0.04 | 2.03 |  | 202000 | 200320 | 199863 | 280 | 280 | 202000 | 200040 | 0.9798% | 12.55 | 202000 | 200020.7958 | 39.21
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 6:15 | 18:30 | 20282.6 | 20148.7 | 27587.1 | 27793.9 | 27700.1 | 22845.3 | 22527.8 |  |  | 5.25 | 5.42 | 32.74 | 43.09 | 47.8 | 0 | 1.96 | 6.64 | 123512.4 | 45373.1 | 168885.5 |  | 16817 |  | 10908.3 | 16505.777 | 0.04 | 2.27 |  | 167000 | 166080 | 165725 | 240 | 240 | 167000 | 165840 | 0.6995% | 12.25 | 167000 | 165831.8862 | 39.21
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 6:00 | 18:35 | 26245.1 | 26085.3 | 35795.8 | 36050.9 | 35745.3 | 28654.3 | 28496.3 |  |  | 6.77 | 7.22 | 35.74 | 36.48 | 46.55 | 0 | 2.27 | 6.36 | 159922.4 | 57150.6 | 217073 |  | 17031 |  | 11041.6 | 16718.843 | 0.04 | 2.5 |  | 214000 | 213280 | 213066 | 230 | 230 | 214000 | 213050 | 0.4459% | 12.5833 | 214000 | 213045.7639 | 39.21
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 5:59 | 18:18 | 20548.2 | 20519.9 | 28227.6 | 28506.3 | 28600 | 23079.2 | 22933.7 |  |  | 5.23 | 5.54 | 34.45 | 40.98 | 44.3195 | 0 | 3.45 | 10.47 | 126402 | 46012.9 | 172414.9 |  | 17202 |  | 11147.6 | 16888.119 | 0.04 | 2.74 |  | 171000 | 169600 | 169276 | 240 | 240 | 171000 | 169360 | 0.9684% | 12.3167 | 171000 | 169344.119 | 39.21
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 6:02 | 18:35 | 22467.9 | 22693.9 | 31227.6 | 31778.6 | 32087.5 | 25149.6 | 25141.6 |  |  | 5.65 | 5.95 | 35.87 | 42.72 | 41.55 | 0 | 4.45 | 9.21 | 140255.5 | 50291.2 | 190546.7 |  | 17390 |  | 11264.7 | 17075.227 | 0.04 | 2.96 |  | 188000 | 187360 | 187108 | 220 | 220 | 188000 | 187140 | 0.4595% | 12.55 | 188000 | 187136.0479 | 39.21
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 6:02 | 18:11 | 24440.3 | 24606 | 33713.7 | 33988.8 | 34051.3 | 27471.7 | 27192.2 |  |  | 6.21 | 6.56 | 36.05 | 44.68 | 43.57 | 0 | 4.65 | 9.27 | 150800.1 | 54663.9 | 205464 |  | 17594 |  | 11391 | 17277.007 | 0.04 | 3.2 |  | 204000 | 202080 | 201780 | 240 | 240 | 204000 | 201840 | 1.07% | 12.15 | 204000 | 201816.8847 | 39.21
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 6:35 | 16:56 | 19669.8 | 19638 | 27168.4 | 27377 | 27447.1 | 21810.6 | 21651.1 |  |  | 4.76 | 4.93 | 33.84 | 40.71 | 51.23 | 0 | 4.86 | 22.74 | 121300.3 | 43461.7 | 164762 |  | 17757 |  | 11492.3 | 17438 | 0.04 | 3.42 |  | 163000 | 162080 | 160993 | 220 | 220 | 163000 | 161860 | 0.7043% | 10.35 | 163000 | 161851.9708 | 39.21
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 6:26 | 17:02 | 18312.7 | 18334.5 | 25468 | 25744.4 | 25958 | 20180.8 | 20047.6 |  |  | 4.53 | 4.65 | 31.42 | 41.11 | 64.23 | 0 | 2.13 | 9.66 | 113817.6 | 40228.4 | 154046 |  | 17909 |  | 11586.9 | 17589.06 | 0.04 | 3.64 |  | 152000 | 151360 | 151060 | 220 | 220 | 152000 | 151140 | 0.569% | 10.6 | 152000 | 151135.1065 | 39.21
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 6:06 | 18:27 | 13986.1 | 14090.6 | 19199.5 | 19514.1 | 19969.9 | 15961.9 | 15953.9 |  |  | 3.5 | 3.62 | 31.05 | 36.9 | 65.47 | 0 | 2.04 | 7.18 | 86760.2 | 31915.8 | 118676 |  | 18027 |  | 11659.7 | 17704.557 | 0.04 | 3.87 |  | 118000 | 116480 | 115497 | 230 | 230 | 118000 | 116250 | 1.505% | 12.35 | 118000 | 116223.6559 | 39.21
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 6:06 | 18:25 | 19028 | 18954 | 26707.4 | 26933.9 | 27189.7 | 20850.2 | 21106.8 |  |  | 4.83 | 5.05 | 32.37 | 41.61 | 62.81 | 0 | 1.86 | 3.14 | 118813 | 41957 | 160770 |  | 18186 |  | 11758.4 | 17862.624 | 0.04 | 4.08 |  | 159000 | 157920 | 158067 | 210 | 210 | 159000 | 157710 | 0.818% | 12.3167 | 159000 | 157699.4484 | 39.21
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 5:56 | 18:25 | 23598.8 | 23323.8 | 32170 | 32231 | 32053.6 | 26365.1 | 25956.3 |  |  | 6 | 6.42 | 34.28 | 45.49 | 56.84 | 0 | 2.42 | 7.64 | 143377.2 | 52321.4 | 195698.6 |  | 18380 |  | 11879 | 18054.799 | 0.04 | 4.32 |  | 194000 | 192960 | 192175 | 240 | 240 | 194000 | 192720 | 0.6642% | 12.4833 | 194000 | 192711.4985 | 39.21
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 6:02 | 18:37 | 19229.7 | 19593.7 | 26631.2 | 27268.9 | 28666.9 | 22497.4 | 22430.6 |  |  | 5.21 | 5.38 | 32.48 | 41.41 | 60.31 | 0 | 3.51 | 7.84 | 121390.4 | 44928 | 166318.4 |  | 18544 |  | 11981.2 | 18218.125 | 0.04 | 4.5 |  | 164000 | 163520 | 163326 | 180 | 180 | 164000 | 163340 | 0.4041% | 12.5833 | 164000 | 163337.3332 | 39.21
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 6:39 | 18:41 | 14634.9 | 14782.9 | 20383.2 | 20664 | 20721.3 | 16417.5 | 16229.5 |  |  | 3.63 | 3.72 | 29.49 | 36.21 | 71.46 | 0 | 3.05 | 7.5 | 91186.3 | 32647 | 123833.3 |  | 18667 |  | 12057.4 | 18339.58 | 0.04 | 4.77 |  | 123000 | 121920 | 121455 | 270 | 270 | 123000 | 121650 | 1.11% | 12.0333 | 123000 | 121635.0185 | 39.21
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 6:03 | 18:43 | 25045 | 25278.2 | 34231.5 | 34571.9 | 35182.1 | 28771 | 28481.6 |  |  | 6.38 | 6.82 | 32.42 | 42.24 | 56.75 | 0 | 5.16 | 10.17 | 154308.7 | 57252.6 | 211561.3 |  | 18877 |  | 12187.5 | 18547.516 | 0.04 | 4.99 |  | 210000 | 208160 | 207936 | 220 | 220 | 210000 | 207940 | 0.9907% | 12.6667 | 210000 | 207919.5922 | 39.21
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 5:56 | 18:46 | 17037.5 | 17066.6 | 23835 | 24100.7 | 24426.7 | 18929.3 | 18918 |  |  | 4.21 | 4.51 | 30.68 | 36.66 | 63.43 | 0 | 5.1 | 13.52 | 106466.5 | 37847.3 | 144313.8 |  | 19020 |  | 12276.2 | 18688.984 | 0.04 | 5.2 |  | 143000 | 141920 | 141468 | 210 | 210 | 143000 | 141710 | 0.9103% | 12.8333 | 143000 | 141698.257 | 39.21
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 6:08 | 17:08 | 15468.9 | 15540.7 | 21246.8 | 21419.7 | 21764.4 | 17475.4 | 17389.9 |  |  | 3.91 | 4.03 | 29.64 | 36.14 | 70.96 | 0 | 5.14 | 14.85 | 95440.5 | 34865.3 | 130305.8 |  | 19148 |  | 12356.2 | 18816.381 | 0.04 | 5.42 |  | 128000 | 128000 | 127397 | 220 | 220 | 128000 | 127780 | 0.1722% | 11 | 128000 | 127779.6212 | 39.21
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 6:06 | 18:41 | 23879 | 24010.5 | 33031.6 | 33187.7 | 33862.8 | 27356.3 | 27264.3 |  |  | 6.13 | 6.46 | 31.83 | 39.69 | 58.45 | 0 | 5.37 | 11.97 | 147971.6 | 54620.6 | 202592.2 |  | 19349 |  | 12480.8 | 19015.37 | 0.04 | 5.66 |  | 201000 | 199360 | 198989 | 240 | 240 | 201000 | 199120 | 0.9442% | 12.5833 | 201000 | 199102.2499 | 39.21
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 5:59 | 18:28 | 19159 | 19282 | 26286 | 26529 | 26988 | 21917 | 21824 |  |  | 4.85 | 5.11 | 30.4 | 37.59 | 66.71 | 0 | 4.09 | 13.91 | 118244 | 43741 | 161985 |  | 19510 |  | 12580.4 | 19174.533 | 0.04 | 5.88 |  | 161000 | 159360 | 159163 | 220 | 220 | 161000 | 159140 | 1.169% | 12.4833 | 161000 | 159118.2607 | 39.21
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 6:11 | 18:21 | 17917.7 | 17887.8 | 24523.6 | 24714.6 | 24821.6 | 20075.6 | 19939.1 |  |  | 4.4 | 4.5 | 30.53 | 36.64 | 62.02 | 0 | 4.75 | 10.61 | 109865.3 | 40014.7 | 149880 |  | 19658 |  | 12672.6 | 19321.593 | 0.04 | 6.11 |  | 148000 | 147520 | 147060 | 230 | 230 | 148000 | 147290 | 0.482% | 12.1667 | 148000 | 147286.5775 | 39.21
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 5:59 | 18:22 | 12293.2 | 12416.1 | 17123.1 | 17366.9 | 17384.1 | 13692 | 13666.6 |  |  | 2.87 | 3 | 29.43 | 32.99 | 66.76 | 0 | 4.05 | 8.89 | 76583.4 | 27358.6 | 103942 |  | 19761 |  | 12736.6 | 19423.826 | 0.04 | 6.32 |  | 103000 | 102400 | 102233 | 210 | 210 | 103000 | 102190 | 0.7926% | 12.3833 | 103000 | 102183.5796 | 39.21
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 6:04 | 18:17 | 16758.6 | 16851.5 | 23034.3 | 23248.9 | 23351.6 | 18798.3 | 18626 |  |  | 4.112 | 4.222 | 28.766 | 34.624 | 72.556 | 0 | 4.596 | 11.02 | 103244.9 | 37424.3 | 140669.2 |  | 19901 |  | 12822.9 | 19561.877 | 0.04 | 6.53 |  | 140000 | 138080 | 138051 | 210 | 210 | 140000 | 137870 | 1.545% | 12.2167 | 140000 | 137837.0929 | 39.21
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 6:33 | 18:16 | 12609.5 | 12737.7 | 17665.9 | 17933.3 | 17945.6 | 14040 | 13988.5 |  |  | 2.79 | 2.84 | 28.997 | 33.98 | 71.71 | 0 | 2.891 | 10.85 | 78892 | 28028.5 | 106920.5 |  | 20007 |  | 12889 | 19666.453 | 0.04 | 6.74 |  | 106000 | 105760 | 104576 | 210 | 210 | 106000 | 105550 | 0.4263% | 11.7167 | 106000 | 105548.0815 | 39.21
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 8:20 | 18:19 | 3855 | 3926.5 | 5377.9 | 5498.8 | 1681.2 | 2462.6 | 4358 |  |  | 0.9487 | 0.94666 | 25.18 | 25.71 | 95.6 | 0 | 2.33 | 5.3 | 20339.4 | 6820.6 | 27160 |  | 20034 |  | 12905.3 | 19692.2184 | 0.04 | 6.95 |  | 27000 | 26080 | 25765.4 | 210 | 210 | 27000 | 25870 | 4.368% | 9.9833 | 27000 | 25820.6417 | 39.21
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 6:03 | 18:41 | 17531 | 17670 | 24042 | 24689.2 | 24103.4 | 19357 | 19325.6 |  |  | 4.18 | 4.32 | 29.35 | 36.57 | 73.125 | 0 | 3.197 | 8.59 | 108035.6 | 38682.6 | 146718.2 |  | 20179 |  | 12995.6 | 19836.411 | 0.04 | 7.27 |  | 145000 | 144480 | 144192.6 | 320 | 320 | 145000 | 144160 | 0.5827% | 12.6333 | 145000 | 144155.1054 | 39.21
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 6:21 | 18:20 | 19422 | 19525 | 26673.2 | 27035 | 27278.9 | 21988.6 | 21886 |  |  | 4.749 | 4.9455 | 30.309 | 37.622 | 61.89 | 0 | 4.7416 | 10.52 | 119934.1 | 43874.6 | 163808.7 |  | 20342 |  | 13096.5 | 19997.464 | 0.04 | 7.58 |  | 163000 | 161440 | 161053 | 310 | 310 | 163000 | 161130 | 1.161% | 11.9833 | 163000 | 161108.2976 | 39.21
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 6:36 | 18:01 | 3396.8 | 3416.4 | 4476.4 | 4517 | 4592.8 | 3911.8 | 3791.2 |  |  | 1.4 | 1.406 | 25.0888 | 26.024 | 89.5777 | 0 | 2.861 | 8.32 | 20399.4 | 7703 | 28102.4 |  | 20370 |  | 13113.6 | 20023.9872 | 0.04 | 7.84 |  | 28000 | 27360 | 26523.25 | 260 | 260 | 28000 | 27100 | 3.321% | 11.4167 | 28000 | 27070.1107 | 39.21
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 6:16 | 17:39 | 7663.5 | 7720.4 | 10722.5 | 10861 | 10851.6 | 8506.1 | 8401 |  |  | 1.72 | 1.73 | 25.98 | 28.19 | 85.42 | 0 | 2.83 | 7.2 | 47819 | 16907.1 | 64726.1 |  | 20434 |  | 13153.2 | 20087.141 | 0.04 | 8.07 |  | 64000 | 63360 | 63153.75 | 230 | 230 | 64000 | 63130 | 1.378% | 11.3833 | 64000 | 63118.0105 | 39.21
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | 6:20 | 18:08 | 6341.3 | 6426.7 | 8817 | 8960 | 9133 | 7275 | 6626.8 |  |  | 1.747 | 1.749 | 26.297 | 28.05 | 86.71 | 0 | 3.21 | 7.29 | 39678 | 13901.8 | 53579.8 |  | 20487 |  | 13186.1 | 20139.068 | 0.04 | 8.31 |  | 53000 | 52640 | 51927 | 240 | 240 | 53000 | 52400 | 1.145% | 11.8 | 53000 | 52393.1298 | 39.21
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | 6:07 | 17:34 | 12041.9 | 12107.4 | 16149.3 | 16346.6 | 16918.2 | 13360.7 | 13186 |  |  | 2.929 | 2.955 | 28.278 | 33.41 | 76.627 | 0 | 4.26 | 12.1 | 73563.4 | 26546.7 | 100110.1 |  | 20587 |  | 13247.7 | 20236.63 | 0.04 | 8.57 |  | 100000 | 98560 | 97562 | 260 | 260 | 100000 | 98300 | 1.729% | 11.45 | 100000 | 98270.6002 | 39.21
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | 6:11 | 18:31 | 17183.6 | 17231.7 | 23732.6 | 23943.1 | 23990.2 | 19032 | 18697.5 |  |  | 3.92 | 3.99 | 29.07 | 35.27 | 72.93 | 0 | 3.9 | 8.73 | 106081.2 | 37729.5 | 143810.7 |  | 20729 |  | 13336.2 | 20378.059 | 0.04 | 8.85 |  | 142000 | 141600 | 141429 | 280 | 280 | 142000 | 141320 | 0.4812% | 12.3333 | 142000 | 141316.728 | 39.21
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | 6:18 | 17:55 | 11838 | 11956.5 | 16551.2 | 16790.4 | 16926.9 | 13121.7 | 12972.4 |  |  | 2.71 | 2.74 | 28.22 | 32.41 | 76 | 0 | 3.62 | 11.91 | 74063 | 26094.1 | 100157.1 |  | 20829 |  | 13397.8 | 20476.162 | 0.04 | 9.15 |  | 100000 | 98560 | 98103 | 300 | 300 | 100000 | 98260 | 1.771% | 11.6167 | 100000 | 98229.1879 | 39.21
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | 6:28 | 18:00 | 12838.9 | 12924.6 | 17948.4 | 18114.9 | 18066 | 14139 | 13889.7 |  |  | 2.95 | 3 | 28.56 | 33.66 | 73.86 | 0 | 3.87 | 9.07 | 79892.8 | 28028.7 | 107921.5 |  | 20936 |  | 13464.3 | 20581.954 | 0.04 | 9.42 |  | 107000 | 106400 | 105792 | 270 | 270 | 107000 | 106130 | 0.8197% | 11.5333 | 107000 | 106122.8682 | 39.21
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | 6:33 | 17:58 | 9171.7 | 9239.7 | 12856.3 | 12439.5 | 12527.9 | 10081.2 | 9754.2 |  |  | 2.06 | 2.09 | 26.86 | 30 | 82.85 | 0.0012 | 3.47 | 7.6 | 56235.1 | 19835.4 | 76070.5 |  | 21011 |  | 13511 | 20655.466 | 0.04 | 9.7 |  | 75000 | 74720 | 73512 | 280 | 280 | 75000 | 74440 | 0.7523% | 11.4167 | 75000 | 74435.7872 | 39.21
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | 6:33 | 18:30 | 6741.8 | 6826.1 | 9373.1 | 9503.2 | 9534.5 | 7493.6 | 7407.3 |  |  | 1.39 | 1.39 | 25.01 | 25.15 | 89.96 | 0.0007163 | 3.9 | 8.42 | 41978.7 | 14900.9 | 56879.6 |  | 21068 |  | 13545.7 | 20710.618 | 0.04 | 10 |  | 57000 | 55520 | 55152 | 300 | 300 | 57000 | 55220 | 3.223% | 11.95 | 57000 | 55162.6222 | 39.21
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | 6:26 | 18:05 | 7793.1 | 7898.8 | 10974.2 | 11144 | 11197.9 | 8721.4 | 8622.7 |  |  | 1.72 | 1.7 | 25.64 | 26.104 | 88.53 | 0.00014327 | 3.26 | 6.65 | 49008 | 17344.1 | 66352.1 |  | 21134 |  | 13586.2 | 20775.162 | 0.04 | 10.48 |  | 66000 | 64800 | 64544 | 480 | 480 | 66000 | 64320 | 2.612% | 11.65 | 66000 | 64276.1194 | 39.21
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | 6:25 | 18:24 | 6643.7 | 6716.3 | 9291.9 | 9411 | 9415.3 | 7373.5 | 7340.3 |  |  | 1.45 | 1.445 | 25.149 | 26.08 | 83.52 | 0.00027778 | 2.99 | 5.35 | 41478.2 | 14713.8 | 56192 |  | 21189 |  | 13620.5 | 20829.5706 | 0.04 | 10.73 |  | 55000 | 54880 | 54408.625 | 250 | 250 | 55000 | 54630 | 0.6773% | 11.9833 | 55000 | 54627.4941 | 39.21
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | 7:46 | 18:22 | 6886.9 | 6956.3 | 9687.6 | 9796.6 | 9804.3 | 7723 | 7668.7 |  |  | 1.66 | 1.67 | 25.05 | 26.89 | 83 | 0.00015699 | 2.62 | 6.32 | 43131.7 | 15391.7 | 58523.4 |  | 21248 |  | 13656.4 | 20886.389 | 0.04 | 11.02 |  | 59000 | 57440 | 56818.375 | 290 | 290 | 59000 | 57150 | 3.237% | 10.6 | 59000 | 57090.1137 | 39.21
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | 6:07 | 18:46 | 22901 | 23071 | 31689.6 | 31977 | 32413.5 | 25766.4 | 25635.7 |  |  | 5.579 | 5.842 | 29.898 | 37.64 | 69.2604 | 0.00015699 | 3.77 | 7.67 | 142052.1 | 51402.1 | 193454.2 |  | 21439 |  | 13775.6 | 21076.588 | 0.04 | 11.32 |  | 191000 | 190720 | 190199 | 300 | 300 | 191000 | 190420 | 0.3046% | 12.65 | 191000 | 190418.2334 | 39.21
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | 6:01 | 18:38 | 22972.3 | 23080.3 | 31572.2 | 31810.6 | 32423.2 | 24488 | 24239.8 |  |  | 5.93 | 6.17 | 30.19 | 37.99 | 65.68 | 0.00015699 | 4.29 | 9.12 | 141858.6 | 48727.8 | 190586.4 |  | 21628 |  | 13892.2 | 21263 | 0.04 | 11.6 |  | 189000 | 186560 | 186412 | 280 | 280 | 189000 | 186280 | 1.46% | 12.6167 | 189000 | 186240.2834 | 39.21
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | 6:10 | 18:40 | 17940 | 18101 | 25078 | 25281 | 25339.5 | 19902.7 | 19755.5 |  |  | 4.2805 | 4.395 | 29.503 | 35.71 | 67.37 | 0.00015699 | 4.06 | 10.17 | 111739.5 | 39658.2 | 151397.7 |  | 21778 |  | 13986 | 21412.7428 | 0.04 | 11.91 |  | 150000 | 150080 | 149742.8 | 310 | 310 | 150000 | 149770 | 0.1536% | 12.5 | 150000 | 149769.6468 | 39.21
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0 | 39.21
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 39.21
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [19 empty] | 0 | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0

## IGA_BD (hidden)
Sr. No. | Date | Finacial Year | Calendor Year | Contractuyal year | Operating Year | Affected Feeder | SPV | Consumer | Plant Equivalent Weightage | Breakdown Description | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost POA(kWh/m2) | Estimated Energy Loss (kWh)
1 |  | 1900 | 1900 | Year-1 | Year_1 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
2 |  | 2024 | 2023 | Year-1 | Year_1 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
3 |  | 2024 | 2023 | Year-1 | Year_1 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
4 |  | 2024 | 2023 | Year-1 | Year_1 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
5 |  | 2024 | 2023 | Year-1 | Year_1 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
6 |  | 2024 | 2023 | Year-1 | Year_1 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
7 |  | 2024 | 2024 | Year-1 | Year_1 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
8 |  | 2024 | 2024 | Year-1 | Year_1 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
9 |  | 2024 | 2024 | Year-1 | Year_1 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
10 |  | 2024 | 2024 | Year-1 | Year_1 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
11 |  | 2024 | 2024 | Year-1 | Year_1 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
12 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
13 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
14 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
15 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
16 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
17 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
18 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
19 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
20 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
21 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
22 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
23 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
24 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
25 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
26 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
27 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
28 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
29 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
30 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0
31 |  | 2025 | 2024 | Year-1 | Year_2 |  | #N/A | #N/A | [5 empty] | 0 | 0 | 0

## Modelling New
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | CC*Bugt (MTD) | CC*Bugt (YTD) | Capacity | 39.21
1 | April | 4 | 2024-04-01 | 2024 | FY25 | 30 | 205.8 | 208 |  | 32.9 |  |  |  |  | 6.9333 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 99.5% | 99.5% | [6 empty] | 0 | 0
2 | May | 5 | 2024-05-01 | 2024 | FY25 | 31 | 209.8 | 203.8 |  | 34.6 |  |  |  |  | 6.5742 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 99.5% | 99.5% | [6 empty] | 0 | 0
3 | June | 6 | 2024-06-01 | 2024 | FY25 | 30 | 149.5 | 143.4 |  | 30.5 |  |  |  |  | 4.78 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 99.5% | 99.5% | [6 empty] | 0 | 0
4 | July | 7 | 2024-07-01 | 2024 | FY25 | 31 | 122.2 | 118.1 |  | 27.1 |  |  |  |  | 3.8097 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 99.5% | 99.5% | [6 empty] | 0 | 0
5 | August | 8 | 2024-08-01 | 2024 | FY25 | 31 | 123.1 | 121.2 |  | 26.2 |  |  |  |  | 3.9097 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 99.5% | 99.5% | [6 empty] | 0 | 0
6 | September | 9 | 2024-09-01 | 2024 | FY25 | 30 | 143.7 | 147.3 |  | 26.5 |  |  |  |  | 4.91 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 99.5% | 99.5% | [6 empty] | 0 | 0
7 | October | 10 | 2024-10-01 | 2024 | FY25 | 31 | 164.1 | 178.8 |  | 26 |  |  |  |  | 5.7677 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 99.5% | 99.5% | [6 empty] | 0 | 0
8 | November | 11 | 2024-11-01 | 2024 | FY25 | 30 | 147.7 | 169.4 |  | 23.7 |  |  |  |  | 5.6467 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 99.5% | 99.5% | [6 empty] | 0 | 0
9 | December | 12 | 2024-12-01 | 2024 | FY25 | 31 | 144.9 | 171.3 |  | 21.59 |  |  |  |  | 5.5258 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 99.5% | 99.5% | [6 empty] | 0 | 0
10 | January | 1 | 2025-01-01 | 2025 | FY25 | 31 | 150.6 | 174.6 |  | 21.9 |  |  |  |  | 5.6323 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 99.5% | 99.5% | [6 empty] | 0 | 0
11 | February | 2 | 2025-02-01 | 2025 | FY25 | 28 | 159 | 178.1 |  | 25.1 |  | 5728 | 39.21 | 82.02% | 6.3607 | 0 | 0 | 0 | 204.5714 | 0 | 0 | 21.74% | [7 empty] | 99.5% | 99.5% | [6 empty] | 0 | 0
12 | March | 3 | 2025-03-01 | 2025 | FY25 | 31 | 200.8 | 213 |  | 29 |  | 6642 | 39.21 | 79.53% | 6.871 | 3 | 20.6129 | 20.6129 | 214.2581 | 642.7742 | 642.7742 | 22.77% | 22.77% | 22.77% | 30.72 | 30.72 |  |  |  | 99.5% | 99.5% | [6 empty] | 503596.6138 | 503596.6138
13 | April | 4 | 2025-04-01 | 2025 | FY26 | 30 | 167.2997 | 181.9063 |  | 32.9 |  | 4997.8694 | 39.1838 | 70.12% | 6.0635 | 30 | 181.9063 | 181.9063 | 166.5956 | 4997.8694 | 4997.8694 | 17.72% | 17.72% | 17.72% | 35.9047 | 35.9047 |  |  |  | 99.5% | 99.5% | [6 empty] | 4579623.8362 | 4579623.8362
14 | May | 5 | 2025-05-01 | 2025 | FY26 | 31 | 203.1012 | 211.8017 |  | 34.6 |  | 6221.6559 | 45.9338 | 63.95% | 6.8323 | 31 | 211.8017 | 393.708 | 200.6986 | 6221.6559 | 11219.5253 | 18.21% | 18.21% | 16.68% | 39.21 | 37.5573 |  |  |  | 99.5% | 99.5% | [6 empty] | 5310934.3094 | 9890558.1456
15 | June | 6 | 2025-06-01 | 2025 | FY26 | 30 | 149.5 | 143.4 |  | 30.5 |  | 5047.4883 | 45.9338 | 76.63% | 4.78 | 30 | 143.4 | 537.108 | 168.2496 | 5047.4883 | 16267.0137 | 15.26% | 15.26% | 16.22% | 39.21 | 38.1082 |  |  |  | 99.5% | 99.5% | [6 empty] | 4308640.5415 | 14199198.6871
16 | July | 7 | 2025-07-01 | 2025 | FY26 | 31 | 122.2 | 118.1 |  | 27.1 |  | 5310.5158 | 54.3713 | 82.7% | 3.8097 | 13 | 49.5258 | 586.6338 | 171.307 | 2226.9905 | 18494.0042 | 13.13% | 13.13% | 13.63% | 39.21 | 38.3837 |  |  |  | 99.5% | 99.5% | [6 empty] | 3829695.3816 | 18028894.0687
17 | August | 8 | 2025-08-01 | 2025 | FY26 | 31 | 123.1 | 121.2 |  | 26.2 |  | 5749.7768 | 54.3713 | 87.25% | 3.9097 | 0 | 0 | 586.6338 | 185.4767 | 0 | 18494.0042 | 14.21% |  | 13.63% | 0 | 30.7069 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 18028894.0687
18 | September | 9 | 2025-09-01 | 2025 | FY26 | 30 | 143.7 | 147.3 |  | 26.5 |  | 6736.6824 | 54.3713 | 84.12% | 4.91 | 0 | 0 | 586.6338 | 224.5561 | 0 | 18494.0042 | 17.21% |  | 13.63% | 0 | 25.5891 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 18028894.0687
19 | October | 10 | 2025-10-01 | 2025 | FY26 | 31 | 164.1 | 178.8 |  | 26 |  | 17088.3947 | 135 | 70.79% | 5.7677 | 0 | 0 | 586.6338 | 551.2385 | 0 | 18494.0042 | 17.01% |  | 5.488% | 0 | 21.9335 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 18028894.0687
20 | November | 11 | 2025-11-01 | 2025 | FY26 | 30 | 147.7 | 169.4 |  | 23.7 |  | 17210.8315 | 135 | 75.26% | 5.6467 | 0 | 0 | 586.6338 | 573.6944 | 0 | 18494.0042 | 17.71% |  | 5.488% | 0 | 19.1918 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 18028894.0687
21 | December | 12 | 2025-12-01 | 2025 | FY26 | 31 | 144.9 | 171.3 |  | 21.59 |  | 18288.2483 | 135 | 79.08% | 5.5258 | 0 | 0 | 586.6338 | 589.9435 | 0 | 18494.0042 | 18.21% |  | 5.488% | 0 | 17.0594 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 18028894.0687
22 | January | 1 | 2026-01-01 | 2026 | FY26 | 31 | 150.6 | 174.6 |  | 21.9 |  | 20510.8507 | 135 | 87.02% | 5.6323 | 0 | 0 | 586.6338 | 661.6403 | 0 | 18494.0042 | 20.42% |  | 5.488% |  | 17.0594 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 18028894.0687
23 | February | 2 | 2026-02-01 | 2026 | FY26 | 28 | 159 | 178.1 |  | 25.1 |  | 20639.3977 | 135 | 85.84% | 6.3607 | 0 | 0 | 586.6338 | 737.1213 | 0 | 18494.0042 | 22.75% |  | 5.488% |  | 17.0594 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 18028894.0687
24 | March | 3 | 2026-03-01 | 2026 | FY26 | 31 | 200.8 | 213 |  | 29 |  | 23626.5763 | 135 | 82.17% | 6.871 | 0 | 0 | 586.6338 | 762.1476 | 0 | 18494.0042 | 23.52% |  | 5.488% |  | 17.0594 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 18028894.0687
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## Plant_BD
Sr. No. | Date | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Inverter Station Number (if Bd in filed) | Inverter number (If Inv, SCb or Str BD) | Inverter Module Number (If Inv, SCb or Str BD) | SCB Number (If SCB or Str BD) | String Type(If String BD) | Equipment (If any BD other than PV array and inv) | C1 | C2 | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Fault Category | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgement Time | Work Start time on Fault | Work Completion time on fault | Acknow. time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(kWh/m2) | Approximate Energy Loss (KWh) | Bugt Capacity | CC*Bugt | PTW No. | Job Card No.
1 | 2025-04-06 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 6:27 | 18:15 | 11.8 | IS2 | Inv1 |  |  |  |  | 1 | 1 | IS2Inv1 | 6511.66 | 16.61% | IDT |  | ICOG Breaker triped due to HV winding tam. High | 12:55 | 12:55 | 12:55 | 17:30 | 0 | 0 | 4.5833 | 4.5833 | Check the Protection relay, fault reset & charge the breaker | Close | 0.76116 | 3.0036 | 13714.0932
2 | 2025-04-06 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 6:27 | 18:15 | 11.8 | IS2 | Inv2 |  |  |  |  | 1 | 1 | IS2Inv2 | 6495.855 | 16.57% | IDT |  | ICOG Breaker triped due to HV winding tam. High | 12:55 | 12:55 | 12:55 | 17:30 | 0 | 0 | 4.5833 | 4.5833 | Check the Protection relay, fault reset & charge the breaker | Close | 0.75931 | 3.0036 | 13680.8066
3 | 2025-04-07 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 6:27 | 18:15 | 11.8 | IS2 | Inv1 |  |  |  |  | 1 | 1 | IS2Inv1 | 6511.66 | 16.61% | IDT |  | ICOG Breaker triped due to HV winding tam. High | 12:40 | 12:40 | 12:40 | 13:18 | 0 | 0 | 0.63333 | 0.63333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.10518 | 0.60555 | 2764.8723
4 | 2025-04-07 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:27 | 18:15 | 11.8 | IS2 | Inv2 |  |  |  |  | 1 | 1 | IS2Inv2 | 6495.855 | 16.57% | IDT |  | ICOG Breaker triped due to HV winding tam. High | 12:40 | 12:40 | 12:40 | 13:18 | 0 | 0 | 0.63333 | 0.63333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.10492 | 0.60555 | 2758.1614
5 | 2025-04-11 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:26 | 18:08 | 11.7 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | IDT |  | ICOG Breaker triped Due to AC under voltage | 14:51 | 14:51 | 14:51 | 15:38 | 0 | 0 | 0.78333 | 0.78333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.093146 | 0.39826 | 1301.9939
6 | 2025-04-11 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:26 | 18:08 | 11.7 | IS1 | Inv2 |  |  |  |  | 1 | 1 | IS1Inv2 | 4662.475 | 11.89% | IDT |  | ICOG Breaker triped Due to AC under voltage | 14:51 | 14:51 | 14:51 | 15:38 | 0 | 0 | 0.78333 | 0.78333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.093146 | 0.39826 | 1301.9939
7 | 2025-04-11 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:26 | 18:08 | 11.7 | IS2 | Inv1 |  |  |  |  | 1 | 1 | IS2Inv1 | 6511.66 | 16.61% | IDT |  | ICOG Breaker triped Due to AC under voltage | 14:51 | 14:51 | 14:51 | 15:38 | 0 | 0 | 0.78333 | 0.78333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.13009 | 0.39826 | 1818.3779
8 | 2025-04-11 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:26 | 18:08 | 11.7 | IS2 | Inv2 |  |  |  |  | 1 | 1 | IS2Inv2 | 6495.855 | 16.57% | IDT |  | ICOG Breaker triped Due to AC under voltage | 14:51 | 14:51 | 14:51 | 15:38 | 0 | 0 | 0.78333 | 0.78333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.12977 | 0.39826 | 1813.9644
9 | 2025-04-11 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:26 | 18:08 | 11.7 | IS3 | Inv1 |  |  |  |  | 1 | 1 | IS3Inv1 | 6527.465 | 16.65% | IDT |  | ICOG Breaker triped Due to AC under voltage | 14:51 | 14:51 | 14:51 | 15:38 | 0 | 0 | 0.78333 | 0.78333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.13041 | 0.39826 | 1822.7914
10 | 2025-04-11 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:26 | 18:08 | 11.7 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | IDT |  | ICOG Breaker triped Due to AC under voltage | 14:51 | 14:51 | 14:51 | 15:38 | 0 | 0 | 0.78333 | 0.78333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.10197 | 0.39826 | 1425.2895
11 | 2025-04-11 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:26 | 18:08 | 11.7 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | IDT |  | ICOG Breaker triped Due to AC under voltage | 14:51 | 14:51 | 14:51 | 15:38 | 0 | 0 | 0.78333 | 0.78333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.10197 | 0.39826 | 1425.2895
12 | 2025-04-11 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:26 | 18:08 | 11.7 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | Inverter |  | Inverter Trip Due to M_1 _1 Bus over voltage | 15:40 | 15:40 | 15:40 | 17:39 | 0 | 0 | 1.9833 | 1.9833 | Check the field side all SCB's & Inv Bus bar floting & on the inverter | Close | 0.25817 | 0.54269 | 1942.1953
13 | 2025-04-21 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:16 | 18:20 | 12.0667 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | MV Panel |  | ICOG Breaker triped Due to AC under voltage | 14:33 | 14:33 | 14:33 | 14:47 | 0 | 0 | 0.23333 | 0.23333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.027746 | 0.20238 | 661.637
14 | 2025-04-21 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:16 | 18:20 | 12.0667 | IS1 | Inv2 |  |  |  |  | 1 | 1 | IS1Inv2 | 4662.475 | 11.89% | MV Panel |  | ICOG Breaker triped Due to AC under voltage | 14:33 | 14:33 | 14:33 | 14:47 | 0 | 0 | 0.23333 | 0.23333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.027746 | 0.20238 | 661.637
15 | 2025-04-21 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:16 | 18:20 | 12.0667 | IS2 | Inv1 |  |  |  |  | 1 | 1 | IS2Inv1 | 6511.66 | 16.61% | MV Panel |  | ICOG Breaker triped Due to AC under voltage | 14:33 | 14:33 | 14:33 | 14:47 | 0 | 0 | 0.23333 | 0.23333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.03875 | 0.20238 | 924.049
16 | 2025-04-21 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:16 | 18:20 | 12.0667 | IS2 | Inv2 |  |  |  |  | 1 | 1 | IS2Inv2 | 6495.855 | 16.57% | MV Panel |  | ICOG Breaker triped Due to AC under voltage | 14:33 | 14:33 | 14:33 | 14:47 | 0 | 0 | 0.23333 | 0.23333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.038656 | 0.20238 | 921.8062
17 | 2025-04-21 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:16 | 18:20 | 12.0667 | IS3 | Inv1 |  |  |  |  | 1 | 1 | IS3Inv1 | 6527.465 | 16.65% | MV Panel |  | ICOG Breaker triped Due to AC under voltage | 14:33 | 14:33 | 14:33 | 14:47 | 0 | 0 | 0.23333 | 0.23333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.038844 | 0.20238 | 926.2918
18 | 2025-04-21 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:16 | 18:20 | 12.0667 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | MV Panel |  | ICOG Breaker triped Due to AC under voltage | 14:33 | 14:33 | 14:33 | 14:47 | 0 | 0 | 0.23333 | 0.23333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.030373 | 0.20238 | 724.2924
19 | 2025-04-21 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:16 | 18:20 | 12.0667 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | MV Panel |  | ICOG Breaker triped Due to AC under voltage | 14:33 | 14:33 | 14:33 | 14:47 | 0 | 0 | 0.23333 | 0.23333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.030373 | 0.20238 | 724.2924
20 | 2025-04-22 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:14 | 18:18 | 12.0667 | IS2 | Inv1 |  |  |  |  | 1 | 1 | IS2Inv1 | 6511.66 | 16.61% | IDT |  | ICOG Breaker triped due to HV winding tam. High | 12:56 | 12:56 | 12:56 | 13:12 | 0 | 0 | 0.26667 | 0.26667 | Check the Protection relay, fault reset & charge the breaker | Close | 0.044286 | 0.26603 | 1214.6436
21 | 2025-04-22 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:14 | 18:18 | 12.0667 | IS2 | Inv2 |  |  |  |  | 1 | 1 | IS2Inv2 | 6495.855 | 16.57% | IDT |  | ICOG Breaker triped due to HV winding tam. High | 12:56 | 12:56 | 12:56 | 13:12 | 0 | 0 | 0.26667 | 0.26667 | Check the Protection relay, fault reset & charge the breaker | Close | 0.044178 | 0.26603 | 1211.6954
22 | 2025-04-23 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:16 | 18:16 | 12 | IS2 | Inv1 |  |  |  |  | 1 | 1 | IS2Inv1 | 6511.66 | 16.61% | IDT |  | ICOG Breaker triped due to HV winding tam. High | 14:04 | 14:04 | 14:04 | 14:19 | 0 | 0 | 0.25 | 0.25 | Check the Protection relay, fault reset & charge the breaker | Close | 0.041518 | 0.22731 | 1037.8774
23 | 2025-04-23 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:16 | 18:16 | 12 | IS2 | Inv2 |  |  |  |  | 1 | 1 | IS2Inv2 | 6495.855 | 16.57% | IDT |  | ICOG Breaker triped due to HV winding tam. High | 14:04 | 14:04 | 14:04 | 14:19 | 0 | 0 | 0.25 | 0.25 | Check the Protection relay, fault reset & charge the breaker | Close | 0.041417 | 0.22731 | 1035.3583
24 | 2025-04-24 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:14 | 18:18 | 12.0667 | IS3 | Inv1 |  |  |  |  | 1 | 1 | IS3Inv1 | 6527.465 | 16.65% | IDT |  | ICOG Breaker triped due to HV winding tam. High | 13:28 | 13:28 | 13:28 | 14:42 | 0 | 0 | 1.2333 | 1.2333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.20532 | 1.0488 | 4800.1755
25 | 2025-04-26 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:17 | 18:20 | 12.05 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | Inverter |  | Due to inverter setting checking work | 14:22 | 14:22 | 14:22 | 14:30 | 0 | 0 | 0.13333 | 0.13333 | Check the inverter setting & turn On inverter | Close | 0.017356 | 0.095917 | 343.27
26 | 2025-04-27 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:12 | 18:23 | 12.1833 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | Inverter |  | Due to inverter setting Problem | 6:12 | 6:12 | 6:12 | 8:05 | 0 | 0 | 1.8833 | 1.8833 | Check the inverter setting & turn On inverter | Close | 0.24516 | 0.29651 | 1061.1562
27 | 2025-04-28 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 6:15 | 18:22 | 12.1167 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | Inverter |  | Due to inverter setting Problem | 14:48 | 14:48 | 14:48 | 15:22 | 0 | 0 | 0.56667 | 0.56667 | Check the inverter setting & turn On inverter | Close | 0.073763 | 0.43045 | 1540.5089
28 | 2025-05-02 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:12 | 18:25 | 12.2167 | IS1 | Inv1 | M1 | SCB7 | Str_Typ1(545*58) |  | 0 | 0 | Str_Typ1(545*58) | 31.61 | 0.08062% | String Fuses |  | String fuse faulty | 6:12 | 6:12 | 6:12 | 16:50 | 0 | 0 | 10.6333 | 10.6333 | Replaced the fuse | Close | 0.0085723 | 6.2584 | 126.5118
29 | 2025-05-03 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:11 | 18:27 | 12.2667 | IS4 | Inv1 | M3 |  |  |  | 1 | 1 | IS4Inv1M3 | 1276 | 3.254% | Inverter |  | ICR-04 Inv-01 MPPT-03 tripped due to Branch fan fault | 6:11 | 6:11 | 6:11 | 11:52 | 0 | 0 | 5.6833 | 5.6833 | Work in Progress | Close | 0.18495 | 2.955 | 2411.2951
30 | 2025-05-03 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:11 | 18:27 | 12.2667 | IS4 | Inv1 | M4 |  |  |  | 1 | 1 | IS4Inv1M4 | 1276 | 3.254% | Inverter |  | ICR-04 Inv-01 MPPT-03 tripped due to Branch fan fault | 6:11 | 6:11 | 6:11 | 11:52 | 0 | 0 | 5.6833 | 5.6833 | Work in Progress | Close | 0.18495 | 2.955 | 2411.2951
31 | 2025-05-03 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:11 | 18:27 | 12.2667 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | Inverter |  | ICR-04 Inv-01 tripped due to grid overvoltage & rear power cabin fan fault | 11:53 | 11:53 | 11:53 | 13:15 | 0 | 0 | 1.3667 | 1.3667 | Check the inverter parameters & turn On inverter | Close | 0.1779 | 1.3017 | 4248.8
32 | 2025-05-03 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:11 | 18:27 | 12.2667 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | Inverter |  | ICR-04 Inv-01 tripped due to grid overvoltage & rear power cabin fan fault | 14:26 | 14:26 | 14:26 | 15:56 | 0 | 0 | 1.5 | 1.5 | Check the inverter parameters & turn On inverter | Close | 0.19526 | 0.8163 | 2664.445
33 | 2025-05-04 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:10 | 18:28 | 12.3 | IS4 | Inv1 | M3 |  |  |  | 1 | 1 | IS4Inv1M3 | 1276 | 3.254% | Inverter |  | ICR-04 Inv-01 MPPT-03 tripped due to Branch fan fault | 6:10 | 6:10 | 6:10 | 18:28 | 0 | 0 | 12.3 | 12.3 | Work in Progress | Close | 0.40028 | 6.79 | 5540.7052
34 | 2025-05-04 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:10 | 18:28 | 12.3 | IS4 | Inv1 | M4 |  |  |  | 1 | 1 | IS4Inv1M4 | 1276 | 3.254% | Inverter |  | ICR-04 Inv-01 MPPT-04 tripped due to Branch fan fault | 6:10 | 6:10 | 6:10 | 18:28 | 0 | 0 | 12.3 | 12.3 | Work in Progress | Close | 0.40028 | 6.79 | 5540.7052
35 | 2025-05-04 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:10 | 18:28 | 12.3 | IS3 | Inv1 | M4 | SCB1 | Str_Typ2(550*29) |  | 0 | 0 | Str_Typ2(550*29) | 15.95 | 0.04068% | Module |  | MC-4 Connector Open | 6:10 | 6:10 | 6:10 | 16:05 | 0 | 0 | 9.9167 | 9.9167 | Connect the MC-4 Connector | Close | 0.0040339 | 6.2794 | 64.0505
36 | 2025-05-04 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:10 | 18:28 | 12.3 | IS3 | Inv1 | M3 | SCB2 | Str_Typ2(550*29) |  | 0 | 0 | Str_Typ2(550*29) | 15.95 | 0.04068% | Module |  | MC-4 Connector Open | 6:10 | 6:10 | 6:10 | 16:12 | 0 | 0 | 10.0333 | 10.0333 | Connect the MC-4 Connector | Close | 0.0040814 | 6.3335 | 64.6028
37 | 2025-05-04 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:10 | 18:28 | 12.3 | IS3 | Inv1 | M3 | SCB2 | Str_Typ2(550*29) |  | 0 | 0 | Str_Typ2(550*29) | 15.95 | 0.04068% | Module |  | MC-4 Connector Open | 6:10 | 6:10 | 6:10 | 16:26 | 0 | 0 | 10.2667 | 10.2667 | Connect the MC-4 Connector | Close | 0.0041763 | 6.4276 | 65.5626
38 | 2025-05-05 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:10 | 17:19 | 11.15 | IS4 | Inv1 | M3 |  |  |  | 1 | 1 | IS4Inv1M3 | 1276 | 3.254% | Module |  | ICR-04 Inv-01 MPPT-03 tripped due to Branch fan fault | 6:10 | 6:10 | 6:10 | 17:19 | 0 | 0 | 11.15 | 11.15 | Work in Progress | Close | 0.36285 | 5.79 | 4724.6956
39 | 2025-05-05 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:10 | 17:19 | 11.15 | IS4 | Inv1 | M4 |  |  |  | 1 | 1 | IS4Inv1M4 | 1276 | 3.254% | Module |  | ICR-04 Inv-01 MPPT-04 tripped due to Branch fan fault | 6:10 | 6:10 | 6:10 | 17:19 | 0 | 0 | 11.15 | 11.15 | Work in Progress | Close | 0.36285 | 5.79 | 4724.6956
40 | 2025-05-06 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 7:13 | 18:24 | 11.1833 | IS1 | Inv2 |  |  |  |  | 1 | 1 | IS1Inv2 | 4662.475 | 11.89% | Inverter |  | Inverter tripped due to grid voltage abnormal | 7:53 | 7:53 | 7:53 | 9:15 | 0 | 0 | 1.3667 | 1.3667 | Reset the fault & charge the inverter | Close | 0.16251 | 0.80448 | 2398.7122
41 | 2025-05-06 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 7:13 | 18:24 | 11.1833 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | Inverter |  | Inverter tripped due to grid voltage abnormal | 7:46 | 7:46 | 7:46 | 9:41 | 0 | 0 | 1.9167 | 1.9167 | Reset the fault & charge the inverter | Close | 0.22791 | 0.96766 | 2885.2518
42 | 2025-05-06 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 7:13 | 18:24 | 11.1833 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | Inverter |  | ICR-04 Inv-01 MPPT-03 tripped due to Branch fan fault | 7:13 | 7:13 | 7:13 | 8:42 | 0 | 0 | 1.4833 | 1.4833 | Replace the Branch fan, Reset the fault & charge the inverter | Close | 0.19309 | 0.49937 | 1629.9671
43 | 2025-05-06 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 7:13 | 18:24 | 11.1833 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | Inverter |  | ICR-04 Inv-01 MPPT-04 tripped due to Branch fan fault | 7:13 | 7:13 | 7:13 | 7:34 | 0 | 0 | 0.35 | 0.35 | Replace the Branch fan, Reset the fault & charge the inverter | Close | 0.04556 | 0.075863 | 247.6207
44 | 2025-05-06 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 7:13 | 18:24 | 11.1833 | IS4 | Inv1 | M1 |  |  |  | 1 | 1 | IS4Inv1M1 | 1276 | 3.254% | Inverter |  | M-1_1 square matrix insulation resistance abnormal | 7:13 | 7:13 | 7:13 | 18:24 | 0 | 0 | 11.1833 | 11.1833 | Work in Progress | Close | 0.36394 | 7.3 | 5956.8701
45 | 2025-05-07 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:07 | 18:04 | 11.95 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | Inverter |  | Inverter tripped due to grid voltage abnormal | 7:53 | 7:53 | 7:53 | 9:45 | 0 | 0 | 1.8667 | 1.8667 | Reset the fault & charge the inverter | Close | 0.22197 | 1.05 | 3130.7646
46 | 2025-05-07 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:07 | 18:04 | 11.95 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | Inverter |  | Inverter tripped due to grid voltage abnormal | 17:31 | 17:31 | 17:31 | 18:04 | 0 | 0 | 0.55 | 0.55 | Reset the fault & charge the inverter | Close | 0.065401 | 0.031 | 92.4321
47 | 2025-05-07 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:07 | 18:04 | 11.95 | IS4 | Inv1 | M1 |  |  |  | 1 | 1 | IS4Inv1M1 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-1 tripped Due to Inductor Current abnormal | 6:07 | 6:07 | 6:07 | 18:04 | 0 | 0 | 11.95 | 11.95 | Work in Progress | Close | 0.38889 | 7.12 | 5809.9884
48 | 2025-05-07 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:07 | 18:04 | 11.95 | IS4 | Inv1 | M2 |  |  |  | 1 | 1 | IS4Inv1M2 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-2 tripped Due to Inductor Current abnormal | 6:07 | 6:07 | 6:07 | 18:04 | 0 | 0 | 11.95 | 11.95 | Work in Progress | Close | 0.38889 | 7.12 | 5809.9884
49 | 2025-05-07 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:07 | 18:04 | 11.95 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | Inverter |  | Inverter tripped due to grid voltage abnormal | 7:34 | 7:34 | 7:34 | 10:29 | 0 | 0 | 2.9167 | 2.9167 | Reset the fault & charge the inverter | Close | 0.34682 | 1.74 | 5188.1242
50 | 2025-05-07 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:07 | 18:04 | 11.95 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | Inverter |  | Inverter tripped due to grid voltage abnormal | 12:29 | 12:29 | 12:29 | 12:38 | 0 | 0 | 0.15 | 0.15 | Reset the fault & charge the inverter | Close | 0.017837 | 0.16591 | 494.6766
51 | 2025-05-07 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:07 | 18:04 | 11.95 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | Inverter |  | Inverter tripped due to grid voltage abnormal | 13:02 | 13:02 | 13:02 | 13:34 | 0 | 0 | 0.53333 | 0.53333 | Reset the fault & charge the inverter | Close | 0.063419 | 0.50135 | 1494.8796
52 | 2025-05-07 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:07 | 18:04 | 11.95 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | Inverter |  | Inverter tripped due to grid voltage abnormal | 17:23 | 17:23 | 17:23 | 18:04 | 0 | 0 | 0.68333 | 0.68333 | Reset the fault & charge the inverter | Close | 0.081255 | 0.053964 | 160.9034
53 | 2025-05-08 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:11 | 18:04 | 11.8833 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | Inverter |  | Inverter tripped due to grid voltage abnormal | 8:25 | 8:25 | 8:25 | 9:12 | 0 | 0 | 0.78333 | 0.78333 | Reset the fault & charge the inverter | Close | 0.093146 | 0.35966 | 1072.3884
54 | 2025-05-08 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:11 | 18:04 | 11.8833 | IS1 | Inv2 |  |  |  |  | 1 | 1 | IS1Inv2 | 4662.475 | 11.89% | Inverter |  | Inverter tripped due to grid voltage abnormal | 8:01 | 8:01 | 8:01 | 10:07 | 0 | 0 | 2.1 | 2.1 | Reset the fault & charge the inverter | Close | 0.24971 | 1.0978 | 3273.438
55 | 2025-05-08 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:11 | 18:04 | 11.8833 | IS4 | Inv1 | M1 |  |  |  | 1 | 1 | IS4Inv1M1 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-1 tripped Due to M-1-1 square matrix insulation rasistance abnormal | 6:11 | 6:11 | 6:11 | 15:00 | 0 | 0 | 8.8167 | 8.8167 | Reset the fault & charge the inverter | Close | 0.28692 | 6.57 | 5361.1831
56 | 2025-05-08 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:11 | 18:04 | 11.8833 | IS4 | Inv1 | M2 |  |  |  | 1 | 1 | IS4Inv1M2 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-2 tripped Due to M-1-1 square matrix insulation rasistance abnormal | 6:11 | 6:11 | 6:11 | 15:00 | 0 | 0 | 8.8167 | 8.8167 | Reset the fault & charge the inverter | Close | 0.28692 | 6.57 | 5361.1831
57 | 2025-05-08 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:11 | 18:04 | 11.8833 | IS4 | Inv1 | M3 |  |  |  | 1 | 1 | IS4Inv1M3 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-3 tripped Due to M-1-1 square matrix insulation rasistance abnormal | 6:11 | 6:11 | 6:11 | 18:04 | 0 | 0 | 11.8833 | 11.8833 | Work in Progress | Close | 0.38672 | 5.5957 | 4566.1153
58 | 2025-05-08 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:11 | 18:04 | 11.8833 | IS4 | Inv1 | M4 |  |  |  | 1 | 1 | IS4Inv1M4 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-4 tripped Due to M-1-1 square matrix insulation rasistance abnormal | 6:11 | 6:11 | 6:11 | 18:04 | 0 | 0 | 11.8833 | 11.8833 | Work in Progress | Close | 0.38672 | 5.5957 | 4566.1153
59 | 2025-05-09 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:23 | 18:25 | 12.0333 | IS4 | Inv1 | M1 |  |  |  | 1 | 1 | IS4Inv1M1 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-1 tripped Due to M-1-1 square matrix insulation rasistance abnormal | 6:23 | 6:23 | 6:23 | 18:25 | 0 | 0 | 12.0333 | 12.0333 | Work in Progress | Close | 0.3916 | 7.02 | 5728.3875
60 | 2025-05-10 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:07 | 18:33 | 12.4333 | IS4 | Inv1 | M1 |  |  |  | 1 | 1 | IS4Inv1M1 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-2 tripped Due to M-1-1 square matrix insulation rasistance abnormal | 6:07 | 6:07 | 6:07 | 18:33 | 0 | 0 | 12.4333 | 12.4333 | Work in Progress | Close | 0.40461 | 6.01 | 4904.2177
61 | 2025-05-10 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:07 | 18:33 | 12.4333 | IS4 | Inv1 | M2 |  |  |  | 1 | 1 | IS4Inv1M2 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-1 tripped Due to M-1-1 square matrix insulation rasistance abnormal | 6:07 | 6:07 | 6:07 | 18:33 | 0 | 0 | 12.4333 | 12.4333 | Work in Progress | Close | 0.40461 | 6.01 | 4904.2177
62 | 2025-05-11 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:17 | 18:15 | 11.9667 | IS4 | Inv1 | M1 |  |  |  | 1 | 1 | IS4Inv1M1 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-1 tripped Due to M-1-1 hardware bus overvoltage | 6:17 | 6:17 | 6:17 | 18:15 | 0 | 0 | 11.9667 | 11.9667 | Work in Progress | Close | 0.38943 | 6.45 | 5263.262
63 | 2025-05-11 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:17 | 18:15 | 11.9667 | IS4 | Inv1 | M2 |  |  |  | 1 | 1 | IS4Inv1M2 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-2 tripped Due to M-1-1 hardware bus overvoltage | 6:17 | 6:17 | 6:17 | 18:15 | 0 | 0 | 11.9667 | 11.9667 | Work in Progress | Close | 0.38943 | 6.45 | 5263.262
64 | 2025-05-12 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:15 | 17:46 | 11.5167 | IS4 | Inv1 | M1 |  |  |  | 1 | 1 | IS4Inv1M1 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-1 tripped Due to M-1-1 square matrix insulation rasistance abnormal | 6:15 | 6:15 | 6:15 | 17:46 | 0 | 0 | 11.5167 | 11.5167 | Work in Progress | Close | 0.37478 | 2.62 | 2137.9452
65 | 2025-05-12 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:15 | 17:46 | 11.5167 | IS4 | Inv1 | M2 |  |  |  | 1 | 1 | IS4Inv1M2 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-1 tripped Due to M-1-1 square matrix insulation rasistance abnormal | 6:15 | 6:15 | 6:15 | 17:46 | 0 | 0 | 11.5167 | 11.5167 | Work in Progress | Close | 0.37478 | 2.62 | 2137.9452
66 | 2025-05-12 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:15 | 17:46 | 11.5167 | IS4 | Inv2 | M4 | SCB3 | Str_Typ2(550*29) |  | 0 | 0 | Str_Typ2(550*29) | 15.95 | 0.04068% | String Fuses |  | String fuse blown | 6:15 | 6:15 | 6:15 | 16:20 | 0 | 0 | 10.0833 | 10.0833 | Fuse Replaced | Close | 0.0041017 | 2.2944 | 23.4033
67 | 2025-05-12 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:15 | 17:46 | 11.5167 | IS4 | Inv2 | M4 | SCB6 | Str_Typ2(550*29) |  | 0 | 0 | Str_Typ2(550*29) | 15.95 | 0.04068% | String Fuses |  | String fuse blown | 6:15 | 6:15 | 6:15 | 16:42 | 0 | 0 | 10.45 | 10.45 | Fuse Replaced | Close | 0.0042509 | 2.4308 | 24.7948
68 | 2025-05-13 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 7:05 | 18:28 | 11.3833 | IS4 | Inv1 | M1 |  |  |  | 1 | 1 | IS4Inv1M1 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-1 tripped Due to M-1-1 square matrix insulation rasistance abnormal | 7:05 | 7:05 | 7:05 | 18:28 | 0 | 0 | 11.3833 | 11.3833 | Work in Progress | Close | 0.37044 | 3.18 | 2594.9106
69 | 2025-05-13 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 7:05 | 18:28 | 11.3833 | IS4 | Inv1 | M2 |  |  |  | 1 | 1 | IS4Inv1M2 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-2 tripped Due to M-1-1 square matrix insulation rasistance abnormal | 7:05 | 7:05 | 7:05 | 18:28 | 0 | 0 | 11.3833 | 11.3833 | Work in Progress | Close | 0.37044 | 3.18 | 2594.9106
70 | 2025-05-14 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:06 | 18:21 | 12.25 | IS4 | [5 empty] | 1 | 1 | IS4 |  |  | Inverter |  | ICR-4 Inv-1 Replacment & New one inverter installed | 6:06 | 6:06 | 6:06 | 18:21 | 0 | 0 | 12.25 | 12.25 | Work in Progress | Close |  | 4.15
71 | 2025-05-15 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:08 | 18:28 | 12.3333 | IS4 | Inv1 | M1 |  |  |  | 1 | 1 | IS4Inv1M1 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 Replacment & New one inverter installed | 6:08 | 6:08 | 6:08 | 10:36 | 0 | 0 | 4.4667 | 4.4667 | Inverter Replacment work done | Close | 0.14536 | 1.5696 | 1280.8223
72 | 2025-05-15 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:08 | 18:28 | 12.3333 | IS4 | Inv1 | M2 |  |  |  | 1 | 1 | IS4Inv1M2 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 Replacment & New one inverter installed | 6:08 | 6:08 | 6:08 | 10:50 | 0 | 0 | 4.7 | 4.7 | Inverter Replacment work done | Close | 0.15295 | 1.7782 | 1451.0011
73 | 2025-05-15 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:08 | 18:28 | 12.3333 | IS4 | Inv1 | M3 |  |  |  | 1 | 1 | IS4Inv1M3 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 Replacment & New one inverter installed | 6:08 | 6:08 | 6:08 | 11:06 | 0 | 0 | 4.9667 | 4.9667 | Inverter Replacment work done | Close | 0.16163 | 1.997 | 1629.612
74 | 2025-05-15 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:08 | 18:28 | 12.3333 | IS4 | Inv1 | M4 |  |  |  | 1 | 1 | IS4Inv1M4 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 Replacment & New one inverter installed | 6:08 | 6:08 | 6:08 | 11:20 | 0 | 0 | 5.2 | 5.2 | Inverter Replacment work done | Close | 0.16922 | 2.1839 | 1782.097
75 | 2025-05-15 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:08 | 18:28 | 12.3333 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | IDT |  | ICR-4 IDT Tripped Due to Over Current | 11:50 | 11:50 | 11:50 | 12:10 | 0 | 0 | 0.33333 | 0.33333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.04339 | 0.24315 | 793.6509
76 | 2025-05-15 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:08 | 18:28 | 12.3333 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | IDT |  | ICR-4 IDT Tripped Due to Over Current | 11:50 | 11:50 | 11:50 | 12:10 | 0 | 0 | 0.33333 | 0.33333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.04339 | 0.24315 | 793.6509
77 | 2025-05-16 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:08 | 18:23 | 12.25 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | IDT |  | ICR-4 IDT Tripped Due to Over Current | 11:52 | 11:52 | 11:52 | 12:07 | 0 | 0 | 0.25 | 0.25 | Check the Protection relay, fault reset & charge the breaker | Close | 0.032543 | 0.2647 | 863.991
78 | 2025-05-16 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:08 | 18:23 | 12.25 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | IDT |  | ICR-4 IDT Tripped Due to Over Current | 11:52 | 11:52 | 11:52 | 12:07 | 0 | 0 | 0.25 | 0.25 | Check the Protection relay, fault reset & charge the breaker | Close | 0.032543 | 0.2647 | 863.991
79 | 2025-05-16 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:08 | 18:23 | 12.25 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | IDT |  | ICR-4 IDT Tripped Due to Over Current | 12:28 | 12:28 | 12:28 | 12:49 | 0 | 0 | 0.35 | 0.35 | Check the Protection relay, fault reset & charge the breaker | Close | 0.04556 | 0.37037 | 1208.891
80 | 2025-05-16 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:08 | 18:23 | 12.25 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | IDT |  | ICR-4 IDT Tripped Due to Over Current | 12:28 | 12:28 | 12:28 | 12:49 | 0 | 0 | 0.35 | 0.35 | Check the Protection relay, fault reset & charge the breaker | Close | 0.04556 | 0.37037 | 1208.891
81 | 2025-05-16 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:08 | 18:23 | 12.25 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | Inverter |  | ICR-4 Inv-1 Inverter Shutdown taken due to Inverter Parameter Checking | 12:58 | 12:58 | 12:58 | 13:05 | 0 | 0 | 0.11667 | 0.11667 | Check the Parameter & Turn on the Inverter | Close | 0.015187 | 0.062933 | 205.4168
82 | 2025-05-16 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:08 | 18:23 | 12.25 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | Inverter |  | ICR-4 Inv-1 Inverter Shutdown taken due to Inverter Parameter Checking | 13:13 | 13:13 | 13:13 | 13:20 | 0 | 0 | 0.11667 | 0.11667 | Check the Parameter & Turn on the Inverter | Close | 0.015187 | 0.0581 | 189.6406
83 | 2025-05-16 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:08 | 18:23 | 12.25 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | Inverter |  | ICR-4 Inv-1 Inverter Shutdown taken due to Inverter Parameter Checking | 13:48 | 13:48 | 13:48 | 14:07 | 0 | 0 | 0.31667 | 0.31667 | Check the Parameter & Turn on the Inverter | Close | 0.041221 | 0.079683 | 260.0895
84 | 2025-05-17 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:20 | 17:49 | 11.4833 | IS4 | Inv1 | M1 | SCB1 | Str_Typ2(550*29) |  | 0 | 0 | Str_Typ2(550*29) | 15.95 | 0.04068% | String Fuses |  | String fuse blown | 6:20 | 6:20 | 6:20 | 16:20 | 0 | 0 | 10 | 10 | Fuse Replaced | Close | 0.0040678 | 5.0789 | 51.805
85 | 2025-05-18 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:07 | 18:24 | 12.2833 | IS4 | Inv1 | M2 |  |  |  | 1 | 1 | IS4Inv1M2 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-2 Inverter Shutdown taken due to Inverter Parameter Checking | 11:28 | 11:28 | 11:28 | 11:36 | 0 | 0 | 0.13333 | 0.13333 | Check the Parameter & Turn on the Inverter | Close | 0.004339 | 0.12086 | 98.6214
86 | 2025-05-18 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:07 | 18:24 | 12.2833 | IS4 | Inv1 | M3 |  |  |  | 1 | 1 | IS4Inv1M3 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-3 Inverter Shutdown taken due to Inverter Parameter Checking | 11:28 | 11:28 | 11:28 | 11:36 | 0 | 0 | 0.13333 | 0.13333 | Check the Parameter & Turn on the Inverter | Close | 0.004339 | 0.12086 | 98.6214
87 | 2025-05-18 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:07 | 18:24 | 12.2833 | IS4 | Inv1 | M4 |  |  |  | 1 | 1 | IS4Inv1M4 | 1276 | 3.254% | Inverter |  | ICR-4 Inv-1 MPPT-4 Inverter Shutdown taken due to Inverter Parameter Checking | 11:28 | 11:28 | 11:28 | 11:36 | 0 | 0 | 0.13333 | 0.13333 | Check the Parameter & Turn on the Inverter | Close | 0.004339 | 0.12086 | 98.6214
88 | 2025-05-19 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:06 | 18:25 | 12.3167 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | Inverter |  | ICR-4 Inv-1 Inverter Shutdown taken due to Inverter Parameter Checking | 12:02 | 12:02 | 12:02 | 12:08 | 0 | 0 | 0.1 | 0.1 | Check the Parameter & Turn on the Inverter | Close | 0.013017 | 0.10349 | 337.7964
89 | 2025-05-22 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:02 | 18:20 | 12.3 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | Inverter |  | ICR-1 Inv-1 Grid Voltage Abnormal | 7:55 | 7:55 | 7:55 | 8:11 | 0 | 0 | 0.26667 | 0.26667 | Reset the fault & charge the inverter | Close | 0.031709 | 0.093576 | 279.0137
90 | 2025-05-22 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:02 | 18:20 | 12.3 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | Inverter |  | ICR-1 Inv-1 PV Reverse-Current | 8:21 | 8:21 | 8:21 | 8:27 | 0 | 0 | 0.1 | 0.1 | Reset the fault & charge the inverter | Close | 0.011891 | 0.027882 | 83.1342
91 | 2025-05-22 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:02 | 18:20 | 12.3 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | Inverter |  | ICR-1 Inv-1 PV Reverse-Current | 12:27 | 12:27 | 12:27 | 12:35 | 0 | 0 | 0.13333 | 0.13333 | Reset the fault & charge the inverter | Close | 0.015855 | 0.10993 | 327.7652
92 | 2025-05-22 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:02 | 18:20 | 12.3 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | Inverter |  | ICR-1 Inv-1 PV Reverse-Current | 13:00 | 13:00 | 13:00 | 13:19 | 0 | 0 | 0.31667 | 0.31667 | Reset the fault & charge the inverter | Close | 0.037655 | 0.22344 | 666.2244
93 | 2025-05-22 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:02 | 18:20 | 12.3 | IS1 | Inv2 |  |  |  |  | 1 | 1 | IS1Inv2 | 4662.475 | 11.89% | Inverter |  | ICR-1 Inv-2 Grid Voltage Abnormal | 7:59 | 7:59 | 7:59 | 8:06 | 0 | 0 | 0.11667 | 0.11667 | Reset the fault & charge the inverter | Close | 0.013873 | 0.040205 | 119.8772
94 | 2025-05-23 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:08 | 17:13 | 11.0833 | IS4 | Inv1 | M1 | SCB2 | Str_Typ2(550*29) |  | 0 | 0 | Str_Typ2(550*29) | 15.95 | 0.04068% | String Fuses |  | String fuse blown | 6:08 | 6:08 | 6:08 | 16:10 | 0 | 0 | 10.0333 | 10.0333 | Fuse Replaced | Close | 0.0040814 | 3.6084 | 36.8058
95 | 2025-05-24 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:19 | 17:40 | 11.35 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | Inverter |  | ICR-1 Inv-1 Grid Voltage Abnormal | 7:54 | 7:54 | 7:54 | 8:27 | 0 | 0 | 0.55 | 0.55 | Reset the fault & charge the inverter | Close | 0.065401 | 0.078118 | 232.9225
96 | 2025-05-24 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:19 | 17:40 | 11.35 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | Inverter |  | ICR-1 Inv-1 Grid Voltage Abnormal | 8:51 | 8:51 | 8:51 | 9:07 | 0 | 0 | 0.26667 | 0.26667 | Reset the fault & charge the inverter | Close | 0.031709 | 0.071735 | 213.8898
97 | 2025-05-24 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:19 | 17:40 | 11.35 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | Inverter |  | ICR-1 Inv-1 Grid Voltage Abnormal | 9:51 | 9:51 | 9:51 | 10:06 | 0 | 0 | 0.25 | 0.25 | Reset the fault & charge the inverter | Close | 0.029728 | 0.11111 | 331.3031
98 | 2025-05-24 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:19 | 17:40 | 11.35 | IS1 | Inv2 |  |  |  |  | 1 | 1 | IS1Inv2 | 4662.475 | 11.89% | Inverter |  | ICR-1 Inv-2 Grid Voltage Abnormal | 10:00 | 10:00 | 10:00 | 10:07 | 0 | 0 | 0.11667 | 0.11667 | Reset the fault & charge the inverter | Close | 0.013873 | 0.058793 | 175.3026
99 | 2025-05-24 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:19 | 17:40 | 11.35 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | PTR |  | PTR Tripped dur to Under Voltage/Over Voltage | 13:03 | 13:03 | 13:03 | 13:39 | 0 | 0 | 0.6 | 0.6 | Reset the fault & charge the PTR | Close | 0.071346 | 0.37615 | 1121.5492
100 | 2025-05-24 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:19 | 17:40 | 11.35 | IS1 | Inv2 |  |  |  |  | 1 | 1 | IS1Inv2 | 4662.475 | 11.89% | PTR |  | PTR Tripped dur to Under Voltage/Over Voltage | 13:03 | 13:03 | 13:03 | 13:39 | 0 | 0 | 0.6 | 0.6 | Reset the fault & charge the PTR | Close | 0.071346 | 0.37615 | 1121.5492
101 | 2025-05-24 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:19 | 17:40 | 11.35 | IS2 | Inv1 |  |  |  |  | 1 | 1 | IS2Inv1 | 6511.66 | 16.61% | PTR |  | PTR Tripped dur to Under Voltage/Over Voltage | 13:03 | 13:03 | 13:03 | 13:52 | 0 | 0 | 0.81667 | 0.81667 | Reset the fault & charge the PTR | Close | 0.13562 | 0.42639 | 1775.5794
102 | 2025-05-24 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:19 | 17:40 | 11.35 | IS2 | Inv2 |  |  |  |  | 1 | 1 | IS2Inv2 | 6495.855 | 16.57% | PTR |  | PTR Tripped dur to Under Voltage/Over Voltage | 13:03 | 13:03 | 13:03 | 13:52 | 0 | 0 | 0.81667 | 0.81667 | Reset the fault & charge the PTR | Close | 0.1353 | 0.42639 | 1771.2697
103 | 2025-05-24 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:19 | 17:40 | 11.35 | IS3 | Inv1 |  |  |  |  | 1 | 1 | IS3Inv1 | 6527.465 | 16.65% | PTR |  | PTR Tripped dur to Under Voltage/Over Voltage | 13:03 | 13:03 | 13:03 | 13:49 | 0 | 0 | 0.76667 | 0.76667 | Reset the fault & charge the PTR | Close | 0.12763 | 0.41502 | 1732.4231
104 | 2025-05-24 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:19 | 17:40 | 11.35 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | PTR |  | PTR Tripped dur to Under Voltage/Over Voltage | 13:03 | 13:03 | 13:03 | 13:35 | 0 | 0 | 0.53333 | 0.53333 | Reset the fault & charge the PTR | Close | 0.069424 | 0.3582 | 1169.1687
105 | 2025-05-24 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:19 | 17:40 | 11.35 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | PTR |  | PTR Tripped dur to Under Voltage/Over Voltage | 13:03 | 13:03 | 13:03 | 13:35 | 0 | 0 | 0.53333 | 0.53333 | Reset the fault & charge the PTR | Close | 0.069424 | 0.3582 | 1169.1687
106 | 2025-05-25 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:04 | 18:14 | 12.1667 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | IDT |  | ICR-4 IDT Tripped Due to Over Current | 12:19 | 12:19 | 12:19 | 12:54 | 0 | 0 | 0.58333 | 0.58333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.075933 | 0.42488 | 1386.8221
107 | 2025-05-25 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:04 | 18:14 | 12.1667 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | IDT |  | ICR-4 IDT Tripped Due to Over Current | 12:19 | 12:19 | 12:19 | 12:54 | 0 | 0 | 0.58333 | 0.58333 | Check the Protection relay, fault reset & charge the breaker | Close | 0.075933 | 0.42488 | 1386.8221
108 | 2025-05-30 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:06 | 18:30 | 12.4 | IS4 | Inv1 | M2 | SCB2 | Str_Typ2(550*58) |  | 0 | 0 | Str_Typ2(550*58) | 31.9 | 0.08136% | Cables |  | String Cable Open | 6:06 | 6:06 | 6:06 | 16:05 | 0 | 0 | 9.9833 | 9.9833 | Connect the String Cable | Close | 0.0081221 | 3.1902 | 65.0807
109 | 2025-06-03 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:01 | 18:35 | 12.5667 | IS2 | Inv1 | M3 | SCB4 | Str_Typ2(550*58) |  | 0 | 0 | Str_Typ2(550*58) | 31.9 | 0.08136% | Cables |  | String Cable Open | 6:01 | 6:01 | 6:01 | 17:40 | 0 | 0 | 11.65 | 11.65 | Connect the String Cable | Close | 0.0094781 | 6.0188 | 147.1268
110 | 2025-06-05 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:15 | 18:30 | 12.25 | IS2 | Inv1 | M2 | SCB3 | Str_Typ2(550*29) |  | 0 | 0 | Str_Typ2(550*29) | 15.95 | 0.04068% | Cables |  | MC-4 Connector Open | 6:15 | 6:15 | 6:15 | 14:00 | 0 | 0 | 7.75 | 7.75 | Connect the MC-4 Connector | Close | 0.0031526 | 4.928 | 60.2318
111 | 2025-06-05 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:15 | 18:30 | 12.25 | IS2 | Inv1 | M2 | SCB3 | Str_Typ2(550*29) |  | 0 | 0 | Str_Typ2(550*29) | 15.95 | 0.04068% | Cables |  | MC-4 Connector Open | 6:15 | 6:15 | 6:15 | 14:00 | 0 | 0 | 7.75 | 7.75 | Connect the MC-4 Connector | Close | 0.0031526 | 4.928 | 60.2318
112 | 2025-06-09 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:02 | 18:11 | 12.15 | IS3 | Inv1 | M2 | SCB6 | Str_Typ2(550*58) |  | 0 | 0 | Str_Typ2(550*58) | 31.9 | 0.08136% | Cables |  | Y-Connector Damage | 8:00 | 8:00 | 8:00 | 16:29 | 0 | 0 | 8.4833 | 8.4833 | Y-connector replaced | Close | 0.0069018 | 5.55 | 135.6682
113 | 2025-06-12 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:06 | 18:27 | 12.35 | IS1 | Inv2 | M1 | SCB4 | Str_Typ1(545*58) |  | 0 | 0 | Str_Typ1(545*58) | 31.61 | 0.08062% | Cables |  | Y-Connector open | 7:00 | 7:00 | 7:00 | 16:19 | 0 | 0 | 9.3167 | 9.3167 | Y-Connector Connected | Close | 0.0075108 | 3.39 | 82.1142 |  |  | 4218 | JOB_622
114 | 2025-06-13 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:06 | 18:25 | 12.3167 | IS4 | Inv1 | M3 | SCB5 | Str_Typ2(550*58) |  | 0 | 0 | Str_Typ2(550*58) | 31.9 | 0.08136% | Cables |  | Y-Connector open & MC-4 Connector damage | 8:00 | 8:00 | 8:00 | 15:50 | 0 | 0 | 7.8333 | 7.8333 | Replace the MC-4 Connector | Close | 0.0063729 | 3.98 | 97.29 |  |  | 4250 | JOB_623
115 | 2025-06-13 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:06 | 18:25 | 12.3167 | IS4 | Inv1 | M3 | SCB5 | Str_Typ2(550*58) |  | 0 | 0 | Str_Typ2(550*58) | 31.9 | 0.08136% | Cables |  | Y-Connector open & MC-4 Connector damage | 8:00 | 8:00 | 8:00 | 15:50 | 0 | 0 | 7.8333 | 7.8333 | Replace the MC-4 Connector | Close | 0.0063729 | 3.98 | 97.29 |  |  | 4250 | JOB_623
116 | 2025-06-26 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:47 | 18:19 | 11.5333 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | PTR |  | PTR Tripped due to HV REF fault & MCR Incomer-1 Panel flashover Due low clearance between the panel body and B-phase VDI | 6:47 | 6:47 | 6:47 | 8:22 | 0 | 0 | 1.5833 | 1.5833 | Panel busbar Position has been checked and adjusted post-flashover reseted the fault & charge the trafo | Close | 0.18827 | 0.074766 | 267.1252 |  |  | 4533
117 | 2025-06-26 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:47 | 18:19 | 11.5333 | IS1 | Inv2 |  |  |  |  | 1 | 1 | IS1Inv2 | 4662.475 | 11.89% | PTR |  | PTR Tripped due to HV REF fault & MCR Incomer-1 Panel flashover Due low clearance between the panel body and B-phase VDI | 6:47 | 6:47 | 6:47 | 8:22 | 0 | 0 | 1.5833 | 1.5833 | Panel busbar Position has been checked and adjusted post-flashover reseted the fault & charge the trafo | Close | 0.18827 | 0.074766 | 267.1252 |  |  | 4533
118 | 2025-06-26 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:47 | 18:19 | 11.5333 | IS2 | Inv1 |  |  |  |  | 1 | 1 | IS2Inv1 | 6511.66 | 16.61% | PTR |  | PTR Tripped due to HV REF fault & MCR Incomer-1 Panel flashover Due low clearance between the panel body and B-phase VDI | 6:47 | 6:47 | 6:47 | 8:22 | 0 | 0 | 1.5833 | 1.5833 | Panel busbar Position has been checked and adjusted post-flashover reseted the fault & charge the trafo | Close | 0.26295 | 0.074766 | 373.0698 |  |  | 4533
119 | 2025-06-26 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:47 | 18:19 | 11.5333 | IS2 | Inv2 |  |  |  |  | 1 | 1 | IS2Inv2 | 6495.855 | 16.57% | PTR |  | PTR Tripped due to HV REF fault & MCR Incomer-1 Panel flashover Due low clearance between the panel body and B-phase VDI | 6:47 | 6:47 | 6:47 | 8:22 | 0 | 0 | 1.5833 | 1.5833 | Panel busbar Position has been checked and adjusted post-flashover reseted the fault & charge the trafo | Close | 0.26231 | 0.074766 | 372.1643 |  |  | 4533
120 | 2025-06-26 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:47 | 18:19 | 11.5333 | IS3 | Inv1 |  |  |  |  | 1 | 1 | IS3Inv1 | 6527.465 | 16.65% | PTR |  | PTR Tripped due to HV REF fault & MCR Incomer-1 Panel flashover Due low clearance between the panel body and B-phase VDI | 6:47 | 6:47 | 6:47 | 13:18 | 0 | 0 | 6.5167 | 6.5167 | Panel busbar Position has been checked and adjusted post-flashover reseted the fault & charge the trafo & Inverter turned on late due to heavy rain. | Close | 1.0849 | 0.45841 | 2292.9161 |  |  | 4533
121 | 2025-06-26 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:47 | 18:19 | 11.5333 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | PTR |  | PTR Tripped due to HV REF fault & MCR Incomer-1 Panel flashover Due low clearance between the panel body and B-phase VDI | 6:47 | 6:47 | 6:47 | 13:08 | 0 | 0 | 6.35 | 6.35 | Panel busbar Position has been checked and adjusted post-flashover reseted the fault & charge the trafo & Inverter turned on late due to heavy rain. | Close | 0.82659 | 0.44956 | 1758.3102 |  |  | 4533
122 | 2025-06-26 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:47 | 18:19 | 11.5333 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | PTR |  | PTR Tripped due to HV REF fault & MCR Incomer-1 Panel flashover Due low clearance between the panel body and B-phase VDI | 6:47 | 6:47 | 6:47 | 8:11 | 0 | 0 | 1.4 | 1.4 | Panel busbar Position has been checked and adjusted post-flashover reseted the fault & charge the trafo | Close | 0.18224 | 0.062624 | 244.9321 |  |  | 4533
123 | 2025-06-26 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:47 | 18:19 | 11.5333 | IS3 | Inv1 |  |  |  |  | 1 | 1 | IS3Inv1 | 6527.465 | 16.65% | Inverter |  | ICR-3 Inv-1 tripped Due to M-1-2 square matrix insulation rasistance abnormal | 14:23 | 14:23 | 14:23 | 14:46 | 0 | 0 | 0.38333 | 0.38333 | Reset the fault & charge the inverter | Close | 0.063815 | 0.04324 | 216.2841
124 | 2025-06-28 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:21 | 18:20 | 11.9833 | IS3 | Inv1 | M3 | SCB6 | Str_Typ2(550*58) |  | 0 | 0 | Str_Typ2(550*58) | 31.9 | 0.08136% | Cables |  | 6 Sq mm Positive & Negative string cable ground fault | 6:21 | 6:21 | 6:21 | 15:40 | 0 | 0 | 9.3167 | 9.3167 | Replaced 40 mtr Posi & 40 mtr. Neg 6 sq mm string cable & Male & Female MC-4 Connector | Close | 0.0075797 | 4.247 | 103.8167 |  |  | 4585 | JOB_671
125 | 2025-06-29 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:36 | 18:01 | 11.4167 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 12:01 | 12:01 | 12:01 | 13:57 | 0 | 0 | 1.9333 | 1.9333 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.22989 | 0.37617 | 1343.9789 |  |  | 4611
126 | 2025-06-29 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:36 | 18:01 | 11.4167 | IS1 | Inv2 |  |  |  |  | 1 | 1 | IS1Inv2 | 4662.475 | 11.89% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 12:01 | 12:01 | 12:01 | 13:57 | 0 | 0 | 1.9333 | 1.9333 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.22989 | 0.37617 | 1343.9789 |  |  | 4611
127 | 2025-06-29 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:36 | 18:01 | 11.4167 | IS2 | Inv1 |  |  |  |  | 1 | 1 | IS2Inv1 | 6511.66 | 16.61% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 12:01 | 12:01 | 12:01 | 14:04 | 0 | 0 | 2.05 | 2.05 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.34045 | 0.39957 | 1993.78 |  |  | 4611
128 | 2025-06-29 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:36 | 18:01 | 11.4167 | IS2 | Inv2 |  |  |  |  | 1 | 1 | IS2Inv2 | 6495.855 | 16.57% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 12:01 | 12:01 | 12:01 | 14:04 | 0 | 0 | 2.05 | 2.05 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.33962 | 0.39957 | 1988.9408 |  |  | 4611
129 | 2025-06-29 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:36 | 18:01 | 11.4167 | IS3 | Inv1 |  |  |  |  | 1 | 1 | IS3Inv1 | 6527.465 | 16.65% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 12:01 | 12:01 | 12:01 | 14:01 | 0 | 0 | 2 | 2 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.33295 | 0.38944 | 1947.937 |  |  | 4611
130 | 2025-06-29 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:36 | 18:01 | 11.4167 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 12:01 | 12:01 | 12:01 | 13:49 | 0 | 0 | 1.8 | 1.8 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.23431 | 0.34862 | 1363.5063 |  |  | 4611
131 | 2025-06-29 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:36 | 18:01 | 11.4167 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 12:01 | 12:01 | 12:01 | 13:49 | 0 | 0 | 1.8 | 1.8 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.23431 | 0.34862 | 1363.5063 |  |  | 4611
132 | 2025-06-29 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:36 | 18:01 | 11.4167 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:10 | 14:10 | 14:10 | 16:18 | 0 | 0 | 2.1333 | 2.1333 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.25368 | 0.31531 | 1126.5305 |  |  | 4610
133 | 2025-06-29 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:36 | 18:01 | 11.4167 | IS1 | Inv2 |  |  |  |  | 1 | 1 | IS1Inv2 | 4662.475 | 11.89% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:10 | 14:10 | 14:10 | 16:18 | 0 | 0 | 2.1333 | 2.1333 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.25368 | 0.31531 | 1126.5305 |  |  | 4610
134 | 2025-06-29 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:36 | 18:01 | 11.4167 | IS2 | Inv1 |  |  |  |  | 1 | 1 | IS2Inv1 | 6511.66 | 16.61% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:10 | 14:10 | 14:10 | 16:09 | 0 | 0 | 1.9833 | 1.9833 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.32937 | 0.30112 | 1502.5574 |  |  | 4610
135 | 2025-06-29 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:36 | 18:01 | 11.4167 | IS2 | Inv2 |  |  |  |  | 1 | 1 | IS2Inv2 | 6495.855 | 16.57% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:10 | 14:10 | 14:10 | 16:09 | 0 | 0 | 1.9833 | 1.9833 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.32858 | 0.30112 | 1498.9104 |  |  | 4610
136 | 2025-06-29 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:36 | 18:01 | 11.4167 | IS3 | Inv1 |  |  |  |  | 1 | 1 | IS3Inv1 | 6527.465 | 16.65% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:10 | 14:10 | 14:10 | 16:15 | 0 | 0 | 2.0833 | 2.0833 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.34682 | 0.31083 | 1554.7544 |  |  | 4610
137 | 2025-06-29 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:36 | 18:01 | 11.4167 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:10 | 14:10 | 14:10 | 16:04 | 0 | 0 | 1.9 | 1.9 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.24732 | 0.29204 | 1142.1975 |  |  | 4610
138 | 2025-06-29 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:36 | 18:01 | 11.4167 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:10 | 14:10 | 14:10 | 16:04 | 0 | 0 | 1.9 | 1.9 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.24732 | 0.29204 | 1142.1975 |  |  | 4610
139 | 2025-07-01 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:20 | 18:08 | 11.8 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 0.54028 | 0.54028 | 0.54028 | 14:29 | 0 | 0 | 1.5167 | 1.5167 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.18035 | 0.23712 | 914.3195 |  |  | 4657
140 | 2025-07-01 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:20 | 18:08 | 11.8 | IS1 | Inv2 |  |  |  |  | 1 | 1 | IS1Inv2 | 4662.475 | 11.89% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 0.54028 | 0.54028 | 0.54028 | 14:29 | 0 | 0 | 1.5167 | 1.5167 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.18035 | 0.23712 | 914.3195 |  |  | 4657
141 | 2025-07-01 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:20 | 18:08 | 11.8 | IS2 | Inv1 |  |  |  |  | 1 | 1 | IS2Inv1 | 6511.66 | 16.61% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 0.54028 | 0.54028 | 0.54028 | 14:32 | 0 | 0 | 1.5667 | 1.5667 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.26018 | 0.24 | 1292.4921 |  |  | 4657
142 | 2025-07-01 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:20 | 18:08 | 11.8 | IS2 | Inv2 |  |  |  |  | 1 | 1 | IS2Inv2 | 6495.855 | 16.57% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 0.54028 | 0.54028 | 0.54028 | 14:32 | 0 | 0 | 1.5667 | 1.5667 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.25955 | 0.24 | 1289.355 |  |  | 4657
143 | 2025-07-01 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:20 | 18:08 | 11.8 | IS3 | Inv1 |  |  |  |  | 1 | 1 | IS3Inv1 | 6527.465 | 16.65% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 0.54028 | 0.54028 | 0.54028 | 14:28 | 0 | 0 | 1.5 | 1.5 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.24971 | 0.23398 | 1263.0882 |  |  | 4657
144 | 2025-07-01 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:20 | 18:08 | 11.8 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 0.54028 | 0.54028 | 0.54028 | 14:22 | 0 | 0 | 1.4 | 1.4 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.18224 | 0.21787 | 919.6671 |  |  | 4657
145 | 2025-07-01 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:20 | 18:08 | 11.8 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 0.54028 | 0.54028 | 0.54028 | 14:54 | 0 | 0 | 1.9333 | 1.9333 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.25166 | 0.32362 | 1366.0394 |  |  | 4657
146 | 2025-07-01 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:20 | 18:08 | 11.8 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 15:02 | 15:02 | 15:02 | 15:29 | 0 | 0 | 0.45 | 0.45 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.05351 | 0.084871 | 327.2595 |  |  | 4657
147 | 2025-07-01 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:20 | 18:08 | 11.8 | IS1 | Inv2 |  |  |  |  | 1 | 1 | IS1Inv2 | 4662.475 | 11.89% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 15:02 | 15:02 | 15:02 | 15:29 | 0 | 0 | 0.45 | 0.45 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.05351 | 0.084871 | 327.2595 |  |  | 4657
148 | 2025-07-01 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:20 | 18:08 | 11.8 | IS2 | Inv1 |  |  |  |  | 1 | 1 | IS2Inv1 | 6511.66 | 16.61% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 15:02 | 15:02 | 15:02 | 15:28 | 0 | 0 | 0.43333 | 0.43333 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.071964 | 0.081273 | 437.6806 |  |  | 4657
149 | 2025-07-01 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:20 | 18:08 | 11.8 | IS2 | Inv2 |  |  |  |  | 1 | 1 | IS2Inv2 | 6495.855 | 16.57% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 15:02 | 15:02 | 15:02 | 15:28 | 0 | 0 | 0.43333 | 0.43333 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.07179 | 0.081273 | 436.6183 |  |  | 4657
150 | 2025-07-01 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:20 | 18:08 | 11.8 | IS3 | Inv1 |  |  |  |  | 1 | 1 | IS3Inv1 | 6527.465 | 16.65% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 15:02 | 15:02 | 15:02 | 15:25 | 0 | 0 | 0.38333 | 0.38333 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.063815 | 0.070936 | 382.9376 |  |  | 4657
151 | 2025-07-01 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:20 | 18:08 | 11.8 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 15:02 | 15:02 | 15:02 | 15:23 | 0 | 0 | 0.35 | 0.35 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.04556 | 0.065985 | 278.5291 |  |  | 4657
152 | 2025-07-01 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:20 | 18:08 | 11.8 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 15:02 | 15:02 | 15:02 | 15:26 | 0 | 0 | 0.4 | 0.4 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.052068 | 0.073909 | 311.9787 |  |  | 4657
153 | 2025-07-02 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:07 | 17:34 | 11.45 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:01 | 14:01 | 14:01 | 14:33 | 0 | 0 | 0.53333 | 0.53333 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.063419 | 0.13823 | 533.0048 |  |  | 4674
154 | 2025-07-02 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:07 | 17:34 | 11.45 | IS1 | Inv2 |  |  |  |  | 1 | 1 | IS1Inv2 | 4662.475 | 11.89% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:01 | 14:01 | 14:01 | 14:33 | 0 | 0 | 0.53333 | 0.53333 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.063419 | 0.13823 | 533.0048 |  |  | 4674
155 | 2025-07-02 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:07 | 17:34 | 11.45 | IS2 | Inv1 |  |  |  |  | 1 | 1 | IS2Inv1 | 6511.66 | 16.61% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:01 | 14:01 | 14:01 | 16:01 | 0 | 0 | 2 | 2 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.33214 | 0.22273 | 1199.477 |  |  | 4674
156 | 2025-07-02 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:07 | 17:34 | 11.45 | IS2 | Inv2 |  |  |  |  | 1 | 1 | IS2Inv2 | 6495.855 | 16.57% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:01 | 14:01 | 14:01 | 16:01 | 0 | 0 | 2 | 2 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.33134 | 0.22273 | 1196.5656 |  |  | 4674
157 | 2025-07-02 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:07 | 17:34 | 11.45 | IS3 | Inv1 |  |  |  |  | 1 | 1 | IS3Inv1 | 6527.465 | 16.65% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:01 | 14:01 | 14:01 | 14:28 | 0 | 0 | 0.45 | 0.45 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.074914 | 0.12925 | 697.7424 |  |  | 4674
158 | 2025-07-02 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:07 | 17:34 | 11.45 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:01 | 14:01 | 14:01 | 14:28 | 0 | 0 | 0.45 | 0.45 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.058577 | 0.12925 | 545.5835 |  |  | 4674
159 | 2025-07-02 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:07 | 17:34 | 11.45 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:01 | 14:01 | 14:01 | 14:31 | 0 | 0 | 0.5 | 0.5 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.065085 | 0.13481 | 569.0373 |  |  | 4674
160 | 2025-07-02 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:07 | 17:34 | 11.45 | IS3 | Inv1 |  |  |  |  | 1 | 1 | IS3Inv1 | 6527.465 | 16.65% | IDT |  | O/G Panel Tripped due to ICR-2 VCB Breaker Checking | 15:24 | 15:24 | 15:24 | 15:55 | 0 | 0 | 0.51667 | 0.51667 | Check the ICR-2 breaker & charge the O/G breaker panel | Close | 0.086012 | 0.018623 | 100.5317 |  |  | 4674
161 | 2025-07-03 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:11 | 18:31 | 12.3333 | IS4 | Inv2 | M1 | SCB4 | Str_Typ2(550*58) |  | 0 | 0 | Str_Typ2(550*58) | 31.9 | 0.08136% | Cables |  | String Cable Open | 6:11 | 6:11 | 6:11 | 16:00 | 0 | 0 | 9.8167 | 9.8167 | Connect the String Cable | Close | 0.0079865 | 3.6445 | 96.1502 |  |  | 4703 | JOB_684
162 | 2025-07-06 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:33 | 17:58 | 11.4167 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:00 | 14:00 | 14:00 | 14:40 | 0 | 0 | 0.66667 | 0.66667 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.079274 | 0.25966 | 1001.2293 |  |  | 4774 | JOB_704
163 | 2025-07-06 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:33 | 17:58 | 11.4167 | IS1 | Inv2 |  |  |  |  | 1 | 1 | IS1Inv2 | 4662.475 | 11.89% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:00 | 14:00 | 14:00 | 14:40 | 0 | 0 | 0.66667 | 0.66667 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.079274 | 0.25966 | 1001.2293 |  |  | 4774 | JOB_705
164 | 2025-07-06 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:33 | 17:58 | 11.4167 | IS2 | Inv1 |  |  |  |  | 1 | 1 | IS2Inv1 | 6511.66 | 16.61% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:00 | 14:00 | 14:00 | 14:32 | 0 | 0 | 0.53333 | 0.53333 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.088571 | 0.24567 | 1322.9884 |  |  | 4774 | JOB_706
165 | 2025-07-06 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:33 | 17:58 | 11.4167 | IS2 | Inv2 |  |  |  |  | 1 | 1 | IS2Inv2 | 6495.855 | 16.57% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:00 | 14:00 | 14:00 | 15:21 | 0 | 0 | 1.35 | 1.35 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.22365 | 0.24517 | 1317.118 |  |  | 4774 | JOB_707
166 | 2025-07-06 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:33 | 17:58 | 11.4167 | IS3 | Inv1 |  |  |  |  | 1 | 1 | IS3Inv1 | 6527.465 | 16.65% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:00 | 14:00 | 14:00 | 15:13 | 0 | 0 | 1.2167 | 1.2167 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.20254 | 0.30487 | 1645.7826 |  |  | 4774 | JOB_708
167 | 2025-07-06 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:33 | 17:58 | 11.4167 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:00 | 14:00 | 14:00 | 14:38 | 0 | 0 | 0.63333 | 0.63333 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.082442 | 0.32971 | 1391.7343 |  |  | 4774 | JOB_709
168 | 2025-07-06 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:33 | 17:58 | 11.4167 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:00 | 14:00 | 14:00 | 15:03 | 0 | 0 | 1.05 | 1.05 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.13668 | 0.3257 | 1374.816 |  |  | 4774 | JOB_710
169 | 2025-07-08 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:26 | 18:05 | 11.65 | IS4 | Inv2 | M4 | SCB6 | Str_Typ2(550*58) |  | 0 | 0 | Str_Typ2(550*58) | 31.9 | 0.08136% | Cables |  | Y-Connector open | 6:26 | 6:26 | 6:26 | 16:10 | 0 | 0 | 9.7333 | 9.7333 | Y-Connector Connected | Close | 0.0079187 | 1.6 | 42.2112 |  |  | 4829 | JOB_717
170 | 2025-07-10 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 7:46 | 18:22 | 10.6 | IS1 | Inv1 |  |  |  |  | 1 | 1 | IS1Inv1 | 4662.475 | 11.89% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:33 | 14:33 | 14:33 | 15:15 | 0 | 0 | 0.7 | 0.7 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.083237 | 0.18509 | 713.6894 |  |  | 4876 | JOB_733
171 | 2025-07-10 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 7:46 | 18:22 | 10.6 | IS1 | Inv2 |  |  |  |  | 1 | 1 | IS1Inv2 | 4662.475 | 11.89% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:33 | 14:33 | 14:33 | 15:14 | 0 | 0 | 0.68333 | 0.68333 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.081255 | 0.18089 | 697.5116 |  |  | 4876 | JOB_733
172 | 2025-07-10 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 7:46 | 18:22 | 10.6 | IS2 | Inv1 |  |  |  |  | 1 | 1 | IS2Inv1 | 6511.66 | 16.61% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:33 | 14:33 | 14:33 | 15:11 | 0 | 0 | 0.63333 | 0.63333 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.10518 | 0.16827 | 906.1665 |  |  | 4876 | JOB_733
173 | 2025-07-10 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 7:46 | 18:22 | 10.6 | IS2 | Inv2 |  |  |  |  | 1 | 1 | IS2Inv2 | 6495.855 | 16.57% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:33 | 14:33 | 14:33 | 15:12 | 0 | 0 | 0.65 | 0.65 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.10768 | 0.17247 | 926.5617 |  |  | 4876 | JOB_733
174 | 2025-07-10 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 7:46 | 18:22 | 10.6 | IS3 | Inv1 |  |  |  |  | 1 | 1 | IS3Inv1 | 6527.465 | 16.65% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:33 | 14:33 | 14:33 | 15:11 | 0 | 0 | 0.63333 | 0.63333 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.10543 | 0.16827 | 908.3659 |  |  | 4876 | JOB_733
175 | 2025-07-10 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 7:46 | 18:22 | 10.6 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 5104 | 13.02% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:33 | 14:33 | 14:33 | 15:10 | 0 | 0 | 0.61667 | 0.61667 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.080272 | 0.16406 | 692.5272 |  |  | 4876 | JOB_733
176 | 2025-07-10 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 7:46 | 18:22 | 10.6 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 5104 | 13.02% | PTR |  | PTR Tripped Due To Over voltage/Under Voltage Protection | 14:33 | 14:33 | 14:33 | 15:10 | 0 | 0 | 0.61667 | 0.61667 | Inspection the trafo, checking the relay setting, fault reset & charge the breaker | Close | 0.080272 | 0.16406 | 692.5272 |  |  | 4876 | JOB_733
177 | 2025-07-12 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:01 | 18:38 | 12.6167 | IS4 | INV1 |  |  |  |  | 1 | 1 | IS4INV1 | 5104 | 13.02% | IDT |  | IDT Tripped Due To Over current /LS fault | 13:11 | 13:11 | 13:11 | 13:50 | 0 | 0 | 0.65 | 0.65 | Check the Protection relay, fault reset & charge the breaker | Close | 0.084611 | 0.50745 | 2142.0085 |  |  | 4932 | JOB_746
178 | 2025-07-12 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 6:01 | 18:38 | 12.6167 | IS4 | INV2 |  |  |  |  | 1 | 1 | IS4INV2 | 5104 | 13.02% | IDT |  | IDT Tripped Due To Over current /LS fault | 13:11 | 13:11 | 13:11 | 13:50 | 0 | 0 | 0.65 | 0.65 | Check the Protection relay, fault reset & charge the breaker | Close | 0.084611 | 0.50745 | 2142.0085 |  |  | 4932 | JOB_746
179 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
180 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
181 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
182 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
183 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
184 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
185 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
186 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
187 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
188 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
189 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
190 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
191 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
192 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
193 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
194 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
195 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
196 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
197 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
198 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
199 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
200 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
201 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
202 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
203 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
204 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
205 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
206 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
207 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
208 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
209 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
210 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
211 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
212 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
213 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
214 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
215 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
216 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
217 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
218 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
219 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
220 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
221 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
222 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
223 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
224 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
225 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
226 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
227 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
228 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
229 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
230 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
231 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
232 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
233 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
234 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
235 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
236 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
237 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
238 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
239 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
240 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
241 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
242 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
243 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
244 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
245 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
246 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
247 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
248 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
249 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
250 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
251 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
252 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
253 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
254 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
255 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
256 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
257 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
258 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
259 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
260 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
261 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
262 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
263 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
264 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
265 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
266 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
267 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
268 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
269 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
270 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
271 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
272 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
273 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
274 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
275 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
276 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
277 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
278 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
279 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
280 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
281 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
282 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
283 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
284 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
285 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
286 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
287 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
288 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
289 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
290 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
291 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
292 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
293 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
294 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
295 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
296 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
297 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
298 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
299 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
300 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
301 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
302 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
303 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
304 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
305 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
306 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
307 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
308 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
309 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
310 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
311 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
312 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
313 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
314 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
315 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
316 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
317 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
318 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
319 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
320 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
321 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
322 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
323 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
324 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
325 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
326 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
327 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
328 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
329 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
330 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
331 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
332 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
333 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
334 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
335 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
336 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
337 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
338 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
339 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
340 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
341 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
342 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
343 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
344 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
345 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
346 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
347 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
348 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
349 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
350 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
351 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
352 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
353 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
354 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
355 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
356 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
357 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
358 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
359 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
360 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
361 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
362 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
363 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
364 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
365 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
366 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
367 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
368 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
369 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
370 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
371 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
372 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
373 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
374 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
375 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
376 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
377 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
378 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
379 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
380 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
381 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
382 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
383 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
384 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
385 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
386 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
387 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
388 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
389 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
390 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
391 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
392 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
393 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
394 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
395 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
396 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
397 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
398 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
399 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
400 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
401 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
402 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
403 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
404 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
405 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
406 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
407 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
408 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
409 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
410 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
411 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
412 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
413 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
414 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
415 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
416 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
417 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
418 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
419 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
420 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
421 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
422 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
423 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
424 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
425 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
426 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
427 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
428 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
429 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
430 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
431 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
432 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
433 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
434 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
435 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
436 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
437 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
438 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
439 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
440 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
441 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
442 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
443 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
444 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
445 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
446 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
447 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
448 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
449 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
450 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
451 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
452 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
453 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
454 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
455 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
456 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
457 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
458 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
459 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
460 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
461 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
462 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
463 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
464 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
465 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
466 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
467 |  | 1900 | 1900 | Year_2 | Year_2 | 1899-12-31 | 31 |  |  | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0
Formulas:
Month Year = PA[[#This Row],[Date]]-DAY(PA[[#This Row],[Date]])+1
Days = DAY(EOMONTH(PA[[#This Row],[Month Year]],0))

## Grid_BD
Sr. No. | Date | Finacial Year | Calendor Year | Operating Year | Affected Feeder | Op. Hours | Concumaer | Plant Equivalent Weightage | Breakdown Description | Breakdown Type | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | POA Lost (kWh/m2) | Estimated Energy Loss (kWh) | Curtailment Order imit. | EGA_Including_CurtailmentOrder | PTW No. | Job Card No.
1 | 2025-02-01 | 2025 | 2025 | Year_1 | [9 empty] | 0 | 0 | 0 |  |  |  | 0 |  |  | 100%
2 | 2025-02-02 | 2025 | 2025 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
3 | 2025-06-01 | 2026 | 2025 | Year_1 |  | 12.5833 |  |  | Shutdown taken from 220 kv Grid side |  | 0.43056 | 0.43056 | 0.62153 | 0 | 4.5833 | 4.5833 | Charged the line after work completion |  | PTR | 3.886 | 116759.3663 |  | 100%
4 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
5 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
6 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
7 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
8 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
9 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
10 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
11 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
12 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
13 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
14 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
15 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
16 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
17 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
18 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
19 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
20 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
21 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
22 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
23 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
24 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
25 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
26 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
27 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
28 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
29 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
30 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
31 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
32 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
b

## Curtailment Records
Sr. No | Month | Date | Plant Name | Categoty | Equipment Name | Inverter No. | From | To | Duration in MIN | Total Breakdown Hrs. | Avg POA During BD time | Lost POA | Total POA | Net POA | Loss of Capacity in KWp | Estimated PR % (Pvsyst) | Loss of Generation kWh | Remark | Current Load befor Load Sheeding (AC MW) | Load to be maintain (AC Mw)
1 | 1899-12-31 |  | Ghatodi | [5 empty] | 0:00 | 0:00 |  |  |  | 0
2 | 1899-12-31 | [7 empty] | 0:00 | 0:00 |  |  |  | 0
3 | 1899-12-31 | [7 empty] | 0:00 | 0:00 |  |  |  | 0
4 | 1899-12-31 | [7 empty] | 0:00 | 0:00 |  |  |  | 0
5 | 1899-12-31 | [7 empty] | 0:00 | 0:00 |  |  |  | 0
Formulas:
Month = Table7[[#This Row],[Date]]-DAY(Table7[[#This Row],[Date]])+1

## Inv_SY_B
DC Capacity | 4650.15 | 4662.475 | 6555.45 | 6571.4 | 6571.4 | 5097.91 | 5104
| 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
Date | IS1Inv1 | IS1Inv2 | IS2Inv1 | IS2Inv2 | IS3Inv1 | IS4Inv1 | IS4Inv2 | Avg_SY
2025-05-15 | 4.1106 | 4.1194 | 4.0081 | 4.0608 | 4.0995 | 2.4 | 3.9571 | 3.8222
2025-05-16 | 4.5381 | 4.5519 | 4.3901 | 4.4391 | 4.4744 | 3.9082 | 4.1314 | 4.3476
2025-05-17 | 4.4549 | 4.436 | 4.3018 | 4.3346 | 4.3521 | 4.5163 | 4.4549 | 4.4072
2025-05-18 | 4.7458 | 4.7916 | 4.6534 | 4.7545 | 4.8316 | 4.5612 | 4.8381 | 4.7395
2025-05-19 | 4.5085 | 4.5501 | 4.38 | 4.4784 | 4.5942 | 4.4707 | 4.635 | 4.5167
2025-05-20 | 4.1751 | 4.1966 | 4.1142 | 4.1952 | 4.2244 | 4.2357 | 4.228 | 4.1956
2025-05-21 | 3.8587 | 3.9044 | 3.8614 | 3.9207 | 3.9337 | 3.9176 | 3.8942 | 3.8987
2025-05-22 | 2.5932 | 2.9084 | 2.9089 | 2.9867 | 3.0544 | 3.0442 | 3.0399 | 2.9337
2025-05-23 | 3.2099 | 3.2629 | 3.2117 | 3.2861 | 3.3362 | 3.3031 | 3.3015 | 3.273
2025-05-24 | 2.2991 | 2.4767 | 2.4616 | 2.5034 | 2.5366 | 2.6343 | 2.6369 | 2.5069
2025-05-25 | 4.1963 | 4.1736 | 4.0789 | 4.0826 | 4.1495 | 3.8931 | 3.8403 | 4.0592
2025-05-26 | 4.7093 | 4.7126 | 4.5595 | 4.6303 | 4.6832 | 4.8933 | 4.8937 | 4.726
2025-05-27 | 3.3278 | 3.308 | 3.2128 | 3.2254 | 3.2523 | 3.3638 | 3.347 | 3.291
2025-05-28 | 2.5381 | 2.568 | 2.508 | 2.5539 | 2.5737 | 2.5792 | 2.5947 | 2.5594
2025-05-29 | 4.6815 | 4.7229 | 4.6198 | 4.6839 | 4.7588 | 4.7578 | 4.7729 | 4.714
2025-05-30 | 3.1208 | 3.1347 | 3.1059 | 3.149 | 3.1736 | 3.1298 | 3.1501 | 3.1377
2025-05-31 | 5.5895 | 5.5867 | 5.4097 | 5.4421 | 5.4953 | 5.8692 | 5.8389 | 5.6045
2025-06-01 | 2.4408 | 2.4418 | 2.3895 | 2.4281 | 2.458 | 2.4519 | 2.4083 | 2.4312
2025-06-02 | 5.08 | 5.0755 | 4.9542 | 4.9915 | 5.1123 | 5.2526 | 5.2373 | 5.1005
2025-06-03 | 5.0855 | 5.0875 | 4.9436 | 4.9888 | 5.0346 | 5.2974 | 5.2706 | 5.1011
2025-06-04 | 5.2006 | 5.1912 | 5.0786 | 5.1166 | 5.1411 | 5.3509 | 5.3468 | 5.2037
2025-06-05 | 4.3617 | 4.3215 | 4.2083 | 4.2295 | 4.2153 | 4.4813 | 4.4138 | 4.3188
2025-06-06 | 5.6439 | 5.5947 | 5.4605 | 5.486 | 5.4395 | 5.6208 | 5.5831 | 5.5469
2025-06-07 | 4.4188 | 4.4011 | 4.306 | 4.3379 | 4.3522 | 4.5272 | 4.4933 | 4.4052
2025-06-08 | 4.8317 | 4.8674 | 4.7636 | 4.8359 | 4.8829 | 4.9333 | 4.9259 | 4.8629
2025-06-09 | 5.2558 | 5.2775 | 5.1429 | 5.1722 | 5.1817 | 5.3888 | 5.3276 | 5.2495
2025-06-10 | 4.2299 | 4.2119 | 4.1444 | 4.1661 | 4.1768 | 4.2783 | 4.242 | 4.2071
2025-06-11 | 3.9381 | 3.9324 | 3.885 | 3.9176 | 3.9501 | 3.9586 | 3.9278 | 3.93
2025-06-12 | 3.0077 | 3.0221 | 2.9288 | 2.9695 | 3.0389 | 3.1311 | 3.1258 | 3.032
2025-06-13 | 4.0919 | 4.0652 | 4.0741 | 4.0987 | 4.1376 | 4.09 | 4.1353 | 4.099
2025-06-14 | 5.0748 | 5.0025 | 4.9074 | 4.9047 | 4.8777 | 5.1717 | 5.0855 | 5.0035
2025-06-15 | 4.1353 | 4.2024 | 4.0625 | 4.1496 | 4.3624 | 4.4131 | 4.3947 | 4.2457
2025-06-16 | 3.1472 | 3.1706 | 3.1094 | 3.1445 | 3.1533 | 3.2204 | 3.1798 | 3.1607
2025-06-17 | 5.3858 | 5.4216 | 5.2218 | 5.261 | 5.3538 | 5.6437 | 5.5803 | 5.4097
2025-06-18 | 3.6639 | 3.6604 | 3.6359 | 3.6675 | 3.7171 | 3.7131 | 3.7065 | 3.6806
2025-06-19 | 3.3265 | 3.3331 | 3.2411 | 3.2595 | 3.312 | 3.428 | 3.4071 | 3.3296
2025-06-20 | 5.1351 | 5.1497 | 5.0388 | 5.0503 | 5.1531 | 5.3662 | 5.3418 | 5.1764
2025-06-21 | 4.1201 | 4.1356 | 4.0098 | 4.037 | 4.1069 | 4.2992 | 4.2759 | 4.1406
2025-06-22 | 3.8531 | 3.8365 | 3.7409 | 3.7609 | 3.7772 | 3.938 | 3.9066 | 3.8305
2025-06-23 | 2.6436 | 2.663 | 2.612 | 2.6428 | 2.6454 | 2.6858 | 2.6776 | 2.6529
2025-06-24 | 3.6039 | 3.6143 | 3.5138 | 3.5379 | 3.5535 | 3.6875 | 3.6493 | 3.5943
2025-06-25 | 2.7116 | 2.732 | 2.6948 | 2.729 | 2.7309 | 2.7541 | 2.7407 | 2.7276
2025-06-26 | 0.82901 | 0.84215 | 0.82037 | 0.83678 | 0.25584 | 0.48306 | 0.85384 | 0.70301
2025-06-27 | 3.77 | 3.7898 | 3.6675 | 3.7571 | 3.6679 | 3.797 | 3.7864 | 3.748
2025-06-28 | 4.1766 | 4.1877 | 4.0689 | 4.114 | 4.1512 | 4.3133 | 4.288 | 4.1857
2025-06-29 | 0.73047 | 0.73274 | 0.68285 | 0.68737 | 0.69891 | 0.76733 | 0.74279 | 0.72035
2025-06-30 | 1.648 | 1.6559 | 1.6357 | 1.6528 | 1.6513 | 1.6685 | 1.646 | 1.6512
2025-07-01 | 1.3637 | 1.3784 | 1.345 | 1.3635 | 1.3898 | 1.4271 | 1.2984 | 1.3665
2025-07-02 | 2.5896 | 2.5968 | 2.4635 | 2.4875 | 2.5745 | 2.6208 | 2.5835 | 2.5595
2025-07-03 | 3.6953 | 3.6958 | 3.6203 | 3.6435 | 3.6507 | 3.7333 | 3.6633 | 3.6717
2025-07-04 | 2.5457 | 2.5644 | 2.5248 | 2.5551 | 2.5758 | 2.5739 | 2.5416 | 2.5545
2025-07-05 | 2.761 | 2.772 | 2.7379 | 2.7566 | 2.7492 | 2.7735 | 2.7213 | 2.7531
2025-07-06 | 1.9723 | 1.9817 | 1.9612 | 1.893 | 1.9064 | 1.9775 | 1.9111 | 1.9433
2025-07-07 | 1.4498 | 1.4641 | 1.4298 | 1.4461 | 1.4509 | 1.4699 | 1.4513 | 1.4517
2025-07-08 | 1.6759 | 1.6941 | 1.6741 | 1.6958 | 1.704 | 1.7108 | 1.6894 | 1.692
2025-07-09 | 1.4287 | 1.4405 | 1.4174 | 1.4321 | 1.4328 | 1.4464 | 1.4381 | 1.4337
2025-07-10 | 1.481 | 1.492 | 1.4778 | 1.4908 | 1.492 | 1.5149 | 1.5025 | 1.493
2025-07-11 | 4.9248 | 4.9482 | 4.8341 | 4.8661 | 4.9325 | 5.0543 | 5.0227 | 4.9404
2025-07-12 | 4.9401 | 4.9502 | 4.8162 | 4.8408 | 4.934 | 4.8035 | 4.7492 | 4.862
2025-07-13 | 3.8579 | 3.8823 | 3.8255 | 3.8471 | 3.856 | 3.9041 | 3.8706 | 3.8634
2025-07-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
Formulas:
Date = [Date, row above]+1

## Inv_SY_D
Date | IS1Inv1 | IS1Inv2 | IS2Inv1 | IS2Inv2 | IS3Inv1 | IS4Inv1 | IS4Inv2
2025-05-15 | 7.544% | 7.775% | 4.865% | 6.242% | 7.255% | -37.21% | 3.529%
2025-05-16 | 4.382% | 4.698% | 0.9783% | 2.105% | 2.917% | -10.11% | -4.974%
2025-05-17 | 1.081% | 0.6532% | -2.391% | -1.648% | -1.251% | 2.476% | 1.081%
2025-05-18 | 0.1336% | 1.1% | -1.815% | 0.3174% | 1.943% | -3.761% | 2.082%
2025-05-19 | -0.1808% | 0.7392% | -3.027% | -0.8475% | 1.715% | -1.017% | 2.618%
2025-05-20 | -0.4879% | 0.02349% | -1.939% | -0.009652% | 0.686% | 0.9551% | 0.7721%
2025-05-21 | -1.027% | 0.1476% | -0.9559% | 0.5648% | 0.8989% | 0.486% | -0.1148%
2025-05-22 | -11.6% | -0.8617% | -0.844% | 1.808% | 4.114% | 3.767% | 3.621%
2025-05-23 | -1.93% | -0.3111% | -1.875% | 0.3995% | 1.928% | 0.9195% | 0.8685%
2025-05-24 | -8.29% | -1.206% | -1.807% | -0.1414% | 1.181% | 5.08% | 5.183%
2025-05-25 | 3.377% | 2.819% | 0.486% | 0.5769% | 2.225% | -4.092% | -5.391%
2025-05-26 | -0.3529% | -0.2827% | -3.523% | -2.024% | -0.9055% | 3.54% | 3.548%
2025-05-27 | 1.119% | 0.5163% | -2.377% | -1.993% | -1.175% | 2.211% | 1.7%
2025-05-28 | -0.8315% | 0.3377% | -2.007% | -0.2155% | 0.561% | 0.773% | 1.382%
2025-05-29 | -0.6888% | 0.1893% | -1.997% | -0.6368% | 0.9514% | 0.9308% | 1.251%
2025-05-30 | -0.5383% | -0.09444% | -1.014% | 0.3597% | 1.144% | -0.2518% | 0.3941%
2025-05-31 | -0.2673% | -0.317% | -3.476% | -2.898% | -1.949% | 4.724% | 4.183%
2025-06-01 | 0.3954% | 0.4361% | -1.715% | -0.1299% | 1.103% | 0.8529% | -0.9429%
2025-06-02 | -0.4018% | -0.4893% | -2.869% | -2.136% | 0.2315% | 2.982% | 2.683%
2025-06-03 | -0.3068% | -0.2676% | -3.089% | -2.201% | -1.305% | 3.847% | 3.323%
2025-06-04 | -0.05904% | -0.2396% | -2.405% | -1.673% | -1.202% | 2.829% | 2.75%
2025-06-05 | 0.9946% | 0.06267% | -2.558% | -2.066% | -2.397% | 3.764% | 2.2%
2025-06-06 | 1.748% | 0.8615% | -1.559% | -1.098% | -1.937% | 1.331% | 0.6524%
2025-06-07 | 0.3091% | -0.09387% | -2.253% | -1.527% | -1.204% | 2.769% | 1.999%
2025-06-08 | -0.6434% | 0.09068% | -2.043% | -0.5562% | 0.4105% | 1.447% | 1.294%
2025-06-09 | 0.1201% | 0.5324% | -2.032% | -1.472% | -1.291% | 2.654% | 1.488%
2025-06-10 | 0.5436% | 0.1157% | -1.489% | -0.974% | -0.7204% | 1.694% | 0.8302%
2025-06-11 | 0.2069% | 0.06095% | -1.144% | -0.3134% | 0.5137% | 0.7299% | -0.05437%
2025-06-12 | -0.802% | -0.325% | -3.404% | -2.059% | 0.2285% | 3.268% | 3.093%
2025-06-13 | -0.172% | -0.8231% | -0.6072% | -0.007519% | 0.9421% | -0.2199% | 0.8876%
2025-06-14 | 1.426% | -0.02062% | -1.921% | -1.973% | -2.513% | 3.363% | 1.639%
2025-06-15 | -2.601% | -1.019% | -4.316% | -2.263% | 2.748% | 3.942% | 3.51%
2025-06-16 | -0.4286% | 0.3125% | -1.626% | -0.5125% | -0.2366% | 1.889% | 0.602%
2025-06-17 | -0.4413% | 0.2201% | -3.473% | -2.75% | -1.033% | 4.325% | 3.152%
2025-06-18 | -0.4559% | -0.5494% | -1.215% | -0.3566% | 0.9912% | 0.8833% | 0.7028%
2025-06-19 | -0.09265% | 0.1058% | -2.659% | -2.105% | -0.5296% | 2.953% | 2.327%
2025-06-20 | -0.7982% | -0.5156% | -2.659% | -2.436% | -0.4514% | 3.666% | 3.194%
2025-06-21 | -0.4964% | -0.1223% | -3.16% | -2.502% | -0.815% | 3.83% | 3.266%
2025-06-22 | 0.5917% | 0.1584% | -2.337% | -1.816% | -1.391% | 2.807% | 1.986%
2025-06-23 | -0.35% | 0.3802% | -1.54% | -0.3806% | -0.282% | 1.24% | 0.9321%
2025-06-24 | 0.2667% | 0.556% | -2.241% | -1.569% | -1.135% | 2.592% | 1.53%
2025-06-25 | -0.5846% | 0.1606% | -1.2% | 0.0518% | 0.1204% | 0.9712% | 0.4808%
2025-06-26 | 17.92% | 19.79% | 16.69% | 19.03% | -63.61% | -31.29% | 21.46%
2025-06-27 | 0.5877% | 1.117% | -2.147% | 0.2431% | -2.135% | 1.31% | 1.025%
2025-06-28 | -0.2156% | 0.0484% | -2.791% | -1.711% | -0.8245% | 3.048% | 2.445%
2025-06-29 | 1.405% | 1.72% | -5.206% | -4.578% | -2.977% | 6.522% | 3.115%
2025-06-30 | -0.1909% | 0.2843% | -0.9389% | 0.09715% | 0.01051% | 1.053% | -0.3149%
2025-07-01 | -0.2093% | 0.8673% | -1.577% | -0.2234% | 1.703% | 4.429% | -4.989%
2025-07-02 | 1.177% | 1.458% | -3.749% | -2.81% | 0.5886% | 2.398% | 0.9381%
2025-07-03 | 0.6409% | 0.6559% | -1.402% | -0.7684% | -0.5732% | 1.676% | -0.2299%
2025-07-04 | -0.343% | 0.3885% | -1.162% | 0.02294% | 0.8361% | 0.7614% | -0.5039%
2025-07-05 | 0.2863% | 0.6888% | -0.5502% | 0.1287% | -0.1416% | 0.7412% | -1.153%
2025-07-06 | 1.494% | 1.976% | 0.9182% | -2.591% | -1.898% | 1.76% | -1.658%
2025-07-07 | -0.131% | 0.8504% | -1.508% | -0.383% | -0.05486% | 1.256% | -0.02972%
2025-07-08 | -0.9536% | 0.1245% | -1.061% | 0.2256% | 0.7104% | 1.109% | -0.1546%
2025-07-09 | -0.3497% | 0.4729% | -1.136% | -0.112% | -0.06638% | 0.8827% | 0.3087%
2025-07-10 | -0.8029% | -0.06818% | -1.018% | -0.1474% | -0.0689% | 1.47% | 0.6359%
2025-07-11 | -0.3157% | 0.1589% | -2.152% | -1.504% | -0.1593% | 2.306% | 1.666%
2025-07-12 | 1.607% | 1.815% | -0.9425% | -0.4367% | 1.481% | -1.202% | -2.32%
2025-07-13 | -0.1405% | 0.4894% | -0.9797% | -0.4204% | -0.19% | 1.054% | 0.187%
2025-07-14
Formulas:
Date = [Date, row above]+1

## Inv_PR
DC Capacity | 4662.475 | 4662.475 | 6511.66 | 6495.855 | 6527.465 | 5104 | 5104
| 8 | 9 | 10 | 11 | 12 | 13 | 14
Date | IS1Inv1 | IS1Inv2 | IS2Inv1 | IS2Inv2 | IS3Inv1 | IS4Inv1 | IS4Inv2
2025-05-15 | 85.95% | 86.36% | 84.59% | 86.12% | 86.52% | 50.25% | 82.96%
2025-05-16 | 83.97% | 84.45% | 82% | 83.32% | 83.57% | 72.42% | 76.65%
2025-05-17 | 83.2% | 83.07% | 81.1% | 82.12% | 82.05% | 84.47% | 83.42%
2025-05-18 | 81.33% | 82.33% | 80.49% | 82.64% | 83.58% | 78.28% | 83.13%
2025-05-19 | 84.68% | 85.69% | 83.04% | 85.32% | 87.1% | 84.09% | 87.29%
2025-05-20 | 84.81% | 85.47% | 84.36% | 86.44% | 86.62% | 86.16% | 86.11%
2025-05-21 | 88.27% | 89.55% | 89.16% | 90.97% | 90.83% | 89.75% | 89.32%
2025-05-22 | 77.9% | 87.6% | 88.21% | 91.01% | 92.62% | 91.58% | 91.56%
2025-05-23 | 87.23% | 88.91% | 88.1% | 90.58% | 91.52% | 89.9% | 89.96%
2025-05-24 | 68.86% | 74.38% | 74.42% | 76.05% | 76.69% | 79.01% | 79.19%
2025-05-25 | 82.71% | 82.48% | 81.15% | 81.62% | 82.56% | 76.85% | 75.9%
2025-05-26 | 84.17% | 84.46% | 82.26% | 83.95% | 84.49% | 87.59% | 87.7%
2025-05-27 | 89.46% | 89.16% | 87.18% | 87.95% | 88.25% | 90.56% | 90.21%
2025-05-28 | 90.73% | 92.04% | 90.5% | 92.6% | 92.87% | 92.33% | 93%
2025-05-29 | 86.79% | 87.79% | 86.45% | 88.07% | 89.05% | 88.33% | 88.72%
2025-05-30 | 92.42% | 93.07% | 92.84% | 94.58% | 94.86% | 92.82% | 93.53%
2025-05-31 | 83.08% | 83.26% | 81.16% | 82.05% | 82.45% | 87.37% | 87.02%
2025-06-01 | 37% | 37.11% | 36.56% | 37.33% | 37.61% | 37.22% | 36.6%
2025-06-02 | 83.06% | 83.21% | 81.76% | 82.78% | 84.37% | 86% | 85.86%
2025-06-03 | 83.42% | 83.68% | 81.86% | 83.01% | 83.36% | 87.02% | 86.69%
2025-06-04 | 82.07% | 82.14% | 80.9% | 81.9% | 81.89% | 84.57% | 84.6%
2025-06-05 | 82.86% | 82.31% | 80.7% | 81.5% | 80.83% | 85.26% | 84.07%
2025-06-06 | 83.15% | 82.64% | 81.2% | 81.98% | 80.89% | 82.93% | 82.47%
2025-06-07 | 84.27% | 84.15% | 82.89% | 83.91% | 83.78% | 86.46% | 85.91%
2025-06-08 | 85.29% | 86.15% | 84.88% | 86.59% | 87% | 87.21% | 87.18%
2025-06-09 | 84.41% | 84.98% | 83.37% | 84.26% | 84% | 86.67% | 85.79%
2025-06-10 | 88.63% | 88.49% | 87.65% | 88.54% | 88.34% | 89.77% | 89.12%
2025-06-11 | 86.7% | 86.81% | 86.34% | 87.49% | 87.79% | 87.28% | 86.71%
2025-06-12 | 85.71% | 86.35% | 84.24% | 85.83% | 87.41% | 89.35% | 89.31%
2025-06-13 | 84.49% | 84.17% | 84.92% | 85.85% | 86.24% | 84.58% | 85.62%
2025-06-14 | 84.36% | 83.37% | 82.34% | 82.7% | 81.84% | 86.09% | 84.76%
2025-06-15 | 79.16% | 80.66% | 78.5% | 80.57% | 84.29% | 84.6% | 84.35%
2025-06-16 | 86.47% | 87.34% | 86.23% | 87.63% | 87.45% | 88.61% | 87.6%
2025-06-17 | 84.19% | 84.98% | 82.4% | 83.42% | 84.48% | 88.35% | 87.46%
2025-06-18 | 86.8% | 86.95% | 86.94% | 88.13% | 88.89% | 88.09% | 88.04%
2025-06-19 | 84.85% | 85.25% | 83.45% | 84.33% | 85.28% | 87.57% | 87.14%
2025-06-20 | 83.55% | 84.01% | 82.75% | 83.35% | 84.63% | 87.44% | 87.14%
2025-06-21 | 84.73% | 85.27% | 83.23% | 84.21% | 85.25% | 88.54% | 88.16%
2025-06-22 | 87.34% | 87.19% | 85.59% | 86.47% | 86.42% | 89.39% | 88.79%
2025-06-23 | 91.87% | 92.79% | 91.62% | 93.15% | 92.8% | 93.47% | 93.3%
2025-06-24 | 87.41% | 87.9% | 86.03% | 87.04% | 87% | 89.57% | 88.75%
2025-06-25 | 96.93% | 97.92% | 97.24% | 98.95% | 98.54% | 98.59% | 98.23%
2025-06-26 | 87.15% | 88.77% | 87.05% | 89.23% | 27.15% | 50.86% | 90%
2025-06-27 | 89.95% | 90.67% | 88.33% | 90.93% | 88.34% | 90.73% | 90.58%
2025-06-28 | 87.72% | 88.18% | 86.25% | 87.64% | 88% | 90.72% | 90.29%
2025-06-29 | 52.04% | 52.34% | 49.1% | 49.67% | 50.26% | 54.74% | 53.06%
2025-06-30 | 95.56% | 96.27% | 95.74% | 97.21% | 96.65% | 96.89% | 95.7%
2025-07-01 | 77.85% | 78.9% | 77.51% | 78.95% | 80.09% | 81.59% | 74.32%
2025-07-02 | 88.18% | 88.66% | 84.67% | 85.92% | 88.49% | 89.37% | 88.2%
2025-07-03 | 94.02% | 94.28% | 92.98% | 94.03% | 93.76% | 95.12% | 93.45%
2025-07-04 | 93.69% | 94.63% | 93.79% | 95.38% | 95.69% | 94.87% | 93.79%
2025-07-05 | 93.34% | 93.97% | 93.44% | 94.53% | 93.82% | 93.9% | 92.25%
2025-07-06 | 95.49% | 96.2% | 95.84% | 92.96% | 93.17% | 95.88% | 92.77%
2025-07-07 | 104% | 105.3% | 103.6% | 105.2% | 105.1% | 105.6% | 104.4%
2025-07-08 | 97.18% | 98.5% | 97.98% | 99.74% | 99.74% | 99.35% | 98.22%
2025-07-09 | 98.27% | 99.34% | 98.41% | 99.92% | 99.48% | 99.63% | 99.18%
2025-07-10 | 88.98% | 89.88% | 89.62% | 90.85% | 90.48% | 91.15% | 90.51%
2025-07-11 | 88.04% | 88.69% | 87.23% | 88.24% | 89.01% | 90.49% | 90.03%
2025-07-12 | 83.09% | 83.48% | 81.76% | 82.58% | 83.76% | 80.91% | 80.09%
2025-07-13 | 89.89% | 90.7% | 89.97% | 90.92% | 90.69% | 91.1% | 90.42%
2025-07-14
Formulas:
Date = [Date, row above]+1

## MC
Sr. No. | Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Cycle Number | Resources | ICR1 | ICR2 | ICR3 | ICR4 | ICR10 | ICR11 | ICR12 | Total NO. Module cleaned | Morning Start Time | Morning End Time | Evening Start Time | Evening End time | Brush/MOP Replcemnet | Water Test Report | Remarks for the day
1 | 2025-02-01 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
2 | 2025-02-02 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
3 | 2025-02-03 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
4 | 2025-02-04 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
5 | 2025-02-05 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
6 | 2025-02-06 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
7 | 2025-02-07 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
8 | 2025-02-08 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
9 | 2025-02-09 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
10 | 2025-02-10 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
11 | 2025-02-11 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
12 | 2025-02-12 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
13 | 2025-02-13 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
14 | 2025-02-14 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
15 | 2025-02-15 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
16 | 2025-02-16 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
17 | 2025-02-17 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
18 | 2025-02-18 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
19 | 2025-02-19 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
20 | 2025-02-20 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
21 | 2025-02-21 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
22 | 2025-02-22 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
23 | 2025-02-23 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
24 | 2025-02-24 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
25 | 2025-02-25 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
26 | 2025-02-26 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
27 | 2025-02-27 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
28 | 2025-02-28 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [9 empty] | 0
29 | 2025-03-01 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
30 | 2025-03-02 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
31 | 2025-03-03 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
32 | 2025-03-04 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
33 | 2025-03-05 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
34 | 2025-03-06 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
35 | 2025-03-07 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
36 | 2025-03-08 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
37 | 2025-03-09 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
38 | 2025-03-10 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
39 | 2025-03-11 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
40 | 2025-03-12 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
41 | 2025-03-13 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
42 | 2025-03-14 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
43 | 2025-03-15 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
44 | 2025-03-16 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
45 | 2025-03-17 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
46 | 2025-03-18 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
47 | 2025-03-19 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
48 | 2025-03-20 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
49 | 2025-03-21 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
50 | 2025-03-22 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
51 | 2025-03-23 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
52 | 2025-03-24 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
53 | 2025-03-25 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
54 | 2025-03-26 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
55 | 2025-03-27 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
56 | 2025-03-28 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
57 | 2025-03-29 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
58 | 2025-03-30 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
59 | 2025-03-31 | 2025 | 2025 | Year_1 | Year_1 | Mar-25 | 31 | [9 empty] | 0
60 | 2025-04-01 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
61 | 2025-04-02 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
62 | 2025-04-03 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
63 | 2025-04-04 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
64 | 2025-04-05 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
65 | 2025-04-06 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
66 | 2025-04-07 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
67 | 2025-04-08 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
68 | 2025-04-09 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
69 | 2025-04-10 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
70 | 2025-04-11 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
71 | 2025-04-12 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
72 | 2025-04-13 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
73 | 2025-04-14 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
74 | 2025-04-15 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
75 | 2025-04-16 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
76 | 2025-04-17 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
77 | 2025-04-18 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
78 | 2025-04-19 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
79 | 2025-04-20 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
80 | 2025-04-21 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
81 | 2025-04-22 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
82 | 2025-04-23 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
83 | 2025-04-24 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
84 | 2025-04-25 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
85 | 2025-04-26 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
86 | 2025-04-27 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
87 | 2025-04-28 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
88 | 2025-04-29 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
89 | 2025-04-30 | 2026 | 2025 | Year_1 | Year_1 | Apr-25 | 30 | [9 empty] | 0
90 | 2025-05-01 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
91 | 2025-05-02 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
92 | 2025-05-03 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
93 | 2025-05-04 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
94 | 2025-05-05 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
95 | 2025-05-06 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
96 | 2025-05-07 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
97 | 2025-05-08 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
98 | 2025-05-09 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
99 | 2025-05-10 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
100 | 2025-05-11 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
101 | 2025-05-12 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
102 | 2025-05-13 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
103 | 2025-05-14 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
104 | 2025-05-15 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
105 | 2025-05-16 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
106 | 2025-05-17 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
107 | 2025-05-18 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
108 | 2025-05-19 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
109 | 2025-05-20 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
110 | 2025-05-21 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
111 | 2025-05-22 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
112 | 2025-05-23 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
113 | 2025-05-24 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
114 | 2025-05-25 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
115 | 2025-05-26 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
116 | 2025-05-27 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
117 | 2025-05-28 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
118 | 2025-05-29 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
119 | 2025-05-30 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
120 | 2025-05-31 | 2026 | 2025 | Year_1 | Year_1 | May-25 | 31 | [9 empty] | 0
120 | 2025-06-01 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
122 | 2025-06-02 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
123 | 2025-06-03 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
124 | 2025-06-04 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
125 | 2025-06-05 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
126 | 2025-06-06 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
127 | 2025-06-07 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
127 | 2025-06-08 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
127 | 2025-06-09 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
127 | 2025-06-10 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
127 | 2025-06-11 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
127 | 2025-06-12 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
127 | 2025-06-13 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
127 | 2025-06-14 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
127 | 2025-06-15 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
127 | 2025-06-16 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
127 | 2025-06-17 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
127 | 2025-06-18 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
139 | 2025-06-19 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
140 | 2025-06-20 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
141 | 2025-06-21 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
142 | 2025-06-22 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
143 | 2025-06-23 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
144 | 2025-06-24 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
145 | 2025-06-25 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
146 | 2025-06-26 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
147 | 2025-06-27 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
148 | 2025-06-28 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
149 | 2025-06-29 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
150 | 2025-06-30 | 2026 | 2025 | Year_1 | Year_1 | Jun-25 | 30 | [9 empty] | 0
151 | 2025-07-01 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
152 | 2025-07-02 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
153 | 2025-07-03 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
154 | 2025-07-04 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
155 | 2025-07-05 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
156 | 2025-07-06 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
157 | 2025-07-07 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
158 | 2025-07-08 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
159 | 2025-07-09 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
160 | 2025-07-10 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
161 | 2025-07-11 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
162 | 2025-07-12 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
163 | 2025-07-13 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
164 | 2025-07-14 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
165 | 2025-07-15 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
166 | 2025-07-16 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
167 | 2025-07-17 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
168 | 2025-07-18 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
169 | 2025-07-19 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
170 | 2025-07-20 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
171 | 2025-07-21 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
172 | 2025-07-22 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
173 | 2025-07-23 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
174 | 2025-07-24 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
175 | 2025-07-25 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
176 | 2025-07-26 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
177 | 2025-07-27 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
177 | 2025-07-28 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
179 | 2025-07-29 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
180 | 2025-07-30 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
181 | 2025-07-31 | 2026 | 2025 | Year_1 | Year_1 | Jul-25 | 31 | [9 empty] | 0
182 | 2025-08-01 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
183 | 2025-08-02 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
184 | 2025-08-03 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
185 | 2025-08-04 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
186 | 2025-08-05 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
187 | 2025-08-06 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
188 | 2025-08-07 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
189 | 2025-08-08 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
190 | 2025-08-09 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
191 | 2025-08-10 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
192 | 2025-08-11 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
193 | 2025-08-12 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
194 | 2025-08-13 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
195 | 2025-08-14 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
196 | 2025-08-15 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
197 | 2025-08-16 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
198 | 2025-08-17 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
199 | 2025-08-18 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
200 | 2025-08-19 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
201 | 2025-08-20 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
202 | 2025-08-21 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
203 | 2025-08-22 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
204 | 2025-08-23 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
205 | 2025-08-24 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
206 | 2025-08-25 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
207 | 2025-08-26 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
208 | 2025-08-27 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
209 | 2025-08-28 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
210 | 2025-08-29 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
211 | 2025-08-30 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
212 | 2025-08-31 | 2026 | 2025 | Year_1 | Year_1 | Aug-25 | 31 | [9 empty] | 0
213 | 2025-09-01 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
214 | 2025-09-02 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
215 | 2025-09-03 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
216 | 2025-09-04 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
217 | 2025-09-05 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
218 | 2025-09-06 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
219 | 2025-09-07 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
220 | 2025-09-08 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
221 | 2025-09-09 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
222 | 2025-09-10 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
223 | 2025-09-11 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
224 | 2025-09-12 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
225 | 2025-09-13 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
226 | 2025-09-14 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
227 | 2025-09-15 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
228 | 2025-09-16 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
229 | 2025-09-17 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
230 | 2025-09-18 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
231 | 2025-09-19 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
232 | 2025-09-20 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
233 | 2025-09-21 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
234 | 2025-09-22 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
235 | 2025-09-23 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
236 | 2025-09-24 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
237 | 2025-09-25 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
238 | 2025-09-26 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
239 | 2025-09-27 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
240 | 2025-09-28 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
241 | 2025-09-29 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
242 | 2025-09-30 | 2026 | 2025 | Year_1 | Year_1 | Sep-25 | 30 | [9 empty] | 0
243 | 2025-10-01 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
244 | 2025-10-02 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
245 | 2025-10-03 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
246 | 2025-10-04 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
247 | 2025-10-05 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
248 | 2025-10-06 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
249 | 2025-10-07 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
250 | 2025-10-08 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
251 | 2025-10-09 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
252 | 2025-10-10 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
253 | 2025-10-11 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
254 | 2025-10-12 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
255 | 2025-10-13 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
256 | 2025-10-14 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
257 | 2025-10-15 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
258 | 2025-10-16 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
259 | 2025-10-17 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
260 | 2025-10-18 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
261 | 2025-10-19 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
262 | 2025-10-20 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
263 | 2025-10-21 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
264 | 2025-10-22 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
265 | 2025-10-23 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
266 | 2025-10-24 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
267 | 2025-10-25 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
268 | 2025-10-26 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
269 | 2025-10-27 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
270 | 2025-10-28 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
271 | 2025-10-29 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
272 | 2025-10-30 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
273 | 2025-10-31 | 2026 | 2025 | Year_1 | Year_1 | Oct-25 | 31 | [9 empty] | 0
274 | 2025-11-01 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
275 | 2025-11-02 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
276 | 2025-11-03 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
277 | 2025-11-04 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
278 | 2025-11-05 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
279 | 2025-11-06 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
280 | 2025-11-07 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
281 | 2025-11-08 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
282 | 2025-11-09 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
283 | 2025-11-10 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
284 | 2025-11-11 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
285 | 2025-11-12 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
286 | 2025-11-13 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
287 | 2025-11-14 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
288 | 2025-11-15 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
289 | 2025-11-16 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
290 | 2025-11-17 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
291 | 2025-11-18 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
292 | 2025-11-19 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
293 | 2025-11-20 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
294 | 2025-11-21 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
295 | 2025-11-22 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
296 | 2025-11-23 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
297 | 2025-11-24 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
298 | 2025-11-25 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
299 | 2025-11-26 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
300 | 2025-11-27 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
301 | 2025-11-28 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
302 | 2025-11-29 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
303 | 2025-11-30 | 2026 | 2025 | Year_1 | Year_1 | Nov-25 | 30 | [9 empty] | 0
304 | 2025-12-01 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
305 | 2025-12-02 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
306 | 2025-12-03 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
307 | 2025-12-04 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
308 | 2025-12-05 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
309 | 2025-12-06 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
310 | 2025-12-07 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
311 | 2025-12-08 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
312 | 2025-12-09 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
313 | 2025-12-10 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
314 | 2025-12-11 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
315 | 2025-12-12 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
316 | 2025-12-13 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
317 | 2025-12-14 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
318 | 2025-12-15 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
319 | 2025-12-16 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
320 | 2025-12-17 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
321 | 2025-12-18 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
322 | 2025-12-19 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
323 | 2025-12-20 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
324 | 2025-12-21 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
325 | 2025-12-22 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
326 | 2025-12-23 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
327 | 2025-12-24 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
328 | 2025-12-25 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
329 | 2025-12-26 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
330 | 2025-12-27 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
331 | 2025-12-28 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
332 | 2025-12-29 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
333 | 2025-12-30 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
334 | 2025-12-31 | 2026 | 2025 | Year_1 | Year_1 | Dec-25 | 31 | [9 empty] | 0
335 | 2026-01-01 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
336 | 2026-01-02 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
337 | 2026-01-03 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
338 | 2026-01-04 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
339 | 2026-01-05 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
340 | 2026-01-06 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
341 | 2026-01-07 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
342 | 2026-01-08 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
343 | 2026-01-09 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
344 | 2026-01-10 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
345 | 2026-01-11 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
346 | 2026-01-12 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
347 | 2026-01-13 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
348 | 2026-01-14 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
349 | 2026-01-15 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
350 | 2026-01-16 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
351 | 2026-01-17 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
352 | 2026-01-18 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
353 | 2026-01-19 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
354 | 2026-01-20 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
355 | 2026-01-21 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
356 | 2026-01-22 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
357 | 2026-01-23 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
358 | 2026-01-24 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
359 | 2026-01-25 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
360 | 2026-01-26 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
361 | 2026-01-27 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
362 | 2026-01-28 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
363 | 2026-01-29 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
364 | 2026-01-30 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
365 | 2026-01-31 | 2026 | 2026 | Year_1 | Year_1 | Jan-26 | 31 | [9 empty] | 0
366 | 2026-02-01 | 2026 | 2026 | Year_1 | Year_1 | Feb-26 | 28 | [9 empty] | 0
367 | 2026-02-02 | 2026 | 2026 | Year_1 | Year_1 | Feb-26 | 28 | [9 empty] | 0
368 | 2026-02-03 | 2026 | 2026 | Year_1 | Year_1 | Feb-26 | 28 | [9 empty] | 0
369 | 2026-02-04 | 2026 | 2026 | Year_1 | Year_1 | Feb-26 | 28 | [9 empty] | 0
370 | 2026-02-05 | 2026 | 2026 | Year_1 | Year_1 | Feb-26 | 28 | [9 empty] | 0
371 | 2026-02-06 | 2026 | 2026 | Year_1 | Year_1 | Feb-26 | 28 | [9 empty] | 0
372 | 2026-02-07 | 2026 | 2026 | Year_1 | Year_1 | Feb-26 | 28 | [9 empty] | 0
373 | 2026-02-08 | 2026 | 2026 | Year_1 | Year_1 | Feb-26 | 28 | [9 empty] | 0
374 | 2026-02-09 | 2026 | 2026 | Year_1 | Year_1 | Feb-26 | 28 | [9 empty] | 0
375 | 2026-02-10 | 2026 | 2026 | Year_1 | Year_1 | Feb-26 | 28 | [9 empty] | 0
376 | 2026-02-11 | 2026 | 2026 | Year_1 | Year_1 | Feb-26 | 28 | [9 empty] | 0
377 | 2026-02-12 | 2026 | 2026 | Year_1 | Year_1 | Feb-26 | 28 | [9 empty] | 0
378 | 2026-02-13 | 2026 | 2026 | Year_1 | Year_1 | Feb-26 | 28 | [9 empty] | 0
379 | 2026-02-14 | 2026 | 2026 | Year_1 | Year_1 | Feb-26 | 28 | [9 empty] | 0
Formulas:
Days = DAY(EOMONTH(MC[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## Wet MC
Sr. No. | Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Cycle Number | Resources | ICR1 | ICR2 | ICR3 | ICR4 | ICR5 | ICR6 | ICR7 | ICR8 | Total NO. Module cleaned | Morning Start Time | Morning End Time | Evening Start Time | Evening End time | Brush/MOP Replcemnet | Water Test Report | Remarks for the day
1 | 2025-02-01 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 522; ICR2: 0; ICR3: 0; ICR4: 0
2 | 2025-02-02 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 1044; ICR2: 0; ICR3: 0; ICR4: 0
3 | 2025-02-03 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 1450; ICR2: 0; ICR3: 0; ICR4: 0
4 | 2025-02-04 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 1392; ICR2: 0; ICR3: 0; ICR4: 0
5 | 2025-02-05 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 1450; ICR2: 0; ICR3: 0; ICR4: 0
6 | 2025-02-06 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 1102; ICR2: 0; ICR3: 0; ICR4: 0
7 | 2025-02-07 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 1682; ICR2: 0; ICR3: 0; ICR4: 0
8 | 2025-02-08 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 0; ICR2: 1450; ICR3: 0; ICR4: 0
9 | 2025-02-09 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 0; ICR2: 1247; ICR3: 0; ICR4: 0
10 | 2025-02-10 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 0; ICR2: 0; ICR3: 870; ICR4: 580
11 | 2025-02-11 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 1102
12 | 2025-02-12 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 435
13 | 2025-02-13 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0
14 | 2025-02-14 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 812
15 | 2025-02-15 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 1276; ICR2: 0; ICR3: 0; ICR4: 0
16 | 2025-02-16 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 1160; ICR2: 725; ICR3: 0; ICR4: 0
17 | 2025-02-17 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 1276; ICR2: 1218; ICR3: 0; ICR4: 0
18 | 2025-02-18 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0
19 | 2025-02-19 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 1740; ICR2: 1015; ICR3: 0; ICR4: 0
20 | 2025-02-20 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 1508; ICR2: 1798; ICR3: 0; ICR4: 0
21 | 2025-02-21 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 0; ICR2: 2436; ICR3: 0; ICR4: 0
22 | 2025-02-22 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 0; ICR2: 2320; ICR3: 0; ICR4: 0
23 | 2025-02-23 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 0; ICR2: 2639; ICR3: 0; ICR4: 0
24 | 2025-02-24 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 0; ICR2: 2378; ICR3: 0; ICR4: 0
25 | 2025-02-25 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 1450; ICR2: 0; ICR3: 0; ICR4: 0
26 | 2025-02-26 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 3712; ICR2: 0; ICR3: 0; ICR4: 0
27 | 2025-02-27 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0
28 | 2025-02-28 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | ICR1: 1276; ICR2: 580; ICR3: 0; ICR4: 0
29 | 2025-03-01 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 580; ICR2: 2378; ICR3: 0; ICR4: 0
30 | 2025-03-02 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 435; ICR3: 1769; ICR4: 0
31 | 2025-03-03 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 2784; ICR2: 0; ICR3: 0; ICR4: 0
32 | 2025-03-04 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0
33 | 2025-03-05 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 696; ICR2: 0; ICR3: 0; ICR4: 986
34 | 2025-03-06 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 1972
35 | 2025-03-07 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 928; ICR2: 0; ICR3: 0; ICR4: 58
36 | 2025-03-08 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 1943; ICR3: 0; ICR4: 0
37 | 2025-03-09 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 1769; ICR3: 0; ICR4: 0
38 | 2025-03-10 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 1740; ICR3: 0; ICR4: 0
39 | 2025-03-11 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 3103; ICR3: 0; ICR4: 0
40 | 2025-03-12 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 4002; ICR3: 0; ICR4: 0
41 | 2025-03-13 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0
42 | 2025-03-14 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0
43 | 2025-03-15 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0
44 | 2025-03-16 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0
45 | 2025-03-17 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 2726; ICR2: 0; ICR3: 0; ICR4: 0
46 | 2025-03-18 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 2117; ICR3: 580; ICR4: 754
47 | 2025-03-19 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 2900; ICR2: 0; ICR3: 348; ICR4: 0
48 | 2025-03-20 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 3161; ICR2: 0; ICR3: 0; ICR4: 0
49 | 2025-03-21 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0
50 | 2025-03-22 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 4524; ICR2: 0; ICR3: 0; ICR4: 0
51 | 2025-03-23 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 3509
52 | 2025-03-24 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 2233; ICR3: 1653; ICR4: 2233
53 | 2025-03-25 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 3364; ICR3: 0; ICR4: 0
54 | 2025-03-26 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 3132; ICR3: 0; ICR4: 0
55 | 2025-03-27 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 0; ICR2: 1218; ICR3: 1218; ICR4: 0
56 | 2025-03-28 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 2088; ICR2: 0; ICR3: 696; ICR4: 1450
57 | 2025-03-29 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 754; ICR2: 0; ICR3: 0; ICR4: 0
58 | 2025-03-30 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 1566; ICR2: 0; ICR3: 0; ICR4: 2726
59 | 2025-03-31 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | ICR1: 1566; ICR2: 0; ICR3: 0; ICR4: 4031
60 | 2025-04-01 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 3567
61 | 2025-04-02 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 4321
62 | 2025-04-03 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 5829; ICR2: 0; ICR3: 0; ICR4: 0
63 | 2025-04-04 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 4234; ICR2: 1276; ICR3: 0; ICR4: 0
64 | 2025-04-05 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 0; ICR3: 3509; ICR4: 0
65 | 2025-04-06 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 3219; ICR3: 0; ICR4: 0
66 | 2025-04-07 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 2697; ICR3: 0; ICR4: 0 | 2697 | 0.35417 | 0.41667 | 0.66667 | 0.77083
67 | 2025-04-08 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 1450; ICR2: 1943; ICR3: 0; ICR4: 0 | 3393 | 0.28125 | 0.40625 | 0.6875 | 0.79167
68 | 2025-04-09 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 4756; ICR2: 0; ICR3: 0; ICR4: 0 | 4756 | 0.23958 | 0.39583 | 0.64583 | 0.77083
69 | 2025-04-10 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 2320; ICR2: 0; ICR3: 0; ICR4: 0 | 2320 | 0.28125 | 0.40625 | 0.69792 | 0.79167
70 | 2025-04-11 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 1972; ICR2: 0; ICR3: 0; ICR4: 1160 | 3132 | 0.22917 | 0.39583 | 0.60417 | 0.6875
71 | 2025-04-12 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 1392 | 1392 | 0.23958 | 0.39583 | 0.64583 | 0.77083
72 | 2025-04-13 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 2030 | 2030 | 0.22917 | 0.39583 | 0.60417 | 0.6875
73 | 2025-04-14 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 3045 | 3045 | 0.21875 | 0.39583 | 0.625 | 0.6875
74 | 2025-04-15 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 2842 | 2842
75 | 2025-04-16 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 957 | 957 | 0.22917 | 0.39583 | 0.60417 | 0.6875
76 | 2025-04-17 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 0; ICR3: 1102; ICR4: 1537 | 2639 | 0.22917 | 0.39583 | 0.60417 | 0.6875
77 | 2025-04-18 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 0; ICR3: 2320; ICR4: 0 | 2320 | 0.22917 | 0.39583 | 0.60417 | 0.6875
78 | 2025-04-19 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 1015; ICR3: 2871; ICR4: 0 | 3886
79 | 2025-04-20 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 3799; ICR3: 638; ICR4: 0 | 4437
80 | 2025-04-21 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 3480; ICR3: 0; ICR4: 0 | 3480
81 | 2025-04-22 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 1856; ICR3: 0; ICR4: 0 | 1856
82 | 2025-04-23 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 2639; ICR3: 0; ICR4: 0 | 2639
83 | 2025-04-24 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0 | 0
84 | 2025-04-25 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 0; ICR2: 3741; ICR3: 464; ICR4: 0 | 4205
85 | 2025-04-26 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 1102; ICR2: 2929; ICR3: 116; ICR4: 232 | 4379
86 | 2025-04-27 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 2668; ICR2: 174; ICR3: 0; ICR4: 2349 | 5191
87 | 2025-04-28 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 1102; ICR2: 2929; ICR3: 116; ICR4: 232 | 4379
88 | 2025-04-29 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 2668; ICR2: 174; ICR3: 2349; ICR4: 0 | 5191
89 | 2025-04-30 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  |  | ICR1: 2494; ICR2: 1392; ICR3: 0; ICR4: 0 | 3886 |  |  | 0.70833 | 0.79167
90 | 2025-05-01 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 3654; ICR2: 0; ICR3: 0; ICR4: 0 | 3654 |  |  | 0.58333 | 0.8125
91 | 2025-05-02 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 3828; ICR2: 0; ICR3: 0; ICR4: 377 | 4205
92 | 2025-05-03 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 232; ICR2: 0; ICR3: 0; ICR4: 4466 | 4698
93 | 2025-05-04 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 4872 | 4872
94 | 2025-05-05 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 4089 | 4089
95 | 2025-05-06 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 957; ICR2: 0; ICR3: 0; ICR4: 0 | 957
96 | 2025-05-07 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 464; ICR2: 0; ICR3: 0; ICR4: 0 | 464
97 | 2025-05-08 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 1392; ICR2: 609; ICR3: 0; ICR4: 0 | 2001
98 | 2025-05-09 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 2407; ICR2: 0; ICR3: 0; ICR4: 1914 | 4321
99 | 2025-05-10 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 4756; ICR3: 0; ICR4: 0 | 4756
100 | 2025-05-11 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 3712; ICR3: 0; ICR4: 0 | 3712
101 | 2025-05-12 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0 | 0
102 | 2025-05-13 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0 | 0
103 | 2025-05-14 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0 | 0
104 | 2025-05-15 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0 | 0
105 | 2025-05-16 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0 | 0
106 | 2025-05-17 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0 | 0
107 | 2025-05-18 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0 | 0
108 | 2025-05-19 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0 | 0
109 | 2025-05-20 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0 | 0
110 | 2025-05-21 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0 | 0
111 | 2025-05-22 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0 | 0
112 | 2025-05-23 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0 | 0
113 | 2025-05-24 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0 | 0
114 | 2025-05-25 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 |  |  | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0 | 0
115 | 2025-05-26 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 | [10 empty] | 0
116 | 2025-05-27 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 | [10 empty] | 0
117 | 2025-05-28 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 | [10 empty] | 0
118 | 2025-05-29 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 | [10 empty] | 0
119 | 2025-05-30 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 | [10 empty] | 0
120 | 2025-05-31 | 2026 | 2025 | Year_2 | Year_2 | May-25 | 31 | [10 empty] | 0
120 | 2025-06-01 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
122 | 2025-06-02 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
123 | 2025-06-03 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
124 | 2025-06-04 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
125 | 2025-06-05 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
126 | 2025-06-06 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
127 | 2025-06-07 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
127 | 2025-06-08 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
127 | 2025-06-09 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
127 | 2025-06-10 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
127 | 2025-06-11 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
127 | 2025-06-12 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
127 | 2025-06-13 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
127 | 2025-06-14 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
127 | 2025-06-15 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
127 | 2025-06-16 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
127 | 2025-06-17 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
127 | 2025-06-18 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
139 | 2025-06-19 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
140 | 2025-06-20 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
141 | 2025-06-21 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
142 | 2025-06-22 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
143 | 2025-06-23 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
144 | 2025-06-24 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
145 | 2025-06-25 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
146 | 2025-06-26 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
147 | 2025-06-27 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
148 | 2025-06-28 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
149 | 2025-06-29 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
150 | 2025-06-30 | 2026 | 2025 | Year_2 | Year_2 | Jun-25 | 30 | [10 empty] | 0
151 | 2025-07-01 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
152 | 2025-07-02 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
153 | 2025-07-03 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
154 | 2025-07-04 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
155 | 2025-07-05 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
156 | 2025-07-06 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
157 | 2025-07-07 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
158 | 2025-07-08 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
159 | 2025-07-09 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
160 | 2025-07-10 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
161 | 2025-07-11 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
162 | 2025-07-12 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
163 | 2025-07-13 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
164 | 2025-07-14 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
165 | 2025-07-15 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
166 | 2025-07-16 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
167 | 2025-07-17 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
168 | 2025-07-18 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
169 | 2025-07-19 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
170 | 2025-07-20 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
171 | 2025-07-21 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
172 | 2025-07-22 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
173 | 2025-07-23 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
174 | 2025-07-24 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
175 | 2025-07-25 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
176 | 2025-07-26 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
177 | 2025-07-27 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
177 | 2025-07-28 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
179 | 2025-07-29 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
180 | 2025-07-30 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
181 | 2025-07-31 | 2026 | 2025 | Year_2 | Year_2 | Jul-25 | 31 | [10 empty] | 0
182 | 2025-08-01 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
183 | 2025-08-02 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
184 | 2025-08-03 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
185 | 2025-08-04 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
186 | 2025-08-05 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
187 | 2025-08-06 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
188 | 2025-08-07 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
189 | 2025-08-08 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
190 | 2025-08-09 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
191 | 2025-08-10 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
192 | 2025-08-11 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
193 | 2025-08-12 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
194 | 2025-08-13 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
195 | 2025-08-14 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
196 | 2025-08-15 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
197 | 2025-08-16 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
198 | 2025-08-17 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
199 | 2025-08-18 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
200 | 2025-08-19 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
201 | 2025-08-20 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
202 | 2025-08-21 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
203 | 2025-08-22 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
204 | 2025-08-23 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
205 | 2025-08-24 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
206 | 2025-08-25 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
207 | 2025-08-26 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
208 | 2025-08-27 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
209 | 2025-08-28 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
210 | 2025-08-29 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
211 | 2025-08-30 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
212 | 2025-08-31 | 2026 | 2025 | Year_2 | Year_2 | Aug-25 | 31 | [10 empty] | 0
213 | 2025-09-01 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
214 | 2025-09-02 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
215 | 2025-09-03 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
216 | 2025-09-04 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
217 | 2025-09-05 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
218 | 2025-09-06 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
219 | 2025-09-07 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
220 | 2025-09-08 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
221 | 2025-09-09 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
222 | 2025-09-10 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
223 | 2025-09-11 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
224 | 2025-09-12 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
225 | 2025-09-13 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
226 | 2025-09-14 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
227 | 2025-09-15 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
228 | 2025-09-16 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
229 | 2025-09-17 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
230 | 2025-09-18 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
231 | 2025-09-19 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
232 | 2025-09-20 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
233 | 2025-09-21 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
234 | 2025-09-22 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
235 | 2025-09-23 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
236 | 2025-09-24 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
237 | 2025-09-25 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
238 | 2025-09-26 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
239 | 2025-09-27 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
240 | 2025-09-28 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
241 | 2025-09-29 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
242 | 2025-09-30 | 2026 | 2025 | Year_2 | Year_2 | Sep-25 | 30 | [10 empty] | 0
243 | 2025-10-01 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
244 | 2025-10-02 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
245 | 2025-10-03 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
246 | 2025-10-04 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
247 | 2025-10-05 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
248 | 2025-10-06 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
249 | 2025-10-07 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
250 | 2025-10-08 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
251 | 2025-10-09 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
252 | 2025-10-10 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
253 | 2025-10-11 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
254 | 2025-10-12 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
255 | 2025-10-13 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
256 | 2025-10-14 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
257 | 2025-10-15 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
258 | 2025-10-16 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
259 | 2025-10-17 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
260 | 2025-10-18 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
261 | 2025-10-19 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
262 | 2025-10-20 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
263 | 2025-10-21 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
264 | 2025-10-22 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
265 | 2025-10-23 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
266 | 2025-10-24 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
267 | 2025-10-25 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
268 | 2025-10-26 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
269 | 2025-10-27 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
270 | 2025-10-28 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
271 | 2025-10-29 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
272 | 2025-10-30 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
273 | 2025-10-31 | 2026 | 2025 | Year_2 | Year_2 | Oct-25 | 31 | [10 empty] | 0
274 | 2025-11-01 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
275 | 2025-11-02 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
276 | 2025-11-03 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
277 | 2025-11-04 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
278 | 2025-11-05 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
279 | 2025-11-06 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
280 | 2025-11-07 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
281 | 2025-11-08 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
282 | 2025-11-09 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
283 | 2025-11-10 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
284 | 2025-11-11 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
285 | 2025-11-12 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
286 | 2025-11-13 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
287 | 2025-11-14 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
288 | 2025-11-15 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
289 | 2025-11-16 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
290 | 2025-11-17 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
291 | 2025-11-18 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
292 | 2025-11-19 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
293 | 2025-11-20 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
294 | 2025-11-21 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
295 | 2025-11-22 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
296 | 2025-11-23 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
297 | 2025-11-24 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
298 | 2025-11-25 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
299 | 2025-11-26 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
300 | 2025-11-27 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
301 | 2025-11-28 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
302 | 2025-11-29 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
303 | 2025-11-30 | 2026 | 2025 | Year_2 | Year_2 | Nov-25 | 30 | [10 empty] | 0
304 | 2025-12-01 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
305 | 2025-12-02 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
306 | 2025-12-03 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
307 | 2025-12-04 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
308 | 2025-12-05 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
309 | 2025-12-06 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
310 | 2025-12-07 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
311 | 2025-12-08 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
312 | 2025-12-09 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
313 | 2025-12-10 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
314 | 2025-12-11 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
315 | 2025-12-12 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
316 | 2025-12-13 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
317 | 2025-12-14 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
318 | 2025-12-15 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
319 | 2025-12-16 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
320 | 2025-12-17 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
321 | 2025-12-18 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
322 | 2025-12-19 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
323 | 2025-12-20 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
324 | 2025-12-21 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
325 | 2025-12-22 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
326 | 2025-12-23 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
327 | 2025-12-24 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
328 | 2025-12-25 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
329 | 2025-12-26 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | 2 | 2 | 464 | 0 | 0 | 0 | 0 |  |  |  | 464 |  |  | 0.625 | 0.75 | MOP
330 | 2025-12-27 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
331 | 2025-12-28 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | 2 | 5 | 2088 | 0 | 0 | 0 | 0 |  |  |  | 2088 | 0.16667 | 0.45833 |  |  | MOP
332 | 2025-12-29 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | [10 empty] | 0
333 | 2025-12-30 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | 2 | 5 | 2088 | 0 | 0 | 0 | 0 |  |  |  | 2088 | 0.16667 | 0.45833 |  |  | MOP
334 | 2025-12-31 | 2026 | 2025 | Year_2 | Year_2 | Dec-25 | 31 | 2 | 5 | 1392 | 0 | 0 | 0 | 0 |  |  |  | 1392 |  |  | 0.625 | 0.75 | MOP
335 | 2026-01-01 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 5 | 0 | 0 | 754 | 0 | 0 | 2436 |  |  | 3190 | 0.25 | 0.54167 | 0.58333 | 0.625 | MOP
336 | 2026-01-02 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | [10 empty] | 0
337 | 2026-01-03 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 5 | 0 | 0 | 3016 | 0 | 0 | 0 |  |  | 3016 | 0.25 | 0.54167 | 0.58333 | 0.625 | MOP
338 | 2026-01-04 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | [10 empty] | 0
339 | 2026-01-05 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 5 | 0 | 0 | 464 | 0 | 0 | 0 |  |  | 464 |  |  | 0.70833 | 0.75 | MOP
340 | 2026-01-06 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 5 | 0 | 0 | 2987 | 0 | 0 | 0 |  |  | 2987 | 0.16667 | 0.45833 |  |  | MOP
341 | 2026-01-07 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 3248 |  |  | 3248 | 0.25 | 0.58333 |  |  | MOP
342 | 2026-01-08 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 2523 |  |  | 2523 | 0.25 | 0.58333 |  |  | MOP
343 | 2026-01-09 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 2407 |  |  | 2407 | 0.25 | 0.58333 |  |  | MOP
344 | 2026-01-10 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 7 | 0 | 0 | 0 | 0 | 2320 | 0 |  |  | 2320 | 0.25 | 0.58333 |  |  | MOP
345 | 2026-01-11 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | [10 empty] | 0
346 | 2026-01-12 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | [10 empty] | 0
347 | 2026-01-13 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | [10 empty] | 0
348 | 2026-01-14 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | [10 empty] | 0
349 | 2026-01-15 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | [10 empty] | 0
350 | 2026-01-16 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | [10 empty] | 0
351 | 2026-01-17 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | [10 empty] | 0
352 | 2026-01-18 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | [10 empty] | 0
353 | 2026-01-19 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 7 | 0 | 0 | 1595 | 0 | 0 | 0 |  |  | 1595 |  |  | 0.5 | 0.75 | MOP
354 | 2026-01-20 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 7 | 0 | 0 | 1856 | 0 | 0 | 0 |  |  | 1856 | 0.33333 | 0.5 | 0.5 | 0.75 | MOP
355 | 2026-01-21 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 7 | 0 | 0 | 2262 | 0 | 0 | 0 |  |  | 2262 | 0.41667 | 0.58333 | 0.58333 | 0.75 | MOP
356 | 2026-01-22 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 7 | 0 | 1218 | 1827 | 0 | 0 | 0 |  |  | 3045 | 0.25 | 0.58333 |  |  | MOP
357 | 2026-01-23 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 5 | 0 | 2407 | 870 | 0 | 0 | 0 |  |  | 3277 | 0.29167 | 0.54167 | 0.58333 | 0.70833 | MOP
358 | 2026-01-24 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 5 | 0 | 464 | 0 | 0 | 3480 | 0 |  |  | 3944 | 0.29167 | 0.54167 | 0.58333 | 0.70833 | MOP
359 | 2026-01-25 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 5 | 0 | 0 | 0 | 1392 | 754 | 0 |  |  | 2146 | 0.25 | 0.58333 |  |  | MOP
360 | 2026-01-26 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 5 | 0 | 0 | 0 | 2146 | 957 | 0 |  |  | 3103 | 0.25 | 0.58333 |  |  | MOP
361 | 2026-01-27 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | [10 empty] | 0 | 0.25 | 0.58333 |  |  | MOP
362 | 2026-01-28 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 5 | 1798 | 522 | 0 | 812 | 0 | 0 |  |  | 3132 | 0.25 | 0.58333 |  |  | MOP
363 | 2026-01-29 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 5 | 0 | 3306 | 0 | 1740 | 0 | 0 |  |  | 5046 | 0.25 | 0.54167 | 0.58333 | 0.70833 | MOP
364 | 2026-01-30 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 5 | 0 | 0 | 0 | 2378 | 0 | 0 | 0 | 1798 | 4176 | 0.25 | 0.54167 | 0.58333 | 0.70833 | MOP
365 | 2026-01-31 | 2026 | 2026 | Year_2 | Year_2 | Jan-26 | 31 | 2 | 15 | 3828 | 0 | 0 | 0 | 0 | 0 | 0 | 2842 | 6670 | 0.25 | 0.54167 | 0.58333 | 0.70833 | MOP
366 | 2026-02-01 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | 2 | 15 | 3480 | 0 | 0 | 0 | 0 | 0 | 0 | 5713 | 9193 | 0.25 | 0.54167 | 0.58333 | 0.70833 | MOP
367 | 2026-02-02 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | 2 | 15 | 406 | 3132 | 0 | 0 | 0 | 0 | 0 | 2320 | 5858 | 0.25 | 0.54167 | 0.58333 | 0.70833 | MOP
368 | 2026-02-03 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | 2 | 15 | 0 | 2233 | 4727 | 0 | 0 | 0 | 0 | 0 | 6960 | 0.25 | 0.54167 | 0.58333 | 0.70833 | MOP
369 | 2026-02-04 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | 2 | 15 | 0 | 3306 | 5104 | 0 | 0 | 0 | 0 | 0 | 8410 | 0.25 | 0.54167 | 0.58333 | 0.70833 | MOP
370 | 2026-02-05 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | 2 | 15 | 2436 | 3074 | 1566 | 3306 | 0 | 0 | 0 | 0 | 10382 | 0.25 | 0.54167 | 0.58333 | 0.70833 | MOP
371 | 2026-02-06 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | 2 | 15 | 0 | 3074 | 0 | 928 | 0 | 0 | 0 | 696 | 4698 | 0.25 | 0.54167 | 0.58333 | 0.70833 | MOP
372 | 2026-02-07 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | 2 | 15 | 0 | 0 | 0 | 2320 | 1334 | 0 | 0 | 2610 | 6264 | 0.25 | 0.54167 | 0.58333 | 0.70833 | MOP
373 | 2026-02-08 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3480 | 3480 | 0.25 | 0.54167 | 0.58333 | 0.70833 | MOP
374 | 2026-02-09 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3944 | 3944 | 0.25 | 0.54167 | 0.58333 | 0.70833 | MOP
375 | 2026-02-10 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | 2 | 5 | 0 | 0 | 0 | 1624 | 812 | 0 | 0 | 0 | 2436 | 0.375 | 0.54167 | 0.58333 | 0.70833 | MOP
376 | 2026-02-11 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | 2 | 13 | 0 | 0 | 0 | 0 | 1566 | 1044 | 0 | 3828 | 6438 | 0.375 | 0.54167 | 0.58333 | 0.70833 | MOP
377 | 2026-02-12 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | [10 empty] | 0
378 | 2026-02-13 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | [10 empty] | 0
379 | 2026-02-14 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | [10 empty] | 0
380 | 2026-02-15 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | [10 empty] | 0
381 | 2026-02-16 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | [10 empty] | 0
382 | 2026-02-17 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | [10 empty] | 0
383 | 2026-02-18 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | [10 empty] | 0
384 | 2026-02-19 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | [10 empty] | 0
385 | 2026-02-20 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | [10 empty] | 0
386 | 2026-02-21 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | [10 empty] | 0
387 | 2026-02-22 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | [10 empty] | 0
388 | 2026-02-23 | 2026 | 2026 | Year_2 | Year_2 | Feb-26 | 28 | [10 empty] | 0
Formulas:
Days = DAY(EOMONTH(MC_2[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## GC
Sr. No. | Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Cycle Number | Resources | ICR1 | ICR2 | ICR3 | ICR4 | ICR5 | ICR6 | ICR7 | ICR8 | ICR9 | ICR10 | ICR11 | ICR12 | ICR13 | ICR14 | Total No.Table GC done | Mrthod of Cutting | Remarks for the day
1 | 2024-04-01 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
2 | 2024-04-02 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
3 | 2024-04-03 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
4 | 2024-04-04 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
5 | 2024-04-05 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
6 | 2024-04-06 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
7 | 2024-04-07 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
8 | 2024-04-08 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
9 | 2024-04-09 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
10 | 2024-04-10 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
11 | 2024-04-11 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
12 | 2024-04-12 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
13 | 2024-04-13 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
14 | 2024-04-14 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
15 | 2024-04-15 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
16 | 2024-04-16 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
17 | 2024-04-17 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
18 | 2024-04-18 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
19 | 2024-04-19 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
20 | 2024-04-20 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
21 | 2024-04-21 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
22 | 2024-04-22 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
23 | 2024-04-23 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
24 | 2024-04-24 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
25 | 2024-04-25 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
26 | 2024-04-26 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
27 | 2024-04-27 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
28 | 2024-04-28 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
29 | 2024-04-29 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
30 | 2024-04-30 | 2025 | 2024 | Year_1 | Year_1 | Apr-24 | 30 | [16 empty] | 0
31 | 2024-05-01 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
32 | 2024-05-02 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
33 | 2024-05-03 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
34 | 2024-05-04 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
35 | 2024-05-05 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
36 | 2024-05-06 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
37 | 2024-05-07 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
38 | 2024-05-08 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
39 | 2024-05-09 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
40 | 2024-05-10 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
41 | 2024-05-11 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
42 | 2024-05-12 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
43 | 2024-05-13 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
44 | 2024-05-14 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
45 | 2024-05-15 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
46 | 2024-05-16 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
47 | 2024-05-17 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
48 | 2024-05-18 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
49 | 2024-05-19 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
50 | 2024-05-20 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
51 | 2024-05-21 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
52 | 2024-05-22 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
53 | 2024-05-23 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
54 | 2024-05-24 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
55 | 2024-05-25 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
56 | 2024-05-26 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
57 | 2024-05-27 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
58 | 2024-05-28 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
59 | 2024-05-29 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
60 | 2024-05-30 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
61 | 2024-05-31 | 2025 | 2024 | Year_1 | Year_1 | May-24 | 31 | [16 empty] | 0
62 | 2024-06-01 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
63 | 2024-06-02 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
64 | 2024-06-03 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
65 | 2024-06-04 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
66 | 2024-06-05 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
67 | 2024-06-06 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
68 | 2024-06-07 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
69 | 2024-06-08 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
70 | 2024-06-09 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
71 | 2024-06-10 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
72 | 2024-06-11 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
73 | 2024-06-12 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
74 | 2024-06-13 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
75 | 2024-06-14 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
76 | 2024-06-15 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
77 | 2024-06-16 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
78 | 2024-06-17 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
79 | 2024-06-18 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
80 | 2024-06-19 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
81 | 2024-06-20 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
82 | 2024-06-21 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
83 | 2024-06-22 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
84 | 2024-06-23 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
85 | 2024-06-24 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
86 | 2024-06-25 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
87 | 2024-06-26 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
88 | 2024-06-27 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
89 | 2024-06-28 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
90 | 2024-06-29 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
91 | 2024-06-30 | 2025 | 2024 | Year_1 | Year_1 | Jun-24 | 30 | [16 empty] | 0
92 | 2024-07-01 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | [16 empty] | 0
93 | 2024-07-02 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | [16 empty] | 0
94 | 2024-07-03 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | [16 empty] | 0
95 | 2024-07-04 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | [16 empty] | 0
96 | 2024-07-05 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | [16 empty] | 0
97 | 2024-07-06 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | [16 empty] | 0
98 | 2024-07-07 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | [16 empty] | 0
99 | 2024-07-08 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | [16 empty] | 0
100 | 2024-07-09 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | [16 empty] | 0
101 | 2024-07-10 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | [16 empty] | 0
102 | 2024-07-11 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | [16 empty] | 0
103 | 2024-07-12 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 55; ICR4: 0; ICR5: 0 | 55 | Bush Cutter | 55 tables Grass cutting work completed
104 | 2024-07-13 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 94; ICR4: 0; ICR5: 0 | 94 | Bush Cutter | 94tables Grass cutting work completed
105 | 2024-07-14 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 107; ICR4: 0; ICR5: 0 | 107 | Bush Cutter | 107 Tables Grass Cutting Work Completed
106 | 2024-07-15 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 85; ICR3: 0; ICR4: 0; ICR5: 0 | 85 | Bush Cutter | 85 Tables Grass Cutting Work Completed
107 | 2024-07-16 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 32; ICR3: 0; ICR4: 72; ICR5: 12 | 116 | Bush Cutter | 116 Tables Grass Cutting Work Completed
108 | 2024-07-17 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 17; ICR3: 0; ICR4: 53; ICR5: 24 | 94 | Bush Cutter | 94 Tables Grass Cutting Work Completed
109 | 2024-07-18 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 58 | 58 | Bush Cutter | 58 Tables Grass Cutting Work Completed
110 | 2024-07-19 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0 | 0 |  | Labours Absent
111 | 2024-07-20 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 31; ICR3: 0; ICR4: 18; ICR5: 0 | 49 | Bush Cutter | 49 Tables Grass Cutting Work Completed
112 | 2024-07-21 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 43; ICR4: 0; ICR5: 0; ICR6: 0 | 43 | Bush Cutter | 43 Tables & Non PV area Grass Cutting Work Completed
113 | 2024-07-22 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 31; ICR6: 27 | 58 | Bush Cutter | 58 Tables & Non PV area Grass Cutting Work Completed
114 | 2024-07-23 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 10; ICR5: 10; ICR6: 0 | 20 | Bush Cutter | 20 Tables & Non PV area Grass Cutting Work Completed
115 | 2024-07-24 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 26; ICR5: 18; ICR6: 0 | 44 | Bush Cutter | 44 Tables & Non PV area Grass Cutting Work Completed
116 | 2024-07-25 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 5; ICR5: 65; ICR6: 0 | 70 | Bush Cutter | 70 Tables & Non PV area Grass Cutting Work Completed
117 | 2024-07-26 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 3; ICR4: 0; ICR5: 0; ICR6: 0 | 3 | Bush Cutter | 3 Tables & Non PV area Grass Cutting Work Completed
118 | 2024-07-27 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 42; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0 | 42 | Bush Cutter | 42 Tables & Non PV area Grass Cutting Work Completed
119 | 2024-07-28 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 69; ICR2: 0; ICR3: 0; ICR4: 6; ICR5: 0; ICR6: 0 | 75 | Bush Cutter | 75 Tables & Non PV area Grass Cutting Work Completed
120 | 2024-07-29 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | [16 empty] | 0
120 | 2024-07-30 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 36; ICR3: 0; ICR4: 58; ICR5: 0; ICR6: 0 | 94 | Bush Cutter | 94 Tables & Non PV area Grass Cutting Work Completed
122 | 2024-07-31 | 2025 | 2024 | Year_1 | Year_1 | Jul-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 115 | 115 | Bush Cutter | 115 Tables & Non PV area Grass Cutting Work Completed
123 | 2024-08-01 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 77 | 77 | Bush Cutter | 77 Tables & Non PV area Grass Cutting Work Completed
124 | 2024-08-02 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 113; ICR8: 0 | 113 | Bush Cutter | 113 Tables & Non PV area Grass Cutting Work Completed
125 | 2024-08-03 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 19; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 22; ICR8: 0 | 41 | Bush Cutter | 41 Tables & Non PV area Grass Cutting Work Completed
126 | 2024-08-04 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
127 | 2024-08-05 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
127 | 2024-08-06 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
127 | 2024-08-07 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
127 | 2024-08-08 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
127 | 2024-08-09 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
127 | 2024-08-10 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
127 | 2024-08-11 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
127 | 2024-08-12 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
127 | 2024-08-13 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
127 | 2024-08-14 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
127 | 2024-08-15 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
127 | 2024-08-16 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
139 | 2024-08-17 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
140 | 2024-08-18 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
141 | 2024-08-19 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
142 | 2024-08-20 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
143 | 2024-08-21 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
144 | 2024-08-22 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
145 | 2024-08-23 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
146 | 2024-08-24 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
147 | 2024-08-25 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
148 | 2024-08-26 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | [16 empty] | 0
149 | 2024-08-27 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 12 | 12 | Bush Cutter | 12 Tables & Non PV area Grass Cutting Work Completed by Project team
150 | 2024-08-28 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 29 | 29 | Bush Cutter | 29 Tables & Non PV area Grass Cutting Work Completed by Project team
151 | 2024-08-29 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 25 | 25 | Bush Cutter | 25 Tables & Non PV area Grass Cutting Work Completed by Project team
152 | 2024-08-30 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 23 | 23 | Bush Cutter | 23 Tables & Non PV area Grass Cutting Work Completed by Project team
153 | 2024-08-31 | 2025 | 2024 | Year_1 | Year_1 | Aug-24 | 31 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 28 | 28 | Bush Cutter | 28 Tables & Non PV area Grass Cutting Work Completed by Project team
154 | 2024-09-01 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
155 | 2024-09-02 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 30 | 30 | Bush Cutter | 30 Tables & Non PV area Grass Cutting Work Completed by Project team
156 | 2024-09-03 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 31 | 31 | Bush Cutter | 31 Tables & Non PV area Grass Cutting Work Completed by Project team
157 | 2024-09-04 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | 1 | Bush Cutter | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 35 | 35 | Bush Cutter | 35 Tables & Non PV area Grass Cutting Work Completed by Project team
158 | 2024-09-05 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
159 | 2024-09-06 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
160 | 2024-09-07 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
161 | 2024-09-08 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
162 | 2024-09-09 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
163 | 2024-09-10 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
164 | 2024-09-11 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
165 | 2024-09-12 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
166 | 2024-09-13 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
167 | 2024-09-14 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
168 | 2024-09-15 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
169 | 2024-09-16 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
170 | 2024-09-17 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
171 | 2024-09-18 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
172 | 2024-09-19 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
173 | 2024-09-20 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
174 | 2024-09-21 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
175 | 2024-09-22 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
176 | 2024-09-23 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
177 | 2024-09-24 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
177 | 2024-09-25 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
179 | 2024-09-26 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
180 | 2024-09-27 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
181 | 2024-09-28 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0 | Rotavator
182 | 2024-09-29 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0 | Manually Grass Cutting
183 | 2024-09-30 | 2025 | 2024 | Year_1 | Year_1 | Sep-24 | 30 | [16 empty] | 0
184 | 2024-10-01 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
185 | 2024-10-02 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
186 | 2024-10-03 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
187 | 2024-10-04 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
188 | 2024-10-05 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
189 | 2024-10-06 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
190 | 2024-10-07 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
191 | 2024-10-08 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
192 | 2024-10-09 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
193 | 2024-10-10 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
194 | 2024-10-11 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
195 | 2024-10-12 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
196 | 2024-10-13 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
197 | 2024-10-14 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
198 | 2024-10-15 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
199 | 2024-10-16 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
200 | 2024-10-17 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
201 | 2024-10-18 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
202 | 2024-10-19 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
203 | 2024-10-20 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
204 | 2024-10-21 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
205 | 2024-10-22 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
206 | 2024-10-23 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
207 | 2024-10-24 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
208 | 2024-10-25 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
209 | 2024-10-26 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
210 | 2024-10-27 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
211 | 2024-10-28 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
212 | 2024-10-29 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | [16 empty] | 0
213 | 2024-10-30 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | 2 | Rotavator | ICR1: 0; ICR2: 38; ICR3: 17; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 55 | Rotavator | 55 Tables & along with supporting Non PV area Grass Cutting Work Completed
214 | 2024-10-31 | 2025 | 2024 | Year_1 | Year_1 | Oct-24 | 31 | 2 | Rotavator | ICR1: 0; ICR2: 16; ICR3: 32; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 48 | Rotavator | 48 Tables & along with supporting Non PV area Grass Cutting Work Completed
215 | 2024-11-01 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | [16 empty] | 0
216 | 2024-11-02 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | [16 empty] | 0
217 | 2024-11-03 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | [16 empty] | 0
218 | 2024-11-04 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | [16 empty] | 0
219 | 2024-11-05 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | [16 empty] | 0
220 | 2024-11-06 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | [16 empty] | 0
221 | 2024-11-07 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 61; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 61 | Rotavator | 61 Tables & along with supporting Non PV area Grass Cutting Work Completed
222 | 2024-11-08 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 24; ICR2: 0; ICR3: 35; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 59 | Rotavator | 59 Tables & along with supporting Non PV area Grass Cutting Work Completed
223 | 2024-11-09 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 35; ICR3: 10; ICR4: 6; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 51 | Rotavator | 51 Tables & along with supporting Non PV area Grass Cutting Work Completed
224 | 2024-11-10 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 30; ICR3: 6; ICR4: 17; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 53 | Rotavator | 53 Tables & along with supporting Non PV area Grass Cutting Work Completed
225 | 2024-11-11 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 18; ICR3: 0; ICR4: 35; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 53 | Rotavator | 53 Tables & along with supporting Non PV area Grass Cutting Work Completed
226 | 2024-11-12 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 14; ICR3: 0; ICR4: 34; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 48 | Rotavator | 48 Tables & along with supporting Non PV area Grass Cutting Work Completed
227 | 2024-11-13 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | [16 empty] | 0
228 | 2024-11-14 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 32; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 32 | Rotavator | 32 Tables & along with supporting Non PV area Grass Cutting Work Completed
229 | 2024-11-15 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 30; ICR2: 15; ICR3: 0; ICR4: 15; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 60 | Rotavator | 60 Tables & along with supporting Non PV area Grass Cutting Work Completed
230 | 2024-11-16 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 34; ICR2: 18; ICR3: 0; ICR4: 14; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 66 | Rotavator | 66 Tables & along with supporting Non PV area Grass Cutting Work Completed
231 | 2024-11-17 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 22; ICR3: 0; ICR4: 35; ICR5: 11; ICR6: 0; ICR7: 0; ICR8: 0 | 68 | Rotavator | 68 Tables & along with supporting Non PV area Grass Cutting Work Completed
232 | 2024-11-18 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 45; ICR5: 35; ICR6: 0; ICR7: 0; ICR8: 0 | 80 | Rotavator | 80 Tables & along with supporting Non PV area Grass Cutting Work Completed
233 | 2024-11-19 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 71; ICR6: 0; ICR7: 0; ICR8: 0 | 71 | Rotavator | 71 Tables & along with supporting Non PV area Grass Cutting Work Completed
234 | 2024-11-20 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 61; ICR6: 19; ICR7: 0; ICR8: 0 | 80 | Rotavator | 80 Tables & along with supporting Non PV area Grass Cutting Work Completed
235 | 2024-11-21 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 21; ICR7: 0; ICR8: 0 | 21 | Rotavator | 21 Tables & along with supporting Non PV area Grass Cutting Work Completed
236 | 2024-11-22 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 34; ICR7: 0; ICR8: 0 | 34 | Rotavator | 34 Tables & along with supporting Non PV area Grass Cutting Work Completed
237 | 2024-11-23 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 9; ICR6: 27; ICR7: 0; ICR8: 0 | 36 | Rotavator | 36 Tables & along with supporting Non PV area Grass Cutting Work Completed
238 | 2024-11-24 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 17; ICR6: 29; ICR7: 0; ICR8: 0 | 46 | Rotavator | 46 Tables & along with supporting Non PV area Grass Cutting Work Completed
239 | 2024-11-25 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | [16 empty] | 0
240 | 2024-11-26 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 42; ICR7: 0; ICR8: 0 | 42 | Rotavator | 42 Tables & along with supporting Non PV area Grass Cutting Work Completed
241 | 2024-11-27 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 12; ICR7: 31; ICR8: 0 | 43 | Rotavator | 43 Tables & along with supporting Non PV area Grass Cutting Work Completed
242 | 2024-11-28 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 64; ICR8: 0 | 64 | Rotavator | 64 Tables & along with supporting Non PV area Grass Cutting Work Completed
243 | 2024-11-29 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 40; ICR8: 0 | 40 | Rotavator | 40 Tables & along with supporting Non PV area Grass Cutting Work Completed
244 | 2024-11-30 | 2025 | 2024 | Year_1 | Year_1 | Nov-24 | 30 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 20; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 20 | Rotavator | 20 Tables & along with supporting Non PV area Grass Cutting Work Completed
245 | 2024-12-01 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 10; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 10 | Rotavator | 10 Tables & along with supporting Non PV area Grass Cutting Work Completed
246 | 2024-12-02 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
247 | 2024-12-03 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
248 | 2024-12-04 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
249 | 2024-12-05 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
250 | 2024-12-06 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
251 | 2024-12-07 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
252 | 2024-12-08 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
253 | 2024-12-09 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
254 | 2024-12-10 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
255 | 2024-12-11 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
256 | 2024-12-12 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
257 | 2024-12-13 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
258 | 2024-12-14 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
259 | 2024-12-15 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
260 | 2024-12-16 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
261 | 2024-12-17 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | 2 | Rotavator | ICR1: 0; ICR2: 12; ICR3: 0; ICR4: 4; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 16 | Rotavator | 16 Tables & along with supporting Non PV area Grass Cutting Work Completed
262 | 2024-12-18 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | 2 | Rotavator | ICR1: 0; ICR2: 10; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 37 | 47 | Rotavator | 47 Tables & along with supporting Non PV area Grass Cutting Work Completed
263 | 2024-12-19 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 28 | 28 | Rotavator | 28 Tables & along with supporting Non PV area Grass Cutting Work Completed
264 | 2024-12-20 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 85 | 85 | Rotavator | 85 Tables & along with supporting Non PV area Grass Cutting Work Completed
265 | 2024-12-21 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 103 | 103 | Rotavator | 85 Tables & along with supporting Non PV area Grass Cutting Work Completed
266 | 2024-12-22 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 27; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 85 | 112 | Rotavator | 112 Tables & along with supporting Non PV area Grass Cutting Work Completed
267 | 2024-12-23 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 115 | 115 | Rotavator | 115 Tables & along with supporting Non PV area Grass Cutting Work Completed
268 | 2024-12-24 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | 2 | Rotavator | ICR1: 13; ICR2: 0; ICR3: 31; ICR4: 15; ICR5: 7; ICR6: 0; ICR7: 0; ICR8: 42 | 108 | Rotavator | 115 Tables & along with supporting Non PV area Grass Cutting Work Completed
269 | 2024-12-25 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 5; ICR6: 0; ICR7: 0; ICR8: 6 | 11 | Rotavator | 11 Tables & along with supporting Non PV area Grass Cutting Work Completed
270 | 2024-12-26 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 0; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 17 | 17 | Rotavator | 17 Tables & along with supporting Non PV area Grass Cutting Work Completed
271 | 2024-12-27 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 18; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 13 | 31 | Rotavator | 31 Tables & along with supporting Non PV area Grass Cutting Work Completed
272 | 2024-12-28 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | 2 | Rotavator | ICR1: 0; ICR2: 34; ICR3: 14; ICR4: 15; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 63 | Rotavator | 63 Tables & along with supporting Non PV area Grass Cutting Work Completed
273 | 2024-12-29 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | 2 | Rotavator | ICR1: 0; ICR2: 0; ICR3: 0; ICR4: 28; ICR5: 0; ICR6: 0; ICR7: 0; ICR8: 0 | 28 | Rotavator | 28 Tables & along with supporting Non PV area Grass Cutting Work Completed
274 | 2024-12-30 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
275 | 2024-12-31 | 2025 | 2024 | Year_1 | Year_1 | Dec-24 | 31 | [16 empty] | 0
276 | 2025-01-01 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
277 | 2025-01-02 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
278 | 2025-01-03 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
279 | 2025-01-04 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
280 | 2025-01-05 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
281 | 2025-01-06 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
282 | 2025-01-07 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
283 | 2025-01-08 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
284 | 2025-01-09 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
285 | 2025-01-10 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
286 | 2025-01-11 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
287 | 2025-01-12 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
288 | 2025-01-13 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
289 | 2025-01-14 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
290 | 2025-01-15 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
291 | 2025-01-16 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | Rotavator | 55 Tables & along with supporting Non PV area Grass Cutting Work Completed
292 | 2025-01-17 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 44 | Rotavator | 44 Tables & along with supporting Non PV area Grass Cutting Work Completed
293 | 2025-01-18 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 40 | Rotavator | 40 Tables & along with supporting Non PV area Grass Cutting Work Completed
294 | 2025-01-19 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 6 | 33 | Rotavator | 33 Tables & along with supporting Non PV area Grass Cutting Work Completed
295 | 2025-01-20 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 31 | Rotavator | 31 Tables & along with supporting Non PV area Grass Cutting Work Completed
296 | 2025-01-21 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
297 | 2025-01-22 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 39 | Rotavator | 39 Tables & along with supporting Non PV area Grass Cutting Work Completed
298 | 2025-01-23 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 38 | Rotavator | 38 Tables & along with supporting Non PV area Grass Cutting Work Completed
299 | 2025-01-24 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | Rotavator | 35 Tables & along with supporting Non PV area Grass Cutting Work Completed
300 | 2025-01-25 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
301 | 2025-01-26 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
302 | 2025-01-27 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | Rotavator | 30 Tables & along with supporting Non PV area Grass Cutting Work Completed
303 | 2025-01-28 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 25 | Rotavator | 25 Tables & along with supporting Non PV area Grass Cutting Work Completed
304 | 2025-01-29 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | [16 empty] | 0
305 | 2025-01-30 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 32 | Rotavator | 32 Tables & along with supporting Non PV area Grass Cutting Work Completed
306 | 2025-01-31 | 2025 | 2025 | Year_1 | Year_1 | Jan-25 | 31 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 6 | 4 | 0 | 42 | Rotavator | 42 Tables & along with supporting Non PV area Grass Cutting Work Completed
307 | 2025-02-01 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 9 | 0 | 0 | 45 | Rotavator | 45 Tables & along with supporting Non PV area Grass Cutting Work Completed
308 | 2025-02-02 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [16 empty] | 0
309 | 2025-02-03 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 16 | 0 | 0 | 48 | Rotavator | 48 Tables & along with supporting Non PV area Grass Cutting Work Completed
310 | 2025-02-04 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 8 | 0 | 0 | 0 | 0 | 46 | Rotavator | 46 Tables & along with supporting Non PV area Grass Cutting Work Completed
311 | 2025-02-05 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 40 | 0 | 0 | 0 | 0 | 57 | Rotavator | 57 Tables & along with supporting Non PV area Grass Cutting Work Completed
312 | 2025-02-06 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | Rotavator | 35 Tables & along with supporting Non PV area Grass Cutting Work Completed
313 | 2025-02-07 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | 1 | Rotavator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 38 | Rotavator | 38 Tables & along with supporting Non PV area Grass Cutting Work Completed
314 | 2025-02-08 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [16 empty] | 0
315 | 2025-02-09 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [16 empty] | 0
316 | 2025-02-10 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [16 empty] | 0
317 | 2025-02-11 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [16 empty] | 0
318 | 2025-02-12 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [16 empty] | 0
319 | 2025-02-13 | 2025 | 2025 | Year_1 | Year_1 | Feb-25 | 28 | [16 empty] | 0
Formulas:
Days = DAY(EOMONTH(GC[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## Basic Data
Inverter Station | Inverter | Module | SCB | String Type | Equipment | Equipment | Generator | Consumer | Capacity | % Plant Equiva. Weightage | METERING YARD | FEEDER | OG | TRANSFER | Fault Category Plant BD sheet | Status | Capcity |  | Generator | Customer | Metering Yard | AC Capcity | DC Capcity | COD | Feeder No | Inv | Consumer | Capacity | % Plant Equiva. Weightage
IS1 | Inv1 | M1 | SCB1 | Str_Typ1(545*29) | Tx | IS1Inv1M1 | O2RE7 |  | 2339.14 | 5.966% | 0 | Solar_F1 | Line1 | TX1 | Module | Open |  |  | O2RE7 | STT |  | 19.45 | 29.05 | 4568800% | F1 |  |  | 0 | 0% | Solar | 100
IS2 | Inv2 | M2 | SCB2 | Str_Typ2(550*29) | MVP | IS1Inv1M2 | O2RE7 |  | 2323.335 | 5.925% | 0 | Solar_F1 | Line1 | TX1 | Cables | Close | Expecetd DC Capcity | 135000 | O2RE27 | Kores |  | 7.53 | 10.1655 | 4568800% | OG1 |  |  | 100 | 100%
IS3 | Inv3 | M3 | SCB3 | Str_Typ1(545*58) | Aux_Tx | IS1Inv2M1 | O2RE7 |  | 2339.14 | 5.966% | 0 | Solar_F1 | Line1 | TX1 | String Fuses |  | Running DC Capcity | 39210 | [6 empty] | TX1 |  |  | 100 | 100%
IS4 | Inv4 | M4 | SCB4 | Str_Typ2(550*58) | MCR_MVP_SolarF1 | IS1Inv2M2 | O2RE7 |  | 2323.335 | 5.925% | 0 | Solar_F1 | Line1 | TX1 | SCB | [9 empty] | Line1 |  |  | 100 | 100%
|  |  | SCB5 |  | MCR_MVP_SolarF2 | IS2Inv1M1 | O2RE7 |  | 1627.915 | 4.152% | 0 | Solar_F1 | Line1 | TX1 | Inverter
|  |  | SCB6 |  | MCR_MVP_SolarF3 | IS2Inv1M2 | O2RE7 |  | 1627.915 | 4.152% | 0 | Solar_F1 | Line1 | TX1 | IDT
|  |  | SCB7 |  | MCR_MVP_SolarF4 | IS2Inv1M3 | O2RE7 |  | 1627.915 | 4.152% | 0 | Solar_F1 | Line1 | TX1 | PTR
|  |  | SCB8 |  | Power_Tx1 | IS2Inv1M4 | O2RE7 |  | 1627.915 | 4.152% | 0 | Solar_F1 | Line1 | TX1 | MV Panel
|  |  | SCB9 |  | Line_Bay1 | IS2Inv2M1 | O2RE7 |  | 1627.915 | 4.152% | 0 | Solar_F1 | Line1 | TX1 | Metering System Plant
[6 empty] | IS2Inv2M2 | O2RE7 |  | 1612.11 | 4.111% | 0 | Solar_F1 | Line1 | TX1 | Grid System
[6 empty] | IS2Inv2M3 | O2RE7 |  | 1627.915 | 4.152% | 0 | Solar_F1 | Line1 | TX1 | Metering System Grid
[6 empty] | IS2Inv2M4 | O2RE7 |  | 1627.915 | 4.152% | 0 | Solar_F1 | Line1 | TX1 | WMS
[6 empty] | IS3Inv1M1 | O2RE7 |  | 1627.915 | 4.152% | 0 | Solar_F1 | Line1 | TX1 | MMS |  |  |  | Total |  |  | 26.98 | 39.2155
[6 empty] | IS3Inv1M2 | O2RE7 |  | 1627.915 | 4.152% | 0 | Solar_F1 | Line1 | TX1 | Battery Charger_MCR
[6 empty] | IS3Inv1M3 | O2RE7 |  | 1643.72 | 4.192% | 0 | Solar_F1 | Line1 | TX1 | IC_UPS
[6 empty] | IS3Inv1M4 | O2RE7 |  | 1627.915 | 4.152% | 0 | Solar_F1 | Line1 | TX1 | IC_Auxiliary Tranformer
[6 empty] | IS4Inv1M1 | O2RE27 |  | 1276 | 3.254% | 0 | Solar_F1 | Line1 | TX1 | IC_Auxiliary DB
[6 empty] | IS4Inv1M2 | O2RE27 |  | 1276 | 3.254% | 0 | Solar_F1 | Line1 | TX1 | IC_SCADA Panel
[6 empty] | IS4Inv1M3 | O2RE27 |  | 1276 | 3.254% | 0 | Solar_F1 | Line1 | TX1 | Connectors
[6 empty] | IS4Inv1M4 | O2RE27 |  | 1276 | 3.254% | 0 | Solar_F1 | Line1 | TX1 | Manual Stop
[6 empty] | IS4Inv2M1 | O2RE27 |  | 1276 | 3.254% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M2 | O2RE27 |  | 1276 | 3.254% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M3 | O2RE27 |  | 1276 | 3.254% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M4 | O2RE27 |  | 1276 | 3.254% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1 | O2RE7 |  | 4662.475 | 11.89% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2 | O2RE7 |  | 4662.475 | 11.89% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1 | O2RE7 |  | 6511.66 | 16.61% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2 | O2RE7 |  | 6495.855 | 16.57% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1 | O2RE7 |  | 6527.465 | 16.65% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1 | O2RE27 |  | 5104 | 13.02% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2 | O2RE27 |  | 5104 | 13.02% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M1SCB1 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M1SCB2 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M1SCB3 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M1SCB4 | O2RE7 |  | 266.22 | 0.679% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M1SCB5 | O2RE7 |  | 266.22 | 0.679% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M1SCB6 | O2RE7 |  | 266.22 | 0.679% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M1SCB7 | O2RE7 |  | 266.22 | 0.679% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M1SCB8 | O2RE7 |  | 266.22 | 0.679% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M1SCB9 | O2RE7 |  | 268.685 | 0.6852% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M2SCB1 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M2SCB2 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M2SCB3 | O2RE7 |  | 268.685 | 0.6852% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M2SCB4 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M2SCB5 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M2SCB6 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M2SCB7 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M2SCB8 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv1M2SCB9 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M1SCB1 | O2RE7 |  | 268.685 | 0.6852% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M1SCB2 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M1SCB3 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M1SCB4 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M1SCB5 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M1SCB6 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M1SCB7 | O2RE7 |  | 268.685 | 0.6852% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M1SCB8 | O2RE7 |  | 268.685 | 0.6852% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M1SCB9 | O2RE7 |  | 268.685 | 0.6852% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M2SCB1 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M2SCB2 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M2SCB3 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M2SCB4 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M2SCB5 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M2SCB6 | O2RE7 |  | 252.88 | 0.6449% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M2SCB7 | O2RE7 |  | 268.685 | 0.6852% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M2SCB8 | O2RE7 |  | 268.685 | 0.6852% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS1Inv2M2SCB9 | O2RE7 |  | 268.685 | 0.6852% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M1SCB1 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M1SCB2 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M1SCB3 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M1SCB4 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M1SCB5 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M1SCB6 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M2SCB1 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M2SCB2 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M2SCB3 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M2SCB4 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M2SCB5 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M2SCB6 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M3SCB1 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M3SCB2 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M3SCB3 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M3SCB4 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M3SCB5 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M3SCB6 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M4SCB1 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M4SCB2 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M4SCB3 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M4SCB4 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M4SCB5 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv1M4SCB6 | O2RE7 |  | 255.2 | 0.6509% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M1SCB1 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M1SCB2 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M1SCB3 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M1SCB4 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M1SCB5 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M1SCB6 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M2SCB1 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M2SCB2 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M2SCB3 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M2SCB4 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M2SCB5 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M2SCB6 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M3SCB1 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M3SCB2 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M3SCB3 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M3SCB4 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M3SCB5 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M3SCB6 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M4SCB1 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M4SCB2 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M4SCB3 | O2RE7 |  | 255.2 | 0.6509% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M4SCB4 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M4SCB5 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS2Inv2M4SCB6 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M1SCB1 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M1SCB2 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M1SCB3 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M1SCB4 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M1SCB5 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M1SCB6 | O2RE7 |  | 239.25 | 0.6102% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M2SCB1 | O2RE7 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M2SCB2 | O2RE7 |  | 255.2 | 0.6509% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M2SCB3 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M2SCB4 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M2SCB5 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M2SCB6 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M3SCB1 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M3SCB2 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M3SCB3 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M3SCB4 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M3SCB5 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M3SCB6 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M4SCB1 | O2RE7 |  | 287.1 | 0.7322% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M4SCB2 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M4SCB3 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M4SCB4 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M4SCB5 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS3Inv1M4SCB6 | O2RE7 |  | 271.15 | 0.6915% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M1SCB1 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M1SCB2 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M1SCB3 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M1SCB4 | O2RE27 |  | 221.27 | 0.5643% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M1SCB5 | O2RE27 |  | 221.27 | 0.5643% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M1SCB6 | O2RE27 |  | 221.27 | 0.5643% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M2SCB1 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M2SCB2 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M2SCB3 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M2SCB4 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M2SCB5 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M2SCB6 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M3SCB1 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M3SCB2 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M3SCB3 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M3SCB4 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M3SCB5 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M3SCB6 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M4SCB1 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M4SCB2 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M4SCB3 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M4SCB4 | O2RE27 |  | 239.25 | 0.6102% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M4SCB5 | O2RE27 |  | 207.35 | 0.5288% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv1M4SCB6 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M1SCB1 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M1SCB2 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M1SCB3 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M1SCB4 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M1SCB5 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M1SCB6 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M2SCB1 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M2SCB2 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M2SCB3 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M2SCB4 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M2SCB5 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M2SCB6 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M3SCB1 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M3SCB2 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M3SCB3 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M3SCB4 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M3SCB5 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M3SCB6 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M4SCB1 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M4SCB2 | O2RE27 |  | 191.4 | 0.4881% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M4SCB3 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M4SCB4 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M4SCB5 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | IS4Inv2M4SCB6 | O2RE27 |  | 223.3 | 0.5695% | 0 | Solar_F1 | Line1 | TX1
[6 empty] | Str_Typ1(545*29) |  |  | 15.805 | 0.04031% | 0
[6 empty] | Str_Typ2(550*29) |  |  | 15.95 | 0.04068% | 0
[6 empty] | Str_Typ1(545*58) |  |  | 31.61 | 0.08062% | 0
[6 empty] | Str_Typ2(550*58) |  |  | 31.9 | 0.08136% | 0
[6 empty] | Str_Typ2(550*58) |  |  |  | 0% | 0
[6 empty] | Tx |  |  |  | 0% | 0
[6 empty] | MVP |  |  |  | 0% | 0
[6 empty] | Aux_Tx |  |  |  | 0% | 0
[6 empty] | MCR_MVP_SolarF1 |  |  |  | 0% | 0
[6 empty] | MCR_MVP_SolarF2 |  |  |  | 0% | 0
[6 empty] | MCR_MVP_SolarF3 |  |  |  | 0% | 0
[6 empty] | MCR_MVP_SolarF4 |  |  |  | 0% | 0
[6 empty] | Power_Tx1 |  |  |  | 0% | 0
[6 empty] | Line_Bay1 |  |  |  | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0
[10 empty] | 0% | 0