## O2Summary
CEPPL_MH_Solar Performance Summary Solar
Month | 2025-07-01
Date | 2025-07-13
Operation Year | 2026
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks | CC*Bugt (Daily) | CC*Bugt (MTD) | CC*Bugt (YTD)
1 | E_Grid Daily (MWh) | 421.0618 | 418.32 | -0.6512% |  | 414.8431 | 5392.9598 | 57424.2319
| E_Grid MTD(MWh) | 5473.8036 | 4664.808 | -14.78%
| E_Grid YTD (MWh) | 65481.7377 | 50564.952 | -22.78%
2 | POA Daily | 3.7968 | 3.7726 | -0.638%
| POA MTD | 49.3581 | 43.2613 | -12.35%
| POA YTD | 626.2581 | 555.4021 | -11.31%
3 | PR Daily | 85.31% | 86.57% | 1.486%
| PR MTD | 85.31% | 84.19% | -1.312%
| PR YTD | 85.31% | 71.08% | -16.68%
4 | PA Daily | 99.5% | 100% | 0.5025%
| PA MTD | 99.5% | 99.21% | -0.2919%
| PA YTD | 99.5% | 98.61% | -0.8986%
5 | GA Daily | 99.5% | 100% | 0.5025% |  |  |  | 0
| GA MTD | 99.5% | 100% | 0.5025%
| GA YTD | 99.5% | 98.85% | -0.6573%
6 | CUF Daily | 13.5% | 13.41% | -0.6512%
| CUF MTD | 13.5% | 11.5% | -14.78%
| CUF YTD | 20.18% | 15.58% | -22.78%
Performance Summary CEPPL Solar
Month | 2025-07-01
Date | 2025-07-13
Operation Year | 2026
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
SPV | Particular | Target | Measured | Deviation | Remarks
O2R15 | E_Grid MTD(MWh) | 2273918.0173 | 1884191.4 | -17.14%
O2R17 | E_Grid MTD(MWh) | 338851.2841 | 272910.2 | -19.46%
O2R11 | E_Grid MTD(MWh) | 333655.5644 | 274240 | -17.81%
O2R6 | E_Grid MTD(MWh) | 134185.1085 | 110843.3 | -17.4%
O2R12 | E_Grid MTD(MWh) | 648787.2587 | 529524.6 | -18.38%
O2R14 | E_Grid MTD(MWh) | 1181913.279 | 1181441.7 | -0.0399%
O2R24 | E_Grid MTD(MWh) | 280117.0615 | 240288.4 | -14.22%
O2R26 | E_Grid MTD(MWh) | 282376.0701 | 263892.8 | -6.546%

## AnnualKPI
Till Date | 2025-07-13 | 2025-07-01
CEPPL_MH_Solar Performance Summary-YTD
Year | Days | Estimated POA(kWh/M2) | Measured POA(kWh/M2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Budgeted PR (MWh) | Measured PR(MWh)
2026 | 104 | 626.2581 | 555.4021 | 65481.7377 | 50564.952 | 20.18% | 15.58% | 99.5% | 98.85% | 99.5% | 98.61% | 85.31% | 71.08%

## MonthlyKPI
Till Date | 2025-07-13 | 0 | 0 | 0 | 0
CEPPL_MH_Solar Performance Summary Solar
Month | Days | Estimated POA(m/s) | Measured POA (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target PR (%) | Measured PR (%) | Measured WPR (%)
2025-07-01 | 13 | 49.3581 | 43.2613 | 5473.8036 | 4664.808 | 13.5% | 11.5% | 99.5% | 100% | 99.5% | 99.21% | 85.31% | 84.19%
Start Date | 2025-07-07
End Date | 2025-07-13
CEPPL_MH_Solar Performance Summary Solar
Month | Days | Estimated POA(m/s) | Measured POA (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target PR (%) | Measured PR (%) | Measured WPR (%)
2025-07-01 | 7 | 26.5774 | 21.9484 | 2947.4327 | 2446.416 | 13.5% | 11.2% | 99.5% | 100% | 99.5% | 99.92% | 85.31% | 87.03%
Formulas:
Days = [Days, row below]-6

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 11.55 | 6.9921 |  | 5.5478 | 0.89156 | 29.4285 | 36.84 | 0.778 | 2.109 | [7 empty] | 0% |  | 505955.5 |  |  |  | 97 | 6.9226 | 767701.1309 | 81.05% | 23.38% | 99.5% | 99.5% | [9 empty] | 136.82 | 544269.9145
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 11.5333 | 6.6753 |  | 5.2805 | 0.85919 | 30.2239 | 38.0702 | 0.96656 | 2.679 | 100% |  | 100% | 100% |  |  | 92.52% | 0% | 14.43% | 484660.8 | 476136 | 2232 | 473904 | 97 | 6.9226 | 767701.1309 | 81.05% | 23.38% | 99.5% | 99.5% | [9 empty] | 136.82 | 544269.9145
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 11.35 | 5.2572 |  | 4.1068 | 0.68373 | 31.0318 | 38.5221 | 0.9942 | 2.724 | 100% |  | 100% | 100% |  |  | 91.58% | 0% | 11.11% | 375616.8 | 367848 | 3024 | 364824 | 97 | 6.9226 | 767701.1309 | 81.05% | 23.38% | 99.5% | 99.5% | [9 empty] | 136.82 | 544269.9145
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 10.5667 | 2.214 | 0.402 | 1.68 | 0.274 | 30.348 | 37.568 | 0.666 | 1.692 | 100% |  | 100% | 100% |  |  | 102.9% | 0% | 5.372% | 165499.4 | 168840 | 1224 | 167616 | 97 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 529491.428
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 10.4167 | 4.0104 | 0.67438 | 3.0989 | 0.42088 | 28.2032 | 36.1443 | 1.4618 | 2.88 | 100% |  | 100% | 100% |  |  | 101% | 0% | 9.729% | 304616.6 | 306360 | 2808 | 303552 | 97 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 529491.428
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 10.0833 | 4.3914 | 0.74058 | 4.5551 | 0.5057 | 26.4906 | 34.0342 | 1.0991 | 2.952 | 94.76% |  | 100% | 100% |  |  | 73.5% | 0% | 10.52% | 336079.3 | 329904 | 1800 | 328104 | 98 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 534950.1025
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 11.9 | 6.643 | 1.1981 | 6.7137 | 0.77825 | 28.9812 | 37.3022 | 0.73128 | 2.955 | 100% |  | 100% | 100% |  |  | 84.57% | 0% | 18.2% | 581403.7 | 570456 | 2664 | 567792 | 100 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 545867.4516
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 11.8 | 6.9012 | 1.2699 | 7.0238 | 0.83066 | 30.6565 | 38.0926 | 0.82883 | 2.967 | 100% |  | 100% | 100% |  |  | 81.36% | 0% | 18.68% | 596774.3 | 585432 | 2520 | 582912 | 102 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 556784.8006
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 11.7833 | 7.1267 | 1.3176 | 7.2617 | 0.85638 | 32.571 | 39.887 | 0.92548 | 2.496 | 100% |  | 100% | 100% |  |  | 80.87% | 0% | 19.2% | 611640.7 | 601128 | 2160 | 598968 | 102 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 556784.8006
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 11.3667 | 7.1847 | 1.3356 | 7.3115 | 0.87372 | 33.6411 | 40.8465 | 1.025 | 2.88 | 100% |  | 100% | 100% |  |  | 80.65% | 0% | 19.28% | 616547 | 604080 | 2592 | 601488 | 102 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 556784.8006
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 11.8667 | 7.0545 | 1.3287 | 7.1952 | 0.88503 | 33.7987 | 41.1033 | 0.94429 | 2.934 | 99.91% |  | 100% | 100% |  |  | 80% | 0% | 18.82% | 601810.2 | 589536 | 2376 | 587160 | 102 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 556784.8006
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 11.75 | 6.223 | 1.2043 | 6.3737 | 0.80677 | 33.3011 | 43.2647 | 0.67708 | 2.496 | 100% |  | 100% | 100% |  |  | 82.25% | 0% | 17.14% | 548640.4 | 538344 | 3600 | 534744 | 102 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 556784.8006
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 11.85 | 6.8727 | 1.3101 | 7.0734 | 0.90686 | 34.8025 | 48.3812 | 1.3234 | 3.435 | 100% |  | 100% | 100% |  |  | 80.1% | 0% | 18.52% | 591491.9 | 579600 | 1656 | 577944 | 102 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 556784.8006
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 11.8667 | 6.9105 | 1.3229 | 7.0756 | 0.90305 | 32.8579 | 45.9562 | 1.4104 | 3.312 | 100% |  | 100% | 100% |  |  | 81.7% | 0% | 18.9% | 605068.8 | 592920 | 3312 | 589608 | 102 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 556784.8006
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 11.9667 | 6.9941 | 1.3165 | 7.1323 | 0.88439 | 30.363 | 44.855 | 1.3115 | 2.955 | 99.18% |  | 100% | 100% |  |  | 79.63% | 0% | 18.57% | 589858.6 | 581112 | 1800 | 579312 | 102 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 556784.8006
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 11.9833 | 7.1595 | 1.3927 | 7.2977 | 0.93396 | 31.3494 | 44.5878 | 1.2588 | 2.592 | 96.95% |  | 100% | 100% |  |  | 76.65% | 0% | 18.29% | 584026.6 | 573552 | 3024 | 570528 | 102 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 556784.8006
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 11.9167 | 7.1232 | 1.3867 | 7.252 | 0.94167 | 32.8941 | 47.3437 | 1.1613 | 2.4 | 97.55% |  | 100% | 100% |  |  | 77.02% | 0% | 18.8% | 601367.6 | 588528 | 2016 | 586512 | 105 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 573160.8241
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 7.0364 | 1.379 | 7.1475 | 0.92568 | 33.6956 | 47.2413 | 1.3765 | 2.874 | 97.48% |  | 100% | 100% |  |  | 76.21% | 0% | 18.33% | 586386.3 | 574488 | 2520 | 571968 | 105 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 573160.8241
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 11.5 | 6.3114 | 1.2429 | 6.4203 | 0.84144 | 33.8276 | 46.9843 | 1.0568 | 3.009 | 97.64% |  | 100% | 100% |  |  | 77.55% | 0% | 16.76% | 619396.8 | 525960 | 3168 | 522792 | 105 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 573160.8241
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 11.9333 | 7.073 | 1.398 | 7.149 | 0.928 | 34.167 | 45.873 | 1.072 | 2.58 | 99.92% |  | 100% | 100% |  |  | 78.63% | 0% | 18.92% | 604513 | 593208 | 2952 | 590256 | 105 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 573160.8241
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 11.95 | 6.26 | 1.248 | 6.322 | 0.774 | 34.081 | 45.521 | 1.167 | 3.117 | 100% |  | 100% | 100% |  |  | 78.83% | 0% | 16.77% | 548560.6 | 525384 | 2088 | 523296 | 105 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 573160.8241
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 12.0667 | 7.1535 | 1.4177 | 7.2034 | 0.94859 | 33.8542 | 45.8713 | 1.3137 | 3.183 | 100% |  | 100% | 100% |  |  | 80.57% | 0% | 19.53% | 586955.6 | 613224 | 3816 | 609408 | 105 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 573160.8241
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 12.0833 | 7.3982 | 1.4598 | 7.4408 | 0.9629 | 32.9205 | 44.9802 | 1.3652 | 2.991 | 100% |  | 100% | 100% |  |  | 80.8% | 0% | 20.23% | 600717.8 | 632880 | 1584 | 631296 | 105 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 573160.8241
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 12.1167 | 7.0362 | 1.3953 | 7.0777 | 0.94385 | 32.5143 | 44.5121 | 1.0995 | 2.457 | 100% |  | 100% | 100% |  |  | 84.06% | 0% | 20.02% | 566539.599 | 626904 | 2232 | 624672 | 105 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 573160.8241
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 12.1333 | 7.2762 | 1.4462 | 7.3124 | 0.97527 | 33.8944 | 46.2865 | 0.98781 | 2.265 | 98.71% |  | 100% | 100% |  |  | 80.39% | 0% | 19.78% | 581073.5 | 619632 | 2376 | 617256 | 105 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 573160.8241
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 12.1 | 7.2514 | 1.4547 | 7.2675 | 0.98195 | 34.5648 | 47.9862 | 0.99358 | 2.646 | 100% |  | 100% | 100% |  |  | 80.83% | 0% | 19.77% | 585076.1 | 618912 | 2088 | 616824 | 105 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 573160.8241
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 12.1833 | 6.9427 | 1.3974 | 6.9662 | 0.96717 | 34.5347 | 47.4384 | 1.0984 | 2.439 | 100% |  | 100% | 100% |  |  | 80.83% | 0% | 18.95% | 573442.2 | 593712 | 2448 | 591264 | 105 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 573160.8241
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 12.0833 | 7.0079 | 1.4078 | 7.0081 | 0.95771 | 34.7292 | 48.1038 | 1.0152 | 2.091 | 99.61% |  | 100% | 100% |  |  | 81.34% |  | 19.18% | 614346.7 | 601344 | 2808 | 598536 | 105 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 573160.8241
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 12.2167 | 4.9407 | 0.98833 | 4.944 | 0.74732 | 33.1989 | 43.4801 | 1.1836 | 3.045 | 100% |  | 100% | 100% |  |  | 85.09% |  | 14.16% | 452433.9 | 444384 | 2664 | 441720 | 105 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 573160.8241
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 12.1833 | 7.622 | 1.4941 | 7.5636 | 1.0114 | 33.3874 | 46.4294 | 0.83431 | 3.309 | 100% |  | 100% | 100% |  |  | 80.97% |  | 20.61% | 660179.3 | 646056 | 3024 | 643032 | 105 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 573160.8241
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 12.1667 | 7.3132 | 1.4423 | 7.2595 | 0.97668 | 34.4163 | 47.6686 | 0.93262 | 2.835 | 99.65% |  | 100% | 100% |  |  | 80.31% |  | 19.81% | 633561.1 | 620064 | 2088 | 617976 | 106 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 578619.4987
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 12.2 | 7.319 | 1.45 | 7.25 | 0.973 | 34.659 | 46.444 | 1.127 | 3.234 | 99.21% |  | 100% | 100% |  |  | 80.23% |  | 19.76% | 584773.3 | 620136 | 3600 | 616536 | 106 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 578619.4987
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 12.35 | 7.1731 | 1.417 | 7.1097 | 0.95907 | 34.7804 | 46.7997 | 1.3726 | 3.303 | 99.4% |  | 100% | 100% |  |  | 80.78% |  | 19.51% | 622453.6 | 612072 | 3312 | 608760 | 106 | 7.14 | 709627.687 | 76.45% | 22.74% | 99.5% | 99.5% | [9 empty] | 130 | 578619.4987
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 12.25 | 6.7727 | 1.322 | 6.7944 | 1.0523 | 34.348 | 45.5616 | 1.051 | 3.069 | 99.99% |  | 100% | 100% |  |  | 84.33% |  | 19.47% | 618886.1 | 608256 | 936 | 607320 | 106 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 589118.3606
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 12.1167 | 6.5467 | 1.2694 | 6.6065 | 1.0282 | 35.0263 | 46.8323 | 1.2342 | 3.351 | 100% |  | 100% | 100% |  |  | 83.85% |  | 18.82% | 601298.5 | 589968 | 2808 | 587160 | 106 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 589118.3606
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 12.2833 | 6.7389 | 1.3063 | 6.6289 | 1.0335 | 34.2362 | 45.0506 | 1.3777 | 3.138 | 99.32% |  | 100% | 100% |  |  | 81.32% |  | 18.31% | 585677.8 | 573624 | 2232 | 571392 | 106 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 589118.3606
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 12.3167 | 7.0226 | 1.3585 | 6.9749 | 1.0808 | 32.2476 | 44.4579 | 1.211 | 3.534 | 99.41% |  | 100% | 100% |  |  | 83.36% |  | 19.75% | 640105 | 619200 | 2880 | 616320 | 106 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 589118.3606
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 12.9667 | 6.6342 | 1.2551 | 6.5434 | 4.0192 | 32.4776 | 44.325 | 1.1245 | 3.901 | 100% |  | 100% | 100% |  |  | 85.87% |  | 19.09% | 610385.8 | 597960 | 2376 | 595584 | 106 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 589118.3606
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 11.65 | 6.5115 | 1.1526 | 6.6249 | 0.91384 | 28.0598 | 40.5136 | 1.3462 | 5.874 | 100% |  | 100% | 100% |  |  | 85.77% |  | 19.3% | 612105.7 | 604368 | 2088 | 602280 | 106 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 589118.3606
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 12.4167 | 6.925 | 1.198 | 6.8325 | 0.9555 | 26.634 | 39.8195 | 1.1695 | 4.155 | 98.47% |  | 100% | 100% |  |  | 84.88% |  | 19.7% | 627970 | 616392 | 1656 | 614736 | 106 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 589118.3606
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 11.7167 | 1.6429 | 1.6258 | 2.8004 | 1.542 | 27.1844 | 36.659 | 0.7696 | 1.938 | 100% |  | 100% | 100% |  |  | 94.46% |  | 9.411% | 395098.7 | 296424 | 2808 | 293616 | 111 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 616906.9625
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 12.3333 | 6.497 | 3.7762 | 6.3926 | 0.91157 | 30.2397 | 44.219 | 0.90263 | 2.6655 | 95.49% |  | 100% | 100% |  |  | 78.51% |  | 17.85% | 570517.1 | 559512 | 2448 | 557064 | 111 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 616906.9625
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 12.4 | 6.6509 | 1.2471 | 6.6143 | 0.93745 | 31.3122 | 44.3363 | 1.2217 | 3.5745 | 100% |  | 100% | 100% |  |  | 82.48% |  | 19.41% | 618413.7 | 608328 | 2736 | 605592 | 111 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 616906.9625
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 12.4 | 5.0196 | 3.0195 | 5.0238 | 0.72552 | 30.5298 | 42.3628 | 0.98827 | 4.095 | 100% |  | 100% | 100% |  |  | 82.96% |  | 14.83% | 474902.9 | 465840 | 3240 | 462600 | 111 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 616906.9625
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 12.4 | 5.0979 | 0.92995 | 5.1502 | 0.73254 | 30.7463 | 42.6175 | 1.2086 | 3.768 | 100% |  | 100% | 100% |  |  | 82.86% |  | 15.18% | 480784 | 476784 | 3096 | 473688 | 111 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 616906.9625
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 12.4 | 3.453 | 0.60198 | 3.3404 | 0.4679 | 30.3873 | 40.3008 | 1.1788 | 1.9894 | 100% |  | 100% | 100% |  |  | 87.03% |  | 10.34% | 332749.4 | 326160 | 3456 | 322704 | 111 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 616906.9625
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 12.4 | 4.5428 | 0.79799 | 4.3418 | 0.59314 | 31.3817 | 42.7561 | 1.2687 | 2.463 | 100% |  | 100% | 100% |  |  | 85.13% |  | 13.5% | 415627.2 | 423864 | 2520 | 421344 | 114 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 633580.1237
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 12.9 | 4.2141 | 0.75504 | 4.1261 | 0.56931 | 29.971 | 40.7128 | 1.3424 | 5.736 | 100% |  | 100% | 100% |  |  | 83.26% |  | 12.55% | 388249 | 394632 | 3024 | 391608 | 114 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 633580.1237
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 12.9 | 4.7998 | 0.72242 | 4.7412 | 0.63962 | 29.7455 | 40.6824 | 1.2141 | 4.6815 | 97.5% |  | 100% | 100% |  |  | 84.06% |  | 14.56% | 462903.8 | 457056 | 2736 | 454320 | 114 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 633580.1237
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 12.9 | 4.5853 | 0.66042 | 4.3352 | 0.57112 | 29.745 | 40.6404 | 1.2006 | 4.58 | 100% |  | 100% | 100% |  |  | 120% |  | 19% | 606789.7 | 594432 | 1584 | 592848 | 114 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 633580.1237
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 12.9 | 5.8417 | 1.063 | 5.7215 | 0.80573 | 30.9097 | 44.7896 | 1.301 | 6.189 | 99.12% |  | 100% | 100% |  |  | 87.37% |  | 18.27% | 582603.2 | 571536 | 1656 | 569880 | 114 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 633580.1237
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 12.9 | 5.4376 | 0.97585 | 5.3824 | 0.73666 | 31.4078 | 44.8804 | 1.1423 | 4.5195 | 99.31% |  | 100% | 100% |  |  | 82% |  | 16.69% | 540174.1 | 523728 | 2952 | 520776 | 118 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 655811.0052
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 12.9 | 4.4093 | 0.74484 | 4.2949 | 0.55377 | 30.9829 | 41.9812 | 0.94515 | 2.3985 | 100% |  | 100% | 100% |  |  | 86.45% |  | 14.04% | 447367.6 | 441288 | 3168 | 438120 | 118 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 655811.0052
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 12.9 | 5.0689 | 0.74667 | 4.9382 | 0.5425 | 28.7525 | 40.3333 | 1.0779 | 5.6595 | 95.55% |  | 100% | 100% |  |  | 79.98% |  | 14.94% | 474566.3 | 467928 | 1872 | 466056 | 118 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 655811.0052
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 12.5333 | 6.3729 | 0.87287 | 6.2421 | 0.66507 | 27.7276 | 40.7386 | 0.91529 | 3.4965 | 95.34% |  | 100% | 100% |  |  | 76.22% |  | 17.99% | 568018.2 | 563472 | 2088 | 561384 | 118 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 655811.0052
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 11.35 | 2.6958 | 0.37131 | 2.6424 | 0.29558 | 28.2237 | 37.2486 | 0.70151 | 2.0325 | 95.85% |  | 100% | 100% |  |  | 86.57% |  | 8.652% | 285555.5 | 273240 | 3312 | 269928 | 118 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 655811.0052
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 12.1167 | 3.6094 | 0.5133 | 3.5203 | 0.39292 | 27.9237 | 37.9246 | 0.89796 | 2.2845 | 93.61% |  | 100% | 100% |  |  | 83.15% |  | 11.07% | 352565.5 | 348696 | 3312 | 345384 | 118 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 655811.0052
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 11.85 | 1.9566 | 0.24762 | 1.9298 | 0.19268 | 26.6808 | 34.0427 | 0.83719 | 2.3865 | 95.56% |  | 100% | 100% |  |  | 82.53% |  | 6.162% | 198709.1 | 195120 | 2880 | 192240 | 120.7 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 670816.8502
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 12.2667 | 7.0423 | 0.91303 | 6.7432 | 0.69533 | 29.609 | 43.1248 | 0.63662 | 5.3175 | 95.39% |  | 100% | 100% |  |  | 75.4% |  | 19.67% | 627850 | 617976 | 4248 | 613728 | 120.7 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 670816.8502
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 12.6167 | 5.773 | 0.83937 | 5.5894 | 0.6396 | 29.6846 | 40.7387 | 1.4353 | 4.8105 | 97.47% |  | 100% | 100% |  |  | 79.88% |  | 17.27% | 551703.4 | 540864 | 1944 | 538920 | 120.7 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 670816.8502
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 11.4333 | 2.6982 | 0.34551 | 2.6786 | 0.25624 | 26.1144 | 34.7347 | 1.2448 | 3.1275 | 97.63% |  | 100% | 100% |  |  | 84.25% |  | 8.73% | 278512.5 | 275112 | 2736 | 272376 | 120.7 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 670816.8502
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 12.45 | 5.5338 | 0.77424 | 5.3924 | 0.5901 | 29.995 | 42.43 | 1.4937 | 3.3105 | 97.41% |  | 100% | 100% |  |  | 77.2% |  | 16.11% | 516298.6 | 505296 | 2808 | 502488 | 120.7 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 670816.8502
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 12.4 | 5.5909 | 0.82703 | 5.3922 | 0.63643 | 30.6256 | 41.2444 | 1.6668 | 3.2745 | 97.48% |  | 100% | 100% |  |  | 79.19% |  | 16.52% | 526650.9 | 518688 | 3312 | 515376 | 120.7 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 670816.8502
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 12.8333 | 7.2675 | 1.1055 | 7.0124 | 0.86184 | 31.2695 | 43.5274 | 1.8753 | 3.8775 | 97.42% |  | 100% | 100% |  |  | 77.37% |  | 20.99% | 668786.2 | 657144 | 2304 | 654840 | 120.7 | 6.8903 | 722503.6498 | 80.66% | 23.16% | 99.5% | 99.5% | [9 empty] | 130 | 670816.8502
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 12.7667 | 6.7692 | 1.0382 | 6.4937 | 0.80636 | 31.0933 | 45.2488 | 1.7245 | 3.831 | 42.26% |  | 40.53% | 40.53% |  |  | 33.76% |  | 8.481% | 273977.5 | 264600 | 0 | 264600 | 120.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 505129.199
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 12.6667 | 7.0219 | 1.0899 | 6.7174 | 0.87432 | 31.057 | 44.3801 | 1.6665 | 3.2985 | 100% |  | 100% | 100% |  |  | 74.91% |  | 19.47% | 652977.2 | 640152 | 32760 | 607392 | 120.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 505129.199
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 12.65 | 6.5986 | 1.0415 | 6.2994 | 0.83345 | 30.8851 | 42.5264 | 1.7957 | 3.651 | 100% |  | 100% | 100% |  |  | 78.35% |  | 19.41% | 619614.7 | 608184 | 2592 | 605592 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 12.65 | 6.5699 | 1.0372 | 6.2918 | 0.83294 | 30.282 | 43.5838 | 1.1871 | 3.249 | 100% |  | 100% | 100% |  |  | 76.28% |  | 18.87% | 602941.2 | 591768 | 2880 | 588888 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 12.5333 | 6.5917 | 1.027 | 6.2965 | 0.83163 | 29.9098 | 43.464 | 0.98652 | 2.9355 | 100% |  | 100% | 100% |  |  | 81.36% |  | 20.15% | 643766.5 | 631152 | 2592 | 628560 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 12.4833 | 6.5675 | 1.0512 | 6.2743 | 3.6135 | 32.0074 | 44.2845 | 1.2471 | 2.8215 | 100% |  | 100% | 100% |  |  | 80.81% |  | 19.94% | 637487 | 625176 | 3024 | 622152 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 12.6 | 6.193 | 0.99153 | 5.9321 | 0.8091 | 32.8176 | 45.4297 | 1.4968 | 3.0585 | 100% |  | 100% | 100% |  |  | 80.76% |  | 18.84% | 615552.7 | 590112 | 2304 | 587808 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 12.6167 | 6.6092 | 1.0601 | 6.3259 | 0.85359 | 32.8708 | 45.3862 | 1.8951 | 3.438 | 100% |  | 100% | 100% |  |  | 79.64% |  | 19.81% | 633360.1 | 620784 | 2592 | 618192 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 12.75 | 6.8832 | 1.1205 | 6.8251 | 0.89521 | 33.1254 | 45.1702 | 2.386 | 4.245 | 100% |  | 100% | 100% |  |  | 76.98% |  | 20.66% | 656717.7 | 647496 | 2808 | 644688 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 12.7 | 5.7528 | 0.99789 | 6.5442 | 0.79912 | 33.0934 | 45.1397 | 2.1302 | 3.885 | 99.8% |  | 100% | 100% |  |  | 73.2% |  | 18.84% | 601532.5 | 590184 | 2376 | 587808 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 12.2167 | 3.3668 | 0.59826 | 3.8329 | 0.47268 | 30.429 | 39.887 | 1.9158 | 3.5205 | 100% |  | 100% | 100% |  |  | 76.82% |  | 11.58% | 368807.7 | 363888 | 2592 | 361296 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 11.9 | 5.2332 | 0.91361 | 5.9467 | 0.7351 | 29.1159 | 40.7362 | 1.3828 | 6.6585 | 98.81% |  | 100% | 100% |  |  | 75.03% |  | 17.55% | 562363.2 | 551016 | 3528 | 547488 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 12.6167 | 4.5868 | 0.52536 | 5.9436 | 0.37297 | 17.9023 | 25.8494 | 0.51123 | 2.3205 | 98.92% |  | 100% | 100% |  |  | 83.11% |  | 19.43% | 627054.4 | 609840 | 3744 | 606096 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 12.6 | 5.2344 | 0.98105 | 6.8713 | 0.71467 | 30.9354 | 44.8542 | 0.81648 | 4.221 | 100% |  | 100% | 100% |  |  | 68.52% |  | 18.52% | 589602.4 | 582480 | 4752 | 577728 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 12.1 | 5.2119 | 0.96393 | 6.8341 | 0.68744 | 30.2926 | 44.8827 | 1.1508 | 3.342 | 100% |  | 100% | 100% |  |  | 62.08% |  | 16.68% | 531218.1 | 523152 | 2592 | 520560 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 12.9 | 4.8223 | 0.77235 | 5.4329 | 0.62351 | 28.9854 | 41.1083 | 1.0358 | 3.702 | 100% |  | 100% | 100% |  |  | 72.47% |  | 15.48% | 494068.4 | 486792 | 3672 | 483120 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 12.6333 | 5.7466 | 0.97706 | 6.3339 | 0.76304 | 30.3234 | 43.0217 | 1.604 | 4.3785 | 100% |  | 100% | 100% |  |  | 75.19% |  | 18.73% | 597921.7 | 588168 | 3816 | 584352 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 12.4833 | 3.5445 | 0.60834 | 3.9411 | 0.48999 | 29.4328 | 39.1769 | 1.7928 | 4.044 | 100% |  | 100% | 100% |  |  | 79.34% |  | 12.3% | 390585.4 | 387144 | 3456 | 383688 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 12.6667 | 3.4232 | 0.58472 | 3.8326 | 0.47186 | 27.0845 | 36.2962 | 1.6486 | 4.8765 | 100% |  | 100% | 100% |  |  | 80.79% |  | 12.18% | 387344.2 | 383832 | 3888 | 379944 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 12.6667 | 6.0915 | 1.0516 | 6.6175 | 0.84539 | 29.6013 | 41.2547 | 2.0491 | 4.6845 | 100% |  | 100% | 100% |  |  | 76.11% |  | 19.81% | 631571.8 | 621504 | 3528 | 617976 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 12.5 | 4.8533 | 0.8424 | 5.3593 | 0.68393 | 29.1858 | 39.9422 | 1.9041 | 4.5525 | 100% |  | 100% | 100% |  |  | 78.98% |  | 16.65% | 531074.2 | 523368 | 4032 | 519336 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 12.4 | 2.7059 | 0.4766 | 3.0655 | 0.384 | 28.7005 | 37.4056 | 1.8766 | 4.479 | 100% |  | 100% | 100% |  |  | 86.58% |  | 10.44% | 331283.3 | 328464 | 2808 | 325656 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 2.7141 | 0.47811 | 3.0971 | 0.38046 | 27.9111 | 36.7475 | 1.8272 | 4.6605 | 100% |  | 100% | 100% |  |  | 86.26% |  | 10.51% | 333237.3 | 330984 | 3168 | 327816 | 122.7 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 513499.194
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 11.8667 | 1.4412 | 0.24974 | 1.6486 | 0.20363 | 26.247 | 32.7328 | 1.0584 | 3.48 | 100% |  | 39.45% | 39.45% |  |  | 33.94% |  | 2.245% | 74503.2 | 74664 | 4608 | 70056 | 125.2 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 523961.6878
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 12.2333 | 2.7174 | 0.46288 | 3.0751 | 0.37644 | 27.2072 | 35.7354 | 1.0114 | 3.1095 | 100% |  | 100% | 100% |  |  | 82.35% |  | 10.25% | 324816.7 | 322560 | 2736 | 319824 | 126.3 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 528565.1851
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 12.0167 | 1.3216 | 0.20202 | 1.5239 | 0.21145 | 25.6335 | 31.2687 | 1.0771 | 3.018 | 100% |  | 100% | 100% |  |  | 78.97% |  | 4.872% | 155419.9 | 156240 | 4248 | 151992 | 126.3 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 528565.1851
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 12.25 | 4.4129 | 0.69915 | 4.845 | 0.56129 | 27.7739 | 39.2121 | 1.2009 | 3.2265 | 98.46% |  | 100% | 100% |  |  | 79.13% |  | 15.52% | 495286.6 | 487728 | 3528 | 484200 | 126.3 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 528565.1851
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 11.8167 | 4.097 | 0.65818 | 4.475 | 0.53023 | 27.736 | 37.9305 | 1.3515 | 3.414 | 100% |  | 100% | 100% |  |  | 79.89% |  | 14.47% | 461152.8 | 454968 | 3456 | 451512 | 126.3 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 528565.1851
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 11.9667 | 2.4143 | 0.39063 | 2.6657 | 0.32433 | 26.2095 | 33.7519 | 1.6407 | 4.9095 | 99.9% |  | 100% | 100% |  |  | 82.74% |  | 8.928% | 283345.4 | 282096 | 3528 | 278568 | 126.3 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 528565.1851
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 12.3167 | 2.615 | 0.43169 | 2.9608 | 0.34034 | 27.0483 | 35.1607 | 1.2229 | 3.3585 | 99.88% |  | 100% | 100% |  |  | 84.32% |  | 10.25% | 326124.8 | 323568 | 3816 | 319752 | 128.08 | 4.97 | 544049.6758 | 84.21% | 17.44% | 99.5% | 99.5% | [9 empty] | 130 | 536014.4806
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | 12.2833 | 3.1193 | 0.52606 | 3.5154 | 0.43491 | 27.0607 | 36.0563 | 1.7952 | 4.5915 | 99.92% |  | 100% | 100% |  |  | 82.16% |  | 11.86% | 377116 | 373680 | 3744 | 369936 | 128.08 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 414843.0596
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | 12.7833 | 3.796 | 0.64314 | 4.206 | 0.54071 | 26.9902 | 36.2565 | 1.6883 | 3.8325 | 97.95% |  | 100% | 100% |  |  | 80.81% |  | 13.95% | 443864.6 | 438696 | 3384 | 435312 | 128.08 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 414843.0596
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | 12.5833 | 3.7906 | 0.63615 | 4.2448 | 0.51341 | 26.9746 | 36.8039 | 1.0506 | 3.3195 | 100% |  | 100% | 100% |  |  | 83.01% |  | 14.46% | 460516.8 | 454752 | 3456 | 451296 | 128.08 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 414843.0596
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | 12.3667 | 2.9782 | 0.50634 | 3.385 | 0.41029 | 27.0222 | 36.258 | 1.2928 | 3.231 | 99.56% |  | 100% | 100% |  |  | 83.04% |  | 11.54% | 366784.3 | 363600 | 3600 | 360000 | 128.08 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 414843.0596
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | 12.45 | 2.7211 | 0.45757 | 3.0826 | 0.37991 | 26.4172 | 34.8541 | 0.98163 | 4.3305 | 97.36% |  | 100% | 100% |  |  | 78.14% |  | 9.888% | 315070.4 | 311976 | 3456 | 308520 | 128.08 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 414843.0596
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | 12.6167 | 2.5539 | 0.41116 | 2.8792 | 0.36957 | 25.9245 | 33.7263 | 1.2283 | 3.609 | 95.51% |  | 100% | 100% |  |  | 79.54% |  | 9.402% | 299305.3 | 296928 | 3600 | 293328 | 128.08 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 414843.0596
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | 12.1333 | 1.5646 | 0.24905 | 1.7787 | 0.2173 | 25.0946 | 31.1982 | 1.2582 | 3.207 | 99.87% |  | 100% | 100% |  |  | 85.18% |  | 6.219% | 197441.9 | 197568 | 3528 | 194040 | 128.08 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 414843.0596
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | 12.05 | 1.6904 | 0.25764 | 1.9325 | 0.2331 | 25.1596 | 31.2248 | 0.93158 | 1.98 | 99.78% |  | 100% | 100% |  |  | 89.71% |  | 7.117% | 226127 | 225792 | 3744 | 222048 | 128.08 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 414843.0596
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | 11.75 | 1.8882 | 0.2855 | 2.1368 | 0.26785 | 25.1703 | 31.4236 | 0.91581 | 2.337 | 100% |  | 100% | 100% |  |  | 88.79% |  | 7.788% | 247307.5 | 246600 | 3600 | 243000 | 128.08 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 414843.0596
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | 11.8333 | 2.2321 | 0.35533 | 2.5245 | 0.29586 | 26.1789 | 34.2672 | 0.76077 | 1.755 | 100% |  | 100% | 100% |  |  | 86.29% |  | 8.942% | 284479.2 | 283176 | 4176 | 279000 | 128.08 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 414843.0596
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | 12.7333 | 5.6987 | 0.94672 | 5.6533 | 0.76291 | 27.8477 | 40.4954 | 1.1098 | 3.0285 | 99.78% |  | 100% | 100% |  |  | 83.36% |  | 19.35% | 617373.6 | 606600 | 3024 | 603576 | 128.08 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 414843.0596
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | 12.6833 | 4.1837 | 0.71307 | 4.15 | 0.58509 | 27.784 | 38.3107 | 1.4762 | 2.976 | 100% |  | 100% | 100% |  |  | 91.52% |  | 15.59% | 496370.6 | 489384 | 2952 | 486432 | 128.08 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 414843.0596
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | 12.5167 | 3.461 | 0.60713 | 3.7726 | 0.49891 | 27.4671 | 37.1035 | 1.5939 | 3.3015 | 100% |  | 100% | 100% |  |  | 86.57% |  | 13.41% | 425575.2 | 420984 | 2664 | 418320 | 128.08 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 414843.0596
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [16 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [16 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [16 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [16 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [16 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [16 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [16 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [16 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [16 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [16 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [16 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [16 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [16 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [16 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [16 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 |  |  | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 |  |  | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | 0 | [17 empty] | 0 | 0 |  |  | 0 | 3.7968 | 421061.8187 | 85.31% | 13.5% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 |  |  | 0 | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 |  |  | 0 | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 |  |  | 0 | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 |  |  | 0 | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 |  |  | 0 | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 |  |  | 0 | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | 0 | [17 empty] | 0 | 0 |  |  | 0 | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130 | 0
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 3.9839 | 442502.1574 | 85.44% | 14.18% | 99.5% | 99.5% | [9 empty] | 130
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0167 | 549869.3244 | 84.31% | 17.62% | 99.5% | 99.5% | [9 empty] | 130
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.8258 | 635344.2761 | 83.89% | 20.36% | 99.5% | 99.5% | [9 empty] | 130
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.5833 | 618179.8754 | 85.17% | 19.81% | 99.5% | 99.5% | [9 empty] | 130
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.329 | 595399.7919 | 85.94% | 19.08% | 99.5% | 99.5% | [9 empty] | 130
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.5161 | 613939.4922 | 85.61% | 19.68% | 99.5% | 99.5% | [9 empty] | 130
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.3107 | 682247.6602 | 83.16% | 21.87% | 99.5% | 99.5% | [9 empty] | 130
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.9226 | 725267.6966 | 80.59% | 23.25% | 99.5% | 99.5% | [9 empty] | 130
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Input_Raw
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 |  |  |  |  | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159
[121 empty] | 70.5988 | 6.1 | 0 | 5.7 | [6 empty] | 0.15 | 159985.6064 | 10459.66 | 29.6551 | 51.368 | 316.1287 | 267.3
[7 empty] | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R15 | O2R11 | O2R11 | O2R11 | O2R11 | O2R17 | O2R17 | O2R17 | O2R17 | O2R6 | O2R6 | O2R12 | O2R12 | O2R12 | O2R12 | O2R12 | O2R12 | O2R12 | O2R12 | O2R14 | O2R14 | O2R14 | O2R14 | O2R14 | O2R14 | O2R14 | O2R14 | O2R14 | O2R14 | O2R14 | O2R14 | O2R24 | O2R24 | O2R24 | O2R24 | O2R26 | O2R26 | O2R26 | O2R26 | O2R14 | O2R14 | O2R14 | O2R14 | 74: O2R14; 75: O2R14; 76: O2R14; 77: O2R14; 118: Meter Readings
Date | Finacial Year | Calendor Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | IS1Inv1M1 | IS1Inv1M2 | IS1Inv1M3 | IS1Inv1M4 | IS1Inv2M1 | IS1Inv2M2 | IS1Inv2M3 | IS1Inv2M4 | IS2Inv1M1 | IS2Inv1M2 | IS2Inv1M3 | IS2Inv1M4 | IS2Inv2M1 | IS2Inv2M2 | IS2Inv2M3 | IS2Inv2M4 | IS3Inv1M1 | IS3Inv1M2 | IS3Inv2M1 | IS3Inv2M2 | IS4Inv1M1 | IS4Inv1M2 | IS4Inv2M1 | IS4Inv2M2 | IS4Inv3M1 | IS4Inv3M2 | IS4Inv4M1 | IS4Inv4M2 | IS5Inv1M1 | IS5Inv1M2 | IS5Inv2M1 | IS5Inv2M2 | IS6Inv1M1 | IS6Inv1M2 | IS6Inv2M1 | IS6Inv2M2 | IS7Inv1M1 | IS7Inv2M1 | IS8Inv1M1 | IS8Inv1M2 | IS8Inv1M3 | IS8Inv1M4 | IS9Inv1M1 | IS9Inv1M2 | IS9Inv2M1 | IS9Inv2M2 | IS10Inv1M1 | IS10Inv1M2 | IS10Inv2M1 | IS10Inv2M2 | IS10Inv3M1 | IS10Inv3M2 | IS10Inv4M1 | IS10Inv4M2 | IS11Inv1M1 | IS11Inv1M2 | IS11Inv1M3 | IS11Inv1M4 | IS12Inv1M1 | IS12Inv1M2 | IS12Inv1M3 | IS12Inv1M4 | IS13Inv1M1 | IS13Inv1M2 | IS13Inv2M1 | IS13Inv2M2 | IS14Inv1M1 | IS14Inv1M2 | IS14Inv1M3 | IS14Inv1M4 | IS14Inv2M1 | IS14Inv2M2 | IS14Inv2M3 | IS14Inv2M4 | IS1POA1 (KWh/m2) | IS7POA2 (KWh/m2) | IS1GHI1 (KWh/m2) | IS7GHI2 (KWh/m2) | IS1POA_BS1 (KWh/m2) | IS7POA_BS2 (KWh/m2) | IS1GHI_BS1 (KWh/m2) | IS1GHI_BS1 (KWh/m2)2 | IS1AT1 (°C) | IS7AT2 (°C) | IS1MT1 (°C) | IS7MT2 (°C) | IS1RH1 (%) | IS7RH2 (%) | IS1Rain1 (mm) | IS7Rain2 (mm) | WS_Solar1_Avg (m/s) | IS7_WS_Solar1_Avg (m/s) | WS_Solar1_Max (m/s) | IS7_WS_Solar1_Max (m/s) | Avg POA (KWh/m2) | Avg GHI (KWh/m2) | Avg POA_BS (KWh/m2) | Avg GHI_BS (KWh/m2) | Avg AT (°C) | Avg MT (°C) | Avg RH (%) | Avg Rain (mm) | WS_Solar Avg (m/s) | WS_Solar_Max (m/s) | O2R15 | O2R6 | O2R11 | O2R12 | O2R17 | O2R14 | O2R24 | O2R26 | Inv Total Gneration (MWh) | 33 kV_F3_Ex Incomer1 | 34 kV_F3_Im Incomer1 | 33 kV_F4_Ex Incomer2 | 34 kV_F4_Im Incomer2 | 33 kV_F5_Ex Incomer3 | 34 kV_F5_Im Incomer3 | 33 kV_F6_Ex Incomer4 | 33 kV_F6_Im Incomer4 | 33 kV_F7_Ex Incomer5 | 33 kV_F7_Im Incomer5 | 33 kV_Aux Trafo | 33kV_OG1_Ex_ | 33kV_OG1_Im | 132kV_TX1_EX | 132 kV_Tx1_Im | 132kV_L1_Ex | 132kV_L1_Im | 33 kV_F3_Ex (kWh) | 33 kV_F3_Im (kWh) | 33 kV_F4_Ex (kWh) | 33 kV_F4_Im (kWh) | 33 kV_F5_Ex (kWh) | 33 kV_F5_Im (kWh) | 33 kV_F6_Ex (kWh) | 33 kV_F6_Im (kWh) | 33 kV_F7_Ex (kWh) | 33 kV_F7_Im (kWh) | 33 kV_Aux Trafo_Im (kWh) | 33kV_OG1_Ex (MWh) | 33kV_OG1_Im (MWh) | 132kV_TX1_Ex(MWh) | 132kV_TX1_Im(MWh) | 132kV_L1_Ex(MWh) | 132kV_L1_Im(MWh) | 33kV_Ex(MWh) | 33kV_Net_Ex (MWh) | 132kV_Net_Ex (MWh)\ | AC System Loss(%) | Solar Operating Hours | Connected DC Capcity (MWp) | E_AC (WPR) | E_DC (WPR) | WPR (%)
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 6:42 | 18:15 | 8339.7 | 8248.8 | 7719.3 | 7619.9 | 7857.5 | 8179.8 | 7713.2 | 8719.6 | 8058.4 | 7768.8 | 8109.4 | 8109.3 | 8340.9 | 8149.2 | 8324.6 | 8161.3 | 11093 | 12491 | 11071.6 | 11673.3 | 12083.6 | 7449.7 | 11431.4 | 11400.8 | 10844.9 | 11237 | 11365.8 | 11421.2 | 9372.8 | 9558.6 | 9202.1 | 9281.4 | 9352.3 | 9706.9 | 9517.2 | 9400.5 | 7652.7 | 7695 | 7734.3 | 7604.3 | 7885.8 | 7754.8 | 10510.4 | 11943.2 | 8752.4 | 10655.6 | 10577.8 | 6785.7 | 6813.4 | 10587.4 | 8345.2 | 9089.2 | 9135.7 | 3159.6 | 1178 | 869 | 5994.4 | 6856.8 | [16 empty] | 5.5478 |  | 6.9921 |  | 0.89156 |  |  |  | 29.4285 |  | 36.84 |  | 23.8741 |  | 0 |  | 0.778 |  | 2.109 |  | 5.5478 | 6.9921 | 0.89156 |  | 29.4285 | 36.84 | 23.8741 |  | 0.778 | 2.109 | 262983 | 15347.7 | 37414.9 | 72840.8 | 37976.9 | 79392.2 | 0 | 0 | 505955.5 | 34503.8 | 194.9 | 29377.8 | 208.3 | 33403.8 | 373.2 | 2696.5 | 11.6 |  |  | 82.52 | 100763295 | 834286.656 | 992.88 | 95164 | 139813 | 1654.4 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! |  |  | 11.55 | 97 | Moving cloudy weather.
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 6:39 | 18:11 | 7963.4 | 7911 | 7371.5 | 7304.9 | 7474.2 | 7760.6 | 7367.2 | 8345.4 | 7740.9 | 7426.3 | 7786.6 | 7806.4 | 8001.5 | 7770.1 | 7947.8 | 7787.9 | 10559.9 | 11925 | 10539 | 11084.1 | 11509.6 | 7090.6 | 10906 | 10976.8 | 10310 | 10687 | 10841.5 | 10901.9 | 8914.1 | 9214.1 | 8763 | 8844.3 | 8886.5 | 9213.6 | 9027 | 8927.8 | 7275.3 | 7317.4 | 7418.7 | 7238.6 | 7563 | 7377.4 | 10013 | 11495 | 8357 | 10143 | 10108.4 | 6861.4 | 8068.1 | 10185.3 | 7915.4 | 8551 | 8615 | 2974.8 | 1103.5 | 813 | 6023.9 | 6355.1 | [16 empty] | 5.2805 |  | 6.6753 |  | 0.85919 |  |  |  | 30.2239 |  | 38.0702 |  | 21.0317 |  | 0 |  | 0.96656 |  | 2.679 |  | 5.2805 | 6.6753 | 0.85919 |  | 30.2239 | 38.0702 | 21.0317 |  | 0.96656 | 2.679 | 251097.1 | 14592.7 | 35735.5 | 69605.7 | 36054.9 | 77574.9 | 0 | 0 | 484660.8 | 34630.2 | 195.3 | 29498.1 | 208.6 | 33557.6 | 373.8 | 2773.4 | 11.9 |  |  | 82.78 | 101241118 | 835956.608 | 995.088 | 95640 | 140474.3 | 1657.5 | 126400 | 400 | 120300 | 300 | 153800 | 600 | 76900 | 300 | 0 | 0 | 260 | 477823 | 1669.952 | 1589.76 | 342720 | 476136 | 2232 | 479492.952 | 476153.048 | 473904 | -1.066% | 11.5333 | 97 | Moving cloudy weather.
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 6:48 | 18:09 | 6217.2 | 6187.2 | 5750.2 | 5827.9 | 5977.9 | 6071.3 | 5757.7 | 6597.9 | 6094.2 | 5799.3 | 6104.9 | 6124.6 | 6339.5 | 6149.9 | 6281.8 | 6113.2 | 8334 | 9386.9 | 8268 | 8687 | 9012.3 | 5550.4 | 8504.9 | 8584.9 | 8095 | 10687 | 8480.3 | 8510 | 6661.3 | 6886 | 6586.2 | 6722.8 | 6666.5 | 6920.1 | 6766 | 6705 | 5433.8 | 5467.9 | 5541.3 | 5403.3 | 5648.9 | 5520.3 | 7500 | 8634 | 6258.6 | 7581.5 | 7888.3 | 6027.8 | 6435.8 | 7909.7 | 6166.5 | 6522.8 | 4864.8 | 2252.6 | 822.2 | 635.4 | 4908.1 | 4783.9 | [16 empty] | 4.1068 |  | 5.2572 |  | 0.68373 |  |  |  | 31.0318 |  | 38.5221 |  | 21.5804 |  | 0 |  | 0.9942 |  | 2.724 |  | 4.1068 | 5.2572 | 0.68373 |  | 31.0318 | 38.5221 | 21.5804 |  | 0.9942 | 2.724 | 199495.4 | 10901.7 | 26856.3 | 52087.9 | 27057.6 | 59217.9 | 0 | 0 | 375616.8 | 34729.4 | 195.8 | 29593.5 | 209 | 33673.2 | 374.5 | 2832.2 | 12.2 |  |  | 83.15 | 101610283 | 837989.376 | 998.16 | 96008 | 140985.2 | 1661.7 | 99200 | 500 | 95400 | 400 | 115600 | 700 | 58800 | 300 | 0 | 0 | 370 | 369165 | 2032.768 | 2211.84 | 264960 | 367848 | 3024 | 371197.768 | 367132.232 | 364824 | -1.176% | 11.35 | 97 | Moving cloudy weather.
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 6:56 | 17:30 | 2664 | 2647 | 2477 | 2495 | 2581 | 2622 | 2464 | 2832 | 2580 | 2513 | 2626 | 2518 | 2699 | 2672 | 2688 | 2562 | 3625 | 4171 | 3563 | 3759 | 3944 | 2415 | 3675 | 3729 | 3533 | 3640 | 3660 | 3685 | 3099 | 3167 | 3083 | 3132 | 3069 | 3180 | 3114 | 3087 | 2433 | 2452 | 2483 | 2457 | 2533 | 2469 | 3493 | 4021 | 2912 | 3550 | 3455 | 2656.6 | 2808 | 3461.8 | 2839 | 2820 | 2779 | 1005 | 515 | 223 | 2129 | 2035 | [16 empty] | 1.68 |  | 2.214 |  | 0.274 |  | 0.402 |  | 30.348 |  | 37.568 |  | 30.976 |  | 0 |  | 0.666 |  | 1.692 |  | 1.68 | 2.214 | 0.274 | 0.402 | 30.348 | 37.568 | 30.976 |  | 0.666 | 1.692 | 85039 | 4885 | 12481 | 23918 | 12450 | 26726.4 | 0 | 0 | 165499.4 | 34772.5 | 195.9 | 29634.7 | 209.1 | 33726.8 | 374.8 | 2863 | 12.3 |  |  | 83.32 | 101779857 | 839260.288 | 999.408 | 96176 | 141219.7 | 1663.4 | 43100 | 100 | 41200 | 100 | 53600 | 300 | 30800 | 100 | 0 | 0 | 170 | 169574 | 1270.912 | 898.56 | 120960 | 168840 | 1224 | 170844.912 | 168303.088 | 167616 | 3.23% | 10.5667 | 97 | Moving cloudy weather.
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 7:10 | 17:35 | 5003 | 4966.3 | 4646.8 | 4677 | 4827.5 | 4888.9 | 4624.6 | 5295.5 | 4897.3 | 4820.7 | 5005.6 | 4934.5 | 5131.5 | 5025.5 | 5129.9 | 4859.6 | 6699.1 | 7746.6 | 6621.1 | 7004.6 | 7483.8 | 4593.2 | 6871.2 | 7021.8 | 6633.8 | 6760 | 6853.3 | 6880.5 | 5733.2 | 5892.7 | 5795.3 | 5824.4 | 5788.9 | 6010.9 | 5893.7 | 5839.8 | 4716.3 | 4731.8 | 4763.5 | 4712.8 | 4837 | 4765.9 | 6706 | 7528 | 5443 | 6633 | 6316.7 | 4838.4 | 5078.8 | 6320.8 | 4197.5 | 287.5 | 68.1 | 632.8 | 504 | 201 | 2120 | 2010 | 2842 | 945.4 | 831.7 | 1890 | 0 | 0 | 206 | 97.5 |  |  |  |  | 625 | 523 | 1460 | 1101 | 3.0989 |  | 4.0104 |  | 0.42088 |  | 0.67438 |  | 28.2032 |  | 36.1443 |  | 46.2168 |  | 0.233 |  | 1.4618 |  | 2.88 |  | 3.0989 | 4.0104 | 0.42088 | 0.67438 | 28.2032 | 36.1443 | 46.2168 | 0.233 | 1.4618 | 2.88 | 159903.2 | 9448.1 | 23245.6 | 45389.2 | 23533.3 | 36284.6 | 6509.1 | 303.5 | 304616.6 | 34853.3 | 196.3 | 29711.9 | 209.5 | 33827.6 | 375.6 | 2910.9 | 12.9 |  |  | 83.57 | 102087270 | 841200.768 | 1002 | 96483 | 141645.2 | 1667.3 | 80800 | 400 | 77200 | 400 | 100800 | 800 | 47900 | 600 | 0 | 0 | 250 | 307413 | 1940.48 | 1866.24 | 221040 | 306360 | 2808 | 309353.48 | 305472.52 | 303552 | 1.555% | 10.4167 | 97 | Fully cloudy weather.
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 7:45 | 17:50 | 6100.5 | 6126 | 5801.6 | 5758.8 | 5917.3 | 6011.4 | 5752.3 | 6309.6 | 5908 | 5806.3 | 5993.5 | 6001.1 | 6098.2 | 6082.3 | 6068.2 | 5902.6 | 8511.2 | 9391.9 | 8317.1 | 8708.6 | 2091.8 | 1266.6 | 1905.3 | 1939.2 | 1823.7 | 1868 | 1890.9 | 1900.8 | 7088.4 | 7272.5 | 7031.6 | 7120 | 7093.9 | 7338 | 7230.5 | 7102.2 | 5745.5 | 5769.3 | 5762.3 | 5792.1 | 5890.7 | 5793.7 | 8246 | 8945 | 6593 | 7964 | 6741.3 | 5133.8 | 5389.4 | 6687.4 | 5532.7 | 6423.4 | 3852.3 | 1692.8 | 1571.5 | 650.7 | 4128.1 | 4178.9 | 3745 | 1076 | 1298 | 2058 | 0 | 0 | 497 | 393 |  |  |  |  | 771.7 | 659 | 2762.4 | 1805.4 | 4.5551 |  | 4.3914 |  | 0.5057 |  | 0.74058 |  | 26.4906 |  | 34.0342 |  | 68.4472 |  | 0.088197 |  | 1.0991 |  | 2.952 |  | 4.5551 | 4.3914 | 0.5057 | 0.74058 | 26.4906 | 34.0342 | 68.4472 | 0.088197 | 1.0991 | 2.952 | 145252.8 | 11514.8 | 28512.5 | 54986.8 | 28764.6 | 57980.8 | 8177 | 890 | 336079.3 | 34902.5 | 196.5 | 29804.6 | 209.7 | 33949.5 | 375.9 | 2977.2 | 13.2 |  |  | 83.8 | 102418341 | 842331.456 | 1004 | 96812 | 142103.4 | 1669.8 | 49200 | 200 | 92700 | 200 | 121900 | 300 | 66300 | 300 | 0 | 0 | 230 | 331071 | 1130.688 | 1440 | 236880 | 329904 | 1800 | 332201.688 | 329940.312 | 328104 | -1.154% | 10.0833 | 98 | ICR 4 06:34 to 14:00 oil top up work & incomer 04 (phase 3)S/D 11:50 To 12:48 MSEDCL Work
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 6:34 | 18:28 | 8967.2 | 8913.3 | 8392.3 | 8461.1 | 8690.7 | 8812.8 | 8390.6 | 9306.6 | 8557.4 | 8500.5 | 8742.6 | 8717.2 | 8866 | 8733.1 | 8824.9 | 8595.4 | 12050.4 | 13316.1 | 11851.6 | 12477.9 | 12654.6 | 7933.6 | 12299 | 12526.2 | 11913.4 | 12213 | 12203.7 | 12286.6 | 10133.7 | 10432.8 | 10154.7 | 10309.5 | 10227.1 | 10613.4 | 10415.7 | 10266 | 8420 | 8456.4 | 8418.7 | 8476.1 | 8701.1 | 8511 | 11886 | 13035 | 8751 | 11436 | 11540 | 8858 | 9367 | 11532 | 9551 | 11214 | 6651 | 3393 | 2915 | 1140 | 7050 | 7124 | 6730 | 2989 | 3660 | 3515 | 0 | 0 | 844.9 | 669.9 |  |  |  |  | 1320 | 1127.9 | 4632 | 3738 | 6.7137 |  | 6.643 |  | 0.77825 |  | 1.1981 |  | 28.9812 |  | 37.3022 |  | 51.1453 |  | 0 |  | 0.73128 |  | 2.955 |  | 6.7137 | 6.643 | 0.77825 | 1.1981 | 28.9812 | 37.3022 | 51.1453 |  | 0.73128 | 2.955 | 283197.8 | 16876.4 | 41030.7 | 79214.9 | 41522.2 | 101152.9 | 16894 | 1514.8 | 581403.7 | 35045.1 | 196.9 | 29939.9 | 210.1 | 34125.4 | 376.6 | 3095.4 | 13.7 |  |  | 84.06 | 102990856 | 844410.56 | 1007 | 97383 | 142895.7 | 1673.5 | 142600 | 400 | 135300 | 400 | 175900 | 700 | 118200 | 500 | 0 | 0 | 260 | 572515 | 2079.104 | 2160 | 411120 | 570456 | 2664 | 574594.104 | 570435.896 | 567792 | -1.171% | 11.9 | 100 | Moving cloudy weather.
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 6:31 | 18:19 | 8957.4 | 8930.8 | 8552 | 8605.7 | 8801.1 | 8868.6 | 8575.8 | 9289.7 | 8687.6 | 8623.4 | 8867.3 | 8843.8 | 9000.9 | 8861.8 | 8946.8 | 8727.3 | 12361.2 | 13529.4 | 12158.5 | 12712.4 | 13344.1 | 8201.1 | 12600.7 | 12888.3 | 12271 | 12500.3 | 12565.3 | 12595.7 | 10417.4 | 10722.5 | 10438.9 | 10586.2 | 10522.2 | 10912.7 | 10701.7 | 10544.9 | 8609.9 | 8655.9 | 8668.3 | 8691.2 | 8855.2 | 8717.7 | 12223.7 | 13261.4 | 8481.4 | 11906.7 | 11811.3 | 9089.9 | 9636.9 | 11844.8 | 9766.7 | 11489.5 | 6805.8 | 3486.8 | 3033.1 | 1168.1 | 7276.4 | 7440.1 | 6951 | 3648 | 4383 | 3495 | 0 | 0 | 876 | 678 |  |  |  |  | 1343 | 1154 | 4879 | 4732 | 7.0238 |  | 6.9012 |  | 0.83066 |  | 1.2699 |  | 30.6565 |  | 38.0926 |  | 33.9257 |  | 0 |  | 0.82883 |  | 2.967 |  | 7.0238 | 6.9012 | 0.83066 | 1.2699 | 30.6565 | 38.0926 | 33.9257 |  | 0.82883 | 2.967 | 288868 | 17265.8 | 42165 | 80805.6 | 42681.5 | 104957.4 | 18477 | 1554 | 596774.3 | 35191.7 | 197.3 | 30076.6 | 210.4 | 34305.4 | 377.2 | 3219 | 14.1 |  |  | 84.34 | 103578411 | 846357.632 | 1009 | 97968 | 143708.8 | 1677 | 146600 | 400 | 136700 | 300 | 180000 | 600 | 123600 | 400 | 0 | 0 | 280 | 587555 | 1947.072 | 1440 | 421200 | 585432 | 2520 | 589502.072 | 585607.928 | 582912 | -1.219% | 11.8 | 102 | Moving cloudy weather.
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 6:31 | 18:18 | 9034.7 | 9022 | 8668.9 | 8730.1 | 8920.1 | 8976.7 | 8717.8 | 9375.6 | 8802 | 8738.4 | 8973.6 | 8951.2 | 9113.7 | 8970.7 | 9053.9 | 8867.5 | 12619.4 | 13698.8 | 12442.5 | 12924.6 | 13541.8 | 8461.7 | 12863.6 | 13007.5 | 12530.8 | 12739 | 12769.1 | 12857.3 | 10703.6 | 11018.8 | 10726.5 | 10872.8 | 10814.4 | 11216.2 | 10987.6 | 10827 | 8772.1 | 8821.8 | 8841.9 | 8850.9 | 8993.5 | 8878.3 | 12531.3 | 13521.6 | 8899.2 | 11300 | 12143.1 | 9369.9 | 9916.5 | 12152.6 | 9966.4 | 11716.5 | 6957.4 | 3693.1 | 3681 | 1668.7 | 7499 | 7644 | 7084 | 4120 | 5899 | 3709 | 0 | 0 | 903 | 685 |  |  |  |  | 1394 | 1189 | 5120 | 5179 | 7.2617 |  | 7.1267 |  | 0.85638 |  | 1.3176 |  | 32.571 |  | 39.887 |  | 22.4463 |  | 0 |  | 0.92548 |  | 2.496 |  | 7.2617 | 7.1267 | 0.85638 | 1.3176 | 32.571 | 39.887 | 22.4463 |  | 0.92548 | 2.496 | 293373 | 17593.9 | 43321.7 | 81816.7 | 43845.2 | 109290.2 | 20812 | 1588 | 611640.7 | 35340.9 | 197.7 | 30214.4 | 210.7 | 34490.6 | 377.8 | 3348.5 | 14.4 |  |  | 84.6 | 104181514 | 848075.906 | 1011 | 98568 | 144543.7 | 1680 | 149200 | 400 | 137800 | 300 | 185200 | 600 | 129500 | 300 | 0 | 0 | 260 | 603103 | 1718.274 | 1440 | 432000 | 601128 | 2160 | 604821.274 | 601384.726 | 598968 | -1.115% | 11.7833 | 102 | Moving cloudy weather.
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 6:58 | 18:20 | 9028.4 | 9020.1 | 8664.8 | 8729 | 8915.4 | 8995.5 | 8717.5 | 9369 | 8814.7 | 8747.4 | 8989.3 | 8970.8 | 9129.4 | 8983.5 | 9075.8 | 8901.1 | 12660.3 | 13738.7 | 12487.1 | 13149.6 | 13533.4 | 8453.2 | 12874.4 | 13004.9 | 12494.2 | 12729 | 12758.8 | 12863.9 | 10662.6 | 10968.3 | 10671.9 | 10822.1 | 10764.4 | 11159.1 | 10948.3 | 10794.8 | 8736.1 | 8775.9 | 8786.8 | 8800.9 | 8948.6 | 8831.5 | 12468 | 13508 | 10143 | 12261 | 12176 | 9415 | 10005 | 12175 | 10777 | 11709 | 6952 | 3733 | 3857 | 2267 | 7485 | 7812 | 3706 | 5918.6 | 3831 | 7092.6 | 0 | 0 | 1613 | 874.9 |  |  |  |  | 1395.2 | 1189.5 | 5120.7 | 5592 | 7.3115 |  | 7.1847 |  | 0.87372 |  | 1.3356 |  | 33.6411 |  | 40.8465 |  | 18.5767 |  | 0 |  | 1.025 |  | 2.88 |  | 7.3115 | 7.1847 | 0.87372 | 1.3356 | 33.6411 | 40.8465 | 18.5767 |  | 1.025 | 2.88 | 293799.2 | 17512 | 43124.9 | 83747.8 | 43666.6 | 111660.4 | 20548.2 | 2487.9 | 616547 | 35490.4 | 198.1 | 30353.1 | 211.1 | 34675.6 | 378.5 | 3480.9 | 14.9 |  |  | 84.88 | 104787632 | 850093.504 | 1014 | 99172 | 145382.7 | 1683.6 | 149500 | 400 | 138700 | 400 | 185000 | 700 | 132400 | 500 | 0 | 0 | 280 | 606118 | 2017.598 | 2160 | 434880 | 604080 | 2592 | 608135.598 | 604100.402 | 601488 | -1.364% | 11.3667 | 102 | Weather clear
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 6:29 | 18:21 | 8902.2 | 8897 | 8557.2 | 8617.2 | 8814.4 | 8910 | 8603.9 | 9244 | 8675.4 | 8631.2 | 8880.9 | 8859.2 | 9032.9 | 8874.4 | 8972.7 | 8784.4 | 12461.6 | 13586.3 | 12269.5 | 12889.6 | 13368 | 8318.6 | 12687 | 12834.8 | 12295.3 | 12586 | 12573.5 | 12699.1 | 10445 | 10743.3 | 10453.1 | 10603 | 10549 | 10946.5 | 10737 | 10599.2 | 8620.8 | 8665.5 | 8661.1 | 8674.2 | 8835.5 | 8719.9 | 12284 | 13371 | 9963 | 12046 | 8057.3 | 5287 | 9819.4 | 11891.4 | 10776.5 | 11468.6 | 6800 | 3640 | 5207.5 | 3476.9 | 7263.9 | 7003.3 | 6923 | 3921 | 5782 | 3611 | 0 | 0 | 1740 | 845 |  |  |  |  | 1356 | 1156 | 4988 | 6053 | 7.1952 |  | 7.0545 |  | 0.88503 |  | 1.3287 |  | 33.7987 |  | 41.1033 |  | 18.1982 |  | 0 |  | 0.94429 |  | 2.934 |  | 7.1952 | 7.0545 | 0.88503 | 1.3287 | 33.7987 | 41.1033 | 18.1982 |  | 0.94429 | 2.934 | 289826.3 | 17286.3 | 42244.4 | 82554.7 | 42831.7 | 104244.8 | 20237 | 2585 | 601810.2 | 35637.8 | 198.5 | 30490 | 211.4 | 34857.5 | 379.1 | 3605.8 | 15.3 |  |  | 85.18 | 105379184 | 851951.232 | 1016 | 99761 | 146201.5 | 1686.9 | 147400 | 400 | 136900 | 300 | 181900 | 600 | 124900 | 400 | 0 | 0 | 300 | 591552 | 1857.728 | 1440 | 424080 | 589536 | 2376 | 593409.728 | 589694.272 | 587160 | -1.396% | 11.8667 | 102 | Weather clear Block 10 Inv01 GFDI Fault
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 6:32 | 18:17 | 8229.2 | 8180.5 | 7655.2 | 7720.5 | 7942.9 | 8133.6 | 7704 | 8638 | 8033.8 | 7840.5 | 8182.5 | 8179.8 | 8360.4 | 8194.8 | 8283.3 | 8051.5 | 11092.5 | 12527.8 | 10870.1 | 11408.5 | 12308 | 7405 | 11386.5 | 11603.1 | 10933.1 | 11249.8 | 11249.4 | 11407.4 | 9250.1 | 9507.3 | 9250 | 9380.6 | 9406.6 | 9741.9 | 9584.7 | 9438.6 | 7726.7 | 7771.9 | 7699.8 | 7715.5 | 7927.4 | 7798.4 | 11003.1 | 12299.8 | 8824.5 | 10644.6 | 10517 | 8164.4 | 8661.6 | 10521 | 9490.4 | 10196 | 5973.6 | 4158.9 | 4597.3 | 4248.4 | 6315 | 6214.6 | 6081.8 | 3559.8 | 5072.4 | 3166 | 0 | 0 | 1578 | 737 |  |  |  |  | 1172.9 | 999.5 | 4349.6 | 5122 | 6.3737 |  | 6.223 |  | 0.80677 |  | 1.2043 |  | 33.3011 |  | 43.2647 |  | 19.7708 |  | 0 |  | 0.67708 |  | 2.496 |  | 6.3737 | 6.223 | 0.80677 | 1.2043 | 33.3011 | 43.2647 | 19.7708 |  | 0.67708 | 2.496 | 262771.7 | 15498.6 | 37388 | 73913.1 | 38171.8 | 100702.2 | 17880 | 2315 | 548640.4 | 35770.3 | 199.1 | 30615.4 | 211.9 | 35020 | 380 | 3725 | 15.9 |  |  | 85.55 | 105919365 | 854759.232 | 1020 | 100299 | 146949.2 | 1691.9 | 132500 | 600 | 125400 | 500 | 162500 | 900 | 119200 | 600 | 0 | 0 | 370 | 540181 | 2808 | 2880 | 387360 | 538344 | 3600 | 542989 | 537373 | 534744 | -1.03% | 11.75 | 102 | Moving cloudy weather.
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 6:29 | 18:20 | 8779 | 8766.9 | 8369.2 | 8426 | 8617 | 8734.3 | 8435.2 | 9140.9 | 8555.4 | 8444.4 | 8718.2 | 8712.7 | 8871.9 | 8730.9 | 8804.5 | 8633.8 | 12147.3 | 13296.7 | 11945.7 | 12529.3 | 13059.2 | 8030 | 12369 | 12520.3 | 11890.8 | 12240 | 12264.5 | 12393.2 | 10039.3 | 10324.7 | 9901.1 | 10192.7 | 10236 | 10571.8 | 10391 | 10261.1 | 8351.3 | 8428.9 | 8355.4 | 8378.7 | 8560.9 | 8489.8 | 11891 | 12969 | 9527 | 11514 | 8099 | 5450 | 9467 | 11504 | 10430 | 11193 | 7137 | 4613 | 6374 | 4745 | 7094 | 7047 | 6864 | 4374 | 5354 | 3502.5 | 0 | 0 | 1765.8 | 825 |  |  |  |  | 1312.6 | 1118 | 4670 | 6743 | 7.0734 |  | 6.8727 |  | 0.90686 |  | 1.3101 |  | 34.8025 |  | 48.3812 |  | 20.8841 |  | 0 |  | 1.3234 |  | 3.435 |  | 7.0734 | 6.8727 | 0.90686 | 1.3101 | 34.8025 | 48.3812 | 20.8841 |  | 1.3234 | 3.435 | 283426.3 | 16780.2 | 40457.8 | 79685.8 | 41459.9 | 106996.6 | 20094.5 | 2590.8 | 591491.9 | 35913.8 | 199.3 | 30749.6 | 212.1 | 35195.6 | 380.4 | 3852.5 | 16.3 |  |  | 85.81 | 106500956 | 856109.248 | 1022 | 100878 | 147754.2 | 1694.2 | 143500 | 200 | 134200 | 200 | 175600 | 400 | 127500 | 400 | 0 | 0 | 260 | 581591 | 1350.016 | 1440 | 416880 | 579600 | 1656 | 582941.016 | 580240.984 | 577944 | -1.446% | 11.85 | 102 | Moving cloudy weather.
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 6:30 | 18:22 | 8884 | 8858.5 | 8441.7 | 8540.4 | 8713.2 | 8832 | 8519 | 9265.7 | 8631.6 | 8568.4 | 8787.4 | 8766 | 8933.8 | 8812.6 | 8880.2 | 8699.1 | 12270.6 | 13420.9 | 12043 | 12628.5 | 13205.7 | 8105.5 | 12467.7 | 12627.3 | 12027.3 | 12349 | 12389.2 | 12482.7 | 10256.8 | 10515.9 | 10202.6 | 10244.3 | 10324.8 | 10649 | 10480.1 | 10333.9 | 8428.7 | 8483.8 | 8485.7 | 8433.6 | 8702.3 | 8578.3 | 11986 | 13111 | 9629 | 11593 | 11553 | 8957 | 9496 | 11524 | 10733 | 11224 | 7158 | 4624 | 6637 | 5033 | 7133 | 7097 | 6970 | 4377 | 5649 | 3324 | 0 | 0 | 1764 | 824 |  |  |  |  | 1325 | 1129 | 4688 | 7260 | 7.0756 |  | 6.9105 |  | 0.90305 |  | 1.3229 |  | 32.8579 |  | 45.9562 |  | 28.4713 |  | 0 |  | 1.4104 |  | 3.312 |  | 7.0756 | 6.9105 | 0.90305 | 1.3229 | 32.8579 | 45.9562 | 28.4713 |  | 1.4104 | 3.312 | 286151 | 16912.5 | 41219.6 | 80518.9 | 41787.8 | 115571 | 20320 | 2588 | 605068.8 | 36058.7 | 199.8 | 30885.5 | 212.6 | 35373.2 | 381.2 | 3988.6 | 16.9 |  |  | 86.13 | 107095990 | 858690.816 | 1025 | 101471 | 148577.7 | 1698.8 | 144900 | 500 | 135900 | 500 | 177600 | 800 | 136100 | 600 | 0 | 0 | 320 | 595034 | 2581.568 | 2160 | 426960 | 592920 | 3312 | 597615.568 | 592452.432 | 589608 | -1.232% | 11.8667 | 102 | Weather clear
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 6:28 | 18:26 | 9054.8 | 9025 | 8571.1 | 8711.4 | 8854.8 | 8972.9 | 8652.2 | 9410.4 | 8743.9 | 8686.5 | 8875.2 | 8846.5 | 9024.6 | 8891.4 | 8981.1 | 8820 | 12436.8 | 13510.8 | 12234.1 | 12800.7 | 13276.5 | 8331.1 | 12544.8 | 12712.9 | 12120 | 12453 | 12476.1 | 12585.9 | 10360.5 | 10753 | 10379.5 | 10400.5 | 10492.2 | 10823 | 10643 | 10503.6 | 8550.9 | 8612.9 | 8479.2 | 8576.8 | 8896.5 | 8707.9 | 12170 | 13314 | 9811 | 11771 | 0 | 0 | 9322.1 | 11309.2 | 10655.7 | 11178.7 | 7487.2 | 4550.7 | 6810 | 4999 | 7045 | 6950 | 6917 | 4325 | 5659 | 3292 | 0 | 0 | 1482 | 692 |  |  |  |  | 1326 | 1134 | 4679 | 7195 | 7.1323 |  | 6.9941 |  | 0.88439 |  | 1.3165 |  | 30.363 |  | 44.855 |  | 38.9168 |  | 0 |  | 1.3115 |  | 2.955 |  | 7.1323 | 6.9941 | 0.88439 | 1.3165 | 30.363 | 44.855 | 38.9168 |  | 1.3115 | 2.955 | 289604.5 | 17163.8 | 41893.5 | 81726.4 | 42461.8 | 94641.6 | 20193 | 2174 | 589858.6 | 36205 | 200.1 | 31023.7 | 212.8 | 35553.5 | 381.7 | 4106.7 | 17.2 |  |  | 86.37 | 107679096 | 860142.784 | 1027 | 102052 | 149384.8 | 1701.3 | 146300 | 300 | 138200 | 200 | 180300 | 500 | 118100 | 300 | 0 | 0 | 240 | 583106 | 1451.968 | 1440 | 418320 | 581112 | 1800 | 584557.968 | 581654.032 | 579312 | -0.8986% | 11.9667 | 102 | Moving cloudy weather.incomer 04 (phase-3) O/C & E/F ICR-10 Inv1 GFDI-pro Internal fault.
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 6:25 | 18:24 | 8838.6 | 8816.1 | 8389.5 | 8507.7 | 8727.9 | 8774.8 | 8472.3 | 9170.5 | 8511.8 | 8486.5 | 8700.3 | 8678.3 | 8798.7 | 8695 | 8762.1 | 8607.4 | 12285.1 | 13278.4 | 12035.8 | 12486.9 | 13138.4 | 8303.1 | 12551.4 | 12597.2 | 12047 | 12324 | 12379.1 | 12481.1 | 10282.6 | 10592.3 | 10256.6 | 10291.8 | 10255.4 | 10559.4 | 10395.5 | 10248.9 | 8343.4 | 8427 | 8277.2 | 8509.4 | 8697 | 8522.7 | 11931 | 13033.9 | 9608.7 | 11530.7 | 0 | 0 | 9402 | 11317.8 | 10829.4 | 12147 | 7432.8 | 4576 | 6828.1 | 5047 | 7137.8 | 7103.2 | 6987 | 4235 | 5722 | 3379 | 0 | 0 | 1848 | 863 |  |  |  |  | 1353 | 1140 | 4745 | 7325 | 7.2977 |  | 7.1595 |  | 0.93396 |  | 1.3927 |  | 31.3494 |  | 44.5878 |  | 38.075 |  | 0 |  | 1.2588 |  | 2.592 |  | 7.2977 | 7.1595 | 0.93396 | 1.3927 | 31.3494 | 44.5878 | 38.075 |  | 1.2588 | 2.592 | 284845 | 16770.4 | 41423.3 | 80110.6 | 41459.2 | 96384.1 | 20323 | 2711 | 584026.6 | 36349.8 | 200.6 | 31158.4 | 213.2 | 35730.4 | 382.5 | 4225.3 | 17.8 |  |  | 86.66 | 108254601 | 862512.896 | 1030 | 102625 | 150181.4 | 1705.5 | 144800 | 500 | 134700 | 400 | 176900 | 800 | 118600 | 600 | 0 | 0 | 290 | 575505 | 2370.112 | 2160 | 412560 | 573552 | 3024 | 577875.112 | 573134.888 | 570528 | -1.053% | 11.9833 | 102 | Moving cloudy weather. Power Trafo Tripped at 16:22 to 16:48 due to OV/UV & ICR-10 Inv1 GFDI-pro Internal fault
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 6:28 | 18:23 | 8944.4 | 8953.2 | 8519.8 | 8645.4 | 8862.7 | 8882 | 8600.9 | 9250.9 | 8658 | 8626.9 | 8821.2 | 8811.6 | 8969.8 | 8836.3 | 8921.2 | 8781.2 | 12515.2 | 13502.4 | 12340.4 | 12730.8 | 13412.3 | 8457.2 | 12718.7 | 12802.2 | 12351 | 12545 | 12662.9 | 12751.7 | 10671.4 | 10932.7 | 10652.3 | 10727.4 | 10658.9 | 10907.3 | 10813.9 | 10611.9 | 8465.1 | 8622.7 | 8495 | 8637.1 | 8850 | 8606.6 | 12324 | 13381 | 9971 | 12000 | 0 | 0 | 9982 | 12023 | 12684 | 12797 | 7849 | 4821 | 7552 | 5105 | 7459 | 7421 | 7321 | 4703 | 5990 | 3531 | 0 | 0 | 1914 | 887 |  |  |  |  | 1371 | 445 | 4843 | 7466 | 7.252 |  | 7.1232 |  | 0.94167 |  | 1.3867 |  | 32.8941 |  | 47.3437 |  | 26.7984 |  | 0 |  | 1.1613 |  | 2.4 |  | 7.252 | 7.1232 | 0.94167 | 1.3867 | 32.8941 | 47.3437 | 26.7984 |  | 1.1613 | 2.4 | 289875.3 | 17087.8 | 42983.8 | 82264.7 | 42992 | 101818 | 21545 | 2801 | 601367.6 | 36497.1 | 200.9 | 31295.4 | 213.5 | 35912.5 | 383 | 4348.3 | 18.2 |  |  | 86.9 | 108845178 | 864107.456 | 1032 | 103213 | 150998.8 | 1708.3 | 147300 | 300 | 137000 | 300 | 182100 | 500 | 123000 | 400 | 0 | 0 | 240 | 590577 | 1594.56 | 1440 | 423360 | 588528 | 2016 | 592171.56 | 588982.44 | 586512 | -1.529% | 11.9167 | 105 | Moving cloudy weather .ICR-10 Inv1 GFDI-pro Internal fault
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 6:24 | 18:24 | 8989.8 | 8950.8 | 8463 | 8594.1 | 8819.2 | 8872 | 8543.8 | 9320.3 | 8769.8 | 8714.3 | 8969.4 | 8932.6 | 9138.9 | 8967.5 | 9079.2 | 8879.4 | 12476.7 | 13577.3 | 12217.3 | 12723.1 | 13459.1 | 8410.1 | 12679.1 | 12862.9 | 12217.6 | 12573 | 12586.7 | 12694.2 | 10444.4 | 10727.5 | 10518 | 10569 | 10506 | 10841.9 | 10694.3 | 10461.4 | 8463.4 | 8520.3 | 8476.1 | 8705 | 8858.4 | 8617.3 | 12058 | 13324 | 9858 | 11859 | 0 | 0 | 8825.7 | 10710 | 11471.9 | 11386.7 | 6970.6 | 4258 | 6777.5 | 3794 | 6577.7 | 6335 | 6482 | 4417 | 5296 | 3127 | 0 | 0 | 1682 | 782 |  |  |  |  | 1255 | 1074 | 4414 | 6767 | 7.1475 |  | 7.0364 |  | 0.92568 |  | 1.379 |  | 33.6956 |  | 47.2413 |  | 24.0033 |  | 0 |  | 1.3765 |  | 2.874 |  | 7.1475 | 7.0364 | 0.92568 | 1.379 | 33.6956 | 47.2413 | 24.0033 |  | 1.3765 | 2.874 | 290481.2 | 16983.7 | 42258.9 | 81755.8 | 42503.6 | 90617.1 | 19322 | 2464 | 586386.3 | 36641.8 | 201.3 | 31429.5 | 213.8 | 36090 | 383.7 | 4456.5 | 18.8 |  |  | 87.17 | 109421699 | 866123.328 | 1034 | 103787 | 151796.7 | 1711.8 | 144700 | 400 | 134100 | 300 | 177500 | 700 | 108200 | 600 | 0 | 0 | 270 | 576521 | 2015.872 | 1440 | 413280 | 574488 | 2520 | 578536.872 | 574505.128 | 571968 | -1.339% | 12 | 105 | Moving cloudy weather .ICR-10 Inv1 GFDI-pro Internal fault Incomer4 Hand Trip T L Line maintance work at 6:30 AM to 8:53AM
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 6:27 | 17:57 | 8151.5 | 8140.7 | 7642.9 | 7749.1 | 8011.4 | 8079.1 | 7663 | 8452.5 | 8066.4 | 8021.3 | 8337.5 | 8285.7 | 8465.1 | 8362.1 | 8422.7 | 8157.8 | 11291.9 | 12637.8 | 10963.7 | 11457.8 | 12480.5 | 7653 | 11580.6 | 11787.8 | 11107.2 | 114551.7 | 11454.2 | 11585.3 | 9332.1 | 9561.2 | 9339.3 | 9396.2 | 9373.5 | 9712.1 | 9594.6 | 9411.4 | 7527 | 7594.2 | 7540.9 | 7736.9 | 7979.4 | 7743.9 | 10808.5 | 12160.6 | 8756.8 | 10491.1 | 104.9 | 107.5 | 8609.1 | 10319.4 | 11185.1 | 10911.8 | 6579.8 | 4033 | 6524.5 | 3724.2 | 6133.4 | 6120.1 |  |  |  |  | 0 | 0 | [6 empty] | 1131 | 963 | 4049 | 6281 | 6.4203 |  | 6.3114 |  | 0.84144 |  | 1.2429 |  | 33.8276 |  | 46.9843 |  | 26.5597 |  | 0 |  | 1.0568 |  | 3.009 |  | 6.4203 | 6.3114 | 0.84144 | 1.2429 | 33.8276 | 46.9843 | 26.5597 |  | 1.0568 | 3.009 | 368560.3 | 15121.2 | 37628.8 | 73218.1 | 38091.6 | 86776.8 | 0 | 0 | 619396.8 | 36763 | 201.7 | 31544 | 214.2 | 36235.9 | 384.6 | 4551.1 | 19.9 |  |  | 87.45 | 109949534 | 868605.952 | 1038 | 104313 | 152527.2 | 1716.2 | 121200 | 400 | 114500 | 400 | 145900 | 900 | 94600 | 1100 | 0 | 0 | 280 | 527835 | 2482.624 | 2880 | 378720 | 525960 | 3168 | 530317.624 | 525352.376 | 522792 | -14.38% | 11.5 | 105 | Moving cloudy weather .ICR-10 Inv1 GFDI-pro Internal fault
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 6:25 | 18:21 | 8869 | 7908 | 8481 | 8494 | 8705 | 8792 | 8612 | 9197 | 8698 | 8658 | 8931 | 8886 | 9164 | 8938 | 9061 | 8870 | 12378 | 13483 | 12107 | 12591 | 13271 | 8276 | 12510 | 12746 | 12104 | 12432 | 12426 | 12533 | 10281 | 10559 | 10349 | 10398 | 10390 | 10787 | 10595 | 10441 | 8361 | 8438 | 8323 | 8518 | 8709 | 8557 | 11940 | 13177 | 9737 | 11685 | 7362 | 5707 | 9575 | 11513 | 12428 | 12421 | 7553 | 4601 | 7610 | 4294 | 7084 | 7053 | 6930 | 5434 | 5675 | 3356 | 440 | 0 | 1806 | 831 |  |  |  |  | 1332 | 1134 | 4723 | 7285 | 7.149 |  | 7.073 |  | 0.928 |  | 1.398 |  | 34.167 |  | 45.873 |  | 29.608 |  | 0 |  | 1.072 |  | 2.58 |  | 7.149 | 7.073 | 0.928 | 1.398 | 34.167 | 45.873 | 29.608 |  | 1.072 | 2.58 | 287121 | 16799 | 41587 | 80646 | 42213 | 111675 | 21395 | 3077 | 604513 | 36880.3 | 201.9 | 31653.1 | 214.3 | 36380 | 385.4 | 4658.4 | 21.1 |  |  | 87.69 | 110544773 | 871004.992 | 1041 | 104906 | 153351.1 | 1720.3 | 117300 | 200 | 109100 | 100 | 144100 | 800 | 107300 | 1200 | 0 | 0 | 240 | 595239 | 2399.04 | 2160 | 426960 | 593208 | 2952 | 597638.04 | 592839.96 | 590256 | -1.137% | 11.9333 | 105 | Moving cloudy weather.ICR-04 Inv1 DSP Internal Fault.at 09:03 AM to 09:51 AM
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 6:26 | 18:23 | 7852.7 | 7869.8 | 7409.9 | 7368.2 | 7528.6 | 7747.8 | 7563.6 | 8180.9 | 7685.5 | 7586.8 | 7806.8 | 7759.2 | 8114.6 | 7805 | 7979.5 | 7805.8 | 10933.7 | 11863.4 | 10677.7 | 11043.3 | 11593.4 | 7238.6 | 10857.1 | 11015.9 | 10795.4 | 10825 | 10856.7 | 10937.8 | 8756.4 | 9062.8 | 8894.2 | 8943.5 | 8906.9 | 9320 | 9107 | 9002.8 | 7272.3 | 7334 | 7958 | 8105 | 8287 | 8097 | 10002.7 | 11407 | 8417 | 10094.4 | 10263 | 7976 | 8343 | 9998.9 | 20679 | 10686 | 6595 | 4033 | 6583 | 3669 | 6382 | 6042 | 6679 | 4699 | 5234 | 2882 | 1373 | 0 | 1556 | 713 |  |  |  |  | 1139 | 969 | 4100 | 6296 | 6.322 |  | 6.26 |  | 0.774 |  | 1.248 |  | 34.081 |  | 45.521 |  | 28.576 |  | 0 |  | 1.167 |  | 3.117 |  | 6.322 | 6.26 | 0.774 | 1.248 | 34.081 | 45.521 | 28.576 |  | 1.167 | 3.117 | 252702.7 | 14606.3 | 35656.9 | 72368.1 | 36336.7 | 113753.9 | 19494 | 3642 | 548560.6 | 36973.6 | 202.1 | 31741.3 | 214.5 | 36492.6 | 385.8 | 4749.5 | 21.7 |  |  | 87.87 | 111071920 | 872561.6 | 1043 | 105431 | 154080.8 | 1723.2 | 93300 | 200 | 88200 | 200 | 112600 | 400 | 91100 | 600 | 0 | 0 | 180 | 527147 | 1556.608 | 1440 | 378000 | 525384 | 2088 | 528703.608 | 525590.392 | 523296 | -3.62% | 11.95 | 105 | Moving cloudy weather.
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 6:21 | 18:25 | 9048.5 | 9015.9 | 8548.3 | 8558.1 | 8769.5 | 9032.6 | 8815.7 | 9393.1 | 8821.8 | 8758 | 9017.3 | 9019.3 | 9284.6 | 9006.8 | 9145.1 | 8977.8 | 12653 | 13628.1 | 12198.8 | 12728.9 | 13443.2 | 8325.7 | 12683.5 | 12813.3 | 12499 | 12432 | 12587.8 | 12714 | 10389.6 | 10672.1 | 10466.5 | 10509.8 | 10571.4 | 10904.9 | 10750.4 | 10588.7 | 8624.2 | 8688.1 | 8452.9 | 8650 | 8836.7 | 8708 | 12246 | 13347.4 | 9864 | 11841.4 | 12082.9 | 9243.8 | 9745.3 | 11762.4 | 12586 | 12729 | 7681.1 | 4714.3 | 7610 | 4294 | 7084 | 7053 |  |  |  |  | 1647 | 0 | 1845 | 846 | [8 empty] | 7.2034 |  | 7.1535 |  | 0.94859 |  | 1.4177 |  | 33.8542 |  | 45.8713 |  | 27.3839 |  | 0 |  | 1.3137 |  | 3.183 |  | 7.2034 | 7.1535 | 0.94859 | 1.4177 | 33.8542 | 45.8713 | 27.3839 |  | 1.3137 | 3.183 | 291919.7 | 17312.3 | 42038 | 81946.4 | 42815.4 | 106585.8 | 0 | 4338 | 586955.6 | 37072.8 | 202.3 | 31834.4 | 214.8 | 36614.4 | 386.4 | 4848.4 | 22.5 |  |  | 88.09 | 111687254 | 875620.546 | 1047 | 106044 | 154932.5 | 1728.5 | 99200 | 200 | 93100 | 300 | 121800 | 600 | 98900 | 800 | 0 | 0 | 220 | 615334 | 3058.946 | 2880 | 441360 | 613224 | 3816 | 618392.946 | 612275.054 | 609408 | 5.356% | 12.0667 | 105 | Moving cloudy weather.
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 6:21 | 18:26 | 9254.1 | 9204 | 8747.7 | 8833.2 | 9063.9 | 9292 | 9027.5 | 9599.5 | 9009.4 | 8967.3 | 9252.2 | 9201.5 | 9482.5 | 9265.8 | 9353.2 | 9188.5 | 12988.5 | 13874.6 | 12635 | 13027.4 | 13729.1 | 8605.6 | 13040.4 | 13113.4 | 12883.4 | 12816 | 12984.2 | 13072.4 | 10866.1 | 11126.3 | 10806.9 | 10863.8 | 10970.4 | 11279.9 | 11122.2 | 10982.4 | 8873.3 | 8924.3 | 8981 | 8895.2 | 9091.7 | 8990.1 | 12625.1 | 13614.6 | 10196.6 | 12234 | 12486.2 | 9353.4 | 10022 | 12126.5 | 12948.2 | 12924.6 | 7910 | 4852.8 | 8060.5 | 4622.2 | 8032.7 | 7422.5 | [16 empty] | 7.4408 |  | 7.3982 |  | 0.9629 |  | 1.4598 |  | 32.9205 |  | 44.9802 |  | 27.4185 |  | 0 |  | 1.3652 |  | 2.991 |  | 7.4408 | 7.3982 | 0.9629 | 1.4598 | 32.9205 | 44.9802 | 27.4185 |  | 1.3652 | 2.991 | 299512.3 | 17797.6 | 43663.1 | 84628.3 | 44354.9 | 110761.6 | 0 | 0 | 600717.8 | 37174.7 | 202.5 | 31929.9 | 214.9 | 36740.3 | 386.8 | 4951.4 | 22.6 |  |  | 88.25 | 112322347 | 876825.28 | 1048 | 106676 | 155811.5 | 1730.7 | 101900 | 200 | 95500 | 100 | 125900 | 400 | 103000 | 100 | 0 | 0 | 160 | 635093 | 1204.734 | 720 | 455040 | 632880 | 1584 | 636297.734 | 633888.266 | 631296 | 5.923% | 12.0833 | 105 | Weather clear
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 6:19 | 18:26 | 9143.4 | 9125.4 | 8682.1 | 8785 | 8994.9 | 9195.1 | 8949.1 | 9504 | 8944 | 8888 | 9192 | 9124.1 | 9400.8 | 9224.5 | 9276.3 | 9101.3 | 10730.3 | 11509.4 | 11338.8 | 11696.2 | 11883 | 7362.3 | 12432.1 | 12497.3 | 10717.9 | 10781.8 | 10671.4 | 10771.6 | 10702 | 11003 | 10189 | 10203 | 10716 | 11013 | 10774 | 10641 | 9122 | 8791 | 8844.1 | 8803.4 | 8973.6 | 8831.6 | 10414.9 | 11284 | 7961 | 9544.099 | 12609.2 | 9952 | 9842.6 | 11868.1 | 12852.1 | 12839.1 | 7812.9 | 4770 | 7969.2 | 5005 | 7949 | 7337.6 | [16 empty] | 7.0777 |  | 7.0362 |  | 0.94385 |  | 1.3953 |  | 32.5143 |  | 44.5121 |  | 25.2678 |  | 0 |  | 1.0995 |  | 2.457 |  | 7.0777 | 7.0362 | 0.94385 | 1.3953 | 32.5143 | 44.5121 | 25.2678 |  | 1.0995 | 2.457 | 277922.1 | 17913 | 42097 | 74656.699 | 43144 | 110806.8 | 0 | 0 | 566539.599 | 37275.2 | 202.8 | 32024.9 | 215.2 | 36864.5 | 387.2 | 5054.3 | 22.8 |  |  | 88.44 | 112951762 | 878577.088 | 1050 | 107303 | 156682.2 | 1733.8 | 100500 | 300 | 95000 | 300 | 124200 | 400 | 102900 | 200 | 0 | 0 | 190 | 629415 | 1751.808 | 1440 | 451440 | 626904 | 2232 | 631166.808 | 627663.192 | 624672 | 11.41% | 12.1167 | 105 | Weather clear
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 6:18 | 18:26 | 9033.3 | 9013.2 | 8619.5 | 8675.8 | 8903.9 | 9112.5 | 8875.4 | 9372.3 | 8854.3 | 8824.2 | 9102.8 | 9038.1 | 9285.1 | 9102.4 | 9165.3 | 9003 | 12989 | 13875 | 12297.8 | 12775.3 | 13407.8 | 8263.8 | 12781.9 | 12844.6 | 12557.6 | 12615 | 12681.2 | 12813.7 | 10501.5 | 10802.8 | 10595.6 | 10664.9 | 10560.6 | 10860.6 | 10703.3 | 10574.7 | 8611.4 | 8668 | 8769.1 | 8758.8 | 8902.8 | 8754.7 | 10642.6 | 11602.3 | 8294 | 9937 | 12365.5 | 9355 | 9692.2 | 11647 | 12656.9 | 12669.7 | 7693.7 | 4670 | 7779.9 | 5429.2 | 7817.1 | 7208.8 | [16 empty] | 7.3124 |  | 7.2762 |  | 0.97527 |  | 1.4462 |  | 33.8944 |  | 46.2865 |  | 25.6953 |  | 0 |  | 0.98781 |  | 2.265 |  | 7.3124 | 7.2762 | 0.97527 | 1.4462 | 33.8944 | 46.2865 | 25.6953 |  | 0.98781 | 2.265 | 293883.8 | 17279.4 | 42564.8 | 75661.3 | 42699.2 | 108985 | 0 | 0 | 581073.5 | 37374.3 | 203 | 32118.6 | 215.4 | 36986.6 | 387.6 | 5156.1 | 23.1 |  |  | 88.63 | 113573044 | 880431.424 | 1053 | 107922 | 157542.8 | 1737.1 | 99100 | 200 | 93700 | 200 | 122100 | 400 | 101800 | 300 | 0 | 0 | 190 | 621282 | 1854.336 | 2160 | 445680 | 619632 | 2376 | 623136.336 | 619427.664 | 617256 | 7.239% | 12.1333 | 105 | Weather clear. ICR -10 Inv 01 GFDI -pro Internal Fault at 07:30 AM to 12:39 PM
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 6:17 | 18:23 | 9012.7 | 8982.7 | 8573.4 | 8647.3 | 8863.1 | 9085.6 | 8847.4 | 9410 | 8836.1 | 8727.2 | 9058.2 | 9013.5 | 9265.9 | 9055 | 9125.2 | 8953.4 | 12660 | 13603.7 | 12211.7 | 12687.3 | 13485.5 | 8306.9 | 12738.2 | 12776.6 | 12519.8 | 12523 | 12656.4 | 12766.4 | 10537.8 | 10879.9 | 10617.1 | 10651.6 | 10537.8 | 10835.6 | 10678.4 | 10548.8 | 8579.8 | 8653.3 | 8789.2 | 8776.9 | 8912.3 | 8718.7 | 12207.7 | 13459.5 | 9830.9 | 11760.7 | 11884 | 8450 | 9832 | 11705 | 12609 | 12494 | 7660 | 4698 | 7855.4 | 5600.1 | 7760.8 | 7159.6 | [16 empty] | 7.2675 |  | 7.2514 |  | 0.98195 |  | 1.4547 |  | 34.5648 |  | 47.9862 |  | 17.935 |  | 0 |  | 0.99358 |  | 2.646 |  | 7.2675 | 7.2514 | 0.98195 | 1.4547 | 34.5648 | 47.9862 | 17.935 |  | 0.99358 | 2.646 | 292392.2 | 17233.1 | 42686.4 | 82455.9 | 42600.6 | 107707.9 | 0 | 0 | 585076.1 | 37473.5 | 203.2 | 32211.7 | 215.6 | 37108.8 | 388 | 5257.9 | 23.5 |  |  | 88.8 | 114193997 | 882212.096 | 1055 | 108540 | 158402.4 | 1740 | 99200 | 200 | 93100 | 200 | 122200 | 400 | 101800 | 400 | 0 | 0 | 170 | 620953 | 1780.672 | 1440 | 444960 | 618912 | 2088 | 622733.672 | 619172.328 | 616824 | 6.436% | 12.1 | 105 | Weather clear
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 6:17 | 18:28 | 8853.7 | 8758.8 | 8252.6 | 8339.2 | 8597.8 | 8840.8 | 8555.1 | 9273 | 8632.3 | 8543.5 | 8856.2 | 8813.7 | 9078 | 8839.6 | 8950.2 | 8717.9 | 12252.3 | 13318.6 | 11766.4 | 12220.7 | 13197.8 | 8024.1 | 12337.5 | 12379.2 | 12093.1 | 12131.2 | 12212.9 | 12355.6 | 10262.6 | 10522.6 | 10227.3 | 10268.1 | 10186.8 | 10464.6 | 10327.1 | 10193.8 | 8312.1 | 8368 | 8536.1 | 8498.5 | 8691.2 | 8457.4 | 11825.1 | 13201.9 | 9565.8 | 11411.4 | 12366 | 9355 | 9972 | 11763 | 12657 | 12670 | 7694 | 4726 | 7930 | 5771 | 7817 | 7209 | [16 empty] | 6.9662 |  | 6.9427 |  | 0.96717 |  | 1.3974 |  | 34.5347 |  | 47.4384 |  | 15.7351 |  | 0 |  | 1.0984 |  | 2.439 |  | 6.9662 | 6.9427 | 0.96717 | 1.3974 | 34.5347 | 47.4384 | 15.7351 |  | 1.0984 | 2.439 | 284191.8 | 16680.1 | 41280.6 | 80187.4 | 41172.3 | 109930 | 0 | 0 | 573442.2 | 37569.5 | 203.4 | 32302.9 | 215.8 | 37227.3 | 388.4 | 5351.7 | 23.8 |  |  | 89 | 114789728 | 884037.76 | 1057 | 109133 | 159227 | 1743.4 | 96000 | 200 | 91200 | 200 | 118500 | 400 | 93800 | 300 | 0 | 0 | 200 | 595731 | 1825.664 | 1440 | 426960 | 593712 | 2448 | 597556.664 | 593905.336 | 591264 | 4.205% | 12.1833 | 105 | Weather clear
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 6:18 | 18:23 | 8818.1 | 8739 | 8249.6 | 8403.2 | 8608.1 | 8814.9 | 8587.6 | 9228.5 | 8600.8 | 8534.7 | 8811.6 | 8768.7 | 9042.5 | 8818.4 | 8920.7 | 8713.6 | 12239.4 | 13277.9 | 11765.7 | 12200.1 | 13202.5 | 8028 | 12361.4 | 12388.3 | 12092.3 | 12135 | 12197 | 12300.5 | 10194.7 | 10464.9 | 10179.5 | 10218.2 | 10184.4 | 10451.6 | 10298.4 | 10176.3 | 8251.2 | 8323.4 | 8509.1 | 8442.3 | 8654.5 | 8464.5 | 11700 | 13054 | 9537 | 11354 | 10428 | 8416 | 8246.8 | 11278.8 | 12168.8 | 12083.1 | 7292 | 4482.1 | 7887 | 5586 | 7561 | 7036 | 7563 | 7968 | 7245 | 4771 | 2742 | 0 | 2651 | 964 |  |  |  |  | 1318 | 1127 | 4697 | 8529 | 7.0081 |  | 7.0079 |  | 0.95771 |  | 1.4078 |  | 34.7292 |  | 48.1038 |  | 24.2883 |  | 0 |  | 1.0152 |  | 2.091 |  | 7.0081 | 7.0079 | 0.95771 | 1.4078 | 34.7292 | 48.1038 | 24.2883 |  | 1.0152 | 2.091 | 283848.1 | 16574.6 | 41057.3 | 79715.4 | 41110.7 | 118136.6 | 27547 | 6357 | 614346.7 | 37665.5 | 203.8 | 32392.9 | 216 | 37345.3 | 388.9 | 5451.5 | 24.2 |  |  | 89.21 | 115393232 | 886279.616 | 1060 | 109734 | 160062.2 | 1747.3 | 96000 | 400 | 90000 | 200 | 118000 | 500 | 99800 | 400 | 0 | 0 | 210 | 603504 | 2241.856 | 2160 | 432720 | 601344 | 2808 | 605745.856 | 601262.144 | 598536 | -1.4% | 12.0833 | 105 | Weather clear. ICR -10 Inv 01 GFDI -pro Internal Fault at 08:03 AM to 09:39 PM & ICR -04 Inv 04 DSP Internal Fault at 02:55 PM to 03:08 PM.
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 6:16 | 18:29 | 6436.5 | 6445.1 | 6030.3 | 6084.3 | 6257.3 | 6412.3 | 6209.6 | 6774.2 | 6286.7 | 6233.4 | 6510 | 6496.9 | 6660.2 | 6506.6 | 6591.8 | 6375.4 | 9136.6 | 9993.3 | 8662.3 | 8989 | 9946.3 | 6109.7 | 9183.6 | 9143.8 | 9029.1 | 9099 | 9036.5 | 9146.1 | 7474.9 | 7577.3 | 7275.8 | 7309.9 | 7375.6 | 7565.1 | 7484.9 | 7348.6 | 5878 | 5946 | 5997.5 | 5962 | 6123 | 6015.4 | 8492 | 9452 | 6861 | 8171 | 8594 | 7012 | 6011 | 8118 | 8849 | 8832 | 5308 | 3270 | 5839 | 4319 | 5884 | 5150 | 5377 | 5692 | 5475 | 3415 | 3119 | 0 | 1953 | 769 |  |  |  |  | 929 | 790 | 3402 | 6231 | 4.944 |  | 4.9407 |  | 0.74732 |  | 0.98833 |  | 33.1989 |  | 43.4801 |  | 26.8505 |  | 0 |  | 1.1836 |  | 3.045 |  | 4.944 | 4.9407 | 0.74732 | 0.98833 | 33.1989 | 43.4801 | 26.8505 |  | 1.1836 | 3.045 | 209785.9 | 11824 | 29637.9 | 57073.9 | 29774.2 | 88538 | 19959 | 5841 | 452433.9 | 37737 | 204 | 32460 | 216.3 | 37430.4 | 389.3 | 5526.7 | 24.7 |  |  | 89.42 | 115839008 | 888411.264 | 1063 | 110178 | 160679.4 | 1751 | 71500 | 200 | 67100 | 300 | 85100 | 400 | 75200 | 500 | 0 | 0 | 210 | 445776 | 2131.648 | 2160 | 319680 | 444384 | 2664 | 447907.648 | 443644.352 | 441720 | -1% | 12.2167 | 105 | Fully cloudy weather.
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 6:15 | 18:26 | 9324.2 | 9314.7 | 8849.7 | 8962 | 9144.1 | 9289.1 | 9085.7 | 9691.4 | 9068.5 | 9032.6 | 9300 | 9249.2 | 9517.8 | 9306.8 | 9408.6 | 9232.3 | 13058.3 | 13986 | 12585.8 | 13037.2 | 13881.7 | 8692 | 13099 | 13113.1 | 13034 | 13003 | 13036.4 | 13132.1 | 10754.7 | 11041.9 | 10776.1 | 10831.1 | 10850 | 11255.4 | 11071.8 | 10951 | 8947.8 | 9000.6 | 8997.6 | 8936.1 | 9133 | 9018.9 | 12419 | 13737 | 10126 | 12095 | 12774 | 10499 | 8851 | 12002 | 12657 | 13257 | 7942 | 4837 | 8539 | 6307 | 8021 | 7731 | 8045 | 8462 | 8232 | 5485 | 4662 | 0 | 2809 | 1118 |  |  |  |  | 1398 | 1196 | 4969 | 9008 | 7.5636 |  | 7.622 |  | 1.0114 |  | 1.4941 |  | 33.3874 |  | 46.4294 |  | 24.6889 |  | 0 |  | 0.83431 |  | 3.309 |  | 7.5636 | 7.622 | 1.0114 | 1.4941 | 33.3874 | 46.4294 | 24.6889 |  | 0.83431 | 3.309 | 301435.3 | 17948.4 | 43403.8 | 84462.6 | 44128.2 | 129988 | 30224 | 8589 | 660179.3 | 37839.2 | 204.2 | 32555.9 | 216.5 | 37555.7 | 389.7 | 5637.4 | 25.4 |  |  | 89.61 | 116487249 | 890774.336 | 1066 | 110824 | 161576.7 | 1755.2 | 102200 | 200 | 95900 | 200 | 125300 | 400 | 110700 | 700 | 0 | 0 | 190 | 648241 | 2363.072 | 2160 | 465120 | 646056 | 3024 | 650604.072 | 645877.928 | 643032 | -1.45% | 12.1833 | 105 | Weather clear
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 6:17 | 18:27 | 9045.6 | 9016.6 | 8559.4 | 8643.2 | 8841.5 | 9043.2 | 8808 | 9430.4 | 8821.4 | 8753.2 | 9023.9 | 8961.1 | 9250.4 | 9023.2 | 9145.3 | 8964.6 | 12709.7 | 13669.9 | 12193.2 | 12684.6 | 13469.6 | 8365.7 | 12677.4 | 12651.5 | 12563.7 | 12542 | 12625.5 | 12697 | 10367.9 | 10618.1 | 10351.7 | 10372.5 | 10509.9 | 10881.3 | 10704.8 | 10567.4 | 8592.3 | 8636 | 8707.8 | 8581.2 | 8819 | 8692.4 | 11953 | 13251 | 9785 | 11746 | 12188 | 10177 | 8450 | 11425 | 10979 | 11052 | 7513 | 4616 | 8072 | 5967 | 7671 | 7589 | 7619 | 8011 | 7808 | 5201 | 4484 | 0 | 2654 | 1070 |  |  |  |  | 1323 | 1130 | 4716 | 8528 | 7.2595 |  | 7.3132 |  | 0.97668 |  | 1.4423 |  | 34.4163 |  | 47.6686 |  | 24.3535 |  | 0 |  | 0.93262 |  | 2.835 |  | 7.2595 | 7.3132 | 0.97668 | 1.4423 | 34.4163 | 47.6686 | 24.3535 |  | 0.93262 | 2.835 | 292180.8 | 17228.3 | 41710.2 | 81535.4 | 42663.4 | 121396 | 28639 | 8208 | 633561.1 | 37938.2 | 204.4 | 32648.9 | 216.7 | 37676.7 | 390 | 5741.2 | 25.9 |  |  | 89.78 | 117109415 | 892512.128 | 1068 | 111443 | 162437.9 | 1758.1 | 99000 | 200 | 93000 | 200 | 121000 | 300 | 103800 | 500 | 0 | 0 | 170 | 622166 | 1737.792 | 1440 | 445680 | 620064 | 2088 | 623903.792 | 620428.208 | 617976 | -1.524% | 12.1667 | 106 | Weather clear. ICR-10 Inv 03 Intarnal Breakdown at 06:30 AM to 09:07 AM.
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 6:14 | 18:26 | 9096.8 | 9075.3 | 8571.1 | 8660.4 | 8916.2 | 9141.4 | 8845.4 | 9479.9 | 8364.2 | 8255.9 | 8519.7 | 8511.7 | 8778.2 | 8507.8 | 8658.8 | 8488.2 | 11883.9 | 12903.8 | 11392.9 | 11828.4 | 13538.8 | 8332.7 | 12677.1 | 12651.2 | 12603.2 | 12534 | 12618.1 | 12721 | 10478.7 | 10720.1 | 10447.3 | 10462.2 | 10534.9 | 10894.5 | 10701.3 | 10592.2 | 8618.2 | 8692.9 | 8790.1 | 8696.7 | 8934.3 | 8774.8 | 12425 | 13277 | 9780 | 11735 | 12190 | 10335 | 8464 | 11435 | 10985 | 11069 | 7519 | 4601 | 8109 | 5857 | 7817 | 7160 |  |  |  |  | 5172 | 0 | 2690 | 1259 | [8 empty] | 7.25 |  | 7.319 |  | 0.973 |  | 1.45 |  | 34.659 |  | 46.444 |  | 25.8 |  | 0 |  | 1.127 |  | 3.234 |  | 7.25 | 7.319 | 0.973 | 1.45 | 34.659 | 46.444 | 25.8 |  | 1.127 | 3.234 | 285556.1 | 17311.1 | 42108.3 | 82412.9 | 42722.9 | 105541 | 0 | 9121 | 584773.3 | 38035.1 | 204.7 | 32739.9 | 217 | 37798.4 | 390.5 | 5848.7 | 26.8 |  |  | 90.04 | 117731704 | 895351.616 | 1072 | 112063 | 163299.2 | 1763.1 | 96900 | 300 | 91000 | 300 | 121700 | 500 | 107500 | 900 | 0 | 0 | 260 | 622289 | 2839.488 | 2880 | 446400 | 620136 | 3600 | 625128.488 | 619449.512 | 616536 | 6.901% | 12.2 | 106 | Weather clear
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 6:13 | 18:34 | 8835.5 | 8799.2 | 8388.5 | 8456.3 | 8664.6 | 8885.8 | 8612.3 | 9211.9 | 8629.9 | 8532.6 | 8769.2 | 8765 | 9043.9 | 8794.2 | 8957.7 | 8786.6 | 12381.3 | 13343.7 | 11890.1 | 12276.5 | 13273.8 | 8229.7 | 12495.8 | 12460.8 | 12428 | 12392 | 12459.7 | 12551.2 | 9070.2 | 9304.1 | 9044.7 | 9066.7 | 10284.4 | 10640.1 | 10455.5 | 10341 | 8407.1 | 8477 | 8562.7 | 8488 | 8671.6 | 8551.4 | 11663.5 | 13052 | 9659.7 | 11527.1 | 12103.9 | 10113.5 | 8303.4 | 11370 | 10689 | 11087 | 7526.2 | 4627 | 8173 | 6082 | 7704 | 7640 | 7685 | 8095 | 7857 | 6302 | 5960 | 0 | 2650 | 1240 |  |  |  |  | 1311 | 1119 | 4712 | 8521 | 7.1097 |  | 7.1731 |  | 0.95907 |  | 1.417 |  | 34.7804 |  | 46.7997 |  | 25.7319 |  | 0 |  | 1.3726 |  | 3.303 |  | 7.1097 | 7.1731 | 0.95907 | 1.417 | 34.7804 | 46.7997 | 25.7319 |  | 1.3726 | 3.303 | 286315.8 | 16884.1 | 36485.7 | 80176 | 41721 | 121082 | 29939 | 9850 | 622453.6 | 38180.1 | 205.2 | 32874.7 | 217.4 | 37970.9 | 391 | 6009.1 | 27.9 |  |  | 90.38 | 118345875 | 898020.608 | 1075 | 112675 | 164149.3 | 1767.7 | 145000 | 500 | 134800 | 400 | 172500 | 500 | 160400 | 1100 | 0 | 0 | 340 | 614171 | 2668.992 | 2160 | 440640 | 612072 | 3312 | 616839.992 | 611502.008 | 608760 | -0.9019% | 12.35 | 106 | Weather clear
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 6:14 | 18:29 | 8791.2 | 8750.1 | 8252.9 | 8346.7 | 8587.3 | 8831.8 | 8523.8 | 9187.6 | 8571.4 | 8484.6 | 8749.6 | 8725.4 | 8991.4 | 8706.8 | 8942.4 | 8728.6 | 12207.9 | 13295.8 | 11746 | 12207.7 | 13204.2 | 8072.8 | 12289.5 | 12239.9 | 12196.9 | 12146.9 | 12231.6 | 12333.9 | 10145 | 10411.5 | 10122.3 | 10169.6 | 10177.4 | 10539.1 | 10340.3 | 10236.8 | 8335.3 | 8402.2 | 8483.4 | 8412.5 | 8648 | 8496.5 | 11551.7 | 13067.4 | 9559.5 | 11438.3 | 11783.5 | 9850.1 | 8095.2 | 11067.7 | 10767 | 11072 | 7309.9 | 4497.2 | 7935.2 | 5894.5 | 7435 | 7400.8 | 7392.7 | 7848 | 7532.2 | 6042.4 | 6009.8 | 0 | 2584.1 | 1205.4 |  |  |  |  | 1273.8 | 1086 | 4590.8 | 8331.3 | 6.9949 | 6.594 | 7.0734 | 6.472 | 0.96664 | 1.138 | 1.408 | 1.236 | 34.279 | 34.417 | 47.0722 | 44.051 | 24.8578 | 24.924 | 0 | 0 | 0.99899 | 1.103 | 3.087 | 3.051 | 6.7944 | 6.7727 | 1.0523 | 1.322 | 34.348 | 45.5616 | 24.8909 |  | 1.051 | 3.069 | 283344.7 | 16737.5 | 40848.4 | 79657.3 | 41293.6 | 118390 | 28815.3 | 9799.3 | 618886.1 | 38323.2 | 205.3 | 33009.7 | 217.6 | 38146.7 | 391.2 | 6165.1 | 28.1 |  |  | 90.59 | 118956154 | 898801.66 | 1076 | 113283 | 164994.1 | 1769 | 143100 | 100 | 135000 | 200 | 175800 | 200 | 156000 | 200 | 0 | 0 | 210 | 610279 | 781.052 | 720 | 437760 | 608256 | 936 | 611060.052 | 609497.948 | 607320 | -1.265% | 12.25 | 106 | Weather clear
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 6:14 | 18:21 | 8440.5 | 8429.9 | 8032.9 | 8090.2 | 8297.1 | 8510.5 | 8296.9 | 8828.4 | 8227.5 | 8228.5 | 8512 | 8439.3 | 8640.6 | 8467 | 8635.2 | 8443 | 11989.6 | 12916.3 | 11504.6 | 11939.7 | 12876.4 | 8040.9 | 12101.2 | 12059.2 | 12001.7 | 11971.6 | 12028.1 | 12101 | 9989.3 | 10214.9 | 9918 | 10012.2 | 9922.6 | 10249.2 | 10086.5 | 9964.3 | 8058.3 | 8132.7 | 8209.2 | 8174.1 | 8335.2 | 8208.2 | 11368.8 | 12731.5 | 9297.9 | 11102.9 | 11279.9 | 9405.5 | 7761.8 | 10624 | 10656 | 11054 | 6976.2 | 4397.3 | 7600.7 | 5683.8 | 7137 | 7096 | 7080.2 | 7497.9 | 7229.7 | 5831.3 | 5742.8 | 0 | 2476.9 | 1155.2 |  |  |  |  | 1212.9 | 1032.7 | 4373.8 | 7967.3 | 6.8395 | 6.3734 | 6.8447 | 6.2488 | 0.98368 | 1.0727 | 1.3549 | 1.1839 | 35.0457 | 35.007 | 48.1279 | 45.5367 | 21.831 | 23.3449 | 0 | 0 | 1.209 | 1.2595 | 3.093 | 3.609 | 6.6065 | 6.5467 | 1.0282 | 1.2694 | 35.0263 | 46.8323 | 22.588 |  | 1.2342 | 3.351 | 276049.8 | 16191 | 40134.4 | 77427.8 | 40222.6 | 114258.9 | 27639.1 | 9374.9 | 601298.5 | 38463.6 | 205.7 | 33140.5 | 217.9 | 38318 | 391.8 | 6314.5 | 28.9 |  |  | 90.91 | 119548133 | 901027.712 | 1079 | 113872 | 165813.5 | 1772.9 | 140400 | 400 | 130800 | 300 | 171300 | 600 | 149400 | 800 | 0 | 0 | 320 | 591979 | 2226.052 | 2160 | 424080 | 589968 | 2808 | 594205.052 | 589752.948 | 587160 | -1.18% | 12.1167 | 106 | Moving cloudy weather.
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 6:12 | 18:29 | 8397.4 | 8262.7 | 7810.7 | 8074.8 | 8287.7 | 8511.4 | 8245.9 | 8884.4 | 8053.5 | 8060 | 8306.4 | 8129.9 | 8424 | 8210 | 8423.1 | 8139.9 | 11358.9 | 12339.9 | 11011.7 | 11496.5 | 12312 | 7667.7 | 11504.3 | 11589.4 | 11396.2 | 11727 | 11445.7 | 11508.6 | 10052.8 | 10262.9 | 10099.2 | 10138.5 | 8626.3 | 8908.4 | 8771 | 8674.8 | 8164.8 | 8200.9 | 8327.3 | 8297.3 | 8440.2 | 8291 | 11474.2 | 12684.2 | 9407.5 | 11279.8 | 10819.9 | 9086.2 | 7473 | 10174.4 | 10948.5 | 11110.5 | 6823 | 4139.7 | 7310.1 | 5430.4 | 6834.6 | 6788.8 | 6888 | 7309.4 | 7103.3 | 5697.9 | 5345.6 | 945.2 | 2405.2 | 1134.5 |  |  |  |  | 1183.2 | 1009 | 4281.4 | 7755.2 | 6.7846 | 6.4731 | 6.8618 | 6.616 | 0.92739 | 1.1397 | 1.3817 | 1.2309 | 34.1376 | 34.3347 | 45.9728 | 44.1284 | 22.1825 | 23.9055 | 0 | 0 | 1.3179 | 1.4375 | 3.237 | 3.039 | 6.6289 | 6.7389 | 1.0335 | 1.3063 | 34.2362 | 45.0506 | 23.044 |  | 1.3777 | 3.138 | 267579.7 | 16365.7 | 40553.4 | 78201.5 | 34980.5 | 111167.9 | 26998.6 | 9830.5 | 585677.8 | 38597.9 | 206 | 33268.5 | 218.3 | 38485.5 | 392.1 | 6459.7 | 29.5 |  |  | 91.2 | 120123752 | 902716.288 | 1081 | 114445 | 166610.2 | 1776 | 134300 | 300 | 128000 | 400 | 167500 | 300 | 145200 | 600 | 0 | 0 | 290 | 575619 | 1688.576 | 1440 | 412560 | 573624 | 2232 | 577307.576 | 573930.424 | 571392 | -1.429% | 12.2833 | 106 | Moving cloudy weather.
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 6:12 | 18:31 | 9229.8 | 9178.8 | 8547.6 | 8639 | 8867 | 9134.4 | 8875.8 | 9611.9 | 8868.7 | 8782.7 | 9192 | 9022 | 9315.7 | 9153 | 9296.7 | 9067.1 | 12592.3 | 13604.8 | 12121.5 | 12578.1 | 12257.7 | 7548.9 | 11418.7 | 11547.7 | 11286.1 | 11238.7 | 11361.7 | 11462.9 | 10490.1 | 10710.5 | 10484.4 | 10537.9 | 10573 | 10923.3 | 10718.4 | 10590.9 | 8055.5 | 8103.8 | 8786.9 | 8712.7 | 8960.9 | 8778 | 12137.3 | 13418.4 | 9794.1 | 11728.1 | 12064.5 | 10082.1 | 8312.8 | 11359.2 | 10650 | 11289 | 12203.8 | 7579 | 8236.8 | 6125 | 7677.4 | 7620.9 | 7734.1 | 8248.8 | 8010.4 | 6433.4 | 7811.5 | 1298.2 | 2687.1 | 1449.7 |  |  |  |  | 1353.3 | 1139.9 | 4800.1 | 8632.5 | 7.1994 | 6.7505 | 7.3277 | 6.7175 | 1.0031 | 1.1585 | 1.4494 | 1.2676 | 32.1904 | 32.3048 | 45.6109 | 43.3049 | 30.3379 | 32.2417 | 0 | 0 | 1.1477 | 1.2743 | 3.474 | 3.594 | 6.9749 | 7.0226 | 1.0808 | 1.3585 | 32.2476 | 44.4579 | 31.2898 |  | 1.211 | 3.534 | 283801.3 | 16159.3 | 42222.9 | 82316.4 | 42805.6 | 129126.3 | 30426.7 | 13246.5 | 640105 | 38735.6 | 206.3 | 33407.5 | 218.6 | 38666.2 | 392.6 | 6621.4 | 30.4 |  |  | 91.51 | 120745099 | 905073.088 | 1084 | 115064 | 167470.2 | 1780 | 137700 | 300 | 139000 | 300 | 180700 | 500 | 161700 | 900 | 0 | 0 | 310 | 621347 | 2356.8 | 2160 | 445680 | 619200 | 2880 | 623703.8 | 618990.2 | 616320 | -2.562% | 12.3167 | 106 | Moving cloudy weather.
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 6:37 | 19:35 | 8716.4 | 8674.7 | 8088.5 | 8157.3 | 8396.9 | 8675.4 | 8411 | 9112.4 | 8399.5 | 8325 | 8734.1 | 8587.6 | 8823.4 | 8700.2 | 8830.5 | 8590.2 | 11990 | 13023.4 | 11496.1 | 11903.2 | 12992.4 | 8021 | 12116.8 | 12228.9 | 11980.3 | 11906.3 | 12012.5 | 12132.6 | 10046.1 | 10230.9 | 9980.5 | 10078.7 | 10074.3 | 10415.6 | 10249.4 | 10138.4 | 8139.8 | 8201.9 | 8347.3 | 8307.2 | 8566.4 | 8403.8 | 11650.4 | 12918.4 | 9328.9 | 11175.2 | 11209.9 | 9380.6 | 7766.9 | 10547.1 | 11235 | 11350 | 6924.1 | 4286.2 | 7651.3 | 5546.2 | 7183.4 | 7129.3 | 7165.1 | 7373 | 7445.5 | 5977.7 | 6126.4 | 1478.9 | 2872.8 | 1542.5 |  |  |  |  | 1247.7 | 1041.9 | 4464.4 | 8160.1 | 6.8117 | 6.275 | 6.9184 | 6.35 | 6.9184 | 1.12 | 1.3562 | 1.154 | 31.7502 | 33.205 | 46.448 | 42.202 | 33.4677 | 31.1 | 0 | 0 | 1.14 | 1.109 | 4.368 | 3.434 | 6.5434 | 6.6342 | 4.0192 | 1.2551 | 32.4776 | 44.325 | 32.2838 |  | 1.1245 | 3.901 | 279026.6 | 16341.7 | 40336.2 | 78697.6 | 40877.7 | 115124.1 | 27961.3 | 12020.6 | 610385.8 | 38876.3 | 206.6 | 33540.6 | 218.9 | 38839.8 | 393.1 | 6773.8 | 31.1 |  |  | 91.78 | 121345286 | 906982.336 | 1086 | 115662 | 168300.7 | 1783.3 | 140700 | 300 | 133100 | 300 | 173600 | 500 | 152400 | 700 | 0 | 0 | 270 | 600187 | 1909.248 | 1440 | 430560 | 597960 | 2376 | 602096.248 | 598277.752 | 595584 | -1.358% | 12.9667 | 106 | Moving cloudy weather.
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 6:14 | 17:53 | 8590.2 | 8548.6 | 8171 | 8240.9 | 8468.7 | 8664 | 8408.5 | 8982.5 | 8421.4 | 8381.6 | 8687 | 8633.4 | 8862.7 | 8724.4 | 8751.3 | 8474.8 | 11980.8 | 12942.5 | 11570.5 | 12099 | 12828.5 | 8142.8 | 12097.7 | 12293.1 | 12022.8 | 11949.5 | 11940.8 | 12051.7 | 10102.8 | 10344.6 | 10059 | 10165.1 | 10099.8 | 10427.5 | 10270.6 | 10134.9 | 8257.6 | 8331.5 | 8362.5 | 8323.8 | 8513.8 | 8197.7 | 11718.8 | 12766.8 | 9440 | 11395.2 | 11759 | 9799.5 | 8131.8 | 11103.3 | 12037.2 | 11993.5 | 7142.5 | 4461.8 | 7235 | 5230 | 6932 | 6909 | 6858 | 7030 | 7134 | 5875 | 6173.1 | 1514.3 | 2961.2 | 1547.8 |  |  |  |  | 1210 | 1009 | 4231 | 7985 | 6.6926 | 6.5573 | 6.7917 | 6.2313 | 0.89071 | 0.93697 | 1.2269 | 1.0783 | 28.1879 | 27.9317 | 41.9003 | 39.1269 | 53.4182 | 57.7609 | 0 | 0 | 1.3612 | 1.3311 | 5.856 | 5.892 | 6.6249 | 6.5115 | 0.91384 | 1.1526 | 28.0598 | 40.5136 | 55.5896 |  | 1.3462 | 5.874 | 278930.7 | 16589.1 | 40671.5 | 78718.6 | 40932.8 | 117169.6 | 26897 | 12196.4 | 612105.7 | 39017 | 207 | 33673.9 | 219.2 | 39013.8 | 393.7 | 6932.2 | 31.3 |  |  | 92.04 | 121951952 | 908554.176 | 1089 | 116266 | 169140.1 | 1786.2 | 140700 | 400 | 133300 | 300 | 174000 | 600 | 158400 | 200 | 0 | 0 | 260 | 606666 | 1571.84 | 2160 | 434880 | 604368 | 2088 | 608237.84 | 605094.16 | 602280 | -0.6319% | 11.65 | 106 | Moving cloudy weather.
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 6:07 | 18:32 | 8765 | 8719 | 8366 | 8505 | 8762 | 8929 | 8630 | 9171 | 8577 | 8588 | 8858 | 8807 | 9012 | 8898 | 8935 | 8577 | 12187 | 13013 | 11857 | 12234 | 12963 | 8403 | 12283 | 12439 | 12204 | 12194 | 12176 | 12441 | 10748 | 10996 | 10712 | 10835 | 10100 | 10428 | 10922 | 10782 | 8648 | 8710 | 7266 | 7230 | 7378 | 7133 | 11100 | 11943 | 9038 | 10852 | 12117 | 10231 | 8488 | 11592 | 12369 | 12321 | 7296 | 4623 | 8293 | 5966 | 7742 | 7668 | 7582 | 7739 | 7859 | 7232 | 6468 | 2698 | 3075 | 1613 |  |  |  |  | 1324 | 1114 | 4735 | 8511 | 6.769 | 6.896 | 6.951 | 6.899 | 0.907 | 1.004 | 1.263 | 1.133 | 26.716 | 26.552 | 41.007 | 38.632 | 52.8 | 55.662 | 0 | 0 | 1.164 | 1.175 | 4.47 | 3.84 | 6.8325 | 6.925 | 0.9555 | 1.198 | 26.634 | 39.8195 | 54.231 |  | 1.1695 | 4.155 | 284493 | 17358 | 43291 | 71940 | 42232 | 124390 | 30412 | 13854 | 627970 | 39160.2 | 207.2 | 33810 | 219.6 | 39187.4 | 393.8 | 7097.3 | 31.4 |  |  | 92.3 | 122570506 | 909515.264 | 1090 | 116882 | 169996.2 | 1788.5 | 143200 | 200 | 136100 | 400 | 173600 | 100 | 165100 | 100 | 0 | 0 | 260 | 618554 | 961.088 | 720 | 443520 | 616392 | 1656 | 619515.088 | 617592.912 | 614736 | -1.346% | 12.4167 | 106 | Moving cloudy weather.
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 6:42 | 18:25 | 4199.9 | 4166.9 | 3878.4 | 3887.4 | 4024 | 4180 | 3980.4 | 4500.5 | 4073 | 3984.4 | 4161.2 | 4157.6 | 4305.8 | 4188.9 | 4290.2 | 4096.1 | 5806.2 | 6561.3 | 5625.3 | 5882.7 | 6411.4 | 3910 | 5826.2 | 5911.9 | 5757.6 | 5663 | 5759.5 | 5804 | 4643.9 | 4766.1 | 4609.1 | 4668 | 4633.5 | 4794 | 4709.2 | 4669.9 | 3717.1 | 3753.5 | 3767 | 3733.6 | 3835.7 | 3699.1 | 11700 | 13054 | 9537 | 11354 | 10428 | 8416 | 8246.8 | 11728.8 | 12168.3 | 12083.1 | 7292 | 4482.1 | 7887 | 5586 | 7561 | 7036 | 7563 | 7968 | 7245 | 4771 | 2742 | 1990 | 2631 | 964.1 |  |  |  |  | 1318 | 1127 | 4697 | 8529 | 2.8944 | 2.7065 | 2.8901 | 0.39562 | 0.37744 | 2.7065 | 0.55234 | 2.6992 | 27.2227 | 27.1461 | 37.9652 | 35.3528 | 53.5438 | 55.5985 | 0 | 0 | 0.76299 | 0.77621 | 1.827 | 2.049 | 2.8004 | 1.6429 | 1.542 | 1.6258 | 27.1844 | 36.659 | 54.5712 |  | 0.7696 | 1.938 | 134993.8 | 7470.6 | 18687.1 | 60680.4 | 18806.6 | 118586.1 | 27547 | 8327.1 | 395098.7 | 39228.9 | 207.6 | 33876.4 | 220 | 39268.1 | 394.5 | 7179.6 | 32 |  |  | 92.54 | 122867957 | 911764.736 | 1093 | 117178 | 170407.9 | 1792.4 | 68700 | 400 | 66400 | 400 | 80700 | 700 | 82300 | 600 | 0 | 0 | 240 | 297451 | 2249.472 | 2160 | 213120 | 296424 | 2808 | 299700.472 | 295201.528 | 293616 | -24.15% | 11.7167 | 111 | Cloudy weather
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 6:10 | 18:30 | 7936.5 | 7902.1 | 7513.3 | 7523.4 | 7712.1 | 7942.9 | 7690.3 | 8358.3 | 7771.4 | 7680.4 | 8021 | 7996.7 | 8221.8 | 8114.8 | 8158.6 | 7863.1 | 11176.9 | 11969.5 | 10812.3 | 11177.2 | 11700.4 | 7362.7 | 10993 | 11382.3 | 10975.5 | 10934 | 11012.4 | 11276.1 | 9147.7 | 9353.9 | 9164.6 | 9341.7 | 9220.3 | 9570.7 | 9355.7 | 9302.9 | 7467.2 | 7573.6 | 7557.6 | 7535.4 | 7708 | 7477.8 | 10618 | 11660 | 8812 | 10634 | 10621 | 8996 | 7428 | 10148 | 10791 | 10780 | 6444 | 4120 | 7345 | 5290 | 6980 | 6836 | 7108 | 6890 | 7332 | 6656 | 6871 | 3052 | 2731 | 1587 |  |  |  |  | 1173 | 984 | 4206 | 7468 | 6.6069 | 6.1783 | 6.784 | 6.2101 | 0.89711 | 0.92603 | 1.3424 | 6.2101 | 30.2015 | 30.2779 | 45.5748 | 42.8632 | 52.3645 | 53.2849 | 0 | 0 | 0.86715 | 0.9381 | 2.625 | 2.706 | 6.3926 | 6.497 | 0.91157 | 3.7762 | 30.2397 | 44.219 | 52.8247 |  | 0.90263 | 2.6655 | 257179 | 15040.8 | 37007.9 | 72002.8 | 37449.6 | 109610 | 27986 | 14241 | 570517.1 | 39358.7 | 208 | 33992.3 | 220.3 | 39427.3 | 395.1 | 7328.5 | 32.3 |  |  | 92.81 | 123429380 | 913647.616 | 1096 | 117737 | 171185 | 1795.8 | 129800 | 400 | 115900 | 300 | 159200 | 600 | 148900 | 300 | 0 | 0 | 270 | 561423 | 1882.88 | 2160 | 402480 | 559512 | 2448 | 563305.88 | 559540.12 | 557064 | -1.264% | 12.3333 | 111 | Cloudy weather. Power Trafo Trip 09:59 AM To 10:18 AM
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 6:09 | 18:28 | 8530.9 | 8513.9 | 8073.1 | 8182.9 | 8417.3 | 8601.6 | 8288.6 | 8940.7 | 8350.6 | 8288.1 | 8599.4 | 8559.8 | 8843 | 8664.8 | 8739.5 | 8446.6 | 12089.4 | 13088.5 | 11595.3 | 12094.9 | 13202.2 | 8147.5 | 12052.9 | 12258.3 | 12017.3 | 12012.4 | 11934.1 | 12059 | 9879.2 | 10131.4 | 9845.3 | 9967.3 | 9961 | 10289.2 | 10118.8 | 10014.5 | 8133 | 8232.8 | 8177 | 8147.7 | 8379.9 | 8124 | 11616.3 | 12781.2 | 9421.5 | 11426.9 | 11582.9 | 9710 | 8096.4 | 10923 | 11530 | 11510 | 6969.7 | 4440.3 | 8026.1 | 5758.1 | 7706.6 | 7475.6 | 7923.2 | 7568.9 | 8571.1 | 7674.8 | 6871.2 | 3051.5 | 3049.2 | 1740.2 |  |  |  |  | 1251.6 | 1052.4 | 4499 | 8192.3 | 6.694 | 6.5346 | 6.8187 | 6.483 | 0.89043 | 0.98447 | 1.3779 | 1.1163 | 31.2046 | 31.4198 | 45.431 | 43.2415 | 50.1297 | 50.894 | 0 | 0 | 1.1677 | 1.2757 | 3.405 | 3.744 | 6.6143 | 6.6509 | 0.93745 | 1.2471 | 31.3122 | 44.3363 | 50.5118 |  | 1.2217 | 3.5745 | 278592.6 | 16365.8 | 39823.2 | 78074.5 | 40383.5 | 118724 | 31738 | 14712.1 | 618413.7 | 39500.2 | 208.4 | 34119.9 | 220.6 | 39599.4 | 395.7 | 7493 | 33.1 |  |  | 93.08 | 124039970 | 915893.184 | 1098 | 118346 | 172029.9 | 1799.6 | 141500 | 400 | 127600 | 300 | 172100 | 600 | 164500 | 800 | 0 | 0 | 270 | 610590 | 2245.568 | 1440 | 438480 | 608328 | 2736 | 612835.568 | 608344.432 | 605592 | -0.902% | 12.4 | 111 | Cloudy weather
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 6:11 | 18:12 | 6311.3 | 6224.5 | 5851.8 | 5901.8 | 6163.3 | 6454 | 6079.9 | 6861.2 | 5936.2 | 5960.2 | 6215.4 | 6173.3 | 6325.4 | 6240.6 | 6286 | 5994.6 | 8467.9 | 9308.7 | 8176.1 | 8480.2 | 9686.1 | 5949.3 | 8892 | 9006.2 | 8757.6 | 8658 | 8699.3 | 8803.2 | 7834.3 | 7908.9 | 7614.2 | 7714.1 | 7809.9 | 8027.6 | 8004.8 | 7833.5 | 6317 | 6360.7 | 6311 | 6278.4 | 6433.3 | 6218.1 | 9263 | 10253 | 7522 | 9031 | 9399 | 7899 | 6760 | 8923 | 9643 | 9742 | 5804 | 3563 | 6330 | 4562 | 5938 | 5864 | 6412 | 5956 | 6757 | 6054 | 7001 | 3538 | 2906 | 1357 |  |  |  |  | 981 | 821 | 3573 | 6521 | 4.9531 | 5.0946 | 5.0114 | 5.0278 | 0.72586 | 0.72519 | 1.0113 | 5.0278 | 30.3556 | 30.704 | 43.101 | 41.6247 | 53.9242 | 52.9687 | 0.039571 | 0 | 0.97939 | 0.99715 | 3.81 | 4.38 | 5.0238 | 5.0196 | 0.72552 | 3.0195 | 30.5298 | 42.3628 | 53.4464 | 0.039571 | 0.98827 | 4.095 | 201864.1 | 12677.7 | 31071.5 | 61309.8 | 31675.8 | 96323 | 25179 | 14802 | 474902.9 | 39602.3 | 208.8 | 34215.7 | 221 | 39734.3 | 396.4 | 7626.7 | 34.1 |  |  | 93.36 | 124507570 | 918594.88 | 1102 | 118811 | 172676.9 | 1804.1 | 102100 | 400 | 95800 | 400 | 134900 | 700 | 133700 | 1000 | 0 | 0 | 280 | 467600 | 2701.696 | 2880 | 334800 | 465840 | 3240 | 470301.696 | 464898.304 | 462600 | -0.9689% | 12.4 | 111 | fully cloudy weather & rain slowly
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 6:18 | 17:56 | 6592.3 | 6570.9 | 6189.4 | 6189 | 6393.3 | 6629.7 | 6335.8 | 6963.2 | 6314.5 | 6209 | 6474.4 | 6478.7 | 6691.7 | 6663.1 | 6580.9 | 6295.3 | 9197.8 | 10111.1 | 8749.1 | 9227.1 | 9930.1 | 6147.4 | 9199.9 | 9440.1 | 9085.9 | 9078 | 9078.7 | 9224.4 | 8055.3 | 8268.6 | 8078.3 | 8166.8 | 8098.8 | 8408.2 | 8242.7 | 8155.3 | 1539.4 | 6642.9 | 6704.3 | 6667.5 | 6804.9 | 6570.8 | 9415.3 | 10380.6 | 7715.5 | 9175 | 9147 | 7619 | 6472 | 8609 | 9389 | 9453 | 3402 | 3325 | 6240 | 4562 | 5891 | 5976 | 6434 | 6062 | 6612 | 6032 | 6795 | 3583 | 2837 | 1464 |  |  |  |  | 977 | 821 | 3577 | 6374 | 5.0292 | 5.2712 | 5.0541 | 5.1416 | 0.70068 | 0.7644 | 0.98662 | 0.87329 | 30.6094 | 30.8831 | 43.3143 | 41.9206 | 56.7212 | 56.6688 | 0.0086025 | 0 | 1.1711 | 1.2462 | 3.753 | 3.783 | 5.1502 | 5.0979 | 0.73254 | 0.92995 | 30.7463 | 42.6175 | 56.695 | 0.0086025 | 1.2086 | 3.768 | 212040.8 | 8182.3 | 32569 | 63433.9 | 32905 | 91834 | 25140 | 14679 | 480784 | 39710 | 209.2 | 34316.1 | 221.4 | 39874.5 | 397.1 | 7755.8 | 35.1 |  |  | 93.61 | 124986056 | 921149.632 | 1105 | 119288 | 173339.1 | 1808.4 | 107700 | 400 | 100400 | 400 | 140200 | 700 | 129100 | 1000 | 0 | 0 | 250 | 478486 | 2554.752 | 2160 | 343440 | 476784 | 3096 | 481040.752 | 475931.248 | 473688 | 0.0534% | 12.4 | 111 | fully cloudy weather & rain slowly
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 6:39 | 18:28 | 4633.6 | 4482.6 | 4244.9 | 4323.7 | 4449.7 | 4624.2 | 4417.9 | 4962.7 | 4493.6 | 4399.4 | 4558.6 | 4497 | 4751.9 | 4577.6 | 4679.5 | 4435.9 | 6242.3 | 7042.3 | 6074.4 | 6380.9 | 6811.4 | 4130.9 | 6194.1 | 6350.7 | 6208.1 | 6184.7 | 6217.9 | 6265.1 | 5286.5 | 5443.9 | 5350.4 | 5414.7 | 5359.9 | 5583.3 | 5449.6 | 5433.9 | 1539.4 | 4428.8 | 4415.3 | 4370.4 | 4507.8 | 4446.3 | 6183.9 | 7057.9 | 5169.2 | 6266 | 6098.8 | 5136 | 4333.9 | 5835.6 | 9050 | 9175 | 3623.3 | 1525.1 | 4122.5 | 2393.2 | 3950.6 | 3975.2 | 4353.2 | 4117.4 | 4532.3 | 4043 | 4670.3 | 2579.9 | 1915.9 | 976.3 |  |  |  |  | 627.3 | 521.5 | 2508.4 | 4341.9 | 3.2975 | 3.3833 | 3.4431 | 3.4629 | 0.39895 | 0.53685 | 0.63484 | 0.56911 | 30.2638 | 30.5108 | 41.1582 | 39.4433 | 58.0468 | 58.3426 | 0 | 0 | 1.1238 | 1.2338 | 1.2338 | 2.745 | 3.3404 | 3.453 | 0.4679 | 0.60198 | 30.3873 | 40.3008 | 58.1947 |  | 1.1788 | 1.9894 | 146635.6 | 5968.2 | 21495.5 | 42416.8 | 21826.7 | 67218.3 | 17045.9 | 10142.4 | 332749.4 | 39783.7 | 209.7 | 34387.6 | 221.8 | 39968.3 | 397.9 | 7843.8 | 36.1 |  |  | 93.88 | 125313302 | 923961.344 | 1108 | 119614 | 173792.1 | 1813.2 | 73700 | 500 | 71500 | 400 | 93800 | 800 | 88000 | 1000 | 0 | 0 | 270 | 327246 | 2811.712 | 2160 | 234720 | 326160 | 3456 | 330057.712 | 324434.288 | 322704 | -0.8089% | 12.4 | 111 | fully cloudy weather
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 6:17 | 18:26 | 6118.3 | 5926.4 | 5629.2 | 5730.8 | 5877.4 | 6080 | 5836 | 6531.7 | 5979.8 | 5818.3 | 6041.1 | 5997.9 | 6327.5 | 6089.1 | 6230.8 | 5957.2 | 7754 | 8775 | 7603.5 | 8006.6 | 8510.5 | 5179.1 | 7756.6 | 7943.1 | 7749 | 7685.8 | 7767.4 | 7790.3 | 6841.9 | 7054.3 | 6852.5 | 6915.3 | 6897.4 | 7129.7 | 6978.9 | 6918.1 | 5578.6 | 5624.3 | 5679.6 | 5619.4 | 5756.4 | 5652.1 | 7884.7 | 8922.8 | 6459.9 | 7838.3 | 8246.3 | 6904.9 | 5781 | 7794.7 | 1123 | 1113.5 | 5294 | 3559.1 | 5465.7 | 3095.7 | 5203.1 | 5272.3 | 5838.8 | 5455.9 | 6128.6 | 5579 | 6108.4 | 3863.6 | 2500.1 | 1406.9 |  |  |  |  | 862.3 | 721.3 | 3313.7 | 5698.7 | 4.4299 | 4.2537 | 4.7243 | 4.3613 | 0.49737 | 0.68892 | 0.87055 | 0.72543 | 31.2839 | 31.4795 | 43.8824 | 41.6298 | 54.0879 | 54.3352 | 0 | 0 | 1.2172 | 1.3203 | 2.151 | 2.775 | 4.3418 | 4.5428 | 0.59314 | 0.79799 | 31.3817 | 42.7561 | 54.2116 |  | 1.2687 | 2.463 | 188692.4 | 11202.9 | 27664 | 53813.2 | 27924.1 | 69449.3 | 23002.3 | 13879 | 415627.2 | 39875.8 | 210 | 34481 | 222.1 | 40087.8 | 398.5 | 7963 | 36.8 |  |  | 94.11 | 125738500 | 926045.376 | 1111 | 120037 | 174380.8 | 1816.7 | 92100 | 300 | 93400 | 300 | 119500 | 600 | 119200 | 700 | 0 | 0 | 230 | 425198 | 2084.032 | 2160 | 304560 | 423864 | 2520 | 427282.032 | 423113.968 | 421344 | 2.804% | 12.4 | 114 | fully cloudy weather
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 6:19 | 17:45 | 5690.5 | 5501.3 | 5303.7 | 5476.1 | 5577.9 | 5750.8 | 5576.5 | 6036.1 | 5669.8 | 5608.9 | 5777.7 | 5722.4 | 5945.7 | 5829.5 | 5882.8 | 5598 | 7477.5 | 8234.2 | 7188.5 | 7477 | 8754.2 | 5347.3 | 7969.3 | 8129.5 | 7975.8 | 7926.6 | 7978.3 | 7991.9 | 5975.9 | 6232.8 | 6222.8 | 6319 | 6091.2 | 6341.2 | 6158.8 | 6140.8 | 5031.3 | 5082.9 | 5128.9 | 5116.9 | 5223.3 | 5101.9 | 6967.1 | 7744.7 | 5672.7 | 6921.2 | 7529.6 | 6305.2 | 5350.5 | 7181.3 | 1071.5 | 1182.5 | 4988.9 | 3575.4 | 5236.4 | 3004 | 5073.6 | 5090.6 | 4484 | 4232.6 | 4729.4 | 4272.8 | 5816.3 | 4101.6 | 2385.4 | 1467 |  |  |  |  | 855.8 | 721.1 | 3231.2 | 5491.1 | 4.3346 | 3.9175 | 4.4218 | 4.0064 | 0.50341 | 0.63521 | 0.84212 | 0.66795 | 29.8686 | 30.0735 | 41.9114 | 39.5141 | 61.7786 | 61.9531 | 0.037383 | 0 | 1.3289 | 1.356 | 5.646 | 5.826 | 4.1261 | 4.2141 | 0.56931 | 0.75504 | 29.971 | 40.7128 | 61.8658 | 0.037383 | 1.3424 | 5.736 | 183397.8 | 10114.2 | 24750.5 | 47876.7 | 24732 | 65888.7 | 17718.8 | 13770.3 | 388249 | 39967.6 | 210.4 | 34569.3 | 222.5 | 40194 | 399.2 | 8071.9 | 37.6 |  |  | 94.36 | 126134534 | 928454.656 | 1114 | 120432 | 174928.9 | 1820.9 | 91800 | 400 | 88300 | 400 | 106200 | 700 | 108900 | 800 | 0 | 0 | 250 | 396034 | 2409.28 | 2160 | 284400 | 394632 | 3024 | 398443.28 | 393624.72 | 391608 | 2.626% | 12.9 | 114 | fully cloudy weather & rain slowly
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 6:04 | 18:13 | 6251 | 6252.5 | 5977.1 | 5994.5 | 6144.9 | 6275.4 | 6105.5 | 6549 | 6177.7 | 6107.2 | 6334.2 | 6341.3 | 6512.8 | 6424.7 | 6430 | 6215.1 | 8831.1 | 9574.5 | 8567 | 8853.6 | 9845.9 | 6149.9 | 9116.8 | 9285.3 | 9009.1 | 8947 | 8959.7 | 9018.9 | 7382.9 | 7568.3 | 6222.8 | 6319 | 7385.9 | 7628.4 | 7494.3 | 7404 | 6000.5 | 6042.7 | 6055.8 | 6032.8 | 6153 | 6076.4 | 8532.7 | 9361.2 | 6905.3 | 8352.1 | 8689 | 7224 | 6129 | 8192 | 8813 | 8933 | 5549 | 3008 | 6002 | 3379 | 5657 | 5751 | 6240 | 5901 | 6511 | 6049 | 6587 | 5210 | 2639 | 1686 |  |  |  |  | 950 | 805 | 3585 | 6245 | 4.7752 | 4.7072 | 4.8163 | 4.7833 | 0.59292 | 0.68632 | 0.6686 | 0.77624 | 29.3938 | 30.0972 | 40.9857 | 40.3791 | 67.4881 | 64.9005 | 0 | 0 | 1.1453 | 1.2828 | 4.455 | 4.908 | 4.7412 | 4.7998 | 0.63962 | 0.72242 | 29.7455 | 40.6824 | 66.1943 |  | 1.2141 | 4.6815 | 206251.7 | 12043.2 | 27493 | 57469.3 | 29912.6 | 88911 | 24701 | 16122 | 462903.8 | 40072.9 | 210.8 | 34666.4 | 222.8 | 40321.6 | 399.8 | 8199.5 | 38.6 |  |  | 94.6 | 126593277 | 930819.264 | 1117 | 120888 | 175563.7 | 1824.7 | 105300 | 400 | 97100 | 300 | 127600 | 600 | 127600 | 1000 | 0 | 0 | 240 | 458743 | 2364.608 | 2160 | 328320 | 457056 | 2736 | 461107.608 | 456378.392 | 454320 | -0.388% | 12.9 | 114 | fully cloudy weather. Power Trafo Trip 16:37 to 16:52
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 6:07 | 18:32 | 8359.5 | 8265.4 | 7809.3 | 7963 | 8169.9 | 8393.5 | 8095.2 | 8779 | 8206.1 | 8038.9 | 8318 | 8254.5 | 8640.2 | 8384.5 | 8491.1 | 8187.9 | 11335.9 | 12187.6 | 11077.5 | 11560.1 | 12375.3 | 7634 | 11433.3 | 11678.9 | 11428 | 11297 | 11399 | 11460 | 9652 | 9969 | 9833 | 9938 | 9789.5 | 10144 | 9910.6 | 9821.5 | 8056.1 | 8135.9 | 8216.1 | 8145.7 | 8356.1 | 8215.6 | 11263 | 12507 | 9081 | 11051 | 11153 | 9317 | 7859 | 10559 | 11451 | 11596 | 7206 | 4189 | 7694 | 4270 | 7101 | 7203 | 8066 | 7544 | 8406 | 7689 | 8230 | 7643 | 3384 | 2366 |  |  |  |  | 1198 | 1019 | 4572 | 7767 | 4.4202 | 4.2502 | 4.8103 | 4.3603 | 0.50192 | 0.64032 | 0.6556 | 0.66524 | 29.3908 | 30.0992 | 40.9957 | 40.2851 | 67.4581 | 62.9005 | 0 | 0 | 1.1253 | 1.2758 | 4.355 | 4.805 | 4.3352 | 4.5853 | 0.57112 | 0.66042 | 29.745 | 40.6404 | 65.1793 |  | 1.2006 | 4.58 | 267222.6 | 16192 | 39392 | 76835.5 | 39665.6 | 114154 | 31705 | 21623 | 606789.7 | 40206.8 | 211 | 34794.8 | 223.1 | 40491.1 | 400.1 | 8363.6 | 39.1 |  |  | 94.84 | 127189696 | 932201.216 | 1119 | 121482 | 176389.3 | 1826.9 | 133900 | 200 | 128400 | 300 | 169500 | 300 | 164100 | 500 | 0 | 0 | 240 | 596419 | 1381.952 | 1440 | 427680 | 594432 | 1584 | 597800.952 | 595037.048 | 592848 | -1.481% | 12.9 | 114 | fully cloudy weather
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 6:04 | 18:23 | 7898.9 | 7744.5 | 7356.7 | 7712 | 8021.6 | 8270.3 | 7873 | 8528.3 | 7631.3 | 7693.6 | 7932.6 | 7747.9 | 8072.5 | 8030.9 | 8011.7 | 7530.6 | 10560 | 11755.2 | 10178.5 | 10554.3 | 11454.5 | 7121.7 | 10608.6 | 10899.4 | 10674.3 | 10691.6 | 10690.9 | 10767.9 | 7421.8 | 7613.5 | 7523.8 | 7612.6 | 9187 | 9568.3 | 9299.7 | 9304.1 | 7691.2 | 7880.5 | 7759.6 | 7767.8 | 8022.1 | 7981.8 | 10655.1 | 12057.5 | 8811 | 10707.8 | 11304.2 | 9403 | 7958.6 | 10717.6 | 11590 | 11620 | 7322.9 | 6858.6 | 7664.5 | 4916.6 | 7196.2 | 7263.9 | 8127.3 | 7586.7 | 8323.3 | 7812.4 | 8561 | 7926.9 | 3446.4 | 3206 |  |  |  |  | 1228.8 | 1043.4 | 4731.7 | 7914.7 | 6.1104 | 5.3327 | 6.2304 | 5.453 | 0.79717 | 0.81428 | 1.2108 | 0.91532 | 30.9046 | 30.9149 | 45.8836 | 43.6957 | 65.2425 | 61.9796 | 0.077607 | 0 | 1.2861 | 1.316 | 5.82 | 6.558 | 5.7215 | 5.8417 | 0.80573 | 1.063 | 30.9097 | 44.7896 | 63.611 | 0.077607 | 1.301 | 6.189 | 252013.3 | 15571.7 | 30171.7 | 73762.7 | 37359.1 | 118734.7 | 31849.7 | 23140.3 | 582603.2 | 40332 | 211.3 | 34917.5 | 223.3 | 40645.9 | 400.6 | 8534.1 | 39.1 |  |  | 95.08 | 127763161 | 933235.968 | 1120 | 122054 | 177183.1 | 1829.2 | 125200 | 300 | 122700 | 200 | 154800 | 500 | 170500 | 400 | 0 | 0 | 240 | 573465 | 1034.752 | 720 | 411840 | 571536 | 1656 | 574499.752 | 572430.248 | 569880 | -1.391% | 12.9 | 114 | Fully Cloudy Weather & Heavy rain IDT 5 Tripped in Buchloz Relay operated 11:09 to 12:04
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 6:09 | 17:57 | 7276.7 | 7284 | 6805.3 | 6734.4 | 6930.4 | 7185.3 | 6955.1 | 7696.5 | 7037 | 6820.9 | 7120 | 7099.7 | 7453 | 7231.1 | 7302.9 | 6948.8 | 9735 | 10907.3 | 9447.3 | 9919.1 | 10607.7 | 6677.1 | 10044.4 | 10239.2 | 10063.2 | 9984.9 | 10006.4 | 10055.1 | 7030.3 | 7201 | 7062.3 | 7153.2 | 7845.4 | 8129.5 | 7926 | 7883 | 6748.4 | 6832.6 | 6827.6 | 6821.2 | 7003.9 | 6870 | 10655.4 | 12057.8 | 8811 | 10707.8 | 10537.5 | 8802.2 | 7450.9 | 9918.6 | 11250 | 11315 | 6874.5 | 6875.9 | 7264.3 | 5021.1 | 6898.5 | 6997.6 | 7391.8 | 7159.8 | 8020.4 | 7246 | 8064.5 | 7474.4 | 3361.2 | 3127.3 |  |  |  |  | 1147.1 | 975.2 | 4436.4 | 7429.7 | 5.4001 | 5.3646 | 5.5127 | 5.3626 | 0.65076 | 0.82257 | 1.0342 | 0.91748 | 30.9202 | 31.8954 | 45.3271 | 44.4336 | 63.3601 | 58.7128 | 0.29555 | 0 | 1.0485 | 1.2361 | 4.545 | 4.494 | 5.3824 | 5.4376 | 0.73666 | 0.97585 | 31.4078 | 44.8804 | 61.0364 | 0.29555 | 1.1423 | 4.5195 | 231567.8 | 13581 | 28446.8 | 69754.7 | 31783.9 | 113194.5 | 29818 | 22027.4 | 540174.1 | 40448.8 | 211.7 | 35028.8 | 223.7 | 40782.4 | 401.3 | 8694.9 | 39.8 |  |  | 95.39 | 128288612 | 935657.088 | 1123 | 122557 | 177910.5 | 1833.3 | 116800 | 400 | 111300 | 400 | 136500 | 700 | 160800 | 300 | 0 | 0 | 310 | 525451 | 2421.12 | 2160 | 362160 | 523728 | 2952 | 527872.12 | 523029.88 | 520776 | -2.277% | 12.9 | 118 | Fully Cloudy Weather & Heavy rain IDT 5 Tripped in Buchloz Relay operated 12:23 to 13:20
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 6:07 | 18:34 | 6116 | 6052 | 5645.5 | 5715.3 | 5876.7 | 6100.3 | 5889.6 | 6587.8 | 5942.7 | 5767.8 | 5991.1 | 5963 | 6271.3 | 5996.4 | 6150.4 | 5872.5 | 8200 | 9183 | 8022 | 8421 | 8810 | 5346 | 8023 | 8211 | 8033 | 8024 | 8035 | 8092.1 | 6561 | 6746.6 | 6667 | 6761.2 | 6649 | 6948.4 | 6670 | 6730.8 | 5473.9 | 5510.7 | 5508 | 5489.8 | 5642 | 5554 | 7719.7 | 8766 | 6290.1 | 7591.9 | 8785 | 7221 | 6048 | 8271 | 8951 | 9128 | 5718 | 7381 | 5907 | 4066 | 5620 | 5701 | 6186 | 5833 | 6544 | 6030 | 6766 | 6283 | 2833 | 2783 |  |  |  |  | 938 | 792 | 3737 | 6227 | 4.3989 | 4.1909 | 4.5109 | 4.3077 | 0.469 | 0.63854 | 0.77583 | 0.71386 | 30.674 | 31.2917 | 42.669 | 41.2933 | 64.4133 | 61.4937 | 0 | 0 | 0.89437 | 0.99594 | 2.424 | 2.373 | 4.2949 | 4.4093 | 0.55377 | 0.74484 | 30.9829 | 41.9812 | 62.9535 |  | 0.94515 | 2.3985 | 192338.5 | 10984.6 | 26735.8 | 52561.5 | 26998.2 | 94491 | 24593 | 18665 | 447367.6 | 40544.8 | 211.9 | 35123.3 | 224.1 | 40898.8 | 401.9 | 8830.7 | 40.8 |  |  | 95.66 | 128731250 | 938203.52 | 1126 | 123018 | 178523.4 | 1837.7 | 96000 | 200 | 94500 | 400 | 116400 | 600 | 135800 | 300 | 0 | 0 | 270 | 442638 | 2546.432 | 2160 | 331920 | 441288 | 3168 | 445184.432 | 440091.568 | 438120 | -0.488% | 12.9 | 118 | Fully Cloudy Weather
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 6:28 | 18:38 | 6946.4 | 6888 | 6465 | 6485 | 6627 | 6858 | 6690.5 | 7374 | 6846 | 6602 | 6855.5 | 6807 | 7219.5 | 6906 | 7070 | 6767 | 9367 | 10448 | 9167.9 | 9607 | 10270 | 6347 | 9467 | 9646 | 9455 | 9371 | 9417 | 9456 | 7526 | 7755 | 7653.3 | 7724 | 7609.7 | 7910 | 7717.9 | 7665 | 6239.3 | 6289 | 6320.5 | 6285 | 6434 | 6343 | 8743.8 | 9831.6 | 7162.1 | 8753.3 | 8421 | 7018 | 5937 | 8008 | 6223 | 2624 | 620 | 639 | 6158 | 4238 | 5848 | 5914 | 6011 | 5705 | 6244 | 5729 | 7333 | 7140 | 2818 | 3789 |  |  |  |  | 1042 | 884 | 4096 | 6739 | 5.0558 | 4.8206 | 5.1805 | 4.9574 | 0.45501 | 0.63 | 0.78328 | 0.71007 | 29.0557 | 28.4492 | 41.5502 | 39.1163 | 73.7222 | 75.0401 | 0.46137 | 0.46427 | 1.0673 | 1.0885 | 5.253 | 6.066 | 4.9382 | 5.0689 | 0.5425 | 0.74667 | 28.7525 | 40.3333 | 74.3812 | 0.46282 | 1.0779 | 5.6595 | 221425.8 | 12528.3 | 30658.3 | 59873.3 | 30902.6 | 74409 | 23689 | 21080 | 474566.3 | 40656.2 | 212.2 | 35229.8 | 224.4 | 41031.3 | 402.4 | 8949 | 41 |  |  | 95.91 | 129200668 | 939613.632 | 1128 | 123486 | 179173.3 | 1840.3 | 111400 | 300 | 106500 | 300 | 132500 | 500 | 118300 | 200 | 0 | 0 | 250 | 469418 | 1410.112 | 1440 | 336960 | 467928 | 1872 | 470828.112 | 468007.888 | 466056 | -0.7877% | 12.9 | 118 | Fully Cloudy Weather &ICR10 Inverter-3 & inverter-4 tripped due to SCB cable heavy burned in DC side. IDT also tripped during smoke came in inverter down side
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 6:01 | 18:33 | 8211 | 8101 | 7671 | 7721.6 | 7904 | 8138.8 | 7974 | 8550.5 | 7873 | 7673.3 | 7942 | 7904.7 | 8210 | 7809 | 8070 | 7706 | 10990.7 | 12010 | 10820 | 11203 | 11734 | 7583 | 11123 | 11333 | 11092 | 11053 | 11033 | 11121 | 9706 | 9926 | 9756 | 9816 | 9773 | 10068 | 9952 | 9830 | 7901 | 7938 | 7922 | 7761 | 8053 | 7966 | 11186 | 12239 | 9228 | 10984 | 10839.8 | 9077 | 7689.2 | 10303.3 | 6010 | 2150 | 0 | 0 | 7346.8 | 5094.9 | 7064.6 | 7123 | 7102.9 | 6856.1 | 7368 | 6451.3 | 8404.7 | 8163.5 | 3170.1 | 4736.7 |  |  |  |  | 1190.1 | 1009.9 | 4631.9 | 7673.8 | 6.169 | 6.3151 | 6.3302 | 6.4155 | 0.59562 | 0.73453 | 0.88316 | 0.86257 | 28.1357 | 27.3196 | 42.1778 | 39.2994 | 79.752 | 80.0065 | 0.15503 | 0.13183 | 0.91345 | 0.91712 | 3.414 | 3.579 | 6.2421 | 6.3729 | 0.66507 | 0.87287 | 27.7276 | 40.7386 | 79.8793 | 0.14343 | 0.91529 | 3.4965 | 258555.6 | 15839 | 39204 | 75339 | 39623 | 87204.3 | 27778.3 | 24475 | 568018.2 | 40786.4 | 212.6 | 35353.4 | 224.7 | 41198.9 | 403 | 9091.4 | 41.2 |  |  | 96.18 | 129765965 | 941221.888 | 1130 | 124049 | 179955.9 | 1843.2 | 130200 | 400 | 123600 | 300 | 167600 | 600 | 142400 | 400 | 0 | 0 | 270 | 565297 | 1608.256 | 1440 | 405360 | 563472 | 2088 | 566905.256 | 563688.744 | 561384 | -0.1959% | 12.5333 | 118 | Fully Cloudy Weather
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 6:35 | 17:56 | 3698 | 3662 | 3425 | 3482 | 3599 | 3692 | 3572 | 3962 | 3690 | 3605 | 3788 | 3775 | 3909 | 3877 | 3841 | 3612.7 | 5211.8 | 5991.3 | 4971 | 5206.5 | 6011.3 | 3711 | 5555 | 5675 | 5490.5 | 5436.5 | 5471 | 5523 | 4689 | 4791 | 4690 | 4742.1 | 4691 | 4866 | 4778 | 4733 | 3790 | 3820 | 3815 | 3663 | 3898 | 3847 | 5452.5 | 6159.3 | 4422 | 5390 | 5123 | 4278 | 3611 | 4833 | 5850 | 2090 | 0 | 0 | 3431 | 2321 | 3290 | 3255 | 3589 | 3402 | 3756 | 3285 | 8405 | 8164 | 1756 | 2936 |  |  |  |  | 484 | 401 | 2086 | 3529 | 2.5163 | 2.7686 | 2.567 | 2.8246 | 0.26283 | 0.32833 | 0.36693 | 0.37569 | 28.3539 | 28.0935 | 38.0753 | 36.4219 | 80.2364 | 81.4693 | 0 | 0 | 0.68926 | 0.71377 | 2.049 | 2.016 | 2.6424 | 2.6958 | 0.29558 | 0.37131 | 28.2237 | 37.2486 | 80.8528 |  | 0.70151 | 2.0325 | 123443.6 | 7610 | 18912.1 | 36646.8 | 19068 | 44582 | 14032 | 21261 | 285555.5 | 40850.3 | 212.9 | 35411.8 | 225.1 | 41280.8 | 403.6 | 9160.6 | 42.3 |  |  | 96.43 | 130040127 | 943945.344 | 1133 | 124322 | 180335.4 | 1847.8 | 63900 | 300 | 58400 | 400 | 81900 | 600 | 69200 | 400 | 0 | 0 | 250 | 274162 | 2723.456 | 2160 | 196560 | 273240 | 3312 | 276885.456 | 271438.544 | 269928 | -3.036% | 11.35 | 118 | Fully Cloudy Weather & Slowly rain
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 6:18 | 18:25 | 5103 | 5042 | 4730 | 4788 | 4930 | 5101 | 4925 | 5487 | 5032 | 4869 | 5056 | 5044 | 5298 | 5088 | 5184 | 4940 | 6687 | 7565 | 6537 | 6862 | 7209 | 4482 | 6760 | 6917 | 6743 | 6703 | 6721 | 6770 | 5830 | 5994 | 5893 | 5936 | 5873 | 6107 | 5980 | 5934 | 4776 | 4808 | 4825 | 4789 | 4908 | 4849 | 6804 | 7712 | 5549 | 6750 | 6514 | 5455 | 4592 | 6145 | 6065 | 2145 | 0 | 0 | 4314 | 2958 | 4068.5 | 4120 | 4578 | 4317 | 4756 | 4361 | 4809 | 4679 | 2492 | 4032 |  |  |  |  | 650 | 544 | 2654 | 4427 | 3.5132 | 3.5273 | 3.6204 | 3.5984 | 0.339 | 0.44683 | 0.53344 | 0.49316 | 27.9576 | 27.8897 | 38.8285 | 37.0207 | 74.7457 | 76.6463 | 0 | 0 | 0.85523 | 0.94069 | 2.295 | 2.274 | 3.5203 | 3.6094 | 0.39292 | 0.5133 | 27.9237 | 37.9246 | 75.696 |  | 0.89796 | 2.2845 | 160573 | 9584 | 23653 | 46186 | 23894 | 54651.5 | 18012 | 16012 | 352565.5 | 40929.9 | 213.1 | 35490.6 | 225.5 | 41383.4 | 404.3 | 9248.3 | 43.5 |  |  | 96.68 | 130389901 | 946700.288 | 1137 | 124670 | 180819.7 | 1852.4 | 79600 | 200 | 78800 | 400 | 102600 | 700 | 87700 | 300 | 0 | 0 | 250 | 349774 | 2754.944 | 2880 | 250560 | 348696 | 3312 | 352528.944 | 347019.056 | 345384 | -0.01037% | 12.1167 | 118 | Fully Cloudy Weather Incomer 04 [Phase 03] Trip due To TL Line Earth Fault at 16:40 PM 18:21 PM
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 6:36 | 18:27 | 2696 | 2668 | 2497 | 2529 | 2624 | 2720 | 2603 | 2906 | 2629 | 2576 | 2661 | 2642 | 2782 | 2771 | 2730 | 2590 | 3738 | 4240 | 3634 | 3818 | 3964 | 2485 | 3756 | 3836 | 3755 | 3741 | 3725 | 3751 | 3388 | 3469 | 3395 | 3426 | 3389 | 3494 | 3440 | 3390 | 2625 | 2643 | 2682 | 2674 | 2729 | 2676 | 3894 | 4348.5 | 3086 | 3722 | 3951.8 | 3347.3 | 2828 | 3757.9 | 5855 | 2030 | 0 | 0 | 1493 | 1046 | 1417 | 1473 | 2741 | 2605 | 2858 | 2625 | 3056 | 2988 | 1610 | 2549 |  |  |  |  | 342 | 278 | 1599.6 | 2721 | 1.8749 | 1.9846 | 1.9225 | 1.9907 | 0.17191 | 0.21345 | 0.25388 | 0.24136 | 27.1734 | 26.1881 | 34.941 | 33.1443 | 91.6547 | 91.4005 | 0.61244 | 0.69634 | 0.86466 | 0.80971 | 2.523 | 2.25 | 1.9298 | 1.9566 | 0.19268 | 0.24762 | 26.6808 | 34.0427 | 91.5276 | 0.65439 | 0.83719 | 2.3865 | 87067 | 5268 | 13678 | 25811.5 | 13713 | 32139.6 | 10829 | 10203 | 198709.1 | 40974 | 213.4 | 35532.7 | 225.8 | 41441.7 | 404.9 | 9298.6 | 44.5 |  |  | 96.91 | 130585796 | 949158.528 | 1140 | 124865 | 181090.7 | 1856.4 | 44100 | 300 | 42100 | 300 | 58300 | 600 | 50300 | 300 | 0 | 0 | 230 | 195895 | 2458.24 | 2160 | 140400 | 195120 | 2880 | 198353.24 | 193436.76 | 192240 | -0.1791% | 11.85 | 120.7 | Fully Cloudy Weather & Heavy Rain ICR 11 INV 01 Breakdown due to Internal Fault at 07:00 AM To 11:00 AM
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 6:03 | 18:19 | 8748.4 | 8695.4 | 8252.2 | 8345.4 | 8550 | 8791.2 | 8606.2 | 9231.4 | 8224.1 | 8428.6 | 8708.6 | 8660.7 | 9124.3 | 8938.7 | 8917.5 | 8538.3 | 12043 | 13169.1 | 11613.6 | 12032.2 | 12829.2 | 8100.3 | 12042.1 | 12238.7 | 12085.5 | 12108 | 12016.2 | 12089.8 | 10294.5 | 10564.9 | 10369.4 | 10396.8 | 10301.9 | 10598.5 | 10417.5 | 10260.7 | 8332.7 | 8399.3 | 8497.4 | 8455.2 | 8564.7 | 8269 | 11939.8 | 13085 | 9619 | 11753 | 12273 | 10305 | 8653 | 11577 | 12355 | 2991 | 0 | 0 | 8549 | 5288 | 6969 | 7220 | 8626 | 8365 | 8872 | 8420 | 9473 | 9174 | 5337 | 8418 |  |  |  |  | 1373 | 1164 | 2551 | 8649 | 6.7027 | 6.7837 | 7.0626 | 7.0219 | 0.6523 | 0.73835 | 0.95758 | 0.86849 | 30.0052 | 29.2129 | 44.0949 | 42.1546 | 77.9741 | 78.4446 | 0.0002 | 0 | 0.62155 | 0.65169 | 5.847 | 4.788 | 6.7432 | 7.0423 | 0.69533 | 0.91303 | 29.609 | 43.1248 | 78.2093 | 0.0002 | 0.63662 | 5.3175 | 281128.7 | 16732 | 41625.6 | 80183.1 | 41578.6 | 99917 | 34283 | 32402 | 627850 | 41115.3 | 213.8 | 35664.3 | 226.2 | 41619.2 | 405.8 | 9464.3 | 45.9 |  |  | 97.23 | 131205685 | 952748.608 | 1144 | 125482 | 181949 | 1862.3 | 141300 | 400 | 131600 | 400 | 177500 | 900 | 165700 | 400 | 0 | 0 | 320 | 619889 | 3590.08 | 2880 | 444240 | 617976 | 4248 | 623479.08 | 616298.92 | 613728 | -0.6962% | 12.2667 | 120.7 | Cloudy Weather
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 6:05 | 18:42 | 7756.7 | 7652.2 | 7181.9 | 7249.2 | 7468.9 | 7737.2 | 7493.4 | 8306.3 | 7587 | 7362 | 7728.5 | 7726.5 | 8160.1 | 7819.2 | 7924.1 | 7580.6 | 10555.1 | 11778.5 | 10262.3 | 10761.6 | 11584.6 | 7075.7 | 10710.1 | 10927.7 | 10670.4 | 10591.4 | 10582.8 | 10647.3 | 8709.7 | 8918.9 | 8705.7 | 8789.3 | 8732.4 | 9021.5 | 8867.9 | 8759.2 | 7113.1 | 7155.9 | 7196.7 | 7165.2 | 7345.6 | 7064 | 10103 | 11377 | 8152 | 9848 | 10562 | 8834 | 7441 | 9934 | 11221 | 3134 | 0 | 0 | 6867 | 4774 | 6569 | 6702 | 7533 | 7168 | 7864 | 7225 | 8023 | 7830 | 6314 | 7785 |  |  |  |  | 1150 | 972 | 4479 | 7416 | 5.631 | 5.5478 | 5.8759 | 5.6701 | 0.58254 | 0.69666 | 0.91023 | 0.76851 | 29.7277 | 29.6414 | 42.0974 | 39.38 | 71.2768 | 72.5736 | 0.012552 | 0.019727 | 1.3992 | 1.4714 | 4.677 | 4.944 | 5.5894 | 5.773 | 0.6396 | 0.83937 | 29.6846 | 40.7387 | 71.9252 | 0.01614 | 1.4353 | 4.8105 | 248881.3 | 14269 | 35123.6 | 68251.5 | 35381 | 90055 | 29790 | 29952 | 551703.4 | 41240.7 | 213.9 | 35781.6 | 226.5 | 41770.4 | 406.2 | 9610.3 | 46.5 |  |  | 97.47 | 131748265 | 954327.424 | 1146 | 126023 | 182700.2 | 1865 | 125400 | 100 | 117300 | 300 | 151200 | 400 | 146000 | 400 | 0 | 0 | 240 | 542580 | 1578.816 | 1440 | 389520 | 540864 | 1944 | 544158.816 | 541001.184 | 538920 | -1.368% | 12.6167 | 120.7 | fully cloudy weather
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 6:38 | 18:04 | 3850.1 | 3805.3 | 3572.9 | 3636.8 | 3758.5 | 3867.1 | 3730.5 | 4131.6 | 3826.9 | 3735.2 | 3890.4 | 3882.4 | 4051 | 3927.4 | 3964.4 | 3752.6 | 5368.1 | 6123.1 | 5177.8 | 5428.3 | 5278.1 | 3621.7 | 5508.4 | 5619.6 | 5498.8 | 5462.4 | 5449.7 | 5490.3 | 4489.8 | 4607.4 | 4504.1 | 4546.4 | 4503.6 | 4673 | 4585.2 | 4539.9 | 3617.6 | 3644.9 | 3645.6 | 3627 | 3715.1 | 3646 | 5215.9 | 5877.9 | 4206.7 | 5128.6 | 5156 | 4334.3 | 3662.2 | 4874.8 | 5869 | 1567 | 0 | 0 | 3470.9 | 2394.6 | 3178.4 | 3254.3 | 3649.4 | 3472.5 | 3816.1 | 3495.7 | 3962.1 | 3886.3 | 3694.2 | 3917.2 |  |  |  |  | 505.6 | 420.9 | 2143.9 | 3603 | 2.6615 | 2.6957 | 2.7082 | 2.6882 | 0.22399 | 0.28848 | 0.37206 | 0.31896 | 26.4144 | 25.8145 | 35.9187 | 33.5507 | 87.3533 | 87.5739 | 0.14347 | 0.12893 | 1.2076 | 1.2821 | 3.381 | 2.874 | 2.6786 | 2.6982 | 0.25624 | 0.34551 | 26.1144 | 34.7347 | 87.4636 | 0.1362 | 1.2448 | 3.1275 | 125409.4 | 7262.5 | 18147.7 | 35062.8 | 18301.7 | 44434.9 | 14433.7 | 15459.8 | 278512.5 | 41304.3 | 214.1 | 35842.5 | 226.8 | 41848.8 | 406.8 | 9683.1 | 47.4 |  |  | 97.7 | 132024336 | 956550.464 | 1148 | 126298 | 183082.3 | 1868.8 | 63600 | 200 | 60900 | 300 | 78400 | 600 | 72800 | 300 | 0 | 0 | 230 | 276071 | 2223.04 | 1440 | 198000 | 275112 | 2736 | 278294.04 | 273847.96 | 272376 | -0.07844% | 11.4333 | 120.7 | fully cloudy weather & rain slowly
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 6:20 | 18:47 | 7148.8 | 7100.8 | 6770.9 | 6893.5 | 7066.2 | 7237.1 | 7047.4 | 7547.7 | 7160.1 | 6986.8 | 7218.6 | 7195.6 | 7536.9 | 7359.6 | 7376.8 | 7063.9 | 9906.1 | 10854.5 | 9614.2 | 9975.4 | 10487.6 | 6733.2 | 10190.8 | 10386.9 | 10185.4 | 10133.4 | 10119 | 10186.1 | 8381.7 | 8629.8 | 8484.7 | 8544.3 | 8464.7 | 8776.7 | 8589.2 | 8505.8 | 6945.2 | 7008.4 | 7010.8 | 6971.1 | 7155.7 | 7061 | 9740.2 | 10774.1 | 7945.6 | 9633.4 | 10764 | 8939 | 6714.1 | 8891.3 | 9328 | 2202.7 | 0 | 0 | 6204.1 | 4297.2 | 5628.8 | 5852.7 | 6333.4 | 6145.7 | 6546.3 | 6556.6 | 7001.6 | 6810.7 | 7103.9 | 6962.5 |  |  |  |  | 955.9 | 808 | 3809.4 | 6337 | 5.3235 | 5.4612 | 5.517 | 5.5506 | 0.51713 | 0.66307 | 0.81978 | 0.7287 | 30.047 | 29.943 | 43.7903 | 41.0697 | 73.6781 | 75.0638 | 0 | 0.019672 | 1.4556 | 1.5318 | 3.105 | 3.516 | 5.3924 | 5.5338 | 0.5901 | 0.77424 | 29.995 | 42.43 | 74.3709 | 0.019672 | 1.4937 | 3.3105 | 233483.3 | 13953.6 | 34040.5 | 66291.9 | 34336.4 | 80732.2 | 25582 | 27878.7 | 516298.6 | 41422.3 | 214.5 | 35953 | 227.1 | 41995.6 | 407.4 | 9812.8 | 48.2 |  |  | 97.97 | 132531183 | 958852.16 | 1151 | 126803 | 183784.1 | 1872.7 | 118000 | 400 | 110500 | 300 | 146800 | 600 | 129700 | 400 | 0 | 0 | 270 | 506847 | 2301.696 | 2160 | 363600 | 505296 | 2808 | 509148.696 | 504545.304 | 502488 | -1.385% | 12.45 | 120.7 | fully cloudy weather
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 6:11 | 18:35 | 7294.7 | 7173.3 | 6805.1 | 6962.7 | 7157.7 | 7367.4 | 7145.4 | 7785.5 | 7279 | 7103.5 | 7409.9 | 7392.4 | 7679.7 | 7468.7 | 7493.8 | 7094.4 | 9986.1 | 11226.7 | 9644.5 | 10080.1 | 11079.1 | 6782.1 | 10306.4 | 10516 | 10265.7 | 10162.6 | 10234.9 | 10316.1 | 8415.9 | 8648.2 | 8476 | 8519.5 | 8507.6 | 8823.4 | 8605.1 | 8544 | 6988.4 | 7056.7 | 7036 | 6952.5 | 7145.5 | 7078 | 9753.5 | 10885.4 | 7872.9 | 9602.4 | 9838.4 | 8251.1 | 6939.3 | 9305.6 | 9347 | 2234 | 0 | 0 | 6619.2 | 4625.8 | 6124.5 | 6253.2 | 6964.7 | 6703.6 | 7219.7 | 7115 | 7468.4 | 7634.2 | 7578.3 | 7720 |  |  |  |  | 1011.2 | 855.4 | 4014.6 | 6703.2 | 5.3309 | 5.4535 | 5.5902 | 5.5916 | 0.57203 | 0.70084 | 0.89228 | 0.76179 | 30.5659 | 30.6852 | 42.3088 | 40.18 | 66.9416 | 68.5973 | 0 | 0 | 1.621 | 1.7127 | 3.057 | 3.492 | 5.3922 | 5.5909 | 0.63643 | 0.82703 | 30.6256 | 41.2444 | 67.7695 |  | 1.6668 | 3.2745 | 237213.5 | 14045.1 | 34059.6 | 66326.2 | 34480.1 | 82122.5 | 28003 | 30400.9 | 526650.9 | 41542.1 | 214.9 | 36065.6 | 227.5 | 42142.8 | 408.2 | 9951.8 | 49 |  |  | 98.27 | 133051539 | 961587.52 | 1155 | 127321 | 184504.5 | 1877.3 | 119800 | 400 | 112600 | 400 | 147200 | 800 | 139000 | 300 | 0 | 0 | 300 | 520356 | 2735.36 | 2880 | 372960 | 518688 | 3312 | 523091.36 | 517620.64 | 515376 | -0.6759% | 12.4 | 120.7 | Cloudy Weather
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 5:59 | 18:49 | 9249.1 | 9173.6 | 8741.2 | 8818.6 | 9072 | 9302.9 | 9080 | 9704.8 | 9103.7 | 8943.7 | 9237.5 | 9211.2 | 9551.7 | 9287.1 | 9369.1 | 9115 | 12638.3 | 13551.6 | 12403.7 | 12829.4 | 13639.9 | 8445 | 12908.1 | 13124.8 | 12819.9 | 12746.5 | 12835.6 | 12911.3 | 10680.5 | 10976.6 | 10784.4 | 10871.4 | 10782.1 | 11157.5 | 10938.8 | 10821 | 8851.6 | 8913.6 | 8926.7 | 8871.5 | 9080 | 8968 | 12487.5 | 13797.9 | 10159.9 | 12263.7 | 12696.8 | 11047.4 | 9121.7 | 12041.5 | 11320 | 2375 | 255.7 | 241.7 | 8675.4 | 6106.3 | 8018.1 | 8112.2 | 8816.9 | 8633.1 | 9042.9 | 9043.1 | 9719.8 | 9881.5 | 9828.8 | 10074.8 |  |  |  |  | 1365.9 | 1159.2 | 5280.8 | 8779.6 | 6.9961 | 7.0287 | 7.3065 | 7.2285 | 0.79905 | 0.92462 | 1.1971 | 1.0139 | 31.1956 | 31.3433 | 44.7913 | 42.2634 | 55.4825 | 56.6988 | 0 | 0 | 1.8219 | 1.9287 | 3.642 | 4.113 | 7.0124 | 7.2675 | 0.86184 | 1.1055 | 31.2695 | 43.5274 | 56.0906 |  | 1.8753 | 3.8775 | 297815.3 | 17765.2 | 43312.9 | 84555.2 | 43699.4 | 106597.3 | 35536 | 39504.9 | 668786.2 | 41698.8 | 215.1 | 36207.7 | 227.9 | 42329.3 | 408.8 | 10131.7 | 49.5 |  |  | 98.53 | 133710921 | 963453.184 | 1157 | 127978 | 185417.2 | 1880.5 | 156700 | 200 | 142100 | 400 | 186500 | 600 | 179900 | 300 | 0 | 0 | 260 | 659382 | 1865.664 | 1440 | 473040 | 657144 | 2304 | 661247.664 | 657516.336 | 654840 | -1.127% | 12.8333 | 120.7 | Moving Cloudy Weather
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 6:01 | 18:47 | 3732.7 | 3660 | 3457.6 | 3523 | 3619.8 | 3760.3 | 3653.6 | 4020.1 | 3611.4 | 3624.2 | 3770.1 | 3739.2 | 3865.3 | 3739.5 | 3809.1 | 3624.1 | 5168.5 | 5756.6 | 4985.9 | 5183.3 | 5632.2 | 3409.1 | 5240.9 | 5309.8 | 5175.7 | 5177 | 5166.3 | 5215.5 | 4399.6 | 4447.1 | 4319.7 | 4366.4 | 4372.2 | 4514.4 | 4444.2 | 4411.5 | 3547.6 | 3562.4 | 3554.4 | 3542.3 | 3629.4 | 3577.8 | 5187 | 5913 | 4250 | 5150.7 | 4587 | 4229 | 3345 | 4320 | 9011 | 2350 | 938 | 1199 | 3213 | 2336 | 2976 | 3020 | 3260 | 3192 | 3460 | 3478 | 3711 | 3825 | 3764 | 3859 |  |  |  |  | 477 | 396 | 1938 | 3273 | 6.281 | 6.7065 | 6.6241 | 6.9143 | 0.7435 | 0.86923 | 1.0944 | 0.98195 | 30.9792 | 31.2074 | 46.6001 | 43.8975 | 55.1853 | 56.0277 | 0 | 0 | 1.6752 | 1.7738 | 4.032 | 3.63 | 6.4937 | 6.7692 | 0.80636 | 1.0382 | 31.0933 | 45.2488 | 55.6065 |  | 1.7245 | 3.831 | 120630.8 | 7110 | 17532.8 | 34804.6 | 17742.3 | 47608 | 13390 | 15159 | 273977.5 | 41752.9 | 215.5 | 36265.3 | 228.2 | 42405.8 | 409.4 | 10131.7 | 49.5 | 61.7 | 0.5 | 98.77 | 133976416 | 965425.536 | 1160 | 128242 | 185784.7 | 1842.2 | 54100 | 400 | 57600 | 300 | 76500 | 600 | 0 | 300 | 61700 | 500 | 240 | 265495 | 1972.352 | 2160 | 190080 | 264600 | 0 | 267467.352 | 263522.648 | 264600 | -2.376% | 12.7667 | 120.7 | All Incomer Manual Trip Due To Zero load From GSS 132 KV Line Motala and LDC Nagpur at 10:33 AM To 14:56 PM
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 6:03 | 18:43 | 8451.3 | 8328.7 | 7948.1 | 7993.8 | 8264.1 | 8470.3 | 8267.7 | 8851.7 | 8267.1 | 8161.6 | 8406.5 | 8399.5 | 8725.3 | 8477.1 | 8601.4 | 8349.2 | 11615.5 | 12414.7 | 11344.9 | 11819 | 12522 | 7873.5 | 11906.3 | 12072.1 | 11763.5 | 11734.9 | 11739.1 | 11862.7 | 10337 | 10576.2 | 10346.2 | 10430.1 | 10413.2 | 10765.1 | 10429.1 | 10448.9 | 8471.7 | 8510.6 | 8514.3 | 8477.7 | 8645 | 8532.3 | 12155.5 | 13159.3 | 9834.1 | 11840.3 | 11273 | 10663 | 9579 | 10749 | 11220 | 9124 | 11340 | 11730 | 7899 | 6299 | 7302 | 7398 | 7845 | 7713 | 8075 | 8131 | 8959 | 9283 | 9300 | 9432 |  |  |  |  | 1252 | 1058 | 4849 | 7986 | 6.5451 | 6.8897 | 6.9101 | 7.1338 | 0.84083 | 0.90781 | 1.1499 | 1.0298 | 30.9215 | 31.1925 | 45.3212 | 43.439 | 43.439 | 53.8268 | 0 | 0 | 1.5821 | 1.7509 | 3.21 | 3.387 | 6.7174 | 7.0219 | 0.87432 | 1.0899 | 31.057 | 44.3801 | 48.6329 |  | 1.6665 | 3.2985 | 272631.6 | 16982.3 | 41689.5 | 81158.5 | 42056.3 | 129721 | 31764 | 36974 | 652977.2 | 41890.6 | 215.8 | 36395.3 | 228.5 | 42585 | 410 | 10146.7 | 49.7 | 219.8 | 0.9 | 99.03 | 134618800 | 967429.632 | 1162 | 128882 | 186673.8 | 1887.7 | 137700 | 300 | 130000 | 300 | 179200 | 600 | 15000 | 400 | 158100 | 400 | 260 | 642384 | 2004.096 | 1440 | 460800 | 640152 | 32760 | 644388.096 | 640379.904 | 607392 | -1.315% | 12.6667 | 120.7 | Cloudy Weather
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 6:01 | 18:40 | 8019.2 | 7944.6 | 7622.1 | 7603 | 7841.1 | 8059.2 | 7846.2 | 8401 | 7868.5 | 7770.8 | 7980.3 | 7953.3 | 8282 | 8023.3 | 8190.1 | 7911.1 | 11026.5 | 11793.1 | 10788.6 | 11265 | 11804.5 | 7325.1 | 11134.6 | 11278.8 | 11032.9 | 11035 | 11009.6 | 11146.3 | 9748 | 10017.5 | 9741.5 | 9836.3 | 9720.8 | 10035.2 | 9704.1 | 9768 | 7873.1 | 7923.4 | 7894.7 | 7871.1 | 8019.7 | 7929 | 11286.4 | 12436.7 | 9350.3 | 11228.8 | 9081 | 8811 | 9432 | 10511 | 11124 | 10895 | 10820 | 11212 | 7518 | 5991 | 7080 | 7094 | 7570 | 7472 | 7874 | 7867 | 8811.9 | 9067.6 | 8988.3 | 9191.5 |  |  |  |  | 1242 | 1050 | 4795 | 7776 | 6.1679 | 6.4308 | 6.5287 | 6.6685 | 0.79556 | 0.87135 | 1.1013 | 0.98171 | 30.7545 | 31.0157 | 43.5626 | 41.4902 | 53.745 | 54.6118 | 0 | 0 | 1.7325 | 1.8588 | 3.486 | 3.816 | 6.2994 | 6.5986 | 0.83345 | 1.0415 | 30.8851 | 42.5264 | 54.1784 |  | 1.7957 | 3.651 | 257955.8 | 15796.5 | 39343.3 | 76016.7 | 39228.1 | 124432 | 30783 | 36059.3 | 619614.7 | 42020.3 | 216.2 | 36519.8 | 228.8 | 42753.1 | 410.6 | 10161.5 | 49.9 | 372.2 | 1.4 | 99.29 | 135229038 | 969608.576 | 1165 | 129490 | 187518.5 | 1891.3 | 129700 | 400 | 124500 | 300 | 168100 | 600 | 14800 | 400 | 152400 | 500 | 260 | 610238 | 2178.944 | 2160 | 437760 | 608184 | 2592 | 612416.944 | 608059.056 | 605592 | -1.162% | 12.65 | 122.7 | Cloudy Weather
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 6:02 | 18:41 | 7632.1 | 7582.8 | 7210.8 | 7250.3 | 7450.9 | 7631.9 | 7436 | 7898.5 | 7462.1 | 7358 | 7550.4 | 7519.9 | 7925.8 | 7583.1 | 7823.4 | 7605.2 | 10601.5 | 11403.4 | 10362.2 | 10840.6 | 11327.3 | 7063.3 | 10764.3 | 10805 | 10699 | 10690 | 10609.3 | 10642.8 | 9757.7 | 9956.9 | 9741.3 | 9822.9 | 9917.4 | 10314.2 | 9975.3 | 10036.6 | 8190.8 | 8263.5 | 8090.4 | 8011.9 | 8235.5 | 8238.8 | 11691 | 12863 | 9585.9 | 11548.2 | 8576 | 8384 | 8705 | 9668 | 10273 | 10335 | 10176 | 10513 | 7171 | 5724 | 6908 | 6820 | 7202 | 7068 | 7518 | 7475 | 8620 | 8859 | 8452 | 8942 |  |  |  |  | 1215 | 1024 | 4703 | 7639 | 5.8536 | 6.7301 | 6.1861 | 6.9537 | 0.75762 | 0.90826 | 1.0447 | 1.0297 | 30.2949 | 30.2691 | 44.4443 | 42.7233 | 57.9487 | 59.8524 | 0 | 0 | 1.1554 | 1.2188 | 3.078 | 3.42 | 6.2918 | 6.5699 | 0.83294 | 1.0372 | 30.282 | 43.5838 | 58.9006 |  | 1.1871 | 3.249 | 246729.9 | 16454.3 | 39278.8 | 78264.7 | 40243.5 | 117834 | 29263 | 34873 | 602941.2 | 42145.2 | 216.6 | 36638.1 | 229.2 | 42924.9 | 411.2 | 10175.9 | 50.1 | 516.9 | 1.9 | 99.57 | 135822893 | 971933.632 | 1168 | 130001 | 188340.4 | 1895.3 | 124900 | 400 | 118300 | 400 | 171800 | 600 | 14400 | 300 | 144700 | 500 | 280 | 593855 | 2325.056 | 2160 | 367920 | 591768 | 2880 | 596180.056 | 591529.944 | 588888 | -1.121% | 12.65 | 122.7 | Cloudy Weather
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 6:10 | 18:42 | 8281.1 | 8262.6 | 7867.2 | 7912 | 8087.7 | 8282.8 | 8116.3 | 8608.2 | 8254.2 | 7977.2 | 8241.3 | 8310.4 | 8740 | 8432.3 | 8480.1 | 8278.4 | 11671.1 | 12732.4 | 11347.5 | 11970.1 | 12469 | 7791 | 11783 | 12015.7 | 11589.4 | 11553 | 11523.8 | 11585.4 | 9492.4 | 9743.2 | 9467.9 | 9585.9 | 9559.2 | 9907.6 | 9651.3 | 9696.3 | 7927.7 | 8013.7 | 7801.1 | 7783.1 | 8025.1 | 8005.7 | 11323 | 12556.6 | 9277.6 | 11220.9 | 9464 | 9272 | 9868 | 11162 | 12070 | 12149 | 11945 | 12210 | 8216 | 6472 | 7757 | 7736 | 8205 | 7968 | 8486 | 8427 | 9188 | 9510 | 9257 | 9582 |  |  |  |  | 1291 | 1099 | 5018 | 8213 | 6.2058 | 6.3873 | 6.5734 | 6.6101 | 0.76123 | 0.90204 | 1.0786 | 0.97543 | 29.7695 | 30.0501 | 44.4059 | 42.522 | 61.9664 | 61.7493 | 0.034037 | 0.0096463 | 0.95358 | 1.0195 | 2.772 | 3.099 | 6.2965 | 6.5917 | 0.83163 | 1.027 | 29.9098 | 43.464 | 61.8578 | 0.021842 | 0.98652 | 2.9355 | 270163.2 | 15941.4 | 38289.4 | 75993.1 | 38814.4 | 133942 | 33086 | 37537 | 643766.5 | 42282.3 | 216.9 | 36766.5 | 229.5 | 43091.5 | 411.8 | 10191.4 | 50.3 | 679 | 2.4 | 99.84 | 136456110 | 974043.456 | 1171 | 130712 | 189217 | 1898.9 | 137100 | 300 | 128400 | 300 | 166600 | 600 | 15500 | 300 | 162100 | 500 | 270 | 633217 | 2109.824 | 2160 | 511920 | 631152 | 2592 | 635326.824 | 631107.176 | 628560 | -1.311% | 12.5333 | 122.7 | Cloudy Weather
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 6:04 | 18:33 | 8084.3 | 7928.7 | 7489.5 | 7685.5 | 7962.5 | 8215.6 | 7907.7 | 8590 | 7898.9 | 7809.3 | 8123.4 | 8102.8 | 8327.1 | 8232.8 | 8169.1 | 7825.5 | 11133.8 | 12222.2 | 10708 | 11205.4 | 12104 | 7353.6 | 11306.6 | 11537.1 | 11164.4 | 11106 | 11124 | 11243.4 | 9626.6 | 9863.3 | 9669.2 | 9692.8 | 9743.1 | 10070.6 | 9897.3 | 9799.8 | 8031.9 | 8107.7 | 8053.3 | 7966.1 | 8223.7 | 8134.2 | 11357.5 | 12721.3 | 9299.8 | 11318.6 | 9769 | 9550 | 9904 | 11220 | 12372 | 12395 | 12041 | 12292 | 8155 | 6577 | 7458 | 7701 | 8563 | 8204 | 8756 | 8779 | 8897 | 9163 | 9052 | 9439 |  |  |  |  | 1232 | 1044 | 4787 | 7999 | 6.1055 | 6.4431 | 6.4356 | 6.6995 | 0.78389 | 6.4431 | 1.0878 | 1.0146 | 31.8741 | 32.1407 | 45.2262 | 43.3428 | 51.9268 | 52.1104 | 0 | 0 | 1.2548 | 1.2395 | 2.757 | 2.886 | 6.2743 | 6.5675 | 3.6135 | 1.0512 | 32.0074 | 44.2845 | 52.0186 |  | 1.2471 | 2.8215 | 260561.2 | 16139.6 | 38851.9 | 77074.5 | 39510.8 | 134496 | 34302 | 36551 | 637487 | 42413.5 | 217.3 | 36891.6 | 229.9 | 43260.7 | 412.6 | 10206.3 | 50.5 | 842.4 | 2.9 | 100.13 | 137083346 | 976484.672 | 1174 | 131336 | 190085.3 | 1903.1 | 131200 | 400 | 125100 | 400 | 169200 | 800 | 14900 | 300 | 163400 | 500 | 290 | 627236 | 2441.216 | 2160 | 449280 | 625176 | 3024 | 629677.216 | 624794.784 | 622152 | -1.225% | 12.4833 | 122.7 | Cloudy Weather
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 6:03 | 18:39 | 7710.6 | 7646.2 | 7228 | 7291.9 | 7515.8 | 7762.1 | 7533.9 | 8116.7 | 7661.1 | 7484.4 | 7806.7 | 7844.5 | 8078.6 | 7953.7 | 7910.9 | 7645.5 | 10817.7 | 11916.2 | 10419.5 | 10878.3 | 11961.3 | 7275.2 | 11258.2 | 11448.1 | 11162.5 | 11140 | 11111 | 11186.3 | 9284.6 | 9512 | 9312.5 | 9375.9 | 9334.7 | 9629 | 9467.4 | 9335 | 7604 | 7648 | 7687.7 | 7627.7 | 7815.4 | 7688.9 | 10841.4 | 12169.9 | 8766.8 | 10532.2 | 8686.8 | 8546.1 | 8885.1 | 9868.4 | 11380 | 11288 | 10444 | 10765 | 8070 | 6176 | 7265 | 7566 | 8377 | 8035 | 8595 | 8698 | 8400 | 8661.4 | 8331 | 8696.9 |  |  |  |  | 1160 | 9570 | 3820 | 6870 | 5.7961 | 6.0681 | 6.1151 | 6.2708 | 0.76153 | 0.85667 | 1.029 | 0.95407 | 32.6227 | 33.0125 | 46.2008 | 44.6585 | 52.245 | 52.3797 | 0 | 0 | 1.4491 | 1.5446 | 3.177 | 2.94 | 5.9321 | 6.193 | 0.8091 | 0.99153 | 32.8176 | 45.4297 | 52.3123 |  | 1.4968 | 3.0585 | 253764.9 | 15252 | 37485 | 73130 | 37766.1 | 130360.4 | 33705 | 34089.3 | 615552.7 | 42543.1 | 217.7 | 37012 | 230.2 | 43422.1 | 413.1 | 10220.5 | 50.6 | 988.2 | 3.3 | 100.39 | 137675423 | 978373.696 | 1176 | 131926 | 190904.9 | 1906.3 | 129600 | 400 | 120400 | 300 | 161400 | 500 | 14200 | 400 | 145800 | 400 | 260 | 592077 | 1889.024 | 1440 | 424800 | 590112 | 2304 | 593966.024 | 590187.976 | 587808 | -3.507% | 12.6 | 122.7 | Cloudy Weather
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 6:08 | 18:45 | 8389.9 | 8310 | 7918.4 | 7994.6 | 8204.8 | 8435.6 | 8244.7 | 8808 | 8285.2 | 8135.1 | 8407.5 | 8421.3 | 8666.5 | 8414.6 | 8535.7 | 8323.9 | 11615.2 | 12505.8 | 11333.6 | 11812.1 | 12216.1 | 7390 | 11510.8 | 11704 | 11504.9 | 11480.7 | 11476.9 | 11515.6 | 9465.5 | 9695 | 9450.4 | 9512.4 | 9547.5 | 9870.6 | 9724.4 | 9601.2 | 7846.6 | 7879.8 | 7842.4 | 7774.9 | 8025.5 | 7895.3 | 11175.8 | 12607.6 | 9161.1 | 10995.6 | 9260.8 | 9087.9 | 9511.3 | 10687.8 | 11617 | 11512 | 11617 | 11513 | 7807 | 6177.6 | 7112 | 7379.6 | 7930 | 7633 | 8226 | 8227 | 8748 | 9000 | 8746 | 9103 |  |  |  |  | 1216 | 1027 | 4716 | 7872 | 6.3825 | 6.2693 | 6.7277 | 6.4908 | 0.82118 | 0.88601 | 1.129 | 0.99117 | 32.6736 | 33.0679 | 46.4817 | 44.2907 | 54.235 | 54.3715 | 0 | 0 | 1.8531 | 1.937 | 3.261 | 3.615 | 6.3259 | 6.6092 | 0.85359 | 1.0601 | 32.8708 | 45.3862 | 54.3032 |  | 1.8951 | 3.438 | 269561.5 | 15726.4 | 38123.3 | 75478.2 | 38743.7 | 128114 | 32016 | 35597 | 633360.1 | 42678.1 | 218 | 37141.8 | 230.6 | 43587.9 | 413.7 | 10235.2 | 50.8 | 1141.9 | 3.7 | 100.68 | 138298261 | 980442.88 | 1178 | 132546 | 191767.1 | 1909.9 | 135000 | 300 | 129800 | 400 | 165800 | 600 | 14700 | 300 | 153700 | 400 | 290 | 622838 | 2069.184 | 1440 | 446400 | 620784 | 2592 | 624907.184 | 620768.816 | 618192 | -1.335% | 12.6167 | 122.7 | Cloudy Weather
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 6:02 | 18:47 | 8870.8 | 8753.3 | 8254.2 | 8285.7 | 8527.2 | 8844.4 | 8591.9 | 9311.5 | 8673.4 | 8496.2 | 8818.8 | 8806.3 | 9098.5 | 8844 | 8980.8 | 8674.1 | 12087 | 13147.5 | 11759.5 | 12304.4 | 13076 | 7828.1 | 12161.6 | 12308.8 | 12132.8 | 12101.5 | 12106.5 | 12133.1 | 9797 | 10039.6 | 9872.6 | 9954.3 | 9910.8 | 10259.4 | 10078 | 9952.3 | 8150.8 | 8194.3 | 8179 | 8117.4 | 8352.8 | 8223.9 | 11562.6 | 12940.5 | 9393 | 11331.1 | 9708 | 9467 | 9678.7 | 10911 | 11882.7 | 11956 | 11746 | 12063 | 8066 | 6370 | 7534 | 7643 | 8066 | 6370 | 7534 | 7643 | 9121 | 9387 | 9151 | 9519 |  |  |  |  | 1288 | 1090 | 4975 | 8261 | 7.1267 | 6.5235 | 6.9949 | 6.7714 | 0.84055 | 0.94987 | 1.1922 | 1.0488 | 32.9652 | 33.2855 | 46.2951 | 44.0453 | 53.4592 | 53.8545 | 0 | 0 | 2.3182 | 2.4537 | 4.047 | 4.443 | 6.8251 | 6.8832 | 0.89521 | 1.1205 | 33.1254 | 45.1702 | 53.6568 |  | 2.386 | 4.245 | 282977.9 | 16345.1 | 39663.5 | 78100.3 | 40200.5 | 132639.4 | 29613 | 37178 | 656717.7 | 42820.2 | 218.4 | 37277.8 | 231 | 43759.8 | 414.5 | 10250.6 | 50.9 | 1301.5 | 4.1 | 100.99 | 138947952 | 982710.4 | 1181 | 133193 | 192666.4 | 1913.8 | 142100 | 400 | 136000 | 400 | 171900 | 800 | 15400 | 400 | 159600 | 400 | 310 | 649691 | 2267.52 | 2160 | 465840 | 647496 | 2808 | 651958.52 | 647423.48 | 644688 | -0.7247% | 12.75 | 122.7 | Cloudy Weather
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 6:03 | 18:45 | 8065.9 | 7972.5 | 7534.8 | 7570.3 | 7773.5 | 8041.5 | 7826 | 8451.6 | 7929 | 7705.4 | 7953.4 | 7929.3 | 8271.5 | 7948.4 | 8165.1 | 7927.1 | 10990.9 | 11910.5 | 10772 | 11279.4 | 11833 | 7072.2 | 10972.9 | 11079.2 | 10969.8 | 10942 | 10933 | 10936.9 | 8938.8 | 9152.5 | 9001.2 | 9055.7 | 9046.7 | 9367.7 | 9221.1 | 9093.5 | 7399 | 7454.2 | 7438.6 | 7375.7 | 7585.5 | 7497.3 | 10546.6 | 11818.9 | 8561.6 | 10316.8 | 9303 | 9078 | 9261 | 10506 | 11395 | 11447 | 11264 | 11520 | 7675 | 6069 | 7154 | 7249 | 7869 | 7640 | 8225 | 8187 | 5971 | 6458 | 7341 | 7540 |  |  |  |  | 1206 | 1022 | 4704 | 7820 | 7.2046 | 5.8838 | 5.4856 | 6.02 | 0.72814 | 0.8701 | 1.0598 | 0.93599 | 32.9368 | 33.25 | 46.3013 | 43.9781 | 52.1135 | 52.6549 | 0 | 0 | 2.0993 | 2.161 | 3.918 | 3.852 | 6.5442 | 5.7528 | 0.79912 | 0.99789 | 33.0934 | 45.1397 | 52.3842 |  | 2.1302 | 3.885 | 256757.1 | 14853.2 | 36148.2 | 71141 | 36729 | 126673 | 31921 | 27310 | 601532.5 | 42949 | 218.7 | 37401.9 | 231.3 | 43916.6 | 415 | 10265.3 | 51 | 1446 | 4.4 | 101.28 | 139540135 | 984623.68 | 1184 | 133783 | 193486.1 | 1917.1 | 128800 | 300 | 124100 | 300 | 156800 | 500 | 14700 | 300 | 144500 | 300 | 290 | 592183 | 1913.28 | 2160 | 424800 | 590184 | 2376 | 594096.28 | 590269.72 | 587808 | -1.236% | 12.7 | 122.7 | Cloudy Weather. IDT-13 Tripped in overcurrent from 10:45 to 12:37
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 6:02 | 18:15 | 4930 | 4839 | 4535.8 | 4538.5 | 4676 | 4853.2 | 4711.6 | 5251.2 | 4826.7 | 4685.4 | 4851.9 | 4823.2 | 5064.1 | 4831.8 | 5024.6 | 4802.2 | 6650.6 | 7493 | 6538.7 | 6821 | 7225.7 | 4285.8 | 6696.6 | 6830.4 | 6634.4 | 6594.8 | 6669.3 | 6702.2 | 5514.6 | 5689.3 | 5611.6 | 5666.7 | 5617.3 | 5839.6 | 5728.9 | 5660.6 | 4577.4 | 4609.3 | 4597.6 | 4561.3 | 4690.2 | 4634.9 | 6529.7 | 7385.9 | 5323.7 | 6447.3 | 6380.6 | 6164.7 | 5521.1 | 6209 | 6726.7 | 6705 | 6593.3 | 6774 | 4372 | 3422 | 4041 | 4103 | 4508.5 | 4331.9 | 4810 | 4792.2 | 4915.2 | 5074.8 | 4988.3 | 5146 |  |  |  |  | 633 | 530 | 2602 | 4389.8 | 4.1416 | 3.5241 | 3.159 | 3.5746 | 0.40037 | 0.54498 | 0.62536 | 0.57115 | 30.3284 | 30.5296 | 40.9999 | 38.774 | 61.6771 | 62.6436 | 0 | 0 | 1.8193 | 2.0122 | 3.441 | 3.6 | 3.8329 | 3.3668 | 0.47268 | 0.59826 | 30.429 | 39.887 | 62.1603 |  | 1.9158 | 3.5205 | 156387.7 | 9186.7 | 22482.2 | 44170.6 | 22846.4 | 75167.2 | 18442.6 | 20124.3 | 368807.7 | 43027.7 | 219.1 | 37478.3 | 231.7 | 44014.4 | 415.7 | 10273.5 | 51.2 | 1535.6 | 4.9 | 101.55 | 139905236 | 986738.816 | 1186 | 134147 | 193991.5 | 1920.7 | 78700 | 400 | 76400 | 400 | 97800 | 700 | 8200 | 400 | 89600 | 500 | 270 | 365101 | 2115.136 | 1440 | 262080 | 363888 | 2592 | 367216.136 | 362985.864 | 361296 | -0.4315% | 12.2167 | 122.7 | Fully Cloudly Weather
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 6:01 | 17:55 | 7348.3 | 7307.8 | 6868.6 | 6804.2 | 6983.9 | 7253.4 | 7063.4 | 7806.8 | 7172 | 6944.9 | 7230.1 | 7239 | 7567 | 7226.5 | 7359.8 | 7114.1 | 9905.5 | 10960.5 | 9664.2 | 10137.4 | 10610.8 | 6380.8 | 9796.1 | 9967.3 | 9767.2 | 9776.9 | 9696.9 | 9743.7 | 8192.3 | 8393 | 8175 | 8234.5 | 8257.2 | 8536.6 | 8431.8 | 8292.6 | 6777.6 | 6806.8 | 6771.7 | 6713 | 6914.9 | 6834.2 | 9651.9 | 10852.9 | 7805.9 | 9409.9 | 8838 | 8677 | 9095.5 | 10058.5 | 11230 | 10990 | 10671.7 | 11001.2 | 7377 | 5820.5 | 6820 | 6951.9 | 7434.7 | 7194 | 7802.6 | 7798.6 | 8267.1 | 8527.1 | 8274 | 8582 |  |  |  |  | 1180 | 1000 | 4516 | 7506.9 | 6.5063 | 5.3872 | 4.9436 | 5.5228 | 0.6839 | 0.7863 | 0.96311 | 0.8641 | 29.2454 | 28.9864 | 41.8335 | 39.639 | 74.288 | 73.7657 | 0.24809 | 0.15584 | 1.3921 | 1.3735 | 7.263 | 6.054 | 5.9467 | 5.2332 | 0.7351 | 0.91361 | 29.1159 | 40.7362 | 74.0269 | 0.20196 | 1.3828 | 6.6585 | 231697.1 | 13584.4 | 32994.8 | 64954.4 | 33518.2 | 121734.2 | 30229.9 | 33650.2 | 562363.2 | 43143.3 | 219.5 | 37590.7 | 232.1 | 44157.6 | 416.4 | 10287.5 | 51.4 | 1679.8 | 5.6 | 101.82 | 140458016 | 989624.192 | 1190 | 134697 | 194756.8 | 1925.6 | 115600 | 400 | 112400 | 400 | 143200 | 700 | 14000 | 400 | 144200 | 700 | 270 | 552780 | 2885.376 | 2880 | 396000 | 551016 | 3528 | 555665.376 | 549894.624 | 547488 | -1.191% | 11.9 | 122.7 | fully cloudy weather. Power Trafo Trip due to 33 kV 2nd TL Line Over Current & Earth Fault From 16:22 to 16:53
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 6:01 | 18:38 | 8210.1 | 8159.7 | 7744.1 | 7846.4 | 8108.4 | 8353.3 | 8074.8 | 8690.8 | 8079.8 | 7851.2 | 8122.2 | 8130.7 | 8518.4 | 8071.6 | 8240.6 | 8060.5 | 11157.5 | 11932.2 | 10962.6 | 11537.4 | 11635.2 | 7274.9 | 11132.6 | 11272 | 11047.9 | 11088 | 10936 | 10963.4 | 9247.5 | 9501 | 9511.5 | 9717 | 9457 | 9889.6 | 9641.7 | 9643.3 | 8000.7 | 8109.7 | 7942 | 7875 | 8191.6 | 8149 | 10947.5 | 12157 | 9040 | 11042.5 | 9320.8 | 9029.6 | 9678 | 10718 | 12510 | 11215 | 11343.5 | 11721 | 7757 | 6200 | 7294.9 | 7311 | 8075 | 7990 | 8233 | 8102 | 8843.9 | 9162 | 8990 | 9321 |  |  |  |  | 1231.8 | 1050 | 4759 | 7932 | 7.554 | 4.3333 | 5.757 | 3.4167 | 0.74359 | 0.0023462 | 1.0491 | 0.0016296 | 30.572 | 5.2326 | 45.6332 | 6.0657 | 73.4764 | 19.2519 | 0 | 0 | 0.84872 | 0.17375 | 2.973 | 1.668 | 5.9436 | 4.5868 | 0.37297 | 0.52536 | 17.9023 | 25.8494 | 46.3642 |  | 0.51123 | 2.3205 | 261202.3 | 16110.4 | 37977 | 75344.6 | 38631.6 | 129071.6 | 32400 | 36316.9 | 627054.4 | 43273.3 | 219.9 | 37715.5 | 232.4 | 44323.2 | 417.7 | 10302.4 | 51.7 | 1829.7 | 6.4 | 102.11 | 141069860 | 992910.336 | 1194 | 135307 | 195603.8 | 1930.8 | 130000 | 400 | 124800 | 300 | 165600 | 1300 | 14900 | 300 | 149900 | 800 | 290 | 611844 | 3286.144 | 2880 | 439200 | 609840 | 3744 | 615130.144 | 608557.856 | 606096 | -1.902% | 12.6167 | 122.7 | ICR 12 trip Due to Over Current From 13:05 to 14:27 & Block 05 to 09 Communication error & Moving Cloudy Weather
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 5:56 | 18:32 | 7578.7 | 7593.7 | 7075.9 | 6973.4 | 7262.4 | 7550 | 7277.3 | 7994.8 | 7407.5 | 7151.1 | 7592.5 | 7643.1 | 7898.1 | 7840.2 | 7657.8 | 7376.2 | 10755.6 | 11929.6 | 10211.3 | 10803 | 11515.1 | 7180.4 | 10956.9 | 10995.5 | 10849.8 | 10889 | 10785.9 | 10828.4 | 8837.5 | 8972.4 | 8423 | 8365.8 | 8762 | 8875.6 | 8881.9 | 8611 | 6843 | 6803.8 | 6918 | 6837.6 | 6941.9 | 6811 | 10304 | 11440 | 8292 | 9690 | 9065 | 8793.8 | 8925.7 | 9931.7 | 9057 | 9503 | 10791.6 | 11126 | 7749 | 6249.8 | 7508 | 7453.9 | 7972 | 7749 | 8433.6 | 8373 | 9105 | 9403 | 8969.6 | 9540 |  |  |  |  | 1318 | 1115 | 5002 | 8284 | 6.8713 | 6.8713 | 5.2344 | 5.2344 | 0.71467 | 0.71467 | 0.98105 | 0.98105 | 30.9354 | 30.9354 | 44.8542 | 44.8542 | 68.3482 | 68.3482 | 0 | 0 | 0.81648 | 0.81648 | 4.221 | 4.221 | 6.8713 | 5.2344 | 0.71467 | 0.98105 | 30.9354 | 44.8542 | 68.3482 |  | 0.81648 | 4.221 | 247573.2 | 13646.8 | 34598.7 | 67234.5 | 35130.5 | 121873.5 | 32527.6 | 37017.6 | 589602.4 | 43400.2 | 220.4 | 37830.6 | 232.9 | 44472 | 419.4 | 10317.9 | 52 | 1980.7 | 7.1 | 102.45 | 141654163 | 996937.856 | 1198 | 135889 | 196412.8 | 1937.4 | 126900 | 500 | 115100 | 500 | 148800 | 1700 | 15500 | 400 | 151000 | 700 | 340 | 584303 | 4027.52 | 2880 | 419040 | 582480 | 4752 | 588330.52 | 580275.48 | 577728 | -0.2157% | 12.6 | 122.7 | Cloudy Weather
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 6:10 | 18:16 | 7252.8 | 7317.7 | 6979.5 | 6687 | 6735.1 | 7138.4 | 7024.1 | 7553.1 | 6927.4 | 6542 | 6661.7 | 6697.9 | 7254.5 | 6291 | 7022.9 | 6903.7 | 9264.9 | 9725.8 | 9434.2 | 10013.3 | 9562.9 | 6039.6 | 9095.8 | 9142.6 | 8855.9 | 8857.8 | 8872.3 | 8790.1 | 7096.8 | 7232.8 | 7110.8 | 7172.9 | 7063.9 | 7257.8 | 7155.8 | 7080.3 | 5614 | 5648.2 | 5681 | 5680.7 | 5771.3 | 5693 | 8261 | 9352.8 | 6667.8 | 7863.8 | 8851.7 | 8503.9 | 9082.1 | 10040.8 | 10840 | 10971.9 | 10816 | 11200.4 | 7603.5 | 6136 | 7289.8 | 6136 | 7655.1 | 7345.9 | 7833 | 7869.2 | 8864.6 | 9237.3 | 8577.8 | 9229.6 |  |  |  |  | 1268.7 | 1075.5 | 4858.1 | 7882.5 | 6.8341 | 6.8341 | 5.2119 | 5.2119 | 0.68744 | 0.68744 | 0.96393 | 0.96393 | 30.2926 | 30.2926 | 44.8827 | 44.8827 | 74.6609 | 74.6609 | 0.10717 | 0.070963 | 1.1508 | 1.1508 | 3.342 | 3.342 | 6.8341 | 5.2119 | 0.68744 | 0.96393 | 30.2926 | 44.8827 | 74.6609 | 0.089064 | 1.1508 | 3.342 | 218644 | 11262.2 | 28613.3 | 54971.4 | 28557.8 | 122556.9 | 30703.2 | 35909.3 | 531218.1 | 43507.1 | 220.6 | 37938 | 233.1 | 44594.1 | 420.3 | 10332.9 | 52.1 | 2128.1 | 7.6 | 102.68 | 142178959 | 999191.168 | 1201 | 136411 | 197139.4 | 1941 | 106900 | 200 | 107400 | 200 | 122100 | 900 | 15000 | 400 | 147400 | 500 | 230 | 524796 | 2253.312 | 2160 | 375840 | 523152 | 2592 | 527049.312 | 522542.688 | 520560 | -0.7848% | 12.1 | 122.7 | Fully Cloudly Weather
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 5:56 | 18:50 | 6264.3 | 6230.5 | 5935.7 | 5918.3 | 6084.2 | 6303.5 | 6117.1 | 6554.9 | 6156 | 5967.3 | 6240.7 | 6290.9 | 6575 | 6531.4 | 6373.1 | 6179.6 | 8924.9 | 9869.2 | 8527.9 | 9107 | 9668.1 | 6212 | 9358.1 | 9242.4 | 9139.8 | 9172.6 | 9263.1 | 9078.2 | 7633.4 | 7775.4 | 7606.4 | 7628.3 | 7632.3 | 7862.5 | 7773.7 | 7676.7 | 6020.6 | 5994.1 | 6012.3 | 5980.8 | 6068.3 | 6006 | 8777 | 9591 | 7292 | 8493.9 | 8022.2 | 7751.3 | 7938 | 8562.8 | 9127.5 | 9102.7 | 8888 | 9277.8 | 6075.9 | 4869.2 | 5738.4 | 5685.4 | 6170.6 | 5797.1 | 6314.1 | 6399.5 | 6889.3 | 7144.4 | 6695.6 | 7170.8 |  |  |  |  | 906.9 | 758.7 | 3630.5 | 6041.2 | 5.8581 | 5.0077 | 4.4697 | 5.175 | 0.60221 | 0.64481 | 0.8199 | 0.72479 | 29.7293 | 28.2416 | 42.3348 | 39.8817 | 78.5566 | 84.0736 | 0.06789 | 0.20257 | 1.1324 | 0.93926 | 3.543 | 3.861 | 5.4329 | 4.8223 | 0.62351 | 0.77235 | 28.9854 | 41.1083 | 81.3151 | 0.13523 | 1.0358 | 3.702 | 207285.8 | 12014.7 | 30643.5 | 58221.3 | 30945.2 | 102376.5 | 24681.3 | 27900.1 | 494068.4 | 43614 | 221 | 38034.7 | 233.5 | 44724.5 | 421.6 | 10344.2 | 52.3 | 2249.5 | 8.3 | 102.94 | 142667268 | 1002321.216 | 1205 | 136898 | 197815.5 | 1946.1 | 106900 | 400 | 96700 | 400 | 130400 | 1300 | 11300 | 300 | 121400 | 700 | 260 | 488309 | 3130.048 | 2880 | 350640 | 486792 | 3672 | 491439.048 | 485178.952 | 483120 | -0.5322% | 12.9 | 122.7 | Fully Cloudy Weather & Heavy rain
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 6:11 | 18:49 | 7829 | 7899.7 | 7589.5 | 7418.4 | 7520.1 | 7726.1 | 7649.7 | 8123.5 | 7786.6 | 7569.6 | 7878.5 | 7941.7 | 8302.8 | 8170.6 | 8080.4 | 7885.2 | 11189.2 | 12049.6 | 10808.5 | 11624.6 | 12117.2 | 7745.3 | 11790.6 | 11595.5 | 11463.6 | 11430 | 11599.8 | 11622.2 | 8368.6 | 8592.1 | 8402.4 | 8517.5 | 8435.1 | 8771.2 | 8623.1 | 8563.8 | 6859.8 | 6918.6 | 6784.2 | 6779.4 | 6895 | 6896.2 | 9750.3 | 10715.1 | 8070.5 | 9646.8 | 9044.5 | 8769.6 | 9427.6 | 10323.2 | 11031.6 | 11055.6 | 10841.1 | 11208.8 | 7584.6 | 6087.5 | 7178.9 | 6087.5 | 7686 | 7359 | 7880.3 | 7904.9 | 8782.1 | 9057.6 | 8568.3 | 9212.5 |  |  |  |  | 1233.9 | 1045 | 4770 | 7784.4 | 6.9962 | 5.6716 | 5.6284 | 5.8648 | 0.75192 | 0.77416 | 1.08 | 0.87413 | 30.4882 | 30.1585 | 44.8853 | 41.1581 | 62.4295 | 65.8185 | 0 | 0.019704 | 1.6342 | 1.5738 | 4.638 | 4.119 | 6.3339 | 5.7466 | 0.76304 | 0.97706 | 30.3234 | 43.0217 | 64.124 | 0.019704 | 1.604 | 4.3785 | 260407.5 | 13778.4 | 33880.6 | 65537.5 | 34393.2 | 123473.8 | 30830.2 | 35620.5 | 597921.7 | 43748 | 221.4 | 38156 | 233.8 | 44870.3 | 422.9 | 10359 | 52.6 | 2397.9 | 9.1 | 103.22 | 143257403 | 1005652.224 | 1209 | 137486 | 198632.4 | 1951.4 | 134000 | 400 | 121300 | 300 | 145800 | 1300 | 14800 | 500 | 148400 | 800 | 280 | 590135 | 3331.008 | 2880 | 423360 | 588168 | 3816 | 593466.008 | 586803.992 | 584352 | -0.7452% | 12.6333 | 122.7 | Moving Cloudy Weather
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 6:06 | 18:35 | 5006.2 | 4981.4 | 4689.9 | 4720.3 | 4878.1 | 4995.9 | 4846.9 | 5341.9 | 4989 | 4840.9 | 5038.7 | 5079.1 | 5310.2 | 5127.8 | 5170.6 | 4951.7 | 7030.6 | 7920.7 | 6801.4 | 7132.1 | 7731.7 | 4722.8 | 7212 | 7349.3 | 7127.1 | 7119.5 | 7095.5 | 7153.5 | 6012.1 | 6181 | 6063 | 6147.4 | 6029.9 | 6226 | 6094.8 | 6055.7 | 4832.6 | 4870.8 | 4893.7 | 4897.5 | 4992.3 | 4926.4 | 6872 | 7721.2 | 5616.4 | 6799.8 | 6695.4 | 6424.7 | 5996.9 | 6578.3 | 7152.4 | 7135.1 | 6924.8 | 7200.3 | 4645.1 | 3687.7 | 4313.2 | 3687.7 | 4924.8 | 4589.8 | 5089.7 | 5104.1 | 5362 | 5532.1 | 5230.7 | 5642.9 | 121 | 44 | 21 | 33 | 690.4 | 575.5 | 2842.7 | 4742.7 | 4.1243 | 3.7579 | 3.2681 | 3.821 | 0.44054 | 0.53943 | 0.63138 | 0.5853 | 29.4536 | 29.412 | 40.3565 | 37.9973 | 66.2031 | 67.9606 | 0.040489 | 0.1113 | 1.7751 | 1.8104 | 3.909 | 4.179 | 3.9411 | 3.5445 | 0.48999 | 0.60834 | 29.4328 | 39.1769 | 67.0819 | 0.075894 | 1.7928 | 4.044 | 164364.8 | 9703.4 | 24403.5 | 46719.3 | 24406.4 | 79511.9 | 19708.4 | 21767.7 | 390585.4 | 43832 | 221.8 | 38235.2 | 234.1 | 44974.7 | 424.2 | 10368.2 | 52.8 | 2493.5 | 9.6 | 103.47 | 143645736 | 1008574.784 | 1212 | 137872 | 199170.1 | 1956.2 | 84000 | 400 | 79200 | 300 | 104400 | 1300 | 9200 | 200 | 95600 | 500 | 250 | 388333 | 2922.56 | 2160 | 277920 | 387144 | 3456 | 391255.56 | 385410.44 | 383688 | 0.1716% | 12.4833 | 122.7 | Fully Cloudly Weather
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 6:04 | 18:44 | 4827.5 | 4762.6 | 4533.6 | 4592.2 | 4746.9 | 4863.7 | 4711.8 | 5092.9 | 4805.1 | 4692.3 | 4858.3 | 4856.3 | 5069.6 | 4922.4 | 4975.8 | 4720.6 | 6694.7 | 7492.2 | 6485.5 | 6818.1 | 7319.9 | 4533.2 | 6896 | 7042.5 | 6804.7 | 6779.6 | 6796.9 | 6838.5 | 5809.9 | 5950.5 | 5836.5 | 5887.4 | 5900.8 | 6135.1 | 6058.2 | 5986.9 | 4784.3 | 4796.3 | 4720.6 | 4686.1 | 4802.7 | 4790.4 | 6909.5 | 7768.3 | 5749.2 | 6903.9 | 6610.5 | 6270.6 | 5893.4 | 6602.5 | 7240.8 | 7304.9 | 7204.7 | 7452.6 | 4724.9 | 3817.9 | 4469.8 | 3817.9 | 5078 | 4761.6 | 5240.6 | 5247.4 | 5749 | 5929.6 | 5570.8 | 6020.8 | 774 | 225 | 575 | 160 | 762.4 | 641.5 | 3091.5 | 5096.5 | 3.9659 | 3.6994 | 3.1133 | 3.7331 | 0.41415 | 0.52957 | 0.59488 | 0.57456 | 27.5793 | 26.5898 | 37.351 | 35.2414 | 85.8823 | 86.0655 | 0.10784 | 0.087948 | 1.5408 | 1.7563 | 4.533 | 5.22 | 3.8326 | 3.4232 | 0.47186 | 0.58472 | 27.0845 | 36.2962 | 85.9739 | 0.097896 | 1.6486 | 4.8765 | 157533.4 | 9580.6 | 23484.3 | 46330.7 | 24081 | 82736.4 | 20327.6 | 23270.2 | 387344.2 | 43912 | 222.2 | 38311.1 | 234.5 | 45077.4 | 425.6 | 10379.8 | 52.9 | 2591.6 | 10.4 | 103.72 | 144030826 | 1011936.512 | 1216 | 138256 | 199703.2 | 1961.6 | 80000 | 400 | 75900 | 400 | 102700 | 1400 | 11600 | 400 | 98100 | 800 | 250 | 385090 | 3361.728 | 2880 | 276480 | 383832 | 3888 | 388451.728 | 381728.272 | 379944 | 0.2859% | 12.6667 | 122.7 | Fully Cloudy Weather & Heavy rain
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 6:05 | 18:45 | 8059 | 8051.9 | 7670.5 | 7607.4 | 7799.8 | 7995.5 | 7826.6 | 8444.9 | 7916.2 | 7707.8 | 7950.7 | 7975.5 | 8392.1 | 8070 | 8187.6 | 7934.3 | 11059.1 | 12003.8 | 10829.8 | 11523.8 | 11716.2 | 7326 | 11286.2 | 11451.9 | 11065.6 | 11066.8 | 11183.4 | 11193.2 | 9500.2 | 9764.5 | 9583.6 | 9675 | 9663.4 | 10025.6 | 9864.2 | 9750.3 | 7874.4 | 7907 | 7801.4 | 7768.4 | 7922.1 | 7901.9 | 11256.2 | 12409.9 | 9301.6 | 11185.3 | 9545.8 | 9245.6 | 9615.1 | 10825.7 | 11575.8 | 11567.2 | 11429.3 | 11778.9 | 7668.8 | 6204.5 | 7244.7 | 6204.5 | 8099 | 7679.7 | 8283.2 | 8321.4 | 8946.4 | 9240.6 | 8740.7 | 9424.1 | 2296.1 | 721.4 | 2818.1 | 533.5 | 1243.7 | 1057.6 | 4840 | 7969.8 | 6.9304 | 6.3047 | 5.5873 | 6.5957 | 0.74047 | 0.9503 | 1.0686 | 1.0346 | 29.5954 | 29.6072 | 42.4931 | 40.0163 | 68.334 | 69.7369 | 0 | 0 | 2.0351 | 2.063 | 4.575 | 4.794 | 6.6175 | 6.0915 | 0.84539 | 1.0516 | 29.6013 | 41.2547 | 69.0355 |  | 2.0491 | 4.6845 | 259295.6 | 15781.4 | 38523.3 | 75546.8 | 39303.5 | 134386.1 | 32383.3 | 36351.8 | 631571.8 | 44042.8 | 222.6 | 38435 | 234.8 | 45244.3 | 426.8 | 10401.4 | 53.1 | 2745.6 | 11.1 | 103.99 | 144654450 | 1015023.872 | 1220 | 138877 | 200566.4 | 1966.5 | 130800 | 400 | 123900 | 300 | 166900 | 1200 | 21600 | 300 | 154000 | 700 | 270 | 623624 | 3087.36 | 2880 | 447120 | 621504 | 3528 | 626711.36 | 620536.64 | 617976 | -0.7696% | 12.6667 | 122.7 | Moving Cloudy Weather
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 6:04 | 18:34 | 6687.6 | 6588.7 | 6248.8 | 6370.8 | 6591.2 | 6770 | 6529.9 | 7160 | 6619.2 | 6530.1 | 6764.1 | 6743.4 | 7022.2 | 6828 | 6904.8 | 6568.6 | 9260.7 | 10329.3 | 8953 | 9394.2 | 9922 | 6214.5 | 9519.9 | 9676.7 | 9350.7 | 9298.9 | 9378.1 | 9425.6 | 7929.7 | 8155 | 7976.3 | 8093.3 | 7980.2 | 8247.1 | 8107.1 | 8041.6 | 6475.4 | 6510.6 | 6463.1 | 6461.5 | 6588.3 | 6544 | 9204.3 | 10268.3 | 7498 | 9043.2 | 8706.3 | 8391.2 | 8102.6 | 8905.8 | 9657 | 9677.7 | 9543.6 | 9908.3 | 6426.6 | 5141.2 | 6035.3 | 6211 | 6897 | 6459.6 | 7141.9 | 7139 | 7531.4 | 7751 | 7367.4 | 7939.7 | 2484.5 | 602 | 2337 | 757 | 1042.5 | 880.1 | 4075 | 6724.5 | 5.6239 | 5.0946 | 4.4674 | 5.2393 | 0.60994 | 0.75791 | 0.85266 | 0.83215 | 29.2247 | 29.1469 | 41.2986 | 38.5857 | 68.4858 | 70.3006 | 0 | 0 | 1.8532 | 1.955 | 4.548 | 4.557 | 5.3593 | 4.8533 | 0.68393 | 0.8424 | 29.1858 | 39.9422 | 69.3932 |  | 1.9041 | 4.5525 | 217651 | 12986 | 32154.3 | 62070.7 | 32376 | 115609.2 | 27637.5 | 30589.5 | 531074.2 | 44152.9 | 223 | 38536.5 | 235.2 | 45382.4 | 428.3 | 10420.5 | 53.3 | 2876.5 | 11.7 | 104.27 | 145179394 | 1018456.32 | 1224 | 139400 | 201293.3 | 1972.1 | 110100 | 400 | 101500 | 400 | 138100 | 1500 | 19100 | 300 | 130900 | 600 | 280 | 524944 | 3432.448 | 2880 | 376560 | 523368 | 4032 | 528376.448 | 521511.552 | 519336 | -0.508% | 12.5 | 122.7 | Moving Cloudy Weather
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 6:05 | 18:29 | 4193.7 | 4170 | 3919.9 | 3932.4 | 4060.1 | 4171.8 | 4051.6 | 4426.2 | 4173.1 | 4047.1 | 4194.1 | 4203.5 | 4393.6 | 4235.7 | 4302.1 | 4102.3 | 5798.2 | 6559.8 | 5648.4 | 5926.1 | 6295.2 | 3893.5 | 5964.4 | 6070 | 5891.9 | 5867.2 | 5895.6 | 5918.4 | 4502.8 | 4671.3 | 4585.6 | 4648.9 | 4548.3 | 4706.5 | 4604.1 | 4557.1 | 3627.3 | 3647.8 | 3645.4 | 3660.7 | 3718.2 | 3675.2 | 5162 | 5794.3 | 4183.6 | 5069.3 | 5806.8 | 5521.1 | 5166.7 | 5730.1 | 6239.8 | 6336.4 | 6282.3 | 6464.1 | 4232.2 | 3287 | 3991.7 | 3954.2 | 4483.9 | 4121.2 | 4599.9 | 4619 | 4911.4 | 5064.3 | 4890 | 5175 | 2053.1 | 552.5 | 2504.5 | 1752.7 | 642.2 | 536.2 | 2664.1 | 4386.6 | 3.3832 | 2.7478 | 2.6358 | 2.7759 | 0.32665 | 0.44136 | 0.5018 | 0.45141 | 28.8012 | 28.5998 | 38.8154 | 35.9958 | 67.9227 | 70.6827 | 0 | 0.061803 | 1.8879 | 1.8652 | 4.116 | 4.842 | 3.0655 | 2.7059 | 0.384 | 0.4766 | 28.7005 | 37.4056 | 69.3027 | 0.061803 | 1.8766 | 4.479 | 136305.9 | 7275.1 | 18408.6 | 34908.7 | 18416 | 78104.3 | 17824 | 20040.7 | 331283.3 | 44222.2 | 223.3 | 38600.6 | 235.5 | 45461 | 429.4 | 10435.9 | 53.5 | 2962.1 | 12.2 | 104.48 | 145508876 | 1020830.272 | 1226 | 139728 | 201749.5 | 1976 | 69300 | 300 | 64100 | 300 | 78600 | 1100 | 15400 | 400 | 85600 | 500 | 210 | 329482 | 2373.952 | 1440 | 236160 | 328464 | 2808 | 331855.952 | 327108.048 | 325656 | 0.1729% | 12.4 | 122.7 | Fully Cloudly Weather
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 6:05 | 18:40 | 4317.9 | 4326.3 | 4029.8 | 4030.3 | 4134.9 | 4269.5 | 4174.3 | 4617.2 | 4300.3 | 4153.4 | 4310.3 | 4342.9 | 4531.2 | 4345.6 | 4424.7 | 4240.3 | 6027.7 | 6862.2 | 5843.3 | 6127.5 | 6557.9 | 3947.9 | 6068.1 | 6161.2 | 6032.3 | 6065 | 5993 | 6001.9 | 4575.5 | 4716.4 | 4603.2 | 4654.1 | 4583.2 | 4731.5 | 4661 | 4599 | 3657 | 3662.1 | 3668.6 | 3694.2 | 3732.3 | 3689.6 | 5269.2 | 5931.9 | 4229.9 | 5127.1 | 5912.2 | 5653.1 | 5113 | 5635.2 | 6111.3 | 6146.4 | 6074.5 | 6274.1 | 4020.4 | 3103 | 3785 | 3750 | 4264.5 | 3917.8 | 4361 | 4404.7 | 4688.3 | 4846.2 | 4675.3 | 4945.2 | 1898.4 | 498.9 | 3492.6 | 1919.4 | 581.9 | 483.4 | 2479.9 | 4178.9 | 3.4552 | 2.739 | 2.6891 | 2.739 | 0.33593 | 0.42499 | 0.50772 | 0.4485 | 27.9675 | 27.8547 | 38.1745 | 35.3205 | 72.9333 | 74.6751 | 0 | 0 | 1.7811 | 1.8734 | 4.572 | 4.749 | 3.0971 | 2.7141 | 0.38046 | 0.47811 | 27.9111 | 36.7475 | 73.8042 |  | 1.8272 | 4.6605 | 140236.9 | 7319.1 | 18549.2 | 35342.8 | 18574.7 | 77111.6 | 16948 | 19155 | 333237.3 | 44293.6 | 223.7 | 38666.9 | 235.8 | 45540.5 | 430.6 | 10451.8 | 53.6 | 3045.1 | 12.7 | 104.71 | 145840848 | 1023598.272 | 1230 | 140059 | 202209.2 | 1980.4 | 71400 | 400 | 66300 | 300 | 79500 | 1200 | 15900 | 300 | 83000 | 500 | 230 | 331972 | 2768 | 2880 | 238320 | 330984 | 3168 | 334740 | 329204 | 327816 | 0.4509% | 12.5833 | 122.7 | Fully Cloudly Weather
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 6:12 | 18:04 | 886.8 | 899.6 | 834.6 | 816.3 | 838.5 | 861.7 | 844.7 | 943 | 887.9 | 853.3 | 891.5 | 905.4 | 945.6 | 913 | 920.7 | 884.2 | 1314.9 | 1512.9 | 1261 | 1325.7 | 1405.6 | 873.1 | 1347.8 | 1370.5 | 1336 | 1341 | 1322.1 | 1326.5 | 1050.3 | 1083 | 1059.8 | 1072.1 | 1059.2 | 1098.6 | 1080.1 | 1069.1 | 827.7 | 831.1 | 824.5 | 830.8 | 842.4 | 836 | 1223.1 | 1377.8 | 992.2 | 1215.5 | 1392 | 1322 | 1180 | 1301 | 1418.4 | 1433.6 | 1421 | 1471 | 923 | 708 | 868 | 860 | 975 | 895 | 1000.3 | 1010 | 1098.6 | 1134.4 | 1090.6 | 1156.4 | 444.2 | 96.6 | 823.9 | 504.2 | 114.4 | 92.5 | 564.5 | 967.4 | 1.7674 | 1.5297 | 1.3655 | 1.5169 | 0.17 | 0.23726 | 0.25272 | 0.24676 | 26.6699 | 25.824 | 34.3366 | 31.129 | 85.9914 | 87.8148 | 0.070073 | 0.14891 | 1.0231 | 1.0938 | 3.372 | 3.588 | 1.6486 | 1.4412 | 0.20363 | 0.24974 | 26.247 | 32.7328 | 86.9031 | 0.10949 | 1.0584 | 3.48 | 29863.9 | 1658.8 | 4265.2 | 8142.3 | 4307 | 17905.7 | 3880.3 | 4480 | 74503.2 | 44309.2 | 224.1 | 38680.9 | 236.2 | 45558.9 | 432.1 | 10455.6 | 53.9 | 3064.5 | 13.6 | 104.91 | 145915772 | 1027600.64 | 1234 | 140133 | 202312.9 | 1986.8 | 15600 | 400 | 14000 | 400 | 18400 | 1500 | 3800 | 400 | 19400 | 900 | 200 | 74924 | 4002.368 | 2880 | 53280 | 74664 | 4608 | 78926.368 | 70921.632 | 70056 | 5.937% | 11.8667 | 125.2 | 132 KV Line Manual Trip Due To The GSS End Side PT&CT Oil Lealage Attend Work At 11:16AM To 19:51PM
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 6:31 | 18:45 | 4045.4 | 4035.8 | 3766.2 | 3837 | 3960.9 | 4061.7 | 3943.6 | 4348.4 | 4010.8 | 3928.2 | 4048.2 | 4061.7 | 4232.5 | 4063.5 | 4139.7 | 3941.9 | 5589 | 6365.5 | 5424 | 5674.3 | 6143 | 3676.6 | 5649.8 | 5775.8 | 5593.7 | 5601.6 | 5581 | 5608.9 | 4653.7 | 4826.1 | 4763.9 | 4827.8 | 4725.1 | 4901.1 | 4792.7 | 4478.5 | 3804.5 | 3815.5 | 3802.3 | 3838 | 3881.4 | 3846.3 | 5421.6 | 6097 | 4396.5 | 5363.5 | 5711.3 | 5392.9 | 4816.7 | 5333.3 | 5842 | 5943.4 | 5898.2 | 6102 | 3954.7 | 3056.3 | 3739.1 | 3710.2 | 3989.9 | 3863.2 | 4297.8 | 4330 | 4701.8 | 4867 | 4657 | 4941.5 | 2047.1 | 517.5 | 3619.8 | 2265.1 | 606.5 | 503.8 | 2535.2 | 4229.2 | 3.2844 | 2.8657 | 2.5582 | 2.8767 | 0.31596 | 0.43691 | 0.4713 | 0.45446 | 27.6237 | 26.7907 | 37.0188 | 34.452 | 85.641 | 86.7311 | 0.49392 | 0.070516 | 0.98478 | 1.0381 | 2.979 | 3.24 | 3.0751 | 2.7174 | 0.37644 | 0.46288 | 27.2072 | 35.7354 | 86.186 | 0.28222 | 1.0114 | 3.1095 | 131108.7 | 7620 | 19071.5 | 36646.6 | 18897.4 | 75824.3 | 16480.9 | 19167.3 | 324816.7 | 44375.5 | 224.3 | 38742.5 | 236.5 | 45640.9 | 433.1 | 10472.2 | 54.1 | 3145.8 | 14.1 | 105.13 | 146239373 | 1029907.712 | 1237 | 140456 | 202760.9 | 1990.6 | 66300 | 200 | 61600 | 300 | 82000 | 1000 | 16600 | 300 | 81300 | 500 | 220 | 323601 | 2307.072 | 2160 | 232560 | 322560 | 2736 | 325908.072 | 321293.928 | 319824 | 0.336% | 12.2333 | 126.3 | Fully Cloudy Weather & Heavy rain
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 6:28 | 18:29 | 2018.4 | 2017.1 | 1873.8 | 1879 | 1950.3 | 2011.9 | 1940.5 | 2176.5 | 1981.1 | 1927 | 1978.1 | 1991.1 | 2086.8 | 1985.3 | 2044.2 | 1954.2 | 2832.7 | 3226.5 | 2776.3 | 2911 | 2925.6 | 1810.5 | 2816.8 | 2890.9 | 2812.4 | 2821.8 | 2825.4 | 2817.5 | 2322.8 | 2410.6 | 2375.1 | 2417.4 | 2367.8 | 2464.5 | 2418.5 | 2278.2 | 1862.4 | 1879.6 | 1838.1 | 1860.2 | 1889.7 | 1885.1 | 2745.6 | 3118.7 | 2261.5 | 2788.3 | 2780.7 | 2661.2 | 2380.6 | 2607.8 | 2849.1 | 2874.1 | 2837 | 2932.8 | 1798.7 | 1365 | 1670.2 | 1624 | 1896.2 | 1727.9 | 1934.5 | 1964.5 | 2103.6 | 2188.4 | 2119.8 | 2227 | 143.4 | 0 | 686 | 411.4 | 187.6 | 145.1 | 1030.9 | 1805.6 | 1.6409 | 1.407 | 1.2418 | 1.4014 | 0.23494 | 0.18796 | 0.21084 | 0.19321 | 26.3781 | 24.8889 | 32.5365 | 30.0008 | 97.9835 | 96.5447 | 0.97646 | 0.93556 | 1.0142 | 1.14 | 2.682 | 3.354 | 1.5239 | 1.3216 | 0.21145 | 0.20202 | 25.6335 | 31.2687 | 97.2641 | 0.95601 | 1.0771 | 3.018 | 65282.7 | 3742 | 9525.9 | 18387.2 | 9529 | 32791.2 | 7523.1 | 8638.8 | 155419.9 | 44408.8 | 224.8 | 38773.9 | 236.9 | 45682.3 | 434.6 | 10477 | 54.3 | 3184.7 | 14.9 | 105.38 | 146396053 | 1033591.168 | 1241 | 140612 | 202977.9 | 1996.5 | 33300 | 500 | 31400 | 400 | 41400 | 1500 | 4800 | 300 | 38900 | 800 | 250 | 156680 | 3683.456 | 2880 | 112320 | 156240 | 4248 | 160363.456 | 152996.544 | 151992 | 3.181% | 12.0167 | 126.3 | ICR 14 INV 01 Unit 02 SCB Shifted to Unit 01 no anyone scb connected in unit 2 reading is zero & Fully Cloudy Weather & Heavy rain
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 6:21 | 18:36 | 6292.2 | 6273 | 5854.4 | 5839 | 6022.5 | 6196.5 | 6041.2 | 6677.6 | 6290.6 | 6031.9 | 6210.6 | 6252.8 | 6614.6 | 6286.3 | 6416.9 | 6172.9 | 8543.4 | 9590.6 | 8408 | 8794.5 | 9406.9 | 5708.1 | 8635.9 | 8986.2 | 8667.5 | 8614 | 8715.3 | 8701.2 | 7142.5 | 7432 | 7280 | 7343.5 | 7296.4 | 7552.6 | 7432.5 | 7091 | 5919.8 | 5966.9 | 5862.6 | 5862.1 | 5990.8 | 5975.6 | 8367.5 | 9450.6 | 6950.2 | 8416.5 | 7812.4 | 7526.4 | 7293.6 | 8017.3 | 8763.8 | 8855.6 | 8823.6 | 9082.8 | 5979.9 | 4634.5 | 5595.5 | 5504 | 6248 | 5839.9 | 6416.2 | 6435 | 7001.8 | 7085 | 7009.3 | 7382.5 | 3927.2 | 662.2 | 5102.6 | 3746.4 | 908 | 768.8 | 3536.8 | 5749.8 | 5.0552 | 4.6347 | 4.0644 | 4.7614 | 0.45745 | 0.66513 | 0.72989 | 0.66842 | 27.8652 | 27.6827 | 40.4587 | 37.9655 | 81.9125 | 81.9625 | 0.017012 | 0.024315 | 1.1851 | 1.2166 | 3.063 | 3.39 | 4.845 | 4.4129 | 0.56129 | 0.69915 | 27.7739 | 39.2121 | 81.9375 | 0.020664 | 1.2009 | 3.2265 | 202244.6 | 11886.7 | 29198 | 56875.9 | 29372.5 | 112291.2 | 24939.1 | 28478.6 | 495286.6 | 44510.9 | 225.1 | 38868 | 237.2 | 45808.5 | 435.8 | 10501.2 | 54.5 | 3305 | 15.5 | 105.62 | 146885623 | 1036561.536 | 1245 | 141099 | 203655.3 | 2001.4 | 102100 | 300 | 94100 | 300 | 126200 | 1200 | 24200 | 400 | 120300 | 600 | 240 | 489570 | 2970.368 | 2880 | 350640 | 487728 | 3528 | 492540.368 | 486599.632 | 484200 | -0.5545% | 12.25 | 126.3 | Fully Cloudly Weather
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 6:11 | 18:00 | 5832 | 5862.6 | 5501.9 | 5414 | 5581.7 | 5780.5 | 5642.9 | 6202.6 | 5725.4 | 5577.3 | 5775.2 | 5848.8 | 6078.5 | 5806 | 5935.7 | 5705.8 | 8131 | 8968 | 7832.5 | 8202.8 | 8737.7 | 5407.7 | 8065.9 | 8214.2 | 8140 | 8188.4 | 8023.8 | 7994.2 | 6548.2 | 6729.8 | 6550.8 | 6648.2 | 6541.3 | 6692.3 | 6631 | 6310.9 | 5206.8 | 5249.7 | 5171.6 | 5229.8 | 5295.6 | 5250 | 7537.4 | 8402.4 | 6219.6 | 7491.9 | 7467.3 | 7192.2 | 7105.1 | 7790.7 | 8458.2 | 8485.4 | 8265.7 | 8605.2 | 5709 | 4594.5 | 5321.3 | 5235.3 | 5789.1 | 5451.8 | 5892.7 | 6019.6 | 6437 | 6607 | 6424.9 | 6750.9 | 4155.6 | 1365.3 | 4626.1 | 3766.2 | 766 | 175.6 | 5183.1 | 5627.6 | 4.8369 | 4.113 | 3.9197 | 4.2744 | 0.54351 | 0.51695 | 0.72768 | 0.58868 | 27.5984 | 27.8736 | 39.3322 | 36.5288 | 75.8452 | 73.9265 | 0.056337 | 0 | 1.2848 | 1.4182 | 3.168 | 3.66 | 4.475 | 4.097 | 0.53023 | 0.65818 | 27.736 | 37.9305 | 74.8859 | 0.056337 | 1.3515 | 3.414 | 188177.1 | 10456.5 | 26477 | 50598.3 | 26175.5 | 109895.4 | 23153.2 | 26219.8 | 461152.8 | 44606.3 | 225.5 | 38955.5 | 237.5 | 45921.4 | 437 | 10526.8 | 54.7 | 3417.3 | 16.2 | 105.86 | 147342163 | 1039590.848 | 1248 | 141554 | 204287.2 | 2006.2 | 95400 | 400 | 87500 | 300 | 112900 | 1200 | 25600 | 300 | 112300 | 700 | 240 | 456540 | 3029.312 | 2160 | 327600 | 454968 | 3456 | 459569.312 | 453510.688 | 451512 | -0.3434% | 11.8167 | 126.3 | Fully Cloudly Weather
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 6:21 | 18:19 | 3456.7 | 3432 | 3198.2 | 3264 | 3387.6 | 3482.8 | 3356.9 | 3720.9 | 3417.5 | 3348.2 | 3428.8 | 3450.3 | 3580.9 | 3406.8 | 3517.1 | 3345.8 | 4747.6 | 5386.7 | 4632.2 | 4847.4 | 5222 | 3132.2 | 4767.4 | 4961 | 4782.7 | 4778.5 | 4806.3 | 4825.7 | 4282.7 | 4447.3 | 4382.8 | 4429.3 | 4393.7 | 4562.5 | 4476.1 | 4236.8 | 3554.3 | 3577.8 | 3507.4 | 3498.2 | 3592.7 | 3583.6 | 5076.8 | 5785 | 4213.3 | 5155.3 | 4746.6 | 4517.9 | 4035.9 | 4409.8 | 4860.7 | 4908.6 | 4855.2 | 5000.4 | 3183.8 | 2524.8 | 3064.2 | 3029 | 3392 | 3219.7 | 3515.1 | 3498.8 | 3672 | 3796 | 3710.9 | 3893 | 2629.1 | 2102.3 | 2718.2 | 2445.9 | 621.2 | 278.7 | 3017.7 | 3258.1 | 2.6947 | 2.6366 | 2.1412 | 2.6874 | 0.26965 | 0.37901 | 0.4025 | 0.37876 | 26.2064 | 26.2126 | 34.8994 | 32.6045 | 83.4871 | 83.2896 | 0.098522 | 0.068966 | 1.5754 | 1.706 | 4.935 | 4.884 | 2.6657 | 2.4143 | 0.32433 | 0.39063 | 26.2095 | 33.7519 | 83.3884 | 0.083744 | 1.6407 | 4.9095 | 111684.2 | 7132.1 | 17542.1 | 34412.3 | 17669.1 | 66208.1 | 13625.6 | 15071.9 | 283345.4 | 44662.9 | 225.8 | 39008.4 | 237.8 | 45998.1 | 438.3 | 10544.2 | 54.9 | 3483.4 | 16.9 | 106.08 | 147625132 | 1042627.072 | 1252 | 141836 | 204679 | 2011.1 | 56600 | 300 | 52900 | 300 | 76700 | 1300 | 17400 | 400 | 66100 | 700 | 220 | 282969 | 3036.224 | 2880 | 203040 | 282096 | 3528 | 286005.224 | 279932.776 | 278568 | 0.9387% | 11.9667 | 126.3 | Fully Cloudly Weather
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 6:28 | 18:47 | 4080.6 | 4076.2 | 3786.3 | 3796.1 | 3922 | 4044.7 | 3928.5 | 4380.4 | 4009.3 | 3895.3 | 3994 | 4043.9 | 4199.2 | 3967.9 | 4118.7 | 3956.7 | 5592 | 6331.8 | 5450.7 | 5715.1 | 6045 | 3604.7 | 5476 | 5651.3 | 5535.5 | 5580.2 | 5516.3 | 5522.2 | 4425.8 | 4588 | 4496.1 | 4565.5 | 4498.1 | 4649.9 | 4580.3 | 4327.3 | 3611.4 | 3634.2 | 3571 | 3583.5 | 3657.6 | 3645.1 | 5179.6 | 5860.1 | 4229.6 | 5181.8 | 5650.1 | 5401.9 | 4897.4 | 5005.5 | 5902.7 | 5979.5 | 5882.6 | 6046.2 | 3890.2 | 3089.6 | 3751.5 | 4251 | 4144.3 | 3982.9 | 4370.7 | 4271.6 | 4492 | 4622.2 | 4539 | 4741.8 | 3923.2 | 2688.8 | 3401.9 | 3709.5 | 840.7 | 387.5 | 3736.1 | 4018.9 | 3.2022 | 2.7194 | 2.5281 | 2.702 | 0.31492 | 0.36577 | 0.47702 | 0.38635 | 27.1013 | 26.9953 | 36.6212 | 33.7002 | 80.0339 | 81.1125 | 0 | 0.0097087 | 1.2312 | 1.2147 | 3.303 | 3.414 | 2.9608 | 2.615 | 0.34034 | 0.43169 | 27.0483 | 35.1607 | 80.5732 | 0.0097087 | 1.2229 | 3.3585 | 130220.6 | 7245.6 | 18075.4 | 34908.3 | 18055.6 | 82454.8 | 16769.5 | 18395 | 326124.8 | 44728.7 | 226.2 | 39070.1 | 238.1 | 46076.3 | 439.6 | 10567 | 55.2 | 3563.2 | 17.6 | 106.33 | 147949748 | 1045947.328 | 1256 | 142159 | 205128.4 | 2016.4 | 65800 | 400 | 61700 | 300 | 78200 | 1300 | 22800 | 300 | 79800 | 700 | 250 | 324616 | 3320.256 | 2880 | 232560 | 323568 | 3816 | 327936.256 | 321295.744 | 319752 | 0.5554% | 12.3167 | 128.08 | ICR-10 INV-2 Unit2 internal fault at 12:26 to 13:20 Fully Cloudly Weathere
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | 6:23 | 18:40 | 4764.1 | 4732.4 | 4422.3 | 4440.8 | 4585.5 | 4746.5 | 4607 | 5107.1 | 4700.7 | 4554.4 | 4664 | 4726.2 | 4897.4 | 4622.7 | 4801.4 | 4618.7 | 6475.1 | 7281.6 | 6328.7 | 6629.5 | 6941.5 | 4164.8 | 6286.2 | 6536.6 | 6380.7 | 6417 | 6375.7 | 6387.7 | 5257.1 | 5442.8 | 5333.5 | 5402 | 5358.2 | 5542.7 | 5463.6 | 5176.5 | 4331.7 | 4348.1 | 4268 | 4293.2 | 4368.7 | 4352.1 | 6190.4 | 7013.4 | 5071.5 | 6192.2 | 6428.6 | 6137.1 | 5570.4 | 5615.8 | 6700.3 | 6793.6 | 6661.7 | 6877.7 | 4455 | 3548 | 4288.9 | 4070.2 | 4700.4 | 4472.6 | 4918 | 4842.8 | 4919.6 | 5188.5 | 5082.7 | 5496.8 | 4349.7 | 3033.3 | 3750.6 | 4081 | 1349.6 | 437.7 | 4191.9 | 4551.5 | 3.7689 | 3.2619 | 2.9759 | 3.2627 | 0.41227 | 0.45755 | 0.57782 | 0.4743 | 26.903 | 27.2183 | 37.3407 | 34.7719 | 80.651 | 79.4052 | 0.010256 | 0 | 1.6913 | 1.8991 | 4.098 | 5.085 | 3.5154 | 3.1193 | 0.43491 | 0.52606 | 27.0607 | 36.0563 | 80.0281 | 0.010256 | 1.7952 | 4.5915 | 151196.3 | 8679.8 | 21435.4 | 41749.5 | 21541 | 92892.6 | 18933.8 | 20687.6 | 377116 | 44804.5 | 226.6 | 39141.8 | 238.5 | 46169.4 | 440.9 | 10592.8 | 55.4 | 3653.2 | 18.3 | 106.57 | 148324630 | 1049154.752 | 1259 | 142533 | 205647.4 | 2021.6 | 75800 | 400 | 71700 | 400 | 93100 | 1300 | 25800 | 300 | 90000 | 700 | 240 | 374882 | 3207.424 | 2160 | 269280 | 373680 | 3744 | 378089.424 | 371674.576 | 369936 | 0.2581% | 12.2833 | 128.08 | ICR-10 INV-2 Unit2 internal fault at 8:54 to 9:49 Fully Cloudly Weathere
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | 6:15 | 19:02 | 5489.5 | 5494.8 | 5116.8 | 5102 | 5292.2 | 5446.9 | 5286.9 | 5876.1 | 5376 | 5245.6 | 5378.5 | 5467.3 | 5638.8 | 5352.4 | 5537.1 | 5328.6 | 7534.6 | 8477.1 | 7305.2 | 7660.6 | 8160 | 4931.4 | 7515.3 | 7734 | 7474.2 | 7532.3 | 7447.3 | 7503.9 | 6369.2 | 6522 | 6351.6 | 6410.3 | 5785.5 | 5900 | 5887.3 | 4407.3 | 5215.1 | 5244.8 | 3874 | 3902.6 | 3940.3 | 3938.7 | 7438.7 | 8307.3 | 6007.7 | 7329.1 | 7469 | 7091.7 | 6517.6 | 6989.7 | 8045 | 8216 | 8030.5 | 8336.3 | 5553.8 | 4454.4 | 5416 | 5371.5 | 5849.5 | 5657 | 6187.7 | 6065.5 | 6223.2 | 6573.9 | 6449.7 | 6915.5 | 5476.9 | 4172.6 | 4796.4 | 5386.8 | 2334.5 | 713 | 5296.5 | 5737.5 | 4.4195 | 3.9925 | 3.5276 | 4.0645 | 0.53824 | 0.54319 | 0.69194 | 0.59434 | 26.9393 | 27.041 | 37.5633 | 34.9496 | 82.4408 | 81.9139 | 0.10909 | 0.10909 | 1.5998 | 1.7768 | 3.783 | 3.882 | 4.206 | 3.796 | 0.54071 | 0.64314 | 26.9902 | 36.2565 | 82.1774 | 0.10909 | 1.6883 | 3.8325 | 175705.4 | 10459.9 | 25653.1 | 44738.4 | 21980.1 | 115405.7 | 23759.7 | 26162.3 | 443864.6 | 44893.4 | 227 | 39224.1 | 238.8 | 46271.7 | 442.2 | 10626.4 | 55.6 | 3763.6 | 18.8 | 106.82 | 148764606 | 1052034.368 | 1263 | 142971 | 206256.7 | 2026.3 | 88900 | 400 | 82300 | 300 | 102300 | 1300 | 33600 | 300 | 110400 | 500 | 250 | 439976 | 2879.616 | 2880 | 315360 | 438696 | 3384 | 442855.616 | 437096.384 | 435312 | -0.2273% | 12.7833 | 128.08 | ICR 06 & 08 Emergency Shutdown Due to Local Issue From 09:47 to 11:18 Fully Cloudly Weathere
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | 6:01 | 18:36 | 5427.4 | 5441.5 | 5060.9 | 5030 | 5215.7 | 5372.4 | 5219 | 5751.5 | 5363 | 5210.4 | 5365.6 | 5455.2 | 5613.7 | 5383.9 | 5537.6 | 5322 | 7521.7 | 8502.5 | 7297.4 | 7663.6 | 8376.5 | 5074.4 | 7754.4 | 7916.7 | 7628.2 | 7646.4 | 7609.3 | 7651.2 | 6712 | 6901 | 6736.1 | 6781.3 | 6802.8 | 6997.9 | 6939.9 | 6819.2 | 5462.1 | 5518.1 | 5474.7 | 5460.9 | 5522.3 | 5486.7 | 7864.9 | 8866.2 | 6484.2 | 7844 | 7598.6 | 7283.7 | 6796.8 | 6480.4 | 8083.6 | 8219.4 | 8099.5 | 8359.4 | 5464.9 | 4369.4 | 5294.4 | 5250.4 | 5779.7 | 5562.6 | 6074.5 | 5960.1 | 6098.2 | 6519 | 6307 | 6786.4 | 5531.1 | 5133.4 | 4834.1 | 5445.4 | 2460.3 | 722.7 | 5257.1 | 5658.3 | 4.2929 | 4.1967 | 3.3767 | 4.2045 | 0.46469 | 0.56214 | 0.66393 | 0.60837 | 27.519 | 26.4301 | 38.1882 | 35.4196 | 88.1881 | 88.8467 | 0.010256 | 0.010256 | 0.99771 | 1.1034 | 3.3 | 3.339 | 4.2448 | 3.7906 | 0.51341 | 0.63615 | 26.9746 | 36.8039 | 88.5174 | 0.010256 | 1.0506 | 3.3195 | 176412.1 | 10980.2 | 27130.4 | 53003.9 | 27559.8 | 116342.9 | 23376.9 | 25710.6 | 460516.8 | 44983.6 | 227.4 | 39305.8 | 239.1 | 46389.4 | 443.5 | 10661.1 | 55.8 | 3872.9 | 19.4 | 107.05 | 149220737 | 1055073.856 | 1266 | 143425 | 206888.3 | 2031.1 | 90200 | 400 | 81700 | 300 | 117700 | 1300 | 34700 | 300 | 109300 | 600 | 230 | 456131 | 3039.488 | 2160 | 326880 | 454752 | 3456 | 459170.488 | 453091.512 | 451296 | -0.2923% | 12.5833 | 128.08 | Fully Cloudly Weather
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | 6:11 | 18:33 | 4533.8 | 4495 | 4188.7 | 4260.2 | 4436.3 | 4567.2 | 4407.2 | 4882 | 4464.8 | 4382.3 | 4469.8 | 4523 | 4638.6 | 4436.3 | 4589.9 | 4378.9 | 6177.9 | 7001.1 | 6008.3 | 6289.2 | 6733.6 | 4080.5 | 6250.6 | 6399.6 | 6193.8 | 6218 | 6189.1 | 6231.5 | 5234.3 | 5421.8 | 5328.5 | 5373.1 | 5334.4 | 5524.9 | 5443 | 5363 | 4300.5 | 4326.8 | 4352.8 | 4313.6 | 4414.1 | 4335 | 6152.5 | 6977.5 | 5027.9 | 6142.8 | 6296.4 | 6022.9 | 5358.8 | 4255.3 | 6495.8 | 6556.8 | 6416 | 6602 | 4242 | 3373 | 4070.3 | 4032 | 4505.2 | 4255.9 | 4726.7 | 4645.7 | 4668.8 | 5024.6 | 4880.5 | 5236.3 | 3893.8 | 3919.2 | 3654.3 | 4156.4 | 1842.9 | 514.9 | 4010 | 4334.1 | 3.5621 | 3.2079 | 2.7947 | 3.1617 | 0.37876 | 0.44182 | 0.54608 | 0.4666 | 27.0938 | 26.9506 | 37.7227 | 34.7933 | 81.8761 | 82.8921 | 0 | 0 | 1.2829 | 1.3028 | 3.207 | 3.255 | 3.385 | 2.9782 | 0.41029 | 0.50634 | 27.0222 | 36.258 | 82.3841 |  | 1.2928 | 3.231 | 145427.2 | 8627.3 | 21357.7 | 41716.2 | 21665.3 | 90046.9 | 18133.5 | 19810.2 | 366784.3 | 45057 | 227.6 | 39374.4 | 239.4 | 46482.3 | 444.7 | 10687.5 | 56 | 3957.7 | 20 | 107.28 | 149585362 | 1058098.88 | 1270 | 143788 | 207393.3 | 2036.1 | 73400 | 200 | 68600 | 300 | 92900 | 1200 | 26400 | 400 | 84800 | 600 | 230 | 364625 | 3025.024 | 2880 | 261360 | 363600 | 3600 | 367650.024 | 361599.976 | 360000 | 0.236% | 12.3667 | 128.08 | ICR 10 Inv 02 Unit 02 Breakdown due to the soft strat fault at 10:56 AM to 12:46 PM Fully Cloudly Weathere
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | 6:07 | 18:34 | 4028.3 | 4039.9 | 3756.2 | 3699.1 | 3824.1 | 3968.7 | 3874.4 | 4242.5 | 3974 | 3842.2 | 3933.2 | 4014.3 | 4127.1 | 3928.6 | 4081.6 | 3940.2 | 5103.1 | 5767 | 4976.2 | 5221.9 | 6028.1 | 3631.9 | 5563.1 | 5648.3 | 3587 | 3588 | 5509.6 | 5523.9 | 4559.3 | 4708.9 | 4645.3 | 4681 | 4682.4 | 4864.9 | 4793.8 | 4744.8 | 3780.8 | 3806.8 | 3807.3 | 3764 | 3859.9 | 3804.7 | 5446.2 | 6226.6 | 4512.2 | 5498 | 5431.3 | 5230.9 | 2216.1 | 16 | 5805.2 | 5781.5 | 5793.2 | 5970.3 | 3878.1 | 3091.9 | 3744.3 | 3715.4 | 4074 | 3922.6 | 4280.4 | 4204.1 | 4313.3 | 4653.4 | 4530 | 4815 | 3815.9 | 3522.8 | 3248.7 | 3711.1 | 1651.5 | 473.2 | 3634 | 3936.8 | 3.2483 | 2.9169 | 2.5365 | 2.9056 | 0.35943 | 0.40039 | 0.48949 | 0.42565 | 26.7953 | 26.0391 | 36.1674 | 33.5407 | 90.0422 | 89.6617 | 0.65601 | 0.68363 | 0.94824 | 1.015 | 3.99 | 4.671 | 3.0826 | 2.7211 | 0.37991 | 0.45757 | 26.4172 | 34.8541 | 89.852 | 0.66982 | 0.98163 | 4.3305 | 123422.5 | 7587.6 | 18594.5 | 36918.9 | 19085.9 | 74668.2 | 16481.1 | 18311.7 | 315070.4 | 45117 | 228 | 39435 | 239.8 | 46563.9 | 446.1 | 10711.4 | 56.1 | 4028.7 | 20.4 | 107.53 | 149898346 | 1061085.376 | 1274 | 144100 | 207826.6 | 2040.9 | 60000 | 400 | 60600 | 400 | 81600 | 1400 | 23900 | 300 | 71000 | 400 | 250 | 312984 | 2986.496 | 2880 | 224640 | 311976 | 3456 | 315970.496 | 309997.504 | 308520 | 0.2857% | 12.45 | 128.08 | ICR 10 INV 02 Unit 02 Breakdown due to the DC Injection pro Fault at 06:07 to Continue. Fully Cloudly Weathere & rain
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | 6:14 | 18:51 | 3791.9 | 3770 | 3530.3 | 3577.4 | 3733 | 3844.4 | 3692.9 | 4065.6 | 3719.7 | 3672.8 | 3732.6 | 3767.8 | 3864.7 | 3692.6 | 3843 | 3675.3 | 5205.7 | 5851.8 | 5077.5 | 5300.9 | 5606.6 | 3397.7 | 5212.3 | 5352.7 | 5133 | 5164 | 5166 | 5206.4 | 4434.2 | 4574.8 | 4497.1 | 4554.1 | 4511.8 | 4664.5 | 4585.1 | 4541.8 | 3610 | 3637.3 | 3654.3 | 3638.3 | 3720.7 | 3658.6 | 5187.4 | 5825.4 | 4200.3 | 5133.7 | 4369.5 | 4215.1 | 2622.1 | 35.2 | 5354.1 | 5404.3 | 5281.1 | 5463.9 | 3510.7 | 2786.7 | 3356.3 | 3336.3 | 3668.1 | 3511.1 | 3863.5 | 3790.9 | 3929 | 4202 | 3779 | 4348 | 3550.8 | 3253.5 | 3044.4 | 3449 | 1520.5 | 416.3 | 3337.2 | 3628.7 | 3.0487 | 2.7096 | 2.3902 | 2.7176 | 0.38685 | 0.35228 | 0.44735 | 0.37498 | 26.1944 | 25.6546 | 35.2149 | 32.2378 | 91.3226 | 90.8981 | 0.4037 | 0.29268 | 1.1694 | 1.2872 | 3.726 | 3.492 | 2.8792 | 2.5539 | 0.36957 | 0.41116 | 25.9245 | 33.7263 | 91.1104 | 0.34819 | 1.2283 | 3.609 | 121648.6 | 7247.3 | 18060.2 | 35018.7 | 18303.2 | 67935.7 | 14833.6 | 16258 | 299305.3 | 45178.3 | 228.1 | 39492.6 | 240.1 | 46642.1 | 447.4 | 10733.7 | 56.4 | 4092.2 | 21.1 | 107.76 | 150196191 | 1064151.616 | 1277 | 144397 | 208239 | 2045.9 | 61300 | 100 | 57600 | 300 | 78200 | 1300 | 22300 | 300 | 63500 | 700 | 230 | 297845 | 3066.24 | 2160 | 213840 | 296928 | 3600 | 300911.24 | 294778.76 | 293328 | 0.5366% | 12.6167 | 128.08 | ICR 10 INV 02 Unit 02 Breakdown due to the DC Injection pro Fault at 06:30 to Continue. Fully Cloudly Weathere & rain
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | 6:17 | 18:25 | 2482.2 | 2469.8 | 2297.1 | 2299.3 | 2391.8 | 2476.3 | 2389.3 | 2663.7 | 2444.1 | 2387 | 2426.8 | 2467 | 2527.5 | 2416.7 | 2511.5 | 2410.4 | 3466.8 | 3946.3 | 3386 | 3547.9 | 3753.5 | 2253 | 3465.2 | 3542 | 3431.8 | 3470 | 3450.5 | 3463.6 | 2805.2 | 2906.6 | 2862.5 | 2894.6 | 2864 | 2970.1 | 2870 | 2623.5 | 2249.3 | 2266.7 | 2280.3 | 2267.2 | 2314.8 | 2279.7 | 3284.5 | 3722.3 | 2689.4 | 3313.1 | 2103.2 | 2042.7 | 3009.9 | 2649.8 | 3579.8 | 3626.5 | 3564.6 | 3680.2 | 2303 | 1809.6 | 2211.2 | 2189 | 2422 | 2314.2 | 2554.1 | 2509.7 | 2666.7 | 2795.3 | 2626.5 | 2891.5 | 2280.3 | 2097.1 | 1930.9 | 2216.3 | 936.1 | 216.4 | 2152.6 | 2361.8 | 1.9084 | 1.6489 | 1.49 | 1.6391 | 0.21211 | 0.22248 | 0.27281 | 0.22528 | 25.3681 | 24.8212 | 32.5475 | 29.8489 | 95.5333 | 93.5381 | 0.44783 | 0.42894 | 1.1848 | 1.3317 | 2.886 | 3.528 | 1.7787 | 1.5646 | 0.2173 | 0.24905 | 25.0946 | 31.1982 | 94.5357 | 0.43838 | 1.2582 | 3.207 | 80237.1 | 4516 | 11468.9 | 22151.3 | 11327.6 | 46961 | 9800 | 10980 | 197441.9 | 45219.2 | 228.5 | 39530.9 | 240.4 | 46691.6 | 448.6 | 10748.3 | 56.6 | 4136.7 | 21.7 | 107.99 | 150394454 | 1067231.744 | 1281 | 144594 | 208513.4 | 2050.8 | 40900 | 400 | 38300 | 300 | 49500 | 1200 | 14600 | 300 | 44500 | 600 | 230 | 198263 | 3080.128 | 2880 | 141840 | 197568 | 3528 | 201343.128 | 195182.872 | 194040 | 1.976% | 12.1333 | 128.08 | ICR 06 INV 02 Unit 01 & 02 Brakdown due to the GFDI Fault at 15:53 to 16:46 Fully Cloudly Weathere & Heavy Rain.
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | 6:26 | 18:29 | 2806.5 | 2795.5 | 2593.8 | 2584.9 | 2690.2 | 2791.3 | 2696.7 | 3013.7 | 2755.2 | 2679.8 | 2716.1 | 2766.4 | 2831.8 | 2699 | 2819.9 | 2719.2 | 3864.7 | 4389.2 | 3792.9 | 3976 | 4136.5 | 2492.2 | 3837.3 | 3922.7 | 3798.4 | 3846 | 3824.5 | 3836.9 | 3076.5 | 3195 | 3162.2 | 3199.2 | 3156.4 | 3279.2 | 3217.5 | 3028.2 | 2500.6 | 2519.3 | 2532.8 | 2515.5 | 2569.8 | 2532.5 | 3631.4 | 4127.5 | 2884.7 | 3666.9 | 4041.2 | 3732.6 | 2495.6 | 3537.4 | 4112.6 | 4211.5 | 4064.4 | 4260.4 | 2687.3 | 2127.5 | 2585.8 | 2558 | 2859 | 2733.2 | 3010.9 | 2950 | 3134 | 3237 | 3041.7 | 3382 | 2698.3 | 2489.2 | 2326.4 | 2647.8 | 1141.7 | 282.6 | 2536.9 | 2769.5 | 2.0883 | 1.7767 | 1.6186 | 1.7621 | 0.22724 | 0.23896 | 0.28744 | 0.22784 | 25.3219 | 24.9973 | 32.7112 | 29.7383 | 93.2331 | 92.9541 | 0.12683 | 0.13383 | 0.89792 | 0.96525 | 1.77 | 2.19 | 1.9325 | 1.6904 | 0.2331 | 0.25764 | 25.1596 | 31.2248 | 93.0936 | 0.13033 | 0.93158 | 1.98 | 89677.3 | 5019.9 | 12632.9 | 24461.1 | 12681.3 | 57306.7 | 11553.1 | 12794.7 | 226127 | 45264.6 | 228.9 | 39573.6 | 240.7 | 46746.4 | 449.9 | 10765.5 | 56.9 | 4190.3 | 22.3 | 108.2 | 150620979 | 1070458.112 | 1284 | 144819 | 208827 | 2056 | 45400 | 400 | 42700 | 300 | 54800 | 1300 | 17200 | 400 | 53600 | 600 | 210 | 226525 | 3226.368 | 2160 | 162000 | 225792 | 3744 | 229751.368 | 223298.632 | 222048 | 1.603% | 12.05 | 128.08 | ICR 10 INV 02 Unit 01 Brakdown due to the GFDI pro Fault at 13:42 to 15:55 Fully Cloudly Weathere & Heavy Rain.
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | 7:03 | 18:48 | 3048.1 | 3040.8 | 2822.9 | 2817.6 | 2933.7 | 3036.4 | 2903.1 | 3270.8 | 2999.7 | 2932.1 | 2975 | 3028.9 | 3085.1 | 2963.2 | 3080.7 | 2962.6 | 4214.8 | 4801.7 | 4121.8 | 4319.5 | 4574 | 2758.1 | 4245.2 | 4347.7 | 4197.7 | 4228 | 4221.8 | 4243 | 3459.5 | 3589.4 | 3548.5 | 3585.6 | 3549.2 | 3688.8 | 3615 | 3473.2 | 2828.9 | 2850.7 | 2863.8 | 2840.5 | 2904.3 | 2864.4 | 4085.6 | 4649.5 | 3367.7 | 4140.8 | 4274.2 | 3857.4 | 3618.3 | 4002.6 | 4326 | 4425.9 | 4356.2 | 4486.1 | 2843.9 | 2248.5 | 2741.7 | 2711 | 3005.4 | 2871.5 | 3167.4 | 3107.6 | 3291 | 3416.7 | 3195 | 3546 | 2833.1 | 2615.1 | 2421.9 | 2777.5 | 1195.8 | 302.2 | 2671.7 | 2918.4 | 2.2717 | 2.002 | 1.767 | 2.0094 | 0.27289 | 0.26282 | 0.30951 | 0.26148 | 25.5359 | 24.8048 | 32.8589 | 29.9884 | 96.141 | 95.678 | 0.21951 | 0.16718 | 0.86263 | 0.96898 | 2.04 | 2.634 | 2.1368 | 1.8882 | 0.26785 | 0.2855 | 25.1703 | 31.4236 | 95.9095 | 0.19334 | 0.91581 | 2.337 | 98174 | 5679.6 | 14183 | 27716.6 | 14326.2 | 61627.5 | 12151.9 | 13448.7 | 247307.5 | 45314.6 | 229.3 | 39620.2 | 241.1 | 46808.3 | 451.2 | 10783.6 | 57.1 | 4247.2 | 23 | 108.42 | 150868393 | 1073537.6 | 1288 | 145066 | 209169.5 | 2061 | 50000 | 400 | 46600 | 400 | 61900 | 1300 | 18100 | 300 | 56900 | 700 | 220 | 247414 | 3079.488 | 2880 | 177840 | 246600 | 3600 | 250493.488 | 244334.512 | 243000 | 1.288% | 11.75 | 128.08 | Fully Cloudly Weather & rain
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | 6:48 | 18:38 | 3502.9 | 3493.5 | 3252.8 | 3236.5 | 3376.3 | 3499.1 | 3380.9 | 3771.5 | 3365.1 | 3363.1 | 3405.1 | 3471.7 | 3534.7 | 3394.4 | 3528.8 | 3392.2 | 4805 | 5468.7 | 4690.1 | 4917.6 | 5137.7 | 3125.1 | 4815.8 | 4931.1 | 4806.6 | 4804 | 4790.8 | 4815.2 | 3856.9 | 4013.6 | 3977.4 | 4018.2 | 3968.9 | 4128.4 | 4038.4 | 3694.1 | 3186.3 | 3213.1 | 3224.3 | 3196.2 | 3270.4 | 3226.2 | 4568.3 | 5186.2 | 3749.3 | 4624.6 | 4991 | 4748.6 | 4258.1 | 4683.4 | 5077.6 | 5203 | 5108.9 | 5187.4 | 3349.5 | 2666.3 | 3230.4 | 3140 | 3577.2 | 3420.9 | 3765.3 | 3685.2 | 3887 | 4025 | 3838 | 4197 | 3373.5 | 3113.2 | 2911.7 | 3317.2 | 1455.7 | 390.8 | 3185.4 | 3474.8 | 2.6968 | 2.3522 | 2.1263 | 2.3378 | 0.27639 | 0.31533 | 0.39724 | 0.31341 | 26.2389 | 26.1189 | 35.8092 | 32.7252 | 88.5047 | 88.3396 | 0 | 0 | 0.70856 | 0.81298 | 1.818 | 1.692 | 2.5245 | 2.2321 | 0.29586 | 0.35533 | 26.1789 | 34.2672 | 88.4222 |  | 0.76077 | 1.755 | 112076.3 | 6399.4 | 15866.1 | 31045.5 | 15829.8 | 72866.5 | 14448.6 | 15947 | 284479.2 | 45371.5 | 229.7 | 39673.5 | 241.4 | 46877.4 | 452.6 | 10805 | 57.4 | 4313.3 | 23.7 | 108.72 | 151152410 | 1077154.688 | 1292 | 145349 | 209562.8 | 2066.8 | 56900 | 400 | 53300 | 300 | 69100 | 1400 | 21400 | 300 | 66100 | 700 | 300 | 284017 | 3617.088 | 2880 | 203760 | 283176 | 4176 | 287634.088 | 280399.912 | 279000 | 1.109% | 11.8333 | 128.08 | Fully Cloudly Weather
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | 6:07 | 18:51 | 7864.5 | 7796.7 | 7404.6 | 7398.4 | 7328.4 | 7526.3 | 7476.3 | 8003.1 | 7735.9 | 7588.1 | 7698.9 | 7843.7 | 8080.9 | 7732.6 | 8008.1 | 7782.8 | 10837.1 | 11768.4 | 10554.7 | 10928.1 | 11371.4 | 7059.5 | 10597.4 | 10816.2 | 10707 | 10755 | 10577.2 | 10608.5 | 8838.3 | 9104.2 | 9032 | 9067.2 | 9089.1 | 9420.3 | 9163.5 | 8841.3 | 7332.7 | 7358.5 | 7406 | 7069 | 7462.3 | 7366.5 | 10529.9 | 11629.7 | 8734 | 10474.1 | 8987.5 | 8690.5 | 8996.5 | 9823.4 | 10396.1 | 10467.5 | 10404.4 | 10585.9 | 6952 | 5567 | 6602 | 6566 | 7252.3 | 6977.9 | 7499.8 | 7459.2 | 7745 | 8020 | 7658 | 8387 | 7079.9 | 6527.1 | 6179.8 | 6993.9 | 3179.6 | 962.5 | 6645.9 | 6998.5 | 5.3958 | 5.9109 | 5.4085 | 5.989 | 0.70456 | 0.82126 | 1.0423 | 0.85115 | 27.8887 | 27.8067 | 42.324 | 38.6668 | 81.6875 | 81.8165 | 0 | 0 | 1.0691 | 1.1504 | 3.573 | 2.484 | 5.6533 | 5.6987 | 0.76291 | 0.94672 | 27.8477 | 40.4954 | 81.752 |  | 1.1098 | 3.0285 | 249849.8 | 14691.2 | 36041.7 | 70671.5 | 36514.2 | 148606 | 29189.2 | 31810 | 617373.6 | 45497.2 | 229.8 | 39788.1 | 241.7 | 47033.4 | 453.7 | 10848.8 | 57.6 | 4444.6 | 24.2 | 109.01 | 151760994 | 1079802.24 | 1295 | 145955 | 210405.3 | 2071 | 125700 | 100 | 114600 | 300 | 156000 | 1100 | 43800 | 300 | 131300 | 500 | 290 | 608584 | 2647.552 | 2160 | 436320 | 606600 | 3024 | 611231.552 | 605936.448 | 603576 | -0.9949% | 12.7333 | 128.08 | ICR 01 INV 02 Brakdown due to the GFDI pro Fault at 11:29 to 11:40 Moving Cloudly Weathere
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | 6:07 | 18:48 | 5889 | 5891.1 | 5524.9 | 5560.6 | 5718.8 | 5871.1 | 5708.7 | 6287.5 | 5718.9 | 5719.2 | 5797.1 | 5891.1 | 5989.1 | 5804.9 | 6005.1 | 5783.8 | 8071.2 | 9103.9 | 7869.8 | 8224.9 | 8751.3 | 5529.9 | 8313.5 | 8521 | 8242.5 | 8144 | 8263.1 | 8319.4 | 6992.3 | 7206 | 7178.6 | 7237.3 | 7157.8 | 7417.7 | 7257.3 | 7164.4 | 5773.7 | 5811.6 | 5862.8 | 5571.8 | 5926.5 | 5839.6 | 8141.9 | 9119.6 | 6746 | 8216.3 | 8062 | 7760 | 7324 | 8076 | 8586 | 8786 | 8927 | 9033 | 5972 | 4765 | 5796 | 5747 | 6365 | 6123 | 6672 | 6532 | 6909 | 7163 | 6623 | 7453 | 6160 | 5653 | 5254 | 5848 | 2727 | 808 | 5831 | 6279 | 3.7931 | 4.5068 | 3.8029 | 4.5644 | 0.51342 | 0.65675 | 0.76455 | 0.66159 | 27.7423 | 27.8257 | 39.6734 | 36.948 | 77.9441 | 78.0046 | 0 | 0 | 1.4121 | 1.5403 | 2.991 | 2.961 | 4.15 | 4.1837 | 0.58509 | 0.71307 | 27.784 | 38.3107 | 77.9743 |  | 1.4762 | 2.976 | 190515.4 | 11585.3 | 28614.2 | 55424.5 | 28997.2 | 127394 | 25692 | 28148 | 496370.6 | 45594.1 | 230.1 | 39876 | 242 | 47156.9 | 454.9 | 10886.9 | 57.7 | 4557.7 | 24.5 | 109.29 | 152251875 | 1082370.56 | 1298 | 146444 | 211085 | 2075.1 | 96900 | 300 | 87900 | 300 | 123500 | 1200 | 38100 | 400 | 113100 | 300 | 280 | 490881 | 2568.32 | 2160 | 352080 | 489384 | 2952 | 493449.32 | 488312.68 | 486432 | -0.5885% | 12.6833 | 128.08 | Fully Cloudly Weather
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | 6:15 | 18:46 | 5373.2 | 5364.3 | 4967.1 | 4951.5 | 5085.6 | 5282.9 | 5136.8 | 5762.4 | 5158.9 | 5098.1 | 5155.4 | 5273.3 | 5366.3 | 5123.2 | 5395.8 | 5246.8 | 7276 | 8206.8 | 7143.3 | 7485.9 | 7623.7 | 4727.9 | 7276.6 | 7436.7 | 7240 | 7210 | 7210.6 | 7270.3 | 5695.7 | 5858.5 | 5799.9 | 5847.8 | 5801.1 | 6005.4 | 5860.7 | 5431.4 | 4671.3 | 4698.5 | 4742.4 | 4461.4 | 4794.4 | 4712.8 | 6656.9 | 7511.7 | 5418.1 | 6610.8 | 7167 | 6879 | 6425 | 7044 | 7545 | 7697 | 7693 | 7740 | 5094 | 4066 | 4917 | 4872 | 5437 | 5194 | 5704 | 5600 | 5796 | 5951 | 5807 | 6270 | 5137 | 4748 | 4432 | 4952 | 2268 | 649 | 4823 | 5240 | 3.9929 | 3.5522 | 3.3777 | 3.5443 | 0.48201 | 0.51581 | 0.68885 | 0.5254 | 27.4535 | 27.4806 | 38.6345 | 35.5725 | 77.7137 | 78.1615 | 0 | 0 | 1.5336 | 1.6542 | 2.925 | 3.678 | 3.7726 | 3.461 | 0.49891 | 0.60713 | 27.4671 | 37.1035 | 77.9376 |  | 1.5939 | 3.3015 | 169849.4 | 9369.8 | 23201.9 | 44908.5 | 23098.6 | 109388 | 21935 | 23824 | 425575.2 | 45679.8 | 230.5 | 39955.7 | 242.3 | 47257.1 | 455.5 | 10918.9 | 57.8 | 4655.4 | 24.9 | 109.59 | 152674156 | 1084392.064 | 1301 | 146865 | 211669.7 | 2078.8 | 85700 | 400 | 79700 | 300 | 100200 | 600 | 32000 | 300 | 97700 | 400 | 300 | 422281 | 2021.504 | 2160 | 303120 | 420984 | 2664 | 424302.504 | 420259.496 | 418320 | -0.2991% | 12.5167 | 128.08 | Fully Cloudly Weather
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 135: 0; 136: 0; 137: 0; 138: 0; 139: 0; 140: 0; 142: 0; 143: 0; 144: 0; 145: 0; 146: 0; 148: 0; 149: 0; 150: 0; 151: 0; 152: 0; 153: 0; 155: 0
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 135: 0; 136: 0; 137: 0; 138: 0; 139: 0; 140: 0; 142: 0; 143: 0; 144: 0; 145: 0; 146: 0; 148: 0; 149: 0; 150: 0; 151: 0; 152: 0; 153: 0; 155: 0
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 135: 0; 136: 0; 137: 0; 138: 0; 139: 0; 140: 0; 142: 0; 143: 0; 144: 0; 145: 0; 146: 0; 148: 0; 149: 0; 150: 0; 151: 0; 152: 0; 153: 0; 155: 0
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 135: 0; 136: 0; 137: 0; 138: 0; 139: 0; 140: 0; 141: 0; 142: 0; 143: 0; 144: 0; 145: 0; 146: 0; 148: 0; 149: 0; 150: 0; 151: 0; 152: 0; 153: 0; 155: 0
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 135: 0; 136: 0; 137: 0; 138: 0; 139: 0; 140: 0; 141: 0; 142: 0; 143: 0; 144: 0; 145: 0; 146: 0; 148: 0; 149: 0; 150: 0; 151: 0; 152: 0; 153: 0; 155: 0
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 135: 0; 136: 0; 137: 0; 138: 0; 139: 0; 140: 0; 141: 0; 142: 0; 143: 0; 144: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 150: 0; 151: 0; 152: 0; 153: 0; 155: 0
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 135: 0; 137: 0; 138: 0; 139: 0; 140: 0; 141: 0; 142: 0; 143: 0; 144: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 150: 0; 151: 0; 152: 0; 153: 0; 155: 0
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 135: 0; 139: 0; 141: 0; 142: 0; 143: 0; 144: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 150: 0; 151: 0; 152: 0; 153: 0; 155: 0
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 150: 0; 151: 0; 152: 0; 153: 0; 155: 0
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 150: 0; 151: 0; 152: 0; 153: 0; 155: 0
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 150: 0; 151: 0; 152: 0; 153: 0; 155: 0
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 150: 0; 151: 0; 152: 0; 153: 0; 155: 0
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 150: 0; 151: 0; 152: 0; 153: 0; 155: 0
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 150: 0; 151: 0; 152: 0; 153: 0; 155: 0
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 150: 0; 151: 0; 152: 0; 153: 0; 155: 0
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 151: 0; 152: 0; 155: 0
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 151: 0; 152: 0; 155: 0
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 151: 0; 152: 0; 155: 0
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 151: 0; 152: 0; 155: 0
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 151: 0; 152: 0; 155: 0
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 151: 0; 152: 0; 155: 0
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 151: 0; 152: 0; 155: 0
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 151: 0; 152: 0; 155: 0
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 151: 0; 152: 0; 155: 0
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [72 empty] | 108: 0; 109: 0; 110: 0; 111: 0; 112: 0; 113: 0; 114: 0; 115: 0; 116: 0; 134: 0; 142: 0; 143: 0; 145: 0; 146: 0; 147: 0; 148: 0; 149: 0; 151: 0; 152: 0; 155: 0
Formulas:
Month Year = [Date]-DAY([Date])+1
Days = DAY(EOMONTH(RD[[#This Row],[Date]],0))
Date = [Date, row above]+1

## Inv_SY_B
| 1596.305 | 1596.305 | 1501.475 | 1515.25 | 1560.49 | 1614.14 | 1534.97 | 1706.94 | 1584.75 | 1522.2 | 1522.3 | 1590.36 | 1553.53 | 1606.26 | 1620.06 | 1553.53 | 2199.97 | 2469.93 | 2126.86 | 2215.89 | 2424.4 | 1474.505 | 2181.09 | 2227.96 | 2182.4 | 2201.1 | 2181.09 | 2212.7 | 1784.1 | 1866.15 | 1834.25 | 1866.1 | 1834.25 | 1898.05 | 1882.1 | 1850.2 | 1485.67 | 1485.67 | 1485.67 | 1485.67 | 1519.6 | 1501.475 | 2133.675 | 2386.55 | 1722.745 | 2117.87 | 2169.2 | 2041.6 | 1924.95 | 1977.8 | 2280.84 | 2248.95 | 2233 | 2262.002 | 1471.87 | 1201.18 | 1390.84 | 1390.84 | 1534.68 | 1456.38 | 1597.32 | 1583.58 | 1659.285 | 1738.31 | 1817.575 | 1801.829 | 1499.3 | 1351.7 | 1320.57 | 1421.7 | 641.8794 | 172.8 | 1387.65 | 1515.25
| 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82
Date | IS1Inv1M1 | IS1Inv1M2 | IS1Inv1M3 | IS1Inv1M4 | IS1Inv2M1 | IS1Inv2M2 | IS1Inv2M3 | IS1Inv2M4 | IS2Inv1M1 | IS2Inv1M2 | IS2Inv1M3 | IS2Inv1M4 | IS2Inv2M1 | IS2Inv2M2 | IS2Inv2M3 | IS2Inv2M4 | IS3Inv1M1 | IS3Inv1M2 | IS3Inv2M1 | IS3Inv2M2 | IS4Inv1M1 | IS4Inv1M2 | IS4Inv2M1 | IS4Inv2M2 | IS4Inv3M1 | IS4Inv3M2 | IS4Inv4M1 | IS4Inv4M2 | IS5Inv1M1 | IS5Inv1M2 | IS5Inv2M1 | IS5Inv2M2 | IS6Inv1M1 | IS6Inv1M2 | IS6Inv2M1 | IS6Inv2M2 | IS7Inv1M1 | IS7Inv2M1 | IS8Inv1M1 | IS8Inv1M2 | IS8Inv1M3 | IS8Inv1M4 | IS9Inv1M1 | IS9Inv1M2 | IS9Inv2M1 | IS9Inv2M2 | IS10Inv1M1 | IS10Inv1M2 | IS10Inv2M1 | IS10Inv2M2 | IS10Inv3M1 | IS10Inv3M2 | IS10Inv4M1 | IS10Inv4M2 | IS11Inv1M1 | IS11Inv1M2 | IS11Inv1M3 | IS11Inv1M4 | IS12Inv1M1 | IS12Inv1M2 | IS12Inv1M3 | IS12Inv1M4 | IS13Inv1M1 | IS13Inv1M2 | IS13Inv2M1 | IS13Inv2M2 | IS14Inv1M1 | IS14Inv1M2 | IS14Inv1M3 | IS14Inv1M4 | IS14Inv2M1 | IS14Inv2M2 | IS14Inv2M3 | IS14Inv2M4 | Avg_SY
2025-06-12 | 4.6033 | 4.5779 | 4.5746 | 4.4905 | 4.4755 | 4.4937 | 4.6017 | 4.5736 | 4.5256 | 4.5624 | 4.7495 | 4.5518 | 4.8708 | 4.499 | 4.5429 | 4.5793 | 4.5026 | 4.4376 | 4.5439 | 4.5749 | 4.3767 | 4.3274 | 4.4914 | 4.4737 | 4.4754 | 4.4418 | 4.4459 | 4.4035 | 4.5918 | 4.4975 | 4.4569 | 4.4127 | 4.5017 | 4.4976 | 4.48 | 4.482 | 4.562 | 4.5816 | 4.558 | 4.5185 | 4.5505 | 4.5517 | 4.5236 | 4.5475 | 4.5311 | 4.4431 | 4.0743 | 4.2501 | 4.7251 | 5.0857 | 4.9236 | 4.8867 | 4.7791 | 4.8635 | 5.012 | 4.8457 | 4.9035 | 4.9983 | 4.8445 | 4.9396 | 4.8848 | 4.9247 | 4.9823 | 4.9054 | 4.5522 | 4.7629 | 0 | 0 | 0 | 0 | 1.8384 | 5.787 | 3.2544 | 4.9542 | 4.5719
2025-06-13 | 5.1432 | 5.1116 | 5.1577 | 5.1783 | 5.1961 | 5.1751 | 5.2606 | 5.0915 | 5.0985 | 5.1578 | 5.3355 | 5.1125 | 5.4833 | 5.0251 | 5.0866 | 5.1885 | 5.0717 | 4.831 | 5.1544 | 5.2067 | 4.7992 | 4.9338 | 5.1041 | 5.0593 | 5.0623 | 5.0375 | 5.014 | 4.9548 | 5.1833 | 5.0912 | 5.1855 | 5.2071 | 5.1558 | 5.2104 | 5.1228 | 5.212 | 5.3852 | 5.4586 | 5.3457 | 5.3006 | 5.3906 | 5.4273 | 5.1308 | 5.094 | 5.2474 | 5.214 | 4.2969 | 4.4228 | 5.0277 | 5.4192 | 5.4848 | 4.9868 | 5.0799 | 5.1817 | 5.2702 | 5.1616 | 5.245 | 5.2565 | 5.2617 | 5.4862 | 5.1543 | 5.1163 | 5.3299 | 5.2706 | 4.9462 | 5.1731 | 0 | 0 | 0 | 0 | 1.9191 | 6.0764 | 3.4295 | 5.2348 | 5.0946
2025-06-14 | 4.7477 | 4.757 | 4.7126 | 4.6021 | 4.6539 | 4.6774 | 4.741 | 4.6837 | 4.6742 | 4.6979 | 4.9875 | 4.8059 | 5.084 | 4.881 | 4.7269 | 4.748 | 4.889 | 4.8299 | 4.8011 | 4.8752 | 4.7497 | 4.8697 | 5.0236 | 4.9352 | 4.9715 | 4.9471 | 4.9452 | 4.8937 | 4.9535 | 4.808 | 4.5921 | 4.483 | 4.7769 | 4.6762 | 4.7191 | 4.6541 | 4.606 | 4.5796 | 4.6565 | 4.6024 | 4.5682 | 4.5362 | 4.8292 | 4.7935 | 4.8132 | 4.5754 | 4.179 | 4.3073 | 4.6368 | 5.0216 | 3.9709 | 4.2255 | 4.8328 | 4.9187 | 5.2647 | 5.2031 | 5.3982 | 5.3593 | 5.1946 | 5.3207 | 5.2798 | 5.2874 | 5.4873 | 5.4093 | 4.9349 | 5.2946 | 0 | 0 | 0 | 0 | 2.0533 | 6.4525 | 3.6047 | 5.4671 | 4.8034
2025-06-15 | 4.5435 | 4.5841 | 4.6484 | 4.4131 | 4.316 | 4.4224 | 4.5761 | 4.4249 | 4.3713 | 4.2977 | 4.3761 | 4.2116 | 4.6697 | 3.9166 | 4.335 | 4.4439 | 4.2114 | 3.9377 | 4.4357 | 4.5189 | 3.9444 | 4.096 | 4.1703 | 4.1036 | 4.0579 | 4.0243 | 4.0678 | 3.9726 | 3.9778 | 3.8758 | 3.8767 | 3.8438 | 3.8511 | 3.8238 | 3.802 | 3.8268 | 3.7788 | 3.8018 | 3.8239 | 3.8237 | 3.7979 | 3.7916 | 3.8717 | 3.919 | 3.8705 | 3.7131 | 4.0806 | 4.1653 | 4.7181 | 5.0768 | 4.7526 | 4.8787 | 4.8437 | 4.9515 | 5.1659 | 5.1083 | 5.2413 | 4.4117 | 4.9881 | 5.0439 | 4.9038 | 4.9692 | 5.3424 | 5.314 | 4.7194 | 5.1224 | 0 | 0 | 0 | 0 | 1.9765 | 6.224 | 3.501 | 5.2021 | 4.3409
2025-06-16 | 3.9243 | 3.9031 | 3.9532 | 3.9058 | 3.8989 | 3.9052 | 3.9852 | 3.8401 | 3.8845 | 3.9202 | 4.0995 | 3.9556 | 4.2323 | 4.0662 | 3.9339 | 3.9778 | 4.0568 | 3.9957 | 4.0096 | 4.1099 | 3.9878 | 4.2129 | 4.2906 | 4.1484 | 4.188 | 4.1673 | 4.247 | 4.1028 | 4.2786 | 4.1665 | 4.1469 | 4.0878 | 4.161 | 4.1424 | 4.1303 | 4.1491 | 4.0524 | 4.0346 | 4.0469 | 4.0257 | 3.9934 | 4.0001 | 4.1136 | 4.0188 | 4.2328 | 4.0106 | 3.6982 | 3.7967 | 4.1237 | 4.3295 | 4.0018 | 4.0475 | 3.9803 | 4.1016 | 4.128 | 4.0537 | 4.1259 | 4.0877 | 4.0208 | 3.9805 | 3.9529 | 4.0412 | 4.152 | 4.11 | 3.6838 | 3.9797 | 0 | 0 | 0 | 0 | 1.4129 | 4.3906 | 2.6163 | 3.9869 | 3.9928
2025-06-17 | 4.9045 | 4.9487 | 5.0547 | 4.8958 | 4.8191 | 4.7865 | 4.9836 | 4.7591 | 4.9135 | 4.9728 | 5.1754 | 4.9936 | 5.3445 | 5.0867 | 4.9877 | 5.0757 | 5.0861 | 4.8785 | 5.0819 | 5.246 | 4.998 | 5.2528 | 5.4058 | 5.2045 | 5.2527 | 5.1929 | 5.3183 | 5.2525 | 4.6907 | 4.6042 | 4.5808 | 4.5643 | 4.5987 | 4.6212 | 4.5816 | 4.6286 | 4.6173 | 4.6569 | 4.5664 | 4.5632 | 4.5374 | 4.593 | 4.5697 | 4.4898 | 4.6847 | 4.555 | 4.1695 | 4.2955 | 4.8976 | 5.2195 | 4.8366 | 4.9159 | 4.8549 | 4.9553 | 5.153 | 5.0679 | 5.1616 | 4.3769 | 5.0082 | 5.0529 | 4.9335 | 4.9918 | 5.2927 | 5.2106 | 4.7141 | 5.1129 | 0 | 0 | 0 | 0 | 1.9223 | 6.0475 | 3.4375 | 5.1374 | 4.8477
2025-06-18 | 3.1361 | 3.1206 | 3.1235 | 3.1152 | 3.126 | 3.0951 | 3.1577 | 3.1295 | 3.1481 | 3.1802 | 3.3099 | 3.1937 | 3.4182 | 3.1924 | 3.1916 | 3.1874 | 3.1958 | 3.2069 | 3.1979 | 3.2186 | 3.1891 | 3.203 | 3.3066 | 3.2987 | 3.2657 | 3.2345 | 3.2532 | 3.2329 | 3.3698 | 3.3122 | 3.3054 | 3.2943 | 3.2874 | 3.2802 | 3.2383 | 3.273 | 3.2528 | 3.2785 | 3.2939 | 3.2965 | 3.2853 | 3.281 | 3.2207 | 3.2353 | 3.2601 | 3.2107 | 3.0866 | 3.1469 | 3.1154 | 3.3261 | 3.1359 | 3.1726 | 3.1011 | 3.1832 | 3.1559 | 3.0701 | 3.1011 | 2.6514 | 3.209 | 3.1515 | 3.1864 | 3.2231 | 3.2315 | 3.1825 | 2.8778 | 3.1318 | 0.080704 | 0.032552 | 0.015902 | 0.023212 | 1.0756 | 3.3304 | 2.0486 | 3.13 | 3.1518
2025-06-19 | 3.0242 | 2.9835 | 3.0194 | 3.0307 | 3.0419 | 3.0132 | 3.0696 | 2.9836 | 3.0321 | 3.0826 | 3.1914 | 3.0536 | 3.2633 | 3.0645 | 3.0714 | 3.0386 | 3.0431 | 3.0334 | 3.0493 | 3.0769 | 3.0193 | 3.0744 | 3.1617 | 3.161 | 3.118 | 3.0801 | 3.1163 | 3.0906 | 3.2565 | 3.1887 | 3.182 | 3.1549 | 3.217 | 3.2323 | 3.2189 | 3.2358 | 3.2203 | 3.2284 | 3.1774 | 3.1542 | 3.1605 | 3.1905 | 3.2383 | 3.255 | 3.3372 | 3.2598 | 3.0474 | 3.0714 | 3.0616 | 3.3383 | 3.1746 | 3.2481 | 3.2265 | 3.2947 | 3.2101 | 3.1785 | 3.2137 | 2.745 | 3.3088 | 3.2695 | 3.2809 | 3.3136 | 3.4647 | 3.4111 | 3.065 | 3.3415 | 0.51624 | 0.16646 | 0.43542 | 0.11254 | 1.1878 | 3.7124 | 2.2279 | 3.3635 | 2.9714
2025-06-20 | 5.0485 | 5.0441 | 5.1086 | 5.0206 | 4.9983 | 4.9534 | 5.0989 | 4.9474 | 4.9952 | 5.0636 | 5.2228 | 5.0149 | 5.402 | 5.0241 | 5.0539 | 5.1073 | 5.0269 | 4.86 | 5.0919 | 5.2005 | 4.8326 | 4.9684 | 5.1746 | 5.1401 | 5.0704 | 5.0278 | 5.1274 | 5.0586 | 5.3249 | 5.2324 | 5.2248 | 5.1846 | 5.2683 | 5.2821 | 5.2411 | 5.2699 | 5.3002 | 5.3222 | 5.2511 | 5.2289 | 5.2133 | 5.2628 | 5.2755 | 5.1999 | 5.3993 | 5.2814 | 4.4006 | 4.5286 | 4.995 | 5.4736 | 5.0752 | 5.1434 | 5.1184 | 5.2073 | 5.2102 | 5.1653 | 5.2089 | 4.461 | 5.2773 | 5.2731 | 5.1857 | 5.2548 | 5.3917 | 5.3159 | 4.809 | 5.2303 | 1.5314 | 0.5337 | 2.134 | 0.37525 | 1.9376 | 6.1204 | 3.4879 | 5.2597 | 4.8588
2025-06-21 | 4.1894 | 4.1275 | 4.1618 | 4.2045 | 4.2238 | 4.1942 | 4.2541 | 4.1946 | 4.1768 | 4.2899 | 4.4433 | 4.2402 | 4.5202 | 4.2509 | 4.2621 | 4.2282 | 4.2095 | 4.182 | 4.2095 | 4.2395 | 4.0926 | 4.2146 | 4.3647 | 4.3433 | 4.2846 | 4.2247 | 4.2997 | 4.2598 | 4.4446 | 4.37 | 4.3485 | 4.337 | 4.3507 | 4.345 | 4.3075 | 4.3463 | 4.3586 | 4.3823 | 4.3503 | 4.3492 | 4.3355 | 4.3584 | 4.3138 | 4.3026 | 4.3524 | 4.27 | 4.0136 | 4.1101 | 4.2093 | 4.5029 | 4.234 | 4.3032 | 4.2739 | 4.3803 | 4.3663 | 4.2801 | 4.3393 | 4.4656 | 4.4941 | 4.4354 | 4.4712 | 4.5081 | 4.5389 | 4.4589 | 4.0534 | 4.4065 | 1.6571 | 0.44537 | 1.7697 | 0.53246 | 1.6241 | 5.0932 | 2.9366 | 4.4379 | 4.0872
2025-06-22 | 2.6271 | 2.6123 | 2.6107 | 2.5952 | 2.6018 | 2.5845 | 2.6395 | 2.5931 | 2.6333 | 2.6587 | 2.7551 | 2.6431 | 2.8281 | 2.637 | 2.6555 | 2.6406 | 2.6356 | 2.6559 | 2.6557 | 2.6744 | 2.5966 | 2.6405 | 2.7346 | 2.7245 | 2.6997 | 2.6656 | 2.7031 | 2.6747 | 2.5238 | 2.5032 | 2.5 | 2.4912 | 2.4797 | 2.4797 | 2.4463 | 2.463 | 2.4415 | 2.4553 | 2.4537 | 2.464 | 2.4468 | 2.4477 | 2.4193 | 2.4279 | 2.4284 | 2.3936 | 2.6769 | 2.7043 | 2.6841 | 2.8972 | 2.7357 | 2.8175 | 2.8134 | 2.8577 | 2.8754 | 2.7365 | 2.87 | 2.843 | 2.9217 | 2.8298 | 2.8798 | 2.9168 | 2.9599 | 2.9133 | 2.6904 | 2.8721 | 1.3694 | 0.40874 | 1.8965 | 1.2328 | 1.0005 | 3.103 | 1.9199 | 2.895 | 2.5536
2025-06-23 | 2.7049 | 2.7102 | 2.6839 | 2.6598 | 2.6497 | 2.6451 | 2.7195 | 2.705 | 2.7136 | 2.7286 | 2.8314 | 2.7308 | 2.9167 | 2.7054 | 2.7312 | 2.7295 | 2.7399 | 2.7783 | 2.7474 | 2.7653 | 2.705 | 2.6774 | 2.7821 | 2.7654 | 2.7641 | 2.7554 | 2.7477 | 2.7125 | 2.5646 | 2.5273 | 2.5096 | 2.494 | 2.4987 | 2.4928 | 2.4765 | 2.4857 | 2.4615 | 2.4649 | 2.4693 | 2.4866 | 2.4561 | 2.4573 | 2.4695 | 2.4856 | 2.4553 | 2.4209 | 2.7255 | 2.769 | 2.6562 | 2.8492 | 2.6794 | 2.733 | 2.7203 | 2.7737 | 2.7315 | 2.5833 | 2.7214 | 2.6962 | 2.7788 | 2.6901 | 2.7302 | 2.7815 | 2.8255 | 2.7879 | 2.5723 | 2.7445 | 1.2662 | 0.36909 | 2.6448 | 1.3501 | 0.90656 | 2.7975 | 1.7871 | 2.7579 | 2.5623
2025-06-24 | 0.55553 | 0.56355 | 0.55585 | 0.53872 | 0.53733 | 0.53384 | 0.5503 | 0.55245 | 0.56028 | 0.56057 | 0.58563 | 0.56931 | 0.60868 | 0.5684 | 0.56831 | 0.56916 | 0.59769 | 0.61253 | 0.59289 | 0.59827 | 0.57977 | 0.59213 | 0.61795 | 0.61514 | 0.61217 | 0.60924 | 0.60616 | 0.59949 | 0.5887 | 0.58034 | 0.57778 | 0.57451 | 0.57746 | 0.5788 | 0.57388 | 0.57783 | 0.55712 | 0.55941 | 0.55497 | 0.55921 | 0.55436 | 0.55679 | 0.57324 | 0.57732 | 0.57594 | 0.57393 | 0.64171 | 0.64753 | 0.613 | 0.6578 | 0.62188 | 0.63745 | 0.63636 | 0.65031 | 0.62709 | 0.58942 | 0.62408 | 0.61833 | 0.63531 | 0.61454 | 0.62624 | 0.6378 | 0.66209 | 0.65259 | 0.60003 | 0.64179 | 0.29627 | 0.071466 | 0.6239 | 0.35465 | 0.17823 | 0.5353 | 0.4068 | 0.63844 | 0.57742
2025-06-25 | 2.5342 | 2.5282 | 2.5083 | 2.5323 | 2.5382 | 2.5163 | 2.5692 | 2.5475 | 2.5309 | 2.5806 | 2.6593 | 2.554 | 2.7244 | 2.5298 | 2.5553 | 2.5374 | 2.5405 | 2.5772 | 2.5502 | 2.5607 | 2.5338 | 2.4934 | 2.5904 | 2.5924 | 2.5631 | 2.5449 | 2.5588 | 2.5349 | 2.6084 | 2.5861 | 2.5972 | 2.5871 | 2.576 | 2.5822 | 2.5465 | 2.4205 | 2.5608 | 2.5682 | 2.5593 | 2.5833 | 2.5542 | 2.5617 | 2.541 | 2.5547 | 2.552 | 2.5325 | 2.6329 | 2.6415 | 2.5022 | 2.6966 | 2.5613 | 2.6427 | 2.6414 | 2.6976 | 2.6869 | 2.5444 | 2.6884 | 2.6676 | 2.5998 | 2.6526 | 2.6906 | 2.7343 | 2.8336 | 2.7998 | 2.5622 | 2.7425 | 1.3654 | 0.38285 | 2.7411 | 1.5932 | 0.94488 | 2.9155 | 1.827 | 2.7911 | 2.5059
2025-06-26 | 1.2644 | 1.2636 | 1.248 | 1.2401 | 1.2498 | 1.2464 | 1.2642 | 1.2751 | 1.2501 | 1.2659 | 1.2994 | 1.252 | 1.3433 | 1.236 | 1.2618 | 1.2579 | 1.2876 | 1.3063 | 1.3054 | 1.3137 | 1.2067 | 1.2279 | 1.2915 | 1.2976 | 1.2887 | 1.282 | 1.2954 | 1.2733 | 1.3019 | 1.2918 | 1.2949 | 1.2954 | 1.2909 | 1.2984 | 1.285 | 1.2313 | 1.2536 | 1.2652 | 1.2372 | 1.2521 | 1.2436 | 1.2555 | 1.2868 | 1.3068 | 1.3127 | 1.3166 | 1.2819 | 1.3035 | 1.2367 | 1.3185 | 1.2491 | 1.278 | 1.2705 | 1.2966 | 1.2221 | 1.1364 | 1.2009 | 1.1676 | 1.2356 | 1.1864 | 1.2111 | 1.2405 | 1.2678 | 1.2589 | 1.1663 | 1.236 | 0.095645 | 0 | 0.51947 | 0.28937 | 0.29227 | 0.8397 | 0.74291 | 1.1916 | 1.2118
2025-06-27 | 3.9417 | 3.9297 | 3.8991 | 3.8535 | 3.8594 | 3.8389 | 3.9357 | 3.912 | 3.9695 | 3.9626 | 4.0797 | 3.9317 | 4.2578 | 3.9136 | 3.9609 | 3.9735 | 3.8834 | 3.8829 | 3.9532 | 3.9688 | 3.8801 | 3.8712 | 3.9594 | 4.0334 | 3.9715 | 3.9135 | 3.9958 | 3.9324 | 4.0034 | 3.9825 | 3.9689 | 3.9352 | 3.9779 | 3.9791 | 3.949 | 3.8326 | 3.9846 | 4.0163 | 3.9461 | 3.9458 | 3.9424 | 3.9798 | 3.9216 | 3.9599 | 4.0344 | 3.974 | 3.6015 | 3.6865 | 3.789 | 4.0536 | 3.8424 | 3.9377 | 3.9515 | 4.0154 | 4.0628 | 3.8583 | 4.0231 | 3.9573 | 4.0712 | 4.0099 | 4.0169 | 4.0636 | 4.2198 | 4.0758 | 3.8564 | 4.0972 | 2.6194 | 0.4899 | 3.8639 | 2.6352 | 1.4146 | 4.4491 | 2.5488 | 3.7946 | 3.8217
2025-06-28 | 3.6534 | 3.6726 | 3.6643 | 3.573 | 3.5769 | 3.5812 | 3.6762 | 3.6338 | 3.6128 | 3.664 | 3.7937 | 3.6777 | 3.9127 | 3.6146 | 3.6639 | 3.6728 | 3.696 | 3.6309 | 3.6827 | 3.7018 | 3.6041 | 3.6675 | 3.6981 | 3.6869 | 3.7298 | 3.7201 | 3.6788 | 3.6129 | 3.6703 | 3.6062 | 3.5714 | 3.5626 | 3.5662 | 3.5259 | 3.5232 | 3.4109 | 3.5047 | 3.5336 | 3.481 | 3.5202 | 3.4849 | 3.4966 | 3.5326 | 3.5207 | 3.6103 | 3.5375 | 3.4424 | 3.5228 | 3.6911 | 3.9391 | 3.7084 | 3.773 | 3.7016 | 3.8042 | 3.8787 | 3.825 | 3.826 | 3.7641 | 3.7722 | 3.7434 | 3.6891 | 3.8013 | 3.8794 | 3.8008 | 3.5349 | 3.7467 | 2.7717 | 1.0101 | 3.5031 | 2.6491 | 1.1934 | 1.0162 | 3.7352 | 3.714 | 3.525
2025-06-29 | 2.1654 | 2.15 | 2.13 | 2.1541 | 2.1709 | 2.1577 | 2.1869 | 2.1799 | 2.1565 | 2.1996 | 2.2524 | 2.1695 | 2.305 | 2.121 | 2.171 | 2.1537 | 2.158 | 2.1809 | 2.178 | 2.1876 | 2.1539 | 2.1242 | 2.1858 | 2.2267 | 2.1915 | 2.171 | 2.2036 | 2.1809 | 2.4005 | 2.3831 | 2.3894 | 2.3736 | 2.3954 | 2.4038 | 2.3782 | 2.2899 | 2.3924 | 2.4082 | 2.3608 | 2.3546 | 2.3642 | 2.3867 | 2.3794 | 2.424 | 2.4457 | 2.4342 | 2.1882 | 2.2129 | 2.0966 | 2.2296 | 2.1311 | 2.1826 | 2.1743 | 2.2106 | 2.1631 | 2.1019 | 2.2031 | 2.1778 | 2.2102 | 2.2108 | 2.2006 | 2.2094 | 2.213 | 2.1837 | 2.0417 | 2.1606 | 1.7536 | 1.5553 | 2.0584 | 1.7204 | 0.96778 | 1.6128 | 2.1747 | 2.1502 | 2.1814
2025-06-30 | 2.5563 | 2.5535 | 2.5217 | 2.5053 | 2.5133 | 2.5058 | 2.5593 | 2.5662 | 2.5299 | 2.559 | 2.6237 | 2.5428 | 2.703 | 2.4703 | 2.5423 | 2.5469 | 2.5419 | 2.5636 | 2.5628 | 2.5791 | 2.4934 | 2.4447 | 2.5107 | 2.5365 | 2.5364 | 2.5352 | 2.5291 | 2.4957 | 2.4807 | 2.4585 | 2.4512 | 2.4465 | 2.4523 | 2.4498 | 2.4336 | 2.3388 | 2.4308 | 2.4462 | 2.4036 | 2.412 | 2.4069 | 2.4277 | 2.4275 | 2.4555 | 2.4552 | 2.4467 | 2.6047 | 2.6459 | 2.5442 | 2.5308 | 2.588 | 2.6588 | 2.6344 | 2.6729 | 2.643 | 2.5721 | 2.6973 | 3.0564 | 2.7004 | 2.7348 | 2.7363 | 2.6974 | 2.7072 | 2.659 | 2.4973 | 2.6317 | 2.6167 | 1.9892 | 2.5761 | 2.6092 | 1.3097 | 2.2425 | 2.6924 | 2.6523 | 2.525
2025-07-01 | 2.9845 | 2.9646 | 2.9453 | 2.9307 | 2.9385 | 2.9406 | 3.0014 | 2.992 | 2.9662 | 2.992 | 3.0638 | 2.9718 | 3.1524 | 2.8779 | 2.9637 | 2.973 | 2.9433 | 2.9481 | 2.9756 | 2.9918 | 2.8632 | 2.8245 | 2.8821 | 2.9339 | 2.9237 | 2.9154 | 2.9232 | 2.8868 | 2.9466 | 2.9166 | 2.9077 | 2.8948 | 2.9212 | 2.9202 | 2.9029 | 2.7978 | 2.9157 | 2.9267 | 2.8728 | 2.8897 | 2.8749 | 2.8985 | 2.9013 | 2.9387 | 2.9438 | 2.9238 | 2.9636 | 3.006 | 2.8938 | 2.8394 | 2.9376 | 3.0208 | 2.9833 | 3.0405 | 3.0268 | 2.9538 | 3.0837 | 2.9264 | 3.0628 | 3.071 | 3.0789 | 3.0581 | 2.9649 | 2.9848 | 2.7964 | 3.0507 | 2.9012 | 2.2441 | 2.8401 | 2.8705 | 2.1026 | 2.533 | 3.0209 | 3.0038 | 2.9219
2025-07-02 | 3.4389 | 3.4422 | 3.4078 | 3.3671 | 3.3914 | 3.3745 | 3.4443 | 3.4425 | 3.3923 | 3.4461 | 3.5331 | 3.4378 | 3.6297 | 3.3322 | 3.4178 | 3.43 | 3.4249 | 3.4321 | 3.4347 | 3.4571 | 3.3658 | 3.3444 | 3.4457 | 3.4713 | 3.4248 | 3.4221 | 3.4145 | 3.3913 | 3.57 | 3.4949 | 3.4628 | 3.4351 | 3.1542 | 3.1085 | 3.128 | 2.3821 | 3.5103 | 3.5303 | 2.6076 | 2.6268 | 2.593 | 2.6232 | 3.4863 | 3.4809 | 3.4873 | 3.4606 | 3.4432 | 3.4736 | 3.3859 | 3.5341 | 3.5272 | 3.6533 | 3.5963 | 3.6854 | 3.7733 | 3.7084 | 3.894 | 3.8621 | 3.8115 | 3.8843 | 3.8738 | 3.8302 | 3.7505 | 3.7818 | 3.5485 | 3.838 | 3.653 | 3.0869 | 3.6321 | 3.789 | 3.637 | 4.1262 | 3.8169 | 3.7865 | 3.466
2025-07-03 | 3.4 | 3.4088 | 3.3706 | 3.3196 | 3.3423 | 3.3283 | 3.4001 | 3.3695 | 3.3841 | 3.4229 | 3.5247 | 3.4302 | 3.6135 | 3.3518 | 3.4181 | 3.4257 | 3.419 | 3.4424 | 3.4311 | 3.4585 | 3.4551 | 3.4414 | 3.5553 | 3.5533 | 3.4953 | 3.4739 | 3.4888 | 3.4579 | 3.7621 | 3.698 | 3.6724 | 3.6339 | 3.7088 | 3.6869 | 3.6873 | 3.6857 | 3.6765 | 3.7142 | 3.685 | 3.6757 | 3.634 | 3.6542 | 3.6861 | 3.7151 | 3.7639 | 3.7037 | 3.503 | 3.5676 | 3.5309 | 3.2766 | 3.5441 | 3.6548 | 3.6272 | 3.6956 | 3.7129 | 3.6376 | 3.8066 | 3.775 | 3.7661 | 3.8195 | 3.8029 | 3.7637 | 3.6752 | 3.7502 | 3.47 | 3.7664 | 3.6891 | 3.7977 | 3.6606 | 3.8302 | 3.833 | 4.1823 | 3.7885 | 3.7342 | 3.5985
2025-07-04 | 2.8402 | 2.8159 | 2.7897 | 2.8115 | 2.8429 | 2.8295 | 2.8712 | 2.8601 | 2.8174 | 2.8789 | 2.9362 | 2.844 | 2.9858 | 2.7619 | 2.8332 | 2.8187 | 2.8082 | 2.8345 | 2.825 | 2.8382 | 2.7774 | 2.7674 | 2.8658 | 2.8724 | 2.8381 | 2.825 | 2.8376 | 2.8162 | 2.9339 | 2.9053 | 2.905 | 2.8793 | 2.9082 | 2.9108 | 2.892 | 2.8986 | 2.8947 | 2.9124 | 2.9299 | 2.9035 | 2.9048 | 2.8872 | 2.8835 | 2.9237 | 2.9185 | 2.9005 | 2.9026 | 2.9501 | 2.7839 | 2.1515 | 2.848 | 2.9155 | 2.8733 | 2.9187 | 2.882 | 2.8081 | 2.9265 | 2.899 | 2.9356 | 2.9222 | 2.9591 | 2.9337 | 2.8137 | 2.8905 | 2.6852 | 2.9061 | 2.5971 | 2.8995 | 2.7672 | 2.9235 | 2.8711 | 2.9797 | 2.8898 | 2.8603 | 2.8571
2025-07-05 | 2.5235 | 2.5308 | 2.5017 | 2.4412 | 2.4506 | 2.4587 | 2.5241 | 2.4854 | 2.5077 | 2.5241 | 2.5837 | 2.5241 | 2.6566 | 2.4458 | 2.5194 | 2.5363 | 2.3196 | 2.3349 | 2.3397 | 2.3566 | 2.4864 | 2.4631 | 2.5506 | 2.5352 | 1.6436 | 1.6301 | 2.5261 | 2.4965 | 2.5555 | 2.5233 | 2.5325 | 2.5084 | 2.5528 | 2.5631 | 2.547 | 2.5645 | 2.5448 | 2.5623 | 2.5627 | 2.5335 | 2.5401 | 2.534 | 2.5525 | 2.609 | 2.6192 | 2.596 | 2.5038 | 2.5622 | 1.1513 | 0.0080898 | 2.5452 | 2.5708 | 2.5944 | 2.6394 | 2.6348 | 2.5741 | 2.6921 | 2.6713 | 2.6546 | 2.6934 | 2.6797 | 2.6548 | 2.5995 | 2.677 | 2.4923 | 2.6723 | 2.5451 | 2.6062 | 2.4601 | 2.6103 | 2.5729 | 2.7384 | 2.6188 | 2.5981 | 2.5056
2025-07-06 | 2.3754 | 2.3617 | 2.3512 | 2.3609 | 2.3922 | 2.3817 | 2.4058 | 2.3818 | 2.3472 | 2.4128 | 2.4519 | 2.3691 | 2.4877 | 2.2989 | 2.3721 | 2.3658 | 2.3663 | 2.3692 | 2.3873 | 2.3922 | 2.3126 | 2.3043 | 2.3898 | 2.4025 | 2.352 | 2.3461 | 2.3685 | 2.353 | 2.4854 | 2.4515 | 2.4517 | 2.4404 | 2.4598 | 2.4575 | 2.4362 | 2.4548 | 2.4299 | 2.4483 | 2.4597 | 2.4489 | 2.4485 | 2.4367 | 2.4312 | 2.4409 | 2.4381 | 2.424 | 2.0143 | 2.0646 | 1.3622 | 0.017798 | 2.3474 | 2.403 | 2.365 | 2.4155 | 2.3852 | 2.32 | 2.4131 | 2.3988 | 2.3901 | 2.4108 | 2.4187 | 2.3939 | 2.3679 | 2.4173 | 2.0791 | 2.4131 | 2.3683 | 2.407 | 2.3054 | 2.426 | 2.3688 | 2.4091 | 2.4049 | 2.3948 | 2.3694
2025-07-07 | 1.555 | 1.5472 | 1.5299 | 1.5174 | 1.5327 | 1.5341 | 1.5566 | 1.5605 | 1.5423 | 1.5681 | 1.5942 | 1.5512 | 1.6269 | 1.5046 | 1.5503 | 1.5516 | 1.5758 | 1.5977 | 1.592 | 1.6011 | 1.5482 | 1.528 | 1.5887 | 1.5898 | 1.5725 | 1.5765 | 1.582 | 1.5653 | 1.5723 | 1.5575 | 1.5606 | 1.5511 | 1.5614 | 1.5648 | 1.5249 | 1.418 | 1.514 | 1.5257 | 1.5349 | 1.526 | 1.5233 | 1.5183 | 1.5394 | 1.5597 | 1.5611 | 1.5644 | 0.96957 | 1.0005 | 1.5636 | 1.3398 | 1.5695 | 1.6125 | 1.5963 | 1.627 | 1.5647 | 1.5065 | 1.5898 | 1.5739 | 1.5782 | 1.589 | 1.599 | 1.5848 | 1.6071 | 1.6081 | 1.4451 | 1.6048 | 1.5209 | 1.5515 | 1.4622 | 1.5589 | 1.4584 | 1.2523 | 1.5513 | 1.5587 | 1.5333
2025-07-08 | 1.7581 | 1.7512 | 1.7275 | 1.7059 | 1.7239 | 1.7293 | 1.7568 | 1.7656 | 1.7386 | 1.7605 | 1.7842 | 1.7395 | 1.8228 | 1.6803 | 1.7406 | 1.7503 | 1.7567 | 1.7771 | 1.7833 | 1.7943 | 1.7062 | 1.6902 | 1.7593 | 1.7607 | 1.7405 | 1.7473 | 1.7535 | 1.734 | 1.7244 | 1.7121 | 1.724 | 1.7144 | 1.7208 | 1.7277 | 1.7095 | 1.6367 | 1.6831 | 1.6957 | 1.7048 | 1.6932 | 1.6911 | 1.6867 | 1.7019 | 1.7295 | 1.6745 | 1.7314 | 1.863 | 1.8283 | 1.2964 | 1.7886 | 1.8031 | 1.8727 | 1.8202 | 1.8835 | 1.8258 | 1.7712 | 1.8592 | 1.8392 | 1.8629 | 1.8767 | 1.885 | 1.8629 | 1.8888 | 1.8622 | 1.6735 | 1.877 | 1.7997 | 1.8415 | 1.7617 | 1.8624 | 1.7787 | 1.6354 | 1.8282 | 1.8278 | 1.7591
2025-07-09 | 1.9095 | 1.9049 | 1.8801 | 1.8595 | 1.88 | 1.8811 | 1.8913 | 1.9162 | 1.8929 | 1.9262 | 1.9543 | 1.9045 | 1.9859 | 1.8448 | 1.9016 | 1.907 | 1.9158 | 1.9441 | 1.938 | 1.9493 | 1.8867 | 1.8705 | 1.9464 | 1.9514 | 1.9234 | 1.9209 | 1.9356 | 1.9176 | 1.9391 | 1.9234 | 1.9346 | 1.9214 | 1.935 | 1.9435 | 1.9207 | 1.8772 | 1.9041 | 1.9188 | 1.9276 | 1.9119 | 1.9112 | 1.9077 | 1.9148 | 1.9482 | 1.9548 | 1.9552 | 1.9704 | 1.8894 | 1.8797 | 2.0238 | 1.8967 | 1.968 | 1.9508 | 1.9832 | 1.9322 | 1.8719 | 1.9713 | 1.9492 | 1.9583 | 1.9717 | 1.9829 | 1.9624 | 1.9834 | 1.9655 | 1.7578 | 1.968 | 1.8896 | 1.9347 | 1.834 | 1.9536 | 1.863 | 1.7488 | 1.9253 | 1.926 | 1.9203
2025-07-10 | 2.1944 | 2.1885 | 2.1664 | 2.136 | 2.1636 | 2.1678 | 2.2026 | 2.2095 | 2.1234 | 2.2094 | 2.2368 | 2.183 | 2.2753 | 2.1132 | 2.1782 | 2.1835 | 2.1841 | 2.2141 | 2.2052 | 2.2192 | 2.1192 | 2.1194 | 2.208 | 2.2133 | 2.2024 | 2.1825 | 2.1965 | 2.1762 | 2.1618 | 2.1507 | 2.1684 | 2.1533 | 2.1638 | 2.1751 | 2.1457 | 1.9966 | 2.1447 | 2.1627 | 2.1703 | 2.1514 | 2.1521 | 2.1487 | 2.141 | 2.1731 | 2.1764 | 2.1836 | 2.3008 | 2.3259 | 2.2121 | 2.368 | 2.2262 | 2.3135 | 2.2879 | 2.2933 | 2.2757 | 2.2197 | 2.3226 | 2.2576 | 2.3309 | 2.3489 | 2.3573 | 2.3271 | 2.3426 | 2.3155 | 2.1116 | 2.3293 | 2.2501 | 2.3032 | 2.2049 | 2.3333 | 2.2679 | 2.2616 | 2.2955 | 2.2932 | 2.2158
2025-07-11 | 4.9267 | 4.8842 | 4.9316 | 4.8826 | 4.6962 | 4.6627 | 4.8706 | 4.6886 | 4.8815 | 4.985 | 5.0574 | 4.932 | 5.2016 | 4.814 | 4.9431 | 5.0098 | 4.926 | 4.7647 | 4.9626 | 4.9317 | 4.6904 | 4.7877 | 4.8588 | 4.8548 | 4.9061 | 4.8862 | 4.8495 | 4.7944 | 4.9539 | 4.8786 | 4.9241 | 4.8589 | 4.9552 | 4.9631 | 4.8688 | 4.7786 | 4.9356 | 4.953 | 4.985 | 4.7581 | 4.9107 | 4.9062 | 4.9351 | 4.873 | 5.0698 | 4.9456 | 4.1432 | 4.2567 | 4.6736 | 4.9668 | 4.558 | 4.6544 | 4.6594 | 4.6799 | 4.7232 | 4.6346 | 4.7468 | 4.7209 | 4.7256 | 4.7913 | 4.6952 | 4.7103 | 4.6677 | 4.6137 | 4.2133 | 4.6547 | 4.7221 | 4.8288 | 4.6796 | 4.9194 | 4.9536 | 5.57 | 4.7893 | 4.6187 | 4.819
2025-07-12 | 3.6891 | 3.6905 | 3.6796 | 3.6698 | 3.6647 | 3.6373 | 3.7191 | 3.6835 | 3.6087 | 3.7572 | 3.8081 | 3.7043 | 3.8552 | 3.6139 | 3.7067 | 3.723 | 3.6688 | 3.6859 | 3.7002 | 3.7118 | 3.6097 | 3.7503 | 3.8116 | 3.8246 | 3.7768 | 3.7 | 3.7885 | 3.7598 | 3.9192 | 3.8614 | 3.9136 | 3.8783 | 3.9023 | 3.9081 | 3.856 | 3.8722 | 3.8863 | 3.9118 | 3.9462 | 3.7504 | 3.9 | 3.8892 | 3.8159 | 3.8212 | 3.9158 | 3.8795 | 3.7166 | 3.8009 | 3.8048 | 4.0833 | 3.7644 | 3.9067 | 3.9978 | 3.9934 | 4.0574 | 3.9669 | 4.1673 | 4.132 | 4.1474 | 4.2043 | 4.177 | 4.1248 | 4.1638 | 4.1207 | 3.6439 | 4.1364 | 4.1086 | 4.1821 | 3.9786 | 4.1134 | 4.2485 | 4.6759 | 4.2021 | 4.1439 | 3.8863
2025-07-13 | 3.366 | 3.3604 | 3.3081 | 3.2678 | 3.259 | 3.2729 | 3.3465 | 3.3759 | 3.2553 | 3.3492 | 3.3866 | 3.3158 | 3.4543 | 3.1895 | 3.3306 | 3.3773 | 3.3073 | 3.3227 | 3.3586 | 3.3783 | 3.1446 | 3.2064 | 3.3362 | 3.3379 | 3.3174 | 3.2756 | 3.306 | 3.2857 | 3.1925 | 3.1394 | 3.162 | 3.1337 | 3.1627 | 3.164 | 3.1139 | 2.9356 | 3.1442 | 3.1625 | 3.1921 | 3.003 | 3.155 | 3.1388 | 3.1199 | 3.1475 | 3.145 | 3.1214 | 3.304 | 3.3694 | 3.3377 | 3.5615 | 3.308 | 3.4225 | 3.4451 | 3.4217 | 3.4609 | 3.385 | 3.5353 | 3.5029 | 3.5428 | 3.5664 | 3.571 | 3.5363 | 3.4931 | 3.4234 | 3.1949 | 3.4798 | 3.4263 | 3.5126 | 3.3561 | 3.4832 | 3.5334 | 3.7558 | 3.4757 | 3.4582 | 3.3242
Formulas:
Date = [Date, row above]+1

## Inv_SY
| 1596.305 | 1596.305 | 1501.475 | 1515.25 | 1560.49 | 1582.53 | 1473.49 | 1675.33 | 1568.265 | 1522.2 | 1547.15 | 1558.46 | 1622.26 | 1512.93 | 1622.38 | 1553.53 | 2199.07 | 2404.53 | 2126.86 | 2180.99 | 2391.4 | 1474.505 | 2181.09 | 2227.96 | 2149.95 | 2201.1 | 2181.09 | 2212.7 | 1818.3 | 1898.05 | 1834.25 | 1866.1 | 1802.35 | 1914 | 1882.1 | 1850.2 | 1485.67 | 1485.67 | 1485.67 | 1485.67 | 1519.6 | 1501.475 | 2133.675 | 2370.75 | 1722.745 | 2117.87
| 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53
Date | IS1Inv1M1 | IS1Inv1M2 | IS1Inv1M3 | IS1Inv1M4 | IS1Inv2M1 | IS1Inv2M2 | IS1Inv2M3 | IS1Inv2M4 | IS2Inv1M1 | IS2Inv1M2 | IS2Inv1M3 | IS2Inv1M4 | IS2Inv2M1 | IS2Inv2M2 | IS2Inv2M3 | IS2Inv2M4 | IS3Inv1M1 | IS3Inv1M2 | IS3Inv2M1 | IS3Inv2M2 | IS4Inv1M1 | IS4Inv1M2 | IS4Inv2M1 | IS4Inv2M2 | IS4Inv3M1 | IS4Inv3M2 | IS4Inv4M1 | IS4Inv4M2 | IS5Inv1M1 | IS5Inv1M2 | IS5Inv2M1 | IS5Inv2M2 | IS6Inv1M1 | IS6Inv1M2 | IS6Inv2M1 | IS6Inv2M2 | IS7Inv1M1 | IS7Inv2M1 | IS8Inv1M1 | IS8Inv1M2 | IS8Inv1M3 | IS8Inv1M4 | IS9Inv1M1 | IS9Inv1M2 | IS9Inv2M1 | IS9Inv2M2 | IS10Inv1M1 | IS10Inv1M2 | IS10Inv2M1 | IS10Inv2M2 | IS10Inv3M1 | IS10Inv3M2 | IS10Inv4M1 | IS10Inv4M2 | IS11Inv1M1 | IS11Inv1M2 | IS11Inv1M3 | IS11Inv1M4 | IS12Inv1M1 | IS12Inv1M2 | IS12Inv1M3 | IS12Inv1M4 | IS13Inv1M1 | IS13Inv1M2 | IS13Inv2M1 | IS13Inv2M2 | IS14Inv1M1 | IS14Inv1M2 | IS14Inv1M3 | IS14Inv1M4 | IS14Inv2M1 | IS14Inv2M2 | IS14Inv2M3 | IS14Inv2M4
2025-06-12 | 0.6874% | 0.1324% | 0.05851% | -1.781% | -2.109% | -1.711% | 0.6509% | 0.03655% | -1.012% | -0.2074% | 3.884% | -0.4395% | 6.539% | -1.595% | -0.6338% | 0.1623% | -1.516% | -2.938% | -0.6127% | 0.06502% | -4.27% | -5.347% | -1.761% | -2.147% | -2.11% | -2.845% | -2.756% | -3.682% | 0.4363% | -1.627% | -2.516% | -3.482% | -1.536% | -1.626% | -2.01% | -1.966% | -0.2168% | 0.2131% | -0.3036% | -1.168% | -0.4685% | -0.4426% | -1.056% | -0.533% | -0.8926% | -2.817% | -10.88% | -7.039% | 3.35% | 11.24% | 7.693% | 6.886% | 4.532% | 6.378% | 9.626% | 5.988% | 7.253% | 9.328% | 5.962% | 8.044% | 6.844% | 7.716% | 8.977% | 7.295% | -0.4303% | 4.179% | -100% | -100% | -100% | -100% | -59.79% | 26.58% | -28.82% | 8.363%
2025-06-13 | 0.9532% | 0.3335% | 1.237% | 1.642% | 1.991% | 1.579% | 3.257% | -0.06233% | 0.07546% | 1.24% | 4.728% | 0.3507% | 7.628% | -1.365% | -0.1575% | 1.843% | -0.4508% | -5.175% | 1.172% | 2.199% | -5.799% | -3.157% | 0.1869% | -0.6927% | -0.6351% | -1.122% | -1.582% | -2.745% | 1.74% | -0.06664% | 1.784% | 2.208% | 1.2% | 2.272% | 0.5538% | 2.304% | 5.704% | 7.145% | 4.929% | 4.044% | 5.81% | 6.53% | 0.7104% | -0.01298% | 3% | 2.342% | -15.66% | -13.19% | -1.314% | 6.37% | 7.659% | -2.117% | -0.2883% | 1.709% | 3.446% | 1.314% | 2.951% | 3.178% | 3.279% | 7.686% | 1.171% | 0.4246% | 4.619% | 3.455% | -2.914% | 1.54% | -100% | -100% | -100% | -100% | -62.33% | 19.27% | -32.68% | 2.751%
2025-06-14 | -1.161% | -0.9653% | -1.89% | -4.19% | -3.112% | -2.623% | -1.299% | -2.492% | -2.689% | -2.197% | 3.833% | 0.05157% | 5.841% | 1.616% | -1.594% | -1.153% | 1.781% | 0.5521% | -0.0479% | 1.495% | -1.119% | 1.38% | 4.584% | 2.744% | 3.499% | 2.991% | 2.951% | 1.881% | 3.124% | 0.09488% | -4.4% | -6.67% | -0.5523% | -2.649% | -1.754% | -3.109% | -4.11% | -4.659% | -3.059% | -4.186% | -4.896% | -5.563% | 0.5373% | -0.2058% | 0.2047% | -4.748% | -13% | -10.33% | -3.468% | 4.542% | -17.33% | -12.03% | 0.6113% | 2.399% | 9.604% | 8.32% | 12.38% | 11.57% | 8.143% | 10.77% | 9.919% | 10.08% | 14.24% | 12.61% | 2.738% | 10.23% | -100% | -100% | -100% | -100% | -57.25% | 34.33% | -24.96% | 13.82%
2025-06-15 | 4.667% | 5.604% | 7.085% | 1.664% | -0.5728% | 1.878% | 5.418% | 1.936% | 0.7005% | -0.9942% | 0.8107% | -2.979% | 7.575% | -9.775% | -0.1364% | 2.373% | -2.983% | -9.288% | 2.185% | 4.1% | -9.133% | -5.641% | -3.93% | -5.467% | -6.52% | -7.294% | -6.29% | -8.485% | -8.364% | -10.71% | -10.69% | -11.45% | -11.28% | -11.91% | -12.41% | -11.84% | -12.95% | -12.42% | -11.91% | -11.92% | -12.51% | -12.65% | -10.81% | -9.72% | -10.84% | -14.46% | -5.995% | -4.045% | 8.69% | 16.95% | 9.485% | 12.39% | 11.58% | 14.07% | 19.01% | 17.68% | 20.74% | 1.632% | 14.91% | 16.2% | 12.97% | 14.48% | 23.07% | 22.42% | 8.719% | 18% | -100% | -100% | -100% | -100% | -54.47% | 43.38% | -19.35% | 19.84%
2025-06-16 | -1.717% | -2.247% | -0.9907% | -2.178% | -2.352% | -2.195% | -0.1914% | -3.823% | -2.712% | -1.819% | 2.673% | -0.9306% | 5.998% | 1.839% | -1.476% | -0.3762% | 1.604% | 0.0736% | 0.4212% | 2.932% | -0.1245% | 5.513% | 7.457% | 3.896% | 4.888% | 4.37% | 6.367% | 2.754% | 7.157% | 4.351% | 3.859% | 2.38% | 4.212% | 3.747% | 3.444% | 3.915% | 1.494% | 1.047% | 1.354% | 0.8229% | 0.01381% | 0.1819% | 3.024% | 0.6504% | 6.01% | 0.4454% | -7.378% | -4.912% | 3.279% | 8.432% | 0.2257% | 1.371% | -0.3132% | 2.725% | 3.386% | 1.525% | 3.332% | 2.378% | 0.7005% | -0.3085% | -0.9985% | 1.211% | 3.986% | 2.934% | -7.739% | -0.3273% | -100% | -100% | -100% | -100% | -64.61% | 9.964% | -34.47% | -0.147%
2025-06-17 | 1.17% | 2.084% | 4.269% | 0.9922% | -0.5913% | -1.263% | 2.803% | -1.828% | 1.356% | 2.58% | 6.759% | 3.01% | 10.25% | 4.93% | 2.888% | 4.702% | 4.917% | 0.6352% | 4.831% | 8.216% | 3.1% | 8.356% | 11.51% | 7.36% | 8.355% | 7.119% | 9.708% | 8.35% | -3.24% | -5.024% | -5.505% | -5.846% | -5.138% | -4.674% | -5.489% | -4.521% | -4.753% | -3.937% | -5.803% | -5.869% | -6.402% | -5.256% | -5.735% | -7.384% | -3.363% | -6.039% | -13.99% | -11.39% | 1.028% | 7.67% | -0.2287% | 1.406% | 0.149% | 2.218% | 6.298% | 4.542% | 6.474% | -9.713% | 3.31% | 4.233% | 1.768% | 2.972% | 9.179% | 7.485% | -2.756% | 5.469% | -100% | -100% | -100% | -100% | -60.35% | 24.75% | -29.09% | 5.975%
2025-06-18 | -0.4984% | -0.9913% | -0.8978% | -1.162% | -0.8193% | -1.8% | 0.1848% | -0.7078% | -0.1173% | 0.9002% | 5.016% | 1.328% | 8.45% | 1.287% | 1.262% | 1.128% | 1.394% | 1.746% | 1.461% | 2.119% | 1.183% | 1.623% | 4.911% | 4.659% | 3.613% | 2.624% | 3.216% | 2.573% | 6.916% | 5.087% | 4.874% | 4.519% | 4.301% | 4.073% | 2.744% | 3.844% | 3.204% | 4.02% | 4.509% | 4.59% | 4.234% | 4.1% | 2.186% | 2.648% | 3.437% | 1.867% | -2.07% | -0.1565% | -1.157% | 5.528% | -0.5065% | 0.6602% | -1.609% | 0.9939% | 0.1298% | -2.594% | -1.608% | -15.88% | 1.814% | -0.009978% | 1.097% | 2.263% | 2.528% | 0.9719% | -8.693% | -0.6366% | -97.44% | -98.97% | -99.5% | -99.26% | -65.87% | 5.667% | -35% | -0.6932%
2025-06-19 | 1.776% | 0.4082% | 1.617% | 1.995% | 2.374% | 1.407% | 3.307% | 0.4125% | 2.043% | 3.742% | 7.405% | 2.766% | 9.823% | 3.134% | 3.365% | 2.263% | 2.413% | 2.086% | 2.623% | 3.551% | 1.611% | 3.466% | 6.406% | 6.38% | 4.934% | 3.659% | 4.877% | 4.011% | 9.595% | 7.312% | 7.087% | 6.177% | 8.266% | 8.781% | 8.328% | 8.899% | 8.377% | 8.649% | 6.934% | 6.152% | 6.365% | 7.373% | 8.983% | 9.546% | 12.31% | 9.707% | 2.559% | 3.366% | 3.036% | 12.35% | 6.84% | 9.314% | 8.585% | 10.88% | 8.035% | 6.969% | 8.156% | -7.618% | 11.36% | 10.03% | 10.42% | 11.52% | 16.6% | 14.8% | 3.149% | 12.46% | -82.63% | -94.4% | -85.35% | -96.21% | -60.03% | 24.94% | -25.02% | 13.2%
2025-06-20 | 3.905% | 3.814% | 5.142% | 3.329% | 2.871% | 1.947% | 4.941% | 1.823% | 2.808% | 4.215% | 7.492% | 3.213% | 11.18% | 3.402% | 4.015% | 5.114% | 3.46% | 0.02431% | 4.798% | 7.033% | -0.5387% | 2.257% | 6.499% | 5.789% | 4.355% | 3.479% | 5.529% | 4.113% | 9.594% | 7.69% | 7.533% | 6.706% | 8.428% | 8.711% | 7.867% | 8.46% | 9.085% | 9.537% | 8.074% | 7.617% | 7.296% | 8.314% | 8.576% | 7.021% | 11.12% | 8.698% | -9.43% | -6.796% | 2.803% | 12.65% | 4.455% | 5.857% | 5.342% | 7.172% | 7.233% | 6.309% | 7.205% | -8.188% | 8.614% | 8.528% | 6.728% | 8.15% | 10.97% | 9.407% | -1.025% | 7.646% | -68.48% | -89.02% | -56.08% | -92.28% | -60.12% | 25.96% | -28.21% | 8.252%
2025-06-21 | 2.502% | 0.9862% | 1.826% | 2.87% | 3.343% | 2.618% | 4.084% | 2.63% | 2.193% | 4.961% | 8.715% | 3.744% | 10.59% | 4.005% | 4.279% | 3.45% | 2.992% | 2.321% | 2.993% | 3.726% | 0.132% | 3.119% | 6.792% | 6.267% | 4.831% | 3.364% | 5.201% | 4.223% | 8.747% | 6.919% | 6.395% | 6.113% | 6.447% | 6.309% | 5.39% | 6.341% | 6.641% | 7.22% | 6.438% | 6.412% | 6.077% | 6.636% | 5.546% | 5.27% | 6.488% | 4.472% | -1.8% | 0.5614% | 2.987% | 10.17% | 3.592% | 5.286% | 4.569% | 7.173% | 6.829% | 4.721% | 6.169% | 9.26% | 9.956% | 8.52% | 9.396% | 10.3% | 11.05% | 9.096% | -0.8255% | 7.812% | -59.46% | -89.1% | -56.7% | -86.97% | -60.26% | 24.61% | -28.15% | 8.581%
2025-06-22 | 2.881% | 2.3% | 2.238% | 1.631% | 1.89% | 1.213% | 3.367% | 1.547% | 3.122% | 4.118% | 7.893% | 3.507% | 10.75% | 3.268% | 3.993% | 3.41% | 3.212% | 4.007% | 4.002% | 4.731% | 1.686% | 3.407% | 7.09% | 6.693% | 5.724% | 4.387% | 5.854% | 4.746% | -1.163% | -1.973% | -2.098% | -2.44% | -2.894% | -2.894% | -4.202% | -3.545% | -4.387% | -3.847% | -3.91% | -3.507% | -4.18% | -4.144% | -5.258% | -4.921% | -4.899% | -6.265% | 4.832% | 5.903% | 5.111% | 13.46% | 7.135% | 10.34% | 10.18% | 11.91% | 12.6% | 7.163% | 12.39% | 11.34% | 14.42% | 10.82% | 12.77% | 14.23% | 15.91% | 14.09% | 5.359% | 12.47% | -46.37% | -83.99% | -25.73% | -51.72% | -60.82% | 21.52% | -24.82% | 13.37%
2025-06-23 | 5.566% | 5.772% | 4.745% | 3.806% | 3.413% | 3.23% | 6.134% | 5.567% | 5.903% | 6.488% | 10.5% | 6.575% | 13.83% | 5.585% | 6.591% | 6.524% | 6.931% | 8.43% | 7.223% | 7.921% | 5.567% | 4.493% | 8.58% | 7.926% | 7.874% | 7.538% | 7.236% | 5.861% | 0.08955% | -1.364% | -2.058% | -2.665% | -2.483% | -2.712% | -3.349% | -2.991% | -3.933% | -3.8% | -3.629% | -2.956% | -4.145% | -4.097% | -3.62% | -2.995% | -4.175% | -5.52% | 6.37% | 8.065% | 3.663% | 11.2% | 4.57% | 6.662% | 6.167% | 8.25% | 6.603% | 0.8192% | 6.208% | 5.226% | 8.448% | 4.987% | 6.552% | 8.554% | 10.27% | 8.804% | 0.3891% | 7.112% | -50.58% | -85.6% | 3.218% | -47.31% | -64.62% | 9.177% | -30.25% | 7.633%
2025-06-24 | -3.791% | -2.402% | -3.736% | -6.702% | -6.943% | -7.547% | -4.697% | -4.325% | -2.969% | -2.919% | 1.421% | -1.406% | 5.413% | -1.562% | -1.578% | -1.432% | 3.51% | 6.079% | 2.679% | 3.61% | 0.4068% | 2.547% | 7.018% | 6.531% | 6.018% | 5.51% | 4.978% | 3.822% | 1.953% | 0.505% | 0.06247% | -0.5039% | 0.005822% | 0.2392% | -0.6136% | 0.07037% | -3.516% | -3.119% | -3.889% | -3.154% | -3.995% | -3.574% | -0.7251% | -0.01808% | -0.2566% | -0.6057% | 11.13% | 12.14% | 6.162% | 13.92% | 7.699% | 10.4% | 10.21% | 12.62% | 8.602% | 2.078% | 8.081% | 7.085% | 10.03% | 6.428% | 8.454% | 10.46% | 14.66% | 13.02% | 3.915% | 11.15% | -48.69% | -87.62% | 8.049% | -38.58% | -69.13% | -7.295% | -29.55% | 10.57%
2025-06-25 | 1.13% | 0.8896% | 0.09625% | 1.051% | 1.29% | 0.4151% | 2.524% | 1.659% | 0.9957% | 2.98% | 6.119% | 1.917% | 8.72% | 0.9525% | 1.97% | 1.255% | 1.379% | 2.844% | 1.768% | 2.187% | 1.113% | -0.4978% | 3.369% | 3.452% | 2.282% | 1.556% | 2.111% | 1.155% | 4.091% | 3.201% | 3.642% | 3.24% | 2.798% | 3.043% | 1.618% | -3.407% | 2.19% | 2.485% | 2.131% | 3.09% | 1.928% | 2.225% | 1.399% | 1.948% | 1.84% | 1.061% | 5.067% | 5.411% | -0.1466% | 7.608% | 2.211% | 5.46% | 5.406% | 7.649% | 7.22% | 1.536% | 7.281% | 6.452% | 3.747% | 5.853% | 7.371% | 9.114% | 13.08% | 11.73% | 2.246% | 9.44% | -45.51% | -84.72% | 9.384% | -36.42% | -62.29% | 16.34% | -27.09% | 11.38%
2025-06-26 | 4.338% | 4.271% | 2.981% | 2.328% | 3.132% | 2.853% | 4.319% | 5.218% | 3.157% | 4.463% | 7.226% | 3.312% | 10.84% | 1.991% | 4.122% | 3.801% | 6.252% | 7.795% | 7.716% | 8.404% | -0.4223% | 1.322% | 6.57% | 7.072% | 6.339% | 5.788% | 6.895% | 5.073% | 7.435% | 6.593% | 6.85% | 6.897% | 6.522% | 7.145% | 6.036% | 1.607% | 3.443% | 4.399% | 2.093% | 3.321% | 2.616% | 3.602% | 6.184% | 7.834% | 8.325% | 8.64% | 5.781% | 7.562% | 2.051% | 8.804% | 3.078% | 5.456% | 4.839% | 6.989% | 0.8418% | -6.227% | -0.9071% | -3.648% | 1.957% | -2.097% | -0.06259% | 2.368% | 4.615% | 3.884% | -3.76% | 1.99% | -92.11% | -100% | -57.13% | -76.12% | -75.88% | -30.71% | -38.7% | -1.669%
2025-06-27 | 3.141% | 2.827% | 2.026% | 0.8325% | 0.9862% | 0.4504% | 2.984% | 2.364% | 3.867% | 3.688% | 6.753% | 2.879% | 11.41% | 2.406% | 3.643% | 3.972% | 1.616% | 1.603% | 3.443% | 3.851% | 1.529% | 1.296% | 3.605% | 5.539% | 3.922% | 2.403% | 4.557% | 2.897% | 4.756% | 4.209% | 3.853% | 2.971% | 4.087% | 4.12% | 3.333% | 0.2848% | 4.263% | 5.093% | 3.256% | 3.247% | 3.158% | 4.138% | 2.616% | 3.618% | 5.566% | 3.987% | -5.761% | -3.537% | -0.8555% | 6.07% | 0.5412% | 3.035% | 3.396% | 5.069% | 6.309% | 0.9581% | 5.271% | 3.549% | 6.529% | 4.925% | 5.107% | 6.33% | 10.42% | 6.65% | 0.9087% | 7.21% | -31.46% | -87.18% | 1.106% | -31.05% | -62.98% | 16.42% | -33.31% | -0.7079%
2025-06-28 | 3.644% | 4.188% | 3.953% | 1.362% | 1.473% | 1.594% | 4.291% | 3.086% | 2.492% | 3.943% | 7.624% | 4.331% | 11% | 2.543% | 3.94% | 4.193% | 4.851% | 3.004% | 4.473% | 5.016% | 2.244% | 4.042% | 4.911% | 4.593% | 5.812% | 5.536% | 4.364% | 2.493% | 4.123% | 2.305% | 1.316% | 1.068% | 1.169% | 0.02558% | -0.05072% | -3.236% | -0.5759% | 0.2433% | -1.248% | -0.1367% | -1.138% | -0.8062% | 0.2159% | -0.1206% | 2.42% | 0.3543% | -2.342% | -0.06113% | 4.711% | 11.75% | 5.203% | 7.037% | 5.011% | 7.922% | 10.04% | 8.511% | 8.539% | 6.784% | 7.013% | 6.196% | 4.656% | 7.838% | 10.05% | 7.825% | 0.2807% | 6.29% | -21.37% | -71.35% | -0.6205% | -24.85% | -66.15% | -71.17% | 5.963% | 5.362%
2025-06-29 | -0.7325% | -1.442% | -2.355% | -1.252% | -0.4841% | -1.088% | 0.2536% | -0.07112% | -1.143% | 0.8326% | 3.253% | -0.5459% | 5.666% | -2.772% | -0.479% | -1.272% | -1.072% | -0.02316% | -0.1588% | 0.2818% | -1.26% | -2.621% | 0.2004% | 2.076% | 0.4616% | -0.4794% | 1.018% | -0.02324% | 10.04% | 9.247% | 9.535% | 8.808% | 9.808% | 10.19% | 9.023% | 4.974% | 9.671% | 10.4% | 8.224% | 7.94% | 8.381% | 9.411% | 9.074% | 11.12% | 12.11% | 11.59% | 0.31% | 1.444% | -3.887% | 2.211% | -2.307% | 0.05507% | -0.3265% | 1.338% | -0.8398% | -3.644% | 0.9953% | -0.1649% | 1.321% | 1.345% | 0.8805% | 1.284% | 1.448% | 0.106% | -6.406% | -0.9551% | -19.61% | -28.7% | -5.641% | -21.13% | -55.64% | -26.06% | -0.3087% | -1.431%
2025-06-30 | 1.237% | 1.128% | -0.1314% | -0.7832% | -0.4643% | -0.7622% | 1.358% | 1.631% | 0.1936% | 1.345% | 3.906% | 0.7018% | 7.048% | -2.169% | 0.6842% | 0.8662% | 0.6659% | 1.525% | 1.495% | 2.143% | -1.253% | -3.182% | -0.569% | 0.4553% | 0.4511% | 0.4019% | 0.1628% | -1.163% | -1.756% | -2.634% | -2.925% | -3.109% | -2.881% | -2.978% | -3.621% | -7.375% | -3.731% | -3.123% | -4.808% | -4.475% | -4.677% | -3.856% | -3.861% | -2.755% | -2.768% | -3.102% | 3.155% | 4.787% | 0.7577% | 0.2299% | 2.492% | 5.297% | 4.331% | 5.857% | 4.673% | 1.865% | 6.822% | 21.04% | 6.946% | 8.307% | 8.366% | 6.827% | 7.214% | 5.306% | -1.099% | 4.223% | 3.63% | -21.22% | 2.022% | 3.333% | -48.13% | -11.19% | 6.628% | 5.04%
2025-07-01 | 2.14% | 1.46% | 0.7997% | 0.3012% | 0.5669% | 0.6379% | 2.718% | 2.397% | 1.515% | 2.397% | 4.855% | 1.706% | 7.889% | -1.506% | 1.43% | 1.749% | 0.73% | 0.8954% | 1.837% | 2.391% | -2.011% | -3.333% | -1.362% | 0.4093% | 0.06064% | -0.225% | 0.04228% | -1.201% | 0.8455% | -0.1829% | -0.4863% | -0.9285% | -0.0254% | -0.05916% | -0.6505% | -4.248% | -0.215% | 0.1628% | -1.682% | -1.102% | -1.61% | -0.8004% | -0.7067% | 0.5744% | 0.7499% | 0.06333% | 1.425% | 2.878% | -0.9633% | -2.824% | 0.5376% | 3.383% | 2.1% | 4.059% | 3.588% | 1.089% | 5.535% | 0.1539% | 4.821% | 5.103% | 5.372% | 4.661% | 1.47% | 2.151% | -4.296% | 4.406% | -0.7112% | -23.2% | -2.799% | -1.76% | -28.04% | -13.31% | 3.386% | 2.802%
2025-07-02 | -0.7813% | -0.6855% | -1.677% | -2.852% | -2.152% | -2.639% | -0.6248% | -0.6775% | -2.124% | -0.574% | 1.938% | -0.8131% | 4.723% | -3.859% | -1.388% | -1.038% | -1.186% | -0.9763% | -0.9009% | -0.255% | -2.89% | -3.506% | -0.5856% | 0.1552% | -1.189% | -1.267% | -1.485% | -2.154% | 3.001% | 0.8349% | -0.09177% | -0.8894% | -8.996% | -10.31% | -9.749% | -31.27% | 1.278% | 1.855% | -24.77% | -24.21% | -25.19% | -24.31% | 0.5878% | 0.4306% | 0.6153% | -0.1546% | -0.6565% | 0.2204% | -2.311% | 1.965% | 1.767% | 5.404% | 3.76% | 6.33% | 8.867% | 6.994% | 12.35% | 11.43% | 9.971% | 12.07% | 11.77% | 10.51% | 8.211% | 9.112% | 2.382% | 10.74% | 5.396% | -10.94% | 4.793% | 9.32% | 4.934% | 19.05% | 10.12% | 9.248%
2025-07-03 | -5.516% | -5.271% | -6.332% | -7.75% | -7.118% | -7.507% | -5.514% | -6.364% | -5.957% | -4.878% | -2.051% | -4.677% | 0.4179% | -6.854% | -5.011% | -4.8% | -4.988% | -4.337% | -4.652% | -3.891% | -3.985% | -4.364% | -1.2% | -1.254% | -2.866% | -3.462% | -3.049% | -3.908% | 4.548% | 2.765% | 2.054% | 0.9856% | 3.065% | 2.457% | 2.469% | 2.423% | 2.169% | 3.216% | 2.405% | 2.146% | 0.9885% | 1.549% | 2.435% | 3.24% | 4.596% | 2.925% | -2.655% | -0.8568% | -1.878% | -8.946% | -1.51% | 1.564% | 0.7978% | 2.698% | 3.18% | 1.087% | 5.784% | 4.905% | 4.657% | 6.141% | 5.682% | 4.591% | 2.132% | 4.216% | -3.57% | 4.666% | 2.519% | 5.537% | 1.727% | 6.44% | 6.516% | 16.22% | 5.28% | 3.773%
2025-07-04 | -0.5933% | -1.444% | -2.359% | -1.596% | -0.4986% | -0.9674% | 0.4921% | 0.1034% | -1.392% | 0.7626% | 2.768% | -0.4594% | 4.505% | -3.334% | -0.8389% | -1.346% | -1.714% | -0.7911% | -1.126% | -0.6618% | -2.79% | -3.142% | 0.3038% | 0.5344% | -0.6674% | -1.126% | -0.6831% | -1.431% | 2.685% | 1.687% | 1.675% | 0.7765% | 1.788% | 1.879% | 1.22% | 1.451% | 1.313% | 1.933% | 2.545% | 1.622% | 1.667% | 1.051% | 0.9235% | 2.329% | 2.149% | 1.516% | 1.593% | 3.253% | -2.564% | -24.7% | -0.3202% | 2.043% | 0.5645% | 2.153% | 0.8719% | -1.717% | 2.428% | 1.464% | 2.746% | 2.279% | 3.57% | 2.679% | -1.519% | 1.168% | -6.019% | 1.714% | -9.102% | 1.481% | -3.147% | 2.324% | 0.4888% | 4.291% | 1.142% | 0.1115%
2025-07-05 | 0.7141% | 1.004% | -0.1576% | -2.569% | -2.197% | -1.872% | 0.737% | -0.8054% | 0.08098% | 0.7379% | 3.117% | 0.7393% | 6.025% | -2.387% | 0.5504% | 1.224% | -7.423% | -6.814% | -6.622% | -5.949% | -0.766% | -1.696% | 1.795% | 1.18% | -34.4% | -34.94% | 0.8163% | -0.366% | 1.991% | 0.7065% | 1.074% | 0.1125% | 1.881% | 2.294% | 1.653% | 2.349% | 1.565% | 2.264% | 2.277% | 1.114% | 1.375% | 1.132% | 1.871% | 4.127% | 4.533% | 3.607% | -0.07166% | 2.256% | -54.05% | -99.68% | 1.58% | 2.599% | 3.541% | 5.339% | 5.156% | 2.731% | 7.443% | 6.614% | 5.947% | 7.494% | 6.949% | 5.954% | 3.746% | 6.838% | -0.5304% | 6.652% | 1.576% | 4.014% | -1.818% | 4.179% | 2.686% | 9.291% | 4.518% | 3.692%
2025-07-06 | 0.2531% | -0.3259% | -0.7683% | -0.3585% | 0.961% | 0.5181% | 1.537% | 0.5225% | -0.9387% | 1.832% | 3.483% | -0.01169% | 4.991% | -2.977% | 0.1143% | -0.1542% | -0.1336% | -0.008823% | 0.7553% | 0.9621% | -2.399% | -2.749% | 0.8585% | 1.396% | -0.7355% | -0.9845% | -0.03737% | -0.6948% | 4.895% | 3.462% | 3.474% | 2.997% | 3.812% | 3.718% | 2.817% | 3.602% | 2.551% | 3.327% | 3.81% | 3.355% | 3.336% | 2.838% | 2.607% | 3.018% | 2.9% | 2.303% | -14.99% | -12.86% | -42.51% | -99.25% | -0.9286% | 1.418% | -0.1858% | 1.945% | 0.6656% | -2.087% | 1.845% | 1.238% | 0.8742% | 1.748% | 2.081% | 1.032% | -0.06494% | 2.02% | -12.25% | 1.843% | -0.0473% | 1.584% | -2.704% | 2.386% | -0.02536% | 1.676% | 1.498% | 1.07%
2025-07-07 | 1.415% | 0.9088% | -0.2197% | -1.032% | -0.03522% | 0.05647% | 1.521% | 1.777% | 0.5869% | 2.274% | 3.972% | 1.171% | 6.11% | -1.873% | 1.108% | 1.193% | 2.777% | 4.205% | 3.832% | 4.425% | 0.9753% | -0.3452% | 3.619% | 3.687% | 2.558% | 2.819% | 3.179% | 2.091% | 2.548% | 1.583% | 1.782% | 1.167% | 1.835% | 2.058% | -0.546% | -7.52% | -1.257% | -0.4927% | 0.1043% | -0.4708% | -0.6501% | -0.9755% | 0.3978% | 1.724% | 1.816% | 2.028% | -36.76% | -34.74% | 1.98% | -12.62% | 2.364% | 5.17% | 4.113% | 6.111% | 2.049% | -1.744% | 3.689% | 2.648% | 2.929% | 3.636% | 4.287% | 3.363% | 4.818% | 4.878% | -5.753% | 4.663% | -0.8057% | 1.186% | -4.637% | 1.673% | -4.884% | -18.32% | 1.173% | 1.658%
2025-07-08 | -0.05677% | -0.4485% | -1.797% | -3.024% | -2% | -1.696% | -0.1296% | 0.3658% | -1.168% | 0.07713% | 1.426% | -1.117% | 3.621% | -4.481% | -1.052% | -0.4994% | -0.1373% | 1.019% | 1.376% | 2.001% | -3.009% | -3.918% | 0.01298% | 0.08797% | -1.06% | -0.6715% | -0.3206% | -1.426% | -1.974% | -2.674% | -1.998% | -2.544% | -2.178% | -1.788% | -2.819% | -6.96% | -4.319% | -3.603% | -3.087% | -3.749% | -3.867% | -4.118% | -3.25% | -1.685% | -4.812% | -1.575% | 5.905% | 3.931% | -26.3% | 1.673% | 2.5% | 6.454% | 3.469% | 7.068% | 3.789% | 0.6852% | 5.687% | 4.551% | 5.901% | 6.684% | 7.154% | 5.898% | 7.37% | 5.857% | -4.868% | 6.7% | 2.307% | 4.685% | 0.1445% | 5.872% | 1.112% | -7.032% | 3.927% | 3.901%
2025-07-09 | -0.5626% | -0.8007% | -2.093% | -3.165% | -2.098% | -2.039% | -1.509% | -0.2134% | -1.428% | 0.3098% | 1.771% | -0.8196% | 3.416% | -3.931% | -0.9727% | -0.6907% | -0.2308% | 1.239% | 0.9217% | 1.513% | -1.751% | -2.591% | 1.359% | 1.622% | 0.1644% | 0.03033% | 0.8% | -0.1411% | 0.9789% | 0.164% | 0.7448% | 0.06067% | 0.7647% | 1.208% | 0.02351% | -2.243% | -0.8411% | -0.07696% | 0.3822% | -0.4345% | -0.4712% | -0.6536% | -0.2842% | 1.455% | 1.8% | 1.817% | 2.61% | -1.608% | -2.114% | 5.389% | -1.229% | 2.485% | 1.591% | 3.279% | 0.6193% | -2.519% | 2.655% | 1.505% | 1.981% | 2.676% | 3.264% | 2.193% | 3.286% | 2.357% | -8.459% | 2.485% | -1.597% | 0.7499% | -4.494% | 1.738% | -2.984% | -8.928% | 0.2638% | 0.2991%
2025-07-10 | -0.9654% | -1.231% | -2.228% | -3.602% | -2.354% | -2.166% | -0.5952% | -0.2826% | -4.168% | -0.289% | 0.9496% | -1.481% | 2.685% | -4.628% | -1.696% | -1.455% | -1.428% | -0.07494% | -0.4782% | 0.1567% | -4.36% | -4.348% | -0.3517% | -0.1124% | -0.6018% | -1.5% | -0.869% | -1.788% | -2.435% | -2.935% | -2.138% | -2.821% | -2.347% | -1.837% | -3.163% | -9.892% | -3.208% | -2.394% | -2.054% | -2.907% | -2.872% | -3.028% | -3.372% | -1.926% | -1.779% | -1.452% | 3.84% | 4.971% | -0.1676% | 6.87% | 0.4705% | 4.412% | 3.256% | 3.498% | 2.704% | 0.1788% | 4.822% | 1.889% | 5.196% | 6.008% | 6.386% | 5.026% | 5.723% | 4.499% | -4.701% | 5.124% | 1.547% | 3.945% | -0.4915% | 5.302% | 2.351% | 2.067% | 3.6% | 3.495%
2025-07-11 | 2.235% | 1.354% | 2.336% | 1.321% | -2.548% | -3.242% | 1.072% | -2.706% | 1.297% | 3.444% | 4.948% | 2.346% | 7.941% | -0.1025% | 2.575% | 3.959% | 2.221% | -1.127% | 2.98% | 2.339% | -2.668% | -0.649% | 0.8255% | 0.7423% | 1.807% | 1.395% | 0.6333% | -0.5107% | 2.8% | 1.237% | 2.181% | 0.8284% | 2.827% | 2.992% | 1.033% | -0.8387% | 2.42% | 2.781% | 3.444% | -1.263% | 1.903% | 1.809% | 2.41% | 1.121% | 5.205% | 2.627% | -14.02% | -11.67% | -3.016% | 3.068% | -5.415% | -3.415% | -3.312% | -2.887% | -1.987% | -3.826% | -1.498% | -2.036% | -1.938% | -0.5752% | -2.568% | -2.254% | -3.14% | -4.26% | -12.57% | -3.409% | -2.01% | 0.2039% | -2.891% | 2.084% | 2.793% | 15.59% | -0.6155% | -4.156%
2025-07-12 | -5.074% | -5.04% | -5.318% | -5.573% | -5.702% | -6.408% | -4.303% | -5.219% | -7.144% | -3.323% | -2.013% | -4.685% | -0.8024% | -7.01% | -4.622% | -4.203% | -5.598% | -5.158% | -4.79% | -4.492% | -7.119% | -3.499% | -1.922% | -1.589% | -2.818% | -4.796% | -2.517% | -3.255% | 0.8463% | -0.641% | 0.7026% | -0.2068% | 0.4108% | 0.559% | -0.7817% | -0.363% | -0.002031% | 0.6544% | 1.541% | -3.499% | 0.3525% | 0.0747% | -1.812% | -1.675% | 0.7592% | -0.1757% | -4.368% | -2.197% | -2.099% | 5.069% | -3.138% | 0.5242% | 2.867% | 2.754% | 4.402% | 2.074% | 7.229% | 6.322% | 6.719% | 8.18% | 7.479% | 6.137% | 7.14% | 6.03% | -6.239% | 6.433% | 5.719% | 7.611% | 2.374% | 5.842% | 9.318% | 20.32% | 8.124% | 6.627%
2025-07-13 | 1.259% | 1.091% | -0.4819% | -1.696% | -1.961% | -1.543% | 0.6723% | 1.555% | -2.07% | 0.7521% | 1.878% | -0.2519% | 3.914% | -4.05% | 0.1941% | 1.6% | -0.5068% | -0.04451% | 1.036% | 1.628% | -5.403% | -3.542% | 0.3627% | 0.4131% | -0.202% | -1.46% | -0.5476% | -1.157% | -3.962% | -5.56% | -4.878% | -5.73% | -4.859% | -4.819% | -6.325% | -11.69% | -5.413% | -4.862% | -3.973% | -9.663% | -5.088% | -5.577% | -6.144% | -5.314% | -5.389% | -6.099% | -0.6071% | 1.361% | 0.4086% | 7.141% | -0.4865% | 2.958% | 3.639% | 2.936% | 4.113% | 1.83% | 6.351% | 5.377% | 6.576% | 7.286% | 7.425% | 6.381% | 5.081% | 2.986% | -3.888% | 4.682% | 3.071% | 5.669% | 0.9615% | 4.783% | 6.294% | 12.98% | 4.557% | 4.031%
2025-07-14
2025-07-15
2025-07-16
2025-07-17
2025-07-18
2025-07-19
2025-07-20
2025-07-21
2025-07-22
2025-07-23
2025-07-24
2025-07-25
2025-07-26
2025-07-27
2025-07-28
2025-07-29
2025-07-30
2025-07-31
2025-08-01
2025-08-02
2025-08-03
Formulas:
Date = [Date, row above]+1

## SPV Group
Sr. No. | Block No. | CEPL-MH-O2RE-XV_PH2_18.75MW | CEPL-MH-O2RE-XV_PH1_17.60MW
1 |  | ICR3 | ICR1
2 |  | ICR4 | ICR2 | 8.8 | 3.125
|  |  |  | 17.6 | 18.75
[6 empty] | 10000 | 200 | 0.98039

## IGA_BD
Sr. No. | Date | Finacial Year | Calendor Year | Operating Year | Affected Feeder | SPV | Consumer | Plant Equivalent Weightage | Breakdown Description | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost POA(kWh/m2) | Estimated Energy Loss (kWh)
1 |  | 1900 | 1900 | Year_1
2 |  | 1900 | 1900 | Year_1
3 |  | 1900 | 1900 | Year_1
4 |  | 1900 | 1900 | Year_1
5 |  | 1900 | 1900 | Year_1
6 |  | 1900 | 1900 | Year_1
7 |  | 1900 | 1900 | Year_1
8 |  | 1900 | 1900 | Year_1
9 |  | 1900 | 1900 | Year_1
10 |  | 1900 | 1900 | Year_1
11 |  | 1900 | 1900 | Year_1
12 |  | 1900 | 1900 | Year_1
13 |  | 1900 | 1900 | Year_1
14 |  | 1900 | 1900 | Year_2
15 |  | 1900 | 1900 | Year_2
16 |  | 1900 | 1900 | Year_2
17 |  | 1900 | 1900 | Year_2
18 |  | 1900 | 1900 | Year_2
19 |  | 1900 | 1900 | Year_2

## Basic Data
Description | Value | Inverter Station | Inverter | Module | SCB | String Type | Equipment | Equpiment No.. | Generator | Consumer | Capacity | % Plant Equiva. Weightage | USS YARD | METERING YARD | FEEDER | OG | TRANSFER | Fault Category Plant BD sheet | Status | SPV | AC | DC | % of Total | Line
Total Solar Capacity | 121155 | IS1 | Inv1 | M1 | SCB1 | Str_Typ1(540*29) | Tx | IS1Inv1M1 | O2R15 | Cosmos | 1596.305 | 1.318% | NA |  | F3 | Line1 | TX1 | Module | Open | O2R6 | 2.2 | 2.97 | 2.451% | Line1
|  | IS2 | Inv2 | M2 | SCB2 | Str_Typ2(545*29) | MVP | IS1Inv1M2 | O2R15 | Cosmos | 1596.305 | 1.318% | NA |  | F3 | Line1 | TX1 | Cables | Close | O2R11 | 5.45 | 7.385 | 6.095%
|  | IS3 | Inv3 | M3 | SCB3 | Str_Typ3(550*29) | Aux_Tx | IS1Inv1M3 | O2R15 | Cosmos | 1501.475 | 1.239% | NA |  | F3 | Line1 | TX1 | String Fuses |  | O2R12 | 10.65 | 14.36 | 11.85%
|  | IS4 | Inv4 | M4 | SCB4 | Str_Typ4(540*58) | MCR_MVP_SolarF3 | IS1Inv1M4 | O2R15 | Cosmos | 1515.25 | 1.251% | NA |  | F3 | Line1 | TX1 | SCB |  | O2R15 | 36.35 | 50.33 | 41.54%
|  | IS5 | Inv5 |  | SCB5 | Str_Typ5(545*58) | MCR_MVP_SolarF4 | IS1Inv2M1 | O2R15 | Cosmos | 1560.49 | 1.288% | NA |  | F3 | Line1 | TX1 | Inverter |  | O2R17 | 5.55 | 7.5 | 6.19%
|  | IS6 | Inv6 |  | SCB6 | Str_Typ6(550*58) | MCR_MVP_SolarF5 | IS1Inv2M2 | O2R15 | Cosmos | 1582.53 | 1.306% | NA |  | F3 | Line1 | TX1 | IDT |  | O2R14 | 25.7 | 26.16 | 21.59%
|  | IS7 | Inv7 |  | SCB7 |  | MCR_MVP_SolarF6 | IS1Inv2M3 | O2R15 | Cosmos | 1473.49 | 1.216% | NA |  | F3 | Line1 | TX1 | PTR |  | O2R24 | 4.4 | 6.2 | 5.117%
|  | IS8 | Inv8 |  | SCB8 |  | Power_TX | IS1Inv2M4 | O2R15 | Cosmos | 1675.33 | 1.383% | NA |  | F3 | Line1 | TX1 | MV Panel |  | O2R26 | 5.33 | 6.25 | 5.159%
|  | IS9 | Inv9 |  | SCB9 |  | Power_Tx2 | IS2Inv1M1 | O2R15 | Cosmos | 1568.265 | 1.294% | NA |  | F3 | Line1 | TX1 | Metering System Plant |  | Total | 95.63 | 121.155 | 100%
|  | IS10 | Inv10 |  | SCB10 |  | Line_Bay1 | IS2Inv1M2 | O2R15 | Cosmos | 1522.2 | 1.256% | NA |  | F3 | Line1 | TX1 | Grid System
|  | IS11 | Inv11 |  | SCB11 |  |  | IS2Inv1M3 | O2R15 | Cosmos | 1547.15 | 1.277% | NA |  | F3 | Line1 | TX1 | Metering System Grid
|  | IS12 | Inv12 |  |  |  |  | IS2Inv1M4 | O2R15 | Cosmos | 1558.46 | 1.286% | NA |  | F3 | Line1 | TX1 | WMS
|  | IS13 | Inv13 |  |  |  |  | IS2Inv2M1 | O2R15 | Cosmos | 1622.26 | 1.339% | NA |  | F3 | Line1 | TX1 | MMS
|  | IS14 | Inv14 |  |  |  |  | IS2Inv2M2 | O2R15 | Cosmos | 1512.93 | 1.249% | NA |  | F3 | Line1 | TX1 | Battery Charger_MCR
|  | IS15 | Inv15 |  |  |  |  | IS2Inv2M3 | O2R15 | Cosmos | 1622.38 | 1.339% | NA |  | F3 | Line1 | TX1 | IC_UPS
|  |  | Inv16 |  |  |  |  | IS2Inv2M4 | O2R15 | Cosmos | 1553.53 | 1.282% | NA |  | F3 | Line1 | TX1 | IC_Auxiliary Tranformer
|  |  | Inv17 |  |  |  |  | IS3Inv1M1 | O2R15 | Cosmos | 2199.07 | 1.815% | NA |  | F4 | Line1 | TX1 | IC_Auxiliary DB
|  |  | Inv18 |  |  |  |  | IS3Inv1M2 | O2R15 | Cosmos | 2404.53 | 1.985% | NA |  | F4 | Line1 | TX1 | IC_SCADA Panel
|  |  | Inv19 |  |  |  |  | IS3Inv2M1 | O2R15 | Cosmos | 2126.86 | 1.755% | NA |  | F4 | Line1 | TX1 | Connectors
|  |  | Inv20 |  |  |  |  | IS3Inv2M2 | O2R15 | Cosmos | 2180.99 | 1.8% | NA |  | F4 | Line1 | TX1 | Tranformer
|  |  | Inv21 |  |  |  |  | IS4Inv1M1 | O2R15 | Cosmos | 2391.4 | 1.974% | NA |  | F4 | Line1 | TX1
|  |  | Inv22 |  |  |  |  | IS4Inv1M2 | O2R15 | Cosmos | 1474.505 | 1.217% | NA |  | F4 | Line1 | TX1
|  |  | Inv23 |  |  |  |  | IS4Inv2M1 | O2R15 | Cosmos | 2181.09 | 1.8% | NA |  | F4 | Line1 | TX1
|  |  | Inv24 |  |  |  |  | IS4Inv2M2 | O2R15 | Cosmos | 2227.96 | 1.839% | NA |  | F4 | Line1 | TX1
|  |  | Inv25 |  |  |  |  | IS4Inv3M1 | O2R15 | Cosmos | 2149.95 | 1.775% | NA |  | F4 | Line1 | TX1
|  |  | Inv26 |  |  |  |  | IS4Inv3M2 | O2R15 | Cosmos | 2201.1 | 1.817% | NA |  | F4 | Line1 | TX1
|  |  | Inv27 |  |  |  |  | IS4Inv4M1 | O2R15 | Cosmos | 2181.09 | 1.8% | NA |  | F4 | Line1 | TX1
|  |  | Inv28 |  |  |  |  | IS4Inv4M2 | O2R15 | Cosmos | 2212.7 | 1.826% | NA |  | F4 | Line1 | TX1
|  |  | Inv29 |  |  |  |  | IS5Inv1M1 | O2R11 | NSIGTPL | 1818.3 | 1.501% | NA |  | F5 | Line1 | TX1
|  |  | Inv30 |  |  |  |  | IS5Inv1M2 | O2R11 | NSIGTPL | 1898.05 | 1.567% | NA |  | F5 | Line1 | TX1
[8 empty] | IS5Inv2M1 | O2R11 | NSIGTPL | 1834.25 | 1.514% | NA |  | F5 | Line1 | TX1
[8 empty] | IS5Inv2M2 | O2R11 | NSIGTPL | 1866.1 | 1.54% | NA |  | F5 | Line1 | TX1
[8 empty] | IS6Inv1M1 | O2R17 | NSICTPL | 1802.35 | 1.488% | NA |  | F5 | Line1 | TX1
[8 empty] | IS6Inv1M2 | O2R17 | NSICTPL | 1914 | 1.58% | NA |  | F5 | Line1 | TX1
[8 empty] | IS6Inv2M1 | O2R17 | NSICTPL | 1882.1 | 1.553% | NA |  | F5 | Line1 | TX1
[8 empty] | IS6Inv2M2 | O2R17 | NSICTPL | 1850.2 | 1.527% | NA |  | F5 | Line1 | TX1
[8 empty] | IS7Inv1M1 | O2R6 | BMCT | 1485.67 | 1.226% | NA |  | F5 | Line1 | TX1
[8 empty] | IS7Inv2M1 | O2R6 | BMCT | 1485.67 | 1.226% | NA |  | F5 | Line1 | TX1
[8 empty] | IS8Inv1M1 | O2R12 | GTIPL | 1485.67 | 1.226% | NA |  | F5 | Line1 | TX1
[8 empty] | IS8Inv1M2 | O2R12 | GTIPL | 1485.67 | 1.226% | NA |  | F5 | Line1 | TX1
[8 empty] | IS8Inv1M3 | O2R12 | GTIPL | 1519.6 | 1.254% | NA |  | F5 | Line1 | TX1
[8 empty] | IS8Inv1M4 | O2R12 | GTIPL | 1501.475 | 1.239% | NA |  | F5 | Line1 | TX1
[8 empty] | IS9Inv1M1 | O2R12 | GTIPL | 2133.675 | 1.761% | NA |  | F5 | Line1 | TX1
[8 empty] | IS9Inv1M2 | O2R12 | GTIPL | 2370.75 | 1.957% | NA |  | F5 | Line1 | TX1
[8 empty] | IS9Inv2M1 | O2R12 | GTIPL | 1722.745 | 1.422% | NA |  | F5 | Line1 | TX1
[8 empty] | IS9Inv2M2 | O2R12 | GTIPL | 2117.87 | 1.748% | NA |  | F5 | Line1 | TX1
[8 empty] | IS1Inv1 | O2R15 |  | 6209.335 | 5.125% | NA |  | F3 | Line1 | TX1
[8 empty] | IS1Inv2 | O2R15 |  | 6291.84 | 5.193% | NA |  | F3 | Line1 | TX1
[8 empty] | IS2Inv1 | O2R15 |  | 6196.075 | 5.114% | NA |  | F3 | Line1 | TX1
[8 empty] | IS2Inv2 | O2R15 |  | 6311.1 | 5.209% | NA |  | F3 | Line1 | TX1
[8 empty] | IS3Inv1 | O2R15 |  | 4603.6 | 3.8% | NA |  | F4 | Line1 | TX1
[8 empty] | IS3Inv2 | O2R15 |  | 4307.85 | 3.556% | NA |  | F4 | Line1 | TX1
[8 empty] | IS4Inv1 | O2R15 |  | 3865.905 | 3.191% | NA |  | F4 | Line1 | TX1
[8 empty] | IS4Inv2 | O2R15 |  | 4409.05 | 3.639% | NA |  | F4 | Line1 | TX1
[8 empty] | IS4Inv3 | O2R15 |  | 4351.05 | 3.591% | NA |  | F4 | Line1 | TX1
[8 empty] | IS4Inv4 | O2R15 |  | 4393.79 | 3.627% | NA |  | F4 | Line1 | TX1
[8 empty] | IS5Inv1 | O2R11 |  | 3716.35 | 3.067% | NA |  | F5 | Line1 | TX1
[8 empty] | IS5Inv2 | O2R11 |  | 3700.35 | 3.054% | NA |  | F5 | Line1 | TX1
[8 empty] | IS6Inv1 | O2R17 |  | 3716.35 | 3.067% | NA |  | F5 | Line1 | TX1
[8 empty] | IS6Inv2 | O2R17 |  | 3732.3 | 3.081% | NA |  | F5 | Line1 | TX1
[8 empty] | IS7Inv1 | O2R6 |  | 1485.67 | 1.226% | NA |  | F5 | Line1 | TX1
[8 empty] | IS7Inv2 | O2R6 |  | 1485.67 | 1.226% | NA |  | F5 | Line1 | TX1
[8 empty] | IS8Inv1 | O2R12 |  | 5992.415 | 4.946% | NA |  | F5 | Line1 | TX1
[8 empty] | IS9Inv1 | O2R12 |  | 4504.425 | 3.718% | NA |  | F5 | Line1 | TX1
[8 empty] | IS9Inv2 | O2R12 |  | 3840.615 | 3.17% | NA |  | F5 | Line1 | TX1
[8 empty] | IS1Inv1M1SCB1 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M1SCB2 |  |  | 237.075 | 0.1957% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M1SCB3 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M1SCB4 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M1SCB5 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M1SCB6 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M2SCB1 |  |  | 268.685 | 0.2218% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M2SCB2 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M2SCB3 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M2SCB4 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M2SCB5 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M2SCB6 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M3SCB1 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M3SCB2 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M3SCB3 |  |  | 268.685 | 0.2218% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M3SCB4 |  |  | 189.66 | 0.1565% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M3SCB5 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M3SCB6 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M4SCB1 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M4SCB2 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M4SCB3 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M4SCB4 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M4SCB5 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv1M4SCB6 |  |  | 271.15 | 0.2238% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M1SCB1 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M1SCB2 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M1SCB3 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M1SCB4 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M1SCB5 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M1SCB6 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M2SCB1 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M2SCB2 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M2SCB3 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M2SCB4 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M2SCB5 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M2SCB6 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M3SCB1 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M3SCB2 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M3SCB3 |  |  | 207.35 | 0.1711% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M3SCB4 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M3SCB5 |  |  | 191.4 | 0.158% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M3SCB6 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M4SCB1 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M4SCB2 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M4SCB3 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M4SCB4 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M4SCB5 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS1Inv2M4SCB6 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M1SCB1 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M1SCB2 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M1SCB3 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M1SCB4 |  |  | 268.685 | 0.2218% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M1SCB5 |  |  | 252.2 | 0.2082% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M1SCB6 |  |  | 252.2 | 0.2082% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M2SCB1 |  |  | 252.2 | 0.2082% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M2SCB2 |  |  | 252.2 | 0.2082% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M2SCB3 |  |  | 252.2 | 0.2082% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M2SCB4 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M2SCB5 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M2SCB6 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M3SCB1 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M3SCB2 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M3SCB3 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M3SCB4 |  |  | 271.15 | 0.2238% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M3SCB5 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M3SCB6 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M4SCB1 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M4SCB2 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M4SCB3 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M4SCB4 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M4SCB5 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv1M4SCB6 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M1SCB1 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M1SCB2 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M1SCB3 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M1SCB4 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M1SCB5 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M1SCB6 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M2SCB1 |  |  | 239.25 | 0.1975% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M2SCB2 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M2SCB3 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M2SCB4 |  |  | 271.15 | 0.2238% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M2SCB5 |  |  | 271.15 | 0.2238% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M2SCB6 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M3SCB1 |  |  | 284.9 | 0.2352% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M3SCB2 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M3SCB3 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M3SCB4 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M3SCB5 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M3SCB6 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M4SCB1 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M4SCB2 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M4SCB3 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M4SCB4 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M4SCB5 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS2Inv2M4SCB6 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M1SCB1 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M1SCB2 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M1SCB3 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M1SCB4 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M1SCB5 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M1SCB6 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M1SCB7 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M1SCB8 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M1SCB9 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M2SCB1 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M2SCB2 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M2SCB3 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M2SCB4 |  |  | 221.7 | 0.183% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M2SCB5 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M2SCB6 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M2SCB7 |  |  | 271.15 | 0.2238% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M2SCB8 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv1M2SCB9 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M1SCB1 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M1SCB2 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M1SCB3 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M1SCB4 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M1SCB5 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M1SCB6 |  |  | 158.05 | 0.1305% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M1SCB7 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M1SCB8 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M1SCB9 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M2SCB1 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M2SCB2 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M2SCB3 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M2SCB4 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M2SCB5 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M2SCB6 |  |  | 221.17 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M2SCB7 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M2SCB8 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS3Inv2M2SCB9 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M1SCB1 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M1SCB2 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M1SCB3 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M1SCB4 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M1SCB5 |  |  | 286 | 0.2361% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M1SCB6 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M1SCB7 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M1SCB8 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M1SCB9 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M2SCB1 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M2SCB2 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M2SCB3 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M2SCB4 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M2SCB5 |  |  | 189.66 | 0.1565% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M2SCB6 |  |  | 205.465 | 0.1696% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M2SCB7 |  |  | 0 | 0% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M2SCB8 |  |  | 0 | 0% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv1M2SCB9 |  |  | 0 | 0% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M1SCB1 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M1SCB2 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M1SCB3 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M1SCB4 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M1SCB5 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M1SCB6 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M1SCB7 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M1SCB8 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M1SCB9 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M2SCB1 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M2SCB2 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M2SCB3 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M2SCB4 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M2SCB5 |  |  | 220.725 | 0.1822% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M2SCB6 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M2SCB7 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M2SCB8 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv2M2SCB9 |  |  | 268.685 | 0.2218% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M1SCB1 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M1SCB2 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M1SCB3 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M1SCB4 |  |  | 287.1 | 0.237% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M1SCB5 |  |  | 220.55 | 0.182% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M1SCB6 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M1SCB7 |  |  | 254.65 | 0.2102% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M1SCB8 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M1SCB9 |  |  | 207.35 | 0.1711% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M2SCB1 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M2SCB2 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M2SCB3 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M2SCB4 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M2SCB5 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M2SCB6 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M2SCB7 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M2SCB8 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv3M2SCB9 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M1SCB1 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M1SCB2 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M1SCB3 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M1SCB4 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M1SCB5 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M1SCB6 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M1SCB7 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M1SCB8 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M1SCB9 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M2SCB1 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M2SCB2 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M2SCB3 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M2SCB4 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M2SCB5 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M2SCB6 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M2SCB7 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M2SCB8 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS4Inv4M2SCB9 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M1SCB1 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M1SCB2 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M1SCB3 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M1SCB4 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M1SCB5 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M1SCB6 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M1SCB7 |  |  | 191.4 | 0.158% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M1SCB8 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M2SCB1 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M2SCB2 |  |  | 239.25 | 0.1975% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M2SCB3 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M2SCB4 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M2SCB5 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M2SCB6 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M2SCB7 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv1M2SCB8 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M1SCB1 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M1SCB2 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M1SCB3 |  |  | 239.25 | 0.1975% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M1SCB4 |  |  | 239.25 | 0.1975% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M1SCB5 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M1SCB6 |  |  | 207.35 | 0.1711% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M1SCB7 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M1SCB8 |  |  | 191.4 | 0.158% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M2SCB1 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M2SCB2 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M2SCB3 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M2SCB4 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M2SCB5 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M2SCB6 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M2SCB7 |  |  | 207.3 | 0.1711% | NA |  |  | Line1 | TX1
[8 empty] | IS5Inv2M2SCB8 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M1SCB1 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M1SCB2 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M1SCB3 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M1SCB4 |  |  | 271.15 | 0.2238% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M1SCB5 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M1SCB6 |  |  | 207.35 | 0.1711% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M1SCB7 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M1SCB8 |  |  | 207.35 | 0.1711% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M2SCB1 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M2SCB2 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M2SCB3 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M2SCB4 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M2SCB5 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M2SCB6 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M2SCB7 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv1M2SCB8 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M1SCB1 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M1SCB2 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M1SCB3 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M1SCB4 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M1SCB5 |  |  | 191.4 | 0.158% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M1SCB6 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M1SCB7 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M1SCB8 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M2SCB1 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M2SCB2 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M2SCB3 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M2SCB4 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M2SCB5 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M2SCB6 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M2SCB7 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS6Inv2M2SCB8 |  |  | 223.3 | 0.1843% | NA |  |  | Line1 | TX1
[8 empty] | IS7Inv1M1SCB1 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS7Inv1M1SCB2 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS7Inv1M1SCB3 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS7Inv1M1SCB4 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS7Inv1M1SCB5 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS7Inv1M1SCB6 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS7Inv2M1SCB1 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS7Inv2M1SCB2 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS7Inv2M1SCB3 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS7Inv2M1SCB4 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS7Inv2M1SCB5 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS7Inv2M1SCB6 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M1SCB1 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M1SCB2 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M1SCB3 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M1SCB4 |  |  | 237.075 | 0.1957% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M1SCB5 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M1SCB6 |  |  | 268.685 | 0.2218% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M2SCB1 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M2SCB2 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M2SCB3 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M2SCB4 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M2SCB5 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M2SCB6 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M3SCB1 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M3SCB2 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M3SCB3 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M3SCB4 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M3SCB5 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M3SCB6 |  |  | 255.2 | 0.2106% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M4SCB1 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M4SCB2 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M4SCB3 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M4SCB4 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M4SCB5 |  |  | 237.075 | 0.1957% | NA |  |  | Line1 | TX1
[8 empty] | IS8Inv1M4SCB6 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M1SCB1 |  |  | 189.66 | 0.1565% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M1SCB2 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M1SCB3 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M1SCB4 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M1SCB5 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M1SCB6 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M1SCB7 |  |  | 237.075 | 0.1957% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M1SCB8 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M1SCB9 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M2SCB1 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M2SCB2 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M2SCB3 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M2SCB4 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M2SCB5 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M2SCB6 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M2SCB7 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M2SCB8 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv1M2SCB9 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M1SCB1 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M1SCB2 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M1SCB3 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M1SCB4 |  |  | 284.49 | 0.2348% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M1SCB5 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M1SCB6 |  |  | 0 | 0% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M1SCB7 |  |  | 94.83 | 0.07827% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M1SCB8 |  |  | 173.855 | 0.1435% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M1SCB9 |  |  | 189.66 | 0.1565% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M2SCB1 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M2SCB2 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M2SCB3 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M2SCB4 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M2SCB5 |  |  | 221.27 | 0.1826% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M2SCB6 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M2SCB7 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M2SCB8 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS9Inv2M2SCB9 |  |  | 252.88 | 0.2087% | NA |  |  | Line1 | TX1
[8 empty] | IS1Tx | O2R15 | Cosmos | 12501.175 | 10.32% | NA |  |  | Line1 | TX1
[8 empty] | IS2Tx | O2R15 | Cosmos | 12507.175 | 10.32% | NA |  |  | Line1 | TX1
[8 empty] | IS3Tx | O2R15 | Cosmos | 8911.45 | 7.355% | NA |  |  | Line1 | TX1
[8 empty] | IS4Tx | O2R15 | Cosmos | 17019.795 | 14.05% | NA |  |  | Line1 | TX1
[8 empty] | IS5Tx |  |  | 7416.7 | 6.122% | NA |  |  | Line1 | TX1
[8 empty] | IS6Tx |  |  | 7448.65 | 6.148% | NA |  |  | Line1 | TX1
[8 empty] | IS7Tx |  |  | 2971.34 | 2.453% | NA |  |  | Line1 | TX1
[8 empty] | IS8Tx |  |  | 5992.415 | 4.946% | NA |  |  | Line1 | TX1
[8 empty] | IS9Tx |  |  | 8345.04 | 6.888% | NA |  |  | Line1 | TX1
[8 empty] | IS1VCB |  |  | 12501.175 | 10.32% | NA |  |  | Line1 | TX1
[8 empty] | IS2VCB |  |  | 12507.175 | 10.32% | NA |  |  | Line1 | TX1
[8 empty] | IS3VCB |  |  | 8911.45 | 7.355% | NA |  |  | Line1 | TX1
[8 empty] | IS4VCB |  |  | 17019.795 | 14.05% | NA |  |  | Line1 | TX1
[8 empty] | IS5VCB |  |  | 7416.7 | 6.122% | NA |  |  | Line1 | TX1
[8 empty] | IS6VCB |  |  | 7448.65 | 6.148% | NA |  |  | Line1 | TX1
[8 empty] | IS7VCB |  |  | 2971.34 | 2.453% | NA |  |  | Line1 | TX1
[8 empty] | IS8VCB |  |  | 5992.415 | 4.946% | NA |  |  | Line1 | TX1
[8 empty] | IS9VCB |  |  | 8345.04 | 6.888% | NA |  |  | Line1 | TX1
[8 empty] | SolarF3Iso | O2R15 | Cosmos | 25008.35 | 20.64% | NA |  |  | Line1 | TX1
[8 empty] | SolarF4Iso | O2R15 | Cosmos | 25931.245 | 21.4% | NA |  |  | Line1 | TX1
[8 empty] | SolarF5Iso |  |  | 32174.145 | 26.56% | NA |  |  | Line1 | TX1
[8 empty] | MCR_MVP_SolarF3 | O2R15 | Cosmos | 25008.35 | 20.64% | NA |  |  | Line1 | TX1
[8 empty] | MCR_MVP_SolarF4 | O2R15 | Cosmos | 25931.245 | 21.4% | NA |  |  | Line1 | TX1
[8 empty] | MCR_MVP_SolarF5 |  |  | 32174.145 | 26.56% | NA |  |  | Line1 | TX1
[8 empty] | OG | O2R15 | Cosmos | 83113.74 | 68.6% | NA |  |  | Line1 | TX1
[8 empty] | Power_TX | O2R15 | Cosmos | 122106 | 100.8% | NA |  |  | Line1 | TX1
[8 empty] | Line_Bay1 | O2R15 | Cosmos | 83113.74 | 68.6% | NA |  |  | Line1 | TX1
[8 empty] | Str_Typ1(540*29) |  |  | 15.66 | 0.01293% | NA |  |  | Line1 | TX1
[8 empty] | Str_Typ2(545*29) |  |  | 15.805 | 0.01305% | NA |  |  | Line1 | TX1
[8 empty] | Str_Typ3(550*29) |  |  | 15.95 | 0.01316% | NA |  |  | Line1 | TX1
[8 empty] | Str_Typ4(540*58) |  |  | 31.32 | 0.02585% | NA |  |  | Line1 | TX1
[8 empty] | Str_Typ5(545*58) |  |  | 31.61 | 0.02609% | NA |  |  | Line2 | TX2
[8 empty] | Str_Typ6(550*58) |  |  | 31.9 | 0.02633% | NA |  |  | Line3 | TX3
[8 empty] | IS10Inv1M1 | O2R14 |  | 1914 | 1.58%
[8 empty] | IS10Inv1M2 | O2R14 |  | 669.9 | 0.5529%
[8 empty] | IS10Inv2M1 | O2R14 |  | 478.5 | 0.3949%
[8 empty] | IS10Inv2M2 | O2R14 |  | 2041.6 | 1.685%
[8 empty] | IS10Inv3M1 | O2R14 |  | 988.9 | 0.8162%
[8 empty] | IS10Inv3M2 | O2R14 |  | 2041.6 | 1.685%
[8 empty] | IS10Inv4M1 | O2R14 |  | 1818.3 | 1.501%
[8 empty] | IS10Inv4M2 | O2R14 |  | 542.3 | 0.4476%
[8 empty] | IS11Inv1M1 | O2R14 |  | 0 | 0%
[8 empty] | IS11Inv1M2 | O2R14 |  | 159.5 | 0.1316%
[8 empty] | IS11Inv1M3 | O2R14 |  | 382.8 | 0.316%
[8 empty] | IS11Inv1M4 | O2R14 |  | 191.4 | 0.158%
[8 empty] | IS10Inv1 | O2R14 |  | 2583.9 | 2.133%
[8 empty] | IS10Inv2 | O2R14 |  | 2520.1 | 2.08%
[8 empty] | IS10Inv3 | O2R14 |  | 3030.5 | 2.501%
[8 empty] | IS10Inv4 | O2R14 |  | 2360.6 | 1.948%
[8 empty] | IS11Inv1 | O2R14 |  | 733.7 | 0.6056%
[8 empty] | IS10Inv1M1SCB1 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv1M1SCB2 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv1M1SCB3 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv1M1SCB4 | O2R14 |  | 287.1 | 0.237%
[8 empty] | IS10Inv1M1SCB5 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv1M1SCB6 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv1M1SCB7 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv1M1SCB8 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv1M1SCB9 | O2R14 |  | 0 | 0%
[8 empty] | IS10Inv1M2SCB1 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv1M2SCB2 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv1M2SCB3 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv1M2SCB4 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv1M2SCB5 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv1M2SCB6 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv1M2SCB7 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv1M2SCB8 | O2R14 |  | 159.5 | 0.1316%
[8 empty] | IS10Inv1M2SCB9 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv2M1SCB1 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv2M1SCB2 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv2M1SCB3 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv2M1SCB4 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv2M1SCB5 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv2M1SCB6 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv2M1SCB7 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv2M1SCB8 | O2R14 |  | 175.45 | 0.1448%
[8 empty] | IS10Inv2M1SCB9 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS10Inv2M2SCB1 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv2M2SCB2 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv2M2SCB3 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv2M2SCB4 | O2R14 |  | 287.1 | 0.237%
[8 empty] | IS10Inv2M2SCB5 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv2M2SCB6 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv2M2SCB7 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv2M2SCB8 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv2M2SCB9 | O2R14 |  | 0 | 0%
[8 empty] | IS10Inv3M1SCB1 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv3M1SCB2 | O2R14 |  | 191.4 | 0.158%
[8 empty] | IS10Inv3M1SCB3 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv3M1SCB4 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv3M1SCB5 | O2R14 |  | 271.15 | 0.2238%
[8 empty] | IS10Inv3M1SCB6 | O2R14 |  | 63.8 | 0.05266%
[8 empty] | IS10Inv3M1SCB7 | O2R14 |  | 63.8 | 0.05266%
[8 empty] | IS10Inv3M1SCB8 | O2R14 |  | 159.5 | 0.1316%
[8 empty] | IS10Inv3M1SCB9 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv3M2SCB1 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv3M2SCB2 | O2R14 |  | 159.5 | 0.1316%
[8 empty] | IS10Inv3M2SCB3 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv3M2SCB4 | O2R14 |  | 159.5 | 0.1316%
[8 empty] | IS10Inv3M2SCB5 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv3M2SCB6 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv3M2SCB7 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv3M2SCB8 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv3M2SCB9 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv4M1SCB1 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv4M1SCB2 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv4M1SCB3 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv4M1SCB4 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv4M1SCB5 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv4M1SCB6 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv4M1SCB7 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv4M1SCB8 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv4M1SCB9 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS10Inv4M2SCB1 | O2R14 |  | 284.49 | 0.2348%
[8 empty] | IS10Inv4M2SCB2 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS10Inv4M2SCB3 | O2R14 |  | 284.49 | 0.2348%
[8 empty] | IS10Inv4M2SCB4 | O2R14 |  | 284.49 | 0.2348%
[8 empty] | IS10Inv4M2SCB5 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS10Inv4M2SCB6 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS10Inv4M2SCB7 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS10Inv4M2SCB8 | O2R14 |  | 237.07 | 0.1957%
[8 empty] | IS10Inv4M2SCB9 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS11Inv1M1SCB1 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS11Inv1M1SCB2 | O2R14 |  | 237.075 | 0.1957%
[8 empty] | IS11Inv1M1SCB3 | O2R14 |  | 237.075 | 0.1957%
[8 empty] | IS11Inv1M1SCB4 | O2R14 |  | 284.49 | 0.2348%
[8 empty] | IS11Inv1M1SCB5 | O2R14 |  | 237.075 | 0.1957%
[8 empty] | IS11Inv1M1SCB6 | O2R14 |  | 205.465 | 0.1696%
[8 empty] | IS11Inv1M2SCB1 | O2R14 |  | 189.66 | 0.1565%
[8 empty] | IS11Inv1M2SCB2 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS11Inv1M2SCB3 | O2R14 |  | 221.27 | 0.1826%
[8 empty] | IS11Inv1M2SCB4 | O2R14 |  | 205.465 | 0.1696%
[8 empty] | IS11Inv1M2SCB5 | O2R14 |  | 126.44 | 0.1044%
[8 empty] | IS11Inv1M2SCB6 | O2R14 |  | 284.49 | 0.2348%
[8 empty] | IS11Inv1M3SCB1 | O2R14 |  | 221.27 | 0.1826%
[8 empty] | IS11Inv1M3SCB2 | O2R14 |  | 221.27 | 0.1826%
[8 empty] | IS11Inv1M3SCB3 | O2R14 |  | 221.27 | 0.1826%
[8 empty] | IS11Inv1M3SCB4 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS11Inv1M3SCB5 | O2R14 |  | 189.66 | 0.1565%
[8 empty] | IS11Inv1M3SCB6 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS11Inv1M4SCB1 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS11Inv1M4SCB2 | O2R14 |  | 221.27 | 0.1826%
[8 empty] | IS11Inv1M4SCB3 | O2R14 |  | 221.27 | 0.1826%
[8 empty] | IS11Inv1M4SCB4 | O2R14 |  | 221.27 | 0.1826%
[8 empty] | IS11Inv1M4SCB5 | O2R14 |  | 221.27 | 0.1826%
[8 empty] | IS11Inv1M4SCB6 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS12Inv1 | O2R24 |  | 6200 | 5.117%
[8 empty] | IS13Inv1 | O2R26 |  | 3635 | 3%
[8 empty] | IS13Inv2 | O2R26 |  | 3066 | 2.531%
[8 empty] | IS14Inv1 | O2R14 |  |  | 0%
[8 empty] | IS14Inv2 | O2R14 |  | 3921 | 3.236%
[8 empty] | IS12Inv1M1 | O2R24 |  | 1534 | 1.266%
[8 empty] | IS12Inv1M2 | O2R24 |  | 1456 | 1.202%
[8 empty] | IS12Inv1M3 | O2R24 |  | 1597 | 1.318%
[8 empty] | IS12Inv1M4 | O2R24 |  | 1581 | 1.305%
[8 empty] | IS13Inv1M1 | O2R26 |  | 1675 | 1.383%
[8 empty] | IS13Inv1M2 | O2R26 |  | 1738 | 1.435%
[8 empty] | IS13Inv2M1 | O2R26 |  | 1485 | 1.226%
[8 empty] | IS13Inv2M2 | O2R26 |  | 1801 | 1.487%
[8 empty] | IS14Inv2M1 | O2R14 |  |  | 0%
[8 empty] | IS14Inv2M2 | O2R14 |  | 1241 | 1.024%
[8 empty] | IS14Inv2M3 | O2R14 |  | 909 | 0.7503%
[8 empty] | IS14Inv2M4 | O2R14 |  | 1515 | 1.25%
[8 empty] | IS12Inv1M1SCB1 | O2R24 |  | 250.56 | 0.2068%
[8 empty] | IS12Inv1M1SCB2 | O2R24 |  | 250.56 | 0.2068%
[8 empty] | IS12Inv1M1SCB3 | O2R24 |  | 281.88 | 0.2327%
[8 empty] | IS12Inv1M1SCB4 | O2R24 |  | 250.56 | 0.2068%
[8 empty] | IS12Inv1M1SCB5 | O2R24 |  | 250.56 | 0.2068%
[8 empty] | IS12Inv1M1SCB6 | O2R24 |  | 250.56 | 0.2068%
[8 empty] | IS12Inv1M2SCB1 | O2R24 |  | 250.56 | 0.2068%
[8 empty] | IS12Inv1M2SCB2 | O2R24 |  | 250.56 | 0.2068%
[8 empty] | IS12Inv1M2SCB3 | O2R24 |  | 219.24 | 0.181%
[8 empty] | IS12Inv1M2SCB4 | O2R24 |  | 203.58 | 0.168%
[8 empty] | IS12Inv1M2SCB5 | O2R24 |  | 250.56 | 0.2068%
[8 empty] | IS12Inv1M2SCB6 | O2R24 |  | 281.88 | 0.2327%
[8 empty] | IS12Inv1M3SCB1 | O2R24 |  | 281.88 | 0.2327%
[8 empty] | IS12Inv1M3SCB2 | O2R24 |  | 281.88 | 0.2327%
[8 empty] | IS12Inv1M3SCB3 | O2R24 |  | 250.56 | 0.2068%
[8 empty] | IS12Inv1M3SCB4 | O2R24 |  | 250.56 | 0.2068%
[8 empty] | IS12Inv1M3SCB5 | O2R24 |  | 281.88 | 0.2327%
[8 empty] | IS12Inv1M3SCB6 | O2R24 |  | 250.56 | 0.2068%
[8 empty] | IS12Inv1M4SCB1 | O2R24 |  | 281.88 | 0.2327%
[8 empty] | IS12Inv1M4SCB2 | O2R24 |  | 281.88 | 0.2327%
[8 empty] | IS12Inv1M4SCB3 | O2R24 |  | 266.22 | 0.2197%
[8 empty] | IS12Inv1M4SCB4 | O2R24 |  | 281.88 | 0.2327%
[8 empty] | IS12Inv1M4SCB5 | O2R24 |  | 250.56 | 0.2068%
[8 empty] | IS12Inv1M4SCB6 | O2R24 |  | 219.24 | 0.181%
[8 empty] | IS13Inv1M1SCB1 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv1M1SCB2 | O2R26 |  | 221.27 | 0.1826%
[8 empty] | IS13Inv1M1SCB3 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv1M1SCB4 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv1M1SCB5 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv1M1SCB6 | O2R26 |  | 221.27 | 0.1826%
[8 empty] | IS13Inv1M1SCB7 | O2R26 |  | 221.27 | 0.1826%
[8 empty] | IS13Inv1M2SCB1 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv1M2SCB2 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv1M2SCB3 | O2R26 |  | 282.88 | 0.2335%
[8 empty] | IS13Inv1M2SCB4 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv1M2SCB5 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv1M2SCB6 | O2R26 |  | 221.27 | 0.1826%
[8 empty] | IS13Inv1M2SCB7 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv2M1SCB1 | O2R26 |  | 221.27 | 0.1826%
[8 empty] | IS13Inv2M1SCB2 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv2M1SCB3 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv2M1SCB4 | O2R26 |  | 268.685 | 0.2218%
[8 empty] | IS13Inv2M1SCB5 | O2R26 |  | 237.075 | 0.1957%
[8 empty] | IS13Inv2M1SCB6 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv2M1SCB7 | O2R26 |  | 0 | 0%
[8 empty] | IS13Inv2M2SCB1 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv2M2SCB2 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv2M2SCB3 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv2M2SCB4 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv2M2SCB5 | O2R26 |  | 284.49 | 0.2348%
[8 empty] | IS13Inv2M2SCB6 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS13Inv2M2SCB7 | O2R26 |  | 252.88 | 0.2087%
[8 empty] | IS14Inv2M1SCB1 | O2R14 |  | 127.6 | 0.1053%
[8 empty] | IS14Inv2M1SCB2 | O2R14 |  | 0 | 0%
[8 empty] | IS14Inv2M1SCB3 | O2R14 |  | 0 | 0%
[8 empty] | IS14Inv2M1SCB4 | O2R14 |  | 0 | 0%
[8 empty] | IS14Inv2M1SCB5 | O2R14 |  | 95.7 | 0.07899%
[8 empty] | IS14Inv2M1SCB6 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS14Inv2M2SCB1 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS14Inv2M2SCB2 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS14Inv2M2SCB3 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS14Inv2M2SCB4 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS14Inv2M2SCB5 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS14Inv2M2SCB6 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS14Inv2M3SCB1 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS14Inv2M3SCB2 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS14Inv2M3SCB3 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS14Inv2M3SCB4 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS14Inv2M3SCB5 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS14Inv2M3SCB6 | O2R14 |  | 239.25 | 0.1975%
[8 empty] | IS14Inv2M4SCB1 | O2R14 |  | 239.25 | 0.1975%
[8 empty] | IS14Inv2M4SCB2 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS14Inv2M4SCB3 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS14Inv2M4SCB4 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS14Inv2M4SCB5 | O2R14 |  | 271.15 | 0.2238%
[8 empty] | IS14Inv2M4SCB6 | O2R14 |  | 271.15 | 0.2238%
[8 empty] | IS10Tx | O2R14 |  | 17236.585 | 14.23%
[8 empty] | IS11Tx | O2R14 |  | 5484.335 | 4.527%
[8 empty] | IS12Tx | O2R24 |  | 6170.4 | 5.093%
[8 empty] | IS13Tx | O2R26 |  | 6701.32 | 5.531%
[8 empty] | IS14Tx | O2R14 |  | 8906.48 | 7.351%
[8 empty] | Tx |  |  |  | 0%
[8 empty] | MVP |  |  |  | 0%
[8 empty] | Aux_Tx |  |  |  | 0%
[8 empty] | MCR_MVP_SolarF3 |  |  |  | 0%
[8 empty] | MCR_MVP_SolarF4 |  |  |  | 0%
[8 empty] | MCR_MVP_SolarF5 |  |  |  | 0%
[8 empty] | MCR_MVP_SolarF6 |  |  | 8906.48 | 7.351%
[8 empty] | MCR_MVP_SolarF7 |  |  | 35592.28 | 29.38%
[8 empty] | Power_TX |  |  |  | 0%
[8 empty] | Power_Tx2 |  |  |  | 0%
[8 empty] | Line_Bay1 |  |  |  | 0%
[8 empty] | IS14Inv1M1 | O2R14 |  | 1499.3 | 1.238%
[8 empty] | IS14Inv1M2 | O2R14 |  | 1052.7 | 0.8689%
[8 empty] | IS14Inv1M3 | O2R14 |  | 1359.23 | 1.122%
[8 empty] | IS14Inv1M4 | O2R14 |  | 1422.45 | 1.174%
[8 empty] | IS14Inv1M1SCB1 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS14Inv1M1SCB2 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS14Inv1M1SCB3 | O2R14 |  | 271.15 | 0.2238%
[8 empty] | IS14Inv1M1SCB4 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS14Inv1M1SCB5 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS14Inv1M1SCB6 | O2R14 |  | 239.25 | 0.1975%
[8 empty] | IS14Inv1M2SCB1 | O2R14 |  | 255.2 | 0.2106%
[8 empty] | IS14Inv1M2SCB2 | O2R14 |  | 31.9 | 0.02633%
[8 empty] | IS14Inv1M2SCB3 | O2R14 |  | 191.4 | 0.158%
[8 empty] | IS14Inv1M2SCB4 | O2R14 |  | 159.5 | 0.1316%
[8 empty] | IS14Inv1M2SCB5 | O2R14 |  | 191.4 | 0.158%
[8 empty] | IS14Inv1M2SCB6 | O2R14 |  | 223.3 | 0.1843%
[8 empty] | IS14Inv1M3SCB1 | O2R14 |  | 221.27 | 0.1826%
[8 empty] | IS14Inv1M3SCB2 | O2R14 |  | 221.27 | 0.1826%
[8 empty] | IS14Inv1M3SCB3 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS14Inv1M3SCB4 | O2R14 |  | 221.27 | 0.1826%
[8 empty] | IS14Inv1M3SCB5 | O2R14 |  | 221.27 | 0.1826%
[8 empty] | IS14Inv1M3SCB6 | O2R14 |  | 221.27 | 0.1826%
[8 empty] | IS14Inv1M4SCB1 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS14Inv1M4SCB2 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS14Inv1M4SCB3 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS14Inv1M4SCB4 | O2R14 |  | 252.88 | 0.2087%
[8 empty] | IS14Inv1M4SCB5 | O2R14 |  | 158.05 | 0.1305%
[8 empty] | IS14Inv1M4SCB6 | O2R14 |  | 252.88 | 0.2087%

## Plant_BD
Sr. No. | Date | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Inverter Station Number (if Bd in filed) | Inverter number (If Inv, SCb or Str BD) | Inverter Module Number (If Inv, SCb or Str BD) | SCB Number (If SCB or Str BD) | String Type(If String BD) | Equipment (If any BD other than PV array and inv) | C1 | C2 | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Fault Category | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgement Time | Work Start time on Fault | Work Completion time on fault | Acknow. time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(Wh/m2) | Approximate Energy Loss (KWh) | Job Card Number
1 | 2025-04-03 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.32292 | 0.74306 | 10.0833 | IS4 |  |  |  |  | Tx | 0 | 1 | IS4Tx | 17019.795 | 14.05% | IDT | Buchholz Relay trip | IDT Tripped | 7:45 |  | 0.39583 | 14:00 | -7.75 | 1.75 | 6.25 | 6.25 | In visual inspection there is observed and oil top up work | Close | 0.878 | 3.7112 | 18147.1029
2 | 2025-04-08 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.27014 | 0.76458 | 11.8667 | IS10 | Inv1 |  |  |  |  | 1 | 1 | IS10Inv1 | 2583.9 | 2.133% | Inverter | GFDI Fault | GFDI Fault | 11:32 |  | 0.48958 | 11:49 | -11.5333 | 0.21667 | 0.28333 | 0.28333 | All SCB visual inspection checked & VOC found checked. | Close | 0.0060427 | 0.239 | 503.9225
3 | 2025-04-12 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.26944 | 0.76806 | 11.9667 | IS10 |  |  |  |  | Tx | 0 | 1 | IS10Tx | 17236.585 | 14.23% | IDT | IDT tripped due to Overcurrent and earth fault | IDT tripped due to Overcurrent and earth fault due to Phase-3 TL Line Bird Electrocution | 7:45 |  | 0.34375 | 8:30 | -7.75 | 0.5 | 0.75 | 0.75 | TL Line visual inspectionn checked Bird removed from line and charged | Close | 0.1067 | 0.132 | 1856.587
4 | 2025-04-12 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.26944 | 0.76806 | 11.9667 | IS11 |  |  |  |  | Tx | 0 | 1 | IS11Tx | 5484.335 | 4.527% | IDT | IDT tripped due to Overcurrent and earth fault | IDT tripped due to Overcurrent and earth fault due to Phase-3 TL Line Bird Electrocution | 7:45 |  | 0.34375 | 8:30 | -7.75 | 0.5 | 0.75 | 0.75 | TL Line visual inspectionn checked Bird removed from line and charged | Close | 0.03395 | 0.132 | 590.7287
5 | 2025-04-12 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.26944 | 0.76806 | 11.9667 | IS12 |  |  |  |  | Tx | 0 | 1 | IS12Tx | 6170.4 | 5.093% | IDT | IDT tripped due to Overcurrent and earth fault | IDT tripped due to Overcurrent and earth fault due to Phase-3 TL Line Bird Electrocution | 7:45 |  | 0.34375 | 8:30 | -7.75 | 0.5 | 0.75 | 0.75 | TL Line visual inspectionn checked Bird removed from line and charged | Close | 0.038197 | 0.132 | 664.6261
6 | 2025-04-12 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.26944 | 0.76806 | 11.9667 | IS13 |  |  |  |  | Tx | 0 | 1 | IS13Tx | 6701.32 | 5.531% | IDT | IDT tripped due to Overcurrent and earth fault | IDT tripped due to Overcurrent and earth fault due to Phase-3 TL Line Bird Electrocution | 7:45 |  | 0.34375 | 8:30 | -7.75 | 0.5 | 0.75 | 0.75 | TL Line visual inspectionn checked Bird removed from line and charged | Close | 0.041484 | 0.132 | 721.8126
7 | 2025-04-12 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.26944 | 0.76806 | 11.9667 | IS14 |  |  |  |  | Tx | 0 | 1 | IS14Tx | 8906.48 | 7.351% | IDT | IDT tripped due to Overcurrent and earth fault | IDT tripped due to Overcurrent and earth fault due to Phase-3 TL Line Bird Electrocution | 7:45 |  | 0.34375 | 8:30 | -7.75 | 0.5 | 0.75 | 0.75 | TL Line visual inspectionn checked Bird removed from line and charged | Close | 0.055135 | 0.132 | 959.3348
8 | 2025-04-13 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.26736 | 0.76667 | 11.9833 | [5 empty] | Power_TX | 0 | 1 | Power_TX | 122106 | 100.8% | PTR | UV/OV | UV/OV 33KV side | 16:22 |  | 0.6875 | 16:48 | -16.3667 | 0.13333 | 0.43333 | 0.43333 | In visual inspection Checked found Birds electrocution and charged IDT | Close | 0.43673 | 0.18013 | 17947.8823
9 | 2025-04-14 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.26944 | 0.76597 | 11.9167 | IS10 | Inv1 |  |  |  |  | 1 | 1 | IS10Inv1 | 2583.9 | 2.133% | Inverter | GFDI Fault | Inverter Tripped on GFDI Fualt | 6:32 |  | 0.64861 | 18:32 | -6.5333 | 9.0333 |  | 12 | Fault not rectified from Sungrow service engineer | Open | 0.25593 | 7 | 14759.2368
10 | 2025-04-15 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.26667 | 0.76667 | 12 | IS10 | Inv1 |  |  |  |  | 1 | 1 | IS10Inv1 | 2583.9 | 2.133% | Inverter | GFDI Fault | Inverter Tripped on GFDI Fualt | 6:34 |  | 0.48194 | 18:32 | -6.5667 | 5 |  | 11.9667 | Fault not rectified from Sungrow service engineer | Open | 0.25522 | 7 | 14759.2368
11 | 2025-04-16 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.26875 | 0.74792 | 11.5 | IS10 | Inv1 |  |  |  |  | 1 | 1 | IS10Inv1 | 2583.9 | 2.133% | Inverter | GFDI Fault | Inverter Tripped on GFDI Fualt | 6:43 |  | 0.48958 | 18:32 | -6.7167 | 5.0333 |  | 11.8167 | Fault not rectified from Sungrow service engineer | Open | 0.25202 | 6 | 12650.7744
12 | 2025-04-17 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.26736 | 0.76458 | 11.9333 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 3865.905 | 3.191% | Inverter | DSP Internal fault | DSP Internal fault as per discussion with service engineer Inverter AC and DC | 9:03 |  | 0.37708 | 9:51 | -9.05 | 0 | 0.8 | 0.8 | DSP Internal fault as per discussion with service engineer Inverter AC and DC OFF and restart the inverter | Close | 0.025527 | 0.156 | 492.1142
13 | 2025-04-22 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.2625 | 0.76806 | 12.1333 | IS10 | Inv1 |  |  |  |  | 1 | 1 | IS10Inv1 | 2583.9 | 2.133% | Inverter | GFDI Fault | GFDI Fault due to Auxiliary Transformer PT broken | 10:03 |  | 0.37708 | 9:51 | -10.05 | -1 | -0.2 | -0.2 | GFDI Fault due to Auxiliary Transformer PT broken so Neutral leakage current came to Inverter. So we bypass R-Phase PT and start the inverter | Close | -0.0042654 | 3.83 | 8075.411
14 | 2025-04-25 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.2625 | 0.76597 | 12.0833 | IS10 | Inv1 |  |  |  |  | 1 | 1 | IS10Inv1 | 2583.9 | 2.133% | Inverter | GFDI Fault | Inverter Tripped on GFDI Fualt | 8:03 |  | 0.35417 | 9:39 | -8.05 | 0.45 | 1.6 | 1.6 | GFDI Fault due to Auxiliary Transformer PT broken so Neutral leakage current came to Inverter. So we bypass R-Phase PT and start the inverter |  | 0.034124 | 0.8407 | 1772.5843
15 | 2025-04-25 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.2625 | 0.76597 | 12.0833 | IS4 | Inv4 |  |  |  |  | 1 | 1 | IS4Inv4 | 4393.79 | 3.627% | Inverter | DSP Internal fault | DSP Internal fault as per discussion with service engineer Inverter AC and DC | 0.62153 |  | 0.62431 | 15:08 | -14.9167 | 0.066667 | 0.21667 | 0.21667 | DSP Internal fault as per discussion with service engineer Inverter AC and DC OFF and restart the inverter |  | 0.0078576 | 0.1649 | 591.2214
16 | 2025-04-28 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.26181 | 0.76875 | 12.1667 | IS10 | Inv3 |  |  |  |  | 1 | 1 | IS10Inv3 | 3030.5 | 2.501% | Inverter | Internal Fault | Inverter Internal fault | 6:30 |  | 0.29861 | 9:07 | -6.5 | 0.66667 | 2.6167 | 2.6167 | Internal fault as per discussion with service engineer Inverter AC and DC OFF and restart the inverter |  | 0.065452 | 0.888 | 2195.9245
17 | 2025-04-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.25972 | 0.76806 | 12.2 | IS2 |  |  |  |  | Tx | 0 | 1 | IS2Tx | 12507.175 | 10.32% | IDT | IDT tripped | IDT Tripped due to IDT Live thermography | 12:32 |  | 12:32 | 12:49 | -12.5333 | 0 | 0.28333 | 0.28333 | IDT Tripped due to IDT live thermography | Close | 0.029249 | 0.2974 | 3035.2212
18 | 2025-04-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.25972 | 0.76806 | 12.2 | IS3 |  |  |  |  | Tx | 0 | 1 | IS3Tx | 8911.45 | 7.355% | IDT | IDT tripped | IDT Tripped due to IDT Live thermography | 13:11 |  | 13:11 | 13:26 | -13.1833 | 0 | 0.25 | 0.25 | IDT Tripped due to IDT live thermography | Close | 0.018389 | 0.2565 | 1865.2021
19 | 2025-04-30 | 2026 | 2025 | Year_1 | Year_1 | 2025-04-01 | 30 | 0.25903 | 0.77361 | 12.35 | IS5 |  |  |  |  | Tx | 0 | 1 | IS5Tx | 7416.7 | 6.122% | IDT | IDT tripped | IDT Tripped due to IDT Live thermography | 12:59 |  | 12:59 | 13:35 | -12.9833 | 0 | 0.6 | 0.6 | IDT Tripped due to IDT live thermography | Close | 0.03673 | 0.6088 | 3684.4742
20 | 2025-05-01 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25972 | 0.77014 | 12.25 | IS10 | Inverter 4 | M1 | SCB5 | Str_Typ4(540*58) | MCR_MVP_SolarF6 | 0 | 0 | Str_Typ4(540*58) | 31.32 | 0.02585% | DC String | Fuse Damage | In SCB Fuse Damage | 14:40 |  | 0.73958 | 18:30 | -14.6667 | 3.0833 | 3.8333 | 3.8333 | 50 Amps Replace Work Donde After Generation & Than String Charge. | Close | 0.00099096 | 1.23 | 31.4353
21 | 2025-05-03 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25833 | 0.77014 | 12.2833 | IS6 |  |  |  |  | Tx | 0 | 1 | IS6Tx | 7448.65 | 6.148% | IDT | IDT tripped | IDT Tripped due to IDT Live thermography | 12:19 |  | 12:19 | 12:57 | -12.3167 | 0 | 0.63333 | 0.63333 | IDT Tripped due to IDT live thermography | Close | 0.038938 | 0.6466 | 3930.0984
22 | 2025-05-04 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25833 | 0.77153 | 12.3167 | IS4 |  |  |  |  | Tx | 0 | 1 | IS4Tx | 17019.795 | 14.05% | IDT | IDT tripped | IDT Tripped due to IDT Live thermography | 11:34 |  | 11:34 | 11:43 | -11.5667 | 0 | 0.15 | 0.15 | IDT Tripped due to IDT live thermography | Close | 0.021072 | 0.1783 | 2476.2576
23 | 2025-05-04 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25833 | 0.77153 | 12.3167 | IS7 |  |  |  |  | Tx | 0 | 1 | IS7Tx | 2971.34 | 2.453% | IDT | IDT tripped | IDT Tripped due to IDT Live thermography | 13:13 |  | 13:13 | 13:43 | -13.2167 | 0 | 0.5 | 0.5 | IDT Tripped due to IDT live thermography | Close | 0.012263 | 0.4834 | 1172.0581
24 | 2025-05-07 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25486 | 0.77222 | 12.4167 | IS8 |  |  |  |  | Tx | 0 | 1 | IS8Tx | 5992.415 | 4.946% | IDT | IDT tripped | IDT Tripped due to IDT Live thermography |  |  | 0.50625 | 13:08 | 0 | 12.15 | 13.1333 | 13.1333 | IDT Tripped due to IDT live thermography |  | 0.64958 | 1.31 | 6405.6519
25 | 2025-05-07 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25486 | 0.77222 | 12.4167 | IS9 |  |  |  |  | Tx | 0 | 1 | IS9Tx | 8345.04 | 6.888% | IDT | IDT tripped | IDT Tripped due to IDT Live thermography |  |  | 0.57986 | 14:30 | 0 | 13.9167 | 14.5 | 14.5 | IDT Tripped due to IDT live thermography |  | 0.99875 | 0.4589 | 3124.9037
26 | 2025-05-09 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25694 | 0.77083 | 12.3333 | [5 empty] | Power_TX | 0 | 1 | Power_TX | 122106 | 100.8% | PTR | OV/UV | UV/OV 33KV side | 9:59 |  | 9:59 | 10:18 | -9.9833 | 0 | 0.31667 | 0.31667 | PTR charged after discussion with GSS end. 132KV Malkapur line Line insulator broken | Close | 0.31915 | 0.2639 | 26294.5991
27 | 2025-05-16 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25278 | 0.75903 | 12.15 | [5 empty] | Power_TX | 0 | 1 | Power_TX | 122106 | 100.8% | PTR | OV/UV | UV/OV 33KV side | 16:37 |  | 16:37 | 16:52 | -16.6167 | 0 | 0.25 | 0.25 | PTR charged after discussion with GSS end. | Close | 0.25196 | 0.117 | 11657.704
28 | 2025-05-18 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25278 | 0.76597 | 12.3167 | IS5 |  |  |  |  | Tx | 0 | 1 | IS5Tx | 7416.7 | 6.122% | IDT | IDT tripped | IDT Tripped due to IDT Buchloz relay operated becaused AUM service engineer LV side busbar changed | 11:09 |  | 11:35 | 12:04 | -11.15 | 0.43333 | 0.91667 | 0.91667 | Air realased from Buchloz relay and transformer charged | Close | 0.056115 | 0.8324 | 5037.7074
29 | 2025-05-19 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25625 | 0.74792 | 11.8 | IS5 |  |  |  |  | Tx | 0 | 1 | IS5Tx | 7416.7 | 6.122% | IDT | IDT tripped | IDT Tripped due to IDT Buchloz relay operated becaused AUM service engineer LV side busbar changed | 12:23 |  | 12:23 | 13:04 | -12.3833 | 0 | 0.68333 | 0.68333 | Air realased from Buchloz relay and transformer charged | Close | 0.041831 | 0.5981 | 3619.7175
30 | 2025-05-21 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.26944 | 0.77639 | 12.1667 | IS10 | Inv3 |  |  |  |  | 1 | 1 | IS10Inv3 | 3030.5 | 2.501% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 10:05 |  | 0.77222 |  | -10.0833 | 8.45 |  | -10.0833 | SCB Cable jointing work is in progress | Open | -0.25222 | 4.9382 | 12211.7176
31 | 2025-05-21 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.26944 | 0.77639 | 12.1667 | IS10 | Inv4 |  |  |  |  | 1 | 1 | IS10Inv4 | 2360.6 | 1.948% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 10:05 |  | 0.77222 |  | -10.0833 | 8.45 |  | -10.0833 | SCB Cable jointing work is in progress | Open | -0.19646 | 4.9382 | 9512.2853
32 | 2025-05-22 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25069 | 0.77292 | 12.5333 | IS10 | Inv3 |  |  |  |  | 1 | 1 | IS10Inv3 | 3030.5 | 2.501% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.16342 | 6.2421 | 15435.9138
33 | 2025-05-22 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25069 | 0.77292 | 12.5333 | IS10 | Inv4 |  |  |  |  | 1 | 1 | IS10Inv4 | 2360.6 | 1.948% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.1273 | 6.2421 | 12023.7645
34 | 2025-05-23 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.27431 | 0.74722 | 11.35 | IS8 | Inv1 | M2 | SCB5 | Str_Typ5(545*58) | Dc String | 0 | 0 | Str_Typ5(545*58) | 31.61 | 0.02609% | String | String No 01 & 07 DC cable Cut and fuse Damage | 02 No's String Breakdown due to the 6 Sq mm DC Cable Cut & Fuse Damge. | 14:30 |  | 0.72917 | 18:30 | -14.5 | 3 | 4 | 4 | Dc Cable Replace Work Done and Fuse Replace done & after Generation & String Charge. | Close | 0.0010436 | 2.54 | 65.5162
35 | 2025-05-23 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.27431 | 0.74722 | 11.35 | IS10 | Inv3 |  |  |  |  | 1 | 1 | IS10Inv3 | 3030.5 | 2.501% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.16342 | 2.6424 | 6534.417
| 2025-05-23 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.27431 | 0.74722 | 11.35 | IS10 | Inv4 |  |  |  |  | 1 | 1 | IS10Inv4 | 2360.6 | 1.948% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.1273 | 2.6424 | 5089.9669
36 | 2025-05-24 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.2625 | 0.76736 | 12.1167 | IS10 | Inv3 |  |  |  |  | 1 | 1 | IS10Inv3 | 3030.5 | 2.501% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.16342 | 3.5203 | 8705.2515
| 2025-05-24 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.2625 | 0.76736 | 12.1167 | IS10 | Inv4 |  |  |  |  | 1 | 1 | IS10Inv4 | 2360.6 | 1.948% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.1273 | 3.5203 | 6780.9327
37 | 2025-05-24 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.2625 | 0.76736 | 12.1167 | IS10 |  |  |  |  | Tx | 0 | 1 | IS10Tx | 17236.585 | 14.23% | IDT | IDT tripped due to Overcurrent and earth fault | IDT tripped due to Overcurrent and earth fault due to Phase-3 TL Line Bird Electrocution | 16:40 |  | 0.76458 | 0.76458 | -16.6667 | 1.6833 | 1.6833 | 1.6833 | TL Line visual inspectionn checked Bird removed from line and charged | Close | 0.23949 | 0.2233 | 3140.7264
38 | 2025-05-24 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.2625 | 0.76736 | 12.1167 | IS11 |  |  |  |  | Tx | 0 | 1 | IS11Tx | 5484.335 | 4.527% | IDT | IDT tripped due to Overcurrent and earth fault | IDT tripped due to Overcurrent and earth fault due to Phase-3 TL Line Bird Electrocution | 16:40 |  | 0.76458 | 0.76458 | -16.6667 | 1.6833 | 1.6833 | 1.6833 | TL Line visual inspectionn checked Bird removed from line and charged | Close | 0.0762 | 0.2233 | 999.316
39 | 2025-05-24 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.2625 | 0.76736 | 12.1167 | IS12 |  |  |  |  | Tx | 0 | 1 | IS12Tx | 6170.4 | 5.093% | IDT | IDT tripped due to Overcurrent and earth fault | IDT tripped due to Overcurrent and earth fault due to Phase-3 TL Line Bird Electrocution | 16:40 |  | 0.76458 | 0.76458 | -16.6667 | 1.6833 | 1.6833 | 1.6833 | TL Line visual inspectionn checked Bird removed from line and charged | Close | 0.085732 | 0.2233 | 1124.3259
40 | 2025-05-24 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.2625 | 0.76736 | 12.1167 | IS13 |  |  |  |  | Tx | 0 | 1 | IS13Tx | 6701.32 | 5.531% | IDT | IDT tripped due to Overcurrent and earth fault | IDT tripped due to Overcurrent and earth fault due to Phase-3 TL Line Bird Electrocution | 16:40 |  | 0.76458 | 0.76458 | -16.6667 | 1.6833 | 1.6833 | 1.6833 | TL Line visual inspectionn checked Bird removed from line and charged | Close | 0.093108 | 0.2233 | 1221.0663
41 | 2025-05-24 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.2625 | 0.76736 | 12.1167 | IS14 |  |  |  |  | Tx | 0 | 1 | IS14Tx | 8906.48 | 7.351% | IDT | IDT tripped due to Overcurrent and earth fault | IDT tripped due to Overcurrent and earth fault due to Phase-3 TL Line Bird Electrocution | 16:40 |  | 0.76458 | 0.76458 | -16.6667 | 1.6833 | 1.6833 | 1.6833 | TL Line visual inspectionn checked Bird removed from line and charged | Close | 0.12375 | 0.2233 | 1622.8747
42 | 2025-05-25 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.275 | 0.76875 | 11.85 | IS10 | Inv3 |  |  |  |  | 1 | 1 | IS10Inv3 | 3030.5 | 2.501% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.16342 | 1.9298 | 4772.1391
| 2025-05-25 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.275 | 0.76875 | 11.85 | IS10 | Inv4 |  |  |  |  | 1 | 1 | IS10Inv4 | 2360.6 | 1.948% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.1273 | 1.9298 | 3717.2452
43 | 2025-05-25 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.275 | 0.76875 | 11.85 | IS11 | Inv1 |  |  |  |  | 1 | 1 | IS11Inv1 | 733.7 | 0.6056% | Inverter | Inverter Internal fault | DSP Internal fault as per discussion with service engineer Inverter AC and DC | 7:00 |  | 0.45833 | 0.45833 | -7 | 4 | 4 | 4 | Internal fault as per discussion with service engineer Inverter AC and DC OFF and restart the inverter | Close | 0.024224 | 0.7494 | 448.6652
44 | 2025-05-26 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25208 | 0.76319 | 12.2667 | IS10 | Inv3 |  |  |  |  | 1 | 1 | IS10Inv3 | 3030.5 | 2.501% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 | -6.5333 | -6.5333 | SCB Cable jointing work is in progress | Close | -0.16342 | 6.7432 | 16675.2952
| 2025-05-26 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25208 | 0.76319 | 12.2667 | IS10 | Inv4 |  |  |  |  | 1 | 1 | IS10Inv4 | 2360.6 | 1.948% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.1273 | 6.7432 | 12989.1773
45 | 2025-05-27 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25347 | 0.77917 | 12.6167 | IS8 | Inv1 | M4 | SCB3 | Str_Typ4(540*58) | MCR_MVP_SolarF5 | 0 | 0 | Str_Typ4(540*58) | 31.32 | 0.02585% | String | 6 sq mm DC Cable Damage | String Breakdown due to the 6 Sq mm DC Cable Damage | 7:32 |  | 0.52083 | 17:30 | -7.5333 | 4.9667 | 9.9667 | 9.9667 | DC Cable Replace Work Done after Generation & String Charge. | Close | 0.0025765 | 5.55 | 141.842
46 | 2025-05-27 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25347 | 0.77917 | 12.6167 | IS10 | Inv3 |  |  |  |  | 1 | 1 | IS10Inv3 | 3030.5 | 2.501% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.16342 | 5.5894 | 13821.9183
|  | 1900 | 1900 |  |  | 1899-12-31 | 31 | 0 | 0 | 0 | IS10 | Inv4 |  |  |  |  | 1 | 1 | IS10Inv4 | 2360.6 | 1.948% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.1273 | 5.5894 | 10766.5469
47 | 2025-05-28 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.27639 | 0.75278 | 11.4333 | IS10 | Inv3 |  |  |  |  | 1 | 1 | IS10Inv3 | 3030.5 | 2.501% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.16342 | 2.6786 | 6623.9607
|  | 1900 | 1900 |  |  | 1899-12-31 | 31 | 0 | 0 | 0 | IS10 | Inv4 |  |  |  |  | 1 | 1 | IS10Inv4 | 2360.6 | 1.948% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.1273 | 2.6786 | 5159.7167
48 | 2025-05-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.26389 | 0.78264 | 12.45 | IS10 | Inv3 |  |  |  |  | 1 | 1 | IS10Inv3 | 3030.5 | 2.501% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.16342 | 5.3924 | 13334.7193
|  | 1900 | 1900 |  |  | 1899-12-31 | 31 | 0 | 0 | 0 | IS10 | Inv4 |  |  |  |  | 1 | 1 | IS10Inv4 | 2360.6 | 1.948% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.1273 | 5.3924 | 10387.0445
49 | 2025-05-30 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.25764 | 0.77431 | 12.4 | IS10 | Inv3 |  |  |  |  | 1 | 1 | IS10Inv3 | 3030.5 | 2.501% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.16342 | 5.3922 | 13334.3342
|  | 1900 | 1900 |  |  | 1899-12-31 | 31 | 0 | 0 | 0 | IS10 | Inv4 |  |  |  |  | 1 | 1 | IS10Inv4 | 2360.6 | 1.948% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.1273 | 5.3924 | 10387.0445
50 | 2025-05-31 | 2026 | 2025 | Year_1 | Year_1 | 2025-05-01 | 31 | 0.24931 | 0.78403 | 12.8333 | IS10 | Inv3 |  |  |  |  | 1 | 1 | IS10Inv3 | 3030.5 | 2.501% | Inverter | Inverter SCB Cable burned in cable trench | Inverter SCB Cable burned in cable trench | 6:32 |  | 0.77222 |  | -6.5333 | 12 |  | -6.5333 | SCB Cable jointing work is in progress | Open | -0.16342 | 7.0124 | 17340.802
51 | 2025-06-01 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25069 | 0.78264 | 12.7667 | [5 empty] | Power_TX | 0 | 1 | Power_TX | 122106 | 100.8% | PTR | Curtailment | As per GSS and LD instruction Plant tripped due to generation curtailment | 10:33 |  | 0.62222 | 0.62222 | -10.55 | 4.3833 | 4.3833 | 4.3833 | All incomer was charged after instruction from LD & GSS | Close | 4.4177 | 3.5169 | 361583.926
52 | 2025-06-03 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25069 | 0.77778 | 12.65 | IS10 | Inv3 | M2 | SCB4 | Str_Typ2(545*29) | String | 0 | 0 | Str_Typ2(545*29) | 15.805 | 0.01305% | String | Fuse Damage | String Breakdown due to the Fuse Damage | 8:40 |  | 0.49306 | 19:00 | -8.6667 | 3.1667 | 10.3333 | 10.3333 | Fuse Replace Work done after generation & String Charge. | Close | 0.001348 | 2.1 | 27.9464
53 | 2025-06-04 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25139 | 0.77847 | 12.65 | IS14 | Inv2 | M4 | SCB3 | Str_Typ2(545*29) | String | 0 | 0 | Str_Typ2(545*29) | 15.805 | 0.01305% | String | Y Connector Damage | Y Connector Damage | 9:30 |  | 0.52083 | 18:30 | -9.5 | 3 | 9 | 9 | Y Connector Replace work at after generation & String Charge. | Close | 0.0011741 | 0.92 | 12.2432
54 | 2025-06-04 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25139 | 0.77847 | 12.65 | IS12 | Inv1 | M2 | SCB4 | Str_Typ3(550*29) | String | 0 | 0 | Str_Typ3(550*29) | 15.95 | 0.01316% | String |  | MC4 Connector Not Proper Connect. | 14:20 |  | 0.72917 | 18:40 | -14.3333 | 3.1667 | 4.3333 | 4.3333 | MC4 Connector Proper Connect & than String Charge. | Close | 0.00057048 | 0.85 | 11.4154
55 | 2025-06-10 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25208 | 0.78125 | 12.7 | IS13 |  |  |  |  | Tx | 0 | 1 | IS13Tx | 6701.32 | 5.531% | IDT | IDT tripped due to Overcurrent | IDT tripped due to Overcurrent | 10:15 |  | 0.44792 | 12:37 | -10.25 | 0.5 | 2.3667 | 2.3667 | Overcurrent setting check by project team and change the setting | Close | 0.1309 | 0.211 | 1190.5699
56 | 2025-06-12 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25069 | 0.74653 | 11.9 | [5 empty] | Power_TX | 0 | 1 | Power_TX | 122106 | 100.8% | PTR | PTR tripped due to over current and earth fault | Phase3 During the heavy wind 33kv TL line conductor were touch each other phase R,Y | 16:22 |  | 0.6875 | 16:53 | -16.3667 | 0.13333 | 0.51667 | 0.51667 | phase3 TL Line visual inspection done wind position normal then after gate trial and charge | Close | 0.52072 | 0.064 | 6580.0481
57 | 2025-06-13 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25069 | 0.77639 | 12.6167 | IS12 |  |  |  |  | Tx | 0 | 1 | IS12Tx | 6170.4 | 5.093% | IDT | IDT tripped due to Overcurrent | IDT tripped due to Overcurrent | 13:05 |  | 0.59722 | 14:27 | -13.0833 | 1.25 | 1.3667 | 1.3667 | Overcurrent setting check by project team and change the setting | Close | 0.069604 | 1.268 | 6587.8646
58 | 2025-06-13 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25069 | 0.77639 | 12.6167 | IS12 | Inv1 | M1 | SCB3 | Str_Typ2(545*29) | String | 0 | 0 | Str_Typ2(545*29) | 15.805 | 0.01305% | String | Series Connection Worng. | String Breakdown due to the Module Interchange. | 14:30 |  | 0.72222 | 18:30 | -14.5 | 2.8333 | 4 | 4 | After Series Conncection Proper Done Than String Done. | Close | 0.00052181 | 1.22 | 16.2355
59 | 2025-06-13 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25069 | 0.77639 | 12.6167 | IS11 | Inv1 | M3 | SCB5 | Str_Typ3(550*29) | String | 0 | 0 | Str_Typ3(550*29) | 15.95 | 0.01316% | String | MC4 Connector was Open | String Breakdown due to the MC4 Connector was Open. | 13:40 |  | 0.71528 | 18:30 | -13.6667 | 3.5 | 4.8333 | 4.8333 | After Connect MC4 Connector & than String Charge. | Close | 0.00063631 | 1.34 | 17.9961
60 | 2025-06-18 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25417 | 0.77431 | 12.4833 | IS10 | Inv4 | M1 | SCB3 | Str_Typ2(545*29) | String | 0 | 0 | Str_Typ2(545*29) | 15.805 | 0.01305% | String | Series Connection Worng. | String Breakdown due to Series Connection not Proper. | 12:30 |  | 0.68889 | 18:40 | -12.5 | 4.0333 | 6.1667 | 6.1667 | Series Connection Correct and then Charge String. | Close | 0.00080446 | 1.02 | 13.574
61 | 2025-06-18 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.25417 | 0.77431 | 12.4833 | IS10 | Inv4 | M1 | SCB4 | Str_Typ2(545*29) | String | 0 | 0 | Str_Typ2(545*29) | 15.805 | 0.01305% | String | MC4 Connector was Open | String Breakdown due to the MC4 Connector was Open. | 14:43 |  | 0.69444 | 18:30 | -14.7167 | 1.95 | 3.7833 | 3.7833 | After Connect MC4 Connector & than String Charge. | Close | 0.00049355 |  | 0
62 | 2025-06-26 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26944 | 0.77014 | 12.0167 | IS14 | Inv1 |  |  |  |  | 1 | 1 | IS14Inv1 | 0 | 0% | String | Inv Trip By Project Team | DC Capacity increase Durating Night Time | 6:28 |  | 0.50833 | 12:18 | -6.4667 | 5.7333 | 5.8333 | 5.8333 | Inv Start After Rain Over | Close | 0 | 0.18 | 0
63 | 2025-06-27 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26458 | 0.775 | 12.25 | IS14 |  |  |  |  | Tx | 0 | 1 | IS14Tx | 8906.48 | 7.351% | String | IDT Tripped due to Project work | DC Capacity increase | 16:00 |  | 0.66667 | 18:30 | -16 | 0 | 2.5 | 2.5 | SCB Cable work completed | Close | 0.18378 | 1.01 | 7574.2487
64 | 2025-06-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26458 | 0.76319 | 11.9667 | IS11 | Inv1 | M4 | SCB4 | Str_Typ2(545*29) |  | 0 | 0 | Str_Typ2(545*29) | 15.805 | 0.01305% | String | String No 04 Breakdown Due to Sreise Open | String No 04 Breakdown Due to Sreise Open | 12:30 |  | 0.6875 | 18:30 | -12.5 | 4 | 6 | 6 | After Generation String Rectification Done | Close |  | 1.61 | 21.4256
65 | 2025-06-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26458 | 0.76319 | 11.9667 | IS11 | Inv1 | M4 | SCB1 | Str_Typ4(540*58) |  | 0 | 0 | Str_Typ4(540*58) | 31.32 | 0.02585% | String | String No 07 Breakdown Due to Sreise Open | String No 07 Breakdown Due to Sreise Open | 12:40 |  | 0.6875 | 18:40 | -12.6667 | 3.8333 | 6 | 6 | After Generation String Rectification Done | Close | 0.0015511 | 1.59 | 41.9306
66 | 2025-06-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26458 | 0.76319 | 11.9667 | IS11 | Inv1 | M3 | SCB2 | Str_Typ4(540*58) |  | 0 | 0 | Str_Typ4(540*58) | 31.32 | 0.02585% | String | String No 02 Breakdown Due to Sreise Open | String No 02 Breakdown Due to Sreise Open | 12:40 |  | 0.6875 | 18:30 | -12.6667 | 3.8333 | 5.8333 | 5.8333 | After Generation String Rectification Done | Close | 0.001508 | 1.5 | 39.5572
67 | 2025-06-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26458 | 0.76319 | 11.9667 | IS11 | Inv1 | M3 | SCB4 | Str_Typ5(545*58) |  | 0 | 0 | Str_Typ5(545*58) | 31.61 | 0.02609% | String | String No 06 Breakdown Due to Sreise Open | String No 06 Breakdown Due to Sreise Open | 12:30 |  | 0.6875 | 18:45 | -12.5 | 4 | 6.25 | 6.25 | After Generation String Rectification Done | Close | 0.0016307 | 1.2 | 31.9387
68 | 2025-06-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26458 | 0.76319 | 11.9667 | IS11 | Inv1 | M2 | SCB2 | Str_Typ3(550*29) |  | 0 | 0 | Str_Typ3(550*29) | 15.95 | 0.01316% | String | String No 06 Breakdown Due to Sreise Open | String No 06 Breakdown Due to Sreise Open | 12:45 |  | 0.6875 | 19:00 | -12.75 | 3.75 | 6.25 | 6.25 | After Generation String Rectification Done | Close | 0.00082281 | 1.31 | 17.5932
69 | 2025-06-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26458 | 0.76319 | 11.9667 | IS12 | Inv1 | M3 | SCB6 | Str_Typ2(545*29) |  | 0 | 0 | Str_Typ2(545*29) | 15.805 | 0.01305% | String | String No 06&07 Breakdown Due to MC4 Connector Damage. | String No 06&07 Breakdown Due to MC4 Connector Damage. | 14:20 |  | 0.6875 | 19:10 | -14.3333 | 2.1667 | 4.8333 | 4.8333 | After Generation String Rectification Done | Close | 0.00063052 | 1.2 | 15.9694
70 | 2025-06-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26458 | 0.76319 | 11.9667 | IS12 | Inv1 | M2 | SCB6 | Str_Typ2(545*29) |  | 0 | 0 | Str_Typ2(545*29) | 15.805 | 0.01305% | String | String No 01&09 Breakdown Due to Sreise Open | String No 01&09 Breakdown Due to Sreise Open | 14:35 |  | 0.6875 | 19:30 | -14.5833 | 1.9167 | 4.9167 | 4.9167 | After Generation String Rectification Done | Close | 0.00064139 | 1.4 | 18.6309
71 | 2025-06-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26458 | 0.76319 | 11.9667 | IS12 | Inv1 | M2 | SCB4 | Str_Typ2(545*29) |  | 0 | 0 | Str_Typ2(545*29) | 15.805 | 0.01305% | String | String No 06 Breakdown Due to Y Connector Damage | String No 06 Breakdown Due to Y Connector Damage | 14:22 |  | 0.6875 | 18:30 | -14.3667 | 2.1333 | 4.1333 | 4.1333 | After Generation String Rectification Done | Close | 0.0005392 | 1.43 | 19.0302
72 | 2025-06-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26458 | 0.76319 | 11.9667 | IS13 | Inv2 | M1 | SCB2 | Str_Typ3(550*29) |  | 0 | 0 | Str_Typ3(550*29) | 15.95 | 0.01316% | String | String No 02 Breakdown Due to Sreise Open | String No 02 Breakdown Due to Sreise Open | 14:20 |  | 0.6875 | 18:30 | -14.3333 | 2.1667 | 4.1667 | 4.1667 | After Generation String Rectification Done | Close | 0.00054854 | 1.6 | 21.4878
73 | 2025-06-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26458 | 0.76319 | 11.9667 | IS11 | Inv1 | M4 | SCB5 | Str_Typ2(545*29) |  | 0 | 0 | Str_Typ2(545*29) | 15.805 | 0.01305% | String | String No 05 Breakdown Due to MC4 Connector Damage. | String No 05 Breakdown Due to MC4 Connector Damage. | 12:30 |  | 0.6875 | 18:40 | -12.5 | 4 | 6.1667 | 6.1667 | After Generation String Rectification Done | Close | 0.00080446 | 1.6 | 21.2925
74 | 2025-06-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26458 | 0.76319 | 11.9667 | IS11 | Inv1 | M3 | SCB3 | Str_Typ2(545*29) |  | 0 | 0 | Str_Typ2(545*29) | 15.805 | 0.01305% | String | String No 08 Breakdown Due to Sreise Open | String No 08 Breakdown Due to Sreise Open | 12:35 |  | 0.6875 | 18:40 | -12.5833 | 3.9167 | 6.0833 | 6.0833 | After Generation String Rectification Done | Close | 0.00079359 | 1.6 | 21.2925
75 | 2025-06-29 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26458 | 0.76319 | 11.9667 | IS12 | Inv1 | M3 | SCB5 | Str_Typ3(550*29) |  | 0 | 0 | Str_Typ3(550*29) | 15.95 | 0.01316% | String | String No 02 Breakdown Due to Sreise Open | String No 02 Breakdown Due to Sreise Open | 12:40 |  | 0.6875 | 18:40 | -12.6667 | 3.8333 | 6 | 6 | After Generation String Rectification Done | Close | 0.0007899 | 1.32 | 17.7275
76 | 2025-06-30 | 2026 | 2025 | Year_1 | Year_1 | 2025-06-01 | 30 | 0.26944 | 0.78264 | 12.3167 | IS10 | Inv2 | M2 |  |  |  | 1 | 1 | IS10Inv2M2 | 2041.6 | 1.685% | Inverter | Internal Fault | Internal Fault | 12:26 |  | 0.52083 | 13:20 | -12.4333 | 0.066667 | 0.9 | 0.9 | Check All SCB Cable is Healthey | Close | 0.015166 | 0.22 | 378.186
77 | 2025-07-01 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.26597 | 0.77778 | 12.2833 | IS10 | Inv2 | M2 |  |  |  | 1 | 1 | IS10Inv2M2 | 2041.6 | 1.685% | Inverter | Internal Fault | Unit Breakdown due to DC Component Fault | 8:54 |  | 0.375 | 9:49 | -8.9 | 0.1 | 0.91667 | 0.91667 | Check Voc All SCB Cable is Healthey | Close | 0.015447 | 0.18 | 309.4249
78 | 2025-07-02 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.26042 | 0.79306 | 12.7833 | IS6 | Inv1 |  |  |  |  | 1 | 1 | IS6Inv1 | 3716.35 | 3.067% | Inverter | Emergency Shutdown | Emergency Shutdown | 9:59 |  | 0.42708 | 10:37 | -9.9833 | 0.26667 | 0.63333 | 0.63333 | Visual Check All Inverter & IDT Found ok Then Inverter Charge. | Close | 0.019427 | 0.42 | 1314.25
79 | 2025-07-02 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.26042 | 0.79306 | 12.7833 | IS6 | Inv2 | M2 |  |  |  | 1 | 1 | IS6Inv2M2 | 1850.2 | 1.527% | Inverter | Emergency Shutdown | Emergency Shutdown | 9:59 |  | 0.42708 | 11:26 | -9.9833 | 0.26667 | 1.45 | 1.45 | Visual Check All Inverter & IDT Found ok Then Inverter Charge. | Close | 0.022143 | 0.95 | 1479.975
80 | 2025-07-02 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.26042 | 0.79306 | 12.7833 | IS6 | Inv2 |  |  |  |  | 1 | 1 | IS6Inv2 | 3732.3 | 3.081% | Inverter | Emergency Shutdown | Emergency Shutdown | 9:59 |  | 0.42708 | 10:37 | -9.9833 | 0.26667 | 0.63333 | 0.63333 | Visual Check All Inverter & IDT Found ok Then Inverter Charge. | Close | 0.01951 | 0.42 | 1319.8906
81 | 2025-07-02 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.26042 | 0.79306 | 12.7833 | IS8 | Inv1 |  |  |  |  | 1 | 1 | IS8Inv1 | 5992.415 | 4.946% | Inverter | Emergency Shutdown | Emergency Shutdown | 9:47 |  | 0.42708 | 11:18 | -9.7833 | 0.46667 | 1.5167 | 1.5167 | Visual Check All Inverter & IDT Found ok Then Inverter Charge. | Close | 0.075015 | 0.99 | 4995.1573
82 | 2025-07-04 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25764 | 0.77292 | 12.3667 | IS10 | Inv2 | M2 |  |  |  | 1 | 1 | IS10Inv2M2 | 2041.6 | 1.685% | Unit | Unit Brakdown due the soft start foult of unit 02 | Unit Brakdown due the soft start foult of unit 02 | 10:56 |  | 0.46528 | 12:46 | -10.9333 | 0.23333 | 1.8333 | 1.8333 | Check Voc of INV 02 Unit 02 DC Cable Found Floating Voltage Not Proper & Damage Module has been Bypassed and then Unit 02 Charge. | Close | 0.030894 | 0.92 | 1581.505
83 | 2025-07-05 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25486 | 0.77361 | 12.45 | IS3 |  |  |  |  | Tx | 0 | 1 | IS3Tx | 8911.45 | 7.355% | Inverter | ICR 03 Trip due to Master Relay Trip | ICR 03 Trip due to the Over Current & Earth Fault | 12:00 |  | 0.50694 | 12:20 | -12 | 0.16667 | 0.33333 | 0.33333 | Check Visual all is Normal Candition and then Charge | Close | 0.024518 | 0.25 | 1875.8602
84 | 2025-07-05 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25486 | 0.77361 | 12.45 | IS14 |  |  |  |  | Tx | 0 | 1 | IS14Tx | 8906.48 | 7.351% | Inverter | Incomer 04 shudown due to the Over Currrent Fault | Incomer 04 shudown due to the Over Currrent Fault | 14:28 |  | 0.60764 | 15:07 | -14.4667 | 0.11667 | 0.65 | 0.65 | Check Visual all is Normal Candition and then Charge | Close | 0.047784 | 0.04 | 299.9702
85 | 2025-07-05 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25486 | 0.77361 | 12.45 | IS4 | Inv1 |  |  |  |  | 1 | 1 | IS4Inv1 | 3865.905 | 3.191% | Inverter | Inverter Brakdown due to the GFDI Pro Fault | Inverter Brakdown due to the GFDI Pro Fault | 12:27 |  | 0.51389 | 12:36 | -12.45 | -0.11667 | 0.15 | 0.15 | Check all SCB Cable is Voltage Floating ok Then INV Charge. | Close | 0.0047863 | 0.09 | 292.9583
86 | 2025-07-05 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25486 | 0.77361 | 12.45 | IS4 | Inv2 |  |  |  |  | 1 | 1 | IS4Inv2 | 4409.05 | 3.639% | Inverter | Inverter Brakdown due to the GFDI Pro Fault | Inverter Brakdown due to the GFDI Pro Fault | 12:27 |  | 0.51389 | 12:36 | -12.45 | -0.11667 | 0.15 | 0.15 | Check all SCB Cable is Voltage Floating ok Then INV Charge. | Close | 0.0054588 | 0.09 | 334.1178
87 | 2025-07-05 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25486 | 0.77361 | 12.45 | IS10 | Inv2 | M2 |  |  |  | 1 | 1 | IS10Inv2M2 | 2041.6 | 1.685% | Unit | Unit Brakdown due the DC Injection Pro | Unit Brakdown due the DC Injection Pro | 6:30 |  | 0.27778 | 18:40 | -6.5 | 0.16667 |  | 12.1667 | Restoration Work Is Underprogress | Open | 0.20502 | 3.24 | 5569.6481
88 | 2025-07-06 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25972 | 0.78542 | 12.6167 | IS10 | Inv2 | M1 |  |  |  | 1 | 1 | IS10Inv2M1 | 478.5 | 0.3949% | Unit | Unit Brakdown due the DC Injection Pro | Unit Brakdown due the DC Injection Pro | 6:30 |  | 0.27778 | 18:40 | -6.5 | 0.16667 |  | 12.1667 | Restoration Work Is Underprogress | Open | 0.048052 | 3.04 | 1224.8069
89 | 2025-07-06 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25972 | 0.78542 | 12.6167 | IS10 | Inv2 | M2 |  |  |  | 1 | 1 | IS10Inv2M2 | 2041.6 | 1.685% | Unit | Unit Brakdown due the DC Injection Pro | Unit Brakdown due the DC Injection Pro | 6:30 |  | 0.27778 | 18:40 | -6.5 | 0.16667 |  | 12.1667 | Restoration Work Is Underprogress | Open | 0.20502 | 3.04 | 5225.8427
90 | 2025-07-06 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25972 | 0.78542 | 12.6167 | IS10 | Inv1 |  |  |  |  | 1 | 1 | IS10Inv1 | 2583.9 | 2.133% | Inverter | Unit Brakdown due the DC Injection Pro | Unit Brakdown due the DC Injection Pro | 6:30 |  | 0.27778 | 18:40 | -6.5 | 0.16667 |  | 12.1667 | Restoration Work Is Underprogress | Open | 0.25948 | 3.04 | 6613.9572
91 | 2025-07-06 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25972 | 0.78542 | 12.6167 | IS10 | Inv1 | M1 |  |  |  | 1 | 1 | IS10Inv1M1 | 1914 | 1.58% | Inverter | Inverter Brakdown due to the Stand By Fault | Inverter Brakdown due to the Stand by Fault | 12:30 |  | 0.52778 | 14:20 | -12.5 | 0.16667 | 1.8333 | 1.8333 | Inverter Restart & then Charge. | Close | 0.028963 | 0.34 | 547.9399
92 | 2025-07-06 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25972 | 0.78542 | 12.6167 | IS10 | Inv1 | M2 |  |  |  | 1 | 1 | IS10Inv1M2 | 669.9 | 0.5529% | Inverter | Inverter Brakdown due to the Stand By Fault | Inverter Brakdown due to the Stand by Fault | 12:30 |  | 0.52778 | 14:20 | -12.5 | 0.16667 | 1.8333 | 1.8333 | Inverter Restart & then Charge. | Close | 0.010137 | 0.34 | 191.779
93 | 2025-07-07 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.26181 | 0.76736 | 12.1333 | IS6 | Inv2 | M1 |  |  |  | 1 | 1 | IS6Inv2M1 | 1882.1 | 1.553% | Unit | Unit Breakdown due to the GFDI pro Fault | Unit Breakdown due to the GFDI pro Fault | 15:20 |  | 0.64583 | 15:42 | -15.3333 | 0.16667 | 0.36667 | 0.36667 | Check SCB 2-2-6 String Cable Found DC String Cable Graund Fault then Isolate Faulty Cable and the Unit Charge | Close | 0.005696 | 0.02 | 31.6946
94 | 2025-07-07 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.26181 | 0.76736 | 12.1333 | IS6 | Inv2 | M2 |  |  |  | 1 | 1 | IS6Inv2M2 | 1850.2 | 1.527% | Unit | Unit Breakdown due to the GFDI pro Fault | Unit Breakdown due to the GFDI pro Fault | 15:53 |  | 0.65972 | 16:46 | -15.8833 | -0.05 | 0.88333 | 0.88333 | Check SCB 2-2-6 String Cable Found DC String Cable Graund Fault then Isolate Faulty Cable and the Unit Charge | Close | 0.01349 | 0.14 | 218.1016
95 | 2025-07-08 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.26806 | 0.77014 | 12.05 | IS10 | Inv2 | M1 |  |  |  | 1 | 1 | IS10Inv2M1 | 478.5 | 0.3949% | Unit | Unit Breakdown due to the GFDI pro Fault | Unit Breakdown due to the GFDI pro Fault | 13:42 |  | 0.58681 | 15:55 | -13.7 | 0.38333 | 2.2167 | 2.2167 | Check SCB 2-1-4 String Cable Found DC String Cable Graund Fault then Isolate Faulty Cable and the Unit Charge | Close | 0.0087547 | 0.53 | 213.5354
96 | 2025-07-08 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.26806 | 0.77014 | 12.05 | IS10 | Inv2 | M2 |  |  |  | 1 | 1 | IS10Inv2M2 | 2041.6 | 1.685% | Unit | Unit S/down to Unit 01 fault restoration | Unit S/down to Unit 01 fault restoration | 15:12 |  | 0.63333 | 15:50 | -15.2 | 0 | 0.63333 | 0.63333 | Unit 01 Fault Restoration Work Compalete after then Unit 02 Charge. | Close | 0.010672 | 0.14 | 240.6638
97 | 2025-07-08 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.26806 | 0.77014 | 12.05 | IS6 | Inv2 | M2 | SCB6 | Str_Typ2(545*29) | MCR_MVP_SolarF5 | 0 | 0 | Str_Typ2(545*29) | 15.805 | 0.01305% | String | String Brakdown due to the PV 07 Graound Fault. | String Brakdown due to the PV 07 Graound Fault. | 6:00 |  | 0.60417 | 16:50 | -6 | 8.5 | 10.8333 | 10.8333 | Pv 07 of SCB 2-2-6 Replace the MC4 Connctor and then Pv 07 Charge. | Close | 0.0014132 | 2 | 26.6156
98 | 2025-07-11 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25486 | 0.78542 | 12.7333 | IS1 | Inv2 | M1 |  |  |  | 1 | 1 | IS1Inv2M1 | 1560.49 | 1.288% | Unit | Unit Breakdown due to the GFDI pro Fault | Unit Breakdown due to the GFDI pro Fault | 11:29 |  | 0.48264 | 11:40 | -11.4833 | 0.1 | 0.18333 | 0.18333 | unit 01 Auto start | Close | 0.0023614 | 0.23 | 302.2045
99 | 2025-07-11 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25486 | 0.78542 | 12.7333 | IS1 | Inv2 | M2 |  |  |  | 1 | 1 | IS1Inv2M2 | 1582.53 | 1.306% | Unit | Unit Breakdown due to the GFDI pro Fault | Unit Breakdown due to the GFDI pro Fault | 11:29 |  | 0.48264 | 11:46 | -11.4833 | 0.1 | 0.28333 | 0.28333 | Isolate the Faulty String Cable and Then Uint 02 Charge. | Close | 0.0037009 | 0.32 | 426.3969
100 | 2025-07-11 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25486 | 0.78542 | 12.7333 | IS1 | Inv2 | M3 |  |  |  | 1 | 1 | IS1Inv2M3 | 1473.49 | 1.216% | Unit | Unit Breakdown due to the GFDI pro Fault | Unit Breakdown due to the GFDI pro Fault | 11:29 |  | 0.48264 | 11:40 | -11.4833 | 0.1 | 0.18333 | 0.18333 | unit 01 Auto start | Close | 0.0022297 | 0.23 | 285.3561
101 | 2025-07-11 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25486 | 0.78542 | 12.7333 | IS1 | Inv2 | M4 |  |  |  | 1 | 1 | IS1Inv2M4 | 1675.33 | 1.383% | Unit | Unit Breakdown due to the GFDI pro Fault | Unit Breakdown due to the GFDI pro Fault | 11:29 |  | 0.48264 | 11:40 | -11.4833 | 0.1 | 0.18333 | 0.18333 | unit 01 Auto start | Close | 0.0025351 | 0.23 | 324.4444
102 | 2025-07-11 | 2026 | 2025 | Year_1 | Year_1 | 2025-07-01 | 31 | 0.25486 | 0.78542 | 12.7333 | IS1 | Inv2 | M2 | SCB2 | Str_Typ5(545*58) | MCR_MVP_SolarF4 | 0 | 0 | Str_Typ5(545*58) | 31.61 | 0.02609% | String | String Brakdown due to the PV 04 Graound Fault. | String Brakdown PV 04 Graound Fault due to cut by tractor rotavator | 11:29 |  | 0.48264 | 12:05 | -11.4833 | 0.1 | 0.6 | 0.6 | Pv 04 of SCB 2-2-2 Replace the MC4 Connctor & 06 Sq.mm dc cable then Pv 04 Charge. | Close | 0.00015654 | 0.63 | 16.7678
103 |  | 1900 | 1900 |  |  | 1899-12-31 | 31 | 0 | 0 | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE!
104 |  | 1900 | 1900 |  |  | 1899-12-31 | 31 | 0 | 0 | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE!
105 |  | 1900 | 1900 |  |  | 1899-12-31 | 31 | 0 | 0 | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE!
106 |  | 1900 | 1900 |  |  | 1899-12-31 | 31 | 0 | 0 | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE!
107 |  | 1900 | 1900 |  |  | 1899-12-31 | 31 | 0 | 0 | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE!
108 |  | 1900 | 1900 |  |  | 1899-12-31 | 31 | 0 | 0 | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE!
109 |  | 1900 | 1900 |  |  | 1899-12-31 | 31 | 0 | 0 | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE!
110 |  | 1900 | 1900 |  |  | 1899-12-31 | 31 | 0 | 0 | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE!
111 |  | 1900 | 1900 |  |  | 1899-12-31 | 31 | 0 | 0 | 0 | [6 empty] | 1 | 1 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  |  | #VALUE!
Formulas:
Sunrise Time (POA>20 W/m2) = IFERROR(XLOOKUP(PA_8[[#This Row],[Date]],Input_Raw!$A:$A,Input_Raw!F:F),"")
Sunset Time (POA<20 W/m2) = IFERROR(XLOOKUP(PA_8[[#This Row],[Date]],Input_Raw!$A:$A,Input_Raw!G:G),"")
Month Year = PA_8[[#This Row],[Date]]-DAY(PA_8[[#This Row],[Date]])+1
Days = DAY(EOMONTH(PA_8[[#This Row],[Month Year]],0))

## Grid_BD
Sr. No. | Date | Finacial Year | Calendor Year | Operating Year | Affected Feeder | Op. Hours | Concumaer | Plant Equivalent Weightage | Breakdown Description | Breakdown Type | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | POA Lost (kWh/m2) | Estimated Energy Loss (kWh) | Curtailment Order imit. | EGA_Including_CurtailmentOrder
1 | 2025-06-01 | 2026 | 2025 | Year_1 | Line1 | 12.7667 |  | 100% | All Incomer Manual Trip Due To Zero load From GSS 132 KV Line Motala and LDC Nagpur at 10:33 AM To 14:56 PM |  | 0.43958 | 0.43958 | 0.62222 | 0 | 4.3833 | 4.3833 | Generation start(All incomer) after permission getting from LD nagpur |  | 4.3833 | 3.82 | 388248.1972 | 0 | 100%
2 | 2025-06-24 | 2026 | 2025 | Year_1 | Line1 | 11.8667 |  | 100% | 132 kV TL line Manual Trip due to CT & PT Oil Leakage Attend work From GSS Side. |  | 0.46944 | 0.46944 | 0.82708 | 0 | 8.5833 | 8.5833 | 132 kV TL CT & PT Oil Leakage attend work Complete and then Charge Grid Line. |  | 8.5833 | 1.02 | 107533.3846 | 0 | 100%
3 |  | 1900 | 1900 | Year_1 | Line1 | [8 empty] | 0 | 0 | 0 | [6 empty] | 100%
4 |  | 1900 | 1900 | Year_1 | Line1 | [8 empty] | 0 | 0 | 0 | [6 empty] | 100%
5 |  | 1900 | 1900 | Year_1 | Line1 | [8 empty] | 0 | 0 | 0 | [6 empty] | 100%
6 |  | 1900 | 1900 | Year_1 | Line1 | [8 empty] | 0 | 0 | 0 | [6 empty] | 100%
7 |  | 1900 | 1900 | Year_1 | Line1 | [8 empty] | 0 | 0 | 0 | [6 empty] | 100%
8 |  | 1900 | 1900 | Year_1 | Line1 | [8 empty] | 0 | 0 | 0 | [6 empty] | 100%
9 |  | 1900 | 1900 | Year_1 | Line1 | [8 empty] | 0 | 0 | 0 | [6 empty] | 100%
10 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
11 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
12 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
13 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
14 |  | 1900 | 1900 | Year_1 | [9 empty] | 0 | 0 | 0 | [6 empty] | 100%
b

## MC
Sr. No. | Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Cycle Number | Resources | IS1Inv1M1 | IS1Inv1M2 | IS1Inv1M3 | IS1Inv1M4 | IS1Inv2M1 | IS1Inv2M2 | IS1Inv2M3 | IS1Inv2M4 | IS2Inv3M1 | IS2Inv3M2 | IS2Inv3M3 | IS2Inv3M4 | IS2Inv4M1 | IS2Inv4M2 | IS2Inv4M3 | IS2Inv4M4 | IS3Inv5M1 | IS3Inv5M2 | IS3Inv6M1 | IS3Inv6M2 | IS4Inv7M1 | IS4Inv7M2 | IS4Inv8M1 | IS4Inv8M2 | IS4Inv9M1 | IS4Inv9M2 | IS4Inv10M1 | IS4Inv10M2 | Total NO. Module cleaned | Morning Start Time | Morning End Time | Evening Start Time | Evening End time | Brush/MOP Replcemnet | Water Test Report | Remarks for the day
1 | 2024-02-01 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
2 | 2024-02-02 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
3 | 2024-02-03 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
4 | 2024-02-04 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 0 | [28 empty] | 0
5 | 2024-02-05 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
6 | 2024-02-06 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
7 | 2024-02-07 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
8 | 2024-02-08 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
9 | 2024-02-09 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
10 | 2024-02-10 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 0 | [28 empty] | 0
11 | 2024-02-11 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
12 | 2024-02-12 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
13 | 2024-02-13 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
14 | 2024-02-14 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
15 | 2024-02-15 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
16 | 2024-02-16 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
17 | 2024-02-17 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
18 | 2024-02-18 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 0 | [28 empty] | 0
19 | 2024-02-19 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
20 | 2024-02-20 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
21 | 2024-02-21 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
22 | 2024-02-22 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
23 | 2024-02-23 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
24 | 2024-02-24 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
25 | 2024-02-25 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 0 | [28 empty] | 0
26 | 2024-02-26 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
27 | 2024-02-27 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
28 | 2024-02-28 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
29 | 2024-02-29 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | 1 | 2 | [28 empty] | 0
30 | 2024-03-01 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
31 | 2024-03-02 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
32 | 2024-03-03 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
33 | 2024-03-04 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [30 empty] | 0
34 | 2024-03-05 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [30 empty] | 0
35 | 2024-03-06 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
36 | 2024-03-07 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
37 | 2024-03-08 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
38 | 2024-03-09 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
39 | 2024-03-10 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [30 empty] | 0
40 | 2024-03-11 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
41 | 2024-03-12 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
42 | 2024-03-13 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
43 | 2024-03-14 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
44 | 2024-03-15 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
45 | 2024-03-16 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
46 | 2024-03-17 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [30 empty] | 0
47 | 2024-03-18 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
48 | 2024-03-19 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
49 | 2024-03-20 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
50 | 2024-03-21 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
51 | 2024-03-22 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
52 | 2024-03-23 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 2 | 2 | [28 empty] | 0
53 | 2024-03-24 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [30 empty] | 0
54 | 2024-03-25 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 3 | 2 | [28 empty] | 0
55 | 2024-03-26 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 3 | 2 | [28 empty] | 0
56 | 2024-03-27 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 3 | 2 | [28 empty] | 0
57 | 2024-03-28 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 3 | 2 | [28 empty] | 0
58 | 2024-03-29 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | 3 | 2 | [28 empty] | 0
59 | 2024-03-30 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [30 empty] | 0
60 | 2024-03-31 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [30 empty] | 0
61 | 2024-04-01 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 3 | 2 | [28 empty] | 0
62 | 2024-04-02 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 3 | 2 | [28 empty] | 0
63 | 2024-04-03 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 3 | 2 | [28 empty] | 0
64 | 2024-04-04 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 3 | 2 | [28 empty] | 0
65 | 2024-04-05 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 3 | 2 | [28 empty] | 0
66 | 2024-04-06 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 3 | 2 | [28 empty] | 0
67 | 2024-04-07 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 3 | 2 | [28 empty] | 0
68 | 2024-04-08 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 3 | 2 | [28 empty] | 0
69 | 2024-04-09 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 3 | 2 | [28 empty] | 0
70 | 2024-04-10 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [30 empty] | 0
71 | 2024-04-11 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 3 | 2 | [28 empty] | 0
72 | 2024-04-12 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 3 | 2 | [28 empty] | 0
73 | 2024-04-13 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 3 | 2 | [28 empty] | 0
74 | 2024-04-14 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [30 empty] | 0
75 | 2024-04-15 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 3 | 2 | [28 empty] | 0
76 | 2024-04-16 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 4 | 2 | [28 empty] | 0
77 | 2024-04-17 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 4 | 2 | [28 empty] | 0
78 | 2024-04-18 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 4 | 2 | [28 empty] | 0
79 | 2024-04-19 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 4 | 2 | [28 empty] | 0
80 | 2024-04-20 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 4 | 2 | [28 empty] | 0
81 | 2024-04-21 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [30 empty] | 0
82 | 2024-04-22 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [30 empty] | 0
83 | 2024-04-23 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [30 empty] | 0
84 | 2024-04-24 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 4 | 2 | [28 empty] | 0
85 | 2024-04-25 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 4 | 2 | [28 empty] | 0
86 | 2024-04-26 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 4 | 2 | [28 empty] | 0
87 | 2024-04-27 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 4 | 2 | [28 empty] | 0
88 | 2024-04-28 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 4 | 2 | [28 empty] | 0
89 | 2024-04-29 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [30 empty] | 0
90 | 2024-04-30 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [30 empty] | 0
91 | 2024-05-01 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [30 empty] | 0
92 | 2024-05-02 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [30 empty] | 0
93 | 2024-05-03 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [30 empty] | 0
94 | 2024-05-04 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [30 empty] | 0
95 | 2024-05-05 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [30 empty] | 0
96 | 2024-05-06 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [30 empty] | 0
97 | 2024-05-07 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [30 empty] | 0
98 | 2024-05-08 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
99 | 2024-05-09 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
100 | 2024-05-10 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
101 | 2024-05-11 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
102 | 2024-05-12 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
103 | 2024-05-13 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
104 | 2024-05-14 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
105 | 2024-05-15 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
106 | 2024-05-16 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
107 | 2024-05-17 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
108 | 2024-05-18 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
109 | 2024-05-19 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
110 | 2024-05-20 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
111 | 2024-05-21 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
112 | 2024-05-22 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
113 | 2024-05-23 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
114 | 2024-05-24 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
115 | 2024-05-25 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
116 | 2024-05-26 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
117 | 2024-05-27 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
118 | 2024-05-28 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
119 | 2024-05-29 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
120 | 2024-05-30 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
120 | 2024-05-31 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Water Tanker | [28 empty] | 0
122 | 2024-06-01 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0
123 | 2024-06-02 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0
124 | 2024-06-03 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0
125 | 2024-06-04 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0
126 | 2024-06-05 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0
127 | 2024-06-06 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0
127 | 2024-06-07 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-08 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-09 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-10 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-11 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-12 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-13 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0 |  |  | 0.16667 | 0.375 | MOP |  | Cleaning Stop due to Fanbalt Broken
127 | 2024-06-14 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-15 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-16 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | [29 empty] | 0 | [6 empty] | Cleaning not done due to marriage in vendor's family
127 | 2024-06-17 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | [29 empty] | 0 | [6 empty] | Cleaning not done due to marriage in vendor's family
139 | 2024-06-18 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0 |  |  | 0.16667 | 0.375 | MOP |  | Cleaning stop due to Tractor pulli Broken
140 | 2024-06-19 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | [29 empty] | 0 | [6 empty] | Cleaning Stop due to Tractor under breakdown
141 | 2024-06-20 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | [29 empty] | 0 | [6 empty] | Cleaning Stop due to Tractor under breakdown
142 | 2024-06-21 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
143 | 2024-06-22 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0 |  |  | 0.20833 | 0.45833 | MOP
144 | 2024-06-23 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0 |  |  | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
145 | 2024-06-24 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0 |  |  | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
146 | 2024-06-25 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | 1 | Water Tanker | [28 empty] | 0 |  |  | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
147 | 2024-06-26 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [30 empty] | 0
148 | 2024-06-27 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [30 empty] | 0
149 | 2024-06-28 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [30 empty] | 0
150 | 2024-06-29 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [30 empty] | 0
151 | 2024-06-30 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [30 empty] | 0
152 | 2024-07-01 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
153 | 2024-07-02 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
154 | 2024-07-03 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
155 | 2024-07-04 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
156 | 2024-07-05 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
157 | 2024-07-06 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
158 | 2024-07-07 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
159 | 2024-07-08 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
160 | 2024-07-09 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
161 | 2024-07-10 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
162 | 2024-07-11 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
163 | 2024-07-12 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
164 | 2024-07-13 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
165 | 2024-07-14 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
166 | 2024-07-15 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
167 | 2024-07-16 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
168 | 2024-07-17 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
169 | 2024-07-18 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
170 | 2024-07-19 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
171 | 2024-07-20 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
172 | 2024-07-21 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
173 | 2024-07-22 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
174 | 2024-07-23 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
175 | 2024-07-24 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
176 | 2024-07-25 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
177 | 2024-07-26 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
177 | 2024-07-27 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
179 | 2024-07-28 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
180 | 2024-07-29 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
181 | 2024-07-30 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
182 | 2024-07-31 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
183 | 2024-08-01 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
Formulas:
Days = DAY(EOMONTH(MC[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## Wet MC
Sr. No. | Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Cycle Number | Resources | IS1Inv1M1 | IS1Inv1M2 | IS1Inv1M3 | IS1Inv1M4 | IS1Inv2M1 | IS1Inv2M2 | IS1Inv2M3 | IS1Inv2M4 | IS2Inv3M1 | IS2Inv3M2 | IS2Inv3M3 | IS2Inv3M4 | IS2Inv4M1 | IS2Inv4M2 | IS2Inv4M3 | IS2Inv4M4 | IS3Inv5M1 | IS3Inv5M2 | IS3Inv6M1 | IS3Inv6M2 | IS4Inv7M1 | IS4Inv7M2 | IS4Inv8M1 | IS4Inv8M2 | IS4Inv9M1 | IS4Inv9M2 | IS4Inv10M1 | IS4Inv10M2 | IS5Inv11M1 | IS5Inv11M2 | IS5Inv12M1 | IS5Inv12M2 | IS6Inv13M1 | IS6Inv13M2 | IS6Inv14M1 | IS6Inv14M2 | IS7Inv15M1 | IS7Inv16M1 | IS8Inv17M1 | IS8Inv17M2 | IS8Inv17M3 | IS8Inv17M4 | IS9Inv18M1 | IS9Inv18M2 | IS9Inv19M1 | IS9Inv19M2 | Total NO. Module cleaned | Morning Start Time | Morning End Time | Evening Start Time | Evening End time | Brush/MOP Replcemnet | Water Test Report | Remarks for the day
1 | 2024-02-01 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
2 | 2024-02-02 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
3 | 2024-02-03 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
4 | 2024-02-04 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
5 | 2024-02-05 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
6 | 2024-02-06 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
7 | 2024-02-07 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
8 | 2024-02-08 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
9 | 2024-02-09 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
10 | 2024-02-10 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
11 | 2024-02-11 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
12 | 2024-02-12 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
13 | 2024-02-13 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
14 | 2024-02-14 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
15 | 2024-02-15 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
16 | 2024-02-16 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
17 | 2024-02-17 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
18 | 2024-02-18 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
19 | 2024-02-19 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
20 | 2024-02-20 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
21 | 2024-02-21 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
22 | 2024-02-22 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
23 | 2024-02-23 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
24 | 2024-02-24 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
25 | 2024-02-25 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
26 | 2024-02-26 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
27 | 2024-02-27 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
28 | 2024-02-28 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
29 | 2024-02-29 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [48 empty] | 0
30 | 2024-03-01 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
31 | 2024-03-02 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
32 | 2024-03-03 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
33 | 2024-03-04 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
34 | 2024-03-05 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
35 | 2024-03-06 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
36 | 2024-03-07 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
37 | 2024-03-08 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
38 | 2024-03-09 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
39 | 2024-03-10 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
40 | 2024-03-11 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
41 | 2024-03-12 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
42 | 2024-03-13 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
43 | 2024-03-14 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
44 | 2024-03-15 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
45 | 2024-03-16 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
46 | 2024-03-17 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
47 | 2024-03-18 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
48 | 2024-03-19 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
49 | 2024-03-20 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
50 | 2024-03-21 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
51 | 2024-03-22 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
52 | 2024-03-23 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
53 | 2024-03-24 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
54 | 2024-03-25 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
55 | 2024-03-26 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
56 | 2024-03-27 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
57 | 2024-03-28 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
58 | 2024-03-29 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
59 | 2024-03-30 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
60 | 2024-03-31 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [48 empty] | 0
61 | 2024-04-01 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
62 | 2024-04-02 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
63 | 2024-04-03 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
64 | 2024-04-04 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
65 | 2024-04-05 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
66 | 2024-04-06 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 1 | 4 | [46 empty] | 0 | 0.35417 | 0.41667 | 0.66667 | 0.77083
67 | 2024-04-07 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 1 | 4 | [46 empty] | 0 | 0.28125 | 0.40625 | 0.6875 | 0.79167
68 | 2024-04-08 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 1 | 4 | [46 empty] | 0 | 0.23958 | 0.39583 | 0.64583 | 0.77083
69 | 2024-04-09 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
70 | 2024-04-10 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
71 | 2024-04-11 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 1 | 4 | [46 empty] | 0 | 0.23958 | 0.39583 | 0.64583 | 0.77083
72 | 2024-04-12 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 1 | 4 | [46 empty] | 0 | 0.22917 | 0.39583 | 0.60417 | 0.6875
73 | 2024-04-13 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 1 | 4 | [46 empty] | 0 | 0.21875 | 0.39583 | 0.625 | 0.6875
74 | 2024-04-14 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
75 | 2024-04-15 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 1 | 4 | [46 empty] | 0 | 0.22917 | 0.39583 | 0.60417 | 0.6875
76 | 2024-04-16 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 1 | 4 | [46 empty] | 0 | 0.22917 | 0.39583 | 0.60417 | 0.6875
77 | 2024-04-17 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | 1 | 4 | [46 empty] | 0 | 0.22917 | 0.39583 | 0.60417 | 0.6875
78 | 2024-04-18 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
79 | 2024-04-19 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
80 | 2024-04-20 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
81 | 2024-04-21 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
82 | 2024-04-22 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
83 | 2024-04-23 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
84 | 2024-04-24 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
85 | 2024-04-25 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
86 | 2024-04-26 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
87 | 2024-04-27 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
88 | 2024-04-28 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
89 | 2024-04-29 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
90 | 2024-04-30 | 2025 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [48 empty] | 0
91 | 2024-05-01 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
92 | 2024-05-02 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
93 | 2024-05-03 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
94 | 2024-05-04 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
95 | 2024-05-05 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
96 | 2024-05-06 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
97 | 2024-05-07 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
98 | 2024-05-08 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
99 | 2024-05-09 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
100 | 2024-05-10 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
101 | 2024-05-11 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
102 | 2024-05-12 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
103 | 2024-05-13 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
104 | 2024-05-14 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | 1 | Rin fall | [46 empty] | 0
105 | 2024-05-15 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
106 | 2024-05-16 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
107 | 2024-05-17 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
108 | 2024-05-18 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
109 | 2024-05-19 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
110 | 2024-05-20 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
111 | 2024-05-21 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
112 | 2024-05-22 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
113 | 2024-05-23 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
114 | 2024-05-24 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
115 | 2024-05-25 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
116 | 2024-05-26 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
117 | 2024-05-27 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
118 | 2024-05-28 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
119 | 2024-05-29 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
120 | 2024-05-30 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
120 | 2024-05-31 | 2025 | 2024 | Year_2 | Year_2 | May-24 | 31 | [48 empty] | 0
122 | 2024-06-01 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0
123 | 2024-06-02 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0
124 | 2024-06-03 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0
125 | 2024-06-04 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0
126 | 2024-06-05 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0
127 | 2024-06-06 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0
127 | 2024-06-07 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-08 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-09 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-10 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-11 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-12 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-13 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 |  |  | 0.16667 | 0.375 | MOP |  | Cleaning Stop due to Fanbalt Broken
127 | 2024-06-14 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-15 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-06-16 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 | [6 empty] | Cleaning not done due to marriage in vendor's family
127 | 2024-06-17 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 | [6 empty] | Cleaning not done due to marriage in vendor's family
139 | 2024-06-18 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 |  |  | 0.16667 | 0.375 | MOP |  | Cleaning stop due to Tractor pulli Broken
140 | 2024-06-19 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 | [6 empty] | Cleaning Stop due to Tractor under breakdown
141 | 2024-06-20 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 | [6 empty] | Cleaning Stop due to Tractor under breakdown
142 | 2024-06-21 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 |  |  | 0.16667 | 0.375 | MOP
143 | 2024-06-22 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 |  |  | 0.20833 | 0.45833 | MOP
144 | 2024-06-23 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 |  |  | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
145 | 2024-06-24 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 |  |  | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
146 | 2024-06-25 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0 |  |  | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
147 | 2024-06-26 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0
148 | 2024-06-27 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0
149 | 2024-06-28 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0
150 | 2024-06-29 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0
151 | 2024-06-30 | 2025 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [48 empty] | 0
152 | 2024-07-01 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
153 | 2024-07-02 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
154 | 2024-07-03 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
155 | 2024-07-04 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
156 | 2024-07-05 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
157 | 2024-07-06 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
158 | 2024-07-07 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
159 | 2024-07-08 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
160 | 2024-07-09 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
161 | 2024-07-10 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
162 | 2024-07-11 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
163 | 2024-07-12 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
164 | 2024-07-13 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
165 | 2024-07-14 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
166 | 2024-07-15 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
167 | 2024-07-16 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
168 | 2024-07-17 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
169 | 2024-07-18 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
170 | 2024-07-19 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
171 | 2024-07-20 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
172 | 2024-07-21 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
173 | 2024-07-22 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
174 | 2024-07-23 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
175 | 2024-07-24 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
176 | 2024-07-25 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
177 | 2024-07-26 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
177 | 2024-07-27 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
179 | 2024-07-28 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
180 | 2024-07-29 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
181 | 2024-07-30 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
182 | 2024-07-31 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [48 empty] | 0
183 | 2024-08-01 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
184 | 2024-08-02 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
185 | 2024-08-03 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
186 | 2024-08-04 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
187 | 2024-08-05 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
188 | 2024-08-06 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
189 | 2024-08-07 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
190 | 2024-08-08 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
191 | 2024-08-09 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
192 | 2024-08-10 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
193 | 2024-08-11 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
194 | 2024-08-12 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
195 | 2024-08-13 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
196 | 2024-08-14 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
197 | 2024-08-15 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
198 | 2024-08-16 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
199 | 2024-08-17 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
200 | 2024-08-18 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
201 | 2024-08-19 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
202 | 2024-08-20 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
203 | 2024-08-21 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
204 | 2024-08-22 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
205 | 2024-08-23 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
206 | 2024-08-24 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
207 | 2024-08-25 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
208 | 2024-08-26 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
209 | 2024-08-27 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
210 | 2024-08-28 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
211 | 2024-08-29 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
212 | 2024-08-30 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
213 | 2024-08-31 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [48 empty] | 0
214 | 2024-09-01 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
215 | 2024-09-02 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
216 | 2024-09-03 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
217 | 2024-09-04 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
218 | 2024-09-05 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
219 | 2024-09-06 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
220 | 2024-09-07 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
221 | 2024-09-08 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
222 | 2024-09-09 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
223 | 2024-09-10 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
224 | 2024-09-11 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
225 | 2024-09-12 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
226 | 2024-09-13 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
227 | 2024-09-14 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
228 | 2024-09-15 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
229 | 2024-09-16 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
230 | 2024-09-17 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
231 | 2024-09-18 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
232 | 2024-09-19 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
233 | 2024-09-20 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
234 | 2024-09-21 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
235 | 2024-09-22 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
236 | 2024-09-23 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
237 | 2024-09-24 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
238 | 2024-09-25 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
239 | 2024-09-26 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
240 | 2024-09-27 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
241 | 2024-09-28 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
242 | 2024-09-29 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
243 | 2024-09-30 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [48 empty] | 0
244 | 2024-10-01 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
245 | 2024-10-02 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
246 | 2024-10-03 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
247 | 2024-10-04 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
248 | 2024-10-05 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
249 | 2024-10-06 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
250 | 2024-10-07 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
251 | 2024-10-08 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
252 | 2024-10-09 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
253 | 2024-10-10 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
254 | 2024-10-11 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
255 | 2024-10-12 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
256 | 2024-10-13 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
257 | 2024-10-14 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
258 | 2024-10-15 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
259 | 2024-10-16 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
260 | 2024-10-17 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
261 | 2024-10-18 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
262 | 2024-10-19 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
263 | 2024-10-20 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
264 | 2024-10-21 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
265 | 2024-10-22 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
266 | 2024-10-23 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
267 | 2024-10-24 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
268 | 2024-10-25 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
269 | 2024-10-26 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
270 | 2024-10-27 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
271 | 2024-10-28 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
272 | 2024-10-29 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
273 | 2024-10-30 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
274 | 2024-10-31 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [48 empty] | 0
275 | 2024-11-01 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
276 | 2024-11-02 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
277 | 2024-11-03 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
278 | 2024-11-04 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
279 | 2024-11-05 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
280 | 2024-11-06 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
281 | 2024-11-07 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
282 | 2024-11-08 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
283 | 2024-11-09 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
284 | 2024-11-10 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
285 | 2024-11-11 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
286 | 2024-11-12 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
287 | 2024-11-13 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
288 | 2024-11-14 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
289 | 2024-11-15 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
290 | 2024-11-16 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
291 | 2024-11-17 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
292 | 2024-11-18 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
293 | 2024-11-19 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
294 | 2024-11-20 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
295 | 2024-11-21 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
296 | 2024-11-22 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
297 | 2024-11-23 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
298 | 2024-11-24 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
299 | 2024-11-25 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
300 | 2024-11-26 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
301 | 2024-11-27 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
302 | 2024-11-28 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
303 | 2024-11-29 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
304 | 2024-11-30 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [48 empty] | 0
305 | 2024-12-01 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
306 | 2024-12-02 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
307 | 2024-12-03 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
308 | 2024-12-04 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
309 | 2024-12-05 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
310 | 2024-12-06 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
311 | 2024-12-07 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
312 | 2024-12-08 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
313 | 2024-12-09 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
314 | 2024-12-10 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
315 | 2024-12-11 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
316 | 2024-12-12 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
317 | 2024-12-13 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
318 | 2024-12-14 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
319 | 2024-12-15 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
320 | 2024-12-16 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
321 | 2024-12-17 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
322 | 2024-12-18 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
323 | 2024-12-19 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
324 | 2024-12-20 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
325 | 2024-12-21 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
326 | 2024-12-22 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
327 | 2024-12-23 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
328 | 2024-12-24 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
329 | 2024-12-25 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
330 | 2024-12-26 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
331 | 2024-12-27 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
332 | 2024-12-28 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
333 | 2024-12-29 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
334 | 2024-12-30 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
335 | 2024-12-31 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [48 empty] | 0
336 | 2025-01-01 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [48 empty] | 0
337 | 2025-01-02 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [48 empty] | 0
338 | 2025-01-03 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [48 empty] | 0
339 | 2025-01-04 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [6 empty] | 9 | 9 | [40 empty] | 18
340 | 2025-01-05 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [7 empty] | 12 | [40 empty] | 12
341 | 2025-01-06 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [7 empty] | 19 | [40 empty] | 19
342 | 2025-01-07 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [8 empty] | 20 | [39 empty] | 20
343 | 2025-01-08 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | 8 | [6 empty] | 10 | [38 empty] | 18
344 | 2025-01-09 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [7 empty] | 9 |  | 33 | [38 empty] | 42
345 | 2025-01-10 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | 42 | 8 | [44 empty] | 50
346 | 2025-01-11 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  |  | 50 | 2 | [43 empty] | 52
347 | 2025-01-12 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  |  |  | 24.5 |  | 20 | 7 | [40 empty] | 51.5
348 | 2025-01-13 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [5 empty] | 28 | 20 | [41 empty] | 48
349 | 2025-01-14 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [5 empty] | 20 | 4 |  | 24 | 5 | [38 empty] | 53
350 | 2025-01-15 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [48 empty] | 0
351 | 2025-01-16 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  |  |  | 17 | [7 empty] | 8 | 20 | [34 empty] | 45
352 | 2025-01-17 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [12 empty] | 32 |  |  | 16 | [32 empty] | 48
353 | 2025-01-18 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [11 empty] | 11 | 14 |  |  | 4 | 2 | [31 empty] | 31
354 | 2025-01-19 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 47 | 28 |  | 8 | [20 empty] | 22 | 18 | [12 empty] | 123
355 | 2025-01-20 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [13 empty] | 9 |  |  |  | 41 | [17 empty] | 5 | 33 | [11 empty] | 88
356 | 2025-01-21 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [13 empty] | 19 | 13 |  |  | 17 | 21 |  | 3 | [9 empty] | 59 | 31.5 |  |  | 28 | [13 empty] | 191.5
357 | 2025-01-22 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [14 empty] | 32 | 19 |  |  | 12 | 5 | 10 | [10 empty] | 29 | 23.5 | 31 | [14 empty] | 161.5
358 | 2025-01-23 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [20 empty] | 29 | [11 empty] | 34 |  | 8.5 |  |  | 16 |  |  | 8 |  |  | 11.5 |  |  |  |  | 107
359 | 2025-01-24 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [14 empty] | 8 | 8 |  |  | 17.5 | 20 | [17 empty] | 22 |  |  | 9.5 |  | 20 | 20.5 |  |  |  |  | 125.5
360 | 2025-01-25 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [18 empty] | 14.5 | 42 | [18 empty] | 6 | 8 | 21 | 3 | 17 | 15.5 |  |  |  |  | 127
361 | 2025-01-26 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [32 empty] | 4 | [5 empty] | 41 | 35 | 6 | 1 | [6 empty] | 87
362 | 2025-01-27 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [20 empty] | 31 | 30 | [22 empty] | 6 | 51 |  |  | 118
363 | 2025-01-28 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [35 empty] | 25 | [8 empty] | 52 |  | 22.5 |  | 99.5
364 | 2025-01-29 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [21 empty] | 39 | [5 empty] | 45 | [7 empty] | 14 | 16.5 | 28 |  |  | 15 |  | 11.5 | [5 empty] | 169
365 | 2025-01-30 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [26 empty] | 16 | 23 | [20 empty] | 39
366 | 2025-01-31 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [22 empty] | 15 |  |  |  | 29 | [5 empty] | 3.5 | 6.5 | [6 empty] | 2 | 28 | 11 | [5 empty] | 95
367 | 2025-02-01 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [21 empty] | 35.5 | 8 | 7 |  |  | 21 | [6 empty] | 23.5 | 2 | 7.5 | 3 | 6 | [10 empty] | 113.5
368 | 2025-02-02 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [46 empty] | 14.5 | 67 | 81.5
369 | 2025-02-03 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [30 empty] | 21 | 8 |  |  | 7 |  |  | 1 | [10 empty] | 37
370 | 2025-02-04 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [24 empty] | 65 | [5 empty] | 22 | 23 |  |  | 4.5 |  | 9 | [11 empty] | 123.5
371 | 2025-02-05 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [24 empty] | 24 | 29 |  |  |  | 32 |  |  |  |  | 23.5 | 34 | 4 | [11 empty] | 146.5
372 | 2025-02-06 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [31 empty] | 12 |  |  |  |  | 23 | 21 | [6 empty] | 4 |  |  |  | 60
373 | 2025-02-07 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [23 empty] | 28 |  | 21 |  |  |  | 29 |  | 17.5 | 11 | 31.5 | [14 empty] | 138
374 | 2025-02-08 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [25 empty] | 45 | [6 empty] | 16 | 33 | [14 empty] | 94
375 | 2025-02-09 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [7 empty] | 43 | 18 | 15 | [22 empty] | 17.5 | [8 empty] | 23.5 | [6 empty] | 117
376 | 2025-02-10 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | 9 | 50 | 11 | [30 empty] | 15 |  |  |  |  | 5 |  |  | 20 |  |  |  |  | 110
377 | 2025-02-11 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  |  | 49 | 27.5 | [29 empty] | 9.5 | [5 empty] | 19 |  | 29 | 3 |  |  |  |  | 137
378 | 2025-02-12 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [5 empty] | 17 |  |  | 21.5 | 26 | [30 empty] | 23.5 | 10.5 | 17 | [5 empty] | 115.5
379 | 2025-02-13 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [5 empty] | 27 | 36.5 | 1.5 | [29 empty] | 22 | 7 | 5 |  |  |  | 22 |  |  |  |  | 121
380 | 2025-02-14 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  |  |  | 21 |  | 10.5 | 8 | 8 |  |  |  | 6 | 16 | [24 empty] | 35 | 30.5 |  |  |  | 7.5 |  |  |  |  | 142.5
381 | 2025-02-15 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [11 empty] | 22.5 | 36 |  |  | 17.5 | [16 empty] | 19.5 | [5 empty] | 17 |  |  |  |  | 24 | 15 |  |  |  | 151.5
382 | 2025-02-16 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [11 empty] | 10 |  |  |  | 6 | 48 | 7 | [26 empty] | 51 | 30 |  |  | 152
383 | 2025-02-17 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 36 | 14 | [33 empty] | 39 | 40 |  | 129
384 | 2025-02-18 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [48 empty] | 0
385 | 2025-02-19 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [13 empty] | 16.5 | 29 |  |  | 12 | [18 empty] | 20.5 | [10 empty] | 41 | 119
386 | 2025-02-20 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [30 empty] | 17 |  |  |  | 21 | 8 | 12.5 | 15 | [10 empty] | 73.5
387 | 2025-02-21 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [14 empty] | 16 | 19 |  |  | 32 |  | 6 | [9 empty] | 35 | 25 | [16 empty] | 133
388 | 2025-02-22 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [18 empty] | 28 | 50 |  | 2 | [8 empty] | 3 | 6 |  |  | 28 | 23.5 | [12 empty] | 140.5
389 | 2025-02-23 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [18 empty] | 8 | 19 | 53 | [27 empty] | 80
390 | 2025-02-24 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [20 empty] | 9 | 68 | [9 empty] | 29 | 5.5 | 3 | [14 empty] | 114.5
391 | 2025-02-25 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [22 empty] | 11 |  |  |  |  | 69 |  |  |  |  | 5 | 17 | [14 empty] | 102
392 | 2025-02-26 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [22 empty] | 46 |  |  |  | 33 | [5 empty] | 3.5 | [8 empty] | 10.5 | [6 empty] | 93
393 | 2025-02-27 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [22 empty] | 10 | 15 |  |  | 35 |  | 4 | [5 empty] | 5.5 |  |  | 5 |  |  |  | 32.5 | [6 empty] | 107
394 | 2025-02-28 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [24 empty] | 38 |  |  |  | 41 | [19 empty] | 79
395 | 2025-03-01 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [40 empty] | 12 |  | 15 | [5 empty] | 27
396 | 2025-03-02 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [24 empty] | 21 |  |  |  | 13 | 6 |  |  |  | 7 |  |  |  | 10 |  |  | 23 |  | 20 | [5 empty] | 100
397 | 2025-03-03 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [24 empty] | 13 |  |  |  | 8 | 33 | [17 empty] | 32 | 86
398 | 2025-03-04 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [25 empty] | 27.5 |  |  |  | 38 | [8 empty] | 31 | [9 empty] | 96.5
399 | 2025-03-05 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [39 empty] | 13.5 | [8 empty] | 13.5
400 | 2025-03-06 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31
401 | 2025-03-07 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [25 empty] | 33 | [22 empty] | 33
402 | 2025-03-08 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [23 empty] | 29 | [24 empty] | 29
403 | 2025-03-09 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
404 | 2025-03-10 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
405 | 2025-03-11 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
406 | 2025-03-12 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [6 empty] | 9 | 31 | [40 empty] | 40
407 | 2025-03-13 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
408 | 2025-03-14 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | 28 |  |  |  |  | 11 | 18 | 23 | [38 empty] | 80
409 | 2025-03-15 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
410 | 2025-03-16 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 |  |  | 19.5 | 35 | 44.5 | [43 empty] | 99
411 | 2025-03-17 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
412 | 2025-03-18 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
413 | 2025-03-19 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
414 | 2025-03-20 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
415 | 2025-03-21 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
416 | 2025-03-22 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
417 | 2025-03-23 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
418 | 2025-03-24 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
419 | 2025-03-25 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
420 | 2025-03-26 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
421 | 2025-03-27 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
422 | 2025-03-28 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
423 | 2025-03-29 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
424 | 2025-03-30 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
425 | 2025-03-31 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [48 empty] | 0
426 | 2025-04-01 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | [48 empty] | 0
427 | 2025-04-02 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | [22 empty] | 21 |  |  |  |  | 55 |  |  |  |  | 12 |  | 5.5 | [6 empty] | 16 | [6 empty] | 109.5
428 | 2025-04-03 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | [48 empty] | 0
429 | 2025-04-04 | 2026 | 2025 |  |  | Apr-25 | 30 | [22 empty] | 48 |  |  |  | 35 | [21 empty] | 83
430 | 2025-04-05 | 2026 | 2025 |  |  | Apr-25 | 30 | [22 empty] | 9 |  | 19 |  | 37 | 21 | [20 empty] | 86
431 | 2025-04-06 | 2026 | 2025 |  |  | Apr-25 | 30 | [24 empty] | 39 |  |  |  | 35 | [19 empty] | 74
432 | 2025-04-07 | 2026 | 2025 |  |  | Apr-25 | 30 | [24 empty] | 29 |  |  |  | 21 | 27 | [18 empty] | 77
433 | 2025-04-08 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
434 | 2025-04-09 | 2026 | 2025 |  |  | Apr-25 | 30 | [25 empty] | 36 |  |  |  | 44 | [18 empty] | 80
435 | 2025-04-10 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
436 | 2025-04-11 | 2026 | 2025 |  |  | Apr-25 | 30 | [25 empty] | 34 |  |  |  | 9 | [18 empty] | 43
437 | 2025-04-12 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
438 | 2025-04-13 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
439 | 2025-04-14 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
440 | 2025-04-15 | 2026 | 2025 |  |  | Apr-25 | 30 | [23 empty] | 79 |  | 9 |  | 3 | [20 empty] | 91
441 | 2025-04-16 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
442 | 2025-04-17 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
443 | 2025-04-18 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
444 | 2025-04-19 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
445 | 2025-04-20 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
446 | 2025-04-21 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
447 | 2025-04-22 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
448 | 2025-04-23 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
449 | 2025-04-24 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
450 | 2025-04-25 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
451 | 2025-04-26 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
452 | 2025-04-27 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
453 | 2025-04-28 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
454 | 2025-04-29 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
455 | 2025-04-30 | 2026 | 2025 |  |  | Apr-25 | 30 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
|  | 1900 | 1900 |  |  | Jan-00 | 31 | [48 empty] | 0
Formulas:
Days = DAY(EOMONTH(MC_2[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## GC
Sr. No. | Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Cycle Number | Resources | IS1Inv1M1 | IS1Inv1M2 | IS1Inv1M3 | IS1Inv1M4 | IS1Inv2M1 | IS1Inv2M2 | IS1Inv2M3 | IS1Inv2M4 | IS2Inv3M1 | IS2Inv3M2 | IS2Inv3M3 | IS2Inv3M4 | IS2Inv4M1 | IS2Inv4M2 | IS2Inv4M3 | IS2Inv4M4 | IS3Inv5M1 | IS3Inv5M2 | IS3Inv6M1 | IS3Inv6M2 | IS4Inv7M1 | IS4Inv7M2 | IS4Inv8M1 | IS4Inv8M2 | IS4Inv9M1 | IS4Inv9M2 | IS4Inv10M1 | IS4Inv10M2 | Total No.Table GC done | Mrthod of Cutting | Remarks for the day
1 | 2024-07-01 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
2 | 2024-07-02 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
3 | 2024-07-03 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
4 | 2024-07-04 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
5 | 2024-07-05 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
6 | 2024-07-06 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
7 | 2024-07-07 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
8 | 2024-07-08 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
9 | 2024-07-09 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
10 | 2024-07-10 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
11 | 2024-07-11 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
12 | 2024-07-12 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
13 | 2024-07-13 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
14 | 2024-07-14 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
15 | 2024-07-15 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
16 | 2024-07-16 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
17 | 2024-07-17 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
18 | 2024-07-18 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
19 | 2024-07-19 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
20 | 2024-07-20 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
21 | 2024-07-21 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
22 | 2024-07-22 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
23 | 2024-07-23 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
24 | 2024-07-24 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
25 | 2024-07-25 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
26 | 2024-07-26 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
27 | 2024-07-27 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
28 | 2024-07-28 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
29 | 2024-07-29 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
30 | 2024-07-30 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
31 | 2024-07-31 | 2025 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [30 empty] | 0
32 | 2024-08-01 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
33 | 2024-08-02 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
34 | 2024-08-03 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
35 | 2024-08-04 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
36 | 2024-08-05 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
37 | 2024-08-06 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
38 | 2024-08-07 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
39 | 2024-08-08 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
40 | 2024-08-09 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
41 | 2024-08-10 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
42 | 2024-08-11 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
43 | 2024-08-12 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
44 | 2024-08-13 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
45 | 2024-08-14 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
46 | 2024-08-15 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
47 | 2024-08-16 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
48 | 2024-08-17 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
49 | 2024-08-18 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
50 | 2024-08-19 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
51 | 2024-08-20 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
52 | 2024-08-21 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
53 | 2024-08-22 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
54 | 2024-08-23 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
55 | 2024-08-24 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
56 | 2024-08-25 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
57 | 2024-08-26 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
58 | 2024-08-27 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
59 | 2024-08-28 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
60 | 2024-08-29 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
61 | 2024-08-30 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
62 | 2024-08-31 | 2025 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [30 empty] | 0
63 | 2024-09-01 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
64 | 2024-09-02 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
65 | 2024-09-03 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
66 | 2024-09-04 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
67 | 2024-09-05 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
68 | 2024-09-06 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
69 | 2024-09-07 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
70 | 2024-09-08 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
71 | 2024-09-09 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
72 | 2024-09-10 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
73 | 2024-09-11 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
74 | 2024-09-12 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
75 | 2024-09-13 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
76 | 2024-09-14 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
77 | 2024-09-15 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
78 | 2024-09-16 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
79 | 2024-09-17 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
80 | 2024-09-18 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
81 | 2024-09-19 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
82 | 2024-09-20 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
83 | 2024-09-21 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
84 | 2024-09-22 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
85 | 2024-09-23 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
86 | 2024-09-24 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
87 | 2024-09-25 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
88 | 2024-09-26 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
89 | 2024-09-27 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
90 | 2024-09-28 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
91 | 2024-09-29 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
92 | 2024-09-30 | 2025 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [30 empty] | 0
93 | 2024-10-01 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
94 | 2024-10-02 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
95 | 2024-10-03 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
96 | 2024-10-04 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
97 | 2024-10-05 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
98 | 2024-10-06 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
99 | 2024-10-07 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
100 | 2024-10-08 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
101 | 2024-10-09 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
102 | 2024-10-10 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
103 | 2024-10-11 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
104 | 2024-10-12 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
105 | 2024-10-13 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
106 | 2024-10-14 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
107 | 2024-10-15 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
108 | 2024-10-16 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
109 | 2024-10-17 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
110 | 2024-10-18 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
111 | 2024-10-19 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
112 | 2024-10-20 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
113 | 2024-10-21 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
114 | 2024-10-22 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
115 | 2024-10-23 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
116 | 2024-10-24 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
117 | 2024-10-25 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
118 | 2024-10-26 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
119 | 2024-10-27 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
120 | 2024-10-28 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
120 | 2024-10-29 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
122 | 2024-10-30 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
123 | 2024-10-31 | 2025 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [30 empty] | 0
124 | 2024-11-01 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0
125 | 2024-11-02 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0
126 | 2024-11-03 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0
127 | 2024-11-04 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0
127 | 2024-11-05 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Rotavator
127 | 2024-11-06 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Rotavator
127 | 2024-11-07 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Rotavator
127 | 2024-11-08 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Rotavator
127 | 2024-11-09 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Rotavator
127 | 2024-11-10 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Rotavator
127 | 2024-11-11 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Rotavator
127 | 2024-11-12 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Rotavator
127 | 2024-11-13 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Rotavator
127 | 2024-11-14 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Rotavator
127 | 2024-11-15 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Rotavator
139 | 2024-11-16 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Rotavator
140 | 2024-11-17 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Rotavator
141 | 2024-11-18 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Rotavator
142 | 2024-11-19 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Rotavator
143 | 2024-11-20 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Manually Grass Cutting
144 | 2024-11-21 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Manually Grass Cutting
145 | 2024-11-22 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Manually Grass Cutting
146 | 2024-11-23 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0 | Manually Grass Cutting
147 | 2024-11-24 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0
148 | 2024-11-25 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0
149 | 2024-11-26 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0
150 | 2024-11-27 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0
151 | 2024-11-28 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0
152 | 2024-11-29 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0
153 | 2024-11-30 | 2025 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [30 empty] | 0
154 | 2024-12-01 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
155 | 2024-12-02 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
156 | 2024-12-03 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
157 | 2024-12-04 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
158 | 2024-12-05 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
159 | 2024-12-06 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
160 | 2024-12-07 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
161 | 2024-12-08 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
162 | 2024-12-09 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
163 | 2024-12-10 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
164 | 2024-12-11 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
165 | 2024-12-12 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
166 | 2024-12-13 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
167 | 2024-12-14 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
168 | 2024-12-15 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
169 | 2024-12-16 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
170 | 2024-12-17 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
171 | 2024-12-18 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
172 | 2024-12-19 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
173 | 2024-12-20 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [6 empty] | 10 | 10 | [22 empty] | 20
174 | 2024-12-21 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [7 empty] | 31 | 10 | [21 empty] | 41
175 | 2024-12-22 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [9 empty] | 26 | [20 empty] | 26
176 | 2024-12-23 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [7 empty] | 9 | 12 | 10 | [20 empty] | 31
177 | 2024-12-24 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | 15.5 | [6 empty] | 18 | [20 empty] | 33.5
178 | 2024-12-25 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | 24 | [27 empty] | 24
179 | 2024-12-26 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | 9 | 22 | [26 empty] | 31
180 | 2024-12-27 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  |  | 22 | [26 empty] | 22
181 | 2024-12-28 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  |  | 9 | 26.5 | [25 empty] | 35.5
182 | 2024-12-29 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [30 empty] | 0
183 | 2024-12-30 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [5 empty] | 10 |  |  | 21.5 | [21 empty] | 31.5
184 | 2024-12-31 | 2025 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [5 empty] | 26 | [24 empty] | 26
185 | 2025-01-01 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | 11 |  |  | 8.5 | 18.5 | [23 empty] | 38
186 | 2025-01-02 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [6 empty] | 21 | 6 | [22 empty] | 27
187 | 2025-01-03 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  |  |  | 12.5 |  |  |  | 16 | [21 empty] | 28.5
188 | 2025-01-04 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  |  |  | 6 | [7 empty] | 8 | 7 | [16 empty] | 21
189 | 2025-01-05 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [12 empty] | 22 | 13 |  | 11 | [14 empty] | 46
190 | 2025-01-06 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [11 empty] | 32.5 | 18 |  |  | 8 | 8 | [13 empty] | 66.5
191 | 2025-01-07 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 37 | 24 | [18 empty] | 61
192 | 2025-01-08 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 15 | [6 empty] | 33 | [12 empty] | 48
193 | 2025-01-09 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [13 empty] | 16 | 31 |  |  | 21 | [12 empty] | 68
194 | 2025-01-10 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [14 empty] | 8 | 25 | [14 empty] | 33
195 | 2025-01-11 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [16 empty] | 43.5 | 7 | [12 empty] | 50.5
196 | 2025-01-12 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [18 empty] | 9 | 40 | [10 empty] | 49
197 | 2025-01-13 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [18 empty] | 21 |  | 33 | [9 empty] | 54
198 | 2025-01-14 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [20 empty] | 38 | 16 | [8 empty] | 54
199 | 2025-01-15 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [30 empty] | 0
200 | 2025-01-16 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [20 empty] | 7 | 11 | [8 empty] | 18
201 | 2025-01-17 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [30 empty] | 0
202 | 2025-01-18 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [20 empty] | 2 | 20 | [8 empty] | 22
203 | 2025-01-19 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [27 empty] | 21 |  |  | 21
204 | 2025-01-20 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [30 empty] | 0
205 | 2025-01-21 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [27 empty] | 36 |  |  | 36
206 | 2025-01-22 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [22 empty] | 37 |  |  |  | 11 | 12 |  |  | 60
207 | 2025-01-23 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [22 empty] | 12 |  |  |  | 12 |  |  |  | 24
208 | 2025-01-24 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [22 empty] | 12 |  |  |  | 13 |  |  |  | 25
209 | 2025-01-25 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [22 empty] | 8 | 4 |  |  | 9 |  |  |  | 21
210 | 2025-01-26 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [30 empty] | 0
211 | 2025-01-27 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [18 empty] | 10 | 26 | [10 empty] | 36
212 | 2025-01-28 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [18 empty] | 22 | 14 | [10 empty] | 36
213 | 2025-01-29 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [26 empty] | 19 |  |  |  | 19
214 | 2025-01-30 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [28 empty] | 18 |  | 18
215 | 2025-01-31 | 2025 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [24 empty] | 21 | [5 empty] | 21
216 | 2025-02-01 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [24 empty] | 16 |  |  |  |  | 20 | 36
217 | 2025-02-02 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [24 empty] | 16 |  |  |  | 14 | 4 | 34
218 | 2025-02-03 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [24 empty] | 11 |  |  |  | 6 | 17 | 34
219 | 2025-02-04 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [30 empty] | 0
220 | 2025-02-05 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [25 empty] | 11 |  |  |  | 24 | 35
221 | 2025-02-06 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [29 empty] | 22 | 22
222 | 2025-02-07 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [23 empty] | 27 |  | 9 |  |  |  |  | 36
223 | 2025-02-08 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [25 empty] | 40 |  |  |  |  | 40
224 | 2025-02-09 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28
225 | 2025-02-10 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28
Formulas:
Days = DAY(EOMONTH(GC[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## Modelling New
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | CC*Bugt (MTD) | CC*Bugt (YTD) | Capacity | 136.82
1 | April | 5 | 2024-04-01 | 2024 | FY25 | 30 | 211.4 | 214.2 |  |  |  | 0 |  |  | 7.14 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 0
2 | May | 6 | 2024-05-01 | 2024 | FY25 | 31 | 219.5 | 213.6 |  |  |  | 8914.1691 | 50.96 | 81.89% | 6.8903 | 0 | 0 | 0 | 287.5538 | 0 | 0 | 23.51% |  |  | 0 | 0 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 0
3 | June | 7 | 2024-06-01 | 2024 | FY25 | 30 | 155.2 | 149.1 |  |  |  | 6430.6478 | 50.96 | 84.63% | 4.97 | 0 | 0 | 0 | 214.3549 | 0 | 0 | 17.53% |  |  | 0 | 0 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 0
4 | July | 8 | 2024-07-01 | 2024 | FY25 | 31 | 121.5 | 117.7 |  |  |  | 7423.9879 | 83.1575 | 75.85% | 3.7968 | 0 | 0 | 0 | 239.4835 | 0 | 0 | 12% |  |  | 0 | 0 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 0
5 | August | 9 | 2024-08-01 | 2024 | FY25 | 31 | 124.7 | 123.5 |  |  |  | 8136.5383 | 83.1575 | 79.23% | 3.9839 | 0 | 0 | 0 | 262.469 | 0 | 0 | 13.15% |  |  | 0 | 0 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 0
6 | September | 10 | 2024-09-01 | 2024 | FY25 | 30 | 146.3 | 150.5 |  |  |  | 10149.1588 | 83.1575 | 81.09% | 5.0167 | 0 | 0 | 0 | 338.3053 | 0 | 0 | 16.95% |  |  | 0 | 0 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 0
7 | October | 11 | 2024-10-01 | 2024 | FY25 | 31 | 165.6 | 180.6 |  |  |  | 17354.2081 | 136.82 | 70.23% | 5.8258 | 0 | 0 | 0 | 559.8132 | 0 | 0 | 17.05% |  |  | 0 | 0 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 0
8 | November | 12 | 2024-11-01 | 2024 | FY25 | 30 | 146.1 | 167.5 |  |  |  | 17240.8237 | 136.82 | 75.23% | 5.5833 | 0 | 0 | 0 | 574.6941 | 0 | 0 | 17.5% |  |  | 0 | 0 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 0
9 | December | 2 | 2024-12-01 | 2024 | FY25 | 31 | 140.3 | 165.2 |  |  |  | 18551.2913 | 136.82 | 82.08% | 5.329 | 0 | 0 | 0 | 598.4288 | 0 | 0 | 18.22% |  |  | 0 | 0 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 0
10 | January | 3 | 2025-01-01 | 2025 | FY25 | 31 | 147.3 | 171 |  |  |  | 20347.6286 | 136.82 | 86.97% | 5.5161 | 0 | 0 | 0 | 656.3751 | 0 | 0 | 19.99% |  |  | 0 | 0 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 0
11 | February | 4 | 2025-02-01 | 2025 | FY25 | 28 | 157.7 | 176.7 |  |  |  | 19824.2255 | 136.82 | 82% | 6.3107 | 0 | 0 | 0 | 708.0081 | 0 | 2303.1034 | 21.56% |  |  | 0 | 0 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 0
12 | March | 5 | 2025-03-01 | 2025 | FY25 | 31 | 201.5 | 214.6 |  |  |  | 23798.7351 | 136.82 | 81.05% | 6.9226 | 3 | 20.7677 | 20.7677 | 767.7011 | 2303.1034 | 2303.1034 | 23.38% | 23.38% | 23.38% | 97 | 8.0833 |  |  |  | 99.5% | 99.5% | [6 empty] | 1632809.7434 | 1632809.7434
13 | April | 5 | 2025-04-01 | 2025 | FY26 | 30 | 211.4 | 214.2 |  |  |  | 21288.8306 | 130 | 76.45% | 7.14 | 30 | 214.2 | 214.2 | 709.6277 | 21288.8306 | 21288.8306 | 22.74% | 22.74% | 22.74% | 103.2667 | 103.2667 |  |  |  | 99.5% | 99.5% | [6 empty] | 16910973.6494 | 16910973.6494
14 | May | 6 | 2025-05-01 | 2025 | FY26 | 31 | 219.5 | 213.6 |  |  |  | 22397.6131 | 130 | 80.66% | 6.8903 | 31 | 213.6 | 427.8 | 722.5036 | 22397.6131 | 43686.4438 | 23.16% | 23.16% | 22.95% | 113.9 | 108.5833 |  |  |  | 99.5% | 99.5% | [6 empty] | 19623754.9002 | 36534728.5496
15 | June | 7 | 2025-06-01 | 2025 | FY26 | 30 | 155.2 | 149.1 |  |  |  | 16321.4903 | 130 | 84.21% | 4.97 | 30 | 149.1 | 626.2581 | 544.0497 | 16321.4903 | 65481.7377 | 17.44% | 17.44% | 23.06% | 123.4293 | 113.532 |  |  |  | 99.5% | 99.5% | [6 empty] | 15496543.5663 | 52031272.1159
16 | July | 8 | 2025-07-01 | 2025 | FY26 | 31 | 121.5 | 117.7 |  |  |  | 13052.9164 | 130 | 85.31% | 3.7968 | 13 | 49.3581 | 626.2581 | 421.0618 | 5473.8036 | 65481.7377 | 13.5% | 13.5% | 20.18% | 53.711 | 98.5767 |  |  |  | 99.5% | 99.5% | [6 empty] | 5392959.7745 | 57424231.8905
17 | August | 9 | 2025-08-01 | 2025 | FY26 | 31 | 124.7 | 123.5 |  |  |  | 13717.5669 | 130 | 85.44% | 3.9839 | 0 | 0 | 626.2581 | 442.5022 | 0 | 65481.7377 | 14.18% |  | 20.18% | 0 | 78.8614 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 57424231.8905
18 | September | 10 | 2025-09-01 | 2025 | FY26 | 30 | 146.3 | 150.5 |  |  |  | 16496.0797 | 130 | 84.31% | 5.0167 | 0 | 0 | 626.2581 | 549.8693 | 0 | 65481.7377 | 17.62% |  | 20.18% | 0 | 65.7178 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 57424231.8905
19 | October | 11 | 2025-10-01 | 2025 | FY26 | 31 | 165.6 | 180.6 |  |  |  | 19695.6726 | 130 | 83.89% | 5.8258 | 0 | 0 | 626.2581 | 635.3443 | 0 | 65481.7377 | 20.36% |  | 20.18% | 0 | 56.3296 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 57424231.8905
20 | November | 12 | 2025-11-01 | 2025 | FY26 | 30 | 146.1 | 167.5 |  |  |  | 18545.3963 | 130 | 85.17% | 5.5833 | 0 | 0 | 626.2581 | 618.1799 | 0 | 65481.7377 | 19.81% |  | 20.18% | 0 | 49.2884 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 57424231.8905
21 | December | 2 | 2025-12-01 | 2025 | FY26 | 31 | 140.3 | 165.2 |  |  |  | 18457.3935 | 130 | 85.94% | 5.329 | 0 | 0 | 626.2581 | 595.3998 | 0 | 65481.7377 | 19.08% |  | 20.18% | 0 | 43.8119 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 57424231.8905
22 | January | 3 | 2026-01-01 | 2026 | FY26 | 31 | 147.3 | 171 |  |  |  | 19032.1243 | 130 | 85.61% | 5.5161 | 0 | 0 | 626.2581 | 613.9395 | 0 | 65481.7377 | 19.68% |  | 20.18% | 0 | 39.4307 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 57424231.8905
23 | February | 4 | 2026-02-01 | 2026 | FY26 | 28 | 157.7 | 176.7 |  |  |  | 19102.9345 | 130 | 83.16% | 6.3107 | 0 | 0 | 626.2581 | 682.2477 | 0 | 65481.7377 | 21.87% |  | 20.18% | 0 | 35.8461 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 57424231.8905
24 | March | 5 | 2026-03-01 | 2026 | FY26 | 31 | 201.5 | 214.6 |  |  |  | 22483.2986 | 130 | 80.59% | 6.9226 | 0 | 0 | 626.2581 | 725.2677 | 0 | 65481.7377 | 23.25% |  | 20.18% | 0 | 32.8589 |  |  |  | 99.5% | 99.5% | [6 empty] | 0 | 57424231.8905
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))