## Daily Dashboard
10 MW ES Energy Private Limited Performance Summary
Month | 2025-07-01
Date | 2025-07-15
Operation Year | FY2025-26
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 31.4251 | 27.7365 | -11.74%
| E_Grid MTD(MWh) | 471.3769 | 490.2435 | 4.002%
| E_Grid YTD (MWh) | 4752.3742 | 4431.6645 | -6.748%
2 | CUF Daily(%) | 12.46% | 11% | -11.74%
| CUF MTD(%) | 12.46% | 12.96% | 4.002%
| CUF YTD(%) | 17.78% | 16.58% | -6.748%
3 | PR_Daily (%) | 70.05% | 76.74% | 9.544%
| PR_MTD (%) | 70.05% | 73.91% | 5.504%
| PR_YTD (%) | 68.08% | 71.27% | 4.691%
4 | POA Daily (KWh/m2) | 4.2694 | 3.44 | -19.43%
| POA MTD(KWh/m2) | 64.0417 | 63.13 | -1.424%
| POA YTD(KWh/m2) | 664.3912 | 591.7915 | -10.93%
5 | PA Daily (%) | 99.5% | 100% | 0.5025%
| PA MTD(%) | 99.5% | 99.41% | -0.09078%
| PA YTD(%) | 99.5% | 99.33% | -0.1718%
6 | GA Daily (%) | 99.7% | 100% | 0.3009%
| GA MTD(%) | 99.7% | 100% | 0.3009%
| GA YTD(%) | 99.7% | 99.07% | -0.6363%
7 | TA Daily (%) | 99.9% | 100% | 0.1001%
| TA MTD(%) | 99.9% | 100% | 0.1001%
| TA YTD(%) | 99.9% | 100% | 0.1001%

## Modelling New (hidden)
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS_YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | Bugt Capacity | CC*Bugt | DC Capacity | 10.507
1 | April | 4 | 2022-04-01 | 2022 | FY23 | 30 | 192.7392 | 227.6882 |  | 27.5 |  | 1670.3636 | 10.507 | 69.82% | 7.5896 | 0 | 0 | 0 | 55.6788 | 0 | 0 | 22.08% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1670363.6167 | 1670.3636
2 | May | 5 | 2022-05-01 | 2022 | FY23 | 31 | 184.4934 | 215.5443 |  | 26.7001 |  | 1602.1141 | 10.507 | 70.74% | 6.953 | 0 | 0 | 0 | 51.6811 | 0 | 0 | 20.49% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1602114.0818 | 1602.1141
3 | June | 6 | 2022-06-01 | 2022 | FY23 | 30 | 140.1651 | 157.117 |  | 24.6999 |  | 1181.2419 | 10.507 | 71.55% | 5.2372 | 0 | 0 | 0 | 39.3747 | 0 | 0 | 15.61% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1181241.95 | 1181.2419
4 | July | 7 | 2022-07-01 | 2022 | FY23 | 31 | 122.3162 | 132.3528 |  | 23.8 |  | 991.3682 | 10.507 | 71.29% | 4.2694 | 0 | 0 | 0 | 31.9796 | 0 | 0 | 12.68% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 991368.2439 | 991.3682
5 | August | 8 | 2022-08-01 | 2022 | FY23 | 31 | 126.2928 | 137.8495 |  | 23.6001 |  | 1037.7429 | 10.507 | 71.65% | 4.4468 | 0 | 0 | 0 | 33.4756 | 0 | 0 | 13.28% | [6 empty] | 99.5% | 99.7% | 99.9% | [7 empty] | For wind EGA | 99.5% | 1037742.9279 | 1037.7429
6 | September | 9 | 2022-09-01 | 2022 | FY23 | 30 | 144.0447 | 163.0405 |  | 23.7001 |  | 1224.9917 | 10.507 | 71.51% | 5.4347 | 0 | 0 | 0 | 40.8331 | 0 | 0 | 16.19% | [6 empty] | 99.5% | 99.7% | 99.9% | [7 empty] | Wind PA equal Bugt PA for wind |  | 1224991.6518 | 1224.9917
7 | October | 10 | 2022-10-01 | 2022 | FY23 | 31 | 146.567 | 169.4187 |  | 23.3999 |  | 1279.2413 | 10.507 | 71.86% | 5.4651 | 0 | 0 | 0 | 41.2658 | 0 | 0 | 16.36% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1279241.2821 | 1279.2413
8 | November | 11 | 2022-11-01 | 2022 | FY23 | 30 | 136.383 | 157.9207 |  | 22.5 |  | 1206.6168 | 10.507 | 72.72% | 5.264 | 0 | 0 | 0 | 40.2206 | 0 | 0 | 15.95% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1206616.7771 | 1206.6168
9 | December | 12 | 2022-12-01 | 2022 | FY23 | 31 | 149.3793 | 175.8024 |  | 21.493 |  | 1343.1158 | 10.507 | 72.71% | 5.671 | 0 | 0 | 0 | 43.3263 | 0 | 0 | 17.18% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1343115.8468 | 1343.1158
10 | January | 1 | 2023-01-01 | 2023 | FY23 | 31 | 172.6591 | 210.7416 |  | 22.1 |  | 1607.364 | 10.507 | 72.59% | 6.7981 | 0 | 0 | 0 | 51.8505 | 0 | 0 | 20.56% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1607364.046 | 1607.364
11 | February | 2 | 2023-02-01 | 2023 | FY23 | 28 | 174.4061 | 212.7888 |  | 24.1999 |  | 1596.8641 | 10.507 | 71.42% | 7.5996 | 0 | 0 | 0 | 57.0309 | 0 | 0 | 22.62% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1596864.1176 | 1596.8641
12 | March | 3 | 2023-03-01 | 2023 | FY23 | 31 | 205.4467 | 247.3821 |  | 26.7003 |  | 1826.9875 | 10.507 | 70.29% | 7.9801 | 0 | 0 | 0 | 58.9351 | 0 | 0 | 23.37% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1826987.5493 | 1826.9875
13 | April | 4 | 2023-04-01 | 2023 | FY24 | 30 | 192.7392 | 227.6882 |  | 27.5 |  | 1610 | 10.507 | 67.3% | 7.5896 | 0 | 0 | 0 | 53.6667 | 0 | 0 | 21.28% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1610000 | 1610
14 | May | 5 | 2023-05-01 | 2023 | FY24 | 31 | 184.4934 | 215.5443 |  | 26.7001 |  | 1600 | 10.507 | 70.65% | 6.953 | 0 | 0 | 0 | 51.6129 | 0 | 0 | 20.47% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1600000 | 1600
15 | June | 6 | 2023-06-01 | 2023 | FY24 | 30 | 140.1651 | 157.117 |  | 24.6999 |  | 1140 | 10.507 | 69.06% | 5.2372 | 0 | 0 | 0 | 38 | 0 | 0 | 15.07% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1140000 | 1140
16 | July | 7 | 2023-07-01 | 2023 | FY24 | 31 | 122.3162 | 132.3528 |  | 23.8 |  | 990 | 10.507 | 71.19% | 4.2694 | 0 | 0 | 0 | 31.9355 | 0 | 0 | 12.66% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 990000 | 990
17 | August | 8 | 2023-08-01 | 2023 | FY24 | 31 | 126.2928 | 137.8495 |  | 23.6001 |  | 1040 | 10.507 | 71.8% | 4.4468 | 0 | 0 | 0 | 33.5484 | 0 | 0 | 13.3% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1040000 | 1040
18 | September | 9 | 2023-09-01 | 2023 | FY24 | 30 | 144.0447 | 163.0405 |  | 23.7001 |  | 1180 | 10.507 | 68.88% | 5.4347 | 0 | 0 | 0 | 39.3333 | 0 | 0 | 15.6% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1180000 | 1180
19 | October | 10 | 2023-10-01 | 2023 | FY24 | 31 | 146.567 | 169.4187 |  | 23.3999 |  | 1680 | 10.507 | 94.38% | 5.4651 | 0 | 0 | 0 | 54.1935 | 0 | 0 | 21.49% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1680000 | 1680
20 | November | 11 | 2023-11-01 | 2023 | FY24 | 30 | 136.383 | 157.9207 |  | 22.5 |  | 1530 | 10.507 | 92.21% | 5.264 | 0 | 0 | 0 | 51 | 0 | 0 | 20.22% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1530000 | 1530
21 | December | 12 | 2023-12-01 | 2023 | FY24 | 31 | 149.3793 | 175.8024 |  | 21.493 |  | 1760 | 10.507 | 95.28% | 5.671 | 0 | 0 | 0 | 56.7742 | 0 | 0 | 22.51% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1760000 | 1760
22 | January | 1 | 2024-01-01 | 2024 | FY24 | 31 | 172.6591 | 210.7416 |  | 22.1 |  | 2110 | 10.507 | 95.29% | 6.7981 | 0 | 0 | 0 | 68.0645 | 0 | 0 | 26.99% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 2110000 | 2110
23 | February | 2 | 2024-02-01 | 2024 | FY24 | 29 | 174.4061 | 212.7888 |  | 24.1999 |  | 1960 | 10.507 | 87.67% | 7.3375 | 0 | 0 | 0 | 67.5862 | 0 | 0 | 26.8% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1960000 | 1960
24 | March | 3 | 2024-03-01 | 2024 | FY24 | 31 | 205.4467 | 247.3821 |  | 26.7003 |  | 2400 | 10.507 | 92.33% | 7.9801 | 0 | 0 | 0 | 77.4194 | 0 | 0 | 30.7% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 2400000 | 2400
25 | April | 4 | 2024-04-01 | 2024 | FY25 | 30 | 192.7392 | 227.6882 |  | 27.5 |  | 1598.2 | 10.507 | 66.81% | 7.5896 | 0 | 0 | 0 | 53.2733 | 0 | 0 | 21.13% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1598200 | 1598.2
26 | May | 5 | 2024-05-01 | 2024 | FY25 | 31 | 184.4934 | 215.5443 |  | 26.7001 |  | 1587.9 | 10.507 | 70.11% | 6.953 | 0 | 0 | 0 | 51.2226 | 0 | 0 | 20.31% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1587900 | 1587.9
27 | June | 6 | 2024-06-01 | 2024 | FY25 | 30 | 140.1651 | 157.117 |  | 24.6999 |  | 1131.6 | 10.507 | 68.55% | 5.2372 | 0 | 0 | 0 | 37.72 | 0 | 0 | 14.96% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1131600 | 1131.6
28 | July | 7 | 2024-07-01 | 2024 | FY25 | 31 | 122.3162 | 132.3528 |  | 23.8 |  | 982.5 | 10.507 | 70.65% | 4.2694 | 0 | 0 | 0 | 31.6935 | 0 | 0 | 12.57% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 982500 | 982.5
29 | August | 8 | 2024-08-01 | 2024 | FY25 | 31 | 126.2928 | 137.8495 |  | 23.6001 |  | 1032.2 | 10.507 | 71.27% | 4.4468 | 0 | 0 | 0 | 33.2968 | 0 | 0 | 13.2% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1032200 | 1032.2
30 | September | 9 | 2024-09-01 | 2024 | FY25 | 30 | 144.0447 | 163.0405 |  | 23.7001 |  | 1171.3 | 10.507 | 68.37% | 5.4347 | 0 | 0 | 0 | 39.0433 | 0 | 0 | 15.48% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1171300 | 1171.3
31 | October | 10 | 2024-10-01 | 2024 | FY25 | 31 | 146.567 | 169.4187 |  | 23.3999 |  | 1280.3 | 10.507 | 71.92% | 5.4651 | 0 | 0 | 0 | 41.3 | 0 | 0 | 16.38% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1280300 | 1280.3
32 | November | 11 | 2024-11-01 | 2024 | FY25 | 30 | 136.383 | 157.9207 |  | 22.5 |  | 1171.3 | 10.507 | 70.59% | 5.264 | 0 | 0 | 0 | 39.0433 | 0 | 0 | 15.48% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1171300 | 1171.3
33 | December | 12 | 2024-12-01 | 2024 | FY25 | 31 | 149.3793 | 175.8024 |  | 21.493 |  | 1349.7 | 10.507 | 73.07% | 5.671 | 0 | 0 | 0 | 43.5387 | 0 | 0 | 17.27% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1349700 | 1349.7
34 | January | 1 | 2025-01-01 | 2025 | FY25 | 31 | 172.6591 | 210.7416 |  | 22.1 |  | 1607.8 | 10.507 | 72.61% | 6.7981 | 0 | 0 | 0 | 51.8645 | 0 | 0 | 20.57% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1607800 | 1607.8
35 | February | 2 | 2025-02-01 | 2025 | FY25 | 28 | 174.4061 | 212.7888 |  | 24.1999 |  | 1479.9 | 10.507 | 66.19% | 7.5996 | 0 | 0 | 0 | 52.8536 | 0 | 0 | 20.96% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1479900 | 1479.9
36 | March | 3 | 2025-03-01 | 2025 | FY25 | 31 | 205.4467 | 247.3821 |  | 26.7003 |  | 1826.1 | 10.507 | 70.26% | 7.9801 | 3 | 23.9402 | 23.9402 | 58.9065 | 176.7194 | 176.7194 | 23.36% | 23.36% | 23.36% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9% | [9 empty] | 1826100 | 1826.1
37 | April | 4 | 2025-04-01 | 2025 | FY26 | 30 | 192.7392 | 227.6882 |  | 27.5 |  | 1584.5717 | 10.507 | 66.24% | 7.5896 | 30 | 227.6882 | 227.6882 | 52.8191 | 1584.5717 | 1584.5717 | 20.95% | 20.95% | 20.95% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
38 | May | 5 | 2025-05-01 | 2025 | FY26 | 31 | 184.4934 | 215.5443 |  | 26.7001 |  | 1574.4307 | 10.507 | 69.52% | 6.953 | 31 | 215.5443 | 664.3912 | 50.7881 | 1574.4307 | 4752.3742 | 20.14% | 20.14% | 30.9% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
39 | June | 6 | 2025-06-01 | 2025 | FY26 | 30 | 140.1651 | 157.117 |  | 24.6999 |  | 1121.9949 | 10.507 | 67.97% | 5.2372 | 30 | 157.117 | 600.3495 | 37.3998 | 1121.9949 | 4280.9973 | 14.83% | 14.83% | 18.66% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
40 | July | 7 | 2025-07-01 | 2025 | FY26 | 31 | 122.3162 | 132.3528 |  | 23.8 |  | 974.179 | 10.507 | 70.05% | 4.2694 | 15 | 64.0417 | 664.3912 | 31.4251 | 471.3769 | 4752.3742 | 12.46% | 12.46% | 17.78% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
41 | August | 8 | 2025-08-01 | 2025 | FY26 | 31 | 126.2928 | 137.8495 |  | 23.6001 |  | 1023.38 | 10.507 | 70.66% | 4.4468 | 0 | 0 | 664.3912 | 33.0123 | 0 | 4752.3742 | 13.09% |  | 17.78% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
42 | September | 9 | 2025-09-01 | 2025 | FY26 | 30 | 144.0447 | 163.0405 |  | 23.7001 |  | 1161.3631 | 10.507 | 67.79% | 5.4347 | 0 | 0 | 664.3912 | 38.7121 | 0 | 4752.3742 | 15.35% |  | 17.78% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
43 | October | 10 | 2025-10-01 | 2025 | FY26 | 31 | 146.567 | 169.4187 |  | 23.3999 |  | 1269.3848 | 10.507 | 71.31% | 5.4651 | 0 | 0 | 664.3912 | 40.9479 | 0 | 4752.3742 | 16.24% |  | 17.78% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
44 | November | 11 | 2025-11-01 | 2025 | FY26 | 30 | 136.383 | 157.9207 |  | 22.5 |  | 1161.3631 | 10.507 | 69.99% | 5.264 | 0 | 0 | 664.3912 | 38.7121 | 0 | 4752.3742 | 15.35% |  | 17.78% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
45 | December | 12 | 2025-12-01 | 2025 | FY26 | 31 | 149.3793 | 175.8024 |  | 21.493 |  | 1338.2661 | 10.507 | 72.45% | 5.671 | 0 | 0 | 664.3912 | 43.1699 | 0 | 4752.3742 | 17.12% |  | 17.78% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
46 | January | 1 | 2026-01-01 | 2026 | FY26 | 31 | 172.6591 | 210.7416 |  | 22.1 |  | 1594.1111 | 10.507 | 71.99% | 6.7981 | 0 | 0 | 664.3912 | 51.4229 | 0 | 4752.3742 | 20.39% |  | 17.78% |  | 10.507 |  |  | 99.5% | 99.7% | 99.9%
47 | February | 2 | 2026-02-01 | 2026 | FY26 | 28 | 174.4061 | 212.7888 |  | 24.1999 |  | 1467.2907 | 10.507 | 65.63% | 7.5996 | 0 | 0 | 664.3912 | 52.4032 | 0 | 4752.3742 | 20.78% |  | 17.78% |  | 10.507 |  |  | 99.5% | 99.7% | 99.9%
48 | March | 3 | 2026-03-01 | 2026 | FY26 | 31 | 205.4467 | 247.3821 |  | 26.7003 |  | 1810.5953 | 10.507 | 69.66% | 7.9801 | 0 | 0 | 664.3912 | 58.4063 | 0 | 4752.3742 | 23.16% |  | 17.78% |  | 10.507 |  |  | 99.5% | 99.7% | 99.9%
[12 empty] | 1796043.7401 | 1796.0437
[12 empty] | 1722663.7863 | 1722.6638
[12 empty] | 1270329.9882 | 1270.33
[12 empty] | 1065924.7176 | 1065.9247
[12 empty] | 1106298.1096 | 1106.2981
[12 empty] | 1316920.9396 | 1316.9209
[12 empty] | 1364355.656 | 1364.3557
[12 empty] | 1286868.6937 | 1286.8687
[12 empty] | 1432329.582 | 1432.3296
[12 empty] | 1634508.3255 | 1634.5083
[12 empty] | 1635740.3774 | 1635.7404
[12 empty] | 1947603.0582 | 1947.6031
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## CMS_Data
Daily
Tagname | Date | Target | Actual | Difference
E Grid Target | 4585300% | 31.4251 | 27.7365 | 3.6887
Shadding | 4585300% | 0 | 0 | 0
Soiling | 4585300% | 0 | 0 | 0
IAM | 4585300% | 0 | 0 | 0
Bifacial Gain | 4585300% | 0 | 0 | 0
Temperature | 4585300% | 0 | 0 | 0
Mismatch | 4585300% | 0 | 0 | 0
DC Ohmic | 4585300% | 0 | 0 | 0
AC Ohmic | 4585300% | 0 | 0 | 0
Inverter Conversion | 4585300% | 0 | 0 | 0
MPPT Mismatch | 4585300% | 0 | 0 | 0
Clipping Loss | 4585300% | 0 | 0 | 0
Curtailment Order | 4585300% | 0 | 0 | 0
Reactive Power | 4585300% | 0 | 0 | 0
Plant Uptime | 4585300% | 99.5 | 100 | 0.5 | 0.15713
Grid Uptime | 4585300% | 99.7 | 100 | 0.3 | 0.094275
Tracker Uptime | 4585300% | 99.9 | 100 | 0.1 | 0.006285
Tracker Gain | 4585300% | 0 | 0 | 0
Dc Unbalanced Load | 4585300% | 0 | 0 | 0
Measured | 4585300% | 27.7365 | 27.7365 | 27.7365
Repowering Delay | 4585300% | 0 | 0 | 0
Capacity Shortfall | 4585300% | 0 | 0 | 0
PR | 4585300% | 0 | 2.6741 | 2.6741
POA | 4585300% | 4.2694 | 3.44 | -0.82945 | -6.1051

## Monthly KPI
Till Date | 2025-07-15
ES Energy Private Limited Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target TA (%) | Measured TA (%)
2025-07-01 | 15 | 64.0417 | 63.13 | 471.3769 | 490.2435 | 70.05% | 73.91% | 12.46% | 12.96% | 99.7% | 100% | 99.5% | 99.41% | 99.9% | 100%
Start Date | 2025-07-09
End Date | 2025-07-15
ES Energy Private Limited Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target TA (%) | Measured TA (%)
2025-07-01 | 7 | 29.8861 | 31.14 | 219.9759 | 239.3476 | 70.05% | 73.15% | 12.46% | 13.56% | 99.7% | 100% | 99.5% | 99.96% | 99.9% | 100%
Formulas:
Days = [Days, row below]-6

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 12 | 6.6 |  | 7.375 |  | 30.4938 | 46.4586 | 0.67534 | 0.69938 | [5 empty] | 100% |  |  |  | 54235 |  |  |  | 10.507 | 7.9801 | 58906.4516 | 70.26% | 23.36% | 99.5% | 99.7% | [9 empty] | 10.507
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 12.0167 | 6.48 |  | 7.35 |  | 30.195 | 46.4332 | 0.77069 | 3.0956 | 99.41% |  |  | 100% |  | 100% | 69.07% |  | 21.15% | 53893 | 53644.4 | 307.2 | 53337.2 | 10.507 | 7.9801 | 58906.4516 | 70.26% | 23.36% | 99.5% | 99.7% | [9 empty] | 10.507
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 12.0667 | 6.12 |  | 6.55 |  | 30.0404 | 44.9267 | 0.68876 | 3.2757 | 100% |  |  | 100% |  | 100% | 70.32% |  | 19.19% | 49194 | 48696.2 | 300.12 | 48396.08 | 10.507 | 7.9801 | 58906.4516 | 70.26% | 23.36% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 12.0333 | 5.15 |  | 5.39 |  | 28.4382 | 41.5418 | 0.68871 | 0.7893 | 100% |  |  | 100% |  | 100% | 70.39% |  | 15.81% | 40482 | 40160.4 | 298.14 | 39862.26 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 11.85 | 5.9 |  | 6.35 |  | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 99.72% |  |  | 100% |  | 100% | 69.35% |  | 18.35% | 46883 | 46564.5 | 297.24 | 46267.26 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 11.8167 | 3.96 |  | 4.01 |  | 25.546 | 35.8572 | 0.82389 | 5.4078 | 100% |  |  | 100% |  | 100% | 71.45% |  | 11.94% | 30661 | 30406.1 | 303.66 | 30102.44 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 11.7167 | 6.87 |  | 7.54 |  | 29.7818 | 46.949 | 0.66326 | 3.4188 | 93.78% |  |  | 100% |  | 100% | 63.81% |  | 20.05% | 51196 | 50867.5 | 315.9 | 50551.6 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 12.0333 | 5.83 |  | 6.46 |  | 28.4187 | 45.7694 | 0.68469 | 1.9063 | 94.53% |  |  | 100% |  | 100% | 62.01% |  | 16.69% | 42695 | 42409.8 | 320.28 | 42089.52 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 11.9333 | 6.67 |  | 7.57 |  | 28.7698 | 47.3622 | 0.80936 | 5.3675 | 92.12% |  |  | 100% |  | 100% | 62.28% |  | 19.64% | 50173 | 49870.8 | 333.6 | 49537.2 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 12.0833 | 6.71 |  | 7.795 |  | 30.2429 | 47.9448 | 0.93582 | 4.3852 | 95.38% |  |  | 100% |  | 100% | 64.3% |  | 20.88% | 53234 | 52971 | 306.72 | 52664.28 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 11.75 | 6.17 |  | 6.915 |  | 29.8993 | 45.5016 | 0.88285 | 3.6838 | 100% |  |  | 100% |  | 100% | 67.4% |  | 19.42% | 49687 | 49299.7 | 330.24 | 48969.46 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 11.95 | 6.37 |  | 7.28 |  | 29.6186 | 46.9441 | 0.86043 | 2.7865 | 99.55% |  |  | 100% |  | 100% | 68.17% |  | 20.68% | 52795 | 52462 | 321.78 | 52140.22 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 12.2333 | 5.79 |  | 6.5 |  | 28.7091 | 41.8396 | 1.2756 | 3.9577 | 100% |  |  | 100% |  | 100% | 70.66% |  | 19.14% | 48867 | 48565 | 310.32 | 48254.68 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 11.8833 | 6.45 |  | 7.39 |  | 30.195 | 46.4332 | 0.77069 | 3.0956 | 99.08% |  |  | 100% |  | 100% | 69% |  | 21.25% | 54147 | 53890.1 | 311.7 | 53578.4 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 6.28 |  | 6.92 |  | 29.689 | 46.6091 | 0.67979 | 4.34 | 99.76% |  |  | 100% |  | 100% | 70.78% |  | 20.41% | 52068 | 51780.9 | 316.32 | 51464.58 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 12.1167 | 6.52 |  | 7.375 |  | 30.195 | 46.4332 | 0.77069 | 3.0956 | 99.82% |  |  | 100% |  | 100% | 68.99% |  | 21.2% | 54092 | 53778 | 319.02 | 53458.98 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 12.0167 | 5.86 |  | 6.35 |  | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 100% |  |  | 100% |  | 100% | 69.22% |  | 18.32% | 46808 | 46506.6 | 321 | 46185.6 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 11.9833 | 6.99 |  | 8 |  | 30.166 | 48.516 | 0.50302 | 0.51512 | 91.22% |  |  | 100% |  | 100% | 60.2% |  | 20.07% | 51167 | 50904.5 | 302.22 | 50602.28 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 11.9167 | 5.89 |  | 6.75 |  | 28.7698 | 47.3622 | 0.80936 | 5.3675 | 100% |  |  | 100% |  | 100% | 70.1% |  | 19.71% | 50324 | 50024.5 | 311.52 | 49712.98 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 6.95 |  | 7.71 |  | 28.463 | 43.4858 | 1.6153 | 3.9035 | 99.65% |  |  | 100% |  | 100% | 69.49% |  | 22.32% | 56566 | 56633 | 340.8 | 56292.2 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 12.0333 | 6.15 |  | 6.69 |  | 28.7698 | 47.3622 | 0.80936 | 5.3675 | 100% |  |  | 100% |  | 100% | 70.09% |  | 19.54% | 50070 | 49607.9 | 338.76 | 49269.14 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 11.8167 | 6.15 |  | 6.69 |  | 30.166 | 48.516 | 0.50302 | 0.51512 | 100% |  |  | 100% |  | 100% | 72.48% |  | 20.2% | 51579 | 51255.3 | 304.86 | 50950.44 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 11.6667 | 4.3 |  | 4.67 |  | 25.0801 | 36.1312 | 1.2497 | 5.4514 | 100% |  |  | 100% |  | 100% | 73.2% |  | 14.24% | 36513 | 36221.9 | 302.64 | 35919.26 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 12.0833 | 6.23 |  | 6.94 |  | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 93.32% |  |  | 100% |  | 100% | 62.32% |  | 18.02% | 46107 | 45826.5 | 381.3 | 45445.2 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 12.1667 | 6.42 |  | 7.2 |  | 30.195 | 46.4332 | 0.77069 | 3.0956 | 100% |  |  | 100% |  | 100% | 70.21% |  | 21.06% | 53685 | 53370.8 | 257.4 | 53113.4 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 12.15 | 6.08 |  | 6.4 |  | 30.2277 | 45.4561 | 0.88646 | 4.0239 | 100% |  |  | 100% |  | 100% | 70.54% |  | 18.81% | 48034 | 47736.8 | 305.52 | 47431.28 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 12.2167 | 6.66 |  | 7.175 |  | 30.7169 | 47.3243 | 1.0548 | 4.043 | 100% |  |  | 100% |  | 100% | 69.8% |  | 20.87% | 53244 | 52925.3 | 305.76 | 52619.54 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 12.0333 | 6.14 |  | 6.48 |  | 30.479 | 47.1594 | 0.89744 | 3.3385 | 100% |  |  | 100% |  | 100% | 70.49% |  | 19.03% | 48596 | 48299.1 | 308.7 | 47990.4 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 12.25 | 6.83 |  | 7.555 |  | 30.1302 | 47.6614 | 1.2327 | 4.8132 | 99.65% |  |  | 100% |  | 100% | 68.09% |  | 21.44% | 54705 | 54362.6 | 308.88 | 54053.72 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 12.1333 | 6.07 |  | 6.38 |  | 30.2277 | 45.4561 | 0.88646 | 4.0239 | 100% |  |  | 100% |  | 100% | 70.62% |  | 18.77% | 47907 | 47634.5 | 296.58 | 47337.92 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 11.8667 | 6.45 |  | 7.2 |  | 30.195 | 46.4332 | 0.77069 | 3.0956 | 100% |  |  | 100% |  | 100% | 70.83% |  | 21.25% | 54162 | 53883 | 298.08 | 53584.92 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 12.3167 | 6.32 |  | 6.74 |  | 28.8325 | 45.3299 | 0.84028 | 4.5702 | 100% |  |  | 100% |  | 100% | 69.99% |  | 19.66% | 50174 | 49894.5 | 326.22 | 49568.28 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 12.2167 | 6.39 |  | 6.92 |  | 29.0602 | 45.8714 | 1.0987 | 8.6629 | 100% |  |  | 100% |  | 100% | 70.42% |  | 20.31% | 51819 | 51524.8 | 321.72 | 51203.08 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 12.35 | 3.54 |  | 4.11 |  | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 100% |  |  | 92.34% |  | 100% | 70.43% |  | 12.06% | 30886 | 30715.2 | 301.14 | 30414.06 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 12.25 | 6.09 |  | 6.63 |  | 29.2157 | 45.438 | 0.72585 | 2.4936 | 100% |  |  | 100% |  | 100% | 70.34% |  | 19.43% | 49594 | 49302.6 | 303.9 | 48998.7 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 12.3333 | 6.51 |  | 7.1115 |  | 28.1139 | 44.2016 | 0.9761 | 3.9187 | 100% |  |  | 100% |  | 100% | 70.49% |  | 20.89% | 53263 | 53007.8 | 339.3 | 52668.5 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 12.5667 | 6.85 |  | 7.435 |  | 29.436 | 45.0088 | 1.0626 | 4.7309 | 100% |  |  | 100% |  | 100% | 70% |  | 21.68% | 55317 | 55015.5 | 333.9 | 54681.6 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 12.2 | 7.05 |  | 7.68 |  | 30.0837 | 48.4744 | 0.81191 | 3.4706 | 100% |  |  | 100% |  | 100% | 69.6% |  | 22.27% | 56763 | 56466.9 | 302.4 | 56164.5 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 12.4333 | 7.32 |  | 8.09 |  | 29.9635 | 46.6534 | 1.1117 | 4.0151 | 100% |  |  | 100% |  | 100% | 70.28% |  | 23.69% | 60376 | 60044.3 | 301.5 | 59742.8 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 12.3667 | 7.18 |  | 7.65 |  | 30.1719 | 46.9672 | 1.0444 | 3.5784 | 100% |  |  | 100% |  | 100% | 70.91% |  | 22.6% | 57616 | 57301.1 | 305.22 | 56995.88 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 12.4167 | 7.12 |  | 7.59 |  | 29.0606 | 46.286 | 1.1257 | 4.0229 | 100% |  |  | 100% |  | 100% | 70.37% |  | 22.26% | 56735 | 56430.1 | 308.94 | 56121.16 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 12.4833 | 6.7 |  | 6.9 |  | 29.1228 | 46.1707 | 0.85347 | 5.0674 | 100% |  |  | 100% |  | 100% | 71.25% |  | 20.49% | 52295 | 51954.8 | 297.54 | 51657.26 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 12.5333 | 7.29 |  | 8.055 |  | 29.3381 | 47.275 | 1.0885 | 4.3083 | 100% |  |  | 100% |  | 100% | 69.71% |  | 23.4% | 59587 | 59289.6 | 289.08 | 59000.52 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 12.4667 | 7.31 |  | 7.725 |  | 29.4336 | 47.5887 | 0.77545 | 3.6446 | 99.24% |  |  | 100% |  | 100% | 70.07% |  | 22.55% | 57526 | 57178.6 | 304.98 | 56873.62 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 12.25 | 6.86 |  | 7.49 |  | 29.2109 | 45.9608 | 0.87807 | 3.8396 | 99.7% |  |  | 100% |  | 100% | 67.26% |  | 20.99% | 53536 | 53230.8 | 296.64 | 52934.16 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 12.1667 | 6.74 |  | 7.425 |  | 27.805 | 44.9838 | 1.1785 | 5.2118 | 100% |  |  | 100% |  | 100% | 70.52% |  | 21.82% | 55683 | 55335.7 | 320.16 | 55015.54 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 12.4833 | 6.2 |  | 6.8 |  | 28.8336 | 44.3876 | 0.8506 | 2.5289 | 99.71% |  |  | 100% |  | 100% | 69.96% |  | 19.82% | 50584 | 50304.1 | 322.56 | 49981.54 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 12.3333 | 6.21 |  | 6.475 |  | 28.3453 | 44.0653 | 0.86462 | 3.7344 | 100% |  |  | 100% |  | 100% | 70.97% |  | 19.15% | 48886 | 48587.4 | 304.44 | 48282.96 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 12.4333 | 6.18 |  | 6.82 |  | 27.7906 | 43.4285 | 1.0359 | 5.8035 | 99.61% |  |  | 100% |  | 100% | 69.8% |  | 19.83% | 50672 | 50333.3 | 316.02 | 50017.28 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 11.9667 | 3.77 |  | 3.83 |  | 25.9971 | 35.2061 | 0.98105 | 7.1985 | 100% |  |  | 100% |  | 100% | 74.66% |  | 11.91% | 30557 | 30361.4 | 316.38 | 30045.02 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 12.3333 | 6.05 |  | 6.4 |  | 27.759 | 41.2443 | 1.1753 | 4.1536 | 98.25% |  |  | 100% |  | 100% | 71.09% |  | 18.96% | 48440 | 48124 | 320.16 | 47803.84 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 11.7333 | 2.8 |  | 2.7 |  | 24.5407 | 30.8411 | 0.73105 | 3.1102 | 100% |  |  | 100% |  | 100% | 79.58% |  | 8.952% | 23247 | 22910 | 335.28 | 22574.72 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 11.5833 | 3.4 |  | 3.32 |  | 24.4541 | 32.8874 | 0.9356 | 5.0809 | 100% |  |  | 100% |  | 100% | 76.72% |  | 10.61% | 27334 | 27107.6 | 344.52 | 26763.08 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 12.5333 | 3.84 |  | 3.87 |  | 24.4997 | 32.5266 | 1.7049 | 8.8073 | 100% |  |  | 100% |  | 100% | 75.83% |  | 12.23% | 31363 | 31150.6 | 317.64 | 30832.96 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 12.4667 | 5.17 |  | 5.38 |  | 26.4095 | 37.0329 | 1.5431 | 6.5777 | 100% |  |  | 100% |  | 100% | 74.24% |  | 16.64% | 42418 | 42265.1 | 301.2 | 41963.9 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 12.55 | 4.282 |  | 5.25 |  | 25.4426 | 35.2243 | 2.3078 | 8.0038 | 99.66% |  |  | 100% |  | 100% | 71.48% |  | 15.64% | 39983 | 39726.5 | 297.66 | 39428.84 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 12.2667 | 3.05 |  | 3.005 |  | 24.9328 | 31.1882 | 2.7855 | 9.2161 | 90.67% |  |  | 97.63% |  | 100% | 70.77% |  | 8.861% | 22845 | 22653.2 | 309.54 | 22343.66 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 12.3333 | 3.08 |  | 3.18 |  | 23.9943 | 30.1193 | 2.6118 | 8.8609 | 98.88% |  |  | 97.66% |  | 100% | 82.08% |  | 10.88% | 27658 | 27757.2 | 333.78 | 27423.42 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 12.35 | 3.52 |  | 3.48 |  | 25.965 | 35.6713 | 0.92166 | 10.1554 | 99.69% |  |  | 100% |  | 100% | 79.49% |  | 11.53% | 29675 | 29399 | 334.5 | 29064.5 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 12.4167 | 3.82 |  | 3.825 |  | 24.4997 | 32.5266 | 1.7049 | 8.8073 | 100% |  |  | 100% |  | 100% | 78.08% |  | 12.44% | 31929 | 31673.3 | 292.62 | 31380.68 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 12.0167 | 3.45 |  | 3.35 |  | 25.0635 | 31.196 | 1.7759 | 9.2261 | 99.11% |  |  | 100% |  | 100% | 77.49% |  | 10.82% | 28074 | 27668.9 | 394.98 | 27273.92 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 12.5667 | 3.82 |  | 3.73 |  | 24.8504 | 32.0049 | 1.7221 | 6.348 | 100% |  |  | 100% |  | 100% | 79.72% |  | 12.39% | 31705 | 31459.8 | 217.8 | 31242 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 12.4333 | 3.04 |  | 2.84 |  | 24.9062 | 31.002 | 1.1343 | 6.0709 | 100% |  |  | 100% |  | 100% | 79.81% |  | 9.445% | 24404 | 24174.1 | 357.72 | 23816.38 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 12.5667 | 5.15 |  | 5.185 |  | 26.5776 | 37.2281 | 0.83761 | 4.3921 | 100% |  |  | 100% |  | 100% | 74.66% |  | 16.13% | 41184 | 40932.2 | 256.02 | 40676.18 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 6.55 |  | 6.93 |  | 27.3767 | 41.1267 | 1.6266 | 6.4821 | 100% |  |  | 100% |  | 100% | 72.15% |  | 20.83% | 53154 | 52863.7 | 325.92 | 52537.78 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 12.5667 | 5.57 |  | 6.035 |  | 27.2883 | 39.0841 | 1.9193 | 5.6299 | 100% |  |  | 100% |  | 100% | 72.57% |  | 18.25% | 46599 | 46304.9 | 285.48 | 46019.42 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 12.55 | 4.89 |  | 5.14 |  | 25.605 | 36.1476 | 1.4758 | 6.5289 | 99.48% |  |  | 100% |  | 100% | 73.09% |  | 15.65% | 40194 | 39789.7 | 318.06 | 39471.64 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 12.6167 | 6.58 |  | 7.005 |  | 27.1915 | 41.3755 | 0.88924 | 4.8114 | 100% |  |  | 100% |  | 100% | 72.33% |  | 21.11% | 53894 | 53552.2 | 314.58 | 53237.62 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 6.7 |  | 7.385 |  | 27.7997 | 43.1336 | 0.7642 | 1.0214 | 100% |  |  | 98.49% |  | 100% | 70.06% |  | 21.56% | 54911 | 54650.2 | 284.76 | 54365.44 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 12.6167 | 6.98 |  | 7.81 |  | 28.4327 | 45.7312 | 0.75488 | 0.95623 | 99.44% |  |  | 100% |  | 100% | 68.92% |  | 22.43% | 57121 | 56822.9 | 266.76 | 56556.14 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 12.6667 | 7.33 |  | 8.04 |  | 27.8549 | 45.2894 | 0.74587 | 0.88982 | 99.1% |  |  | 100% |  | 100% | 68.75% |  | 23.03% | 58895 | 58384.4 | 309.24 | 58075.16 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 12.6 | 6.98 |  | 7.535 |  | 28.6728 | 45.2306 | 0.72955 | 0.89025 | 100% |  |  | 100% |  | 100% | 69.66% |  | 21.87% | 55744 | 55431.4 | 281.46 | 55149.94 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 11.1833 | 4.54 |  | 4.545 |  | 26.9089 | 38.0863 | 0.70516 | 0.81437 | 99.64% |  |  | 100% |  | 100% | 72.5% |  | 13.73% | 35220 | 34941 | 318.3 | 34622.7 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 12.6833 | 5.3 |  | 5.63 |  | 26.4095 | 37.0329 | 1.5431 | 6.5777 | 100% |  |  | 94.61% |  | 100% | 72.29% |  | 16.96% | 42814 | 43074.7 | 313.92 | 42760.78 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 11.8167 | 4.31 |  | 4.44 |  | 26.5317 | 37.1209 | 0.73589 | 7.87 | 100% |  |  | 100% |  | 100% | 74.6% |  | 13.8% | 35337 | 35099.7 | 296.88 | 34802.82 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 12.35 | 4.4 |  | 4.555 |  | 25.5925 | 35.2972 | 1.4968 | 6.8728 | 100% |  |  | 100% |  | 100% | 73.13% |  | 13.88% | 35668 | 35332.8 | 334.02 | 34998.78 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 12.3333 | 3.85 |  | 3.94 |  | 24.8504 | 32.0049 | 1.7221 | 6.348 | 100% |  |  | 100% |  | 100% | 75.23% |  | 12.35% | 31579 | 31433.3 | 291.12 | 31142.18 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 11.8167 | 3.86 |  | 3.83 |  | 25.0924 | 33.2292 | 1.4089 | 5.8479 | 99.45% |  |  | 100% |  | 100% | 74.67% |  | 11.92% | 30633 | 30367.5 | 319.62 | 30047.88 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 12.5667 | 3.1 |  | 3 |  | 23.9379 | 28.828 | 2.9794 | 8.7773 | 100% |  |  | 100% |  | 100% | 78.48% |  | 9.81% | 25311 | 25025.9 | 289.14 | 24736.76 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 12.4833 | 4.11 |  | 4.255 |  | 24.539 | 31.5177 | 2.6537 | 10.3186 | 99.68% |  |  | 100% |  | 100% | 74.33% |  | 13.18% | 33762 | 33533.7 | 301.74 | 33231.96 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 12.4833 | 3.62 |  | 3.54 |  | 24.5281 | 31.0709 | 1.4826 | 6.9411 | 100% |  |  | 100% |  | 100% | 77.36% |  | 11.41% | 29336 | 29075.5 | 301.14 | 28774.36 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 12.5333 | 4.15 |  | 4.23 |  | 25.3852 | 34.0119 | 0.74291 | 3.351 | 100% |  |  | 100% |  | 100% | 76.07% |  | 13.41% | 34349 | 34104.8 | 295.98 | 33808.82 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 4.99 |  | 5.1 |  | 26.0367 | 35.6802 | 0.64889 | 2.4967 | 98.86% |  |  | 100% |  | 100% | 74.96% |  | 15.93% | 40659 | 40461.6 | 293.46 | 40168.14 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 12.6667 | 5.7 |  | 6.12 |  | 26.5611 | 38.1114 | 1.2775 | 6.5962 | 100% |  |  | 100% |  | 100% | 72.75% |  | 18.55% | 47760 | 47072.4 | 291.36 | 46781.04 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 5.63 |  | 5.915 |  | 26.6403 | 37.3416 | 2.2367 | 6.7845 | 100% |  |  | 100% |  | 100% | 74.02% |  | 18.24% | 46582 | 46294.7 | 290.22 | 46004.48 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 12.6167 | 0.65 |  | 0.75 |  | 25.1226 | 32.9897 | 1.894 | 7.725 | 100% |  |  | 20.23% |  | 100% | 87.27% |  | 2.727% | 7264 | 7170.4 | 293.4 | 6877 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 12.35 | 4.83 |  | 4.83 |  | 25.3778 | 33.8383 | 2.7888 | 8.3454 | 100% |  |  | 100% |  | 100% | 76.74% |  | 15.44% | 39386 | 39246.1 | 301.26 | 38944.84 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 3.64 |  | 3.56 |  | 24.8022 | 31.1665 | 2.3958 | 8.3188 | 100% |  |  | 100% |  | 100% | 77.68% |  | 11.52% | 29608 | 29364.2 | 308.82 | 29055.38 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 12.5 | 2.97 |  | 2.87 |  | 23.9379 | 28.828 | 2.9794 | 8.7773 | 100% |  |  | 100% |  | 100% | 78.47% |  | 9.384% | 24215 | 23934.7 | 271.5 | 23663.2 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 12.6667 | 4.24 |  | 4.32 |  | 25.9955 | 34.2471 | 2.3294 | 6.7935 | 100% |  |  | 100% |  | 100% | 74.72% |  | 13.45% | 34482 | 34208.7 | 295.02 | 33913.68 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 12.5 | 3.85 |  | 3.935 |  | 24.8504 | 32.0049 | 1.7221 | 6.348 | 100% |  |  | 100% |  | 100% | 74.81% |  | 12.27% | 31473 | 31221 | 291.18 | 30929.82 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 4.44 |  | 4.51 |  | 25.6635 | 34.8133 | 2.1412 | 6.8482 | 100% |  |  | 100% |  | 100% | 74.07% |  | 13.92% | 35660 | 35421.2 | 324.18 | 35097.02 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 12.5667 | 5.59 |  | 6.13 |  | 26.469 | 37.6205 | 2.6835 | 6.9793 | 100% |  |  | 100% |  | 100% | 72.57% |  | 18.54% | 47284 | 47039.1 | 295.56 | 46743.54 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 12.6 | 5.73 |  | 6.1 |  | 26.1369 | 36.905 | 2.8151 | 8.1669 | 100% |  |  | 100% |  | 100% | 72.55% |  | 18.44% | 47160 | 46778.8 | 279.84 | 46498.96 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | 12.5333 | 2.81 |  | 2.73 |  | 24.5237 | 29.5575 | 1.9007 | 6.3871 | 100% |  |  | 100% |  | 100% | 78.26% |  | 8.902% | 22912 | 22756.1 | 308.7 | 22447.4 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | 12.5667 | 4.16 |  | 4.165 |  | 25.305 | 32.8784 | 2.7888 | 8.3454 | 100% |  |  | 100% |  | 100% | 75.08% |  | 13.03% | 33427 | 33176.8 | 322.56 | 32854.24 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | 12.3333 | 3.28 |  | 3.23 |  | 24.0753 | 30.4552 | 2.0251 | 6.7358 | 100% |  |  | 100% |  | 100% | 77.51% |  | 10.43% | 26824 | 26633 | 326.94 | 26306.06 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | 12.5333 | 5.62 |  | 5.42 |  | 26.1687 | 36.736 | 2.5883 | 8.6863 | 99.64% |  |  | 100% |  | 100% | 72.21% |  | 16.31% | 41656 | 41416.1 | 296.28 | 41119.82 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | 12.55 | 2.71 |  | 2.63 |  | 23.9478 | 28.5037 | 1.8307 | 5.4042 | 100% |  |  | 100% |  | 100% | 78.54% |  | 8.606% | 22188 | 21980.1 | 277.98 | 21702.12 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | 12.6333 | 3.76 |  | 3.815 |  | 24.2217 | 47.3601 | 2.4316 | 7.1164 | 100% |  |  | 100% |  | 100% | 76.54% |  | 12.17% | 31174 | 30965.9 | 286.02 | 30679.88 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | 12.6333 | 4.44 |  | 4.51 |  | 25.5325 | 34.3461 | 2.6348 | 8.1784 | 91.8% |  |  | 100% |  | 100% | 72.43% |  | 13.61% | 34776 | 34607.5 | 287.1 | 34320.4 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | 12.5333 | 5.03 |  | 5.49 |  | 26.1687 | 36.736 | 2.5883 | 8.6863 | 100% |  |  | 100% |  | 100% | 71.89% |  | 16.44% | 42326 | 41747.8 | 281.88 | 41465.92 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | 12.6 | 5.02 |  | 5.335 |  | 19.74 | 17.4871 | 0.63784 | 7.0452 | 100% |  |  | 100% |  | 100% | 71.07% |  | 15.8% | 40266 | 40028.3 | 191.46 | 39836.84 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | 12.0333 | 3.3 |  | 3.325 |  | 24.0753 | 30.4552 | 2.0251 | 6.7358 | 100% |  |  | 100% |  | 100% | 74.6% |  | 10.34% | 26496 | 26366.1 | 304.14 | 26061.96 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | 12.35 | 5.1 |  | 5.3 |  | 26.0367 | 35.6802 | 0.64889 | 2.4967 | 99.7% |  |  | 100% |  | 100% | 72.15% |  | 15.93% | 40824 | 40498.9 | 321.9 | 40177 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | 12.6833 | 4.36 |  | 4.445 |  | 25.5618 | 34.0561 | 1.6255 | 6.257 | 100% |  |  | 100% |  | 100% | 73.8% |  | 13.67% | 35045 | 34773 | 307.5 | 34465.5 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | 12.4333 | 4.28 |  | 4.425 |  | 25.6987 | 34.7175 | 1.49 | 5.9534 | 100% |  |  | 100% |  | 100% | 73.63% |  | 13.58% | 34830 | 34549 | 315.6 | 34233.4 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | 12.5667 | 4.67 |  | 4.87 |  | 25.3089 | 34.5544 | 2.4242 | 7.6105 | 100% |  |  | 100% |  | 100% | 71.99% |  | 14.61% | 37310 | 37133.6 | 297.12 | 36836.48 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | 12.55 | 3.52 |  | 3.44 |  | 25.1889 | 31.752 | 1.4626 | 4.9563 | 100% |  |  | 100% |  | 100% | 76.74% |  | 11% | 28280 | 28052 | 315.54 | 27736.46 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Annual KPI
Till Date | 2025-07-15 | 2025-07-01
ES Energy Private Limited Performance Summary
Financial Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target TA (%) | Measured TA (%)
2026 | 106 | 664.3912 | 591.7915 | 4752.3742 | 4431.6645 | 68.08% | 71.27% | 17.78% | 16.58% | 99.7% | 99.07% | 99.5% | 99.33% | 99.9% | 100%
ES Energy Private Limited Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target TA (%) | Measured TA (%)
2025-04-01 | 30 | 227.6882 | 203.345 | 1584.5717 | 1460.2205 | 66.24% | 68.34% | 20.95% | 19.3% | 99.7% | 100% | 99.5% | 98.59% | 99.9% | 100%
2025-05-01 | 31 | 215.5443 | 173.3315 | 1574.4307 | 1312.1832 | 69.52% | 72.05% | 20.14% | 16.79% | 99.7% | 99.6% | 99.5% | 99.5% | 99.9% | 100%
2025-06-01 | 30 | 157.117 | 151.985 | 1121.9949 | 1169.0173 | 67.97% | 73.21% | 14.83% | 15.45% | 99.7% | 97.11% | 99.5% | 99.85% | 99.9% | 100%
2025-07-01 | 15 | 64.0417 | 63.13 | 471.3769 | 490.2435 | 70.05% | 73.91% | 12.46% | 12.96% | 99.7% | 100% | 99.5% | 99.41% | 99.9% | 100%
2025-08-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%
2025-09-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%
2025-10-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%
2025-11-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%
2025-12-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%
2026-01-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%
2026-02-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%
2026-03-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%

## Raw Data
[16 empty] | 68346.586 | 9.5173 | [15 empty] | 68213.041
[7 empty] | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
Finacial Year | Calendar Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Plant DC Capcity (MW) | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | IC1_Inv1 | IC1_Inv2 | IC1_Inv3 | IC1_Inv4 | IC2_Inv1 | IC2_Inv2 | 66 kV ABT Main Meter Reading (Export) | 66 kV CRP MFM Reading (Import) | GHI(Wh/m2) | POA1(Wh/m2) | POA2(Wh/m2) | Avg. POA Lost (W/m2) | Avg. Ambient Temp (POA>20W/m2) | Avg. Module Temp (POA>20W/m2) | Avg. Wind Speed (m/s) | Max. Wind Speed (m/s) | Rain Fall (mm) | Inverters Generation ( kWh) | Export (kWh) | Import (kWh) | Net Export (kWh) | Avg. POA without Exclusion (W/m2)2 | Net Avg. POA with Exclusion (W/m2) | 66 kV ABT Check Meter Reading (Export) | Operating Hours
FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 10.507 | 0.27014 | 0.77014 | 8820 | 9612 | 9180 | 9120 | 9072 | 8431 | 115938.3561 | 15.4725 | 6600 | 7390 | 7360 | 0 | 30.4938 | 46.4586 | 0.67534 | 0.69938 | 0 | 54235 | #REF! | #REF! | #REF! | 7375 | 7375 | 115751.6377 | 12
FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 10.507 | 0.26944 | 0.77014 | 8560 | 9650 | 9150 | 9063 | 9050 | 8420 | 115992.0005 | 15.4776 | 6480 | 7350 | 7350 | 0 | 30.195 | 46.4332 | 0.77069 | 3.0956 | 0 | 53893 | 53644.4 | 307.2 | 53337.2 | 7350 | 7350 | 115805.2136 | 12.0167
FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 10.507 | 0.26806 | 0.77083 | 7943 | 8710 | 8171 | 8270 | 8230 | 7870 | 116040.6967 | 15.4826 | 6120 | 6550 | 6550 | 0 | 30.0404 | 44.9267 | 0.68876 | 3.2757 | 0 | 49194 | 48696.2 | 300.12 | 48396.08 | 6550 | 6550 | 115853.8466 | 12.0667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-01 | 10.507 | 0.27014 | 0.77153 | 6540 | 7074 | 6790 | 6934 | 6783 | 6361 | 116080.8571 | 15.4876 | 5150 | 5390 | 5390 | 0 | 28.4382 | 41.5418 | 0.68871 | 0.7893 | 0 | 40482 | 40160.4 | 298.14 | 39862.26 | 5390 | 5390 | 115893.9519 | 12.0333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 10.507 | 0.26597 | 0.75972 | 7520 | 8243 | 7860 | 8010 | 7820 | 7430 | 116127.4216 | 15.4925 | 5900 | 6350 | 6350 | 0 | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 0 | 46883 | 46564.5 | 297.24 | 46267.26 | 6350 | 6350 | 115940.4547 | 11.85
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-03 | 10.507 | 0.26319 | 0.75556 | 4840 | 5440 | 5230 | 5361 | 4910 | 4880 | 116157.8277 | 15.4976 | 3960 | 4010 | 4010 | 0 | 25.546 | 35.8572 | 0.82389 | 5.4078 | 3.81 | 30661 | 30406.1 | 303.66 | 30102.44 | 4010 | 4010 | 115970.8189 | 11.8167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 10.507 | 0.27153 | 0.75972 | 8884 | 9660 | 9350 | 6091 | 8770 | 8441 | 116208.6952 | 15.5029 | 6870 | 7540 | 7540 | 0 | 29.7818 | 46.949 | 0.66326 | 3.4188 | 0 | 51196 | 50867.5 | 315.9 | 50551.6 | 7540 | 7540 | 116021.6216 | 11.7167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 10.507 | 0.26458 | 0.76597 | 7660 | 8382 | 7993 | 3420 | 7810 | 7430 | 116251.105 | 15.5082 | 5830 | 6460 | 6460 | 0 | 28.4187 | 45.7694 | 0.68469 | 1.9063 | 0 | 42695 | 42409.8 | 320.28 | 42089.52 | 6460 | 6460 | 116063.9771 | 12.0333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 10.507 | 0.27083 | 0.76806 | 8570 | 9534 | 9143 | 5111 | 9171 | 8644 | 116300.9758 | 15.5138 | 6670 | 7600 | 7540 | 0 | 28.7698 | 47.3622 | 0.80936 | 5.3675 | 4.11 | 50173 | 49870.8 | 333.6 | 49537.2 | 7570 | 7570 | 116113.785 | 11.9333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-07 | 10.507 | 0.26458 | 0.76806 | 9130 | 9772 | 9340 | 6838 | 9373 | 8781 | 116353.9468 | 15.5189 | 6710 | 7840 | 7750 | 0 | 30.2429 | 47.9448 | 0.93582 | 4.3852 | 0 | 53234 | 52971 | 306.72 | 52664.28 | 7795 | 7795 | 116166.6905 | 12.0833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-08 | 10.507 | 0.26319 | 0.75278 | 7940 | 8753 | 8484 | 8450 | 8290 | 7770 | 116403.2465 | 15.5244 | 6170 | 6980 | 6850 | 0 | 29.8993 | 45.5016 | 0.88285 | 3.6838 | 0 | 49687 | 49299.7 | 330.24 | 48969.46 | 6915 | 6915 | 116215.9293 | 11.75
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-09 | 10.507 | 0.2625 | 0.76042 | 8330 | 9320 | 9010 | 9142 | 8763 | 8230 | 116455.7085 | 15.5297 | 6370 | 7300 | 7260 | 0 | 29.6186 | 46.9441 | 0.86043 | 2.7865 | 0 | 52795 | 52462 | 321.78 | 52140.22 | 7280 | 7280 | 116268.3252 | 11.95
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-10 | 10.507 | 0.26319 | 0.77292 | 7913 | 8490 | 8390 | 8324 | 8130 | 7620 | 116504.2735 | 15.5349 | 5790 | 6500 | 6500 | 0 | 28.7091 | 41.8396 | 1.2756 | 3.9577 | 0 | 48867 | 48565 | 310.32 | 48254.68 | 6500 | 6500 | 116316.8291 | 12.2333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-11 | 10.507 | 0.26389 | 0.75903 | 8463 | 9493 | 9450 | 9360 | 8881 | 8500 | 116558.1636 | 15.5401 | 6450 | 7420 | 7360 | 0 | 30.195 | 46.4332 | 0.77069 | 3.0956 | 0 | 54147 | 53890.1 | 311.7 | 53578.4 | 7390 | 7390 | 116370.6522 | 11.8833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-12 | 10.507 | 0.26458 | 0.76458 | 8304 | 9120 | 9022 | 9000 | 8620 | 8002 | 116609.9445 | 15.5454 | 6280 | 6940 | 6900 | 0 | 29.689 | 46.6091 | 0.67979 | 4.34 | 0.98 | 52068 | 51780.9 | 316.32 | 51464.58 | 6920 | 6920 | 116422.3683 | 12
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-13 | 10.507 | 0.26389 | 0.76875 | 8700 | 9442 | 9341 | 9224 | 9003 | 8382 | 116663.7225 | 15.5507 | 6520 | 7400 | 7350 | 0 | 30.195 | 46.4332 | 0.77069 | 3.0956 | 0 | 54092 | 53778 | 319.02 | 53458.98 | 7375 | 7375 | 116476.0812 | 12.1167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-14 | 10.507 | 0.26389 | 0.76458 | 7373 | 8182 | 8150 | 8023 | 7800 | 7280 | 116710.2291 | 15.5561 | 5860 | 6350 | 6350 | 0 | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 1.34 | 46808 | 46506.6 | 321 | 46185.6 | 6350 | 6350 | 116522.5312 | 12.0167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-15 | 10.507 | 0.26528 | 0.76458 | 9430 | 9863 | 9980 | 3352 | 9640 | 8902 | 116761.1336 | 15.5611 | 6990 | 8000 | 8000 | 0 | 30.166 | 48.516 | 0.50302 | 0.51512 | 0 | 51167 | 50904.5 | 302.22 | 50602.28 | 8000 | 8000 | 116573.3731 | 11.9833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-16 | 10.507 | 0.26736 | 0.76389 | 8150 | 8624 | 8654 | 8440 | 8466 | 7990 | 116811.1581 | 15.5663 | 5890 | 6750 | 6750 | 0 | 28.7698 | 47.3622 | 0.80936 | 5.3675 | 0 | 50324 | 50024.5 | 311.52 | 49712.98 | 6750 | 6750 | 116623.3354 | 11.9167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-17 | 10.507 | 0.26389 | 0.76389 | 8560 | 9994 | 9810 | 9742 | 9540 | 8920 | 116867.7911 | 15.572 | 6950 | 7710 | 7710 | 0 | 28.463 | 43.4858 | 1.6153 | 3.9035 | 0 | 56566 | 56633 | 340.8 | 56292.2 | 7710 | 7710 | 116679.899 | 12
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-18 | 10.507 | 0.26458 | 0.76597 | 7910 | 8822 | 8600 | 8810 | 8114 | 7814 | 116917.399 | 15.5776 | 6150 | 6690 | 6690 | 0 | 28.7698 | 47.3622 | 0.80936 | 5.3675 | 0 | 50070 | 49607.9 | 338.76 | 49269.14 | 6690 | 6690 | 116729.4457 | 12.0333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-19 | 10.507 | 0.26597 | 0.75833 | 8310 | 8910 | 8811 | 8844 | 8650 | 8054 | 116968.6543 | 15.5827 | 6150 | 6690 | 6690 | 0 | 30.166 | 48.516 | 0.50302 | 0.51512 | 4.24 | 51579 | 51255.3 | 304.86 | 50950.44 | 6690 | 6690 | 116780.6388 | 11.8167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-20 | 10.507 | 0.26736 | 0.75347 | 5892 | 6274 | 6310 | 6382 | 5975 | 5680 | 117004.8762 | 15.5877 | 4300 | 4670 | 4670 | 0 | 25.0801 | 36.1312 | 1.2497 | 5.4514 | 0 | 36513 | 36221.9 | 302.64 | 35919.26 | 4670 | 4670 | 116816.8163 | 11.6667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-21 | 10.507 | 0.26319 | 0.76667 | 8020 | 8530 | 8550 | 5164 | 8150 | 7693 | 117050.7027 | 15.5941 | 6230 | 6940 | 6940 | 0 | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 0 | 46107 | 45826.5 | 381.3 | 45445.2 | 6940 | 6940 | 116862.5864 | 12.0833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-22 | 10.507 | 0.26042 | 0.76736 | 8742 | 9490 | 9130 | 8990 | 8891 | 8442 | 117104.0735 | 15.5984 | 6420 | 7200 | 7200 | 0 | 30.195 | 46.4332 | 0.77069 | 3.0956 | 0 | 53685 | 53370.8 | 257.4 | 53113.4 | 7200 | 7200 | 116915.8931 | 12.1667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-23 | 10.507 | 0.25972 | 0.76597 | 7754 | 8430 | 8210 | 8030 | 8060 | 7550 | 117151.8103 | 15.6035 | 6080 | 6450 | 6350 | 0 | 30.2277 | 45.4561 | 0.88646 | 4.0239 | 0 | 48034 | 47736.8 | 305.52 | 47431.28 | 6400 | 6400 | 116963.5723 | 12.15
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-24 | 10.507 | 0.26042 | 0.76944 | 8640 | 9480 | 9200 | 8880 | 8784 | 8260 | 117204.7356 | 15.6086 | 6660 | 7200 | 7150 | 0 | 30.7169 | 47.3243 | 1.0548 | 4.043 | 0 | 53244 | 52925.3 | 305.76 | 52619.54 | 7175 | 7175 | 117016.4341 | 12.2167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-25 | 10.507 | 0.26528 | 0.76667 | 7962 | 8503 | 8341 | 8020 | 8130 | 7640 | 117253.0347 | 15.6137 | 6140 | 6510 | 6450 | 0 | 30.479 | 47.1594 | 0.89744 | 3.3385 | 0 | 48596 | 48299.1 | 308.7 | 47990.4 | 6480 | 6480 | 117064.6736 | 12.0333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-26 | 10.507 | 0.25625 | 0.76667 | 8730 | 9490 | 9420 | 9260 | 9122 | 8683 | 117307.3973 | 15.6189 | 6830 | 7600 | 7510 | 0 | 30.1302 | 47.6614 | 1.2327 | 4.8132 | 0 | 54705 | 54362.6 | 308.88 | 54053.72 | 7555 | 7555 | 117118.9704 | 12.25
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-27 | 10.507 | 0.25833 | 0.76389 | 7660 | 8302 | 8050 | 7940 | 8224 | 7731 | 117355.0318 | 15.6238 | 6070 | 6380 | 6380 | 0 | 30.2277 | 45.4561 | 0.88646 | 4.0239 | 0 | 47907 | 47634.5 | 296.58 | 47337.92 | 6380 | 6380 | 117166.5503 | 12.1333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-28 | 10.507 | 0.26042 | 0.75486 | 8650 | 9430 | 9140 | 9240 | 9082 | 8620 | 117408.9148 | 15.6288 | 6450 | 7200 | 7200 | 0 | 30.195 | 46.4332 | 0.77069 | 3.0956 | 3.45 | 54162 | 53883 | 298.08 | 53584.92 | 7200 | 7200 | 117220.3686 | 11.8667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-29 | 10.507 | 0.25486 | 0.76806 | 7980 | 8610 | 8541 | 8650 | 8423 | 7970 | 117458.8093 | 15.6342 | 6320 | 6740 | 6740 | 0 | 28.8325 | 45.3299 | 0.84028 | 4.5702 | 1.98 | 50174 | 49894.5 | 326.22 | 49568.28 | 6740 | 6740 | 117270.2043 | 12.3167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-30 | 10.507 | 0.25694 | 0.76597 | 8224 | 9020 | 8731 | 9010 | 8534 | 8300 | 117510.3341 | 15.6396 | 6390 | 6920 | 6920 | 0 | 29.0602 | 45.8714 | 1.0987 | 8.6629 | 0 | 51819 | 51524.8 | 321.72 | 51203.08 | 6920 | 6920 | 117321.6687 | 12.2167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-01 | 10.507 | 0.25694 | 0.77153 | 4980 | 5343 | 5060 | 5243 | 5250 | 5010 | 117541.0493 | 15.6446 | 3540 | 4110 | 4110 | 0 | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 0 | 30886 | 30715.2 | 301.14 | 30414.06 | 4110 | 4110 | 117352.3465 | 12.35
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-02 | 10.507 | 0.25694 | 0.76736 | 7950 | 8510 | 8290 | 8470 | 8490 | 7884 | 117590.3519 | 15.6497 | 6090 | 6630 | 6630 | 0 | 29.2157 | 45.438 | 0.72585 | 2.4936 | 0 | 49594 | 49302.6 | 303.9 | 48998.7 | 6630 | 6630 | 117401.5885 | 12.25
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-03 | 10.507 | 0.25625 | 0.77014 | 8600 | 9220 | 8970 | 9012 | 8980 | 8481 | 117643.3597 | 15.6553 | 6510 | 7110 | 7113 | 0 | 28.1139 | 44.2016 | 0.9761 | 3.9187 | 0 | 53263 | 53007.8 | 339.3 | 52668.5 | 7111.5 | 7111.5 | 117454.5298 | 12.3333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-04 | 10.507 | 0.25694 | 0.78056 | 8891 | 9560 | 9361 | 9471 | 9260 | 8774 | 117698.3752 | 15.6609 | 6850 | 7420 | 7450 | 0 | 29.436 | 45.0088 | 1.0626 | 4.7309 | 0 | 55317 | 55015.5 | 333.9 | 54681.6 | 7435 | 7435 | 117509.4785 | 12.5667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-05 | 10.507 | 0.25556 | 0.76389 | 9100 | 9803 | 9530 | 9760 | 9570 | 9000 | 117754.8421 | 15.6659 | 7050 | 7710 | 7650 | 0 | 30.0837 | 48.4744 | 0.81191 | 3.4706 | 0 | 56763 | 56466.9 | 302.4 | 56164.5 | 7680 | 7680 | 117565.8779 | 12.2
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-06 | 10.507 | 0.25625 | 0.77431 | 9800 | 10640 | 10010 | 10300 | 10094 | 9532 | 117814.8864 | 15.6709 | 7320 | 8090 | 8090 | 0 | 29.9635 | 46.6534 | 1.1117 | 4.0151 | 0 | 60376 | 60044.3 | 301.5 | 59742.8 | 8090 | 8090 | 117625.8493 | 12.4333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-07 | 10.507 | 0.25556 | 0.77083 | 9301 | 10081 | 9670 | 9854 | 9630 | 9080 | 117872.1875 | 15.676 | 7180 | 7650 | 7650 | 0 | 30.1719 | 46.9672 | 1.0444 | 3.5784 | 0 | 57616 | 57301.1 | 305.22 | 56995.88 | 7650 | 7650 | 117683.0804 | 12.3667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-08 | 10.507 | 0.25417 | 0.77153 | 9160 | 10032 | 9581 | 9762 | 9380 | 8820 | 117928.6176 | 15.6812 | 7120 | 7590 | 7590 | 0 | 29.0606 | 46.286 | 1.1257 | 4.0229 | 0 | 56735 | 56430.1 | 308.94 | 56121.16 | 7590 | 7590 | 117739.4425 | 12.4167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-09 | 10.507 | 0.25347 | 0.77361 | 8540 | 9290 | 8832 | 8852 | 8610 | 8171 | 117980.5724 | 15.6861 | 6700 | 6920 | 6880 | 0 | 29.1228 | 46.1707 | 0.85347 | 5.0674 | 0 | 52295 | 51954.8 | 297.54 | 51657.26 | 6900 | 6900 | 117791.3332 | 12.4833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-10 | 10.507 | 0.25208 | 0.77431 | 9780 | 10564 | 10073 | 10100 | 9930 | 9140 | 118039.862 | 15.691 | 7290 | 8080 | 8030 | 0 | 29.3381 | 47.275 | 1.0885 | 4.3083 | 0 | 59587 | 59289.6 | 289.08 | 59000.52 | 8055 | 8055 | 117850.5505 | 12.5333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-11 | 10.507 | 0.25347 | 0.77292 | 8991 | 10070 | 9841 | 9880 | 9780 | 8964 | 118097.0406 | 15.696 | 7310 | 7770 | 7680 | 0 | 29.4336 | 47.5887 | 0.77545 | 3.6446 | 0 | 57526 | 57178.6 | 304.98 | 56873.62 | 7725 | 7725 | 117907.66 | 12.4667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-12 | 10.507 | 0.25139 | 0.76181 | 8641 | 9370 | 9152 | 9140 | 8853 | 8380 | 118150.2714 | 15.701 | 6860 | 7490 | 7490 | 0 | 29.2109 | 45.9608 | 0.87807 | 3.8396 | 0 | 53536 | 53230.8 | 296.64 | 52934.16 | 7490 | 7490 | 117960.8263 | 12.25
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-13 | 10.507 | 0.25625 | 0.76319 | 9032 | 9752 | 9354 | 9360 | 9274 | 8911 | 118205.6071 | 15.7063 | 6740 | 7450 | 7400 | 0 | 27.805 | 44.9838 | 1.1785 | 5.2118 | 1.72 | 55683 | 55335.7 | 320.16 | 55015.54 | 7425 | 7425 | 118016.0937 | 12.1667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-14 | 10.507 | 0.25208 | 0.77222 | 8091 | 8810 | 8560 | 8660 | 8403 | 8060 | 118255.9112 | 15.7117 | 6200 | 6850 | 6750 | 0 | 28.8336 | 44.3876 | 0.8506 | 2.5289 | 1.02 | 50584 | 50304.1 | 322.56 | 49981.54 | 6800 | 6800 | 118066.3357 | 12.4833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-15 | 10.507 | 0.25347 | 0.76736 | 7753 | 8440 | 8311 | 8372 | 8180 | 7830 | 118304.4986 | 15.7168 | 6210 | 6510 | 6440 | 0 | 28.3453 | 44.0653 | 0.86462 | 3.7344 | 0 | 48886 | 48587.4 | 304.44 | 48282.96 | 6475 | 6475 | 118114.8616 | 12.3333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-16 | 10.507 | 0.25347 | 0.77153 | 8023 | 8782 | 8643 | 8653 | 8401 | 8170 | 118354.8319 | 15.722 | 6180 | 6860 | 6780 | 0 | 27.7906 | 43.4285 | 1.0359 | 5.8035 | 0 | 50672 | 50333.3 | 316.02 | 50017.28 | 6820 | 6820 | 118165.1416 | 12.4333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-17 | 10.507 | 0.2625 | 0.76111 | 4873 | 5240 | 5251 | 5240 | 5103 | 4850 | 118385.1933 | 15.7273 | 3770 | 3830 | 3830 | 0 | 25.9971 | 35.2061 | 0.98105 | 7.1985 | 2.24 | 30557 | 30361.4 | 316.38 | 30045.02 | 3830 | 3830 | 118195.4548 | 11.9667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-18 | 10.507 | 0.25903 | 0.77292 | 7091 | 8424 | 8420 | 8413 | 8262 | 7830 | 118433.3173 | 15.7326 | 6050 | 6370 | 6430 | 0 | 27.759 | 41.2443 | 1.1753 | 4.1536 | 0 | 48440 | 48124 | 320.16 | 47803.84 | 6400 | 6400 | 118243.5218 | 12.3333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-19 | 10.507 | 0.27222 | 0.76111 | 3680 | 3950 | 4031 | 3983 | 3960 | 3643 | 118456.2273 | 15.7382 | 2800 | 2690 | 2710 | 0 | 24.5407 | 30.8411 | 0.73105 | 3.1102 | 3.24 | 23247 | 22910 | 335.28 | 22574.72 | 2700 | 2700 | 118266.3984 | 11.7333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-20 | 10.507 | 0.28889 | 0.77153 | 4362 | 4641 | 4806 | 4760 | 4474 | 4291 | 118483.3349 | 15.744 | 3400 | 3380 | 3260 | 0 | 24.4541 | 32.8874 | 0.9356 | 5.0809 | 2.43 | 27334 | 27107.6 | 344.52 | 26763.08 | 3320 | 3320 | 118293.4682 | 11.5833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-21 | 10.507 | 0.25278 | 0.775 | 5010 | 5360 | 5422 | 5411 | 5180 | 4980 | 118514.4855 | 15.7493 | 3840 | 3910 | 3830 | 0 | 24.4997 | 32.5266 | 1.7049 | 8.8073 | 1.43 | 31363 | 31150.6 | 317.64 | 30832.96 | 3870 | 3870 | 118324.5757 | 12.5333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-22 | 10.507 | 0.25556 | 0.775 | 6942 | 7274 | 7250 | 7222 | 7000 | 6730 | 118556.7506 | 15.7543 | 5170 | 5400 | 5360 | 0 | 26.4095 | 37.0329 | 1.5431 | 6.5777 | 0 | 42418 | 42265.1 | 301.2 | 41963.9 | 5380 | 5380 | 118366.7862 | 12.4667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-23 | 10.507 | 0.25278 | 0.77569 | 6620 | 6810 | 6870 | 6800 | 6443 | 6440 | 118596.4771 | 15.7592 | 4282 | 5250 | 5250 | 0 | 25.4426 | 35.2243 | 2.3078 | 8.0038 | 1.21 | 39983 | 39726.5 | 297.66 | 39428.84 | 5250 | 5250 | 118406.4582 | 12.55
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-24 | 10.507 | 0.25278 | 0.76389 | 4030 | 4320 | 4290 | 1955 | 4190 | 4060 | 118619.1303 | 15.7644 | 3050 | 3040 | 2970 | 0 | 24.9328 | 31.1882 | 2.7855 | 9.2161 | 2.12 | 22845 | 22653.2 | 309.54 | 22343.66 | 3005 | 3005 | 11829.0783 | 12.2667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-25 | 10.507 | 0.25833 | 0.77222 | 4590 | 4380 | 4883 | 4344 | 4821 | 4640 | 118646.8875 | 15.77 | 3080 | 3180 | 3180 | 0 | 23.9943 | 30.1193 | 2.6118 | 8.8609 | 5.2 | 27658 | 27757.2 | 333.78 | 27423.42 | 3180 | 3180 | 118456.796 | 12.3333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-26 | 10.507 | 0.25694 | 0.77153 | 4620 | 5083 | 5130 | 5092 | 4990 | 4760 | 118676.2865 | 15.7755 | 3520 | 3480 | 3480 | 0 | 25.965 | 35.6713 | 0.92166 | 10.1554 | 2.1 | 29675 | 29399 | 334.5 | 29064.5 | 3480 | 3480 | 118486.1554 | 12.35
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-27 | 10.507 | 0.25694 | 0.77431 | 5150 | 5414 | 5460 | 5411 | 5362 | 5132 | 118707.9598 | 15.7804 | 3820 | 3830 | 3820 | 0 | 24.4997 | 32.5266 | 1.7049 | 8.8073 | 0.52 | 31929 | 31673.3 | 292.62 | 31380.68 | 3825 | 3825 | 118517.7861 | 12.4167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-28 | 10.507 | 0.25417 | 0.75486 | 4540 | 4770 | 4862 | 4830 | 4630 | 4442 | 118735.6287 | 15.787 | 3450 | 3340 | 3360 | 0 | 25.0635 | 31.196 | 1.7759 | 9.2261 | 0.21 | 28074 | 27668.9 | 394.98 | 27273.92 | 3350 | 3350 | 118545.4165 | 12.0167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-29 | 10.507 | 0.25347 | 0.77708 | 5094 | 5370 | 5461 | 5470 | 5260 | 5050 | 118767.0885 | 15.7906 | 3820 | 3750 | 3710 | 0 | 24.8504 | 32.0049 | 1.7221 | 6.348 | 0.19 | 31705 | 31459.8 | 217.8 | 31242 | 3730 | 3730 | 118576.8343 | 12.5667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-30 | 10.507 | 0.25139 | 0.76944 | 3930 | 4144 | 4223 | 4152 | 4081 | 3874 | 118791.2626 | 15.7966 | 3040 | 2850 | 2830 | 0 | 24.9062 | 31.002 | 1.1343 | 6.0709 | 0 | 24404 | 24174.1 | 357.72 | 23816.38 | 2840 | 2840 | 118600.9739 | 12.4333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-31 | 10.507 | 0.25347 | 0.77708 | 6630 | 7132 | 7072 | 6970 | 6810 | 6570 | 118832.1948 | 15.8009 | 5150 | 5190 | 5180 | 0 | 26.5776 | 37.2281 | 0.83761 | 4.3921 | 0 | 41184 | 40932.2 | 256.02 | 40676.18 | 5185 | 5185 | 118641.8536 | 12.5667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-01 | 10.507 | 0.25 | 0.77431 | 8764 | 9300 | 8953 | 8902 | 8663 | 8572 | 118885.0585 | 15.8063 | 6550 | 7050 | 6810 | 0 | 27.3767 | 41.1267 | 1.6266 | 6.4821 | 0 | 53154 | 52863.7 | 325.92 | 52537.78 | 6930 | 6930 | 118694.65 | 12.5833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-02 | 10.507 | 0.25208 | 0.77569 | 7630 | 8110 | 7970 | 7804 | 7671 | 7414 | 118931.3634 | 15.8111 | 5570 | 6030 | 6040 | 0 | 27.2883 | 39.0841 | 1.9193 | 5.6299 | 0 | 46599 | 46304.9 | 285.48 | 46019.42 | 6035 | 6035 | 118740.8962 | 12.5667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-03 | 10.507 | 0.25139 | 0.77431 | 6550 | 6800 | 6972 | 6780 | 6670 | 6422 | 118971.1531 | 15.8164 | 4890 | 5250 | 5030 | 0 | 25.605 | 36.1476 | 1.4758 | 6.5289 | 0 | 40194 | 39789.7 | 318.06 | 39471.64 | 5140 | 5140 | 118780.6318 | 12.55
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-04 | 10.507 | 0.24861 | 0.77431 | 8710 | 9490 | 9170 | 9034 | 8870 | 8620 | 119024.7053 | 15.8216 | 6580 | 7170 | 6840 | 0 | 27.1915 | 41.3755 | 0.88924 | 4.8114 | 0 | 53894 | 53552.2 | 314.58 | 53237.62 | 7005 | 7005 | 118834.1161 | 12.6167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-05 | 10.507 | 0.25 | 0.77431 | 8760 | 9661 | 9500 | 9230 | 8920 | 8840 | 119079.3555 | 15.8263 | 6700 | 7520 | 7250 | 0 | 27.7997 | 43.1336 | 0.7642 | 1.0214 | 0.98 | 54911 | 54650.2 | 284.76 | 54365.44 | 7385 | 7385 | 118888.6974 | 12.5833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-06 | 10.507 | 0.25069 | 0.77639 | 9050 | 10124 | 9770 | 9810 | 9254 | 9113 | 119136.1784 | 15.8308 | 6980 | 7810 | 7810 | 0 | 28.4327 | 45.7312 | 0.75488 | 0.95623 | 0 | 57121 | 56822.9 | 266.76 | 56556.14 | 7810 | 7810 | 118945.45 | 12.6167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-07 | 10.507 | 0.25069 | 0.77847 | 8972 | 10569 | 10080 | 10140 | 9772 | 9362 | 119194.5628 | 15.8359 | 7330 | 8040 | 8040 | 0 | 27.8549 | 45.2894 | 0.74587 | 0.88982 | 0 | 58895 | 58384.4 | 309.24 | 58075.16 | 8040 | 8040 | 119003.7605 | 12.6667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-08 | 10.507 | 0.24931 | 0.77431 | 9050 | 9940 | 9500 | 9310 | 9204 | 8740 | 119249.9942 | 15.8406 | 6980 | 7590 | 7480 | 0 | 28.6728 | 45.2306 | 0.72955 | 0.89025 | 0 | 55744 | 55431.4 | 281.46 | 55149.94 | 7535 | 7535 | 119059.1237 | 12.6
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-09 | 10.507 | 0.25069 | 0.71667 | 5570 | 6285 | 6084 | 5970 | 5781 | 5530 | 119284.9352 | 15.8459 | 4540 | 4550 | 4540 | 0 | 26.9089 | 38.0863 | 0.70516 | 0.81437 | 0.81 | 35220 | 34941 | 318.3 | 34622.7 | 4545 | 4545 | 119094.018 | 11.1833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-10 | 10.507 | 0.24931 | 0.77778 | 6940 | 7590 | 7400 | 7092 | 7050 | 6742 | 119328.0099 | 15.8512 | 5300 | 5680 | 5580 | 0 | 26.4095 | 37.0329 | 1.5431 | 6.5777 | 0 | 42814 | 43074.7 | 313.92 | 42760.78 | 5630 | 5630 | 119137.038 | 12.6833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-11 | 10.507 | 0.25417 | 0.74653 | 5660 | 6214 | 6071 | 5910 | 5900 | 5582 | 119363.1096 | 15.8561 | 4310 | 4440 | 4440 | 0 | 26.5317 | 37.1209 | 0.73589 | 7.87 | 0 | 35337 | 35099.7 | 296.88 | 34802.82 | 4440 | 4440 | 119172.0926 | 11.8167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-12 | 10.507 | 0.2625 | 0.77708 | 5800 | 6200 | 6121 | 5954 | 5913 | 5680 | 119398.4424 | 15.8617 | 4400 | 4570 | 4540 | 0 | 25.5925 | 35.2972 | 1.4968 | 6.8728 | 1.27 | 35668 | 35332.8 | 334.02 | 34998.78 | 4555 | 4555 | 119207.3791 | 12.35
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-13 | 10.507 | 0.26181 | 0.77569 | 5080 | 5582 | 5401 | 5252 | 5230 | 5034 | 119429.8757 | 15.8665 | 3850 | 3940 | 3940 | 0 | 24.8504 | 32.0049 | 1.7221 | 6.348 | 0 | 31579 | 31433.3 | 291.12 | 31142.18 | 3940 | 3940 | 119238.768 | 12.3333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-14 | 10.507 | 0.25069 | 0.74306 | 4820 | 5390 | 5334 | 5123 | 5124 | 4842 | 119460.2432 | 15.8719 | 3860 | 3850 | 3810 | 0 | 25.0924 | 33.2292 | 1.4089 | 5.8479 | 1.98 | 30633 | 30367.5 | 319.62 | 30047.88 | 3830 | 3830 | 119269.0935 | 11.8167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-15 | 10.507 | 0.25417 | 0.77778 | 4080 | 4470 | 4370 | 4210 | 4200 | 3981 | 119485.2691 | 15.8767 | 3100 | 3010 | 2990 | 0 | 23.9379 | 28.828 | 2.9794 | 8.7773 | 1.75 | 25311 | 25025.9 | 289.14 | 24736.76 | 3000 | 3000 | 119294.0843 | 12.5667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-16 | 10.507 | 0.25347 | 0.77361 | 5490 | 5894 | 5784 | 5643 | 5591 | 5360 | 119518.8028 | 15.8817 | 4110 | 4250 | 4260 | 0 | 24.539 | 31.5177 | 2.6537 | 10.3186 | 0 | 33762 | 33533.7 | 301.74 | 33231.96 | 4255 | 4255 | 119327.5719 | 12.4833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-17 | 10.507 | 0.25764 | 0.77778 | 4714 | 5060 | 5040 | 4960 | 4900 | 4662 | 119547.8783 | 15.8867 | 3620 | 3550 | 3530 | 0 | 24.5281 | 31.0709 | 1.4826 | 6.9411 | 0 | 29336 | 29075.5 | 301.14 | 28774.36 | 3540 | 3540 | 119356.6076 | 12.4833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-18 | 10.507 | 0.25417 | 0.77639 | 5543 | 6090 | 5883 | 5713 | 5740 | 5380 | 119581.9831 | 15.8917 | 4150 | 4230 | 4230 | 0 | 25.3852 | 34.0119 | 0.74291 | 3.351 | 0 | 34349 | 34104.8 | 295.98 | 33808.82 | 4230 | 4230 | 119390.6666 | 12.5333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-19 | 10.507 | 0.25417 | 0.77847 | 6663 | 7320 | 7040 | 6393 | 6823 | 6420 | 119622.4447 | 15.8966 | 4990 | 5130 | 5070 | 0 | 26.0367 | 35.6802 | 0.64889 | 2.4967 | 0 | 40659 | 40461.6 | 293.46 | 40168.14 | 5100 | 5100 | 119431.0748 | 12.5833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-20 | 10.507 | 0.25208 | 0.77986 | 7710 | 8540 | 8120 | 8040 | 7810 | 7540 | 119669.5171 | 15.9014 | 5700 | 6120 | 6120 | 0 | 26.5611 | 38.1114 | 1.2775 | 6.5962 | 0 | 47760 | 47072.4 | 291.36 | 46781.04 | 6120 | 6120 | 119478.0818 | 12.6667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-21 | 10.507 | 0.25347 | 0.77778 | 7630 | 8350 | 7940 | 7761 | 7620 | 7281 | 119715.8118 | 15.9062 | 5630 | 5950 | 5880 | 0 | 26.6403 | 37.3416 | 2.2367 | 6.7845 | 0 | 46582 | 46294.7 | 290.22 | 46004.48 | 5915 | 5915 | 119524.3192 | 12.5833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-22 | 10.507 | 0.25278 | 0.77847 | 1170 | 1310 | 1243 | 1200 | 1201 | 1140 | 119722.9822 | 15.9111 | 650 | 750 | 750 | 0 | 25.1226 | 32.9897 | 1.894 | 7.725 | 0 | 7264 | 7170.4 | 293.4 | 6877 | 750 | 750 | 119531.4777 | 12.6167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-23 | 10.507 | 0.26042 | 0.775 | 6350 | 6973 | 6753 | 6640 | 6480 | 6190 | 119762.2283 | 15.9162 | 4830 | 4830 | 4830 | 0 | 25.3778 | 33.8383 | 2.7888 | 8.3454 | 0 | 39386 | 39246.1 | 301.26 | 38944.84 | 4830 | 4830 | 119570.6723 | 12.35
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-24 | 10.507 | 0.25625 | 0.78056 | 4790 | 5203 | 5070 | 5010 | 4903 | 4632 | 119791.5925 | 15.9213 | 3640 | 3560 | 3560 | 0 | 24.8022 | 31.1665 | 2.3958 | 8.3188 | 0.51 | 29608 | 29364.2 | 308.82 | 29055.38 | 3560 | 3560 | 119599.9961 | 12.5833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-25 | 10.507 | 0.25694 | 0.77778 | 3992 | 4174 | 4190 | 4122 | 3950 | 3787 | 119815.5272 | 15.9258 | 2970 | 2870 | 2870 | 0 | 23.9379 | 28.828 | 2.9794 | 8.7773 | 0 | 24215 | 23934.7 | 271.5 | 23663.2 | 2870 | 2870 | 119623.8965 | 12.5
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-26 | 10.507 | 0.25486 | 0.78264 | 5560 | 6120 | 5970 | 5732 | 5710 | 5390 | 119849.7359 | 15.9307 | 4240 | 4320 | 4320 | 0 | 25.9955 | 34.2471 | 2.3294 | 6.7935 | 0 | 34482 | 34208.7 | 295.02 | 33913.68 | 4320 | 4320 | 119658.0609 | 12.6667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-27 | 10.507 | 0.25347 | 0.77431 | 5071 | 5532 | 5410 | 5320 | 5230 | 4910 | 119880.9569 | 15.9356 | 3850 | 3935 | 3935 | 0 | 24.8504 | 32.0049 | 1.7221 | 6.348 | 0 | 31473 | 31221 | 291.18 | 30929.82 | 3935 | 3935 | 119689.2426 | 12.5
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-28 | 10.507 | 0.25833 | 0.78264 | 5640 | 6302 | 6130 | 6103 | 5894 | 5591 | 119916.3781 | 15.941 | 4440 | 4530 | 4490 | 0 | 25.6635 | 34.8133 | 2.1412 | 6.8482 | 0 | 35660 | 35421.2 | 324.18 | 35097.02 | 4510 | 4510 | 119724.6182 | 12.5833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-29 | 10.507 | 0.25625 | 0.77986 | 7650 | 8270 | 8023 | 8080 | 7800 | 7461 | 119963.4172 | 15.9459 | 5590 | 6130 | 6130 | 0 | 26.469 | 37.6205 | 2.6835 | 6.9793 | 0 | 47284 | 47039.1 | 295.56 | 46743.54 | 6130 | 6130 | 119771.6001 | 12.5667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-30 | 10.507 | 0.25764 | 0.78264 | 7680 | 8240 | 8061 | 8023 | 7762 | 7394 | 120010.196 | 15.9506 | 5730 | 6100 | 6100 | 0 | 26.1369 | 36.905 | 2.8151 | 8.1669 | 0 | 47160 | 46778.8 | 279.84 | 46498.96 | 6100 | 6100 | 119818.3237 | 12.6
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-07-01 | 10.507 | 0.25625 | 0.77847 | 3680 | 4000 | 3950 | 3922 | 3770 | 3590 | 120032.9521 | 15.9557 | 2810 | 2730 | 2730 | 0 | 24.5237 | 29.5575 | 1.9007 | 6.3871 | 0 | 22912 | 22756.1 | 308.7 | 22447.4 | 2730 | 2730 | 119841.0467 | 12.5333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-02 | 10.507 | 0.25625 | 0.77986 | 5420 | 5850 | 5732 | 5722 | 5503 | 5200 | 120066.1289 | 15.9611 | 4160 | 4180 | 4150 | 0 | 25.305 | 32.8784 | 2.7888 | 8.3454 | 0 | 33427 | 33176.8 | 322.56 | 32854.24 | 4165 | 4165 | 119874.1808 | 12.5667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-03 | 10.507 | 0.26181 | 0.77569 | 4340 | 4690 | 4610 | 4601 | 4423 | 4160 | 120092.7619 | 15.9666 | 3280 | 3280 | 3180 | 0 | 24.0753 | 30.4552 | 2.0251 | 6.7358 | 2.54 | 26824 | 26633 | 326.94 | 26306.06 | 3230 | 3230 | 119900.7768 | 12.3333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-04 | 10.507 | 0.25486 | 0.77708 | 6760 | 7273 | 7150 | 7201 | 6770 | 6502 | 120134.178 | 15.9715 | 5620 | 5420 | 5420 | 0 | 26.1687 | 36.736 | 2.5883 | 8.6863 | 0.75 | 41656 | 41416.1 | 296.28 | 41119.82 | 5420 | 5420 | 119942.1462 | 12.5333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-05 | 10.507 | 0.25694 | 0.77986 | 3550 | 3890 | 3798 | 3796 | 3686 | 3468 | 120156.1581 | 15.9761 | 2710 | 2630 | 2630 | 0 | 23.9478 | 28.5037 | 1.8307 | 5.4042 | 0.762 | 22188 | 21980.1 | 277.98 | 21702.12 | 2630 | 2630 | 119964.0942 | 12.55
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-06 | 10.507 | 0.25486 | 0.78125 | 5027 | 5477 | 5334 | 5342 | 5165 | 4829 | 120187.124 | 15.9809 | 3760 | 3820 | 3810 | 0 | 24.2217 | 47.3601 | 2.4316 | 7.1164 | 2.032 | 31174 | 30965.9 | 286.02 | 30679.88 | 3815 | 3815 | 119995.0177 | 12.6333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-07 | 10.507 | 0.25694 | 0.78333 | 5672 | 5890 | 6022 | 5890 | 5800 | 5502 | 120221.7315 | 15.9857 | 4440 | 4530 | 4490 | 0 | 25.5325 | 34.3461 | 2.6348 | 8.1784 | 0 | 34776 | 34607.5 | 287.1 | 34320.4 | 4510 | 4510 | 120029.5803 | 12.6333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-08 | 10.507 | 0.25486 | 0.77708 | 6847 | 7400 | 7215 | 7408 | 6848 | 6608 | 120263.4793 | 15.9904 | 5030 | 5490 | 5490 | 0 | 26.1687 | 36.736 | 2.5883 | 8.6863 | 0 | 42326 | 41747.8 | 281.88 | 41465.92 | 5490 | 5490 | 120071.2751 | 12.5333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-09 | 10.507 | 0.25278 | 0.77778 | 6551 | 7034 | 7015 | 6784 | 6568 | 6314 | 120303.5076 | 15.9936 | 5020 | 5380 | 5290 | 0 | 19.74 | 17.4871 | 0.63784 | 7.0452 | 0 | 40266 | 40028.3 | 191.46 | 39836.84 | 5335 | 5335 | 120111.2552 | 12.6
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-10 | 10.507 | 0.25625 | 0.75764 | 4259 | 4521 | 4593 | 4500 | 4385 | 4238 | 120329.8737 | 15.9986 | 3300 | 3350 | 3300 | 0 | 24.0753 | 30.4552 | 2.0251 | 6.7358 | 1.01 | 26496 | 26366.1 | 304.14 | 26061.96 | 3325 | 3325 | 120137.5851 | 12.0333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-11 | 10.507 | 0.25694 | 0.77153 | 6563 | 7050 | 7110 | 6920 | 6701 | 6480 | 120370.3726 | 16.004 | 5100 | 5300 | 5300 | 0 | 26.0367 | 35.6802 | 0.64889 | 2.4967 | 0 | 40824 | 40498.9 | 321.9 | 40177 | 5300 | 5300 | 120178.0349 | 12.35
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-12 | 10.507 | 0.25486 | 0.78333 | 5661 | 6221 | 6072 | 5850 | 5710 | 5531 | 120405.1456 | 16.0091 | 4360 | 4480 | 4410 | 0 | 25.5618 | 34.0561 | 1.6255 | 6.257 | 0.98 | 35045 | 34773 | 307.5 | 34465.5 | 4445 | 4445 | 120212.7608 | 12.6833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-13 | 10.507 | 0.25972 | 0.77778 | 5530 | 6140 | 6060 | 5970 | 5710 | 5420 | 120439.6946 | 16.0144 | 4280 | 4490 | 4360 | 0 | 25.6987 | 34.7175 | 1.49 | 5.9534 | 0.254 | 34830 | 34549 | 315.6 | 34233.4 | 4425 | 4425 | 120247.2641 | 12.4333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-14 | 10.507 | 0.25625 | 0.77986 | 5820 | 6640 | 6520 | 6450 | 6080 | 5800 | 120476.8282 | 16.0193 | 4670 | 4890 | 4850 | 0 | 25.3089 | 34.5544 | 2.4242 | 7.6105 | 0 | 37310 | 37133.6 | 297.12 | 36836.48 | 4870 | 4870 | 120284.3491 | 12.5667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-15 | 10.507 | 0.25972 | 0.78264 | 4587 | 4959 | 4902 | 4875 | 4625 | 4332 | 120504.8802 | 16.0246 | 3520 | 3460 | 3420 | 0 | 25.1889 | 31.752 | 1.4626 | 4.9563 | 0 | 28280 | 28052 | 315.54 | 27736.46 | 3440 | 3440 | 120312.3626 | 12.55
Formulas:
Days = DAY(EOMONTH(Raw_Data[[#This Row],[Month Year]],0))

## Inv_SY
[9 empty] | 1669.29 | 1833.3 | 1785.84 | 1785.42 | 1763.16 | 1669.29
Finacial Year | Start Month | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Plant DC Capcity (MW) | IC1_Inv1 | IC1_Inv2 | IC1_Inv3 | IC1_Inv4 | IC2_Inv1 | IC2_Inv2 | Avg. SY | Max. SY
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-08-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-01-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-03-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 10.507 | 5.2837 | 5.243 | 5.1404 | 5.108 | 5.1453 | 5.0507 | 5.1619 | 5.2837
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 10.507 | 5.1279 | 5.2637 | 5.1236 | 5.0761 | 5.1328 | 5.0441 | 5.1281 | 5.2637
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 10.507 | 4.7583 | 4.751 | 4.5754 | 4.632 | 4.6678 | 4.7146 | 4.6832 | 4.7583
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-01 | 10.507 | 3.9178 | 3.8586 | 3.8021 | 3.8837 | 3.8471 | 3.8106 | 3.8533 | 3.9178
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 10.507 | 4.5049 | 4.4963 | 4.4013 | 4.4863 | 4.4352 | 4.451 | 4.4625 | 4.5049
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-03 | 10.507 | 2.8994 | 2.9673 | 2.9286 | 3.0027 | 2.7848 | 2.9234 | 2.9177 | 3.0027
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 10.507 | 5.322 | 5.2692 | 5.2356 | 3.4115 | 4.974 | 5.0566 | 4.8782 | 5.322
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 10.507 | 4.5888 | 4.5721 | 4.4758 | 1.9155 | 4.4295 | 4.451 | 4.0721 | 4.5888
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 10.507 | 5.1339 | 5.2005 | 5.1197 | 2.8626 | 5.2015 | 5.1782 | 4.7827 | 5.2015
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-07 | 10.507 | 5.4694 | 5.3303 | 5.23 | 3.8299 | 5.316 | 5.2603 | 5.0727 | 5.4694
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-08 | 10.507 | 4.7565 | 4.7745 | 4.7507 | 4.7328 | 4.7018 | 4.6547 | 4.7285 | 4.7745
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-09 | 10.507 | 4.9901 | 5.0837 | 5.0452 | 5.1204 | 4.9701 | 4.9302 | 5.0233 | 5.1204
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-10 | 10.507 | 4.7403 | 4.631 | 4.6981 | 4.6622 | 4.611 | 4.5648 | 4.6512 | 4.7403
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-11 | 10.507 | 5.0698 | 5.1781 | 5.2916 | 5.2425 | 5.037 | 5.092 | 5.1518 | 5.2916
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-12 | 10.507 | 4.9746 | 4.9746 | 5.052 | 5.0408 | 4.8889 | 4.7937 | 4.9541 | 5.052
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-13 | 10.507 | 5.2118 | 5.1503 | 5.2306 | 5.1663 | 5.1062 | 5.0213 | 5.1477 | 5.2306
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-14 | 10.507 | 4.4168 | 4.463 | 4.5637 | 4.4936 | 4.4239 | 4.3611 | 4.4537 | 4.5637
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-15 | 10.507 | 5.6491 | 5.3799 | 5.5884 | 1.8774 | 5.4675 | 5.3328 | 4.8825 | 5.6491
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-16 | 10.507 | 4.8823 | 4.7041 | 4.8459 | 4.7272 | 4.8016 | 4.7865 | 4.7913 | 4.8823
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-17 | 10.507 | 5.1279 | 5.4514 | 5.4932 | 5.4564 | 5.4107 | 5.3436 | 5.3805 | 5.4932
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-18 | 10.507 | 4.7385 | 4.8121 | 4.8157 | 4.9344 | 4.602 | 4.681 | 4.7639 | 4.9344
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-19 | 10.507 | 4.9782 | 4.8601 | 4.9338 | 4.9535 | 4.906 | 4.8248 | 4.9094 | 4.9782
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-20 | 10.507 | 3.5296 | 3.4222 | 3.5334 | 3.5745 | 3.3888 | 3.4026 | 3.4752 | 3.5745
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-21 | 10.507 | 4.8044 | 4.6528 | 4.7877 | 2.8923 | 4.6224 | 4.6085 | 4.3947 | 4.8044
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-22 | 10.507 | 5.237 | 5.1765 | 5.1124 | 5.0352 | 5.0427 | 5.0572 | 5.1102 | 5.237
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-23 | 10.507 | 4.6451 | 4.5983 | 4.5973 | 4.4975 | 4.5713 | 4.5229 | 4.5721 | 4.6451
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-24 | 10.507 | 5.1759 | 5.171 | 5.1516 | 4.9736 | 4.982 | 4.9482 | 5.067 | 5.1759
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-25 | 10.507 | 4.7697 | 4.6381 | 4.6706 | 4.4919 | 4.611 | 4.5768 | 4.6264 | 4.7697
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-26 | 10.507 | 5.2298 | 5.1765 | 5.2748 | 5.1865 | 5.1737 | 5.2016 | 5.2071 | 5.2748
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-27 | 10.507 | 4.5888 | 4.5284 | 4.5077 | 4.4471 | 4.6644 | 4.6313 | 4.5613 | 4.6644
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-28 | 10.507 | 5.1818 | 5.1437 | 5.118 | 5.1753 | 5.151 | 5.1639 | 5.1556 | 5.1818
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-29 | 10.507 | 4.7805 | 4.6964 | 4.7826 | 4.8448 | 4.7772 | 4.7745 | 4.776 | 4.8448
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-30 | 10.507 | 4.9266 | 4.9201 | 4.889 | 5.0464 | 4.8402 | 4.9722 | 4.9324 | 5.0464
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-01 | 10.507 | 2.9833 | 2.9144 | 2.8334 | 2.9366 | 2.9776 | 3.0013 | 2.9411 | 3.0013
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-02 | 10.507 | 4.7625 | 4.6419 | 4.6421 | 4.744 | 4.8152 | 4.723 | 4.7214 | 4.8152
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-03 | 10.507 | 5.1519 | 5.0292 | 5.0228 | 5.0476 | 5.0931 | 5.0806 | 5.0709 | 5.1519
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-04 | 10.507 | 5.3262 | 5.2146 | 5.2418 | 5.3046 | 5.2519 | 5.2561 | 5.2659 | 5.3262
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-05 | 10.507 | 5.4514 | 5.3472 | 5.3364 | 5.4665 | 5.4278 | 5.3915 | 5.4035 | 5.4665
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-06 | 10.507 | 5.8708 | 5.8037 | 5.6052 | 5.769 | 5.7249 | 5.7102 | 5.7473 | 5.8708
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-07 | 10.507 | 5.5718 | 5.4988 | 5.4148 | 5.5191 | 5.4618 | 5.4394 | 5.4843 | 5.5718
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-08 | 10.507 | 5.4874 | 5.4721 | 5.365 | 5.4676 | 5.32 | 5.2837 | 5.3993 | 5.4874
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-09 | 10.507 | 5.1159 | 5.0674 | 4.9456 | 4.9579 | 4.8833 | 4.8949 | 4.9775 | 5.1159
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-10 | 10.507 | 5.8588 | 5.7623 | 5.6405 | 5.6569 | 5.6319 | 5.4754 | 5.671 | 5.8588
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-11 | 10.507 | 5.3861 | 5.4928 | 5.5106 | 5.5337 | 5.5469 | 5.3699 | 5.4733 | 5.5469
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-12 | 10.507 | 5.1765 | 5.111 | 5.1248 | 5.1192 | 5.0211 | 5.0201 | 5.0954 | 5.1765
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-13 | 10.507 | 5.4107 | 5.3194 | 5.2379 | 5.2425 | 5.2599 | 5.3382 | 5.3014 | 5.4107
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-14 | 10.507 | 4.847 | 4.8055 | 4.7933 | 4.8504 | 4.7659 | 4.8284 | 4.8151 | 4.8504
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-15 | 10.507 | 4.6445 | 4.6037 | 4.6538 | 4.6891 | 4.6394 | 4.6906 | 4.6535 | 4.6906
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-16 | 10.507 | 4.8062 | 4.7903 | 4.8397 | 4.8465 | 4.7647 | 4.8943 | 4.8236 | 4.8943
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-17 | 10.507 | 2.9192 | 2.8582 | 2.9404 | 2.9349 | 2.8942 | 2.9054 | 2.9087 | 2.9404
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-18 | 10.507 | 4.2479 | 4.595 | 4.7149 | 4.7121 | 4.6859 | 4.6906 | 4.6077 | 4.7149
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-19 | 10.507 | 2.2045 | 2.1546 | 2.2572 | 2.2308 | 2.246 | 2.1824 | 2.2126 | 2.2572
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-20 | 10.507 | 2.6131 | 2.5315 | 2.6912 | 2.666 | 2.5375 | 2.5706 | 2.6016 | 2.6912
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-21 | 10.507 | 3.0013 | 2.9237 | 3.0361 | 3.0307 | 2.9379 | 2.9833 | 2.9855 | 3.0361
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-22 | 10.507 | 4.1587 | 3.9677 | 4.0597 | 4.045 | 3.9701 | 4.0317 | 4.0388 | 4.1587
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-23 | 10.507 | 3.9658 | 3.7146 | 3.8469 | 3.8086 | 3.6542 | 3.8579 | 3.808 | 3.9658
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-24 | 10.507 | 2.4142 | 2.3564 | 2.4022 | 1.095 | 2.3764 | 2.4322 | 2.1794 | 2.4322
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-25 | 10.507 | 2.7497 | 2.3891 | 2.7343 | 2.433 | 2.7343 | 2.7796 | 2.6367 | 2.7796
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-26 | 10.507 | 2.7676 | 2.7726 | 2.8726 | 2.852 | 2.8301 | 2.8515 | 2.8244 | 2.8726
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-27 | 10.507 | 3.0851 | 2.9531 | 3.0574 | 3.0307 | 3.0411 | 3.0744 | 3.0403 | 3.0851
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-28 | 10.507 | 2.7197 | 2.6019 | 2.7225 | 2.7052 | 2.626 | 2.661 | 2.6727 | 2.7225
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-29 | 10.507 | 3.0516 | 2.9291 | 3.0579 | 3.0637 | 2.9833 | 3.0252 | 3.0185 | 3.0637
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-30 | 10.507 | 2.3543 | 2.2604 | 2.3647 | 2.3255 | 2.3146 | 2.3207 | 2.3234 | 2.3647
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-31 | 10.507 | 3.9717 | 3.8903 | 3.96 | 3.9038 | 3.8624 | 3.9358 | 3.9207 | 3.9717
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-01 | 10.507 | 5.2501 | 5.0728 | 5.0133 | 4.9859 | 4.9133 | 5.1351 | 5.0618 | 5.2501
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-02 | 10.507 | 4.5708 | 4.4237 | 4.4629 | 4.371 | 4.3507 | 4.4414 | 4.4367 | 4.5708
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-03 | 10.507 | 3.9238 | 3.7092 | 3.904 | 3.7974 | 3.783 | 3.8471 | 3.8274 | 3.9238
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-04 | 10.507 | 5.2178 | 5.1765 | 5.1348 | 5.0599 | 5.0307 | 5.1639 | 5.1306 | 5.2178
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-05 | 10.507 | 5.2477 | 5.2697 | 5.3196 | 5.1697 | 5.0591 | 5.2957 | 5.2269 | 5.3196
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-06 | 10.507 | 5.4215 | 5.5223 | 5.4708 | 5.4945 | 5.2485 | 5.4592 | 5.4361 | 5.5223
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-07 | 10.507 | 5.3747 | 5.765 | 5.6444 | 5.6793 | 5.5423 | 5.6084 | 5.6024 | 5.765
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-08 | 10.507 | 5.4215 | 5.4219 | 5.3196 | 5.2145 | 5.2202 | 5.2358 | 5.3056 | 5.4219
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-09 | 10.507 | 3.3367 | 3.4282 | 3.4068 | 3.3438 | 3.2788 | 3.3128 | 3.3512 | 3.4282
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-10 | 10.507 | 4.1575 | 4.1401 | 4.1437 | 3.9722 | 3.9985 | 4.0388 | 4.0751 | 4.1575
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-11 | 10.507 | 3.3907 | 3.3895 | 3.3995 | 3.3101 | 3.3463 | 3.3439 | 3.3633 | 3.3995
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-12 | 10.507 | 3.4745 | 3.3819 | 3.4275 | 3.3348 | 3.3536 | 3.4026 | 3.3958 | 3.4745
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-13 | 10.507 | 3.0432 | 3.0448 | 3.0243 | 2.9416 | 2.9663 | 3.0157 | 3.006 | 3.0448
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-14 | 10.507 | 2.8875 | 2.9401 | 2.9868 | 2.8694 | 2.9061 | 2.9006 | 2.9151 | 2.9868
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-15 | 10.507 | 2.4442 | 2.4382 | 2.447 | 2.358 | 2.3821 | 2.3848 | 2.4091 | 2.447
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-16 | 10.507 | 3.2888 | 3.215 | 3.2388 | 3.1606 | 3.171 | 3.2109 | 3.2142 | 3.2888
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-17 | 10.507 | 2.824 | 2.7601 | 2.8222 | 2.7781 | 2.7791 | 2.7928 | 2.7927 | 2.824
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-18 | 10.507 | 3.3206 | 3.3219 | 3.2942 | 3.1998 | 3.2555 | 3.2229 | 3.2692 | 3.3219
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-19 | 10.507 | 3.9915 | 3.9928 | 3.9421 | 3.5807 | 3.8698 | 3.8459 | 3.8705 | 3.9928
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-20 | 10.507 | 4.6187 | 4.6583 | 4.5469 | 4.5031 | 4.4295 | 4.5169 | 4.5456 | 4.6583
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-21 | 10.507 | 4.5708 | 4.5546 | 4.4461 | 4.3469 | 4.3218 | 4.3617 | 4.4337 | 4.5708
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-22 | 10.507 | 0.7009 | 0.71456 | 0.69603 | 0.67211 | 0.68116 | 0.68293 | 0.69128 | 0.71456
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-23 | 10.507 | 3.804 | 3.8035 | 3.7814 | 3.719 | 3.6752 | 3.7082 | 3.7486 | 3.804
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-24 | 10.507 | 2.8695 | 2.8381 | 2.839 | 2.8061 | 2.7808 | 2.7748 | 2.818 | 2.8695
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-25 | 10.507 | 2.3914 | 2.2768 | 2.3462 | 2.3087 | 2.2403 | 2.2686 | 2.3053 | 2.3914
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-26 | 10.507 | 3.3308 | 3.3382 | 3.343 | 3.2104 | 3.2385 | 3.2289 | 3.2816 | 3.343
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-27 | 10.507 | 3.0378 | 3.0175 | 3.0294 | 2.9797 | 2.9663 | 2.9414 | 2.9953 | 3.0378
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-28 | 10.507 | 3.3787 | 3.4375 | 3.4326 | 3.4182 | 3.3429 | 3.3493 | 3.3932 | 3.4375
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-29 | 10.507 | 4.5828 | 4.511 | 4.4926 | 4.5255 | 4.4239 | 4.4696 | 4.5009 | 4.5828
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-30 | 10.507 | 4.6008 | 4.4946 | 4.5138 | 4.4936 | 4.4023 | 4.4294 | 4.4891 | 4.6008
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-01 | 10.507 | 2.2045 | 2.1819 | 2.2118 | 2.1967 | 2.1382 | 2.1506 | 2.1806 | 2.2118
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-02 | 10.507 | 3.2469 | 3.191 | 3.2097 | 3.2048 | 3.1211 | 3.1151 | 3.1814 | 3.2469
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-03 | 10.507 | 2.5999 | 2.5582 | 2.5814 | 2.577 | 2.5086 | 2.4921 | 2.5529 | 2.5999
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-04 | 10.507 | 4.0496 | 3.9672 | 4.0037 | 4.0332 | 3.8397 | 3.8951 | 3.9647 | 4.0496
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-05 | 10.507 | 3.0115 | 2.9875 | 2.9868 | 2.992 | 2.9294 | 2.8928 | 2.9667 | 3.0115
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-06 | 10.507 | 3.3979 | 3.2128 | 3.3721 | 3.2989 | 3.2895 | 3.296 | 3.3112 | 3.3979
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-07 | 10.507 | 4.1017 | 4.0364 | 4.0401 | 4.1492 | 3.8839 | 3.9586 | 4.0283 | 4.1492
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-08 | 10.507 | 3.9244 | 3.8368 | 3.9281 | 3.7997 | 3.7251 | 3.7824 | 3.8328 | 3.9281
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-09 | 10.507 | 2.5514 | 2.466 | 2.5719 | 2.5204 | 2.487 | 2.5388 | 2.5226 | 2.5719
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-10 | 10.507 | 3.9316 | 3.8455 | 3.9813 | 3.8758 | 3.8006 | 3.8819 | 3.8861 | 3.9813
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-11 | 10.507 | 3.3913 | 3.3933 | 3.4001 | 3.2765 | 3.2385 | 3.3134 | 3.3355 | 3.4001
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-12 | 10.507 | 3.3128 | 3.3492 | 3.3934 | 3.3438 | 3.2385 | 3.2469 | 3.3141 | 3.3934
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-13 | 10.507 | 3.4865 | 3.6219 | 3.6509 | 3.6126 | 3.4484 | 3.4745 | 3.5491 | 3.6509
[6 empty] | 31 | 2025-07-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Formulas:
Days = DAY(EOMONTH([Month Year],0))
Date = [Date, row above]+1

## Inv_SY_Dev
Finacial Year | Start Month | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Plant DC Capcity (MW) | IC1_Inv1 WRT Avg. | IC1_Inv2 wrt Avg. | IC1_Inv3 wrt Avg. | IC1_Inv4 wrt Avg. | IC2_Inv1 wrt Avg. | IC2_Inv2 wrt Avg. | IC1_Inv1 wrt Max. | IC1_Inv2 wrt Max. | IC1_Inv3 wrt Max. | IC1_Inv4 wrt Max. | IC2_Inv1 wrt Max. | IC2_Inv2 wrt Max.
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-31 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-31 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-31 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-31 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-31 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-01 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-02 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-03 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-04 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-05 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-06 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-07 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-08 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-09 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-10 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-11 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-12 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-13 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-14 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-17 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-18 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-19 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-20 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-21 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-22 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-23 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-24 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-25 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-26 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-27 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-29 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-30 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-31 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-01 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-02 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-03 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-04 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-06 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-07 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-08 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-10 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-11 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-12 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-13 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-14 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-15 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-16 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-18 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-19 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-20 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-21 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-22 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-23 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-24 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-25 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-26 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-27 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-28 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-01 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-02 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-03 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-05 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-06 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-07 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-08 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-09 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-10 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-11 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-12 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-13 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-14 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-15 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-16 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-17 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-18 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-19 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-20 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-21 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-22 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-23 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-24 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-25 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-26 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-27 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-28 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-29 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-30 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-31 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-01 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-02 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-03 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-04 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-05 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-06 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-07 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-08 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-09 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-10 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-11 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-12 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-13 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-14 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-15 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-16 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-17 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-18 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-19 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-20 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-21 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-22 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-23 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-24 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-25 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-26 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-27 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-28 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-29 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-30 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-01 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-02 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-03 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-04 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-05 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-06 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-07 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-08 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-09 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-10 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-11 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-12 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-13 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-14 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-15 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-16 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-17 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-18 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-19 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-20 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-21 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-22 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-23 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-24 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-25 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-26 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-27 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-28 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-29 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-30 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-31 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-01 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-02 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-03 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-04 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-05 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-06 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-07 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-08 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-09 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-10 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-11 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-12 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-13 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-14 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-15 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-16 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-17 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-18 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-19 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-20 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-21 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-22 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-23 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-24 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-25 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-26 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-27 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-28 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-29 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-30 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-01 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-02 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-03 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-04 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-05 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-06 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-07 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-08 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-09 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-10 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-11 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-12 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-13 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-14 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-15 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-16 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-17 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-18 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-19 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-20 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-21 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-22 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-23 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-24 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-25 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-26 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-27 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-28 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-29 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-30 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-31 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-01 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-02 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-03 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-04 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-05 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-06 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-07 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-08 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-09 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-10 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-11 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-12 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-13 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-14 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-15 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-16 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-17 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-18 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-19 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-20 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-21 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-22 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-23 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-24 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-25 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-26 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-27 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-28 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-29 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-30 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-31 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-01 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-02 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-03 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-04 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-05 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-06 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-07 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-08 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-09 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-10 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-11 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-12 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-13 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-14 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-15 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-16 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-17 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-18 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-19 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-20 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-21 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-22 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-23 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-24 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-25 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-26 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-27 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-28 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-29 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-30 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-07 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-08 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-09 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-11 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-12 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-13 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-14 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-15 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-19 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-20 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-21 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-22 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-24 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-25 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-26 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-27 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-28 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-29 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-31 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-01 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-02 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-03 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-04 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-05 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-06 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-07 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-08 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-09 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-10 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-11 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-12 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-13 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-14 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-15 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-16 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-17 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-18 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-19 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-20 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-21 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-22 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-23 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-24 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-25 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-26 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-27 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-28 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-29 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-30 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-01 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-02 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-03 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-04 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-05 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-06 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-07 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-08 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-09 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-10 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-11 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-12 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-13 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-14 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-16 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-17 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-18 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-19 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-20 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-21 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-23 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-24 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-25 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-26 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-27 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-28 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-29 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-30 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-31 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-01 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-02 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-03 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-04 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-05 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-06 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-07 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-08 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-09 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-10 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-12 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-13 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-14 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-15 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-16 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-17 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-18 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-19 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-20 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-21 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-22 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-23 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-24 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-25 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-26 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-27 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-28 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-29 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-30 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-31 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-01 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-02 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-03 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-04 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-05 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-06 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-07 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-08 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-09 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-10 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-12 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-14 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-15 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-16 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-17 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-18 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-19 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-20 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-21 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-22 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-23 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-25 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-27 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-28 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-29 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-01 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-02 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-03 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-04 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-05 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-07 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-08 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-09 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-10 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-11 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-13 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-14 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-15 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-16 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-17 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-18 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-19 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-20 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-21 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-22 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-23 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-24 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-25 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-26 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-27 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-28 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-29 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-30 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-31 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-01 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-02 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-03 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-04 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-05 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-06 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-07 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-08 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-09 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-10 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-11 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-12 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-13 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-14 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-15 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-16 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-17 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-18 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-19 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-20 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-21 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-22 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-23 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-24 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-25 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-26 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-27 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-28 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-29 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-30 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-01 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-02 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-03 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-04 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-05 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-06 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-07 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-11 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-12 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-13 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-14 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-15 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-16 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-17 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-18 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-19 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-20 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-21 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-22 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-23 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-24 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-25 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-26 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-27 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-28 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-29 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-30 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-31 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-01 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-02 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-03 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-04 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-05 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-06 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-07 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-08 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-09 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-10 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-11 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-12 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-13 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-14 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-15 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-16 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-17 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-18 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-19 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-20 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-21 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-22 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-23 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-24 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-25 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-26 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-27 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-28 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-29 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-30 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-01 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-02 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-03 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-04 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-05 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-06 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-07 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-08 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-09 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-10 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-11 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-12 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-13 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-14 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-15 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-16 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-17 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-18 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-19 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-20 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-21 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-22 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-23 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-24 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-25 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-26 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-27 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-28 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-29 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-30 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-31 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-01 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-02 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-03 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-04 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-05 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-06 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-07 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-08 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-09 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-10 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-11 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-12 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-13 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-14 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-15 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-16 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-17 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-18 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-19 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-20 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-21 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-22 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-23 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-24 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-25 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-26 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-27 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-28 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-29 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-30 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-31 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-01 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-02 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-03 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-04 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-05 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-06 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-07 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-08 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-09 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-10 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-11 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-12 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-13 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-14 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-15 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-16 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-17 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-18 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-19 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-20 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-21 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-22 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-23 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-24 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-25 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-26 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-27 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-28 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-29 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-30 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-01 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-02 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-03 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-04 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-05 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-06 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-07 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-08 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-09 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-10 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-11 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-12 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-13 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-14 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-15 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-16 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-17 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-18 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-19 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-20 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-21 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-22 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-23 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-25 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-26 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-27 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-28 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-29 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-30 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-31 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-01 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-02 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-03 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-04 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-05 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-06 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-07 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-08 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-09 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-10 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-11 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-12 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-13 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-14 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-15 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-16 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-17 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-18 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-19 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-20 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-21 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-22 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-23 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-24 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-25 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-26 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-27 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-28 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-29 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-30 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-01 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-02 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-03 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-04 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-05 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-06 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-07 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-08 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-09 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-10 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-11 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-12 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-13 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-14 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-15 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-16 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-17 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-18 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-19 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-20 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-21 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-22 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-23 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-24 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-25 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-26 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-27 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-28 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-29 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-30 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-31 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-01 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-02 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-03 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-04 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-05 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-06 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-07 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-09 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-10 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-11 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-12 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-13 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-14 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-15 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-16 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-17 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-18 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-19 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-20 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-21 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-22 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-23 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-24 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-26 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-27 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-29 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-30 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-31 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-01 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-02 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-03 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-04 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-05 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-06 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-07 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-08 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-09 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-10 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-11 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-12 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-13 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-14 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-15 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-16 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-17 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-18 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-19 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-20 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-21 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-22 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-23 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-24 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-25 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-26 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-27 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-28 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-01 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-02 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-03 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-04 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-05 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-06 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-07 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-08 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-09 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-10 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-11 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-12 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-13 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-14 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-15 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-16 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-17 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-18 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-19 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-20 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-22 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-23 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-24 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-25 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-26 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-27 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-28 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 10.507 | 2.36% | 1.572% | -0.4149% | -1.043% | -0.3206% | -2.154% | 0% | -0.7699% | -2.711% | -3.324% | -2.619% | -4.41%
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 10.507 | -0.002389% | 2.646% | -0.08603% | -1.013% | 0.09318% | -1.638% | -2.58% | 0% | -2.661% | -3.564% | -2.487% | -4.173%
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 10.507 | 1.604% | 1.448% | -2.3% | -1.093% | -0.3292% | 0.6706% | 0% | -0.1537% | -3.843% | -2.655% | -1.903% | -0.919%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 10.507 | 1.674% | 0.1374% | -1.328% | 0.7878% | -0.1623% | -1.109% | 0% | -1.511% | -2.953% | -0.8717% | -1.806% | -2.737%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 10.507 | 0.9503% | 0.7565% | -1.372% | 0.5342% | -0.6114% | -0.2579% | 0% | -0.1919% | -2.3% | -0.4122% | -1.547% | -1.197%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 10.507 | -0.6259% | 1.701% | 0.3735% | 2.912% | -4.556% | 0.1954% | -3.438% | -1.177% | -2.467% | 0% | -7.256% | -2.64%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 10.507 | 9.099% | 8.016% | 7.328% | -30.07% | 1.965% | 3.659% | 0% | -0.9928% | -1.623% | -35.9% | -6.539% | -4.986%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 10.507 | 12.69% | 12.28% | 9.913% | -52.96% | 8.778% | 9.304% | 0% | -0.3638% | -2.463% | -58.26% | -3.47% | -3.003%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 10.507 | 7.343% | 8.734% | 7.046% | -40.15% | 8.755% | 8.27% | -1.298% | -0.01919% | -1.571% | -44.96% | 0% | -0.4462%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 10.507 | 7.821% | 5.079% | 3.102% | -24.5% | 4.798% | 3.699% | 0% | -2.543% | -4.376% | -29.98% | -2.804% | -3.823%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 10.507 | 0.5928% | 0.9721% | 0.4699% | 0.09084% | -0.5646% | -1.561% | -0.3757% | 0% | -0.4973% | -0.8728% | -1.522% | -2.509%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 10.507 | -0.6599% | 1.203% | 0.4369% | 1.932% | -1.06% | -1.852% | -2.543% | -0.7155% | -1.467% | 0% | -2.936% | -3.713%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 10.507 | 1.916% | -0.4354% | 1.007% | 0.2357% | -0.8644% | -1.858% | 0% | -2.307% | -0.8917% | -1.648% | -2.728% | -3.703%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 10.507 | -1.592% | 0.5098% | 2.714% | 1.759% | -2.229% | -1.162% | -4.192% | -2.146% | 0% | -0.9291% | -4.812% | -3.773%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 10.507 | 0.4132% | 0.4145% | 1.975% | 1.751% | -1.315% | -3.239% | -1.532% | -1.531% | 0% | -0.2204% | -3.227% | -5.113%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 10.507 | 1.244% | 0.0493% | 1.61% | 0.3604% | -0.8074% | -2.456% | -0.3593% | -1.536% | 0% | -1.229% | -2.379% | -4.001%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 10.507 | -0.8273% | 0.2088% | 2.47% | 0.8965% | -0.6695% | -2.078% | -3.217% | -2.206% | 0% | -1.535% | -3.063% | -4.438%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 10.507 | 15.7% | 10.19% | 14.46% | -61.55% | 11.98% | 9.222% | 0% | -4.765% | -1.075% | -66.77% | -3.216% | -5.599%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 10.507 | 1.9% | -1.819% | 1.14% | -1.337% | 0.216% | -0.1% | 0% | -3.651% | -0.7459% | -3.178% | -1.653% | -1.963%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 10.507 | -4.695% | 1.316% | 2.094% | 1.41% | 0.5612% | -0.6868% | -6.65% | -0.7617% | 0% | -0.6698% | -1.501% | -2.724%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 10.507 | -0.5333% | 1.01% | 1.085% | 3.578% | -3.4% | -1.741% | -3.97% | -2.479% | -2.407% | 0% | -6.737% | -5.135%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 10.507 | 1.401% | -1.004% | 0.4976% | 0.8978% | -0.06962% | -1.723% | 0% | -2.372% | -0.8909% | -0.4963% | -1.45% | -3.081%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 10.507 | 1.567% | -1.524% | 1.673% | 2.858% | -2.486% | -2.088% | -1.255% | -4.26% | -1.151% | 0% | -5.195% | -4.808%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 10.507 | 9.324% | 5.873% | 8.942% | -34.19% | 5.181% | 4.866% | 0% | -3.156% | -0.3492% | -39.8% | -3.789% | -4.077%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 10.507 | 2.481% | 1.297% | 0.04457% | -1.466% | -1.321% | -1.036% | 0% | -1.155% | -2.378% | -3.852% | -3.71% | -3.432%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 10.507 | 1.597% | 0.5731% | 0.5514% | -1.63% | -0.01591% | -1.076% | 0% | -1.008% | -1.029% | -3.176% | -1.588% | -2.631%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 10.507 | 2.147% | 2.052% | 1.669% | -1.844% | -1.679% | -2.345% | 0% | -0.09371% | -0.4679% | -3.907% | -3.746% | -4.398%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 10.507 | 3.098% | 0.2533% | 0.9568% | -2.906% | -0.3312% | -1.071% | 0% | -2.759% | -2.077% | -5.823% | -3.326% | -4.044%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 10.507 | 0.4347% | -0.5891% | 1.3% | -0.3971% | -0.6427% | -0.106% | -0.8543% | -1.865% | 0% | -1.675% | -1.918% | -1.388%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 10.507 | 0.6028% | -0.7199% | -1.175% | -2.503% | 2.26% | 1.535% | -1.62% | -2.914% | -3.359% | -4.657% | 0% | -0.7084%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 10.507 | 0.5087% | -0.2306% | -0.7289% | 0.3808% | -0.09001% | 0.1601% | 0% | -0.7355% | -1.231% | -0.1272% | -0.5956% | -0.3468%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 10.507 | 0.09354% | -1.666% | 0.1385% | 1.44% | 0.02533% | -0.03189% | -1.328% | -3.062% | -1.283% | 0% | -1.395% | -1.451%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 10.507 | -0.1171% | -0.25% | -0.88% | 2.311% | -1.87% | 0.8059% | -2.374% | -2.504% | -3.119% | 0% | -4.087% | -1.471%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 10.507 | 1.435% | -0.9071% | -3.662% | -0.1541% | 1.241% | 2.046% | -0.5988% | -2.894% | -5.593% | -2.156% | -0.7886% | 0%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 10.507 | 0.8697% | -1.685% | -1.681% | 0.4774% | 1.986% | 0.0323% | -1.095% | -3.599% | -3.596% | -1.479% | 0% | -1.916%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 10.507 | 1.598% | -0.822% | -0.947% | -0.4598% | 0.439% | 0.192% | 0% | -2.382% | -2.505% | -2.025% | -1.141% | -1.384%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 10.507 | 1.146% | -0.9732% | -0.4577% | 0.7357% | -0.265% | -0.1854% | 0% | -2.095% | -1.585% | -0.4052% | -1.395% | -1.316%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 10.507 | 0.8874% | -1.042% | -1.241% | 1.167% | 0.4495% | -0.2212% | -0.2759% | -2.183% | -2.38% | 0% | -0.7088% | -1.372%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 10.507 | 2.148% | 0.982% | -2.472% | 0.3767% | -0.389% | -0.6454% | 0% | -1.142% | -4.523% | -1.734% | -2.484% | -2.735%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 10.507 | 1.596% | 0.2647% | -1.267% | 0.6353% | -0.4107% | -0.8181% | 0% | -1.31% | -2.818% | -0.9455% | -1.975% | -2.376%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 10.507 | 1.631% | 1.348% | -0.6354% | 1.266% | -1.469% | -2.141% | 0% | -0.2782% | -2.23% | -0.3598% | -3.05% | -3.712%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 10.507 | 2.781% | 1.805% | -0.6414% | -0.393% | -1.893% | -1.66% | 0% | -0.9496% | -3.33% | -3.089% | -4.548% | -4.321%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 10.507 | 3.312% | 1.61% | -0.5375% | -0.2475% | -0.6883% | -3.449% | 0% | -1.647% | -3.726% | -3.445% | -3.872% | -6.544%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 10.507 | -1.594% | 0.356% | 0.6802% | 1.103% | 1.343% | -1.889% | -2.898% | -0.9741% | -0.6542% | -0.237% | 0% | -3.189%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 10.507 | 1.59% | 0.3054% | 0.5754% | 0.4671% | -1.459% | -1.479% | 0% | -1.264% | -0.9986% | -1.105% | -3.001% | -3.02%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 10.507 | 2.061% | 0.3388% | -1.199% | -1.112% | -0.7835% | 0.6939% | 0% | -1.688% | -3.194% | -3.109% | -2.787% | -1.34%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 10.507 | 0.6624% | -0.198% | -0.453% | 0.7336% | -1.022% | 0.2767% | -0.07068% | -0.9248% | -1.178% | 0% | -1.743% | -0.4536%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 10.507 | -0.1942% | -1.07% | 0.006608% | 0.7643% | -0.3036% | 0.7971% | -0.9834% | -1.853% | -0.7842% | -0.03249% | -1.092% | 0%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 10.507 | -0.3605% | -0.6915% | 0.334% | 0.4738% | -1.221% | 1.465% | -1.799% | -2.125% | -1.115% | -0.977% | -2.647% | 0%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 10.507 | 0.3604% | -1.736% | 1.087% | 0.8994% | -0.4981% | -0.1133% | -0.7192% | -2.793% | 0% | -0.186% | -1.568% | -1.188%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 10.507 | -7.809% | -0.2763% | 2.325% | 2.264% | 1.697% | 1.799% | -9.904% | -2.542% | 0% | -0.05963% | -0.6143% | -0.5144%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 10.507 | -0.3639% | -2.621% | 2.017% | 0.8255% | 1.509% | -1.366% | -2.333% | -4.546% | 0% | -1.168% | -0.4977% | -3.315%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 10.507 | 0.44% | -2.696% | 3.441% | 2.475% | -2.466% | -1.195% | -2.901% | -5.933% | 0% | -0.9338% | -5.711% | -4.482%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 10.507 | 0.5287% | -2.07% | 1.695% | 1.513% | -1.594% | -0.07323% | -1.147% | -3.703% | 0% | -0.1794% | -3.234% | -1.739%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 10.507 | 2.967% | -1.76% | 0.5176% | 0.1529% | -1.7% | -0.1772% | 0% | -4.592% | -2.379% | -2.733% | -4.533% | -3.054%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 10.507 | 4.142% | -2.453% | 1.022% | 0.01609% | -4.038% | 1.311% | 0% | -6.333% | -2.996% | -3.962% | -7.855% | -2.719%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 10.507 | 10.77% | 8.122% | 10.22% | -49.76% | 9.04% | 11.6% | -0.7389% | -3.115% | -1.231% | -54.98% | -2.292% | 0%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 10.507 | 4.286% | -9.388% | 3.702% | -7.723% | 3.702% | 5.422% | -1.078% | -14.05% | -1.631% | -12.47% | -1.631% | 0%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 10.507 | -2.01% | -1.835% | 1.706% | 0.9763% | 0.2029% | 0.9594% | -3.654% | -3.481% | 0% | -0.7174% | -1.478% | -0.734%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 10.507 | 1.475% | -2.867% | 0.5618% | -0.3172% | 0.02719% | 1.12% | 0% | -4.279% | -0.8998% | -1.766% | -1.427% | -0.3495%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 10.507 | 1.758% | -2.651% | 1.863% | 1.217% | -1.749% | -0.4382% | -0.1032% | -4.432% | 0% | -0.6348% | -3.547% | -2.26%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 10.507 | 1.097% | -2.96% | 1.307% | 1.498% | -1.166% | 0.2237% | -0.3952% | -4.392% | -0.188% | 0% | -2.625% | -1.256%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 10.507 | 1.331% | -2.71% | 1.779% | 0.09155% | -0.378% | -0.1132% | -0.4406% | -4.411% | 0% | -1.658% | -2.119% | -1.859%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 10.507 | 1.303% | -0.7761% | 1.004% | -0.4294% | -1.487% | 0.3858% | 0% | -2.052% | -0.2948% | -1.71% | -2.754% | -0.905%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 10.507 | 3.721% | 0.2181% | -0.9572% | -1.498% | -2.933% | 1.449% | 0% | -3.377% | -4.511% | -5.032% | -6.415% | -2.191%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 10.507 | 3.022% | -0.2937% | 0.5891% | -1.483% | -1.939% | 0.1051% | 0% | -3.218% | -2.361% | -4.372% | -4.815% | -2.831%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 10.507 | 2.519% | -3.09% | 2.002% | -0.7839% | -1.161% | 0.5151% | 0% | -5.471% | -0.5041% | -3.221% | -3.589% | -1.954%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 10.507 | 1.699% | 0.8939% | 0.08271% | -1.378% | -1.946% | 0.6486% | 0% | -0.7921% | -1.59% | -3.026% | -3.585% | -1.033%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 10.507 | 0.3983% | 0.8191% | 1.774% | -1.096% | -3.211% | 1.315% | -1.351% | -0.9379% | 0% | -2.819% | -4.897% | -0.4504%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 10.507 | -0.2698% | 1.585% | 0.638% | 1.074% | -3.451% | 0.4244% | -1.826% | 0% | -0.932% | -0.503% | -4.957% | -1.142%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 10.507 | -4.063% | 2.903% | 0.7504% | 1.374% | -1.072% | 0.1072% | -6.77% | 0% | -2.092% | -1.486% | -3.863% | -2.717%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 10.507 | 2.184% | 2.193% | 0.265% | -1.717% | -1.61% | -1.316% | -0.008302% | 0% | -1.887% | -3.826% | -3.721% | -3.433%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 10.507 | -0.4308% | 2.3% | 1.66% | -0.2218% | -2.161% | -1.146% | -2.669% | 0% | -0.6255% | -2.465% | -4.36% | -3.368%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 10.507 | 2.02% | 1.594% | 1.683% | -2.526% | -1.88% | -0.8904% | 0% | -0.4181% | -0.3307% | -4.457% | -3.823% | -2.853%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 10.507 | 0.8123% | 0.7782% | 1.076% | -1.582% | -0.5077% | -0.5769% | -0.2606% | -0.2943% | 0% | -2.629% | -1.567% | -1.635%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 10.507 | 2.317% | -0.4109% | 0.9331% | -1.798% | -1.243% | 0.2006% | 0% | -2.667% | -1.353% | -4.022% | -3.479% | -2.069%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 10.507 | 1.239% | 1.291% | 0.6111% | -2.141% | -1.321% | 0.3219% | -0.05165% | 0% | -0.6712% | -3.389% | -2.579% | -0.9567%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 10.507 | -0.9476% | 0.8567% | 2.461% | -1.569% | -0.3064% | -0.4955% | -3.327% | -1.566% | 0% | -3.933% | -2.701% | -2.886%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 10.507 | 1.457% | 1.211% | 1.576% | -2.12% | -1.119% | -1.005% | -0.1175% | -0.3597% | 0% | -3.639% | -2.654% | -2.541%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 10.507 | 2.322% | 0.02408% | 0.7659% | -1.667% | -1.343% | -0.101% | 0% | -2.246% | -1.521% | -3.899% | -3.582% | -2.368%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 10.507 | 1.119% | -1.169% | 1.057% | -0.5241% | -0.4868% | 0.003909% | 0% | -2.263% | -0.0621% | -1.625% | -1.588% | -1.103%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 10.507 | 1.573% | 1.613% | 0.7675% | -2.121% | -0.4172% | -1.414% | -0.03929% | 0% | -0.8318% | -3.675% | -1.998% | -2.979%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 10.507 | 3.127% | 3.161% | 1.851% | -7.487% | -0.0184% | -0.6336% | -0.03212% | 0% | -1.269% | -10.32% | -3.082% | -3.678%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 10.507 | 1.609% | 2.479% | 0.02868% | -0.9335% | -2.553% | -0.6311% | -0.8487% | 0% | -2.391% | -3.33% | -4.91% | -3.035%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 10.507 | 3.093% | 2.729% | 0.2804% | -1.957% | -2.523% | -1.622% | 0% | -0.3539% | -2.729% | -4.899% | -5.448% | -4.574%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 10.507 | 1.391% | 3.367% | 0.6871% | -2.773% | -1.464% | -1.209% | -1.912% | 0% | -2.593% | -5.94% | -4.674% | -4.427%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 10.507 | 1.479% | 1.466% | 0.8765% | -0.7882% | -1.956% | -1.078% | 0% | -0.01285% | -0.5941% | -2.234% | -3.386% | -2.52%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 10.507 | 1.826% | 0.7102% | 0.7438% | -0.425% | -1.321% | -1.533% | 0% | -1.095% | -1.062% | -2.21% | -3.09% | -3.299%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 10.507 | 3.734% | -1.24% | 1.774% | 0.1456% | -2.822% | -1.593% | 0% | -4.795% | -1.89% | -3.46% | -6.32% | -5.135%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 10.507 | 1.497% | 1.725% | 1.869% | -2.169% | -1.314% | -1.607% | -0.3652% | -0.1413% | 0% | -3.964% | -3.125% | -3.412%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 10.507 | 1.418% | 0.7401% | 1.137% | -0.5224% | -0.9707% | -1.802% | 0% | -0.6685% | -0.2776% | -1.913% | -2.355% | -3.175%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 10.507 | -0.4278% | 1.306% | 1.16% | 0.7381% | -1.483% | -1.293% | -1.712% | 0% | -0.1443% | -0.5607% | -2.754% | -2.565%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 10.507 | 1.82% | 0.2245% | -0.1849% | 0.5478% | -1.711% | -0.6959% | 0% | -1.567% | -1.969% | -1.249% | -3.468% | -2.471%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 10.507 | 2.487% | 0.1231% | 0.5512% | 0.1007% | -1.933% | -1.329% | 0% | -2.307% | -1.889% | -2.329% | -4.313% | -3.724%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 10.507 | 1.096% | 0.05665% | 1.432% | 0.7365% | -1.945% | -1.376% | -0.3307% | -1.356% | 0% | -0.6855% | -3.329% | -2.768%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 10.507 | 2.057% | 0.2997% | 0.8883% | 0.736% | -1.896% | -2.085% | 0% | -1.722% | -1.146% | -1.295% | -3.874% | -4.059%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 10.507 | 1.843% | 0.2102% | 1.119% | 0.9449% | -1.735% | -2.381% | 0% | -1.603% | -0.7112% | -0.8817% | -3.513% | -4.147%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 10.507 | 2.141% | 0.06087% | 0.9829% | 1.727% | -3.154% | -1.757% | 0% | -2.036% | -1.134% | -0.405% | -5.184% | -3.817%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 10.507 | 1.51% | 0.7022% | 0.6793% | 0.854% | -1.257% | -2.489% | 0% | -0.7953% | -0.8179% | -0.6458% | -2.725% | -3.939%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 10.507 | 2.617% | -2.972% | 1.839% | -0.3703% | -0.654% | -0.4588% | 0% | -5.447% | -0.7584% | -2.911% | -3.187% | -2.997%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 10.507 | 1.823% | 0.2013% | 0.2926% | 3% | -3.584% | -1.732% | -1.143% | -2.717% | -2.628% | 0% | -6.392% | -4.594%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 10.507 | 2.391% | 0.1052% | 2.488% | -0.8636% | -2.808% | -1.313% | -0.09421% | -2.325% | 0% | -3.27% | -5.168% | -3.709%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 10.507 | 1.141% | -2.242% | 1.955% | -0.08633% | -1.411% | 0.6426% | -0.7977% | -4.116% | 0% | -2.002% | -3.301% | -1.287%
[6 empty] | 31 | 2025-07-10 | 0 | 1.171% | -1.045% | 2.45% | -0.2647% | -2.202% | -0.109% | -1.249% | -3.411% | 0% | -2.649% | -4.54% | -2.497%
[6 empty] | 31 | 2025-07-11 | 0 | 1.671% | 1.733% | 1.936% | -1.768% | -2.909% | -0.6636% | -0.2594% | -0.1984% | 0% | -3.633% | -4.752% | -2.55%
[6 empty] | 31 | 2025-07-12 | 0 | -0.03887% | 1.058% | 2.392% | 0.8955% | -2.28% | -2.027% | -2.375% | -1.303% | 0% | -1.462% | -4.564% | -4.316%
[6 empty] | 31 | 2025-07-13 | 0 | -1.764% | 2.05% | 2.868% | 1.788% | -2.84% | -2.102% | -4.504% | -0.7959% | 0% | -1.05% | -5.549% | -4.832%
[6 empty] | 31 | 2025-07-14 | 0
[6 empty] | 31 | 2025-07-15 | 0
[6 empty] | 31 | 2025-07-16 | 0
[6 empty] | 31 | 2025-07-17 | 0
[6 empty] | 31 | 2025-07-18 | 0
[6 empty] | 31 | 2025-07-19 | 0
[6 empty] | 31 | 2025-07-20 | 0
Formulas:
Days = DAY(EOMONTH([Month Year],0))
Date = [Date, row above]+1

## Tracker_BD
Sr. No. | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Date | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affected Equipment | Plant Equivalent Weightage | Angle of affected equipment | Inv Number | Gateway Number | Grid Number | MSAT Number | Table Number | Fault Category | Fault Code (As per HMI) | Breakdown Description | Fault Time | Fault Acknowledgement Time | Work Start time on Fault | Work Completion time on fault | Acknowledgement time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Avg. Target Angle during Fault Time (Radians) | Approximate Energy Loss Factor (%) | Plant Equivalent breakdown | Old equipment Serial Number | New Equipment Serial Number | Column1
1 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:29 | 18:29 | 12 | Actuator Type1 |  | 0 | IC1_Inv4 | G5 | G4 | 37 | T108 | Actuator | Actuator fail | Actuator fail | 8:10 | 8:10 | 8:10 | 8:50 | 0 | 0 | 0.66667 | 0.66667 | Actuator 2 No Limit Switch was replaced | Close
2 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:29 | 18:29 | 12 | Actuator Type1 |  | 0 | IC1_Inv3 | G3 | G5 | 64 | T95 | Actuator | Actuator fail | Actuator fail | 8:40 | 8:40 | 8:40 | 9:30 | 0 | 0 | 0.83333 | 0.83333 | 1 No Medium Gear Replaced | Close
3 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:29 | 18:29 | 12 | Actuator Type1 |  | 0 | IC1_Inv2 | G5 | G4 | 27 | T65 | Actuator | Actuator fail | Actuator fail | 9:20 | 9:20 | 9:20 | 10:10 | 0 | 0 | 0.83333 | 0.83333 | 1 No Actuator Motor | Close
4 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:29 | 18:29 | 12 | Actuator Type1 |  | 0 | IC1_Inv3 | G1 | G3 | 12 | T57 | Actuator | Actuator fail | Actuator fail | 9:40 | 9:40 | 9:40 | 10:20 | 0 | 0 | 0.66667 | 0.66667 | Actuator 2 No Limit Switch was replaced | Close
5 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:23 | 18:14 | 11.85 | Actuator Type1 |  | 0 | IC1_Inv3 | G5 | G4 | 30 | T80 | Actuator | Actuator fail | Actuator fail | 15:50 | 15:50 | 15:50 | 16:20 | 0 | 0 | 0.5 | 0.5 | 2 Nos Actuator Bearing Replaced | Close
6 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:23 | 18:14 | 11.85 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 21 | T34 | Actuator | Actuator fail | Actuator fail | 16:30 | 16:30 | 16:30 | 17:30 | 0 | 0 | 1 | 1 | 1 No Actuator Motor | Close
7 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:31 | 18:14 | 11.7167 | Actuator Type1 |  | 0 | IC1_Inv3 | G5 | G4 | 30 | T80 | Actuator | Actuator fail | Actuator fail | 7:10 | 7:10 | 7:10 | 7:50 | 0 | 0 | 0.66667 | 0.66667 | Actuator 2 No Limit Switch was replaced | Close
8 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:31 | 18:14 | 11.7167 | Actuator Type1 |  | 0 | IC1_Inv2 | G3 | G5 | 63 | T70 | Actuator | Actuator fail | Actuator fail | 8:20 | 8:20 | 8:20 | 8:30 | 0 | 0 | 0.16667 | 0.16667 | Actuator motor 2 no.s Carbon brushes | Close
9 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:31 | 18:14 | 11.7167 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 21 | T32 | Actuator | Actuator fail | Actuator fail | 8:40 | 8:40 | 8:40 | 9:40 | 0 | 0 | 1 | 1 | 1 No Big Gear Replaced | Close
10 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:31 | 18:14 | 11.7167 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 4 | T17 | Actuator | Actuator fail | Actuator fail | 9:10 | 9:10 | 9:10 | 10:10 | 0 | 0 | 1 | 1 | 2 Nos Actuator Bearing Replaced | Close
11 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:21 | 18:23 | 12.0333 | Actuator Type1 |  | 0 | IC2_Inv1 | G5 | G4 | 18 | T20 | Actuator | Actuator fail | Actuator fail | 16:20 | 16:20 | 16:20 | 16:40 | 0 | 0 | 0.33333 | 0.33333 | 1 No Big Gear Replaced | Close |  |  | 0
12 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:21 | 18:23 | 12.0333 | Actuator Type1 |  | 0 | IC1_Inv4 | G3 | G5 | 69 | T116 | Actuator | Actuator fail | Actuator fail | 17:20 | 17:20 | 17:20 | 17:50 | 0 | 0 | 0.5 | 0.5 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
13 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:21 | 18:23 | 12.0333 | Actuator Type1 |  | 0 | IC1_Inv4 | G3 | G5 | 73 | T136 | Actuator | Actuator fail | Actuator fail | 17:35 | 17:35 | 17:35 | 18:20 | 0 | 0 | 0.75 | 0.75 | 1 No Actuator Motor | Close |  |  | 0
14 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:30 | 18:26 | 11.9333 | Actuator Type1 |  | 0 | IC2_Inv1 | G1 | G3 | 121 | TW01 | Actuator | Actuator fail | Actuator fail | 15:30 | 15:30 | 15:30 | 16:30 | 0 | 0 | 1 | 1 | 1 No Actuator Motor | Close |  |  | 0
15 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:30 | 18:26 | 11.9333 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 3 | T16 | Actuator | Actuator fail | Actuator fail | 15:50 | 15:50 | 15:50 | 16:40 | 0 | 0 | 0.83333 | 0.83333 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
16 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:30 | 18:26 | 11.9333 | Actuator Type1 |  | 0 | IC1_Inv2 | G1 | G3 | 10 | T50 | Actuator | Actuator fail | Actuator fail | 16:45 | 16:45 | 16:45 | 17:20 | 0 | 0 | 0.58333 | 0.58333 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
17 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC1_Inv3 | G5 | G4 | 33 | T88 to T92 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 11:10 | 11:10 | 11:10 | 11:30 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
18 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC2_Inv2 | G4 | G6 | 82 | T21 to T25 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 11:40 | 11:40 | 11:40 | 12:00 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
19 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC2_Inv2 | G4 | G6 | 87 | T46 TO T50 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 12:30 | 12:30 | 12:30 | 12:40 | 0 | 0 | 0.16667 | 0.16667 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
20 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC2_Inv2 | G4 | G6 | 79 | T6 TO T10 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 13:30 | 13:30 | 13:30 | 13:50 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
21 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC2_Inv2 | G4 | G6 | 80 | T11 to T15 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 14:00 | 14:00 | 14:00 | 14:20 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
22 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC2_Inv2 | G4 | G6 | 81 | T16 to T20 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 14:30 | 14:30 | 14:30 | 14:40 | 0 | 0 | 0.16667 | 0.16667 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
23 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC1_Inv4 | G3 | G5 | 72 | T131 to T135 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 14:50 | 14:50 | 14:50 | 15:10 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
24 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC1_Inv1 | G3 | G5 | 52 | T36 to T40 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 15:20 | 15:20 | 15:20 | 15:40 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
25 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC1_Inv4 | G3 | G5 | 68 | T111 TO T115 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 15:30 | 15:30 | 15:30 | 15:50 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
26 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:19 | 18:33 | 12.2333 | Actuator Type1 |  | 0 | IC1_Inv4 | G5 | G4 | 40 | T126 | Actuator | Actuator fail | Actuator fail | 15:20 | 15:20 | 15:20 | 16:00 | 0 | 0 | 0.66667 | 0.66667 | 1 No Big Gear Replaced | Close |  |  | 0
27 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:19 | 18:33 | 12.2333 | Actuator Type1 |  | 0 | IC1_Inv2 | G3 | G5 | 42 | T49 | Actuator | Actuator fail | Actuator fail | 16:20 | 16:20 | 16:20 | 16:40 | 0 | 0 | 0.33333 | 0.33333 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
28 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:20 | 18:13 | 11.8833 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G2 | 100 | T21 | Actuator | Actuator fail | Actuator fail | 14:30 | 14:30 | 14:30 | 15:10 | 0 | 0 | 0.66667 | 0.66667 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
29 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:20 | 18:13 | 11.8833 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G1 | 108 | T23 | Actuator | Actuator fail | Actuator fail | 14:50 | 14:50 | 14:50 | 15:20 | 0 | 0 | 0.5 | 0.5 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
30 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:20 | 18:13 | 11.8833 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G2 | 99 | T17 | Actuator | Actuator fail | Actuator fail | 15:40 | 15:40 | 15:40 | 16:30 | 0 | 0 | 0.83333 | 0.83333 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
31 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:20 | 18:13 | 11.8833 | MSAT_Type3 |  | 0 | IC2_Inv1 | G7 | G1 | 107 | T16 to T20 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 16:50 | 16:50 | 16:50 | 17:10 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
32 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:21 | 18:21 | 12 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 5 | T20 | Actuator | Actuator fail | Actuator fail | 15:25 | 15:25 | 15:25 | 15:50 | 0 | 0 | 0.41667 | 0.41667 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
33 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:20 | 18:21 | 12.0167 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 2 | T08 | Actuator | Actuator fail | Actuator fail | 11:00 | 11:00 | 11:00 | 11:40 | 0 | 0 | 0.66667 | 0.66667 | 1 No Medium Gear Replaced | Close |  |  | 0
34 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:20 | 18:21 | 12.0167 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 3 | T10 | Actuator | Actuator fail | Actuator fail | 11:20 | 11:20 | 11:20 | 12:10 | 0 | 0 | 0.83333 | 0.83333 | 1 No Big Gear Replaced | Close |  |  | 0
35 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:22 | 18:21 | 11.9833 | Actuator Type1 |  | 0 | IC1_Inv3 | G3 | G5 | 32 | T86 | Actuator | Actuator fail | Actuator fail | 15:45 | 15:45 | 15:45 | 17:20 | 0 | 0 | 1.5833 | 1.5833 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
36 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:20 | 18:20 | 12 | Actuator Type1 |  | 0 | IC1_Inv2 | G4 | G6 | 90 | T65 | Actuator | Actuator fail | Actuator fail | 8:30 | 8:30 | 8:30 | 9:45 | 0 | 0 | 1.25 | 1.25 | 1 No Actuator Motor | Close |  |  | 0
37 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:23 | 18:12 | 11.8167 | Actuator Type1 |  | 0 | IC1_Inv4 | G3 | G5 | 73 | T142 | Actuator | Actuator fail | Actuator fail | 8:45 | 8:45 | 8:45 | 9:50 | 0 | 0 | 1.0833 | 1.0833 | 1 No Medium Gear Replaced | Close |  |  | 0
38 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:23 | 18:12 | 11.8167 | Actuator Type1 |  | 0 | IC1_Inv4 | G3 | G5 | 67 | T110 | Actuator | Actuator fail | Actuator fail | 9:35 | 9:35 | 9:35 | 10:45 | 0 | 0 | 1.1667 | 1.1667 | 1 No Actuator Motor | Close |  |  | 0
39 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:23 | 18:12 | 11.8167 | Actuator Type1 |  | 0 | IC1_Inv3 | G3 | G5 | 64 | T94 | Actuator | Actuator fail | Actuator fail | 10:00 | 10:00 | 10:00 | 11:00 | 0 | 0 | 1 | 1 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
40 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:25 | 18:05 | 11.6667 | Actuator Type1 |  | 0 | IC1_Inv2 | G3 | G5 | 120 | T16 | Actuator | Actuator fail | Actuator fail | 9:45 | 9:45 | 9:45 | 11:15 | 0 | 0 | 1.5 | 1.5 | 1 No. Nylon brass bush replaced | Close |  |  | 0
41 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:19 | 18:24 | 12.0833 | Actuator Type1 |  | 0 | IC1_Inv3 | G1 | G3 | 12 | T55 | Actuator | Actuator fail | Actuator fail | 14:10 | 14:10 | 14:10 | 14:50 | 0 | 0 | 0.66667 | 0.66667 | 1 No Medium Gear Replaced | Close |  |  | 0
42 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:19 | 18:24 | 12.0833 | Actuator Type1 |  | 0 | IC1_Inv1 | G4 | G6 | 86 | T43 | Actuator | Actuator fail | Actuator fail | 14:40 | 14:40 | 14:40 | 15:40 | 0 | 0 | 1 | 1 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
43 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:19 | 18:24 | 12.0833 | Actuator Type1 |  | 0 | IC1_Inv1 | G4 | G6 | 86 | T45 | Actuator | Actuator fail | Actuator fail | 15:35 | 15:35 | 15:35 | 16:10 | 0 | 0 | 0.58333 | 0.58333 | 1 No Medium Gear Replaced | Close |  |  | 0
44 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:15 | 18:25 | 12.1667 | Actuator Type1 |  | 0 | IC1_Inv4 | G4 | G6 | 116 | TW1 | Actuator | Actuator fail | Actuator fail | 16:10 | 16:10 | 16:10 | 16:40 | 0 | 0 | 0.5 | 0.5 | 1 No. Nylon brass bush replaced | Close |  |  | 0
45 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:15 | 18:25 | 12.1667 | Actuator Type1 |  | 0 | IC2_Inv1 | G5 | G4 | 19 | T23 | Actuator | Actuator fail | Actuator fail | 17:20 | 17:20 | 17:20 | 17:50 | 0 | 0 | 0.5 | 0.5 | 1 No Medium Gear Replaced | Close |  |  | 0
46 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:15 | 18:28 | 12.2167 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 45 | T01 | Actuator | Actuator fail | Actuator fail | 14:30 | 14:30 | 14:30 | 15:10 | 0 | 0 | 0.66667 | 0.66667 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
47 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:15 | 18:28 | 12.2167 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 47 | T13 | Actuator | Actuator fail | Actuator fail | 15:20 | 15:20 | 15:20 | 15:40 | 0 | 0 | 0.33333 | 0.33333 | 1 No. Nylon brass bush replaced | Close |  |  | 0
48 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:09 | 18:24 | 12.25 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 45 | T05 | Actuator | Actuator fail | Actuator fail | 9:10 | 9:10 | 9:10 | 10:30 | 0 | 0 | 1.3333 | 1.3333 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
49 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:09 | 18:24 | 12.25 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 53 | T42 | Actuator | Actuator fail | Actuator fail | 14:20 | 14:20 | 14:20 | 15:40 | 0 | 0 | 1.3333 | 1.3333 | 1 No Small Gear Replaced | Close |  |  | 0
50 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:15 | 18:07 | 11.8667 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 41 | T42 | Actuator | Actuator fail | Actuator fail | 15:10 | 15:10 | 15:10 | 15:50 | 0 | 0 | 0.66667 | 0.66667 | 1 No Medium Gear Replaced | Close |  |  | 0
51 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:15 | 18:07 | 11.8667 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 41 | T44 | Actuator | Actuator fail | Actuator fail | 16:20 | 16:20 | 16:20 | 17:20 | 0 | 0 | 1 | 1 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
52 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:07 | 18:26 | 12.3167 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 27 | T64 | Actuator | Actuator fail | Actuator fail | 13:20 | 13:20 | 13:20 | 14:20 | 0 | 0 | 1 | 1 | 1 No Medium Gear Replaced | Close |  |  | 0
53 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:10 | 18:23 | 12.2167 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 23 | T44 | Actuator | Actuator fail | Actuator fail | 9:10 | 9:10 | 9:10 | 10:20 | 0 | 0 | 1.1667 | 1.1667 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
54 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:10 | 18:23 | 12.2167 | Actuator Type1 |  | 0 | IC1_Inv2 | G4 | G6 | 84 | T27 | Actuator | Actuator fail | Actuator fail | 10:20 | 10:20 | 10:20 | 11:10 | 0 | 0 | 0.83333 | 0.83333 | 1 No. Nylon brass bush replaced | Close |  |  | 0
55 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:10 | 18:23 | 12.2167 | Actuator Type1 |  | 0 | IC1_Inv2 | G4 | G6 | 89 | T60 | Actuator | Actuator fail | Actuator fail | 11:10 | 11:10 | 11:10 | 12:30 | 0 | 0 | 1.3333 | 1.3333 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
56 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:09 | 18:29 | 12.3333 | Actuator Type1 |  | 0 | IC1_Inv1 | G3 | G5 | 118 | Tw5 | Actuator | Actuator fail | Actuator fail | 8:20 | 8:20 | 8:20 | 9:40 | 0 | 0 | 1.3333 | 1.3333 | 1 No Actuator Motor | Close |  |  | 0
57 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:09 | 18:29 | 12.3333 | Actuator Type1 |  | 0 | IC1_Inv2 | G3 | G5 | 58 | T70 | Actuator | Actuator fail | Actuator fail | 12:20 | 12:20 | 12:20 | 13:40 | 0 | 0 | 1.3333 | 1.3333 | 1 No Medium Gear Replaced | Close |  |  | 0
58 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:08 | 18:30 | 12.3667 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 2 | T08 | Actuator | Actuator fail | Actuator fail | 11:30 | 11:30 | 11:30 | 12:30 | 0 | 0 | 1 | 1 | 1 No. Nylon brass bush replaced | Close |  |  | 0
59 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:35 | 12.5333 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 4 | T16 | Actuator | Actuator fail | Actuator fail | 8:10 | 8:10 | 8:10 | 9:30 | 0 | 0 | 1.3333 | 1.3333 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
60 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:35 | 12.5333 | Actuator Type1 |  | 0 | IC1_Inv2 | G1 | G3 | 11 | T52 | Actuator | Actuator fail | Actuator fail | 9:20 | 9:20 | 9:20 | 10:10 | 0 | 0 | 0.83333 | 0.83333 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
61 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:05 | 18:33 | 12.4667 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 25 | T52 | Actuator | Actuator fail | Actuator fail | 14:20 | 14:20 | 14:20 | 15:25 | 0 | 0 | 1.0833 | 1.0833 | 1 No Actuator Motor | Close |  |  | 0
62 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:05 | 18:33 | 12.4667 | Actuator Type1 |  | 0 | IC1_Inv2 | G3 | G5 | 55 | T31 | Actuator | Actuator fail | Actuator fail | 15:30 | 15:30 | 15:30 | 16:10 | 0 | 0 | 0.66667 | 0.66667 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
63 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:02 | 18:17 | 12.25 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 23 | T42 | Actuator | Actuator fail | Actuator fail | 12:00 | 12:00 | 12:00 | 12:50 | 0 | 0 | 0.83333 | 0.83333 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
64 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:09 | 18:19 | 12.1667 | Actuator Type1 |  | 0 | IC1_Inv2 | G4 | G6 | 90 | T62 | Actuator | Actuator fail | Actuator fail | 9:10 | 9:10 | 9:10 | 10:25 | 0 | 0 | 1.25 | 1.25 | 1 No. Nylon brass bush replaced | Close |  |  | 0
65 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:09 | 18:19 | 12.1667 | Actuator Type1 |  | 0 | IC1_Inv1 | G4 | G6 | 86 | T45 | Actuator | Actuator fail | Actuator fail | 10:20 | 10:20 | 10:20 | 11:10 | 0 | 0 | 0.83333 | 0.83333 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
66 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:03 | 18:32 | 12.4833 | Actuator Type1 |  | 0 | IC2_Inv2 | G4 | G6 | 83 | T27 | Actuator | Actuator fail | Actuator fail | 10:20 | 10:20 | 10:20 | 11:30 | 0 | 0 | 1.1667 | 1.1667 | 1 No Actuator Motor | Close |  |  | 0
67 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:13 | 18:33 | 12.3333 | Actuator Type1 |  | 0 | IC1_Inv2 | G3 | G5 | 56 | T37 | Actuator | Actuator fail | Actuator fail | 14:40 | 14:40 | 14:40 | 15:20 | 0 | 0 | 0.66667 | 0.66667 | 1 No Medium Gear Replaced | Close |  |  | 0
68 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 6:56 | 18:31 | 11.5833 | Actuator Type1 |  | 0 | IC1_Inv3 | G3 | G5 |  | T106 | Actuator | Actuator fail | Actuator fail | 10:20 | 10:20 | 10:20 | 11:35 | 0 | 0 | 1.25 | 1.25 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
69 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 6:56 | 18:31 | 11.5833 | Actuator Type1 |  | 0 | IC1_Inv3 | G5 | G4 |  | T95 | Actuator | Actuator fail | Actuator fail | 11:20 | 11:20 | 11:20 | 11:50 | 0 | 0 | 0.5 | 0.5 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
70 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 6:04 | 18:36 | 12.5333 | Actuator Type1 |  | 0 | IC2_Inv2 | G4 | G6 | 54 | T10 | Actuator | Actuator fail | Actuator fail | 9:10 | 9:10 | 9:10 | 10:20 | 0 | 0 | 1.1667 | 1.1667 | 1 No Medium Gear Replaced | Close |  |  | 0
71 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:08 | 18:36 | 12.4667 | Actuator Type1 |  | 0 | IC1_Inv3 | G5 | G4 | 93 | T80 | Actuator | Actuator fail | Actuator fail | 8:30 | 8:30 | 8:30 | 9:45 | 0 | 0 | 1.25 | 1.25 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
72 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:04 | 18:37 | 12.55 | Actuator Type1 |  | 0 | IC1_Inv4 | G5 | G4 | 66 | T133 | Actuator | Actuator fail | Actuator fail | 14:20 | 14:20 | 14:20 | 15:10 | 0 | 0 | 0.83333 | 0.83333 | 1 No. Nylon brass bush replaced | Close |  |  | 0
73 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:04 | 18:37 | 12.55 | Actuator Type1 |  | 0 | IC2_Inv2 | G4 | G6 | 81 | T18 | Actuator | Actuator fail | Actuator fail | 14:50 | 14:50 | 14:50 | 15:50 | 0 | 0 | 1 | 1 | 1 No. Nylon brass bush replaced | Close |  |  | 0
74 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:10 | 18:31 | 12.35 | Actuator Type1 |  | 0 | IC1_Inv2 | G1 | G3 | 11 | T55 | Actuator | Actuator fail | Actuator fail | 15:10 | 15:10 | 15:10 | 16:20 | 0 | 0 | 1.1667 | 1.1667 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
75 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:06 | 18:07 | 12.0167 | Actuator Type1 |  | 0 | IC1_Inv3 | G3 | G5 | 60 | T76 | Actuator | Actuator fail | Actuator fail | 10:10 | 10:10 | 10:10 | 10:40 | 0 | 0 | 0.5 | 0.5 | 1 No. Nylon brass bush replaced | Close |  |  | 0
76 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:06 | 18:07 | 12.0167 | Actuator Type1 |  | 0 | IC1_Inv3 | G5 | G4 | 34 | T97 | Actuator | Actuator fail | Actuator fail | 15:40 | 15:40 | 15:40 | 16:25 | 0 | 0 | 0.75 | 0.75 | 1 No. Nylon brass bush replaced | Close |  |  | 0
77 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:02 | 18:28 | 12.4333 | Actuator Type1 |  | 0 | IC1_Inv4 | G3 | G5 | 73 | T137 | Actuator | Actuator fail | Actuator fail | 8:20 | 8:20 | 8:20 | 9:35 | 0 | 0 | 1.25 | 1.25 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
78 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:02 | 18:28 | 12.4333 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 50 | T30 | Actuator | Actuator fail | Actuator fail | 10:10 | 10:10 | 10:10 | 11:20 | 0 | 0 | 1.1667 | 1.1667 | 1 No Medium Gear Replaced | Close |  |  | 0
79 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 5:58 | 18:35 | 12.6167 | Battery Type_1 |  | 0 | IC1_Inv3 | G3 | G5 | 65 | T97 TO T101 | Battery | Battery Fail | Battery Fail | 9:20 | 9:20 | 9:20 | 12:20 | 0 | 0 | 3 | 3 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
80 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 6:00 | 18:35 | 12.5833 | Actuator Type1 |  | 0 | IC1_Inv2 | G3 | G5 | 56 | T59 | Actuator | Actuator fail | Actuator fail | 8:20 | 8:20 | 8:20 | 10:30 | 0 | 0 | 2.1667 | 2.1667 | 1 No. Nylon brass bush replaced | Close |  |  | 0
81 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 6:00 | 18:35 | 12.5833 | Battery Type_1 |  | 0 | IC1_Inv4 | G5 | G4 | 40 | T122 TO T126 | Battery | Battery Fail | Battery Fail | 12:10 | 12:10 | 12:10 | 13:20 | 0 | 0 | 1.1667 | 1.1667 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
82 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 6:00 | 18:35 | 12.5833 | Battery Type_1 |  | 0 | IC1_Inv2 | G3 | G5 | 54 | T46 TO T50 | Battery | Battery Fail | Battery Fail | 12:45 | 12:45 | 12:45 | 13:40 | 0 | 0 | 0.91667 | 0.91667 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
83 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:38 | 12.6167 | Battery Type_1 |  | 0 | IC1_Inv4 | G3 | G5 | 71 | T126 TO T130 | Battery | Battery Fail | Battery Fail | 9:30 | 9:30 | 9:30 | 10:40 | 0 | 0 | 1.1667 | 1.1667 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
84 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:38 | 12.6167 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 4 | T20 | Actuator | Actuator fail | Actuator fail | 16:20 | 16:20 | 16:20 | 17:10 | 0 | 0 | 0.83333 | 0.83333 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
85 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 6:01 | 18:41 | 12.6667 | Battery Type_1 |  | 0 | IC1_Inv1 | G1 | G3 | 12 | T56 TO T60 | Battery | Battery Fail | Battery Fail | 11:00 | 11:00 | 11:00 | 11:35 | 0 | 0 | 0.58333 | 0.58333 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
86 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 6:01 | 18:41 | 12.6667 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 6 | T30 | Actuator | Actuator fail | Actuator fail | 12:20 | 12:20 | 12:20 | 12:50 | 0 | 0 | 0.5 | 0.5 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
87 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:01 | 17:12 | 11.1833 | Actuator Type1 |  | 0 | IC2_Inv1 | G5 | G4 | 15 | T5 | Actuator | Actuator fail | Actuator fail | 8:10 | 8:10 | 8:10 | 9:25 | 0 | 0 | 1.25 | 1.25 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
88 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 5:59 | 18:40 | 12.6833 | Battery Type_1 |  | 0 | IC2_Inv2 | G3 | G5 | 46 | T6 TO T10 | Battery | Battery Fail | Battery Fail | 9:30 | 9:30 | 9:30 | 10:35 | 0 | 0 | 1.0833 | 1.0833 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
89 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 6:06 | 17:55 | 11.8167 | Battery Type_1 |  | 0 | IC1_Inv2 | G3 | G5 | 55 | T51 TO T55 | Battery | Battery Fail | Battery Fail | 11:10 | 11:10 | 11:10 | 12:10 | 0 | 0 | 1 | 1 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
90 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:01 | 17:50 | 11.8167 | Actuator Type1 |  | 0 | IC2_Inv1 | G5 | G4 | 18 | T16 | Actuator | Actuator fail | Actuator fail | 10:10 | 10:10 | 10:10 | 11:25 | 0 | 0 | 1.25 | 1.25 | 1 No Medium Gear Replaced | Close |  |  | 0
91 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:01 | 17:50 | 11.8167 | Actuator Type1 |  | 0 | IC1_Inv3 | G3 | G5 | 66 | T106 | Actuator | Actuator fail | Actuator fail | 12:20 | 12:20 | 12:20 | 13:25 | 0 | 0 | 1.0833 | 1.0833 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
92 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 6:11 | 18:40 | 12.4833 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G2 | 54 | T31 | Actuator | Actuator fail | Actuator fail | 8:00 | 8:00 | 8:00 | 8:50 | 0 | 0 | 0.83333 | 0.83333 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
93 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 6:11 | 18:40 | 12.4833 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G1 | 35 | T2 | Actuator | Actuator fail | Actuator fail | 9:35 | 9:35 | 9:35 | 10:50 | 0 | 0 | 1.25 | 1.25 | 1 No Actuator Motor | Close |  |  | 0
94 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 6:11 | 18:40 | 12.4833 | Actuator Type1 |  | 0 | IC1_Inv3 | G1 | G3 | 21 | T42 | Actuator | Actuator fail | Actuator fail | 15:30 | 15:30 | 15:30 | 16:45 | 0 | 0 | 1.25 | 1.25 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
95 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 6:06 | 18:38 | 12.5333 | Battery Type_1 |  | 0 | IC2_Inv1 | G7 | G2 | 102 | T31 TO T35 | Battery | Battery Fail | Battery Fail | 15:20 | 15:20 | 15:20 | 16:05 | 0 | 0 | 0.75 | 0.75 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
96 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 6:06 | 18:38 | 12.5333 | Battery Type_1 |  | 0 | IC2_Inv1 | G7 | G1 | 113 | T46 TO T49 | Battery | Battery Fail | Battery Fail | 16:10 | 16:10 | 16:10 | 16:45 | 0 | 0 | 0.58333 | 0.58333 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
97 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 6:06 | 18:41 | 12.5833 | Battery Type_1 |  | 0 | IC1_Inv1 | G1 | G3 | 8 | T36 to T40 | Battery | Battery Fail | Battery Fail | 15:20 | 15:20 | 15:20 | 16:30 | 0 | 0 | 1.1667 | 1.1667 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
98 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 6:09 | 18:44 | 12.5833 | Actuator Type1 |  | 0 | IC1_Inv3 | G3 | G5 | 66 | T106 | Actuator | Actuator fail | Actuator fail | 11:20 | 11:20 | 11:20 | 12:25 | 0 | 0 | 1.0833 | 1.0833 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
99 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:10 | 18:40 | 12.5 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 21 | T32 | Actuator | Actuator fail | Actuator fail | 10:10 | 10:10 | 10:10 | 11:00 | 0 | 0 | 0.83333 | 0.83333 | 1 No Medium Gear Replaced | Close |  |  | 0
100 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:10 | 18:40 | 12.5 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 25 | T51 | Actuator | Actuator fail | Actuator fail | 10:30 | 10:30 | 10:30 | 11:25 | 0 | 0 | 0.91667 | 0.91667 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
101 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:10 | 18:40 | 12.5 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 25 | T52 | Actuator | Actuator fail | Actuator fail | 11:10 | 11:10 | 11:10 | 12:10 | 0 | 0 | 1 | 1 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
102 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 6:07 | 18:47 | 12.6667 | Actuator Type1 |  | 0 | IC1_Inv2 | G4 | G4 | 87 | T51 | Actuator | Actuator fail | Actuator fail | 12:10 | 12:10 | 12:10 | 12:45 | 0 | 0 | 0.58333 | 0.58333 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
103 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 6:09 | 18:43 | 12.5667 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 51 | T32 | Actuator | Actuator fail | Actuator fail | 10:00 | 10:00 | 10:00 | 11:10 | 0 | 0 | 1.1667 | 1.1667 | 1 No Medium Gear Replaced | Close |  |  | 0
104 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 6:09 | 18:43 | 12.5667 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 21 | T32 | Actuator | Actuator fail | Actuator fail | 10:30 | 10:30 | 10:30 | 11:25 | 0 | 0 | 0.91667 | 0.91667 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
105 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 6:09 | 18:43 | 12.5667 | Battery Type_1 |  | 0 | IC1_Inv4 | G3 | G5 | 74 | T146 TO T150 | Battery | Battery Fail | Battery Fail | 12:00 | 12:00 | 12:00 | 12:35 | 0 | 0 | 0.58333 | 0.58333 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
106 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 6:11 | 18:47 | 12.6 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 54 | T47 | Actuator | Actuator fail | Actuator fail | 11:10 | 11:10 | 11:10 | 12:25 | 0 | 0 | 1.25 | 1.25 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
107 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 6:09 | 18:43 | 12.5667 | Actuator Type1 |  | 0 | IC1_Inv2 | G1 | G3 | 10 | T50 | Actuator | Actuator fail | Actuator fail | 13:10 | 13:10 | 13:10 | 14:30 | 0 | 0 | 1.3333 | 1.3333 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
108 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:07 | 18:45 | 12.6333 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G1 | 3 | T15 | Actuator | Actuator fail | Actuator fail | 13:10 | 13:10 | 13:10 | 14:30 | 0 | 0 | 1.3333 | 1.3333 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
109 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:07 | 18:45 | 12.6333 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G2 | 11 | T37 | Actuator | Actuator fail | Actuator fail | 15:32 | 0.64722 | 0.64722 | 16:12 | 0 | 0 | 0.66667 | 0.66667 | 1 No Medium Gear Replaced | Close |  |  | 0
110 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:09 | 18:11 | 12.0333 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G2 | 7 | T31 | Actuator | Actuator fail | Actuator fail | 15:10 | 15:10 | 15:10 | 15:32 | 0 | 0 | 0.36667 | 0.36667 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
111 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:09 | 18:11 | 12.0333 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G1 | 5 | T4 | Actuator | Actuator fail | Actuator fail | 20:20 | 20:20 | 20:20 | 20:34 | 0 | 0 | 0.23333 | 0.23333 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
112 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 6:14 | 18:40 | 12.4333 | Actuator Type1 |  | 0 | IC2_Inv2 | G4 | G5 | 7 | T53 | Actuator | Actuator fail | Actuator fail | 20:20 | 20:20 | 20:20 | 20:34 | 0 | 0 | 0.23333 | 0.23333 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
Formulas:
Days = DAY(EOMONTH(Tracker_BD[[#This Row],[Month Year]],0))

## Plant BD
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affceted Equipment | DC Capacity Affceted (kW) | Plant Equivalent Weightage | Affected Equipmenet Location | Fault Catrgory | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgemnet Time | Work Start time on Fault | Work Completiuon time on fualt | Acknowdlegemnet time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost POA | Approxuimate Energy Loss (KWh) | PTW No. | Job Card No.
1 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 6:28 | 18:29 | 12.0167 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.55903 | 0.55903 | 0.55903 | 0.57083 | 0 | 0 | 0.28333 | 0.28333 | Physically checked & resetted | Close | 0.045017 | 0.26 | 315
2 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:23 | 18:14 | 11.85 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.46875 | 0.46875 | 0.46875 | 0.47431 | 0 | 0 | 0.13333 | 0.13333 | Physically checked & resetted | Close | 0.021185 | 0.1152 | 130
3 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:31 | 18:14 | 11.7167 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.50556 | 0.50556 | 0.50556 | 0.61806 | 0 | 0 | 2.7 | 2.7 | Half Load running due to inverter su 2 side bu current difference | Close | 0.45883 | 2.15 | 3350
4 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:21 | 18:23 | 12.0333 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.36875 | 0.36875 | 0.36875 | 0.46042 | 0 | 0 | 2.2 | 2.2 | Half Load running due to inverter su 2 side bu current difference 2000A Fuse blown replaced | Close | 0.37386 | 2.05 | 2435
5 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:30 | 18:26 | 11.9333 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.39236 | 0.39236 | 0.39236 | 0.43264 | 0 | 0 | 0.96667 | 0.96667 | Half Load running due to inverter su 2 side bu current difference | Close | 0.16427 | 3.02 | 4235
6 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.36736 | 0.36736 | 0.36736 | 0.46528 | 0 | 0 | 2.35 | 2.35 | LCL Filter Replaced | Close | 0.39935 | 2.1 | 2550
7 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:18 | 18:15 | 11.95 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.54306 | 0.54306 | 0.54306 | 0.55208 | 0 | 0 | 0.21667 | 0.21667 | Physically checked & resetted | Close | 0.03682 | 0.2 | 238.1101
8 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:20 | 18:13 | 11.8833 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.6125 | 0.6125 | 0.6125 | 0.63194 | 0 | 0 | 0.46667 | 0.46667 | Physically checked & resetted | Close | 0.074146 | 0.41 | 499.5317
9 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:21 | 18:21 | 12 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.40486 | 0.40486 | 0.40486 | 0.40972 | 0 | 0 | 0.11667 | 0.11667 | Physically checked & resetted | Close | 0.018537 | 0.1 | 124
10 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:20 | 18:27 | 12.1167 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.44167 | 0.44167 | 0.44167 | 0.44792 | 0 | 0 | 0.15 | 0.15 | Physically checked & resetted | Close | 0.023833 | 0.08 | 97
11 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:22 | 18:21 | 11.9833 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.37639 | 0.37639 | 0.37639 | 0.76528 | 0 | 0 | 9.3333 | 9.3333 | Half Load running due to inverter su 2 side bu current difference | Close | 1.5861 | 8 | 4870.56
12 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:20 | 18:20 | 12 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.37361 | 0.37361 | 0.37361 | 0.3875 | 0 | 0 | 0.33333 | 0.33333 | Physically checked & resetted | Close | 0.052962 | 0.2 | 200
13 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:19 | 18:24 | 12.0833 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.44792 | 0.44792 | 0.44792 | 0.63333 | 0 | 0 | 4.45 | 4.45 | 2000A Fuse and AC Contactor CL18 Connector Replaced | Close | 0.75622 | 5.34 | 3251.0988
14 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:09 | 18:24 | 12.25 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.41181 | 0.41181 | 0.41181 | 0.41875 | 0 | 0 | 0.16667 | 0.16667 | Physically checked & resetted | Close | 0.026481 | 0.16 | 190
15 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:05 | 18:33 | 12.4667 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.38542 | 0.38542 | 0.38542 | 0.40417 | 0 | 0 | 0.45 | 0.45 | Physically checked & resetted | Close | 0.071498 | 0.35 | 435
16 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:02 | 18:17 | 12.25 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.49653 | 0.49653 | 0.49653 | 0.50139 | 0 | 0 | 0.11667 | 0.11667 | Physically checked & resetted | Close | 0.018537 | 0.1324 | 158
17 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:03 | 18:32 | 12.4833 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.53056 | 0.53056 | 0.53056 | 0.5375 | 0 | 0 | 0.16667 | 0.16667 | Physically checked & resetted | Close | 0.026481 | 0.123 | 146
18 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:05 | 18:31 | 12.4333 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.53542 | 0.53542 | 0.53542 | 0.54444 | 0 | 0 | 0.21667 | 0.21667 | Physically checked & resetted | Close | 0.034425 | 0.070417 | 85.7936
19 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:05 | 18:31 | 12.4333 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.59861 | 0.59861 | 0.59861 | 0.60486 | 0 | 0 | 0.15 | 0.15 | Physically checked & resetted | Close | 0.023833 | 0.09 | 109.6533
20 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:13 | 18:33 | 12.3333 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.48819 | 0.48819 | 0.48819 | 0.51736 | 0 | 0 | 0.7 | 0.7 | Physically checked & resetted | Close | 0.11122 | 0.7 | 853
21 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:04 | 18:37 | 12.55 | IC1_Inv2 | 1833.3 | 17.45% | IC1_Inv2 | Inverter | Excess Temperature Difference | Excess Temperature Difference | 0.49792 | 0.49792 | 0.49792 | 0.50764 | 0 | 0 | 0.23333 | 0.23333 | Physically checked & resetted | Close | 0.040716 | 0.12 | 135
22 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:04 | 18:20 | 12.2667 | IC1_Inv4 | 892 | 16.99% | IC1_Inv4 | Inverter | Reduced Run | Reduced Run | 0.45347 | 0.45347 | 0.45347 | 0.76389 | 0 | 0 | 7.45 | 7.45 | AC Contactor Replaced | Close | 1.266 | 3.24 | 2300
23 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 6:12 | 18:32 | 12.3333 | IC1_Inv2 | 1833.3 | 17.45% | IC1_Inv2 | Inverter | Excess Temperature Difference | Excess Temperature Difference | 0.51944 | 0.51944 | 0.51944 | 0.52986 | 0 | 0 | 0.25 | 0.25 | Physically checked & resetted | Close | 0.043624 | 0.23 | 312
24 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:10 | 18:31 | 12.35 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.44583 | 0.44583 | 0.44583 | 0.45486 | 0 | 0 | 0.21667 | 0.21667 | Physically checked & resetted | Close | 0.034425 | 0.07 | 90
25 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:06 | 18:07 | 12.0167 | IC1_Inv2 | 1833.3 | 17.45% | IC1_Inv2 | Inverter | Excess Temperature Difference | Excess Temperature Difference | 0.49375 | 0.49375 | 0.49375 | 0.50069 | 0 | 0 | 0.16667 | 0.16667 | Physically checked & resetted | Close | 0.029083 | 0.18 | 245
26 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 6:02 | 18:35 | 12.55 | IC1_Inv2 | 1833.3 | 17.45% | IC1_Inv2 | Inverter | Excess Temperature Difference | Excess Temperature Difference | 0.47153 | 0.47153 | 0.47153 | 0.48125 | 0 | 0 | 0.23333 | 0.23333 | Physically checked & resetted | Close | 0.040716 | 0.15 | 207
27 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:38 | 12.6167 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.62569 | 0.62569 | 0.62569 | 0.63819 | 0 | 0 | 0.3 | 0.3 | Physically checked & resetted | Close | 0.047665 | 0.25 | 320
28 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 6:01 | 18:41 | 12.6667 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.36111 | 0.36111 | 0.36111 | 0.39236 | 0 | 0 | 0.75 | 0.75 | Physically checked & resetted | Close | 0.11916 | 0.58575 | 525
29 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:01 | 17:12 | 11.1833 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.37847 | 0.37847 | 0.37847 | 0.38542 | 0 | 0 | 0.16667 | 0.16667 | Physically checked & resetted | Close | 0.026481 | 0.11633 | 126
30 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:01 | 17:50 | 11.8167 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.54792 | 0.54792 | 0.54792 | 0.55486 | 0 | 0 | 0.16667 | 0.16667 | Physically checked & resetted | Close | 0.026481 | 0.14 | 167.3228
31 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 6:05 | 18:34 | 12.4833 | IC1_Inv2 | 1833.3 | 17.45% | IC1_Inv2 | Inverter | Excess Temperature Difference | Excess Temperature Difference | 0.54236 | 0.54236 | 0.54236 | 0.54931 | 0 | 0 | 0.16667 | 0.16667 | Physically checked & resetted | Close | 0.029083 | 0.084333 | 107.0472
32 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 6:06 | 18:41 | 12.5833 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.36806 | 0.36806 | 0.36806 | 0.39306 | 0 | 0 | 0.6 | 0.6 | Physically checked & resetted | Close | 0.10196 | 0.38 | 462.7369
33 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 30 | 2025-07-04 | 6:07 | 18:39 | 12.5333 | IC1_Inv2 | 1833.3 | 17.45% | IC1_Inv2 | Inverter | Excess Temperature Difference | Excess Temperature Difference | 0.48403 | 0.48403 | 0.48403 | 0.49306 | 0 | 0 | 0.21667 | 0.21667 | Physically checked & resetted | Close | 0.037807 | 0.11 | 147
34 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 30 | 2025-07-07 | 6:10 | 18:48 | 12.6333 | MCR_Battery Charger | 10506.3 | 17.45% | Battery charger | Battery Charger_MCR | Tripped due to Over Voltage | Tripped due to Over Voltage | 0.57292 | 0.57292 | 0.57292 | 0.61458 | 0 | 0 | 1 | 1 | Physically checked & resetted | Close | 0.1745 | 0.4 | 3066
35 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 30 | 2025-07-11 | 6:10 | 18:31 | 12.35 | IC1_Inv2 | 1833.3 | 17.45% | IC1_Inv2 | Inverter | Excess Temperature Difference | Excess Temperature Difference | 0.55069 | 0.55069 | 0.55069 | 0.56181 | 0 | 0 | 0.26667 | 0.26667 | Physically checked & resetted | Close | 0.046532 | 0.22 | 120
36 | [21 empty] | 0 | 0 | 0 | 0
37 | [21 empty] | 0 | 0 | 0 | 0
38 | [21 empty] | 0 | 0 | 0 | 0
39 | [21 empty] | 0 | 0 | 0 | 0
40 | [21 empty] | 0 | 0 | 0 | 0
41 | [21 empty] | 0 | 0 | 0 | 0
42 | [21 empty] | 0 | 0 | 0 | 0
43 | [21 empty] | 0 | 0 | 0 | 0
44 | [21 empty] | 0 | 0 | 0 | 0
45 | [21 empty] | 0 | 0 | 0 | 0
46 | [21 empty] | 0 | 0 | 0 | 0
47 | [21 empty] | 0 | 0 | 0 | 0
48 | [21 empty] | 0 | 0 | 0 | 0
49 | [21 empty] | 0 | 0 | 0 | 0
50 | [21 empty] | 0 | 0 | 0 | 0
51 | [21 empty] | 0 | 0 | 0 | 0
52 | [21 empty] | 0 | 0 | 0 | 0
53 | [21 empty] | 0 | 0 | 0 | 0
54 | [21 empty] | 0 | 0 | 0 | 0
55 | [21 empty] | 0 | 0 | 0 | 0
56 | [21 empty] | 0 | 0 | 0 | 0
57 | [21 empty] | 0 | 0 | 0 | 0
58 | [21 empty] | 0 | 0 | 0 | 0
59 | [21 empty] | 0 | 0 | 0 | 0
60 | [21 empty] | 0 | 0 | 0 | 0
61 | [21 empty] | 0 | 0 | 0 | 0
62 | [21 empty] | 0 | 0 | 0 | 0
63 | [21 empty] | 0 | 0 | 0 | 0
64 | [21 empty] | 0 | 0 | 0 | 0
65 | [21 empty] | 0 | 0 | 0 | 0
66 | [21 empty] | 0 | 0 | 0 | 0
67 | [21 empty] | 0 | 0 | 0 | 0
68 | [21 empty] | 0 | 0 | 0 | 0
69 | [21 empty] | 0 | 0 | 0 | 0
70 | [21 empty] | 0 | 0 | 0 | 0
71 | [21 empty] | 0 | 0 | 0 | 0
72 | [21 empty] | 0 | 0 | 0 | 0
73 | [21 empty] | 0 | 0 | 0 | 0
74 | [21 empty] | 0 | 0 | 0 | 0
75 | [21 empty] | 0 | 0 | 0 | 0
76 | [21 empty] | 0 | 0 | 0 | 0
77 | [21 empty] | 0 | 0 | 0 | 0
78 | [21 empty] | 0 | 0 | 0 | 0
79 | [21 empty] | 0 | 0 | 0 | 0
80 | [21 empty] | 0 | 0 | 0 | 0
81 | [21 empty] | 0 | 0 | 0 | 0
82 | [21 empty] | 0 | 0 | 0 | 0
83 | [21 empty] | 0 | 0 | 0 | 0
84 | [21 empty] | 0 | 0 | 0 | 0
85 | [21 empty] | 0 | 0 | 0 | 0
86 | [21 empty] | 0 | 0 | 0 | 0
87 | [21 empty] | 0 | 0 | 0 | 0
88 | [21 empty] | 0 | 0 | 0 | 0
89 | [21 empty] | 0 | 0 | 0 | 0
90 | [21 empty] | 0 | 0 | 0 | 0
91 | [21 empty] | 0 | 0 | 0 | 0
92 | [21 empty] | 0 | 0 | 0 | 0
93 | [21 empty] | 0 | 0 | 0 | 0
94 | [21 empty] | 0 | 0 | 0 | 0
95 | [21 empty] | 0 | 0 | 0 | 0
96 | [21 empty] | 0 | 0 | 0 | 0
97 | [21 empty] | 0 | 0 | 0 | 0
98 | [21 empty] | 0 | 0 | 0 | 0
99 | [21 empty] | 0 | 0 | 0 | 0
100 | [21 empty] | 0 | 0 | 0 | 0
101 | [21 empty] | 0 | 0 | 0 | 0
102 | [21 empty] | 0 | 0 | 0 | 0
103 | [21 empty] | 0 | 0 | 0 | 0
104 | [21 empty] | 0 | 0 | 0 | 0
105 | [21 empty] | 0 | 0 | 0 | 0
106 | [21 empty] | 0 | 0 | 0 | 0
107 | [21 empty] | 0 | 0 | 0 | 0
108 | [21 empty] | 0 | 0 | 0 | 0
109 | [21 empty] | 0 | 0 | 0 | 0
110 | [21 empty] | 0 | 0 | 0 | 0
111 | [21 empty] | 0 | 0 | 0 | 0
112 | [21 empty] | 0 | 0 | 0 | 0
113 | [21 empty] | 0 | 0 | 0 | 0
114 | [21 empty] | 0 | 0 | 0 | 0
115 | [21 empty] | 0 | 0 | 0 | 0
116 | [21 empty] | 0 | 0 | 0 | 0
117 | [21 empty] | 0 | 0 | 0 | 0
118 | [21 empty] | 0 | 0 | 0 | 0
119 | [21 empty] | 0 | 0 | 0 | 0
120 | [21 empty] | 0 | 0 | 0 | 0
121 | [21 empty] | 0 | 0 | 0 | 0
122 | [21 empty] | 0 | 0 | 0 | 0
123 | [21 empty] | 0 | 0 | 0 | 0
124 | [21 empty] | 0 | 0 | 0 | 0
125 | [21 empty] | 0 | 0 | 0 | 0
126 | [21 empty] | 0 | 0 | 0 | 0
127 | [21 empty] | 0 | 0 | 0 | 0
128 | [21 empty] | 0 | 0 | 0 | 0
129 | [21 empty] | 0 | 0 | 0 | 0
130 | [21 empty] | 0 | 0 | 0 | 0
131 | [21 empty] | 0 | 0 | 0 | 0
132 | [21 empty] | 0 | 0 | 0 | 0
133 | [21 empty] | 0 | 0 | 0 | 0
134 | [21 empty] | 0 | 0 | 0 | 0
135 | [21 empty] | 0 | 0 | 0 | 0
136 | [21 empty] | 0 | 0 | 0 | 0
137 | [21 empty] | 0 | 0 | 0 | 0
138 | [21 empty] | 0 | 0 | 0 | 0
139 | [21 empty] | 0 | 0 | 0 | 0
140 | [21 empty] | 0 | 0 | 0 | 0
141 | [21 empty] | 0 | 0 | 0 | 0
142 | [21 empty] | 0 | 0 | 0 | 0
143 | [21 empty] | 0 | 0 | 0 | 0
144 | [21 empty] | 0 | 0 | 0 | 0
145 | [21 empty] | 0 | 0 | 0 | 0
146 | [21 empty] | 0 | 0 | 0 | 0
147 | [21 empty] | 0 | 0 | 0 | 0
148 | [21 empty] | 0 | 0 | 0 | 0
149 | [21 empty] | 0 | 0 | 0 | 0
150 | [21 empty] | 0 | 0 | 0 | 0
151 | [21 empty] | 0 | 0 | 0 | 0
152 | [21 empty] | 0 | 0 | 0 | 0
153 | [21 empty] | 0 | 0 | 0 | 0
154 | [21 empty] | 0 | 0 | 0 | 0
155 | [21 empty] | 0 | 0 | 0 | 0
156 | [21 empty] | 0 | 0 | 0 | 0
157 | [21 empty] | 0 | 0 | 0 | 0
158 | [21 empty] | 0 | 0 | 0 | 0
159 | [21 empty] | 0 | 0 | 0 | 0
160 | [21 empty] | 0 | 0 | 0 | 0
161 | [21 empty] | 0 | 0 | 0 | 0
162 | [21 empty] | 0 | 0 | 0 | 0
163 | [21 empty] | 0 | 0 | 0 | 0
164 | [21 empty] | 0 | 0 | 0 | 0
165 | [21 empty] | 0 | 0 | 0 | 0
166 | [21 empty] | 0 | 0 | 0 | 0
167 | [21 empty] | 0 | 0 | 0 | 0
168 | [21 empty] | 0 | 0 | 0 | 0
169 | [21 empty] | 0 | 0 | 0 | 0
170 | [21 empty] | 0 | 0 | 0 | 0
171 | [21 empty] | 0 | 0 | 0 | 0
172 | [21 empty] | 0 | 0 | 0 | 0
173 | [21 empty] | 0 | 0 | 0 | 0
174 | [21 empty] | 0 | 0 | 0 | 0
175 | [21 empty] | 0 | 0 | 0 | 0
176 | [21 empty] | 0 | 0 | 0 | 0
177 | [21 empty] | 0 | 0 | 0 | 0
178 | [21 empty] | 0 | 0 | 0 | 0
179 | [21 empty] | 0 | 0 | 0 | 0
180 | [21 empty] | 0 | 0 | 0 | 0
181 | [21 empty] | 0 | 0 | 0 | 0
182 | [21 empty] | 0 | 0 | 0 | 0
183 | [21 empty] | 0 | 0 | 0 | 0
184 | [21 empty] | 0 | 0 | 0 | 0
185 | [21 empty] | 0 | 0 | 0 | 0
186 | [21 empty] | 0 | 0 | 0 | 0
187 | [21 empty] | 0 | 0 | 0 | 0
188 | [21 empty] | 0 | 0 | 0 | 0
189 | [21 empty] | 0 | 0 | 0 | 0
190 | [21 empty] | 0 | 0 | 0 | 0
191 | [21 empty] | 0 | 0 | 0 | 0
192 | [21 empty] | 0 | 0 | 0 | 0
193 | [21 empty] | 0 | 0 | 0 | 0
194 | [21 empty] | 0 | 0 | 0 | 0
195 | [21 empty] | 0 | 0 | 0 | 0
196 | [21 empty] | 0 | 0 | 0 | 0
197 | [21 empty] | 0 | 0 | 0 | 0
198 | [21 empty] | 0 | 0 | 0 | 0
199 | [21 empty] | 0 | 0 | 0 | 0
200 | [21 empty] | 0 | 0 | 0 | 0
201 | [21 empty] | 0 | 0 | 0 | 0
202 | [21 empty] | 0 | 0 | 0 | 0
203 | [21 empty] | 0 | 0 | 0 | 0
204 | [21 empty] | 0 | 0 | 0 | 0
205 | [21 empty] | 0 | 0 | 0 | 0
206 | [21 empty] | 0 | 0 | 0 | 0
207 | [21 empty] | 0 | 0 | 0 | 0
208 | [21 empty] | 0 | 0 | 0 | 0
209 | [21 empty] | 0 | 0 | 0 | 0
210 | [21 empty] | 0 | 0 | 0 | 0
211 | [21 empty] | 0 | 0 | 0 | 0
212 | [21 empty] | 0 | 0 | 0 | 0
213 | [21 empty] | 0 | 0 | 0 | 0
214 | [21 empty] | 0 | 0 | 0 | 0
215 | [21 empty] | 0 | 0 | 0 | 0
216 | [21 empty] | 0 | 0 | 0 | 0
217 | [21 empty] | 0 | 0 | 0 | 0
218 | [21 empty] | 0 | 0 | 0 | 0
219 | [21 empty] | 0 | 0 | 0 | 0
220 | [21 empty] | 0 | 0 | 0 | 0
221 | [21 empty] | 0 | 0 | 0 | 0
222 | [21 empty] | 0 | 0 | 0 | 0
223 | [21 empty] | 0 | 0 | 0 | 0
224 | [21 empty] | 0 | 0 | 0 | 0
225 | [21 empty] | 0 | 0 | 0 | 0
226 | [21 empty] | 0 | 0 | 0 | 0
227 | [21 empty] | 0 | 0 | 0 | 0
228 | [21 empty] | 0 | 0 | 0 | 0
229 | [21 empty] | 0 | 0 | 0 | 0
230 | [21 empty] | 0 | 0 | 0 | 0
231 | [21 empty] | 0 | 0 | 0 | 0
232 | [21 empty] | 0 | 0 | 0 | 0
233 | [21 empty] | 0 | 0 | 0 | 0
234 | [21 empty] | 0 | 0 | 0 | 0
235 | [21 empty] | 0 | 0 | 0 | 0
236 | [21 empty] | 0 | 0 | 0 | 0
237 | [21 empty] | 0 | 0 | 0 | 0
238 | [21 empty] | 0 | 0 | 0 | 0
239 | [21 empty] | 0 | 0 | 0 | 0
240 | [21 empty] | 0 | 0 | 0 | 0
241 | [21 empty] | 0 | 0 | 0 | 0
242 | [21 empty] | 0 | 0 | 0 | 0
243 | [21 empty] | 0 | 0 | 0 | 0
244 | [21 empty] | 0 | 0 | 0 | 0
245 | [21 empty] | 0 | 0 | 0 | 0
246 | [21 empty] | 0 | 0 | 0 | 0
247 | [21 empty] | 0 | 0 | 0 | 0
248 | [21 empty] | 0 | 0 | 0 | 0
249 | [21 empty] | 0 | 0 | 0 | 0
250 | [21 empty] | 0 | 0 | 0 | 0
251 | [21 empty] | 0 | 0 | 0 | 0
252 | [21 empty] | 0 | 0 | 0 | 0
253 | [21 empty] | 0 | 0 | 0 | 0
254 | [21 empty] | 0 | 0 | 0 | 0
255 | [21 empty] | 0 | 0 | 0 | 0
256 | [21 empty] | 0 | 0 | 0 | 0
257 | [21 empty] | 0 | 0 | 0 | 0
258 | [21 empty] | 0 | 0 | 0 | 0
259 | [21 empty] | 0 | 0 | 0 | 0
260 | [21 empty] | 0 | 0 | 0 | 0
261 | [21 empty] | 0 | 0 | 0 | 0
262 | [21 empty] | 0 | 0 | 0 | 0
263 | [21 empty] | 0 | 0 | 0 | 0
264 | [21 empty] | 0 | 0 | 0 | 0
265 | [21 empty] | 0 | 0 | 0 | 0
266 | [21 empty] | 0 | 0 | 0 | 0
267 | [21 empty] | 0 | 0 | 0 | 0
268 | [21 empty] | 0 | 0 | 0 | 0
269 | [21 empty] | 0 | 0 | 0 | 0
270 | [21 empty] | 0 | 0 | 0 | 0
271 | [21 empty] | 0 | 0 | 0 | 0
272 | [21 empty] | 0 | 0 | 0 | 0
273 | [21 empty] | 0 | 0 | 0 | 0
274 | [21 empty] | 0 | 0 | 0 | 0
275 | [21 empty] | 0 | 0 | 0 | 0
276 | [21 empty] | 0 | 0 | 0 | 0
277 | [21 empty] | 0 | 0 | 0 | 0
278 | [21 empty] | 0 | 0 | 0 | 0
279 | [21 empty] | 0 | 0 | 0 | 0
280 | [21 empty] | 0 | 0 | 0 | 0
281 | [21 empty] | 0 | 0 | 0 | 0
282 | [21 empty] | 0 | 0 | 0 | 0
283 | [21 empty] | 0 | 0 | 0 | 0
284 | [21 empty] | 0 | 0 | 0 | 0
285 | [21 empty] | 0 | 0 | 0 | 0
286 | [21 empty] | 0 | 0 | 0 | 0
287 | [21 empty] | 0 | 0 | 0 | 0
288 | [21 empty] | 0 | 0 | 0 | 0
289 | [21 empty] | 0 | 0 | 0 | 0
290 | [21 empty] | 0 | 0 | 0 | 0
291 | [21 empty] | 0 | 0 | 0 | 0
292 | [21 empty] | 0 | 0 | 0 | 0
293 | [21 empty] | 0 | 0 | 0 | 0
294 | [21 empty] | 0 | 0 | 0 | 0
295 | [21 empty] | 0 | 0 | 0 | 0
296 | [21 empty] | 0 | 0 | 0 | 0
297 | [21 empty] | 0 | 0 | 0 | 0
298 | [21 empty] | 0 | 0 | 0 | 0
299 | [21 empty] | 0 | 0 | 0 | 0
300 | [21 empty] | 0 | 0 | 0 | 0
301 | [21 empty] | 0 | 0 | 0 | 0
302 | [21 empty] | 0 | 0 | 0 | 0
303 | [21 empty] | 0 | 0 | 0 | 0
304 | [21 empty] | 0 | 0 | 0 | 0
305 | [21 empty] | 0 | 0 | 0 | 0
306 | [21 empty] | 0 | 0 | 0 | 0
307 | [21 empty] | 0 | 0 | 0 | 0
308 | [21 empty] | 0 | 0 | 0 | 0
309 | [21 empty] | 0 | 0 | 0 | 0
310 | [21 empty] | 0 | 0 | 0 | 0
311 | [21 empty] | 0 | 0 | 0 | 0
312 | [21 empty] | 0 | 0 | 0 | 0
313 | [21 empty] | 0 | 0 | 0 | 0
314 | [21 empty] | 0 | 0 | 0 | 0
315 | [21 empty] | 0 | 0 | 0 | 0
316 | [21 empty] | 0 | 0 | 0 | 0
317 | [21 empty] | 0 | 0 | 0 | 0
318 | [21 empty] | 0 | 0 | 0 | 0
319 | [21 empty] | 0 | 0 | 0 | 0
320 | [21 empty] | 0 | 0 | 0 | 0
321 | [21 empty] | 0 | 0 | 0 | 0
322 | [21 empty] | 0 | 0 | 0 | 0
323 | [21 empty] | 0 | 0 | 0 | 0
324 | [21 empty] | 0 | 0 | 0 | 0
325 | [21 empty] | 0 | 0 | 0 | 0
326 | [21 empty] | 0 | 0 | 0 | 0
327 | [21 empty] | 0 | 0 | 0 | 0
328 | [21 empty] | 0 | 0 | 0 | 0
329 | [21 empty] | 0 | 0 | 0 | 0
330 | [21 empty] | 0 | 0 | 0 | 0
331 | [21 empty] | 0 | 0 | 0 | 0
332 | [21 empty] | 0 | 0 | 0 | 0
333 | [21 empty] | 0 | 0 | 0 | 0
334 | [21 empty] | 0 | 0 | 0 | 0
335 | [21 empty] | 0 | 0 | 0 | 0
336 | [21 empty] | 0 | 0 | 0 | 0
337 | [21 empty] | 0 | 0 | 0 | 0
338 | [21 empty] | 0 | 0 | 0 | 0
339 | [21 empty] | 0 | 0 | 0 | 0
340 | [21 empty] | 0 | 0 | 0 | 0
341 | [21 empty] | 0 | 0 | 0 | 0
342 | [21 empty] | 0 | 0 | 0 | 0
343 | [21 empty] | 0 | 0 | 0 | 0
344 | [21 empty] | 0 | 0 | 0 | 0
345 | [21 empty] | 0 | 0 | 0 | 0
346 | [21 empty] | 0 | 0 | 0 | 0
347 | [21 empty] | 0 | 0 | 0 | 0
348 | [21 empty] | 0 | 0 | 0 | 0
349 | [21 empty] | 0 | 0 | 0 | 0
350 | [21 empty] | 0 | 0 | 0 | 0
351 | [21 empty] | 0 | 0 | 0 | 0
352 | [21 empty] | 0 | 0 | 0 | 0
353 | [21 empty] | 0 | 0 | 0 | 0
354 | [21 empty] | 0 | 0 | 0 | 0
355 | [21 empty] | 0 | 0 | 0 | 0
356 | [21 empty] | 0 | 0 | 0 | 0
357 | [21 empty] | 0 | 0 | 0 | 0
358 | [21 empty] | 0 | 0 | 0 | 0
359 | [21 empty] | 0 | 0 | 0 | 0
360 | [21 empty] | 0 | 0 | 0 | 0
361 | [21 empty] | 0 | 0 | 0 | 0
362 | [21 empty] | 0 | 0 | 0 | 0
363 | [21 empty] | 0 | 0 | 0 | 0
364 | [21 empty] | 0 | 0 | 0 | 0
365 | [21 empty] | 0 | 0 | 0 | 0
366 | [21 empty] | 0 | 0 | 0 | 0
367 | [21 empty] | 0 | 0 | 0 | 0
368 | [21 empty] | 0 | 0 | 0 | 0
369 | [21 empty] | 0 | 0 | 0 | 0
370 | [21 empty] | 0 | 0 | 0 | 0
371 | [21 empty] | 0 | 0 | 0 | 0
372 | [21 empty] | 0 | 0 | 0 | 0
373 | [21 empty] | 0 | 0 | 0 | 0
374 | [21 empty] | 0 | 0 | 0 | 0
375 | [21 empty] | 0 | 0 | 0 | 0
376 | [21 empty] | 0 | 0 | 0 | 0
377 | [21 empty] | 0 | 0 | 0 | 0
378 | [21 empty] | 0 | 0 | 0 | 0
379 | [21 empty] | 0 | 0 | 0 | 0
380 | [21 empty] | 0 | 0 | 0 | 0
381 | [21 empty] | 0 | 0 | 0 | 0
382 | [21 empty] | 0 | 0 | 0 | 0
383 | [21 empty] | 0 | 0 | 0 | 0
384 | [21 empty] | 0 | 0 | 0 | 0
385 | [21 empty] | 0 | 0 | 0 | 0
386 | [21 empty] | 0 | 0 | 0 | 0
387 | [21 empty] | 0 | 0 | 0 | 0
388 | [21 empty] | 0 | 0 | 0 | 0
389 | [21 empty] | 0 | 0 | 0 | 0
390 | [21 empty] | 0 | 0 | 0 | 0
391 | [21 empty] | 0 | 0 | 0 | 0
392 | [21 empty] | 0 | 0 | 0 | 0
393 | [21 empty] | 0 | 0 | 0 | 0
394 | [21 empty] | 0 | 0 | 0 | 0
395 | [21 empty] | 0 | 0 | 0 | 0
396 | [21 empty] | 0 | 0 | 0 | 0
397 | [21 empty] | 0 | 0 | 0 | 0
398 | [21 empty] | 0 | 0 | 0 | 0
399 | [21 empty] | 0 | 0 | 0 | 0

## Grid BD
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affceted Equipment | DC Capacity Affceted (kW) | Affected Equipmenet Location | Fault Catrgory | Plant Equivalent Weightage | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgemnet Time | Work Start time on Fault | Work Completiuon time on fualt | Acknowdlegemnet time | Response Time | Resolution Time | Action taken | Status | Plant Equivalent breakdown | Lost POA | Approxuimate Energy Loss (KWh)
1 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:10 | 18:31 | 12.35 |  | 10507 |  | Grid System | 100% |  | Grid failure due to 220 kV main supply failure | 0.25694 | 0.25694 | 0.25694 | 0.49028 | 0 | 0 | 5.6 |  |  | 5.6 | 2.9 | 2523
2 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:04 | 18:20 | 12.2667 |  | 10507 |  | Grid System | 100% |  | Grid failure due to 220 kV main supply failure | 0.43194 | 0.43194 | 0.43194 | 0.45486 | 0 | 0 | 0.55 |  |  | 0.55 | 0.27 | 543
3 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 6:12 | 18:32 | 12.3333 |  | 10507 |  | Grid System | 100% |  | Grid failure due to 220 kV main supply failure | 0.55278 | 0.55278 | 0.55278 | 0.57083 | 0 | 0 | 0.43333 |  |  | 0.43333 | 0.15 | 657
4 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 2025-06-05 | 6:00 | 18:35 | 12.5833 |  | 10507 |  | Grid System | 100% |  | Grid failure due to 220 kV main supply failure | 0.71042 | 0.71042 | 0.71042 | 0.77431 | 0 | 0 | 1.5333 |  |  | 1.5333 | 0.17 | 835
5 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 2025-06-10 | 5:59 | 18:40 | 12.6833 |  | 10507 |  | Grid System | 100% |  | Grid failure due to 220 kV main supply failure | 0.61042 | 0.61042 | 0.61042 | 0.66458 | 0 | 0 | 1.3 |  |  | 1.3 | 0.8177 | 2435
6 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 2025-06-22 | 6:04 | 18:41 | 12.6167 |  | 10507 |  | Grid System | 100% |  | Grid failure due to 220 kV main supply failure for Quaterly mainteance | 0.41597 | 0.41597 | 0.41597 | 0.71875 | 0 | 0 | 7.2667 |  |  | 7.2667 | 3.42 | 27123
7 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:07 | 18:39 | 12.5333 |  | 10507 |  | Grid System | 100% |  | Shut down taken from22okV KPTCL Substatio Achepalya for Tower repair work | 0.38194 | 0.38194 | 0.38194 | 0.40764 | 0 | 0 | 0.61667 |  |  | 0.61667
8 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:07 | 18:39 | 12.5333 |  | 10507 |  | Grid System | 100% |  | Shut down taken from22okV KPTCL Substatio Achepalya for Tower repair work | 0.69792 | 0.69792 | 0.69792 | 0.71181 | 0 | 0 | 0.33333 |  |  | 0.33333
9 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:09 | 18:11 | 12.0333 |  | 10507 |  | Grid System | 100% |  | Grid failure from 66kv Chowdankuppe station for relay replacement work | 0.50208 | 0.50208 | 0.50208 | 0.51389 | 0 | 0 | 0.28333 |  |  | 0.28333
10 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:09 | 18:11 | 12.0333 |  | 10507 |  | Grid System | 100% |  | Grid failure from 66kv Chowdankuppe station for relay replacement work | 0.55 | 0.55 | 0.55 | 0.56736 | 0 | 0 | 0.41667 |  |  | 0.41667
11 | [26 empty] | 0
12 | [26 empty] | 0
13 | [26 empty] | 0
14 | [26 empty] | 0
15 | [26 empty] | 0
16 | [26 empty] | 0
17 | [26 empty] | 0
18 | [26 empty] | 0
19 | [26 empty] | 0
20 | [26 empty] | 0
21 | [26 empty] | 0
22 | [26 empty] | 0
23 | [26 empty] | 0
24 | [26 empty] | 0
25 | [26 empty] | 0
26 | [26 empty] | 0
27 | [26 empty] | 0
28 | [26 empty] | 0
29 | [26 empty] | 0
30 | [26 empty] | 0
31 | [26 empty] | 0
32 | [26 empty] | 0
33 | [26 empty] | 0
34 | [26 empty] | 0
35 | [26 empty] | 0
36 | [26 empty] | 0
37 | [26 empty] | 0
38 | [26 empty] | 0
39 | [26 empty] | 0
40 | [26 empty] | 0
41 | [26 empty] | 0
42 | [26 empty] | 0
43 | [26 empty] | 0
44 | [26 empty] | 0
45 | [26 empty] | 0
46 | [26 empty] | 0
47 | [26 empty] | 0
48 | [26 empty] | 0
49 | [26 empty] | 0
50 | [26 empty] | 0
51 | [26 empty] | 0
52 | [26 empty] | 0
53 | [26 empty] | 0
54 | [26 empty] | 0
55 | [26 empty] | 0
56 | [26 empty] | 0
57 | [26 empty] | 0
58 | [26 empty] | 0
59 | [26 empty] | 0
60 | [26 empty] | 0
61 | [26 empty] | 0
62 | [26 empty] | 0
63 | [26 empty] | 0
64 | [26 empty] | 0
65 | [26 empty] | 0
66 | [26 empty] | 0
67 | [26 empty] | 0
68 | [26 empty] | 0
69 | [26 empty] | 0
70 | [26 empty] | 0
71 | [26 empty] | 0
72 | [26 empty] | 0
73 | [26 empty] | 0
74 | [26 empty] | 0
75 | [26 empty] | 0
76 | [26 empty] | 0
77 | [26 empty] | 0
78 | [26 empty] | 0
79 | [26 empty] | 0
80 | [26 empty] | 0
81 | [26 empty] | 0
82 | [26 empty] | 0
83 | [26 empty] | 0
84 | [26 empty] | 0
85 | [26 empty] | 0
86 | [26 empty] | 0
87 | [26 empty] | 0
88 | [26 empty] | 0
89 | [26 empty] | 0
90 | [26 empty] | 0
91 | [26 empty] | 0
92 | [26 empty] | 0
93 | [26 empty] | 0
94 | [26 empty] | 0
95 | [26 empty] | 0
96 | [26 empty] | 0
97 | [26 empty] | 0
98 | [26 empty] | 0
99 | [26 empty] | 0
100 | [26 empty] | 0
101 | [26 empty] | 0
102 | [26 empty] | 0
103 | [26 empty] | 0
104 | [26 empty] | 0
105 | [26 empty] | 0
106 | [26 empty] | 0
107 | [26 empty] | 0
108 | [26 empty] | 0
109 | [26 empty] | 0
110 | [26 empty] | 0
111 | [26 empty] | 0
112 | [26 empty] | 0
113 | [26 empty] | 0
114 | [26 empty] | 0
115 | [26 empty] | 0
116 | [26 empty] | 0
117 | [26 empty] | 0
118 | [26 empty] | 0
119 | [26 empty] | 0
120 | [26 empty] | 0
121 | [26 empty] | 0
122 | [26 empty] | 0
123 | [26 empty] | 0
124 | [26 empty] | 0
125 | [26 empty] | 0
126 | [26 empty] | 0
127 | [26 empty] | 0
128 | [26 empty] | 0
129 | [26 empty] | 0
130 | [26 empty] | 0
131 | [26 empty] | 0
132 | [26 empty] | 0
133 | [26 empty] | 0
134 | [26 empty] | 0
135 | [26 empty] | 0
136 | [26 empty] | 0
137 | [26 empty] | 0
138 | [26 empty] | 0
139 | [26 empty] | 0
140 | [26 empty] | 0
141 | [26 empty] | 0
142 | [26 empty] | 0
143 | [26 empty] | 0
144 | [26 empty] | 0
145 | [26 empty] | 0
146 | [26 empty] | 0
147 | [26 empty] | 0
148 | [26 empty] | 0
149 | [26 empty] | 0
150 | [26 empty] | 0
151 | [26 empty] | 0
152 | [26 empty] | 0
153 | [26 empty] | 0
154 | [26 empty] | 0
155 | [26 empty] | 0
156 | [26 empty] | 0
157 | [26 empty] | 0
158 | [26 empty] | 0
159 | [26 empty] | 0
160 | [26 empty] | 0
161 | [26 empty] | 0
162 | [26 empty] | 0
163 | [26 empty] | 0
164 | [26 empty] | 0
165 | [26 empty] | 0
166 | [26 empty] | 0
167 | [26 empty] | 0
168 | [26 empty] | 0
169 | [26 empty] | 0
170 | [26 empty] | 0
171 | [26 empty] | 0
172 | [26 empty] | 0
173 | [26 empty] | 0
174 | [26 empty] | 0
175 | [26 empty] | 0
176 | [26 empty] | 0
177 | [26 empty] | 0
178 | [26 empty] | 0
179 | [26 empty] | 0
180 | [26 empty] | 0
181 | [26 empty] | 0
182 | [26 empty] | 0
183 | [26 empty] | 0
184 | [26 empty] | 0
185 | [26 empty] | 0
186 | [26 empty] | 0
187 | [26 empty] | 0
188 | [26 empty] | 0
189 | [26 empty] | 0
190 | [26 empty] | 0
191 | [26 empty] | 0
192 | [26 empty] | 0
193 | [26 empty] | 0
194 | [26 empty] | 0
195 | [26 empty] | 0
196 | [26 empty] | 0
197 | [26 empty] | 0
198 | [26 empty] | 0
199 | [26 empty] | 0
200 | [26 empty] | 0
201 | [26 empty] | 0
202 | [26 empty] | 0
203 | [26 empty] | 0
204 | [26 empty] | 0
205 | [26 empty] | 0
206 | [26 empty] | 0
207 | [26 empty] | 0
208 | [26 empty] | 0
209 | [26 empty] | 0
210 | [26 empty] | 0
211 | [26 empty] | 0
212 | [26 empty] | 0
213 | [26 empty] | 0
214 | [26 empty] | 0
215 | [26 empty] | 0
216 | [26 empty] | 0
217 | [26 empty] | 0
218 | [26 empty] | 0
219 | [26 empty] | 0
220 | [26 empty] | 0
221 | [26 empty] | 0
222 | [26 empty] | 0
223 | [26 empty] | 0
224 | [26 empty] | 0
225 | [26 empty] | 0
226 | [26 empty] | 0
227 | [26 empty] | 0
228 | [26 empty] | 0
229 | [26 empty] | 0
230 | [26 empty] | 0
231 | [26 empty] | 0
232 | [26 empty] | 0
233 | [26 empty] | 0
234 | [26 empty] | 0
235 | [26 empty] | 0
236 | [26 empty] | 0
237 | [26 empty] | 0
238 | [26 empty] | 0
239 | [26 empty] | 0
240 | [26 empty] | 0
241 | [26 empty] | 0
242 | [26 empty] | 0
243 | [26 empty] | 0
244 | [26 empty] | 0
245 | [26 empty] | 0
246 | [26 empty] | 0
247 | [26 empty] | 0
248 | [26 empty] | 0
249 | [26 empty] | 0
250 | [26 empty] | 0
251 | [26 empty] | 0
252 | [26 empty] | 0
253 | [26 empty] | 0
254 | [26 empty] | 0
255 | [26 empty] | 0
256 | [26 empty] | 0
257 | [26 empty] | 0
258 | [26 empty] | 0
259 | [26 empty] | 0
260 | [26 empty] | 0
261 | [26 empty] | 0
262 | [26 empty] | 0
263 | [26 empty] | 0
264 | [26 empty] | 0
265 | [26 empty] | 0
266 | [26 empty] | 0
267 | [26 empty] | 0
268 | [26 empty] | 0
269 | [26 empty] | 0
270 | [26 empty] | 0
271 | [26 empty] | 0
272 | [26 empty] | 0
273 | [26 empty] | 0
274 | [26 empty] | 0
275 | [26 empty] | 0
276 | [26 empty] | 0
277 | [26 empty] | 0
278 | [26 empty] | 0
279 | [26 empty] | 0
280 | [26 empty] | 0
281 | [26 empty] | 0
282 | [26 empty] | 0
283 | [26 empty] | 0
284 | [26 empty] | 0
285 | [26 empty] | 0
286 | [26 empty] | 0
287 | [26 empty] | 0
288 | [26 empty] | 0
289 | [26 empty] | 0
290 | [26 empty] | 0
291 | [26 empty] | 0
292 | [26 empty] | 0
293 | [26 empty] | 0
294 | [26 empty] | 0
295 | [26 empty] | 0
296 | [26 empty] | 0
297 | [26 empty] | 0
298 | [26 empty] | 0
299 | [26 empty] | 0
300 | [26 empty] | 0
301 | [26 empty] | 0
302 | [26 empty] | 0
303 | [26 empty] | 0
304 | [26 empty] | 0
305 | [26 empty] | 0
306 | [26 empty] | 0
307 | [26 empty] | 0
308 | [26 empty] | 0
309 | [26 empty] | 0
310 | [26 empty] | 0
311 | [26 empty] | 0
312 | [26 empty] | 0
313 | [26 empty] | 0
314 | [26 empty] | 0
315 | [26 empty] | 0
316 | [26 empty] | 0
317 | [26 empty] | 0
318 | [26 empty] | 0
319 | [26 empty] | 0
320 | [26 empty] | 0
321 | [26 empty] | 0
322 | [26 empty] | 0
323 | [26 empty] | 0
324 | [26 empty] | 0
325 | [26 empty] | 0
326 | [26 empty] | 0
327 | [26 empty] | 0
328 | [26 empty] | 0
329 | [26 empty] | 0
330 | [26 empty] | 0
331 | [26 empty] | 0
332 | [26 empty] | 0
333 | [26 empty] | 0
334 | [26 empty] | 0
335 | [26 empty] | 0
336 | [26 empty] | 0
337 | [26 empty] | 0
338 | [26 empty] | 0
339 | [26 empty] | 0
340 | [26 empty] | 0
341 | [26 empty] | 0
342 | [26 empty] | 0
343 | [26 empty] | 0
344 | [26 empty] | 0
345 | [26 empty] | 0
346 | [26 empty] | 0
347 | [26 empty] | 0
348 | [26 empty] | 0
349 | [26 empty] | 0
350 | [26 empty] | 0
351 | [26 empty] | 0
352 | [26 empty] | 0
353 | [26 empty] | 0
354 | [26 empty] | 0
355 | [26 empty] | 0
356 | [26 empty] | 0
357 | [26 empty] | 0
358 | [26 empty] | 0
359 | [26 empty] | 0
360 | [26 empty] | 0
361 | [26 empty] | 0
362 | [26 empty] | 0
363 | [26 empty] | 0
364 | [26 empty] | 0
365 | [26 empty] | 0
366 | [26 empty] | 0
367 | [26 empty] | 0
368 | [26 empty] | 0
369 | [26 empty] | 0
370 | [26 empty] | 0
371 | [26 empty] | 0
372 | [26 empty] | 0
373 | [26 empty] | 0
374 | [26 empty] | 0
375 | [26 empty] | 0
376 | [26 empty] | 0
377 | [26 empty] | 0
378 | [26 empty] | 0
379 | [26 empty] | 0
380 | [26 empty] | 0
381 | [26 empty] | 0
382 | [26 empty] | 0
383 | [26 empty] | 0
384 | [26 empty] | 0
385 | [26 empty] | 0
386 | [26 empty] | 0
387 | [26 empty] | 0
388 | [26 empty] | 0
389 | [26 empty] | 0
390 | [26 empty] | 0
391 | [26 empty] | 0
392 | [26 empty] | 0
393 | [26 empty] | 0
394 | [26 empty] | 0
395 | [26 empty] | 0
396 | [26 empty] | 0
397 | [26 empty] | 0
398 | [26 empty] | 0
399 | [26 empty] | 0
400 | [26 empty] | 0
401 | [26 empty] | 0
402 | [26 empty] | 0
403 | [26 empty] | 0
404 | [26 empty] | 0
405 | [26 empty] | 0
406 | [26 empty] | 0
407 | [26 empty] | 0
408 | [26 empty] | 0
409 | [26 empty] | 0
410 | [26 empty] | 0
411 | [26 empty] | 0
412 | [26 empty] | 0
413 | [26 empty] | 0
414 | [26 empty] | 0
415 | [26 empty] | 0
416 | [26 empty] | 0
417 | [26 empty] | 0
418 | [26 empty] | 0
419 | [26 empty] | 0
420 | [26 empty] | 0
421 | [26 empty] | 0
422 | [26 empty] | 0
423 | [26 empty] | 0
424 | [26 empty] | 0
425 | [26 empty] | 0
426 | [26 empty] | 0
427 | [26 empty] | 0
428 | [26 empty] | 0
429 | [26 empty] | 0
430 | [26 empty] | 0
431 | [26 empty] | 0
432 | [26 empty] | 0
433 | [26 empty] | 0
434 | [26 empty] | 0
435 | [26 empty] | 0
436 | [26 empty] | 0
437 | [26 empty] | 0
438 | [26 empty] | 0
439 | [26 empty] | 0
440 | [26 empty] | 0
441 | [26 empty] | 0
442 | [26 empty] | 0
443 | [26 empty] | 0
444 | [26 empty] | 0
445 | [26 empty] | 0
446 | [26 empty] | 0
447 | [26 empty] | 0
448 | [26 empty] | 0
449 | [26 empty] | 0
450 | [26 empty] | 0
451 | [26 empty] | 0
452 | [26 empty] | 0
453 | [26 empty] | 0
454 | [26 empty] | 0
455 | [26 empty] | 0
456 | [26 empty] | 0
457 | [26 empty] | 0
458 | [26 empty] | 0
459 | [26 empty] | 0
460 | [26 empty] | 0
461 | [26 empty] | 0
462 | [26 empty] | 0
463 | [26 empty] | 0
464 | [26 empty] | 0
465 | [26 empty] | 0
466 | [26 empty] | 0
467 | [26 empty] | 0
468 | [26 empty] | 0
469 | [26 empty] | 0
470 | [26 empty] | 0
471 | [26 empty] | 0
472 | [26 empty] | 0
473 | [26 empty] | 0
474 | [26 empty] | 0
475 | [26 empty] | 0
476 | [26 empty] | 0
477 | [26 empty] | 0
478 | [26 empty] | 0
479 | [26 empty] | 0
480 | [26 empty] | 0
481 | [26 empty] | 0
482 | [26 empty] | 0
483 | [26 empty] | 0
484 | [26 empty] | 0
485 | [26 empty] | 0
486 | [26 empty] | 0
487 | [26 empty] | 0
488 | [26 empty] | 0
489 | [26 empty] | 0
490 | [26 empty] | 0
491 | [26 empty] | 0
492 | [26 empty] | 0
493 | [26 empty] | 0
494 | [26 empty] | 0
495 | [26 empty] | 0
496 | [26 empty] | 0
497 | [26 empty] | 0
498 | [26 empty] | 0
499 | [26 empty] | 0
500 | [26 empty] | 0
501 | [26 empty] | 0
502 | [26 empty] | 0
503 | [26 empty] | 0
504 | [26 empty] | 0
505 | [26 empty] | 0
506 | [26 empty] | 0
507 | [26 empty] | 0
508 | [26 empty] | 0
509 | [26 empty] | 0
510 | [26 empty] | 0
511 | [26 empty] | 0
512 | [26 empty] | 0
513 | [26 empty] | 0
514 | [26 empty] | 0
515 | [26 empty] | 0
516 | [26 empty] | 0
517 | [26 empty] | 0
518 | [26 empty] | 0
519 | [26 empty] | 0
520 | [26 empty] | 0
521 | [26 empty] | 0
522 | [26 empty] | 0
523 | [26 empty] | 0
524 | [26 empty] | 0
525 | [26 empty] | 0
526 | [26 empty] | 0
527 | [26 empty] | 0
528 | [26 empty] | 0
529 | [26 empty] | 0
530 | [26 empty] | 0
531 | [26 empty] | 0
532 | [26 empty] | 0
533 | [26 empty] | 0
534 | [26 empty] | 0
535 | [26 empty] | 0
536 | [26 empty] | 0
537 | [26 empty] | 0
538 | [26 empty] | 0
539 | [26 empty] | 0
540 | [26 empty] | 0
541 | [26 empty] | 0
542 | [26 empty] | 0
543 | [26 empty] | 0
544 | [26 empty] | 0
545 | [26 empty] | 0
546 | [26 empty] | 0
547 | [26 empty] | 0
548 | [26 empty] | 0
549 | [26 empty] | 0
550 | [26 empty] | 0
551 | [26 empty] | 0
552 | [26 empty] | 0
553 | [26 empty] | 0
554 | [26 empty] | 0
555 | [26 empty] | 0
556 | [26 empty] | 0
557 | [26 empty] | 0
558 | [26 empty] | 0
559 | [26 empty] | 0
560 | [26 empty] | 0
561 | [26 empty] | 0
562 | [26 empty] | 0
563 | [26 empty] | 0
564 | [26 empty] | 0
565 | [26 empty] | 0
566 | [26 empty] | 0
567 | [26 empty] | 0
568 | [26 empty] | 0
569 | [26 empty] | 0
570 | [26 empty] | 0
571 | [26 empty] | 0
572 | [26 empty] | 0
573 | [26 empty] | 0
574 | [26 empty] | 0
575 | [26 empty] | 0
576 | [26 empty] | 0
577 | [26 empty] | 0
578 | [26 empty] | 0
579 | [26 empty] | 0
580 | [26 empty] | 0
581 | [26 empty] | 0
582 | [26 empty] | 0
583 | [26 empty] | 0
584 | [26 empty] | 0
585 | [26 empty] | 0
586 | [26 empty] | 0
587 | [26 empty] | 0
588 | [26 empty] | 0
589 | [26 empty] | 0
590 | [26 empty] | 0
591 | [26 empty] | 0
592 | [26 empty] | 0
593 | [26 empty] | 0
594 | [26 empty] | 0
595 | [26 empty] | 0
596 | [26 empty] | 0
597 | [26 empty] | 0
598 | [26 empty] | 0
599 | [26 empty] | 0
600 | [26 empty] | 0
601 | [26 empty] | 0
602 | [26 empty] | 0
603 | [26 empty] | 0
604 | [26 empty] | 0
605 | [26 empty] | 0
606 | [26 empty] | 0
607 | [26 empty] | 0
608 | [26 empty] | 0
609 | [26 empty] | 0
610 | [26 empty] | 0
611 | [26 empty] | 0
612 | [26 empty] | 0
613 | [26 empty] | 0
614 | [26 empty] | 0
615 | [26 empty] | 0
616 | [26 empty] | 0
617 | [26 empty] | 0
618 | [26 empty] | 0
619 | [26 empty] | 0
620 | [26 empty] | 0
621 | [26 empty] | 0
622 | [26 empty] | 0
623 | [26 empty] | 0
624 | [26 empty] | 0
625 | [26 empty] | 0
626 | [26 empty] | 0
627 | [26 empty] | 0
628 | [26 empty] | 0
629 | [26 empty] | 0
630 | [26 empty] | 0
631 | [26 empty] | 0
632 | [26 empty] | 0
633 | [26 empty] | 0
634 | [26 empty] | 0
635 | [26 empty] | 0
636 | [26 empty] | 0
637 | [26 empty] | 0
638 | [26 empty] | 0
639 | [26 empty] | 0
640 | [26 empty] | 0
641 | [26 empty] | 0
642 | [26 empty] | 0
643 | [26 empty] | 0
644 | [26 empty] | 0
645 | [26 empty] | 0
646 | [26 empty] | 0
647 | [26 empty] | 0
648 | [26 empty] | 0
649 | [26 empty] | 0
650 | [26 empty] | 0
651 | [26 empty] | 0
652 | [26 empty] | 0
653 | [26 empty] | 0
654 | [26 empty] | 0
655 | [26 empty] | 0
656 | [26 empty] | 0
657 | [26 empty] | 0
658 | [26 empty] | 0
659 | [26 empty] | 0
660 | [26 empty] | 0
661 | [26 empty] | 0
662 | [26 empty] | 0
663 | [26 empty] | 0
664 | [26 empty] | 0
665 | [26 empty] | 0
666 | [26 empty] | 0
667 | [26 empty] | 0
668 | [26 empty] | 0
669 | [26 empty] | 0
670 | [26 empty] | 0
671 | [26 empty] | 0
672 | [26 empty] | 0
673 | [26 empty] | 0
674 | [26 empty] | 0
675 | [26 empty] | 0
676 | [26 empty] | 0
677 | [26 empty] | 0
678 | [26 empty] | 0
679 | [26 empty] | 0
680 | [26 empty] | 0
681 | [26 empty] | 0
682 | [26 empty] | 0
683 | [26 empty] | 0
684 | [26 empty] | 0
685 | [26 empty] | 0
686 | [26 empty] | 0
687 | [26 empty] | 0
688 | [26 empty] | 0
689 | [26 empty] | 0
690 | [26 empty] | 0
691 | [26 empty] | 0
692 | [26 empty] | 0
693 | [26 empty] | 0
694 | [26 empty] | 0
695 | [26 empty] | 0
696 | [26 empty] | 0
697 | [26 empty] | 0
698 | [26 empty] | 0
699 | [26 empty] | 0
700 | [26 empty] | 0
701 | [26 empty] | 0
702 | [26 empty] | 0
703 | [26 empty] | 0
704 | [26 empty] | 0
705 | [26 empty] | 0
706 | [26 empty] | 0
707 | [26 empty] | 0
708 | [26 empty] | 0
709 | [26 empty] | 0
710 | [26 empty] | 0
711 | [26 empty] | 0
712 | [26 empty] | 0
713 | [26 empty] | 0
714 | [26 empty] | 0
715 | [26 empty] | 0
716 | [26 empty] | 0
717 | [26 empty] | 0
718 | [26 empty] | 0
719 | [26 empty] | 0
720 | [26 empty] | 0
721 | [26 empty] | 0
722 | [26 empty] | 0
723 | [26 empty] | 0
724 | [26 empty] | 0
725 | [26 empty] | 0
726 | [26 empty] | 0
727 | [26 empty] | 0
728 | [26 empty] | 0
729 | [26 empty] | 0
730 | [26 empty] | 0
731 | [26 empty] | 0
732 | [26 empty] | 0
733 | [26 empty] | 0
734 | [26 empty] | 0
735 | [26 empty] | 0
736 | [26 empty] | 0
737 | [26 empty] | 0
738 | [26 empty] | 0
739 | [26 empty] | 0
740 | [26 empty] | 0
741 | [26 empty] | 0
742 | [26 empty] | 0
743 | [26 empty] | 0
744 | [26 empty] | 0
745 | [26 empty] | 0
746 | [26 empty] | 0
747 | [26 empty] | 0
748 | [26 empty] | 0
749 | [26 empty] | 0
750 | [26 empty] | 0
751 | [26 empty] | 0
752 | [26 empty] | 0
753 | [26 empty] | 0
754 | [26 empty] | 0
755 | [26 empty] | 0
756 | [26 empty] | 0
757 | [26 empty] | 0
758 | [26 empty] | 0
759 | [26 empty] | 0
760 | [26 empty] | 0
761 | [26 empty] | 0
762 | [26 empty] | 0
763 | [26 empty] | 0
764 | [26 empty] | 0
765 | [26 empty] | 0
766 | [26 empty] | 0
767 | [26 empty] | 0
768 | [26 empty] | 0
769 | [26 empty] | 0
770 | [26 empty] | 0
771 | [26 empty] | 0
772 | [26 empty] | 0
773 | [26 empty] | 0
774 | [26 empty] | 0
775 | [26 empty] | 0
776 | [26 empty] | 0
777 | [26 empty] | 0
778 | [26 empty] | 0
779 | [26 empty] | 0
780 | [26 empty] | 0
781 | [26 empty] | 0
782 | [26 empty] | 0
783 | [26 empty] | 0
784 | [26 empty] | 0
785 | [26 empty] | 0
786 | [26 empty] | 0
787 | [26 empty] | 0
788 | [26 empty] | 0
789 | [26 empty] | 0
790 | [26 empty] | 0
791 | [26 empty] | 0
792 | [26 empty] | 0
793 | [26 empty] | 0
794 | [26 empty] | 0
795 | [26 empty] | 0
796 | [26 empty] | 0
797 | [26 empty] | 0
798 | [26 empty] | 0
799 | [26 empty] | 0
800 | [26 empty] | 0
801 | [26 empty] | 0
802 | [26 empty] | 0
803 | [26 empty] | 0
804 | [26 empty] | 0
805 | [26 empty] | 0
806 | [26 empty] | 0
807 | [26 empty] | 0
808 | [26 empty] | 0
809 | [26 empty] | 0
810 | [26 empty] | 0
811 | [26 empty] | 0
812 | [26 empty] | 0
813 | [26 empty] | 0
814 | [26 empty] | 0
815 | [26 empty] | 0
816 | [26 empty] | 0
817 | [26 empty] | 0
818 | [26 empty] | 0
819 | [26 empty] | 0
820 | [26 empty] | 0
821 | [26 empty] | 0
822 | [26 empty] | 0
823 | [26 empty] | 0
824 | [26 empty] | 0
825 | [26 empty] | 0
826 | [26 empty] | 0
827 | [26 empty] | 0
828 | [26 empty] | 0
829 | [26 empty] | 0
830 | [26 empty] | 0
831 | [26 empty] | 0
832 | [26 empty] | 0
833 | [26 empty] | 0
834 | [26 empty] | 0
835 | [26 empty] | 0
836 | [26 empty] | 0
837 | [26 empty] | 0
838 | [26 empty] | 0
839 | [26 empty] | 0
840 | [26 empty] | 0
841 | [26 empty] | 0
842 | [26 empty] | 0
843 | [26 empty] | 0
844 | [26 empty] | 0
845 | [26 empty] | 0
846 | [26 empty] | 0
847 | [26 empty] | 0
848 | [26 empty] | 0
849 | [26 empty] | 0
850 | [26 empty] | 0
851 | [26 empty] | 0
852 | [26 empty] | 0
853 | [26 empty] | 0
854 | [26 empty] | 0
855 | [26 empty] | 0
856 | [26 empty] | 0
857 | [26 empty] | 0
858 | [26 empty] | 0
859 | [26 empty] | 0
860 | [26 empty] | 0
861 | [26 empty] | 0
862 | [26 empty] | 0
863 | [26 empty] | 0
864 | [26 empty] | 0
865 | [26 empty] | 0
866 | [26 empty] | 0
867 | [26 empty] | 0
868 | [26 empty] | 0
869 | [26 empty] | 0
870 | [26 empty] | 0
871 | [26 empty] | 0
872 | [26 empty] | 0
873 | [26 empty] | 0
874 | [26 empty] | 0
875 | [26 empty] | 0
876 | [26 empty] | 0
877 | [26 empty] | 0
878 | [26 empty] | 0
879 | [26 empty] | 0
880 | [26 empty] | 0
881 | [26 empty] | 0
882 | [26 empty] | 0
883 | [26 empty] | 0
884 | [26 empty] | 0
885 | [26 empty] | 0
886 | [26 empty] | 0
887 | [26 empty] | 0
888 | [26 empty] | 0
889 | [26 empty] | 0
890 | [26 empty] | 0
891 | [26 empty] | 0
892 | [26 empty] | 0
893 | [26 empty] | 0
894 | [26 empty] | 0
Formulas:
Acknowdlegemnet time = (GA[[#This Row],[Acknowledgemnet Time ]]-GA[[#This Row],[Fault Time]])*24

## Mod_CL
sl no | FY | Calendar Year | Year | year2 | Month Year | Days | Date | Cycle Number | Resources | IC1_Inv1_MC | IC1_Inv2_MC | IC1_Inv3_MC | IC1_Inv4_MC | IC2_Inv1_MC | IC2_Inv2_MC | Total Module cleaned | Morning Start Time | Morning End Time | Evening Start Time | Evening End time | Brush/MOP Replcemnet | Water Test Report | Remarks for the day
1 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-01 | [8 empty] | 0
2 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-02 | [8 empty] | 0
3 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-03 | [8 empty] | 0
4 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-04 | [8 empty] | 0
5 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-05 | [8 empty] | 0
6 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-06 | [8 empty] | 0
7 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-07 | [8 empty] | 0
8 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-08 | [8 empty] | 0
9 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-09 | [8 empty] | 0
10 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-10 | [8 empty] | 0
11 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-11 | [8 empty] | 0
12 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-12 | [8 empty] | 0
13 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-13 | [8 empty] | 0
14 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-14 | [8 empty] | 0
15 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-15 | [8 empty] | 0
16 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-16 | [8 empty] | 0
17 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-17 | [8 empty] | 0
18 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-18 | [8 empty] | 0
19 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-19 | [8 empty] | 0
20 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-20 | [8 empty] | 0
21 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-21 | [8 empty] | 0
22 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-22 | [8 empty] | 0
23 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-23 | [8 empty] | 0
24 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-24 | [8 empty] | 0
25 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-25 | [8 empty] | 0
26 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-26 | [8 empty] | 0
27 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-27 | [8 empty] | 0
28 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-28 | [8 empty] | 0
29 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-29 | [8 empty] | 0
30 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-30 | [8 empty] | 0
31 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-01 | [8 empty] | 0
32 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-02 | [8 empty] | 0
33 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-03 | [8 empty] | 0
34 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-04 | [8 empty] | 0
35 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-05 | [8 empty] | 0
36 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | [8 empty] | 0
37 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-07 | [8 empty] | 0
38 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-08 | [8 empty] | 0
39 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-09 | [8 empty] | 0
40 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-10 | [8 empty] | 0
41 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-11 | [8 empty] | 0
42 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-12 | [8 empty] | 0
43 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-13 | [8 empty] | 0
44 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-14 | [8 empty] | 0
45 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-15 | [8 empty] | 0
46 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-16 | [8 empty] | 0
47 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-17 | [8 empty] | 0
48 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-18 | [8 empty] | 0
49 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-19 | [8 empty] | 0
50 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-20 | [8 empty] | 0
51 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-21 | [8 empty] | 0
52 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-22 | [8 empty] | 0
53 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-23 | [8 empty] | 0
54 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-24 | [8 empty] | 0
55 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-25 | [8 empty] | 0
56 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-26 | [8 empty] | 0
57 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-27 | [8 empty] | 0
58 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-28 | [8 empty] | 0
59 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-29 | [8 empty] | 0
60 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-30 | [8 empty] | 0
61 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-31 | [8 empty] | 0
62 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-01 | [8 empty] | 0
63 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-02 | [8 empty] | 0
64 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-03 | [8 empty] | 0
65 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-04 | [8 empty] | 0
66 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-05 | [8 empty] | 0
67 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-06 | [8 empty] | 0
68 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-07 | [8 empty] | 0
69 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-08 | [8 empty] | 0
70 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-09 | [8 empty] | 0
71 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-10 | [8 empty] | 0
72 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-11 | [8 empty] | 0
73 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-12 | [8 empty] | 0
74 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-13 | [8 empty] | 0
75 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-14 | [8 empty] | 0
76 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-15 | [8 empty] | 0
77 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-16 | [8 empty] | 0
78 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-17 | [8 empty] | 0
79 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-18 | [8 empty] | 0
80 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-19 | [8 empty] | 0
81 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-20 | [8 empty] | 0
82 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-21 | [8 empty] | 0
83 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-22 | [8 empty] | 0
84 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-23 | [8 empty] | 0
85 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-24 | [8 empty] | 0
86 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-25 | [8 empty] | 0
87 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-26 | [8 empty] | 0
88 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-27 | [8 empty] | 0
89 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-28 | [8 empty] | 0
90 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-29 | [8 empty] | 0
91 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-30 | [8 empty] | 0
92 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-01 | [8 empty] | 0
93 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-02 | [8 empty] | 0
94 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-03 | [8 empty] | 0
95 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-04 | [8 empty] | 0
96 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-05 | [8 empty] | 0
97 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-06 | [8 empty] | 0
98 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-07 | [8 empty] | 0
99 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-08 | [8 empty] | 0
100 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-09 | [8 empty] | 0
101 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-10 | [8 empty] | 0
102 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-11 | [8 empty] | 0
103 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | [8 empty] | 0
104 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-13 | [8 empty] | 0
105 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-14 | [8 empty] | 0
106 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | [8 empty] | 0
107 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-16 | [8 empty] | 0
108 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-17 | [8 empty] | 0
109 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-18 | [8 empty] | 0
110 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-19 | [8 empty] | 0
111 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-20 | [8 empty] | 0
112 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-21 | [8 empty] | 0
113 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-22 | [8 empty] | 0
114 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-23 | [8 empty] | 0
115 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-24 | [8 empty] | 0
116 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-25 | [8 empty] | 0
117 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-26 | [8 empty] | 0
118 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-27 | [8 empty] | 0
119 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-28 | [8 empty] | 0
120 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-29 | [8 empty] | 0
121 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-30 | [8 empty] | 0
122 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-31 | 1 | 4 | 980 | 1036 | 1008 | 1008 | 0 | 0 | 4032 | 0.20833 | 0.375 | 0.16667 | 0.83333 | Brush
123 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-01 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-02 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-03 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Modulecleaning stopped due to rain at site so Modules are cleaned
126 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-04 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Modulecleaning stopped due to rain at site so Modules are cleaned
127 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Modulecleaning stopped due to rain at site so Modules are cleaned
128 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-06 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Modulecleaning stopped due to rain at site so Modules are cleaned
129 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-07 | 1 | 2 | 0 | 0 | 0 | 1028 | 0 | 0 | 1028 | 0 | 0 | 0.66667 | 0.83333 | Brush
130 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-08 | 1 | 2 | 0 | 0 | 0 | 2016 | 0 | 0 | 2016 | 0.20833 | 0.375 | 0.66667 | 0.83333 | Brush
131 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-09 | 1 | 2 | 2032 | 0 | 0 | 0 | 0 | 0 | 2032 | 0.20833 | 0.375 | 0.66667 | 0.83333 | Brush
132 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-10 | 1 | 2 | 0 | 1008 | 0 | 0 | 1008 | 0 | 2016 | 0.20833 | 0.375 | 0.66667 | 0.83333 | Brush
133 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-11 | 1 | 2 | 1008 | 0 | 1092 | 0 | 0 | 0 | 2100 | 0.20833 | 0.375 | 0.66667 | 0.83333 | Brush
134 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-12 | 1 | 2 | 0 | 0 | 0 | 1016 | 0 | 1016 | 2032 | 0.20833 | 0.375 | 0.66667 | 0.83333 | Brush
135 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-13 | 1 | 2 | 0 | 1008 | 0 | 0 | 1008 | 0 | 2016 | 0.20833 | 0.375 | 0.66667 | 0.83333 | Brush
136 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-15 | [8 empty] | 0
138 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-16 | [8 empty] | 0
139 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-17 | [8 empty] | 0
140 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-18 | [8 empty] | 0
141 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | [8 empty] | 0
142 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-20 | [8 empty] | 0
143 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-21 | [8 empty] | 0
144 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-22 | [8 empty] | 0
145 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-23 | [8 empty] | 0
146 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-24 | [8 empty] | 0
147 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-25 | [8 empty] | 0
148 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-26 | [8 empty] | 0
149 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-27 | [8 empty] | 0
150 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-28 | [8 empty] | 0
151 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-29 | [8 empty] | 0
152 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-30 | [8 empty] | 0
153 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-31 | [8 empty] | 0
154 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-01 | [8 empty] | 0
155 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-02 | [8 empty] | 0
156 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-03 | [8 empty] | 0
157 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | [8 empty] | 0
158 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-05 | [8 empty] | 0
159 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-06 | [8 empty] | 0
160 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-07 | [8 empty] | 0
161 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-08 | [8 empty] | 0
162 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-09 | [8 empty] | 0
163 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-10 | [8 empty] | 0
164 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-11 | [8 empty] | 0
165 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-12 | [8 empty] | 0
166 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-13 | [8 empty] | 0
167 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-14 | [8 empty] | 0
168 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-15 | [8 empty] | 0
169 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-16 | [8 empty] | 0
170 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-17 | [8 empty] | 0
171 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-18 | [8 empty] | 0
172 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-19 | [8 empty] | 0
173 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-20 | [8 empty] | 0
174 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-21 | [8 empty] | 0
175 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-22 | [8 empty] | 0
176 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-23 | [8 empty] | 0
177 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-24 | [8 empty] | 0
178 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-25 | [8 empty] | 0
179 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-26 | [8 empty] | 0
180 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-27 | [8 empty] | 0
181 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-28 | [8 empty] | 0
182 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-29 | [8 empty] | 0
183 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-30 | [8 empty] | 0
184 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-01 | [8 empty] | 0
185 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-02 | [8 empty] | 0
186 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-03 | [8 empty] | 0
187 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-04 | [8 empty] | 0
188 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-05 | [8 empty] | 0
189 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-06 | [8 empty] | 0
190 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | [8 empty] | 0
191 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-08 | [8 empty] | 0
192 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-09 | [8 empty] | 0
193 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-10 | [8 empty] | 0
194 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | [8 empty] | 0
195 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-12 | [8 empty] | 0
196 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-13 | [8 empty] | 0
197 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-14 | [8 empty] | 0
198 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-15 | [8 empty] | 0
199 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-16 | [8 empty] | 0
200 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-17 | [8 empty] | 0
201 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-18 | [8 empty] | 0
202 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-19 | [8 empty] | 0
203 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-20 | [8 empty] | 0
204 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-21 | [8 empty] | 0
205 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-22 | [8 empty] | 0
206 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-23 | [8 empty] | 0
207 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-24 | [8 empty] | 0
208 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-25 | [8 empty] | 0
209 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-26 | [8 empty] | 0
210 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-27 | [8 empty] | 0
211 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-28 | [8 empty] | 0
212 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-29 | [8 empty] | 0
213 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-30 | [8 empty] | 0
214 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-31 | [8 empty] | 0
215 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-01 | [8 empty] | 0
216 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-02 | [8 empty] | 0
217 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-03 | [8 empty] | 0
218 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-04 | [8 empty] | 0
219 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-05 | [8 empty] | 0
220 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-06 | [8 empty] | 0
221 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-07 | [8 empty] | 0
222 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-08 | [8 empty] | 0
223 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-09 | [8 empty] | 0
224 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-10 | [8 empty] | 0
225 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-11 | [8 empty] | 0
226 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-12 | [8 empty] | 0
227 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-13 | [8 empty] | 0
228 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-14 | [8 empty] | 0
229 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-15 | [8 empty] | 0
230 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-16 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 1995 | 1995 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
231 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-17 | 1 | 2 | 0 | 504 | 504 | 462 | 0 | 588 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
232 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-18 | 1 | 2 | 336 | 672 | 0 | 0 | 0 | 735 | 1743 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
233 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-19 | 1 | 2 | 567 | 0 | 0 | 0 | 1428 | 0 | 1995 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
234 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-20 | 1 | 2 | 1764 | 252 | 0 | 0 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
235 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-21 | 1 | 2 | 0 | 1071 | 945 | 0 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
236 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-22 | 1 | 2 | 0 | 756 | 1008 | 252 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
237 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-23 | 1 | 2 | 0 | 0 | 693 | 1302 | 0 | 0 | 1995 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
238 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-24 | 1 | 2 | 0 | 0 | 0 | 0 | 2016 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
239 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-25 | 1 | 2 | 0 | 0 | 0 | 0 | 1470 | 294 | 1764 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
240 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-26 | 1 | 2 | 0 | 0 | 0 | 672 | 0 | 126 | 798 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
241 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-27 | 1 | 2 | 0 | 0 | 0 | 1407 | 0 | 0 | 1407 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
242 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-28 | 1 | 2 | 0 | 0 | 567 | 1428 | 0 | 0 | 1995 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
243 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-29 | 1 | 2 | 0 | 0 | 987 | 0 | 0 | 0 | 987 | 0.25 | 0.41667 |  |  | MOP
244 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-30 | 1 | 2 | 0 | 0 | 987 | 0 | 0 | 0 | 987 | 0.25 | 0.41667 |  |  | MOP
245 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-01 | 1 | 2 | 1386 | 0 | 0 | 0 | 609 | 0 | 1995 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
246 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-02 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 1512 | 1512 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
247 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-03 | 1 | 2 | 63 | 0 | 0 | 0 | 0 | 945 | 1008 |  |  | 0.66667 | 0.83333 | MOP
248 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-04 | [8 empty] | 0
249 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-05 | 1 | 2 | 189 | 1827 | 0 | 0 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
250 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-06 | 1 | 2 | 0 | 168 | 819 | 0 | 0 | 0 | 987 |  |  | 0.66667 | 0.83333 | MOP |  | Cycle 1 Completed
251 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-07 | 2 | 2 | 0 | 0 | 756 | 1302 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
252 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-08 | 2 | 2 | 0 | 0 | 0 | 1956 | 0 | 0 | 1956 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
253 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-09 | 2 | 2 | 0 | 0 | 504 | 1491 | 0 | 0 | 1995 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
254 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-10 | 2 | 2 | 0 | 252 | 1575 | 0 | 0 | 0 | 1827 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
255 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-11 | 2 | 2 | 630 | 378 | 0 | 0 | 0 | 0 | 1008 | 0.25 | 0.41667 |  |  | MOP
256 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-12 | 2 | 2 | 1008 | 0 | 0 | 0 | 0 | 0 | 1008 | 0.25 | 0.41667 |  |  | MOP
257 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-13 | 2 | 2 | 693 | 0 | 0 | 0 | 315 | 0 | 1008 | 0.25 | 0.41667 |  |  | MOP
258 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-14 | 2 | 2 | 0 | 0 | 0 | 0 | 1008 | 0 | 1008 | 0.25 | 0.41667 |  |  | MOP
259 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-15 | 2 | 2 | 0 | 0 | 0 | 0 | 84 | 1302 | 1386 | 0.25 | 0.41667 |  |  | MOP
260 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-16 | 2 | 2 | 0 | 0 | 294 | 252 | 0 | 504 | 1050 | 0.25 | 0.41667 |  |  | MOP
261 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-17 | 2 | 2 | 0 | 462 | 252 | 252 | 504 | 0 | 1470 | 0.25 | 0.41667 |  |  | MOP
262 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-18 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 1008 | 1008 | 0.25 | 0.41667 |  |  | MOP
263 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-19 | 2 | 2 | 63 | 0 | 0 | 0 | 0 | 945 | 1008 | 0.25 | 0.41667 |  |  | MOP
264 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-20 | 2 | 2 | 189 | 819 | 0 | 0 | 0 | 0 | 1008 | 0.25 | 0.41667 |  |  | MOP
265 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-21 | 2 | 2 | 0 | 1176 | 378 | 0 | 0 | 0 | 1554 | 0.25 | 0.41667 |  |  | MOP
266 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-22 | 2 | 2 | 0 | 0 | 1323 | 0 | 0 | 0 | 1323 | 0.25 | 0.41667 |  |  | MOP
267 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-23 | 2 | 2 | 0 | 1743 | 294 | 0 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
268 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-24 | 2 | 2 | 252 | 294 | 0 | 0 | 0 | 1512 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
269 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-25 | 2 | 2 | 693 | 0 | 0 | 0 | 609 | 735 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
270 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-26 | 2 | 2 | 1638 | 378 | 0 | 0 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
271 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-27 | 2 | 2 | 0 | 189 | 861 | 0 | 588 | 420 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
272 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-28 | 2 | 2 | 0 | 0 | 0 | 0 | 2016 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 2 Completed
273 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-29 | 3 | 2 | 0 | 63 | 2079 | 0 | 882 | 0 | 3024 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
274 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-30 | 3 | 2 | 1449 | 567 | 63 | 1974 | 0 | 0 | 4053 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
275 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-31 | 3 | 2 | 252 | 0 | 0 | 2184 | 0 | 1827 | 4263 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
276 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-01 | 3 | 2 | 1008 | 0 | 126 | 882 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
277 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-02 | 3 | 2 | 0 | 0 | 0 | 0 | 294 | 1680 | 1974 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
278 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-03 | 3 | 2 | 252 | 1155 | 0 | 0 | 0 | 567 | 1974 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
279 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-04 | 3 | 2 | 0 | 882 | 819 | 0 | 252 | 0 | 1953 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
280 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-05 | 3 | 2 | 0 | 0 | 882 | 1176 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
281 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-06 | 3 | 2 | 0 | 0 | 0 | 2016 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
282 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-07 | 3 | 2 | 0 | 441 | 945 | 840 | 0 | 0 | 2226 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
283 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-08 | 3 | 2 | 1449 | 315 | 378 | 0 | 0 | 0 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
284 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-09 | 3 | 2 | 1008 | 0 | 0 | 0 | 1134 | 0 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
285 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-10 | 3&4 | 2 | 1449 | 0 | 0 | 0 | 609 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 3 Completed
286 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-11 | 4 | 2 | 882 | 567 | 630 | 0 | 0 | 0 | 2079 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
287 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-12 | [8 empty] | 0
288 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-13 | 4 | 2 | 0 | 0 | 1491 | 504 | 0 | 0 | 1995 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
289 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-14 | 4 | 2 | 0 | 0 | 0 | 2100 | 0 | 0 | 2100 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
290 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | [8 empty] | 0
291 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | 4 | 2 | 0 | 504 | 504 | 462 | 0 | 567 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
292 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-17 | 4 | 2 | 0 | 0 | 0 | 0 | 588 | 1428 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
293 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-18 | 4 | 2 | 0 | 0 | 0 | 0 | 2016 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
294 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-19 | 4 | 2 | 252 | 0 | 0 | 0 | 840 | 882 | 1974 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
295 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-20 | 4 | 2 | 0 | 1995 | 42 | 0 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
296 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-21 | 4 | 2 | 0 | 0 | 336 | 1722 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
297 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-22 | 4 | 2 | 0 | 0 | 1323 | 735 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
298 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-23 | 4 | 2 | 0 | 1659 | 378 | 0 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
299 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-24 | 4 | 2 | 252 | 378 | 0 | 0 | 0 | 1386 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
300 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-25 | 4 | 2 | 0 | 0 | 0 | 0 | 735 | 861 | 1596 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
301 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-26 | [8 empty] | 0
302 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-27 | 4 | 2 | 1323 | 0 | 0 | 0 | 693 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
303 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | 4 | 2 | 0 | 1701 | 63 | 0 | 0 | 0 | 1764 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
304 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-29 | 4 | 2 | 0 | 0 | 1449 | 252 | 0 | 0 | 1701 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
305 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-30 | 4&5 | 2 | 630 | 567 | 861 | 0 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 4 Completed
306 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-31 | 5 | 2 | 1701 | 0 | 0 | 0 | 357 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
307 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-01 | 5 | 2 | 0 | 504 | 504 | 462 | 252 | 315 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
308 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-02 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 2079 | 2079 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
309 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-03 | 5 | 2 | 0 | 0 | 0 | 0 | 1764 | 252 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
310 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-04 | 5 | 2 | 252 | 0 | 0 | 0 | 1722 | 168 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
311 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | [8 empty] | 0
312 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-06 | 5 | 2 | 252 | 1533 | 0 | 0 | 0 | 252 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
313 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-07 | 5 | 2 | 0 | 462 | 1575 | 0 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
314 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-08 | 5 | 2 | 0 | 504 | 84 | 1428 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
315 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | 5 | 2 | 0 | 336 | 0 | 714 | 0 | 0 | 1050 | 0.25 | 0.41667 |  |  | MOP
316 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-10 | 5 | 2 | 0 | 0 | 0 | 2016 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
317 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-11 | 5 | 2 | 0 | 504 | 210 | 1323 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
318 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-12 | 5 | 2 | 0 | 819 | 945 | 252 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
319 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-13 | 5 | 2 | 0 | 1722 | 252 | 252 | 0 | 0 | 2226 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
320 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-14 | 5 | 2 | 252 | 252 | 0 | 0 | 0 | 1575 | 2079 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
321 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-15 | 5 | 2 | 0 | 336 | 252 | 210 | 546 | 672 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
322 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-16 | 5 | 2 | 0 | 0 | 0 | 0 | 2016 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 5 Completed
323 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | 6 | 2 | 0 | 0 | 0 | 0 | 1722 | 420 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
324 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-18 | 6 | 2 | 378 | 0 | 0 | 0 | 630 | 1008 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
325 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-19 | 6 | 2 | 0 | 0 | 0 | 0 | 0 | 1008 | 1008 | 0.25 | 0.41667 |  |  | MOP
326 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-20 | 6 | 2 | 252 | 1323 | 0 | 0 | 0 | 441 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
327 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-21 | 6 | 2 | 0 | 672 | 1197 | 42 | 0 | 0 | 1911 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
328 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-22 | [8 empty] | 0
329 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-23 | 6 | 2 | 0 | 0 | 441 | 1491 | 0 | 0 | 1932 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
330 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-24 | 6 | 2 | 0 | 0 | 0 | 2016 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
331 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-25 | 6 | 2 | 0 | 0 | 882 | 1176 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
332 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-26 | 6 | 2 | 0 | 1008 | 1575 | 0 | 0 | 0 | 2583 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
333 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-27 | 6 | 2 | 1890 | 126 | 0 | 0 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
334 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-28 | 6 | 2 | 693 | 0 | 0 | 0 | 1428 | 0 | 2121 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
335 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-01 | 6 | 2 | 819 | 0 | 0 | 0 | 1113 | 0 | 1932 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
336 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-02 | 6 | 2 | 1953 | 0 | 0 | 0 | 63 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
337 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-03 | 6 | 2 | 378 | 567 | 861 | 210 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
338 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | 6 | 2 | 0 | 1491 | 504 | 42 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
339 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-05 | 6 | 2 | 252 | 546 | 0 | 0 | 1008 | 252 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 6 Completed
340 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-06 | 7 | 2 | 0 | 0 | 0 | 0 | 1974 | 0 | 1974 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
341 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-07 | 7 | 2 | 0 | 0 | 0 | 0 | 504 | 1680 | 2184 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
342 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-08 | 7 | 2 | 0 | 504 | 420 | 252 | 0 | 861 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
343 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-09 | 7 | 2 | 0 | 0 | 84 | 210 | 0 | 1512 | 1806 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
344 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-10 | 7 | 2 | 252 | 315 | 0 | 0 | 0 | 1008 | 1575 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
345 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-11 | 7 | 2 | 0 | 1680 | 252 | 0 | 0 | 0 | 1932 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
346 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-12 | 7 | 1 | 0 | 0 | 1197 | 546 | 0 | 0 | 1743 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
347 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-13 | 7 | 2 | 0 | 0 | 0 | 2037 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
348 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-14
349 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-15 | 7 | 2 | 0 | 0 | 0 | 1050 | 0 | 0 | 1050 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
350 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-16 | 7 | 2 | 0 | 0 | 819 | 2016 | 1176 | 0 | 4011 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
351 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-17 | 7 | 2 | 0 | 0 | 0 | 0 | 1176 | 420 | 1596 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
352 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-18 | 7 | 2 | 0 | 0 | 0 | 0 | 1008 | 0 | 1008 |  |  | 0.66667 | 0.83333 | MOP
353 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-19 | 7 | 2 | 378 | 0 | 0 | 0 | 903 | 0 | 1281 |  |  | 0.66667 | 0.83333 | MOP
354 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-20 | 7 | 2 | 1134 | 0 | 0 | 0 | 0 | 0 | 1134 |  |  | 0.66667 | 0.83333 | MOP
355 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-21 | 7 | 2 | 693 | 567 | 0 | 0 | 0 | 0 | 1260 |  |  | 0.66667 | 0.83333 | MOP
356 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-22 | 7 | 2 | 0 | 1008 | 0 | 0 | 0 | 0 | 1008 | 0.25 | 0.41667 |  |  | MOP
357 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-23 | 7 | 2 | 441 | 0 | 0 | 0 | 609 | 0 | 1050 | 0.25 | 0.41667 |  |  | MOP
358 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-24 | 7 | 2 | 1890 | 189 | 0 | 0 | 0 | 0 | 2079 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
359 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-25 | 7 | 2 | 0 | 0 | 0 | 0 | 588 | 420 | 1008 | 0.25 | 0.41667 |  |  | MOP
360 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-26 | 7&8 | 2 | 0 | o | 0 | 0 | 1050 | 0 | 1050 | 0.25 | 0.41667 |  |  | MOP |  | Cycle 7 Completed
361 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-27 | 8 | 2 | 0 | 0 | 0 | 0 | 1974 | 0 | 1974 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
362 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-28 | 8 | 2 | 756 | 567 | 735 | 0 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
363 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-29 | 8 | 2 | 1575 | 0 | 0 | 0 | 609 | 0 | 2184 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
364 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-30 | 8 | 2 | 0 | 504 | 504 | 462 | 252 | 378 | 2100 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
365 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-31 | 8 | 2 | 252 | 0 | 0 | 0 | 0 | 1890 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
366 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-01 | [8 empty] | 0
367 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-02 | [8 empty] | 0
368 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-03 | [8 empty] | 0
369 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-04 | [8 empty] | 0
370 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-05 | [8 empty] | 0
371 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-06 | [8 empty] | 0
372 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-07 | [8 empty] | 0
373 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-08 | 8 | 3 | 252 | 252 | 0 | 0 | 1722 | 1575 | 3801 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
374 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-09 | 8 | 4 | 0 | 1743 | 630 | 0 | 1764 | 420 | 4557 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
375 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-10 | 8 | 2 | 0 | 1533 | 504 | 252 | 0 | 0 | 2289 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
376 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-11 | 8 | 2 | 252 | 504 | 0 | 0 | 0 | 1575 | 2331 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
377 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | 8 | 2 | 252 | 0 | 0 | 0 | 1428 | 672 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
378 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-13 | 8 | 2 | 252 | 651 | 0 | 0 | 0 | 441 | 1344 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Grid failure
379 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-14 | 8 | 2 | 567 | 630 | 1260 | 0 | 0 | 0 | 2457 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
380 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-15 | 8 | 2 | 0 | 0 | 819 | 1491 | 0 | 0 | 2310 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 8 Completed
381 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-16 | 9 | 2 | 0 | 0 | 0 | 2331 | 0 | 0 | 2331 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
382 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-17 | 9 | 2 | 0 | 0 | 1365 | 987 | 0 | 0 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
383 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-18 | 9 | 2 | 1134 | 567 | 693 | 0 | 0 | 0 | 2394 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
384 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-19 | 9 | 2 | 1197 | 84 | 252 | 210 | 609 | 0 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
385 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-20 | 9 | 4 | 0 | 315 | 693 | 0 | 1932 | 420 | 3360 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
386 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-21 | 9 | 4 | 0 | 336 | 252 | 210 | 1554 | 1302 | 3654 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
387 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-22 | 9 | 2 | 189 | 168 | 252 | 252 | 0 | 1701 | 2562 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
388 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-23 | 9 | 2 | 252 | 1386 | 0 | 0 | 0 | 756 | 2394 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
389 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | 9 | 2 | 0 | 1302 | 882 | 252 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
390 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-25 | [8 empty] | 0
391 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | [8 empty] | 0
392 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-27 | [8 empty] | 0
393 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-28 | [8 empty] | 0
394 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-29 | [8 empty] | 0 | [6 empty] | Grid5 TW12 to TW18 - 336 No.s ModulesChemical cleaning work completed
395 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-30 | [8 empty] | 0 | [6 empty] | Grid6 TW10 to TW18 & Grid5 TW1 to TW11 - 756 No.s ModulesChemical cleaning work completed
396 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-01 | [8 empty] | 0 | [6 empty] | Grid6 T1 to T13 - 819 No.s Modules Chemical cleaning work completed
397 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-02 | [8 empty] | 0 | [6 empty] | Grid6 T14 - 63 No.s Modules Chemical cleaning work completed
398 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-03 | [8 empty] | 0
399 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-04 | [8 empty] | 0 | [6 empty] | Grid6 T15 to T28 - 882 No.s Modules Chemical cleaning work completed
400 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-05 | [8 empty] | 0 | [6 empty] | Grid6 T29 to T43 - 945 No.s Modules Chemical cleaning work completed
401 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-06 | [8 empty] | 0 | [6 empty] | Grid6 T44 to T59 - 1008 No.s Modules Chemical cleaning work completed
402 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-07 | [8 empty] | 0 | [6 empty] | Grid6 T44 to T59 - 1008 No.s Modules Chemical cleaning work completed
403 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-08 | [8 empty] | 0 | [6 empty] | Grid6 T60 to T68 & TW01 to TW09 - 903 No.s Modules Chemical cleaning work completed
404 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-09 | [8 empty] | 0 | [6 empty] | Grid6 T69 to T88 - 840 No.s Modules Chemical cleaning work completed
405 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-10 | [8 empty] | 0
406 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-11 | [8 empty] | 0 | [6 empty] | Grid5 T92 to T97 - 378 No.s Modules Chemical cleaning work completed
407 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-12 | [8 empty] | 0 | [6 empty] | Grid5 T98 to T105 & Grid2 TW01, T1 to T11 - 1008 No.s Modules Chemical cleaning work completed
408 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-13 | [8 empty] | 0 | [6 empty] | Grid2 T12 to T35 - 1008 No.s Modules Chemical cleaning work completed
409 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-14 | [8 empty] | 0 | [6 empty] | Grid2 T36 to T40 & Grid1 T43 to T52 - 588 No.s Modules Chemical cleaning work completed
410 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-15 | [8 empty] | 0 | [6 empty] | Grid1 T20 to T42 - 966 No.s Modules Chemical cleaning work completed
411 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-16 | [8 empty] | 0 | [6 empty] | Grid1 T1 to T19 & Grid5 T88 to T91 - 966 No.s Modules Chemical cleaning work completed
412 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-17 | [8 empty] | 0 | [6 empty] | Grid5 T70 to T87 - 966 No.s Modules Chemical cleaning work completed
413 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-18 | [8 empty] | 0 | [6 empty] | Grid5 T54 to T69 - 1008 No.s Modules Chemical cleaning work completed
414 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-19 | [8 empty] | 0 | [6 empty] | Grid5 T36 to T53 - 966 No.s Modules Chemical cleaning work completed
415 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | [8 empty] | 0 | [6 empty] | Grid5 T20 to T35 - 1008 No.s Modules Chemical cleaning work completed
416 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-21 | [8 empty] | 0
417 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-22 | [8 empty] | 0 | [6 empty] | Grid5 T04 to T19 - 1008 No.s Modules Chemical cleaning work completed
418 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-23 | [8 empty] | 0 | [6 empty] | Grid5 T01 to T03 & Grid4 T01 to T15 - 966 No.s Modules Chemical cleaning work completed
419 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-24 | [8 empty] | 0 | [6 empty] | Grid4 T16 to T20 - 315 No.s Modules Chemical cleaning work completed
420 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | [8 empty] | 0 | [6 empty] | Grid4 T29 to T44 - 1008 No.s Modules Chemical cleaning work completed
421 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-26 | [8 empty] | 0
422 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-27 | [8 empty] | 0 | [6 empty] | Grid4 T45 to T60 - 1008 No.s Modules Chemical cleaning work completed
423 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-28 | [8 empty] | 0 | [6 empty] | Grid4 T61 to T76 - 1008 No.s Modules Chemical cleaning work completed
424 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-29 | [8 empty] | 0 | [6 empty] | Grid4 T77 to T88 - 756 No.s Modules Chemical cleaning work completed
425 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-30 | [8 empty] | 0 | [6 empty] | Grid3 T54 to T68 - 861 No.s Modules Chemical cleaning work completed
426 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-31 | [8 empty] | 0 | [6 empty] | Grid3 T38 to T53 - 1008 No.s Modules Chemical cleaning work completed
427 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-01 | [8 empty] | 0 | [6 empty] | Grid3 T22 to T37 - 1008 No.s Modules Chemical cleaning work completed
428 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-02 | [8 empty] | 0 | [6 empty] | Grid3 T6 to T21 - 1008 No.s Modules Chemical cleaning work completed
429 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-03 | [8 empty] | 0 | [6 empty] | Grid3 T1 to T5, TW1, Grid3A T1 to T5 & Grid4 T88 to T95 - 987 No.s Modules Chemical cleaning work completed
430 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-04 | [8 empty] | 0 | [6 empty] | Grid4 T96 to T111 - 1008 No.s Modules Chemical cleaning work completed
431 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-05 | [8 empty] | 0 | [6 empty] | Grid4 T112 to T116 - 315 No.s Modules Chemical cleaning work completed
432 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-06 | [8 empty] | 0 | [6 empty] | Grid4 T117 to T136 - 1029 No.s Modules Chemical cleaning work completed
433 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-07 | [8 empty] | 0 | [6 empty] | Grid4 T137 to T143 & Grid5 T145 to T158 - 1029 No.s Modules Chemical cleaning work completed
434 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-08 | [8 empty] | 0 | [6 empty] | Grid5 T127 to T144 - 1008 No.s Modules Chemical cleaning work completed
435 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-09 | [8 empty] | 0 | [6 empty] | Grid5 T111 to T126 - 1008 No.s Modules Chemical cleaning work completed
436 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-10 | [8 empty] | 0 | [6 empty] | Grid5 T105 to T110 & Grid5A T110- 357 No.s Modules Chemical cleaning work completed - Modules Chemical cleanng Cycle 1 completed
437 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-11 | [8 empty] | 0
438 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-12 | [8 empty] | 0
439 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-13 | [8 empty] | 0
440 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-14 | [8 empty] | 0
441 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-15 | [8 empty] | 0
442 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-16 | [8 empty] | 0
443 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-17 | [8 empty] | 0
444 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-18 | [8 empty] | 0
445 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-19 | [8 empty] | 0
446 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-20 | [8 empty] | 0
447 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-21 | [8 empty] | 0
448 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-22 | [8 empty] | 0
449 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-23 | [8 empty] | 0
450 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-24 | [8 empty] | 0
451 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-25 | [8 empty] | 0
452 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-26 | [8 empty] | 0
453 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-27 | 9 | 2 | 0 | 0 | 0 | 0 | 2268 | 0 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
454 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-28 | 9 | 2 | 63 | 0 | 0 | 0 | 1827 | 420 | 2310 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
455 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-29 | 9 | 2 | 2268 | 0 | 0 | 0 | 0 | 0 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
456 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-30 | [8 empty] | 0
457 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-01 | [8 empty] | 0
458 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | [8 empty] | 0
459 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-03 | [8 empty] | 0
460 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-04 | [8 empty] | 0
461 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-05 | [8 empty] | 0
462 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-06 | [8 empty] | 0
463 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-07 | [8 empty] | 0
464 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-08 | [8 empty] | 0
465 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-09 | [8 empty] | 0
466 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-10 | [8 empty] | 0
467 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-11 | [8 empty] | 0
468 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-12 | [8 empty] | 0
469 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-13 | [8 empty] | 0
470 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-14 | [8 empty] | 0
471 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-15 | [8 empty] | 0
472 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-16 | [8 empty] | 0
473 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-17 | [8 empty] | 0
474 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-18 | 9 | 2 | 693 | 567 | 861 | 0 | 0 | 0 | 2121 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
475 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-19 | 9 | 2 | 1197 | 504 | 252 | 210 | 0 | 0 | 2163 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 9 Completed
476 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-20 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 1323 | 1323 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
477 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-21 | 10 | 2 | 441 | 336 | 252 | 210 | 903 | 0 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
478 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-22 | 10 | 2 | 630 | 168 | 252 | 252 | 1134 | 0 | 2436 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
479 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-23 | 10 | 2 | 1764 | 63 | 0 | 0 | 504 | 0 | 2331 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
480 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-24 | 10 | 2 | 0 | 567 | 819 | 0 | 0 | 0 | 1386 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
481 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | [8 empty] | 0
482 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-26 | [8 empty] | 0
483 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-27 | [8 empty] | 0
484 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-28 | [8 empty] | 0
485 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | [8 empty] | 0
486 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-30 | [8 empty] | 0
487 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-31 | [8 empty] | 0
488 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-01 | [8 empty] | 0
489 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-02 | 10 | 2 | 0 | 252 | 2079 | 63 | 0 | 0 | 2394 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
490 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-03 | 10 | 2 | 0 | 0 | 0 | 1197 | 0 | 0 | 1197 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
491 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-04 | [8 empty] | 0
492 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-05 | 10 | 2 | 0 | 504 | 1134 | 966 | 0 | 0 | 2604 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
493 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-06 | [8 empty] | 0
494 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-07 | [8 empty] | 0
495 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-08 | 10 | 2 | 0 | 0 | 567 | 609 | 1302 | 0 | 2478 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
496 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-09 | 10 | 2 | 0 | 504 | 504 | 462 | 987 | 0 | 2457 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
497 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-10 | 10 | 2 | 0 | 0 | 168 | 2184 | 0 | 0 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
498 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-11 | 10 | 2 | 0 | 0 | 0 | 0 | 1764 | 420 | 2184 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
499 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-12 | 10 | 2 | 0 | 245 | 175 | 0 | 1848 | 0 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
500 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-13 | [8 empty] | 0
501 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-14 | [8 empty] | 0
502 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-15 | [8 empty] | 0
503 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-16 | [8 empty] | 0
504 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-17 | [8 empty] | 0
505 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-18 | [8 empty] | 0
506 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-19 | [8 empty] | 0
507 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-20 | [8 empty] | 0
508 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-21 | [8 empty] | 0
509 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-22 | [8 empty] | 0
510 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-23 | [8 empty] | 0
511 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-24 | [8 empty] | 0
512 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-25 | [8 empty] | 0
513 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-26 | [8 empty] | 0
514 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-27 | [8 empty] | 0
515 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-28 | 1 | 2 | 0 | 504 | 504 | 462 | 0 | 735 | 2205 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
516 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-29 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 1512 | 1512 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
517 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-30 | [8 empty] | 0
518 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-31 | [8 empty] | 0
519 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-01 | [8 empty] | 0
520 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-02 | [8 empty] | 0
521 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-03 | [8 empty] | 0
522 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-04 | [8 empty] | 0
523 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-05 | [8 empty] | 0
524 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-06 | [8 empty] | 0
525 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-07 | [8 empty] | 0
526 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-08 | [8 empty] | 0
527 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-09 | [8 empty] | 0
528 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-10 | [8 empty] | 0
529 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-11 | [8 empty] | 0
530 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-12 | 1 | 2 | 504 | 0 | 0 | 0 | 609 | 0 | 1113 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
531 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-13 | 1 | 2 | 1827 | 126 | 0 | 0 | 0 | 0 | 1953 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
532 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-14 | 1 | 2 | 0 | 441 | 1806 | 0 | 0 | 0 | 2247 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
533 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-15 | 1 | 2 | 1701 | 630 | 0 | 0 | 0 | 0 | 2331 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
534 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-16 | 1 | 2 | 0 | 756 | 504 | 210 | 0 | 819 | 2289 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
535 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-17 | [8 empty] | 0
536 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-18 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 1008 | 1008 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
537 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-19 | 1 | 2 | 252 | 1155 | 0 | 0 | 0 | 798 | 2205 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
538 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-20 | 1 | 2 | 0 | 1176 | 546 | 252 | 0 | 0 | 1974 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
539 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-21 | 1 | 2 | 1197 | 630 | 567 | 0 | 0 | 0 | 2394 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
540 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-22 | 1 | 2 | 252 | 189 | 0 | 0 | 0 | 1890 | 2331 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
541 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-23 | 1 | 2 | 504 | 0 | 0 | 0 | 1428 | 357 | 2289 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
542 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-24 | 1 | 2 | 126 | 0 | 1134 | 1008 | 0 | 0 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
543 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-25 | 1 | 2 | 0 | 0 | 0 | 0 | 2221 | 0 | 2221 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
544 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-26 | 1 | 2 | 0 | 0 | 630 | 1680 | 0 | 0 | 2310 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 1 Completed
545 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-27 | 2 | 2 | 0 | 0 | 567 | 0 | 1764 | 0 | 2331 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
546 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-28 | 2 | 2 | 0 | 0 | 0 | 0 | 1134 | 0 | 1134 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
547 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-29 | [8 empty] | 0
548 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-30 | 2 | 2 | 0 | 735 | 378 | 0 | 546 | 420 | 2079 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
549 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | 2 | 2 | 252 | 1260 | 0 | 0 | 0 | 441 | 1953 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
550 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | 2 | 2 | 0 | 0 | 0 | 168 | 0 | 1134 | 1302 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
551 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | 2 | 2 | 0 | 504 | 504 | 294 | 0 | 882 | 2184 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
552 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | [8 empty] | 0
553 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | [8 empty] | 0
554 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | [8 empty] | 0
555 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-07 | 2 | 2 | 0 | 504 | 504 | 462 | 0 | 798 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
556 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-08 | 2 | 2 | 0 | 0 | 0 | 0 | 714 | 1554 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
557 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-09 | 2 | 2 | 0 | 0 | 0 | 0 | 1134 | 0 | 1134 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
558 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | [8 empty] | 0
559 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-11 | 2 | 2 | 189 | 0 | 0 | 0 | 1638 | 315 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
560 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-12 | 2 | 2 | 63 | 2037 | 189 | 0 | 0 | 0 | 2289 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
561 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-13 | 2 | 2 | 0 | 0 | 1512 | 546 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
562 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-14 | [8 empty] | 0
563 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-15 | 2 | 2 | 0 | 0 | 0 | 2247 | 0 | 0 | 2247 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
564 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | 2 | 2 | 0 | 0 | 63 | 2142 | 0 | 0 | 2205 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
565 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | 2 | 2 | 0 | 189 | 2016 | 0 | 0 | 0 | 2205 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
566 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | 2 | 2 | 1827 | 441 | 0 | 0 | 0 | 0 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 2 Completed
567 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-19 | 3 | 2 | 504 | 0 | 0 | 0 | 1764 | 0 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
568 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-20 | 3 | 2 | 2079 | 0 | 0 | 0 | 273 | 0 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
569 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-21 | 3 | 2 | 252 | 903 | 1113 | 210 | 0 | 0 | 2478 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
570 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-22 | 3 | 2 | 0 | 231 | 252 | 252 | 0 | 1701 | 2436 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
571 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | 3 | 2 | 252 | 819 | 0 | 0 | 0 | 756 | 1827 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
572 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-24 | 3 | 2 | 0 | 1239 | 882 | 252 | 0 | 0 | 2373 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
573 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-25 | 3 | 2 | 252 | 1974 | 0 | 0 | 0 | 126 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
574 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-26 | 3 | 2 | 0 | 0 | 0 | 0 | 252 | 2121 | 2373 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
575 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-27 | 3 | 2 | 0 | 0 | 0 | 0 | 1932 | 420 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
576 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-28 | 3 | 2 | 0 | 0 | 0 | 0 | 2352 | 0 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
577 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-29 | 3 | 2 | 1764 | 0 | 0 | 0 | 378 | 0 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
578 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | 3 | 2 | 567 | 630 | 1134 | 0 | 0 | 0 | 2331 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
579 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-31 | 3 | 2 | 0 | 0 | 945 | 1344 | 0 | 0 | 2289 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
580 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-01 | 3 | 2 | 0 | 0 | 0 | 2394 | 0 | 0 | 2394 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
581 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-02 | 3 | 2 | 0 | 273 | 1197 | 1113 | 0 | 0 | 2583 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 3 Completed
582 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-03 | 4 | 2 | 882 | 567 | 1113 | 0 | 0 | 0 | 2562 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
583 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-04 | 4 | 2 | 1449 | 0 | 252 | 252 | 609 | 0 | 2562 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
584 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-05 | 4 | 2 | 0 | 504 | 504 | 462 | 546 | 504 | 2520 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
585 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-06 | 4 | 2 | 252 | 315 | 0 | 0 | 0 | 1953 | 2520 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
586 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-07 | 4 | 2 | 0 | 1869 | 378 | 294 | 0 | 0 | 2541 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
587 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-08 | 4 | 2 | 0 | 1449 | 588 | 504 | 0 | 0 | 2541 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
588 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-09 | 4 | 2 | 252 | 588 | 0 | 252 | 0 | 1449 | 2541 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
589 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
590 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-11 | 4 | 2 | 0 | 336 | 0 | 0 | 1428 | 798 | 2562 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
591 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-12 | 4 | 2 | 1197 | 0 | 0 | 0 | 0 | 0 | 1197 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
592 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-13 | 4 | 2 | 1134 | 630 | 441 | 294 | 0 | 0 | 2499 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
593 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-14 | 4 | 2 | 0 | 0 | 1638 | 378 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
594 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-15 | 4 | 2 | 0 | 0 | 0 | 2499 | 0 | 0 | 2499 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
595 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-16 | 4 | 2 | 0 | 0 | 189 | 2058 | 294 | 0 | 2541 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
596 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-17 | 4 | 2 | 0 | 441 | 1869 | 0 | 0 | 252 | 2562 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP |  | Cycle 4 Completed
597 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-18 | 5 | 2 | 2205 | 0 | 0 | 0 | 0 | 0 | 2205 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
598 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-19 | 5 | 2 | 2205 | 315 | 0 | 0 | 0 | 0 | 2520 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
599 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-20 | 5 | 2 | 126 | 0 | 0 | 0 | 1029 | 1354 | 2509 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
600 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-21 | 5 | 2 | 0 | 0 | 0 | 0 | 2142 | 378 | 2520 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
601 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-22 | 5 | 2 | 0 | 336 | 252 | 588 | 924 | 420 | 2520 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
602 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-23 | 5 | 2 | 0 | 352 | 294 | 252 | 1638 | 0 | 2536 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
603 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-24 | 5 | 2 | 252 | 882 | 0 | 0 | 0 | 945 | 2079 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
604 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-25 | 5 | 2 | 252 | 1758 | 252 | 0 | 0 | 252 | 2514 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
605 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-26 | 5 | 2 | 252 | 1194 | 1071 | 0 | 0 | 0 | 2517 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
606 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-27 | 5 | 2 | 1071 | 0 | 0 | 0 | 1428 | 0 | 2499 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
607 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-28 | 5 | 2 | 294 | 0 | 0 | 0 | 0 | 2247 | 2541 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
608 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-29 | [8 empty] | 0
609 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-30 | 5 | 2 | 1386 | 0 | 0 | 0 | 1176 | 0 | 2562 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
610 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-01 | 5 | 2 | 1449 | 630 | 441 | 0 | 0 | 0 | 2520 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP |  | Cycle 5 Completed
611 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-02 | 6 | 2 | 252 | 630 | 1449 | 0 | 0 | 0 | 2331 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
612 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-03 | 6 | 2 | 0 | 0 | 630 | 567 | 0 | 0 | 1197 | 0.25 | 0.41667 |  |  | MOP
613 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-04 | [8 empty] | 0
614 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-05 | 6 | 2 | 0 | 0 | 0 | 2436 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
615 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-06 | 6 | 2 | 0 | 0 | 441 | 1617 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
616 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-07 | 6 | 2 | 0 | 0 | 1554 | 924 | 0 | 0 | 2478 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
617 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-08 | 6 | 2 | 1071 | 567 | 861 | 0 | 0 | 0 | 2499 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
618 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-09 | 6 | 2 | 1260 | 231 | 0 | 336 | 609 | 0 | 2436 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
619 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-10 | 6 | 2 | 0 | 0 | 0 | 0 | 1984 | 420 | 2404 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
620 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-11 | 6 | 2 | 0 | 504 | 210 | 0 | 1722 | 0 | 2436 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
621 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-12 | 6 | 2 | 0 | 298 | 252 | 252 | 0 | 1638 | 2440 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
622 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-13 | 6 | 2 | 252 | 1071 | 0 | 0 | 0 | 1134 | 2457 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
623 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-14 | 6 | 2 | 0 | 1554 | 630 | 252 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
624 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | 6 | 2 | 0 | 1947 | 504 | 0 | 0 | 0 | 2451 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
625 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-16 | 6 | 2 | 252 | 378 | 0 | 0 | 0 | 1827 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
626 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-17 | 7 | 2 | 630 | 0 | 0 | 0 | 1428 | 420 | 2478 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
627 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-18 | 7 | 2 | 1260 | 0 | 0 | 0 | 0 | 0 | 1260 | 0.25 | 0.41667 |  |  | MOP
628 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-19 | 7 | 2 | 1324 | 630 | 504 | 0 | 0 | 0 | 2458 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
629 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-20 | 7 | 2 | 0 | 0 | 1134 | 0 | 1302 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
630 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-21 | 7 | 2 | 0 | 0 | 0 | 0 | 2016 | 0 | 2016 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
631 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | 7 | 2 | 0 | 0 | 567 | 693 | 1176 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
632 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-23 | 7 | 2 | 0 | 0 | 0 | 2404 | 0 | 0 | 2404 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
633 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-24 | 7 | 2 | 0 | 0 | 252 | 2142 | 0 | 0 | 2394 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
634 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-25 | 7 | 2 | 0 | 189 | 2058 | 168 | 0 | 0 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
635 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-26 | 7 | 2 | 1827 | 567 | 63 | 0 | 0 | 0 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
636 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-27 | 7 | 2 | 756 | 0 | 0 | 0 | 441 | 0 | 1197 | 0.25 | 0.41667 |  |  | MOP
637 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-28 | 7 | 2 | 0 | 462 | 504 | 504 | 210 | 756 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
638 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-29 | 7 | 2 | 252 | 315 | 0 | 0 | 0 | 1890 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
639 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-30 | 7 | 2 | 0 | 2058 | 378 | 0 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
640 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-31 | 7 | 2 | 0 | 1050 | 1197 | 231 | 0 | 0 | 2478 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
641 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-01 | 8 | 2 | 252 | 840 | 0 | 0 | 0 | 1323 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
642 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-02 | 8 | 2 | 0 | 0 | 0 | 0 | 1438 | 987 | 2425 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
643 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-03 | 8 | 2 | 1575 | 0 | 0 | 0 | 861 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
644 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-04 | 8 | 2 | 1071 | 630 | 756 | 0 | 0 | 0 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
645 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-05 | 8 | 2 | 0 | 0 | 1512 | 945 | 0 | 0 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
646 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-06 | 8 | 2 | 0 | 0 | 0 | 2436 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
647 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-07 | 8 | 2 | 0 | 0 | 0 | 1785 | 630 | 0 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
648 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-08 | 8 | 2 | 0 | 0 | 0 | 0 | 2000 | 420 | 2420 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
649 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-09 | 8 | 2 | 0 | 0 | 252 | 1113 | 1050 | 0 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
650 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-10 | 8 | 2 | 0 | 630 | 1806 | 0 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
651 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | 8 | 2 | 1953 | 504 | 0 | 0 | 0 | 0 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
652 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-12 | 8 | 2 | 882 | 504 | 252 | 167 | 609 | 0 | 2414 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
653 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-13 | 8 | 2 | 0 | 231 | 252 | 252 | 0 | 1701 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 8 Completed
654 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-14 | 9 | 2 | 252 | 1134 | 0 | 0 | 0 | 1018 | 2404 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
655 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-15 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Due to festival
656 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-16 | 9 | 2 | 0 | 1113 | 819 | 504 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
657 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-17 | 9 | 2 | 189 | 2037 | 189 | 0 | 0 | 0 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
658 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-18 | 9 | 2 | 0 | 0 | 0 | 0 | 0 | 1512 | 1512 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
659 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-19 | 9 | 2 | 0 | 0 | 0 | 0 | 294 | 861 | 1155 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
660 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-20 | 9 | 2 | 63 | 0 | 0 | 0 | 1134 | 0 | 1197 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
661 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-21 | 9 | 2 | 2331 | 126 | 0 | 0 | 0 | 0 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
662 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-22 | 9 | 2 | 0 | 630 | 1806 | 0 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
663 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-23 | 9 | 2 | 0 | 1071 | 378 | 0 | 1050 | 0 | 2499 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
664 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-24 | 9 | 2 | 0 | 0 | 0 | 0 | 1890 | 420 | 2310 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
665 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-25 | 9 | 2 | 0 | 252 | 0 | 0 | 1722 | 441 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
666 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-26 | 9 | 2 | 0 | 0 | 0 | 1407 | 0 | 0 | 1407 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
667 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-27 | 9 | 2 | 0 | 0 | 0 | 2377 | 0 | 0 | 2377 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
668 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-28 | 9 | 2 | 0 | 0 | 0 | 2331 | 126 | 0 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
669 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-29 | 9 | 2 | 0 | 0 | 702 | 696 | 0 | 1008 | 2406 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
670 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-30 | 9 | 2 | 252 | 768 | 0 | 0 | 0 | 1394 | 2414 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 9 Completed
671 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-31 | 10 | 4 | 630 | 2279 | 630 | 210 | 609 | 0 | 4358 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
672 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-01 | 10 | 2 | 441 | 168 | 252 | 252 | 894 | 420 | 2427 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
673 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-02 | 10 | 4 | 0 | 0 | 0 | 0 | 3434 | 0 | 3434 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
674 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-03 | 10 | 2 | 1386 | 567 | 0 | 0 | 462 | 0 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
675 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-04 | 10 | 2 | 0 | 252 | 1995 | 189 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
676 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-05 | 10 | 4 | 1701 | 693 | 0 | 1050 | 504 | 0 | 3948 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
677 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-06 | 10 | 4 | 630 | 567 | 0 | 2242 | 0 | 0 | 3439 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
678 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-07 | 10 | 4 | 0 | 315 | 2331 | 1869 | 0 | 0 | 4515 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
679 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-08 | 10 | 2 | 0 | 1533 | 882 | 0 | 0 | 0 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
680 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-09 | 10 | 2 | 294 | 378 | 0 | 0 | 0 | 1764 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 10 Completed
681 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-10 | 11 | 2 | 0 | 0 | 0 | 0 | 0 | 2436 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
682 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | 11 | 2 | 0 | 0 | 0 | 0 | 1964 | 440 | 2404 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
683 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-12 | 11 | 2 | 252 | 1386 | 0 | 0 | 0 | 819 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
684 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | 11 | 4 | 0 | 1428 | 504 | 252 | 1554 | 0 | 3738 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
685 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-14 | 11 | 4 | 562 | 504 | 1475 | 504 | 1197 | 0 | 4242 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
686 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-15 | 11 | 4 | 1890 | 315 | 0 | 0 | 1071 | 0 | 3276 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
687 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-16 | 11 | 4 | 0 | 252 | 1806 | 1092 | 0 | 0 | 3150 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
688 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-17 | 11 | 4 | 1512 | 819 | 0 | 987 | 0 | 0 | 3318 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
689 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-18 | 11 | 2 | 945 | 0 | 0 | 0 | 1468 | 0 | 2413 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
690 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-19 | 11 | 4 | 0 | 0 | 0 | 1092 | 168 | 1932 | 3192 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 11 Completed
691 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-20 | 12 | 4 | 252 | 1596 | 1554 | 630 | 0 | 315 | 4347 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
692 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-21 | 12 | 4 | 0 | 945 | 882 | 315 | 1176 | 0 | 3318 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
693 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-22 | 12 | 4 | 252 | 1491 | 0 | 0 | 756 | 861 | 3360 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
694 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-23 | 12 | 4 | 0 | 0 | 0 | 210 | 1134 | 2016 | 3360 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
695 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | 12 | 4 | 693 | 1407 | 903 | 0 | 504 | 861 | 4368 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
696 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-25 | 12 | 4 | 1890 | 546 | 0 | 0 | 609 | 1386 | 4431 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
697 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | 12 | 2 | 0 | 1386 | 504 | 441 | 0 | 0 | 2331 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
698 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-27 | 12 | 4 | 819 | 0 | 819 | 0 | 1428 | 0 | 3066 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
699 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-28 | 12 | 4 | 1575 | 630 | 1113 | 0 | 0 | 0 | 3318 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
700 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-29 | 12 | 4 | 0 | 189 | 945 | 1113 | 1092 | 0 | 3339 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 12 Completed
701 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-01 | 13 | 4 | 0 | 0 | 0 | 2205 | 672 | 420 | 3297 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
702 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-02 | 13 | 2 | 0 | 0 | 0 | 1176 | 1218 | 0 | 2394 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
703 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-03 | 13 | 4 | 189 | 567 | 1365 | 630 | 588 | 0 | 3339 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
704 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-04 | 13 | 4 | 2205 | 1113 | 1071 | 0 | 0 | 0 | 4389 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
705 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-05 | 13 | 4 | 252 | 882 | 0 | 0 | 2163 | 1113 | 4410 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
706 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | 13 | 4 | 1134 | 294 | 252 | 252 | 0 | 1386 | 3318 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
707 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-07 | 13 | 4 | 1134 | 336 | 252 | 210 | 0 | 1491 | 3423 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
708 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-08 | 13 | 4 | 504 | 1659 | 504 | 0 | 0 | 756 | 3423 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
709 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-09 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
710 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-10 | 13 | 4 | 0 | 1449 | 2646 | 567 | 0 | 0 | 4662 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | cycle 13 Completed
711 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-11 | 14 | 4 | 0 | 0 | 0 | 2142 | 0 | 0 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
712 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | 14 | 4 | 0 | 1491 | 420 | 2331 | 0 | 0 | 4242 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
713 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-13 | 14 | 4 | 252 | 630 | 0 | 0 | 0 | 1323 | 2205 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
714 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-14 | 14 | 2 | 0 | 0 | 1806 | 1455 | 0 | 0 | 3261 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
715 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-15 | 14 | 2 | 2200 | 0 | 0 | 0 | 0 | 0 | 2200 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
716 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-16 | 14 | 2 | 1008 | 0 | 0 | 0 | 1197 | 0 | 2205 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
717 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-17 | 14 | 2 | 0 | 0 | 0 | 0 | 2248 | 0 | 2248 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
718 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-18 | 14 | 4 | 0 | 504 | 504 | 462 | 1533 | 987 | 3990 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
719 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-19 | 14 | 4 | 1386 | 0 | 0 | 0 | 819 | 2142 | 4347 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
720 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-20 | 14 | 2 | 0 | 2163 | 0 | 0 | 0 | 0 | 2163 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
721 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-21 | 14 | 4 | 1071 | 630 | 2079 | 609 | 0 | 0 | 4389 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | cycle 14 completed
722 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-02 | 31 | 2024-03-22 | 15 | 4 | 0 | 0 | 1764 | 2541 | 0 | 0 | 4305 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
723 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-03 | 31 | 2024-03-23 | 15 | 2 | 0 | 0 | 0 | 1512 | 1113 | 0 | 2625 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
724 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-24 | 15 | 2 | 0 | 630 | 861 | 546 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
725 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-25 | 15 | 2 | 0 | 1806 | 378 | 0 | 0 | 0 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
726 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-26 | 15 | 4 | 2394 | 315 | 0 | 0 | 0 | 1638 | 4347 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
727 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-27 | 15 | 4 | 0 | 504 | 504 | 252 | 2252 | 819 | 4331 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
728 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-28 | 15 | 4 | 0 | 0 | 0 | 0 | 1722 | 2352 | 4074 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
729 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-29 | 15 | 4 | 630 | 1533 | 0 | 0 | 2100 | 315 | 4578 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
730 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-30 | 15 | 4 | 1134 | 504 | 1386 | 252 | 0 | 0 | 3276 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 15 completed
731 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-31 | 16 | 4 | 882 | 630 | 567 | 2147 | 0 | 0 | 4226 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
732 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-01 | 16 | 4 | 378 | 567 | 1176 | 1127 | 0 | 0 | 3248 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
733 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-02 | 16 | 2 | 1134 | 0 | 0 | 0 | 0 | 0 | 1134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
734 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-03 | 16 | 2 | 1008 | 0 | 0 | 0 | 126 | 0 | 1134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
735 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-04 | 16 | 2 | 0 | 0 | 0 | 1239 | 966 | 0 | 2205 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
736 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-05 | 16 | 2 | 0 | 0 | 0 | 0 | 1764 | 420 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
737 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-06 | 16 | 2 | 0 | 0 | 126 | 693 | 1376 | 0 | 2195 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
738 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-07 | 16 | 2 | 0 | 0 | 1367 | 704 | 0 | 0 | 2071 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
739 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-08 | 16 | 2 | 0 | 1113 | 1071 | 0 | 0 | 0 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
740 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-09 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
741 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-10 | 16 | 2 | 0 | 1109 | 0 | 0 | 0 | 0 | 1109 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
742 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-11 | 16 | 2 | 252 | 812 | 0 | 0 | 0 | 1134 | 2198 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
743 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-12 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 2373 | 2373 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
744 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-13 | 16 | 2 | 0 | 315 | 252 | 210 | 0 | 1365 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
745 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-14 | 16 | 4 | 882 | 903 | 0 | 0 | 1428 | 1008 | 4221 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | cycle 16 completed
746 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-15 | 17 | 2 | 0 | 1323 | 504 | 315 | 0 | 0 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
747 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-16 | 17 | 4 | 1701 | 378 | 1197 | 609 | 0 | 0 | 3885 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
748 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-17 | 17 | 4 | 0 | 315 | 1743 | 2184 | 0 | 0 | 4242 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
749 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-18 | 17 | 4 | 441 | 630 | 63 | 1974 | 0 | 0 | 3108 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
750 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-19 | 17 | 4 | 1890 | 462 | 1575 | 0 | 189 | 0 | 4116 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
751 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-20 | 17 | 2 | 0 | 1050 | 0 | 0 | 1099 | 0 | 2149 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
752 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-21 | 17 | 2 | 252 | 0 | 0 | 0 | 819 | 0 | 1071 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
753 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-22 | 17 | 4 | 1071 | 504 | 0 | 0 | 0 | 1512 | 3087 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
754 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-23 | 17 | 4 | 1071 | 630 | 378 | 0 | 0 | 1071 | 3150 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
755 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-24 | 17 | 4 | 0 | 504 | 504 | 504 | 0 | 609 | 2121 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
756 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-25 | 17 | 4 | 0 | 0 | 0 | 0 | 0 | 2079 | 2079 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
757 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-26 | 17 | 4 | 0 | 1092 | 0 | 0 | 0 | 0 | 1092 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
758 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-05 | 30 | 2024-04-27 | 17 | 2 | 0 | 1134 | 0 | 0 | 1072 | 0 | 2206 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
759 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-06 | 30 | 2024-04-28 | 18 | 2 | 0 | 0 | 0 | 0 | 1722 | 420 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
760 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-07 | 30 | 2024-04-29 | 18 | 2 | 0 | 189 | 819 | 252 | 0 | 0 | 1260 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
761 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-07 | 30 | 2024-04-30 | 18 | 2 | 0 | 0 | 1197 | 987 | 0 | 0 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
762 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-01 | 18 | 2 | 0 | 0 | 441 | 966 | 672 | 0 | 2079 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
763 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-02 | 18 | 2 | 0 | 0 | 0 | 2080 | 0 | 0 | 2080 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
764 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-03 | 18 | 2 | 0 | 0 | 1134 | 882 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
765 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-04 | 18 | 2 | 630 | 567 | 861 | 0 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
766 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-05 | 18 | 2 | 1764 | 0 | 0 | 0 | 357 | 0 | 2121 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
767 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-06 | 18 | 2 | 0 | 1617 | 378 | 0 | 210 | 0 | 2205 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
768 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-07 | 18 | 2 | 252 | 693 | 0 | 0 | 0 | 1197 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
769 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | 18 | 2 | 0 | 0 | 0 | 0 | 0 | 2016 | 2016 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
770 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | 18 | 2 | 0 | 504 | 504 | 462 | 0 | 567 | 2037 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
771 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
772 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-11 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
773 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-12 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
774 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
775 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-14 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
776 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-15 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
777 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-16 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
778 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-17 | 18 | 2 | 1017 | 0 | 0 | 0 | 0 | 0 | 1017 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
779 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-18 | 18 | 2 | 0 | 1110 | 0 | 0 | 0 | 0 | 1110 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
780 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-19 | 18 | 2 | 0 | 0 | 0 | 0 | 0 | 1143 | 1143 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
781 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-20 | 18 | 2 | 0 | 0 | 0 | 0 | 0 | 2143 | 2143 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
782 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-21 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
783 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-22 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
784 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-23 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
785 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-24 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
786 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-25 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
787 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-26 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
788 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-27 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
789 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-28 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
790 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-29 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
791 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-30 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
792 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-31 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
793 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-01 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
794 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-02 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
795 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-03 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
796 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-04 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
797 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-05 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
798 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-06 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
799 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-07 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
800 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-08 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
801 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-09 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
802 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-10 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
803 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-11 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
804 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-12 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
805 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
806 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-14 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
807 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-15 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
808 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-16 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
809 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-17 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
810 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
811 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-19 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
812 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-20 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
813 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-21 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
814 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-22 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
815 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-23 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
816 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-24 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
817 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-25 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
818 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-26 | [8 empty] | 0
819 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-27 | [8 empty] | 0
820 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-28 | [8 empty] | 0
821 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-29 | [8 empty] | 0
822 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-30 | [8 empty] | 0
823 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-01 | [8 empty] | 0
824 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-02 | [8 empty] | 0
825 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-03 | [8 empty] | 0
826 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-04 | [8 empty] | 0
827 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-05 | [8 empty] | 0
828 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-06 | [8 empty] | 0
829 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-07 | [8 empty] | 0
830 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-08 | [8 empty] | 0
831 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-09 | [8 empty] | 0
832 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-10 | [8 empty] | 0
833 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-11 | [8 empty] | 0
834 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-12 | [8 empty] | 0
835 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-13 | [8 empty] | 0
836 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-14 | [8 empty] | 0
837 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-15 | [8 empty] | 0
838 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-16 | [8 empty] | 0
839 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-17 | [8 empty] | 0
840 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-18 | [8 empty] | 0
841 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-19 | [8 empty] | 0
842 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-20 | [8 empty] | 0
843 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-21 | [8 empty] | 0
844 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-22 | [8 empty] | 0
845 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-23 | [8 empty] | 0
846 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-24 | [8 empty] | 0
847 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-25 | [8 empty] | 0
848 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-26 | [8 empty] | 0
849 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-27 | [8 empty] | 0
850 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-28 | [8 empty] | 0
851 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-29 | [8 empty] | 0
852 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-30 | [8 empty] | 0
853 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-31 | [8 empty] | 0
854 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-01 | [8 empty] | 0
855 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-02 | [8 empty] | 0
856 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-03 | [8 empty] | 0
857 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-04 | [8 empty] | 0
858 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-05 | [8 empty] | 0
859 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-06 | [8 empty] | 0
860 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-07 | [8 empty] | 0
861 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-08 | [8 empty] | 0
862 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-09 | [8 empty] | 0
863 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-10 | [8 empty] | 0
864 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-11 | [8 empty] | 0
865 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-12 | [8 empty] | 0
866 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-13 | [8 empty] | 0
867 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-14 | 1 | 2 | 0 | 0 | 0 | 0 | 1764 | 294 | 2058 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
868 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
869 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-16 | 1 | 2 | 0 | 0 | 0 | 0 | 1722 | 420 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
870 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-17 | 1 | 2 | 0 | 0 | 0 | 0 | 1143 | 0 | 1143 | 0.25 | 0.41667 |  |  | MOP
871 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-18 | [8 empty] | 0
872 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-19 | [8 empty] | 0
873 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-20 | [8 empty] | 0
874 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-21 | [8 empty] | 0
875 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-22 | [8 empty] | 0
876 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-23 | [8 empty] | 0
877 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-24 | [8 empty] | 0
878 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-25 | [8 empty] | 0
879 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-26 | [8 empty] | 0
880 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-27 | [8 empty] | 0
881 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-28 | [8 empty] | 0
882 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-29 | [8 empty] | 0
883 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-30 | [8 empty] | 0
884 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-31 | [8 empty] | 0
885 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-01 | [8 empty] | 0
886 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-02 | [8 empty] | 0
887 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-03 | [8 empty] | 0
888 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-04 | [8 empty] | 0
889 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-05 | [8 empty] | 0
890 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-06 | [8 empty] | 0
891 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-07 | [8 empty] | 0
892 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-08 | [8 empty] | 0
893 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-09 | [8 empty] | 0
894 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-10 | [8 empty] | 0
895 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-11 | [8 empty] | 0
896 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-12 | [8 empty] | 0
897 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-13 | [8 empty] | 0
898 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-14 | [8 empty] | 0
899 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-15 | [8 empty] | 0
900 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-16 | [8 empty] | 0
901 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-17 | [8 empty] | 0
902 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-18 | [8 empty] | 0
903 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-19 | [8 empty] | 0
904 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-20 | [8 empty] | 0
905 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-21 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 2142 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
906 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-22 | 1 | 2 | 252 | 1533 | 0 | 0 | 0 | 252 | 2037 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
907 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-23 | 1 | 2 | 0 | 1533 | 567 | 0 | 0 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
908 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-24 | [8 empty] | 0 | [6 empty] | Due to Rain
909 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-25 | 1 | 2 | 0 | 0 | 0 | 2113 | 0 | 0 | 2113 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
910 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-26 | 1 | 2 | 0 | 0 | 513 | 1443 | 0 | 0 | 1956 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
911 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-27 | 1 | 2 | 0 | 0 | 0 | 933 | 0 | 0 | 933 | 0.25 | 0.41667 |  |  | MOP |  | MCS Pipe Damaged
912 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-28 | 1 | 2 | 0 | 0 | 0 | 2110 | 0 | 0 | 2110 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
913 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-29 | 1 | 2 | 0 | 0 | 1112 | 1026 | 0 | 0 | 2138 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
914 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-30 | 1 | 2 | 0 | 0 | 1112 | 984 | 0 | 0 | 2096 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
915 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-01 | [8 empty] | 0 | [6 empty] | Labour taken weekoff
916 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-02 | [8 empty] | 0 | [6 empty] | Due to Rain
917 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-03 | [8 empty] | 0 | [6 empty] | Due to Rain
918 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-04 | [8 empty] | 0 | [6 empty] | Due to Rain
919 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-05 | [8 empty] | 0 | [6 empty] | Due to Rain
920 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-06 | [8 empty] | 0 | [6 empty] | Due to Rain
921 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-07 | [8 empty] | 0 | [6 empty] | Due to Rain
922 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-08 | [8 empty] | 0 | [6 empty] | Due to Rain
923 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-09 | [8 empty] | 0 | [6 empty] | Due to Rain
924 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-10 | [8 empty] | 0 | [6 empty] | Due to Rain
925 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-11 | [8 empty] | 0 | [6 empty] | Due to Rain
926 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-12 | [8 empty] | 0 | [6 empty] | Due to Rain
927 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-13 | [8 empty] | 0 | [6 empty] | Due to Rain
928 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-14 | [8 empty] | 0 | [6 empty] | Due to Rain
929 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-15 | [8 empty] | 0
930 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-16 | [8 empty] | 0
931 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-17 | [8 empty] | 0
932 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-18 | [8 empty] | 0
933 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-19 | [8 empty] | 0
934 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-20 | [8 empty] | 0
935 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-21 | [8 empty] | 0
936 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-22 | [8 empty] | 0
937 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-23 | [8 empty] | 0
938 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | [8 empty] | 0
939 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-25 | [8 empty] | 0
940 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-26 | [8 empty] | 0
941 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-27 | [8 empty] | 0
942 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-28 | [8 empty] | 0
943 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-29 | [8 empty] | 0
944 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-30 | [8 empty] | 0
945 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-31 | [8 empty] | 0
946 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-01 | [8 empty] | 0
947 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-02 | [8 empty] | 0
948 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-03 | [8 empty] | 0
949 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-04 | [8 empty] | 0
950 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-05 | [8 empty] | 0
951 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-06 | [8 empty] | 0
952 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-07 | [8 empty] | 0
953 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-08 | [8 empty] | 0
954 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-09 | [8 empty] | 0
955 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-10 | 1 | 2 | 1134 | 0 | 0 | 0 | 966 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
956 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-11 | 1 | 2 | 1054 | 0 | 0 | 0 | 0 | 0 | 1054 | 0.25 | 0.41667 |  |  | MOP
957 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-12 | 1 | 2 | 0 | 1124 | 980 | 0 | 0 | 0 | 2104 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
958 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-13 | 1 | 2 | 0 | 1024 | 896 | 0 | 0 | 0 | 1920 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
959 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-14 | 1 | 2 | 126 | 1120 | 868 | 0 | 0 | 0 | 2114 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
960 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-15 | 2 | 2 | 1134 | 0 | 0 | 0 | 966 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
961 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-16 | [8 empty] | 0 | [6 empty] | Due to rain Module cleaning stop
962 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-17 | [8 empty] | 0 | [6 empty] | Due to rain Module cleaning stop
963 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-18 | 2 | 2 | 0 | 0 | 840 | 0 | 1120 | 0 | 1960 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
964 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-19 | 2 | 2 | 0 | 916 | 0 | 0 | 0 | 0 | 916 | 0.25 | 0.41667 |  |  | MOP
965 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-20 | 2 | 2 | 988 | 0 | 0 | 0 | 0 | 0 | 988 | 0.25 | 0.41667 |  |  | MOP
966 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-21 | 2 | 2 | 0 | 0 | 0 | 0 | 1008 | 0 | 1008 | 0.25 | 0.41667 |  |  | MOP
967 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-22 | 2 | 2 | 1386 | 0 | 0 | 0 | 756 | 0 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
968 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-23 | 2 | 2 | 0 | 504 | 630 | 210 | 672 | 0 | 2016 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
969 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-24 | 2 | 2 | 0 | 0 | 0 | 940 | 0 | 1120 | 2060 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
970 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-25 | 2 | 2 | 0 | 634 | 0 | 0 | 0 | 1340 | 1974 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
971 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-26 | 2 | 2 | 0 | 984 | 514 | 0 | 0 | 688 | 2186 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
972 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-27 | 2 | 2 | 0 | 0 | 1197 | 861 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
973 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-28 | 2 | 2 | 0 | 0 | 0 | 1995 | 0 | 0 | 1995 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
974 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-29 | 2 | 2 | 0 | 0 | 0 | 2034 | 0 | 0 | 2034 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
975 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-30 | 2 | 2 | 0 | 0 | 2142 | 0 | 0 | 0 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
976 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-01 | 2 | 2 | 1543 | 0 | 0 | 0 | 0 | 0 | 1543 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
977 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-02 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | not done due to rain
978 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-03 | 2 | 2 | 0 | 0 | 1012 | 0 | 0 | 0 | 1012 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
979 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-04 | 2 | 2 | 0 | 988 | 0 | 1024 | 0 | 0 | 2012 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
980 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-05 | 2 | 2 | 1046 | 0 | 985 | 0 | 0 | 0 | 2031 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
981 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-06 | 2 | 2 | 252 | 252 | 0 | 0 | 0 | 1512 | 2016 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 2 Completed
982 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-07 | 3 | 2 | 0 | 0 | 0 | 0 | 1344 | 735 | 2079 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
983 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-08 | 3 | 2 | 0 | 0 | 0 | 0 | 2058 | 0 | 2058 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
984 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-09 | 3 | 2 | 882 | 0 | 0 | 0 | 1155 | 0 | 2037 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
985 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-10 | 3 | 2 | 1449 | 630 | 0 | 0 | 0 | 0 | 2079 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
986 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-11 | 3 | 2 | 441 | 567 | 1050 | 0 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
987 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-12 | 3 | 2 | 315 | 756 | 1008 | 0 | 0 | 0 | 2079 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
988 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-13 | 3 | 2 | 1523 | 441 | 126 | 0 | 0 | 0 | 2090 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
989 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-14 | 3 | 2 | 1008 | 0 | 0 | 0 | 1134 | 0 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
990 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-15 | 3 | 2 | 0 | 504 | 504 | 462 | 0 | 672 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
991 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-16 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 2079 | 2079 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
992 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-17 | 3 | 4 | 252 | 1869 | 0 | 0 | 0 | 1239 | 3360 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
993 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-18 | 3 | 4 | 0 | 126 | 2845 | 294 | 0 | 0 | 3265 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
994 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-19 | 3 | 4 | 0 | 0 | 1201 | 2094 | 0 | 0 | 3295 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 3 Completed
995 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-20 | 4 | 4 | 0 | 0 | 1342 | 2024 | 0 | 0 | 3366 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
996 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-21 | 4 | 4 | 0 | 252 | 1436 | 1302 | 252 | 0 | 3242 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
997 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-22 | 4 | 2 | 324 | 630 | 819 | 252 | 252 | 0 | 2277 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
998 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-23 | 4 | 4 | 1250 | 1407 | 0 | 0 | 0 | 378 | 3035 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
997 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-24 | 4 | 4 | 1204 | 0 | 0 | 0 | 294 | 1743 | 3241 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
998 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-25 | 4 | 4 | 0 | 1242 | 0 | 0 | 2113 | 0 | 3355 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
999 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-26 | 4 | 2 | 0 | 0 | 0 | 0 | 1024 | 0 | 1024 | 0.25 | 0.41667 |  |  | MOP
1000 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-27 | 4 | 4 | 0 | 0 | 1038 | 252 | 2058 | 0 | 3348 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1001 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-28 | 4 | 4 | 2016 | 0 | 0 | 1024 | 189 | 0 | 3229 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1002 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-29 | 4 | 4 | 252 | 569 | 1113 | 0 | 1234 | 0 | 3168 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1003 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-30 | 4 | 4 | 1324 | 1824 | 0 | 0 | 0 | 0 | 3148 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 4 Completed
1004 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-31 | 5 | 4 | 0 | 2145 | 1345 | 0 | 0 | 0 | 3490 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1005 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-01 | 5 | 4 | 504 | 504 | 504 | 462 | 1428 | 168 | 3570 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1006 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-02 | 5 | 4 | 0 | 0 | 252 | 252 | 0 | 2646 | 3150 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1007 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-03 | 5 | 4 | 252 | 1785 | 0 | 0 | 0 | 1197 | 3234 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1008 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-04 | 5 | 4 | 252 | 1386 | 504 | 252 | 0 | 756 | 3150 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1009 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-05 | 5 | 2 | 0 | 1239 | 378 | 504 | 0 | 0 | 2121 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1010 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-06 | 5 | 2 | 0 | 252 | 756 | 609 | 630 | 0 | 2247 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1011 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-07 | 5 | 4 | 0 | 0 | 0 | 2037 | 1050 | 0 | 3087 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1012 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | 5 | 4 | 0 | 0 | 1024 | 2101 | 0 | 0 | 3125 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1013 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-09 | 5 | 4 | 0 | 0 | 1743 | 378 | 1050 | 0 | 3171 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1014 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-10 | 5 | 4 | 1197 | 567 | 315 | 0 | 1050 | 0 | 3129 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 5 Completed
1015 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-11 | 6 | 2 | 1134 | 504 | 0 | 0 | 609 | 0 | 2247 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1016 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-12 | 6 | 2 | 0 | 504 | 504 | 462 | 0 | 672 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1017 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-13 | 6 | 4 | 630 | 0 | 0 | 0 | 1428 | 1124 | 3182 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1018 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-14 | 6 | 2 | 1764 | 0 | 252 | 0 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1019 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-15 | 6 | 4 | 693 | 630 | 882 | 0 | 0 | 1134 | 3339 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1020 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-16 | 6 | 4 | 252 | 1071 | 0 | 892 | 0 | 945 | 3160 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1021 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-17 | 6 | 4 | 430 | 1113 | 378 | 609 | 630 | 0 | 3160 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1022 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-18 | 6 | 4 | 0 | 0 | 1197 | 1113 | 0 | 0 | 2310 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1023 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-19 | 6 | 4 | 0 | 0 | 0 | 2100 | 0 | 1124 | 3224 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1024 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-20 | 6 | 2 | 0 | 0 | 0 | 2184 | 0 | 0 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1025 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-21 | 6 | 2 | 0 | 0 | 1323 | 630 | 0 | 252 | 2205 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1026 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-22 | 6 | 4 | 0 | 1323 | 504 | 252 | 1113 | 0 | 3192 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 6 Completed
1027 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-23 | 7 | 4 | 252 | 1092 | 0 | 1197 | 0 | 693 | 3234 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1028 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-24 | 7 | 2 | 0 | 0 | 0 | 0 | 0 | 2164 | 2164 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1029 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | 7 | 2 | 0 | 0 | 0 | 0 | 2204 | 0 | 2204 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1030 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-26 | 7 | 2 | 0 | 0 | 0 | 0 | 2163 | 0 | 2163 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1031 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-27 | 7 | 4 | 0 | 504 | 504 | 462 | 1420 | 315 | 3205 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1032 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | 7 | 4 | 693 | 567 | 861 | 0 | 0 | 2071 | 4192 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1033 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-29 | 7 | 4 | 252 | 756 | 1134 | 0 | 0 | 1197 | 3339 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1034 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-30 | 7 | 4 | 1638 | 1123 | 0 | 0 | 609 | 0 | 3370 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1035 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-31 | 7 | 4 | 423 | 420 | 630 | 0 | 1638 | 0 | 3111 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1036 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-01 | 7 | 4 | 1071 | 0 | 1945 | 168 | 0 | 0 | 3184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1037 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-02 | 7 | 4 | 1824 | 0 | 1264 | 0 | 252 | 0 | 3340 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 7 Completed
1038 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-03 | 8 | 4 | 945 | 126 | 0 | 2184 | 0 | 0 | 3255 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1039 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-04 | 8 | 2 | 0 | 804 | 1323 | 0 | 0 | 0 | 2127 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1040 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-05 | 8 | 2 | 0 | 0 | 1512 | 693 | 0 | 0 | 2205 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1041 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-06 | 8 | 2 | 0 | 0 | 441 | 609 | 0 | 0 | 1050 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1042 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-07 | 8 | 2 | 0 | 2153 | 0 | 0 | 0 | 0 | 2153 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1043 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-08 | 8 | 2 | 252 | 0 | 0 | 0 | 0 | 819 | 1071 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1044 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-09 | 8 | 2 | 0 | 0 | 0 | 0 | 0 | 1008 | 1008 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1045 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-10 | 8 | 4 | 0 | 1123 | 0 | 0 | 0 | 2142 | 3265 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1046 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-11 | 8 | 4 | 824 | 946 | 0 | 1424 | 0 | 0 | 3194 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1047 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-12 | 8 | 4 | 0 | 1244 | 252 | 1684 | 0 | 0 | 3180 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1048 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-13 | 8 | 2 | 0 | 2146 | 0 | 0 | 0 | 0 | 2146 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1049 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-14 | 8 | 2 | 0 | 1342 | 842 | 0 | 0 | 0 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1050 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-15 | 8 | 2 | 1846 | 252 | 0 | 0 | 0 | 0 | 2098 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1051 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-16 | 8 | 4 | 1134 | 0 | 0 | 0 | 2164 | 0 | 3298 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 8 Completed
1052 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-17 | 9 | 4 | 1204 | 0 | 0 | 0 | 0 | 2240 | 3444 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1053 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-18 | 9 | 4 | 567 | 945 | 0 | 0 | 483 | 1134 | 3129 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1054 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-19 | 9 | 4 | 567 | 1232 | 0 | 0 | 1554 | 0 | 3353 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1055 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-20 | 9 | 4 | 1071 | 1365 | 630 | 252 | 0 | 0 | 3318 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1056 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-21 | 9 | 2 | 0 | 0 | 1008 | 1176 | 0 | 0 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1057 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-22 | 9 | 2 | 0 | 0 | 0 | 2134 | 0 | 1134 | 3268 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1058 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-23 | 9 | 2 | 0 | 1024 | 0 | 1244 | 0 | 0 | 2268 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1059 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-24 | 9 | 2 | 0 | 0 | 0 | 2100 | 0 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1060 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-25 | 9 | 4 | 0 | 1134 | 1386 | 630 | 0 | 0 | 3150 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1061 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-26 | 9 | 4 | 2394 | 0 | 630 | 0 | 0 | 0 | 3024 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1062 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-27 | 9 | 2 | 1230 | 0 | 0 | 0 | 0 | 0 | 1230 | 0.25 | 0.41667 |  |  | MOP |  | Due to festival labours taken weekoff/Cycle 9 completed
1063 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-28 | 10 | 4 | 1701 | 0 | 0 | 252 | 745 | 420 | 3118 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1064 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-01 | 10 | 2 | 0 | 0 | 0 | 0 | 2134 | 0 | 2134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1065 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-02 | 10 | 2 | 0 | 0 | 0 | 0 | 1113 | 0 | 1113 |  |  | 0.60417 | 0.77083 | MOP
1066 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-03 | 10 | 4 | 0 | 252 | 252 | 0 | 1092 | 1743 | 3339 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1067 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-04 | 10 | 4 | 252 | 504 | 504 | 252 | 1234 | 504 | 3250 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1068 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-05 | 10 | 4 | 0 | 945 | 1824 | 0 | 0 | 0 | 2769 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1069 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-06 | 10 | 4 | 0 | 1120 | 1449 | 252 | 0 | 0 | 2821 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1070 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-07 | 10 | 4 | 0 | 0 | 315 | 1743 | 0 | 2079 | 4137 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1071 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-08 | 10 | 4 | 2234 | 1124 | 0 | 0 | 0 | 0 | 3358 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1072 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-09 | 10 | 2 | 0 | 2144 | 0 | 0 | 0 | 0 | 2144 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1073 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-10 | 10 | 2 | 0 | 0 | 2343 | 0 | 0 | 0 | 2343 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1074 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-11 | 10 | 4 | 0 | 0 | 252 | 2724 | 0 | 0 | 2976 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 10 Completed
1075 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-12 | 11 | 2 | 0 | 0 | 2121 | 0 | 0 | 0 | 2121 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1076 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-13 | 11 | 4 | 0 | 0 | 820 | 2346 | 0 | 0 | 3166 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1077 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-14 | 11 | 2 | 1764 | 0 | 0 | 0 | 315 | 0 | 2079 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1078 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-15 | 11 | 4 | 252 | 1449 | 0 | 0 | 1176 | 378 | 3255 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1079 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-16 | 11 | 2 | 0 | 1352 | 504 | 252 | 0 | 0 | 2108 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1080 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-17 | 11 | 2 | 2346 | 0 | 0 | 0 | 0 | 0 | 2346 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1081 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-18 | 11 | 4 | 1260 | 567 | 0 | 0 | 693 | 0 | 2520 | 0.25 | 0.41667 |  |  | MOP
1082 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-19 | 11 | 2 | 252 | 714 | 252 | 0 | 0 | 1071 | 2289 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1083 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-20 | 11 | 2 | 0 | 504 | 504 | 462 | 0 | 1176 | 2646 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1084 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 11 | 4 | 2016 | 1124 | 0 | 0 | 0 | 0 | 3140 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1085 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-22 | 11 | 4 | 0 | 630 | 1449 | 0 | 1320 | 0 | 3399 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1086 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-23 | 11 | 2 | 2124 | 0 | 0 | 0 | 0 | 0 | 2124 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1087 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-24 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | not done due to rain
1088 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-25 | 12 | 2 | 0 | 2120 | 0 | 0 | 0 | 0 | 2120 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1089 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-26 | 12 | 4 | 1214 | 2134 | 0 | 0 | 0 | 0 | 3348 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1090 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-27 | 12 | 4 | 0 | 684 | 252 | 0 | 2234 | 0 | 3170 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1091 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-28 | 12 | 4 | 0 | 1894 | 0 | 0 | 1324 | 0 | 3218 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1092 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 12 | 4 | 0 | 0 | 1142 | 0 | 2134 | 0 | 3276 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1093 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 12 | 0 | [6 empty] | 0 | [6 empty] | Due to festival labours taken weekoff
1094 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 12 | 4 | 0 | 1324 | 1134 | 945 | 0 | 0 | 3403 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1095 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 12 | 2 | 1320 | 0 | 0 | 0 | 0 | 0 | 1320 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1096 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 12 | 2 | 0 | 1743 | 378 | 0 | 0 | 0 | 2121 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1097 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 12 | 2 | 252 | 315 | 0 | 0 | 0 | 567 | 1134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1098 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 12 | 0 | [6 empty] | 0 | [6 empty] | not done due to rain
1099 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 12 | 0 | [6 empty] | 0 | [6 empty] | not done due to rain
1100 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 12 | 4 | 2342 | 0 | 0 | 0 | 0 | 1234 | 3576 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1101 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 12 | 4 | 1164 | 2434 | 0 | 0 | 0 | 0 | 3598 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1102 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 12 | 2 | 0 | 0 | 1224 | 0 | 1110 | 0 | 2334 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 12 Completed
1103 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 13 | 4 | 1224 | 544 | 424 | 0 | 0 | 0 | 2192 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1104 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 13 | 2 | 1434 | 682 | 0 | 0 | 0 | 0 | 2116 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1105 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 13 | 2 | 1646 | 0 | 0 | 0 | 686 | 0 | 2332 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1106 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 13 | 2 | 0 | 0 | 1454 | 824 | 0 | 0 | 2278 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1107 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 13 | 2 | 868 | 1232 | 0 | 0 | 0 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1108 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 13 | 2 | 0 | 0 | 3224 | 0 | 0 | 0 | 3224 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1109 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 13 | 2 | 0 | 2324 | 0 | 0 | 0 | 0 | 2324 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1110 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 13 | 2 | 0 | 0 | 2268 | 0 | 0 | 0 | 2268 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1111 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 13 | 2 | 0 | 0 | 252 | 1980 | 0 | 0 | 2232 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1112 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 2224 | 2224 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1112 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 13 | 2 | 0 | 0 | 0 | 0 | 2134 | 0 | 2134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1113 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 13 | 2 | 0 | 0 | 1224 | 0 | 0 | 0 | 1224 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1114 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 13 | 2 | 1124 | 0 | 0 | 0 | 0 | 0 | 1124 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1115 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 13 | 2 | 0 | 0 | 0 | 0 | 2134 | 0 | 2134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1116 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 13 | 2 | 0 | 2245 | 0 | 0 | 0 | 0 | 2245 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1117 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 14 | 2 | 0 | 0 | 2320 | 0 | 0 | 0 | 2320 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1118 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 14 | 4 | 0 | 0 | 0 | 2342 | 0 | 1104 | 3446 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1119 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 14 | 4 | 0 | 0 | 624 | 2546 | 0 | 0 | 3170 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1120 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 14 | 4 | 0 | 0 | 0 | 0 | 3224 | 0 | 3224 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1121 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | not done due to rain
1122 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 14 | 2 | 2324 | 0 | 0 | 0 | 0 | 0 | 2324 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1123 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 14 | 2 | 0 | 2246 | 0 | 0 | 0 | 0 | 2246 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1124 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 14 | 2 | 0 | 0 | 1134 | 0 | 0 | 0 | 1134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1125 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1126 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 14 | 4 | 0 | 3212 | 0 | 1110 | 0 | 0 | 4322 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1127 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 14 | 2 | 0 | 0 | 0 | 0 | 1344 | 684 | 2028 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1128 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Not done due to labour taken weeklyoff
1129 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 14 | 2 | 0 | 2264 | 0 | 0 | 0 | 0 | 2264 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1130 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 14 | 2 | 1242 | 0 | 0 | 0 | 942 | 0 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1131 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 14 | 2 | 2246 | 0 | 0 | 0 | 0 | 0 | 2246 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1132 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 14 | 2 | 1024 | 504 | 504 | 252 | 0 | 0 | 2284 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | cycle 14 completed
1133 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 15 | 2 | 0 | 735 | 1113 | 252 | 0 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1134 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 15 | 2 | 1024 | 1232 | 0 | 0 | 0 | 0 | 2256 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1135 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 15 | 2 | 252 | 0 | 0 | 0 | 1924 | 0 | 2176 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1136 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 15 | 2 | 1624 | 525 | 0 | 0 | 0 | 0 | 2149 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1137 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 15 | 2 | 0 | 0 | 1638 | 504 | 0 | 0 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1138 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 15 | 2 | 0 | 0 | 0 | 2324 | 0 | 0 | 2324 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1139 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 15 | 2 | 0 | 0 | 0 | 1324 | 0 | 0 | 1324 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1140 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 15 | 2 | 0 | 0 | 0 | 2132 | 0 | 0 | 2132 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1141 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Not Done due to Rain
1142 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Not Done due to Rain
1143 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 15 | 2 | 0 | 0 | 1324 | 0 | 0 | 0 | 1324 |  |  | 0.60417 | 0.77083 | MOP
1144 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 15 | 2 | 0 | 0 | 1320 | 0 | 0 | 0 | 1320 |  |  | 0.60417 | 0.77083 | MOP
1145 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 15 | 2 | 0 | 0 | 1244 | 0 | 0 | 0 | 1244 |  |  | 0.60417 | 0.77083 | MOP
1146 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Not Done due to Rain
1147 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Not Done due to Rain
1148 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1149 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Not Done due to Rain
1150 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 15 | 2 | 1324 | 0 | 0 | 0 | 0 | 0 | 1324 |  |  | 0.60417 | 0.77083 | MOP
1151 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 15 | 2 | 1120 | 0 | 0 | 0 | 0 | 0 | 1120 | 0.25 | 0.41667
1152 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 15 | 2 | 0 | 2120 | 0 | 0 | 0 | 0 | 2120 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1153 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 15 | 2 | 0 | 2246 | 0 | 0 | 0 | 0 | 2246 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1154 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 15 | 2 | 0 | 2186 | 0 | 0 | 0 | 0 | 2186 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1155 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 15 | 2 | 0 | 1214 | 1024 | 0 | 0 | 0 | 2238 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1156 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 16 | 2 | 0 | 0 | 0 | 1232 | 0 | 0 | 1232 | 0.25 | 0.41667
1157 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 16 | [7 empty] | 0
1158 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 16 | 2 | 1424 | 252 | 624 | 0 | 0 | 0 | 2300 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1159 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 16 | 2 | 0 | 0 | 0 | 2132 | 0 | 0 | 2132 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1160 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 16 | 2 | 0 | 0 | 0 | 2234 | 0 | 0 | 2234 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1161 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 16 | 2 | 0 | 0 | 2424 | 0 | 0 | 0 | 2424 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1162 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 16 | 2 | 0 | 1212 | 0 | 0 | 0 | 0 | 1212 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1163 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 16 | 2 | 0 | 2240 | 0 | 0 | 0 | 0 | 2240 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1164 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1165 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Not Done due to Rain
1166 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 16 | 2 | 0 | 0 | 1214 | 0 | 0 | 0 | 1214 | 0.25 | 0.41667
1167 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 16 | 2 | 0 | 0 | 1124 | 0 | 0 | 0 | 1124 | 0.25 | 0.41667
1168 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 16 | 2 | 0 | 2320 | 0 | 0 | 0 | 0 | 2320 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1169 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 16 | 2 | 2100 | 0 | 0 | 0 | 0 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1170 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 16 | 2 | 0 | 0 | 2134 | 0 | 0 | 0 | 2134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1171 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 16 | 2 | 0 | 0 | 0 | 2232 | 0 | 0 | 2232 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1172 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 16 | 2 | 0 | 0 | 0 | 0 | 2104 | 0 | 2104 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1173 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 16 | 2 | 0 | 0 | 1124 | 0 | 0 | 0 | 1124 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1174 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 16 | 2 | 0 | 2232 | 0 | 0 | 0 | 0 | 2232 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1175 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 16 | 2 | 0 | 0 | 0 | 2263 | 0 | 0 | 2263 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1176 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1177 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 17 | 2 | 0 | 0 | 0 | 0 | 2100 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1178 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 17 | 2 | 0 | 0 | 2332 | 0 | 0 | 0 | 2332 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1179 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 17 | 2 | 0 | 0 | 0 | 2123 | 0 | 0 | 2123 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1180 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1181 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 17 | 2 | 0 | 2342 | 0 | 0 | 0 | 0 | 2342 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1182 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 17 | 2 | 0 | 0 | 2323 | 0 | 0 | 0 | 2323 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1183 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 17 | 2 | 0 | 0 | 0 | 0 | 2124 | 0 | 2124 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1184 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 17 | 2 | 0 | 0 | 0 | 0 | 0 | 2234 | 2234 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1185 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 17 | 2 | 2120 | 0 | 0 | 0 | 0 | 0 | 2120 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1186 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 17 | 2 | 2234 | 0 | 0 | 0 | 0 | 0 | 2234 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1187 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 17 | 2 | 0 | 2340 | 0 | 0 | 0 | 0 | 2340 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1188 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 17 | 2 | 0 | 0 | 0 | 0 | 2324 | 0 | 2324 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1189 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 17 | 2 | 0 | 0 | 2120 | 0 | 0 | 0 | 2120 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1190 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 17 | 2 | 0 | 0 | 0 | 2324 | 0 | 0 | 2324 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1191 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 17 | 2 | 0 | 2320 | 0 | 0 | 0 | 0 | 2320 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | cycle 17 completed
1192 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 18 | 2 | 2134 | 0 | 0 | 0 | 0 | 0 | 2134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1193 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 18 | 2 | 0 | 0 | 0 | 0 | 2120 | 0 | 2120 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1194 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 18 | 2 | 0 | 0 | 2120 | 0 | 0 | 0 | 2120 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1195 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 18 | 2 | 0 | 0 | 0 | 0 | 0 | 2140 | 2140 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1196 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 18 | 2 | 0 | 0 | 0 | 0 | 0 | 1132 | 1132 | 0.25 | 0.41667 |  |  | MOP
1197 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 18 | 2 | 2096 | 0 | 0 | 0 | 0 | 0 | 2096 | 0.25 | 0.41667 | 0.60417 | 0.60417 | MOP
1198 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 18 | 2 | 0 | 0 | 0 | 2120 | 0 | 0 | 2120 | 0.25 | 0.41667 | 0.60417 | 0.60417 | MOP
1199 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 18 | 2 | 0 | 0 | 2120 | 2120 | 0 | 0 | 4240 | 0.25 | 0.41667 | 0.60417 | 0.60417 | MOP
Formulas:
Days = DAY(EOMONTH([Month Year],0))
Date = [Date, row above]+1

## Grass_Cutting
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Cycle Number | Resources | IC1_Inv1_GC | IC1_Inv2_GC | IC1_Inv3_GC | IC1_Inv4_GC | IC2_Inv1_GC | IC2_Inv2_GC | Total Number of Table cut | Remarks for the day | Column1
1 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-01 | [8 empty] | 0
2 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-02 | [8 empty] | 0
3 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-03 | [8 empty] | 0
4 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-04 | [8 empty] | 0
5 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-05 | [8 empty] | 0
6 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-06 | [8 empty] | 0
7 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-07 | [8 empty] | 0
8 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-08 | [8 empty] | 0
9 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-09 | [8 empty] | 0
10 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-10 | [8 empty] | 0
11 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-11 | [8 empty] | 0
12 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-12 | [8 empty] | 0
13 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-13 | [8 empty] | 0
14 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-14 | [8 empty] | 0
15 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-15 | [8 empty] | 0
16 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-16 | [8 empty] | 0
17 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-17 | [8 empty] | 0
18 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-18 | [8 empty] | 0
19 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-19 | [8 empty] | 0
20 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-20 | [8 empty] | 0
21 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-21 | [8 empty] | 0
22 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-22 | [8 empty] | 0
23 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-23 | [8 empty] | 0
24 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-24 | [8 empty] | 0
25 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-25 | [8 empty] | 0
26 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-26 | [8 empty] | 0
27 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-27 | [8 empty] | 0
28 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-28 | [8 empty] | 0
29 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-29 | [8 empty] | 0
30 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-30 | [8 empty] | 0
31 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-01 | [8 empty] | 0
32 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-02 | [8 empty] | 0
33 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-03 | [8 empty] | 0
34 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-04 | [8 empty] | 0
35 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-05 | [8 empty] | 0
36 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | [8 empty] | 0
37 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-07 | [8 empty] | 0
38 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-08 | [8 empty] | 0
39 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-09 | [8 empty] | 0
40 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-10 | [8 empty] | 0
41 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-11 | [8 empty] | 0
42 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-12 | [8 empty] | 0
43 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-13 | [8 empty] | 0
44 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-14 | [8 empty] | 0
45 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-15 | [8 empty] | 0
46 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-16 | [8 empty] | 0
47 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-17 | [8 empty] | 0
48 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-18 | [8 empty] | 0
49 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-19 | [8 empty] | 0
50 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-20 | [8 empty] | 0
51 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-21 | [8 empty] | 0
52 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-22 | [8 empty] | 0
53 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-23 | [8 empty] | 0
54 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-24 | [8 empty] | 0
55 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-25 | [8 empty] | 0
56 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-26 | [8 empty] | 0
57 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-27 | [8 empty] | 0
58 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-28 | [8 empty] | 0
59 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-29 | [8 empty] | 0
60 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-30 | [8 empty] | 0
61 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-31 | [8 empty] | 0
62 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-01 | [8 empty] | 0
63 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-02 | [8 empty] | 0
64 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-03 | [8 empty] | 0
65 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-04 | [8 empty] | 0
66 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-05 | [8 empty] | 0
67 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-06 | [8 empty] | 0
68 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-07 | [8 empty] | 0
69 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-08 | [8 empty] | 0
70 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-09 | [8 empty] | 0
71 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-10 | [8 empty] | 0
72 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-11 | [8 empty] | 0
73 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-12 | [8 empty] | 0
74 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-13 | [8 empty] | 0
75 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-14 | [8 empty] | 0
76 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-15 | [8 empty] | 0
77 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-16 | [8 empty] | 0
78 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-17 | [8 empty] | 0
79 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-18 | [8 empty] | 0
80 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-19 | [8 empty] | 0
81 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-20 | [8 empty] | 0
82 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-21 | [8 empty] | 0
83 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-22 | [8 empty] | 0
84 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-23 | [8 empty] | 0
85 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-24 | [8 empty] | 0
86 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-25 | [8 empty] | 0
87 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-26 | [8 empty] | 0
88 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-27 | [8 empty] | 0
89 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-28 | [8 empty] | 0
90 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-29 | [8 empty] | 0
91 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-30 | [8 empty] | 0
92 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-01 | [8 empty] | 0
93 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-02 | [8 empty] | 0
94 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-03 | [8 empty] | 0
95 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-04 | [8 empty] | 0
96 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-05 | [8 empty] | 0
97 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-06 | [8 empty] | 0
98 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-07 | [8 empty] | 0
99 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-08 | [8 empty] | 0
100 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-09 | [8 empty] | 0
101 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-10 | [8 empty] | 0
102 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-11 | [8 empty] | 0
103 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | [8 empty] | 0
104 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-13 | [8 empty] | 0
105 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-14 | [8 empty] | 0
106 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | [8 empty] | 0
107 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-16 | [8 empty] | 0
108 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-17 | [8 empty] | 0
109 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-18 | [8 empty] | 0
110 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-19 | [8 empty] | 0
111 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-20 | [8 empty] | 0
112 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-21 | [8 empty] | 0
113 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-22 | [8 empty] | 0
114 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-23 | [8 empty] | 0
115 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-24 | [8 empty] | 0
116 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-25 | [8 empty] | 0
117 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-26 | [8 empty] | 0
118 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-27 | [8 empty] | 0
119 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-28 | [8 empty] | 0
120 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-29 | [8 empty] | 0
121 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-30 | [8 empty] | 0
122 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-31 | 1 | 2 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | Manually bushes cuttting
123 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-01 |  | 0 | [6 empty] | 0
124 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-02 | 1 | 2 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | Manually bushes cuttting Work completed
125 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-03 | 1 | 2 | 14 | 9 | 0 | 0 | 0 | 0 | 23 | Manually bushes cuttting Work completed
126 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-04 | 1 | 2 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | Manually bushes cuttting Work completed
127 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-05 | 1 | 2 | 6 | 0 | 0 | 0 | 0 | 21 | 27 | Manually bushes cuttting Work completed
128 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-06 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | Manually bushes cuttting Work completed
129 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-07 | 1 | 2 | 0 | 0 | 0 | 0 | 3 | 27 | 30 | Manually bushes cuttting Work completed
130 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-08 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | Manually bushes cuttting Work completed
131 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-09 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 39 | 39 | GRASS CUTTING WORK COMPLETED
132 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-10 | [8 empty] | 0
133 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-11 | [8 empty] | 0
134 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-12 | [8 empty] | 0
135 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-13 | [8 empty] | 0
136 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-14 | [8 empty] | 0
137 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-15 | [8 empty] | 0
138 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-16 | [8 empty] | 0
139 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-17 | [8 empty] | 0
140 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-18 | [8 empty] | 0
141 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | [8 empty] | 0
142 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-20 | [8 empty] | 0
143 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-21 | [8 empty] | 0
144 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-22 | [8 empty] | 0
145 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-23 | [8 empty] | 0
146 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-24 | [8 empty] | 0
147 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-25 | [8 empty] | 0
148 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-26 | [8 empty] | 0
149 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-27 | [8 empty] | 0
150 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-28 | [8 empty] | 0
151 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-29 | [8 empty] | 0
152 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-30 | [8 empty] | 0
153 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-31 | [8 empty] | 0
154 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-01 | [8 empty] | 0
155 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-02 | [8 empty] | 0
156 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-03 | [8 empty] | 0
157 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | [8 empty] | 0
158 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-05 | [8 empty] | 0
159 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-06 | [8 empty] | 0
160 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-07 | [8 empty] | 0
161 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-08 | [8 empty] | 0
162 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-09 | [8 empty] | 0
163 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-10 | [8 empty] | 0
164 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-11 | [8 empty] | 0
165 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-12 | [8 empty] | 0
166 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-13 | [8 empty] | 0
167 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-14 | 1 | 0 | [6 empty] | 0 | Spare area grass cutting work in progress
168 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-15 | 1 | 0 | [6 empty] | 0 | Spare area grass cutting work was completed
169 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-16 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | MCR,Switchyard Grass cutting work was completed
170 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-17 | 1 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 1.5 | Grass cutting work was completed
171 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-18 | [8 empty] | 0
172 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-19 | 1 | 0 | 9 | 0 | 0 | 0 | 4 | 0 | 13 | Grass cutting work was completed
173 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-20 | 1 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 21 | Grass cutting work was completed
174 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-21 | 1 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 15 | Grass cutting work was completed
175 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-22 | 1 | 0 | 13 | 6 | 0 | 0 | 0 | 0 | 19 | Grass cutting work was completed
176 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-23 | [8 empty] | 0
177 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-24 | [8 empty] | 0
178 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-25 | [8 empty] | 0
179 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-26 | [8 empty] | 0
180 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-27 | 1 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | Grass cutting work was completed
181 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-28 | 1 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 11 | ICR 2 Road side Grass cutting work was completed
182 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-29 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | Grass cutting work was completed
183 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-30 | [8 empty] | 0
184 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-01 | [8 empty] | 0
185 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-02 | [8 empty] | 0
186 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-03 | [8 empty] | 0
187 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-04 | [8 empty] | 0
188 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-05 | [8 empty] | 0
189 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-06 | [8 empty] | 0
190 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | [8 empty] | 0
191 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR gate & ICR2 outside area Grass cutting work was completed
192 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-09 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR road side & Store outside area Grass cutting work was completed
193 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-10 | [8 empty] | 0
194 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | [8 empty] | 0
195 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-12 | [8 empty] | 0
196 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-13 | 1 | 0 | 0 | 8 | 1.5 | 0 | 0 | 0 | 9.5 | Main gate & MCR fence area grass cutting work was completed
197 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-14 | 1 | 0 | 0 | 0 | 17.5 | 0 | 0 | 0 | 17.5 | Grass cutting work was completed
198 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-15 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | ICR 1 surrounding area grass cutting work was completed
199 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-16 | [8 empty] | 0
200 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-17 | 1 | 0 | 0 | 0 | 8.5 | 0 | 0 | 0 | 8.5 | Weather station, MCS area grass cutting work was completed
201 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-18 | [8 empty] | 0
202 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-19 | [8 empty] | 0
203 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-20 | [8 empty] | 0
204 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-21 | [8 empty] | 0
205 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-22 | [8 empty] | 0
206 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-23 | [8 empty] | 0
207 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-24 | [8 empty] | 0
208 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-25 | [8 empty] | 0
209 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-26 | [8 empty] | 0
210 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-27 | [8 empty] | 0
211 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-28 | [8 empty] | 0
212 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-29 | [8 empty] | 0
213 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-30 | [8 empty] | 0
214 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-31 | [8 empty] | 0
215 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-01 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR & Switch yard area grass cutting work was completed
216 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-02 | [8 empty] | 0
217 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-03 | [8 empty] | 0
218 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-04 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 2.5 | 2.5 | Main gate road side area grass cutting work was completed
219 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-05 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.5 | 7.5 | Grass cutting work was completed
220 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-06 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 32 | 32 | Grass cutting work was completed
221 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-07 | 1 | 2 | 4 | 0 | 0 | 0 | 0 | 14 | 18 | Grass cutting work was completed
222 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-08 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 31 | 31 | Grass cutting work was completed
223 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-09 | [8 empty] | 0
224 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-10 | [8 empty] | 0
225 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-11 | [8 empty] | 0
226 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-12 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 20.5 | 20.5 | Grass cutting work was completed
227 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-13 | 1 | 2 | 0 | 8 | 6 | 7 | 0 | 0 | 21 | Grass cutting work was completed
228 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-14 | 1 | 2 | 6 | 14 | 6 | 4 | 0 | 0 | 30 | Grass cutting work was completed
229 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-15 | 1 | 2 | 23 | 8.5 | 0 | 0 | 0 | 0 | 31.5 | Grass cutting work was completed
230 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-16 | 1 | 1 | 15.5 | 0 | 0 | 0 | 0 | 0 | 15.5 | Grass cutting work was completed
231 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-17 | 1 | 2 | 24.5 | 8 | 0 | 0 | 4.5 | 0 | 37 | Grass cutting work was completed
232 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-18 | 1 | 1 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | Grass cutting work was completed
233 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-19 | 1 | 2 | 0 | 17.5 | 0 | 0 | 0 | 0 | 17.5 | Grass cutting work was completed
234 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-20 | 1 | 1 | 0 | 10.5 | 0 | 0 | 0 | 0 | 10.5 | Grass cutting work was completed
235 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-21 | [8 empty] | 0
236 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-22 | [8 empty] | 0
237 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-23 | [8 empty] | 0
238 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-24 | 1 | 2 | 0 | 1 | 10 | 0 | 0 | 0 | 11 | Grid5-Grass cutting work done
239 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-25 | 1 | 2 | 4 | 6 | 0 | 6 | 0 | 6 | 22 | Grid5&6-Grass cutting work done
240 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-26 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Grid 5&6 road side area grass cutting work was completed
241 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-27 | 1 | 1 | 0 | 0 | 4 | 1 | 0 | 0 | 5 | Grid 3&4 road side area grass cutting work was completed
242 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-28 | 1 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 9 | Grid5 Grass Cutting work completed
243 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-29 | [8 empty] | 0
244 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-30 | 1 | 2 | 0 | 0 | 6 | 11 | 0 | 0 | 17 | Grid5 Grass Cutting work completed
245 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-01 | 1 | 2 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | Grid5 Grass Cutting work completed
246 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-02 | 1 | 2 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | Grid5 Grass Cutting work completed
247 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-03 | 1 | 2 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | Grid4&5 Grass Cutting work completed
248 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-04 | 1 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | Grid4 Grass Cutting work completed
249 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-05 | [8 empty] | 0
250 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-06 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 10 | 12 | Grid1 Grass Cutting work completed
251 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-07 | 1 | 1 | 0 | 0 | 0 | 0 | 14 | 0 | 14 | Grid1 Grass Cutting work completed
252 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-08 | 1 | 2 | 0 | 0 | 0 | 0 | 29 | 0 | 29 | Grid1&2 Grass Cutting work completed
253 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-09 | [8 empty] | 0
254 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-10 | [8 empty] | 0
255 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-11 | 1 | 2 | 0 | 0 | 0 | 0 | 27 | 0 | 27 | Grid 2 - Inv 5 - T3 to T29 - 27 Tables Grass cutting work completed
256 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-12 | 1 | 2 | 0 | 0 | 13 | 0 | 11 | 0 | 24 | Grid2-Inv5-T30 to T40 & Grid4-Inv3-T88 to T100 - 24 Tables Grass cutting work completed
257 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-13 | 1 | 2 | 0 | 0 | 5 | 16 | 0 | 0 | 21 | Grid4-Inv3-T101 to T105 & Inv4-T106 to T121 - 21 Tables Grass cutting work completed
258 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-14 | 1 | 2 | 0 | 24 | 0 | 5 | 0 | 0 | 29 | Grid4-Inv4-T122 to T126 & Grid6-Inv2-T50 to T73-29 Tables Grass cutting work completed
259 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-15 | 1&2 | 2 | 0 | 6 | 9 | 0 | 17 | 0 | 32 | G6-Inv2-6nos&Inv3-9nos-T74 to T88-15Tables(Cycle1 Completed) & G4-Inv5-T1toT17-17 Tables
260 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-16 | [8 empty] | 0
261 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-17 | 2 | 1 | 0 | 0 | 0 | 0 | 6 | 0 | 6 | G4-Inv5-T18 to 23 - 6 Tables Grass cutting work completed
262 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-18 | 2 | 1 | 6 | 0 | 0 | 0 | 13 | 0 | 19 | G3-Inv1-T8 to T13 & Inv5 -G3A- T1 to T5, G3-TW01,T1 to T7-19 Tables
263 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-19 | [8 empty] | 0
264 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-20 | 2 | 2 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | G3-Inv1-T14 to T27 - 14 Tables Grass cutting work completed
265 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-21 | [8 empty] | 0
266 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-22 | 2 | 1 | 11 | 0 | 0 | 0 | 2 | 0 | 13 | Grid4-Inv5-T24 to T25 & Inv1-T26 to T36 - 13 Tables Grass Cutting work completed
267 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-23 | 2 | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | Inv1-T37 to T48 - 12 Tables Grass Cutting work completed
268 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-24 | [8 empty] | 0
269 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-25 | [8 empty] | 0
270 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-26 | [8 empty] | 0
271 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-27 | [8 empty] | 0
272 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-28 | [8 empty] | 0
273 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-29 | [8 empty] | 0
274 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-30 | [8 empty] | 0
275 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-31 | [8 empty] | 0
276 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-01 | [8 empty] | 0
277 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-02 | [8 empty] | 0
278 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-03 | [8 empty] | 0
279 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-04 | [8 empty] | 0
280 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-05 | [8 empty] | 0
281 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-06 | [8 empty] | 0
282 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-07 | [8 empty] | 0
283 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-08 | [8 empty] | 0
284 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-09 | [8 empty] | 0
285 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-10 | [8 empty] | 0
286 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-11 | 2 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | G3-Inv1-T28 to T35 - 08 Tables & Storage yard area Grass cutting work completed
287 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-12 | 2 | 1 | 9 | 4 | 0 | 0 | 0 | 0 | 13 | G3-T36 to T49 - 13 Tables & Storage yard area Grass cutting work completed
288 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-13 | 2 | 1 | 0 | 4 | 15 | 0 | 0 | 0 | 19 | G3-T50 to T68 - 19 Tables Grass cutting work completed
289 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-14 | [8 empty] | 0
290 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | [8 empty] | 0
291 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | [8 empty] | 0
292 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-17 | [8 empty] | 0
293 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-18 | 3 | 1 | [6 empty] | 0 | ICR 1&2 Non PV area Grass Cutting work done
294 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-19 | 3 | 1 | [6 empty] | 0 | MCR & Storage yard area Grass Cutting work done
295 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-20 | [8 empty] | 0
296 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-21 | [8 empty] | 0
297 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-22 | [8 empty] | 0
298 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-23 | [8 empty] | 0
299 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-24 | [8 empty] | 0
300 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-25 | [8 empty] | 0
301 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-26 | [8 empty] | 0
302 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-27 | [8 empty] | 0
303 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | [8 empty] | 0
304 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-29 | [8 empty] | 0
305 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-30 | [8 empty] | 0
306 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-31 | [8 empty] | 0
307 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-01 | [8 empty] | 0
308 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-02 | [8 empty] | 0
309 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-03 | [8 empty] | 0
310 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-04 | [8 empty] | 0
311 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | [8 empty] | 0
312 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-06 | [8 empty] | 0
313 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-07 | [8 empty] | 0
314 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-08 | [8 empty] | 0
315 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | [8 empty] | 0
316 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-10 | [8 empty] | 0
317 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-11 | [8 empty] | 0
318 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-12 | [8 empty] | 0
319 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-13 | [8 empty] | 0
320 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-14 | [8 empty] | 0
321 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-15 | [8 empty] | 0
322 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-16 | [8 empty] | 0
323 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | [8 empty] | 0
324 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-18 | [8 empty] | 0
325 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-19 | [8 empty] | 0
326 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-20 | [8 empty] | 0
327 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-21 | [8 empty] | 0
328 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-22 | [8 empty] | 0
329 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-23 | [8 empty] | 0
330 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-24 | [8 empty] | 0
331 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-25 | [8 empty] | 0
332 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-26 | [8 empty] | 0
333 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-27 | [8 empty] | 0
334 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-28 | [8 empty] | 0
335 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-01 | [8 empty] | 0
336 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-02 | [8 empty] | 0
337 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-03 | [8 empty] | 0
338 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | [8 empty] | 0
339 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-05 | [8 empty] | 0
340 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-06 | [8 empty] | 0
341 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-07 | [8 empty] | 0
342 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-08 | [8 empty] | 0
343 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-09 | [8 empty] | 0
344 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-10 | [8 empty] | 0
345 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-11 | [8 empty] | 0
346 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-12 | [8 empty] | 0
347 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-13 | [8 empty] | 0
348 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-14 | [8 empty] | 0
349 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-15 | [8 empty] | 0
350 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-16 | [8 empty] | 0
351 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-17 | [8 empty] | 0
352 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-18 | [8 empty] | 0
353 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-19 | [8 empty] | 0
354 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-20 | [8 empty] | 0
355 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-21 | [8 empty] | 0
356 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-22 | [8 empty] | 0
357 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-23 | [8 empty] | 0
358 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-24 | [8 empty] | 0
359 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-25 | [8 empty] | 0
360 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-26 | [8 empty] | 0
361 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-27 | [8 empty] | 0
362 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-28 | [8 empty] | 0
363 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-29 | [8 empty] | 0
364 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-30 | [8 empty] | 0
365 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-31 | [8 empty] | 0
366 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-01 | [8 empty] | 0
367 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-02 | [8 empty] | 0
368 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-03 | [8 empty] | 0
369 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-04 | [8 empty] | 0
370 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-05 | [8 empty] | 0
371 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-06 | [8 empty] | 0
372 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-07 | [8 empty] | 0
373 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-08 | [8 empty] | 0
374 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-09 | [8 empty] | 0
375 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-10 | [8 empty] | 0
376 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-11 | [8 empty] | 0
377 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | [8 empty] | 0
378 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-13 | [8 empty] | 0
379 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-14 | [8 empty] | 0
380 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-15 | [8 empty] | 0
381 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-16 | [8 empty] | 0
382 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-17 | [8 empty] | 0
383 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-18 | [8 empty] | 0
384 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-19 | [8 empty] | 0
385 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-20 | [8 empty] | 0
386 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-21 | [8 empty] | 0
387 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-22 | [8 empty] | 0
388 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-23 | [8 empty] | 0
389 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | [8 empty] | 0
390 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-25 | [8 empty] | 0
391 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | [8 empty] | 0
392 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-27 | [8 empty] | 0
393 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-28 | [8 empty] | 0
394 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-29 | [8 empty] | 0
395 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-30 | [8 empty] | 0
396 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-01 | [8 empty] | 0
397 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-02 | [8 empty] | 0
398 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-03 | [8 empty] | 0
399 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-04 | [8 empty] | 0
400 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-05 | [8 empty] | 0
401 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-06 | [8 empty] | 0
402 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-07 | [8 empty] | 0
403 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-08 | [8 empty] | 0
404 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-09 | [8 empty] | 0
405 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-10 | [8 empty] | 0
406 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-11 | [8 empty] | 0
407 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-12 | [8 empty] | 0
408 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-13 | [8 empty] | 0
409 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-14 | [8 empty] | 0
410 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-15 | [8 empty] | 0
411 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-16 | [8 empty] | 0
412 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-17 | [8 empty] | 0
413 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-18 | [8 empty] | 0
414 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-19 | [8 empty] | 0
415 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | [8 empty] | 0
416 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-21 | [8 empty] | 0
417 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-22 | [8 empty] | 0
418 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-23 | [8 empty] | 0
419 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-24 | [8 empty] | 0
420 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | [8 empty] | 0
421 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-26 | [8 empty] | 0
422 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-27 | [8 empty] | 0
423 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-28 | 2 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G3A-Inv5-TW1, T1 to T5 - 06 Tables & G3-Inv5-T1 to T4 - 04 Tables Grass cutting work completed
424 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-29 | [8 empty] | 0
425 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-30 | 2 | 1 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | G3-Inv5-T5 to T7 & Inv1-T8 toT10 - 06 Tables Grass cutting work completed
426 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-31 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ICR 1 & 2 Surrounding Area Grass cutting work completed
427 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-01 | 2 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G3-Inv1-T11 toT19 - 09 Tables Grass cutting work completed
428 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-02 | [8 empty] | 0
429 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-03 | 2 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | G3-Inv1-T20 toT21 - 02 Tables Grass cutting work completed
430 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-04 | 2 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | G3-Inv1-T22 toT26 - 05 Tables Grass cutting work completed
431 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-05 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Non PV area Grass cutting work done
432 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-06 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Non PV area Grass cutting work done
433 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-07 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Non PV area Grass cutting work done
434 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-08 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Non PV area Grass cutting work done
435 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-09 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Non PV area Grass cutting work done
436 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-10 | 2 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | G3-Inv1-T27 toT31 - 05 Tables Grass cutting work completed
437 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-11 | 2 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G3-Inv1-T32 toT37 - 06 Tables Grass cutting work completed
438 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-12 | [8 empty] | 0
439 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-13 | [8 empty] | 0
440 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-14 | 2 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G3-Inv1-T38 toT43 - 06 Tables Grass cutting work completed
441 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-15 | 2 | 2 | 1 | 9 | 2 | 0 | 0 | 0 | 12 | G3-Inv1-T44, Inv2-T45 to T53 & Inv3-T54 toT55 - 12 Tables Grass cutting work completed
442 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-16 | 2 | 1 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | G3-Inv3-T56 toT65 - 10 Tables Grass cutting work completed
443 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-17 | 2 | 1 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | G3-Inv3-T66 toT68 & G4-Inv3-T85 to T88 - 7 Tables Grass cutting work completed
444 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-18 | 2 | 1 | 0 | 0 | 4 | 0 | 0 | 0 | 4 | G4-Inv3-T81 toT84 - 4 Tables & MCR surrounding area Grass cutting work completed
445 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-19 | 2 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | G4-Inv3-T78 toT80 - 3 Tables & MCR surrounding area Grass cutting work completed
446 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-20 | 2 | 1 | 0 | 1 | 5 | 0 | 0 | 0 | 6 | G4-Inv2-T72 & Inv3 - T73 toT77 - 6 Tables Grass cutting work completed
447 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-21 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ICR 1 surrounding area grass cutting work was completed
448 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-22 | 2 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 6 | G4-Inv3 - T88 toT93 - 6 Tables Grass cutting work completed
449 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-23 | 2 | 1 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | G4-Inv3 - T94 toT100 - 7 Tables Grass cutting work completed
450 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-24 | 2 | 1 | 0 | 0 | 5 | 1 | 2 | 0 | 8 | G4-Inv3 - T101 toT105, Inv4 - T106 & Inv5 - T10 to T11 - 8 Tables Grass cutting work completed
451 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-25 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G4-Inv4 - T107 toT114 - 8 Tables Grass cutting work completed
452 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-26 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G4-Inv4 - T115 toT122 - 8 Tables Grass cutting work completed
453 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-27 | 2 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | G4-Inv4 - T123 toT131 - 9 Tables Grass cutting work completed
454 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-28 | 2 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | G4-Inv4 - T132 toT140 - 9 Tables Grass cutting work completed
455 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-29 | [8 empty] | 0
456 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-30 | [8 empty] | 0
457 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-01 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | G1-Inv6 - T47 toT52 - 6 Tables & MCR road side area Grass cutting work completed
458 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | 2 | 1 | 0 | 0 | 0 | 0 | 7 | 4 | 11 | G1-Inv6 - T43 toT46 & Inv5 - T36 to T42 - 11 Tables Grass cutting work completed
459 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-03 | 2 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G1-Inv5 - T26 to T35 - 10 Tables Grass cutting work completed
460 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-04 | 2 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G1-Inv5 - T17 to T25 - 9 Tables Grass cutting work completed
461 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-05 | 2 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G1-Inv5 - T8 to T16 - 9 Tables Grass cutting work completed
462 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-06 | 2 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G1-Inv5 - T1 to T7 & G2-Inv5 - TW1 - 8 Tables Grass cutting work completed
463 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-07 | 2 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G2-Inv5 - T1 to T7 - 7 Tables Grass cutting work completed
464 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-08 | 2 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G2-Inv5 - T8 to T15 - 8 Tables Grass cutting work completed
465 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-09 | 2 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G2-Inv5 - T16 to T23 - 8 Tables Grass cutting work completed
466 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-10 | 2 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G2-Inv5 - T24 to T31 - 8 Tables Grass cutting work completed
467 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-11 | 2 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G2-Inv5 - T32 to T40 - 9 Tables Grass cutting work completed
468 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-12 | 2 | 1 | 0 | 0 | 0 | 0 | 6 | 0 | 6 | G4-Inv5 - T1 to T6 - 6 Tables & MCR surrounding area Grass cutting work completed
469 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-13 | 2 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G4-Inv5 - T7 to T13 - 7 Tables Grass cutting work completed
470 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-14 | 2 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G4-Inv5 - T14 to T20 - 7 Tables Grass cutting work completed
471 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-15 | 2 | 1 | 2 | 0 | 0 | 0 | 5 | 0 | 7 | G4-Inv5 & Inv1 - T21 to T27 - 7 Tables Grass cutting work completed
472 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-16 | 2 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | G4-Inv1 - T28 to T32 - 5 Tables Grass cutting work completed
473 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-17 | 2 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | G4-Inv1 - T33 to T37 - 5 Tables Grass cutting work completed
474 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-18 | 2 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G4-Inv1 - T38 to T43 - 6 Tables Grass cutting work completed
475 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-19 | 2 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | G4-Inv1 - T44 to T50 - 7 Tables Grass cutting work completed
476 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-20 | 2 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G4-Inv1 - T51 to T56 - 6 Tables Grass cutting work completed
477 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-21 | 2 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G4-Inv1 - T57 to T62 - 6 Tables Grass cutting work completed
478 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-22 | 2 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | G4-Inv2 - T63 to T68 - 6 Tables Grass cutting work completed
479 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-23 | 2 | 1 | 0 | 3 | 2 | 0 | 0 | 0 | 5 | G4-Inv2 - T69 to T71 G5-Inv3-T93 to T94 -5 Tables Grass cutting work completed
480 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-24 | 2 | 1 | 0 | 0 | 4 | 0 | 0 | 0 | 4 | G5-Inv3 - T 94 to T 97 - 4 Tables Grass cutting work completed
481 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | 2 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | G5-Inv3 - T 98 to T 100 - 3 Tables Grass cutting work completed
482 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-26 | [8 empty] | 0
483 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-27 | [8 empty] | 0
484 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-28 | 2 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 5 | G4-Inv3 - T 87 to T 91 - 5 Tables Grass cutting work completed
485 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | 2 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | G5-Inv3 - T 101 to T 108 - 8 Tables Grass cutting work completed
486 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-30 | 2 | 1 | 0 | 0 | 2 | 4 | 0 | 0 | 6 | G5-Inv3 & Inv4 - T109 to T113 - 6 Tables Grass cutting work completed
487 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-31 | 2 | 1 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | G5- Inv4 - T114 to T118 - 5 Tables Grass cutting work completed
488 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-01 | 2 | 1 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | G5- Inv4 - T119 to T123 - 5 Tables Grass cutting work completed
489 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-02 | 2 | 1 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | G5- Inv4 - T124 to T128 - 5 Tables Grass cutting work completed
490 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-03 | 2 | 2 | 0 | 0 | 3 | 7 | 0 | 0 | 10 | G5- Inv4 - T129 to T135 - 7 Tables & G6-Inv3 - T 86 to T 88 - 3 Tables Grass cutting work completed
491 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-04 | 2 | 2 | 0 | 6 | 6 | 12 | 0 | 0 | 24 | G5- Inv4 - T136 to T147 - 12 Tables & G6-Inv2 & Inv 3 - T 86 to T 88 - 12 Tables Grass cutting work completed
492 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-05 | 2 | 2 | 0 | 12 | 0 | 11 | 0 | 0 | 23 | G5- Inv4 - T148 to T158 - 11 Tables & G6-Inv2 - T 62 to T 73 - 12 Tables Grass cutting work completed
493 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-06 | 2 | 2 | 0 | 9 | 0 | 0 | 0 | 8 | 17 | G5- Inv6 - T1 to T8 - 8 Tables & G6-Inv2 - T 53 to T 61 - 9 Tables Grass cutting work completed
494 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-07 | 2 | 2 | 0 | 8 | 0 | 0 | 0 | 10 | 18 | G5- Inv6 - T9 to T18 - 10 Tables & G6-Inv2 - T 45 to T 52 - 8 Tables Grass cutting work completed
495 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-08 | 2 | 2 | 4 | 1 | 0 | 0 | 0 | 10 | 15 | G5- Inv6 - T19 to T22 - 4 Tables & G6- Inv1,2 & 6 - T 44 to T 34 - 11 Tables Grass cutting work completed
496 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-09 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 11 | 11 | G6- Inv6 - T 23 to T 33 - 11 Tables Grass cutting work completed - Cycle 2 Completed
497 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-10 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 13 | 13 | G6- Inv6 - T 22 to T 12 - 11 Tables Grass cutting work completed & G5- Inv6 - 23 to 24 - 2
498 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-11 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | G6- Inv6 - T 6 to T 11 - 6 Tables & Grid 5 Non PV area Grass cutting work completed
499 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-12 | 3 | 1 | 0 | 0 | 0 | 1 | 0 | 5 | 6 | G6- Inv6&4 - T 1 to T 5 & TW1 - 6 Tables Grass cutting work completed
500 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-13 | 3 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 10 | G5- Inv3&4 - TW2 to TW11 - 10 Tables Grass cutting work completed
501 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-14 | 3 | 2 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | G5- Inv2 - TW12 to TW18 - 7 Tables & G6- Inv2 - TW13 to TW16 - 4 Tables & MCR Area Grass cutting work completed
502 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-15 | 1 | 1 | 0 | 0 | 6 | 6 | 0 | 0 | 12 | G6- Inv3 &Inv4 - TW1 to TW12 - 12 Tables Grass cutting work completed - 2nd Contractual year started
503 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-16 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | G5- Inv6 - T25 to T30 - 6 Tables Grass cutting work completed
504 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-17 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | G5- Inv6 - T31 to T35 - 5 Tables Grass cutting work completed
505 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-18 | 1 | 1 | 4 | 1 | 0 | 0 | 0 | 1 | 6 | G5- Inv6 - T36 to T41 - 6 Tables Grass cutting work completed
506 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-19 | 1 | 1 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | G5- Inv6 - T42 to T48 - 7 Tables Grass cutting work completed
507 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-20 | 1 | 1 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | G5- Inv6 - T49 to T57 - 9 Tables Grass cutting work completed
508 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-21 | 1 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | G5- Inv6 - T58 to T63 - 6 Tables Grass cutting work completed
509 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-22 | 1 | 1 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | G5- Inv6 - T64 to T70 - 7 Tables Grass cutting work completed
510 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-23 | 1 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | G5- Inv6 - T71 to T75 - 5 Tables Grass cutting work completed
511 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-24 | 1 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 6 | G5- Inv3 - T76 to T81 - 6 Tables Grass cutting work completed
512 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-25 | 1 | 1 | 0 | 0 | 4 | 6 | 0 | 0 | 10 | G5- Inv3&4 - T82 to T86 & G4-Inv4-T139 to T143 - 10 Tables Grass cutting work completed
513 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-26 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Store Spare Area Grass Cutting Work Done
514 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-27 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Store Spare Area Grass Cutting Work Done
515 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-28 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G3-TW1 & T1, G3A-T1 to T5 - Inv5 - 7 Tables Grass cutting work completed
516 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-29 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 Fence side area Grass cutting work done
517 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-30 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Fence side area Grass cutting work done
518 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-31 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Fence side area Grass cutting work done
519 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-01 | 1 | 1 | 0 | 0 | 0 | 0 | 6 | 0 | 6 | G3 -T3 to T6-Inv 5 -6 Tables Grass cutting work completed & G4 Fence side area Grass cutting work done
520 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-02 | 1 | 1 | 4 | 0 | 0 | 0 | 1 | 0 | 5 | G3 -T7 to T11-Inv 5 & Inv 1 -5 Tables Grass cutting work completed
521 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-03 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G3 -T12 to T20- Inv 1 -9 Tables Grass cutting work completed
522 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-04 | 1 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | G3 -T21 to T28- Inv 1 -8 Tables Grass cutting work completed
523 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-05 | 1 | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | G3 -T29 to T38- Inv 1 -10 Tables Grass cutting work completed
524 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-06 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR Surrounding Area Grass Cutting Work Done
525 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-07 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Store Spare Area Grass Cutting Work Done
526 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-08 | 1 | 1 | 6 | 4 | 0 | 0 | 0 | 0 | 10 | G3 -T39 to T48- Inv 1 & Inv 2 -10 Tables Grass cutting work completed
527 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-09 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Main gate road side area grass cutting work was completed
528 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-10 | 1 | 1 | 0 | 5 | 5 | 0 | 0 | 0 | 10 | G3 -T49 to T58- Inv2 & Inv 3 -10 Tables Grass cutting work completed
529 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-11 | 1 | 1 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | G3 -T59 to T68- Inv 3 -10 Tables Grass cutting work completed
530 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-12 | 1 | 1 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | G4 -T81 to T87- Inv 3 -07 Tables & Main gate road side area Grass cutting work completed
531 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-13 | 1 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 5 | G4 -T76 to T80- Inv 3 -05 Tables Grass cutting work completed
532 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-14 | 1 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 6 | G4 -T88 to T93- Inv 3 -06 Tables Grass cutting work completed
533 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-15 | 1 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | G4 -T94 to T101- Inv 3 -08 Tables Grass cutting work completed
534 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-16 | 1 | 1 | 0 | 0 | 4 | 4 | 0 | 0 | 8 | G4 -T102 to T109- Inv 3& Inv 4 -08 Tables Grass cutting work completed
535 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-17 | 1 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | G4 -T110 to T119- Inv 4 -10 Tables Grass cutting work completed
536 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-18 | 1 | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | G4 -T120 to T125- Inv 4 -06 Tables Grass cutting work completed
537 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-19 | [8 empty] | 0
538 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-20 | [8 empty] | 0
539 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-21 | 1 | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | G4 -T126 to T131- Inv 4 -06 Tables Grass cutting work completed
540 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-22 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | G4 -T32 to T134- Inv 4 -02 Tables Grass cutting work completed
541 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-23 | [7 empty] | 0 | 0 | Store Spare Area & G6 Non PV Area Grass Cutting Work Done
542 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-24 | [8 empty] | 0
543 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-25 | [8 empty] | 0
544 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-26 | [8 empty] | 0
545 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-27 | [8 empty] | 0
546 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-28 | [8 empty] | 0
547 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-29 | [8 empty] | 0
548 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-30 | [8 empty] | 0
549 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | [8 empty] | 0
550 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | [8 empty] | 0
551 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | [8 empty] | 0
552 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | [8 empty] | 0
553 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | [8 empty] | 0
554 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | [8 empty] | 0
555 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-07 | [8 empty] | 0
556 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-08 | [8 empty] | 0
557 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-09 | [8 empty] | 0
558 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | [8 empty] | 0
559 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-11 | [8 empty] | 0
560 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-12 | [8 empty] | 0
561 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-13 | [8 empty] | 0
562 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-14 | [8 empty] | 0
563 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-15 | [8 empty] | 0
564 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | [8 empty] | 0
565 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | [8 empty] | 0
566 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | [8 empty] | 0
567 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-19 | [8 empty] | 0
568 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-20 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | G5- Inv4 - T120 to T121 - 2 Tables Grass cutting work completed
569 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-21 | 1 | 1 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | G5- Inv4 - T122 to T126 - 5 Tables Grass cutting work completed
570 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-22 | 1 | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | G5- Inv4 - T127 to T132 - 6 Tables Grass cutting work completed
571 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | [8 empty] | 0
572 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-24 | [8 empty] | 0
573 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-25 | [8 empty] | 0
574 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-26 | 1 | 1 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | G5- Inv4 - T133 to T146 - 14 Tables Grass cutting work completed
575 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-27 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G4- Inv1 - T31 to T39 - 9 Tables Grass cutting work completed
576 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-28 | 1 | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | G4- Inv1 - T40 to T49 - 10 Tables Grass cutting work completed
577 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-29 | 1 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 11 | G4- Inv1 - T50 to T60 - 11 Tables Grass cutting work completed
578 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | 1 | 1 | 2 | 8 | 0 | 0 | 0 | 0 | 10 | G4- Inv1&2 - T61 to T70 - 10 Tables Grass cutting work completed
579 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-31 | 1 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G3A T1 to T5, G3-TW1, T1 to T6 - Inv5 - 12 Tables Grass cutting work completed
580 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-11-01 | 1 | 1 | 10 | 0 | 0 | 0 | 1 | 0 | 11 | G3 - Inv5&1 -T7 to T17- 11 Tables Grass cutting work completed
581 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-02 | 1 | 1 | 6 | 0 | 0 | 0 | 4 | 0 | 10 | G4 -Inv5&1 - T31 to 21-10 Tables Grass Cutting Work completed
582 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-03 | 1 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G4 -Inv4 - T136 to T143-8 Tables Grass Cutting Work completed
583 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-04 | 1 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G4 -Inv5 - T14 to T21-8 Tables Grass Cutting Work completed
584 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-05 | 1 | 1 | 0 | 3 | 9 | 0 | 0 | 0 | 12 | G6 -Inv2&3 - T77 to T88-12 Tables Grass Cutting Work completed
585 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-06 | 1 | 1 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | G6 -Inv2 - T68 to T76-09 Tables & ICR1 Surrounding Area Grass Cutting Work completed
586 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-07 | 1 | 1 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | G6 -Inv2 - T57 to T67-11 Tables Grass Cutting Work Completed
587 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
588 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-09 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | G6 -Inv2 - T53 to T56-04 Tables Grass Cutting Work Completed
589 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-10 | 1 | 1 | 0 | 3 | 9 | 0 | 0 | 0 | 12 | G6 -Inv2&1 - T41 to T52-12 Tables Grass Cutting Work Completed
590 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-11 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 10 | 11 | G6 -Inv6&1 - T40 to T30-11 Tables Grass Cutting Work Completed
591 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-12 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G6 -Inv6 - T20 to T29-10 Tables Grass Cutting Work Completed
592 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-13 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11 | 11 | G6 -Inv6 - T01 to T11-11 Tables Grass Cutting Work Completed
593 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-14 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G6 -Inv6 - T12 to T19 & G5-Inv 6 T01 to T02-10 Tables Grass Cutting Work Completed
594 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-15 | 1 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 10 | G5 -Inv3&4 - TW01 to TW10-10 Tables Grass Cutting Work Completed
595 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-16 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G5 -Inv6 - T3 to T12-10 Tables Grass Cutting Work Completed
596 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-17 | 1 | 1 | 0 | 0 | 0 | 0 | 13 | 0 | 13 | G2 -Inv5 - T28 to T40-13 Tables Grass Cutting Work Completed
597 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-18 | 1 | 1 | 0 | 0 | 0 | 0 | 11 | 0 | 11 | G2 -Inv5 - T17 to T27-11 Tables Grass Cutting Work Completed
598 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-19 | 1 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G2 -Inv5 - T07 to T16-10 Tables Grass Cutting Work Completed
599 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-20 | 1 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G2 -Inv5 - TW1,T01 to T06 & G1-Inv 5 T01 to T02-09 Tables Grass Cutting Work Completed
600 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-21 | 1 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G1-Inv 5 T03 to T12-10 Tables Grass Cutting Work Completed
601 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-22 | 1 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G1-Inv 5 T13 to T21-9 Tables Grass Cutting Work Completed
602 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-23 | 1 | 1 | 0 | 0 | 0 | 0 | 13 | 0 | 13 | G1-Inv 5 T22 to T34-13 Tables Grass Cutting Work Completed
603 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-24 | 1 | 1 | 0 | 0 | 0 | 0 | 8 | 3 | 11 | G1-Inv 5 T35 to T45-11 Tables Grass Cutting Work Completed
604 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-25 | 1 | 1 | 6 | 0 | 0 | 0 | 0 | 7 | 13 | G1 -Inv6 - T46 to T52 & G3-Inv1 T18 to T23-13 Tables Grass Cutting Work Completed
605 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-26 | 1 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 11 | G3-Inv1 T24 to T34-11 Tables Grass Cutting Work Completed
606 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-27 | 1 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | G3-Inv1 T35 to T41-7 Tables Grass Cutting Work Completed
607 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-28 | 1 | 1 | 3 | 8 | 0 | 0 | 0 | 0 | 11 | G3-Inv1&2 T42 to T52-11 Tables Grass Cutting Work Completed
608 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-29 | 1 | 1 | 0 | 1 | 9 | 0 | 0 | 0 | 10 | G3-Inv2&3 T53 to T62-10 Tables Grass Cutting Work Completed
609 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-30
610 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-01 | 1 | 1 | 0 | 0 | 6 | 5 | 0 | 0 | 11 | G3-Inv3 T63 to T68 & G5-Inv 4 T 154 to T158-11 Tables Grass Cutting Work Completed
611 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-02 | 1 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | G5-Inv 4 T 118,119, 146 to T153-10 Tables Grass Cutting Work Completed | Cycle 1 Completed
612 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-03 | 2 | 1 | 0 | 0 | 0 | 5 | 2 | 0 | 7 | G5-Inv 4 113 to T117 & G4-Inv 5 T10 to T11-7 Tables Grass Cutting Work Completed
613 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-04 | 2 | 1 | 0 | 0 | 5 | 3 | 0 | 0 | 8 | G5-Inv3 & 4 T106 to T112 -8 Tables Grass Cutting Work Completed
614 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-05 | 2 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 5 | G5-Inv3 T101 to T105 -5 Tables Grass Cutting Work Completed
615 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-06 | 2 | 1 | 0 | 0 | 8 | 3 | 0 | 0 | 11 | G5-Inv3 & 4 T90 to T100 -11 Tables Grass Cutting Work Completed
616 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-07 | 2 | 1 | 0 | 0 | 7 | 4 | 0 | 0 | 11 | G5-Inv3 & 4 T79 to T89 -11 Tables Grass Cutting Work Completed
617 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-08 | 2 | 1 | 0 | 0 | 3 | 4 | 0 | 0 | 7 | G5-Inv3 & 4 T72 to T78 -7 Tables Grass Cutting Work Completed
618 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-09 | 2 | 1 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | G5-Inv2 T63 to T71 -9 Tables Grass Cutting Work Completed
619 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-10 | [8 empty] | 0
620 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-11 | 2 | 1 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | G5-Inv2 T56 to T62-7 Tables Grass Cutting Work Completed
621 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-12 | 2 | 1 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | G5-Inv2 T47 to T55-9 Tables Grass Cutting Work Completed
622 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-13 | 2 | 1 | 1 | 6 | 0 | 0 | 0 | 0 | 7 | G5-Inv1 & 2 T40 to T46-7 Tables Grass Cutting Work Completed
623 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-14 | 2 | 1 | 0 | 2 | 8 | 0 | 0 | 0 | 10 | G4-Inv2 & 3 T71 to T80-10 Tables Grass Cutting Work Completed
624 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | 2 | 1 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | G4-Inv 3 T81 to T87-7 Tables Grass Cutting Work Completed
625 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-16 | 2 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | G4-Inv 3 T88 to T95-8 Tables Grass Cutting Work Completed
626 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-17 | 2 | 1 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | G4-Inv 3 T96 to T105-10 Tables Grass Cutting Work Completed
627 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-18 | 2 | 1 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | G4-Inv 5 T01 to T05-5 Tables Grass Cutting Work Completed
628 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-19 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G4-Inv 4 T106 to T113-8 Tables Grass Cutting Work Completed
629 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-20 | 2 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | G4-Inv 4 T114 to T123-10 Tables Grass Cutting Work Completed
630 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-21 | 2 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | G4-Inv 4 T124 to T133-10 Tables Grass Cutting Work Completed
631 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | 2 | 1 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | G4-Inv 4 T134 to T137-4 Tables Grass Cutting Work Completed
632 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-23 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 Non PV Area Grass Cutting Work Completed
633 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-24 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Non PV Area Grass Cutting Work Completed
634 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-25 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Non PV Area Grass Cutting Work Completed
635 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-26 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Non PV Area Grass Cutting Work Completed
636 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-27 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Non PV Area Grass Cutting Work Completed
637 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-28 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Non PV Area Grass Cutting Work Completed
638 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-29 | 2 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | G5-Inv1 T37 to T39-3 Tables & G5 Non PV Area Grass Cutting Work Completed
639 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-30 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Non PV Area Grass Cutting Work Completed
640 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-31 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Non PV Area Grass Cutting Work Completed
641 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-01 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Non PV Area Grass Cutting Work Completed
642 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-02 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Non PV Area Grass Cutting Work Completed
643 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-03 | 2 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | G6 Non PV Area & G5-Inv2 TW16 to TW18-3 Tables Grass Cutting Work Completed
644 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-04 | 2 | 1 | 2 | 0 | 0 | 0 | 0 | 6 | 8 | G5-Inv1 & 6 T31 to T38-8 Tables Grass Cutting Work Completed
645 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-05 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 9 | 9 | G5-Inv6 T22 to T30-9 Tables Grass Cutting Work Completed
646 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-06 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G1 Non PV Area Grass Cutting Work Completed
647 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-07 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G2 Non PV Area Grass Cutting Work Completed
648 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-08 | 2 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | G5-Inv2 TW11 to T15-5 Tables Grass Cutting Work Completed
649 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-09 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G5-Inv6 T21 to T12-10 Tables Grass Cutting Work Completed
650 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-10 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | G5-Inv6 T09 to T-11-2 Tables & Spare Area Surrounding Grass Cutting Work Completed
651 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Spare Area Surrounding Grass Cutting Work Completed
652 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-12 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Store Spare Area & G6 Non PV Area Grass Cutting Work Done
653 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-13 | 2 | 1 | 0 | 0 | 5 | 6 | 0 | 0 | 11 | G5-Inv 3&4 TW 01 to 10 & G6 TW1- 11 Tables Grass Cutting Work Completed
654 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-14 | 2 | 1 | 0 | 3 | 6 | 5 | 0 | 0 | 14 | G6-Inv2, 3&4 TW 02 to 15 - 14 Tables Grass Cutting Work Completed
655 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Due to festival
656 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-16 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ICR2 Surrounding Area Grass Cutting Work Completed
657 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-17 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Manual Tree cutting at grid 5 and fencing side at grid 5 top area
658 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-18 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
659 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-19 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Non PV Area & G2 Non PV Area Grass Cutting Work Completed
660 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-20 | 2 | 1 | 0 | 0 | 0 | 0 | 6 | 0 | 6 | G4 Non PV Area & G4 Inv 5- T04 to T09-6 Tables Grass Cutting Work Completed
661 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-21 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Between G3 &G4 Non PV Area Grass Cutting Work Completed
662 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-22 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
663 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-23 | 2 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 9 | G5 Table 119 to table 127
664 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-24 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Switch Yard & G5 Fench Side Bush Cutting Work Completed
665 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-25 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Fench Side & G1 Fench Side Area Grass Cutting Work Done
666 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-26 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
667 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-27 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G1 Fench Side Area Grass Cutting Work Done
668 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-28 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G2 Fench Side Area Grass Cutting Work Done
669 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-29 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B/w G1&2 fencing and Grass cutting work done
670 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-30 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G1 Fench Side Area Grass Cutting Work Done
671 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-31 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-01 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-02 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G1 Fench Side Area Grass Cutting Work Done
674 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-03 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G1 Fench Side Manual Grass Cutting Work Done
675 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-04 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G1& 2 Fench Side Manual Grass Cutting Work Done
676 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-05 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
677 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-06 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
678 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-07 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
679 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-08 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
680 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-09 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
681 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
682 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
683 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-12 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
684 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
685 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-14 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
686 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-15 | 2 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G3-Inv 5-Ttw01 to T04-10 Tables Grass Cutting Work Completed
687 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-16 | 2 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | G3-Inv 2-Ttw06 toT14-8 Tables Grass Cutting Work Completed
688 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-17 | 2 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 11 | G4-Inv 1-T40 to T51-11 Tables Grass Cutting Work Completed
689 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-18 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G5-inv 4-T140 to T147-8 Tables Grass Cutting Work Completed
690 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-19 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
691 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-20 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
692 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-21 | 2 | 1 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | G5-Inv 1 T60 to T70-11 tables Grass Cutting work Completed
693 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-22 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
694 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-23 | 2 | 1 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | G5-Inv 4 T128 to T139-12 tables Grass Cutting work Completed
695 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
696 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-25 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
697 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
698 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-27 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
699 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-28 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-29 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
701 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-01 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
702 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-02 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
703 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-03 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
704 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-04 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
705 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-05 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
706 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Parcel 2 Vegitation Work Completed
707 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-07 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Parcel 2 Manual Grass Cutting Work Done
708 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-08 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
709 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-09 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
710 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
711 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-11 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
712 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
713 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-02 | 31 | 2024-03-13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
714 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-03 | 31 | 2024-03-14 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
715 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
716 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-05 | 31 | 2024-03-16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
717 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
718 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-18 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
718 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-19 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
719 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-20 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
720 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-21 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
721 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-22 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
722 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-23 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
723 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
724 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-25 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
725 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-26 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
726 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-27 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
727 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-28 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
728 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-29 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
729 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-30 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
730 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-31 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
731 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-01 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
732 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-02 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ICR1 WMS Surrounding Vegitation Work Completed
733 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-03 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
734 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-04 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
735 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-05 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
736 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-02 | 30 | 2024-04-06 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
737 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-07 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
738 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-08 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
739 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-09 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
740 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
741 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-11 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
742 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-12 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
743 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
744 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-14 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
745 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-15 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Manual Grass Cutting work done
746 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
747 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
748 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-18 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
749 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-19 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
750 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-20 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 & G4 Manual Grass Cutting work done
751 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-21 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Manual Grass Cutting work done
752 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-22 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
753 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-23 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
754 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Manual Grass Cutting work done
755 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-25 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | Switch Yard Vegitation Work Done
755 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-26 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
756 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-27 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Switch Yard Vegitation Work Done
757 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-28 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Switch Yard Vegitation Work Done
758 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-29 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Switch Yard Vegitation Work Done
759 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-30 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
780 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-01 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
781 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-02 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 & G4 bushes Grass Removal Work Completed
782 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-03 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 & G4 Manual Grass Removal Work Completed
783 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-04 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Manual Grass Cutting work done
784 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-05 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
785 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-06 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
786 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-07 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Manual Grass Cutting work done
787 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-08 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
788 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-09 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
789 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-10 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Manual Grass Cutting work done
790 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-11 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
791 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-12 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
792 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-13 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Manual Grass Cutting work done
793 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-14 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Manual Grass Cutting Work done
794 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-15 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Manual Grass Cutting Work done
795 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-16 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G1 Manual Grass Cutting Work Done
796 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
797 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-18 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDT2 Switch Yard Vegitation work done
798 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-19 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
799 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-20 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-21 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDT1 Switch Yard Vegitation work done
801 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-22 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDT2 & WMS Switch Yard Vegitation work done
802 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-23 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Manual Grass Cutting work done
803 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-24 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Manual Grass Cutting Work done
804 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-25 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 Manual Grass Cutting Work Done
805 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-26 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4&G6 Manual Grass Cutting Work Done
806 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-27 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3&G4 Manual Grass Cutting Work Done
807 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-28 | 1 | 1 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | G5-inv 4-T148 to T158-11 Tables & G3,G4&G6 Manual Grass Cutting Work Done
808 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-29 | 1 | 1 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | G5-inv 4-T133 to T147-15 Tables & G3,G4&G6 Manual Grass Cutting Work Done
809 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-30 | 1 | 1 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | G5-inv 4-T119 to T132-14 Tables & G3,G4&G6 Manual Grass Cutting Work Done
810 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-31 | 1 | 1 | 0 | 0 | 4 | 9 | 0 | 0 | 13 | G5-inv 4 & 3-T107 to T1118-13 Tables &G6 Manual Grass Cutting Work Done
811 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-01 | 1 | 1 | 0 | 0 | 12 | 0 | 0 | 0 | 12 | G5-inv 3-T96 to T106-12 Tables &G6 Manual Grass Cutting Work Done
812 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-02 | 1 | 1 | 0 | 0 | 5 | 6 | 0 | 0 | 11 | G5-inv 3& 4-T85 to T196-11 Tables Grass Cutting Work Done
813 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-03 | 1 | 1 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | G5-inv 4-T75 to T84-10 Tables Grass Cutting Work Done
814 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-04 | 1 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 9 | G5-inv 3-T66 to T74-09 Tables Grass Cutting Work Done
815 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-05 | 1 | 1 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | G5-inv 2-T55 to T65-11 Tables Grass Cutting Work Done
816 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-06 | 1 | 1 | 0 | 0 | 11 | 0 | 0 | 0 | 11 | G4-Inv 3 -T88 to T98-11 Tables Grass Cutting Work Done
817 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-07 | 1 | 1 | 0 | 0 | 7 | 3 | 0 | 0 | 10 | G4-Inv 3 &4 -T99 to T108-10 Tables Grass Cutting Work Done
818 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-08 | 1 | 1 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | G4-Inv 4 -T109 to T119-11 Tables Grass Cutting Work Done
819 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-09 | 1 | 1 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | G4-Inv 4 -T120 to T131-12 Tables Grass Cutting Work Done
820 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-10 | 1 | 1 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | G4-Inv 4 -T132 to T143-12 Tables Grass Cutting Work Done
821 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-11 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 10 | 12 | G1-Inv 5& 6 -T41 to T52-12 Tables Grass Cutting Work Done
822 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-12 | 1 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G1-Inv 5 -T30 to T40-12 Tables Grass Cutting Work Done
823 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-13 | 1 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G1-Inv 5 -T20 to T29-10 Tables Grass Cutting Work Done
824 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-14 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
825 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-15 | 1 | 1 | 0 | 0 | 0 | 0 | 11 | 0 | 11 | G1-Inv 5 -T19 to T09-11 Tables Grass Cutting Work Done
826 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-16 | 1 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G1 & G2-Inv 5 -T01 to T08 & G2 TW1& T01 TO T03-12 Tables Grass Cutting Work Done
827 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-17 | 1 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G2-Inv 5-T04 to T15-12 Tables Grass Cutting Work Done
828 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-18 | 1 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G2-Inv 5-T16 to T27-12 Tables Grass Cutting Work Done
829 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-19 | 1 | 1 | 0 | 0 | 0 | 0 | 13 | 0 | 13 | G2-Inv 5-T28 to T40-13 Tables Grass Cutting Work Done
830 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Due to Rain Grass Cutting Not Done
831 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-21 | 1 | 1 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | G5-inv 2-T48 to T54-07 Tables Grass Cutting Work Done
832 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-22 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
833 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-23 | 1 | 1 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | G5-inv 2-T42 to T-T47 Tables Grass Cutting Work Done
834 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-24 | 1 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | G5-inv 1-T39 to T-T41 Tables Grass Cutting Work Done
835 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-25 | 1 | 1 | 2 | 0 | 0 | 0 | 6 | 0 | 8 | G5-inv 1 &6-T30 to T-T38 Tables Grass Cutting Work Done
836 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-26 | 1 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G5-inv 6-T22 to T-T29-8 Tables Grass Cutting Work Done
837 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-27 | 1 | 1 | 0 | 0 | 0 | 0 | 6 | 0 | 6 | G5-inv 6-T16 to T-T21-6 Tables Grass Cutting Work Done
838 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-28 | 1 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G5-inv 6-T06 to T-T15-10 Tables Grass Cutting Work Done
839 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-29 | 1 | 1 | 0 | 0 | 0 | 0 | 3 | 5 | 8 | G5-inv 6-T01 to T-T05 & G4 T01 TO T03-08 Tables Grass Cutting Work Done
840 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-30 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G4-Inv 5- T04 TO T10-07 Tables Grass Cutting Work Done
841 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-01 | 1 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G4-Inv 5- T11 TO T19-09 Tables Grass Cutting Work Done
842 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-02 | 1 | 1 | 3 | 0 | 0 | 0 | 6 | 0 | 9 | G4-Inv 5- T20 TO T28-09 Tables Grass Cutting Work Done
843 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-03 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G4-Inv 1- T29 TO T37-09 Tables Grass Cutting Work Done
844 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-04 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G4-Inv 1- T38 TO T46-09 Tables Grass Cutting Work Done
845 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-05 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G4-Inv 1- T47 TO T55-09 Tables Grass Cutting Work Done
846 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-06 | 1 | 1 | 7 | 1 | 0 | 0 | 0 | 0 | 8 | G4-Inv 1 & 2 - T56 TO T63-08 Tables Grass Cutting Work Done
847 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-07 | 1 | 1 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | G4-Inv 2 - T64 TO T72-09 Tables Grass Cutting Work Done
848 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-08 | 1 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 5 | G4-Inv 3 - T73 TO T77-05 Tables Grass Cutting Work Done
849 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-09 | 1 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 9 | G4-Inv 3 - T78 TO T85-09 Tables Grass Cutting Work Done
850 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-10 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Switch Yard Grass Cutting Work Completed
851 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-11 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Non PV Area & ICR2 Surrounding Area Grass Cutting Work Completed
852 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-12 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Non PV Area Grass Cutting Work Completed
853 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-13 | 1 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G3-Inv 5-Ttw01 to T03-09 Tables Grass Cutting Work Completed
854 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-14 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G3-Inv 1-T04 to T12-09 Tables Grass Cutting Work Completed
855 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-15 | 1 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | G3-Inv 1-T13 to T19-07 Tables Grass Cutting Work Completed
856 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-16 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G3-Inv 1-T20 to T28-09 Tables Grass Cutting Work Completed
857 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-17 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G3-Inv 1-T29 to T37-09 Tables Grass Cutting Work Completed
858 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-18 | 1 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | G3-Inv 1-T38 to T44-07 Tables Grass Cutting Work Completed
859 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-19 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Due to Rain Grass Cutting Not Done
860 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-20 | 1 | 1 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | G3-Inv 2-T45 to T51-07 Tables Grass Cutting Work Completed
861 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-21 | 1 | 1 | 0 | 2 | 5 | 0 | 0 | 0 | 7 | G3-Inv 2 & 3-T52 to T58-07 Tables Grass Cutting Work Completed
862 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-22 | 1 | 1 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | G3-Inv 3-T59 to T68-10 Tables Grass Cutting Work Completed
863 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-23 | 1 | 1 | 0 | 0 | 0 | 5 | 4 | 0 | 9 | G5-Inv 4&3-TW1 to TW9-09 Tables Grass Cutting Work Completed
864 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-24 | 1 | 1 | 0 | 4 | 2 | 0 | 0 | 0 | 6 | G5-Inv 2&3-TW10 to TW15-06 Tables Grass Cutting Work Completed
865 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-25 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Due to Rain Grass Cutting Not Done
866 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-26 | 1 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | G6-Inv 3-T81 to T88-08 Tables Grass Cutting Work Completed
867 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-27 | 1 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | G6-Inv 2-1W 16 to TTW12-08 Tables Grass Cutting Work Completed
868 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-28 | 1 | 1 | 0 | 0 | 4 | 6 | 0 | 0 | 10 | G6-Inv 3&4-TW 01 to TW10-10 Tables Grass Cutting Work Completed
869 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-29 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G6-Inv 6-T 01 to T 10-10 Tables Grass Cutting Work Completed | cycle 3 completed
870 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-30 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
871 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-31 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
872 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-01 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 Fence side area Manual Grass cutting work done
873 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-02 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Additional Parcel Fench side Manual Grass Cutting Work Done
874 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-03 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Additional Parcel Fench side Manual Grass Cutting Work Done
875 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-04 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
876 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-05 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
877 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-06 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDT2 Switch Yard Vegitation work done
878 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-07 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Main Switch yard vegitation Work Done
879 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-08 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDT1 Switch Yard Vegitation work done
880 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-09 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
881 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
882 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-11 | [8 empty] | 0
883 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-12 | [8 empty] | 0
884 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-13 | [8 empty] | 0
885 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-14 | [8 empty] | 0
886 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-15 | [8 empty] | 0
887 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-16 | [8 empty] | 0
888 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-17 | [8 empty] | 0
889 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-18 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Main gate road side area grass cutting work was completed
890 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-19 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Switch Yard Grass Cutting Work Completed
891 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-20 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Switch Yard Grass Cutting Work Completed
892 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-21 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR Surrounding Area Grass Cutting Work Done
893 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-22 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR Surrounding Area Grass Cutting Work Done
894 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-23 | [8 empty] | 0
895 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-24 | [8 empty] | 0
896 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-25 | [8 empty] | 0
897 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-26 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G5-Inv 6-T1 to T10-10 Tables Grass Cutting Work Completed
898 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-27 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 7 | 7 | G5-Inv 6-T11 to T17-07 Tables Grass Cutting Work Completed
899 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-28 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | G5-Inv 6-T18 to T25-08 Tables Grass Cutting Work Completed
900 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-29 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | G5-Inv 6-T26 to T29-04 Tables Grass Cutting Work Completed
901 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-30 | 2 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | G4-Inv 3-T88 to T89-02 Tables Grass Cutting Work Completed
902 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-31 | 2 | 1 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | G4-Inv 3-T90 to T99-10 Tables Grass Cutting Work Completed
903 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-01 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 7 | 7 | G5-Inv 6-T29 to T35-07 Tables Grass Cutting Work Completed
904 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-02 | 2 | 1 | 4 | 2 | 0 | 0 | 0 | 1 | 7 | G5-Inv 6-T36 to T42-07 Tables Grass Cutting Work Completed
905 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-03 | 2 | 1 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | G5-Inv 2-T43 to T52-10 Tables Grass Cutting Work Completed
906 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-04 | 2 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | G5-Inv 2-T53 to T60-08 Tables Grass Cutting Work Completed
907 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-05 | 2 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | G5-Inv 2-T61 to T68-08 Tables Grass Cutting Work Completed
908 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-06 | 2 | 1 | 0 | 7 | 1 | 0 | 0 | 0 | 8 | G5-Inv 2-T69 to T76-08 Tables Grass Cutting Work Completed
909 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-07 | 2 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | G5-Inv 3-T77 to T79-03 Tables & Spare Area Grass Cutting Work Completed
910 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-08 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Spare Area Surrounding Grass Cutting Work Completed
911 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-09 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | spare Area Surrounding & ICR1 Surrounding Grass Cutting Work Completed
912 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-10 | 2 | 1 | 0 | 0 | 4 | 8 | 0 | 0 | 12 | G5-Inv 3 & 4-T81 to T91-12 Tables Grass Cutting Work Completed
913 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-11 | 2 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | G5-Inv 3 -T100 to T102-02 Tables Grass Cutting Work Completed
914 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-12 | 2 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | G5-Inv 3 -T102 to T109-08 Tables Grass Cutting Work Completed
915 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-13 | 2 | 1 | 0 | 0 | 1 | 5 | 0 | 0 | 6 | G5-Inv 3 -T110 to T114-06 Tables Grass Cutting Work Completed
916 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-14 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G5-Inv 4 -T115 to T122-08 Tables Grass Cutting Work Completed
917 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-15 | 2 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | G5-Inv 4 -T123 to T131-09 Tables Grass Cutting Work Completed
918 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-16 | 2 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | G5-Inv 4 -T132 to T141-10 Tables Grass Cutting Work Completed
919 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-17 | 2 | 1 | 0 | 0 | 0 | 0 | 4 | 10 | 14 | G1-Inv 6&5 -T39 to T52-14 Tables Grass Cutting Work Completed
920 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-18 | 2 | 1 | 0 | 0 | 0 | 0 | 13 | 0 | 13 | G1-Inv 5 -T26 to T38-13 Tables Grass Cutting Work Completed
921 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-19 | 2 | 1 | 0 | 0 | 0 | 0 | 6 | 0 | 6 | G4-Inv 5 -T01 to T06-06 Tables Grass Cutting Work Completed
922 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-20 | [8 empty] | 0
923 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-21 | 2 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G4-Inv 5 -T07 to T13-08 Tables Grass Cutting Work Completed
924 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-22 | 2 | 1 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | G4-Inv 5 -T14 to T18-05 Tables Grass Cutting Work Completed
925 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-23 | [8 empty] | 0
926 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-24 | [8 empty] | 0
927 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-25 | 2 | 1 | 1 | 0 | 0 | 0 | 7 | 0 | 8 | G4-Inv 5 -T19 to T26-08 Tables Grass Cutting Work Completed
928 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-26 | 2 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G4-Inv 1 -T27 to T32-06 Tables Grass Cutting Work Completed
929 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-27 | 2 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | G4-Inv 1 -T33 to T39-07 Tables Grass Cutting Work Completed
930 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-28 | [8 empty] | 0
931 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-29 | 2 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | G4-Inv 1 -T40 to T46-07 Tables Grass Cutting Work Completed
932 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-30 | 2 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G4-Inv 1 -T47 to T52-06 Tables Grass Cutting Work Completed
933 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-01 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-02 | 2 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | G4-Inv 1 -T53 to T60-08 Tables Grass Cutting Work Completed
935 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-03 | 2 | 1 | 2 | 6 | 0 | 0 | 0 | 0 | 8 | G4-Inv 1 & Inv 2 -T61 to T68-08 Tables Grass Cutting Work Completed
936 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-04 | 2 | 1 | 0 | 4 | 4 | 0 | 0 | 0 | 8 | G4-Inv 2 & Inv 3 -T69 to T76-08 Tables Grass Cutting Work Completed
937 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-05 | 2 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 9 | G4-Inv 3 -T77 to T85-09 Tables Grass Cutting Work Completed
938 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-06 | 2 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | G4-Inv 3 -T86 to T89 & T101 to 104-08 Tables Grass Cutting Work Completed
939 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-07 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G4-Inv 4 -T105 to T112 -08 Tables Grass Cutting Work Completed
940 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-08 | [8 empty] | 0 | Due to Rain Grass Cutting Not Done
941 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-09 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G4-Inv 4 -T113 to T119 -08 Tables Grass Cutting Work Completed
942 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-10 | 2 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | G4-Inv 4 -T120 to T129 -09 Tables Grass Cutting Work Completed
943 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-11 | [8 empty] | 0
944 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-12 | 2 | 1 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | G4-Inv 4 -T130 to T134 -04 Tables Grass Cutting Work Completed
945 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-13 | 2 | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | G4-Inv 4 -T135 to T140 -06 Tables Grass Cutting Work Completed
946 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-14 | 2 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G1-Inv 5 -T14 to T125 -12 Tables Grass Cutting Work Completed
947 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-15 | [8 empty] | 0 | Due to Rain Grass Cutting Not Done
948 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-16 | 2 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G1-Inv 5 -T06 to T113 -08 Tables Grass Cutting Work Completed
949 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-17 | 2 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G1-Inv 5 -T01 to T05 & G2 -T01 TO T05-10 Tables Grass Cutting Work Completed
950 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-18 | 2 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G2-T06 TO T16 -12 Tables Grass Cutting Work Completed
951 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-19 | 2 | 1 | 0 | 0 | 0 | 0 | 4 | 0 | 4 | G2-T17 TO T20 -04 Tables Grass Cutting Work Completed
952 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-20 | [8 empty] | 0 | Due to Rain Grass Cutting Not Done
953 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-21 | [8 empty] | 0 | Due to Rain Grass Cutting Not Done
954 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-22 | 2 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G2-T21 TO T29 -09 Tables Grass Cutting Work Completed
955 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-23 | 2 | 1 | 0 | 0 | 0 | 0 | 11 | 0 | 11 | G2-T30 TO T40 -11 Tables Grass Cutting Work Completed
956 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | [8 empty] | 0 | Due to Rain Grass Cutting Not Done
957 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-25 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G4-Inv 4 -T141 to T143 & G5-inv4-T -08 Tables Grass Cutting Work Completed
958 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-26 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G5-Inv 4-T147 TO T154 -08 Tables Grass Cutting Work Completed
959 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-27 | 2 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | G5-Inv 3-T92 TO T99 -08 Tables Grass Cutting Work Completed
960 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-28 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 9 | 9 | G6-Inv 6-T01 TO T09 -09 Tables Grass Cutting Work Completed
961 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-29 | [8 empty] | 0
962 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-30 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | G6-Inv 6-T10 TO T14 -05 Tables Grass Cutting Work Completed
963 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-31 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | G6-Inv 6-T15 TO T21 -06 Tables Grass Cutting Work Completed
964 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-01 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | G6-Inv 6-T22 TO T27 -06 Tables Grass Cutting Work Completed
965 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-02 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | G6-Inv 6-T28 TO T43 -16 Tables Grass Cutting Work Completed
966 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-03 | 2 | 1 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | G6-Inv 2-T44 TO T55 -12 Tables Grass Cutting Work Completed
967 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-04 | 2 | 1 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | G6-Inv 2-T56 TO T71 -16 Tables Grass Cutting Work Completed
968 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-05 | 2 | 1 | 0 | 8 | 9 | 0 | 0 | 0 | 17 | G6-Inv 2 & 3 -T72 TO T88 -16 Tables Grass Cutting Work Completed
969 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-06 | 2 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G3- Inv 5 & 1-T3A-T1 TO T5 & TW1 TO- T6-12 Tables Grass Cutting Work Completed
970 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-07 | 2 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | G3- Inv1- T07 TO- T14-8 Tables Grass Cutting Work Completed
971 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-08 | 2 | 1 | 18 | 0 | 0 | 0 | 0 | 0 | 18 | G3- Inv1- T15 TO- T32-18 Tables Grass Cutting Work Completed
972 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-09 | 2 | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | G3- Inv1- T33 TO- T44-18 Tables Grass Cutting Work Completed
973 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-10 | 2 | 1 | 0 | 9 | 1 | 0 | 0 | 0 | 10 | G3- Inv2- T45 TO- T54-10 Tables Grass Cutting Work Completed
974 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-11 | 2 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 9 | G3- Inv3- T55 TO- T63-9 Tables Grass Cutting Work Completed
975 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-12 | 2 | 1 | 0 | 0 | 4 | 5 | 0 | 0 | 9 | G3- Inv3- T64 TO- T68 & TW13 TO 17 -9 Tables Grass Cutting Work Completed
976 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-13 | 2 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | G5- TW09 TO 12 -4 Tables Grass Cutting Work Completed
977 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-14 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR Surrounding Area Grass Cutting Work Done
978 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-15 | [8 empty] | 0 | Not done due to Rain
979 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-16 | [8 empty] | 0 | Not done due to Rain
980 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-17 | [8 empty] | 0 | Not done due to Rain
981 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-18 | [8 empty] | 0
982 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-19 | 3 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | G5- TW01 TO 10 -10 Tables Grass Cutting Work Completed
983 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-20 | 3 | 1 | 0 | 0 | 6 | 6 | 0 | 0 | 12 | G6-TW06 TO TW16-12 Tables Grass Cutting Work Completed
984 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-21 | 3 | 1 | 0 | 0 | 8 | 5 | 0 | 0 | 13 | G6-TW01 TO TW05 & G5 T101 to T108-13 Tables Grass Cutting Work Completed
985 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-22 | 3 | 1 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | G5- T109 & T110A to T113-13 Tables Grass Cutting Work Completed
986 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-23 | 3 | 1 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | G5- TT14 T120-07 Tables Grass Cutting Work Completed
987 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-24 | 3 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | G5- TT121 T129-09 Tables Grass Cutting Work Completed
988 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-25 | 3 | 1 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | G5- TT130 T142-13 Tables Grass Cutting Work Completed
989 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-26 | [8 empty] | 0 | Not done due to helpers taken weekoff
990 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-27 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | G5-T01 TO t05-05 tables Grass Cutting Work Completed
991 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-28 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G5-T06 T15 -10 tables Grass Cutting Work Completed
992 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-29 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G5-T16 T25 -10 tables Grass Cutting Work Completed
993 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-30 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | G5-T26 T33 -08 tables Grass Cutting Work Completed
994 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-01 | 3 | 1 | [6 empty] | 0 | Due to Rain Grass Cutting Not Done
995 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-02 | 3 | 1 | [6 empty] | 0 | Due to Rain Grass Cutting Not Done
996 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-03 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Non PV area Manual Grass Cutting work done
997 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-04 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Non PV area Manual Grass Cutting work done
998 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-05 | 3 | 1 | 4 | 3 | 0 | 0 | 0 | 3 | 10 | G5-T34 to T43 -10 tables Grass Cutting Work Completed
999 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-06 | 3 | 1 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | G5-T44 to T52 -09 tables & spare Area Grass Cutting Work Completed
1000 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-07 | 3 | 1 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | G5-T53 to T72 -20 tables & spare Area Grass Cutting Work Completed
1001 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-08 | 3 | 1 | 0 | 3 | 2 | 0 | 0 | 0 | 5 | G5-T73 to T77 -5 tables Grass Cutting work completed
1002 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-09 | 3 | 1 | 0 | 0 | 8 | 6 | 5 | 0 | 19 | G5-T78 to T91 & G4-T01 to T05 -19 tables Grass Cutting work completed
1003 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-10 | 3 | 1 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | G4-T06 to T10 -05 tables Grass Cutting work completed
1004 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-11 | [8 empty] | 0
1005 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-12 | 3 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G4-T11 to T18 -08 tables Grass Cutting work completed
1006 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-13 | 3 | 1 | 2 | 0 | 0 | 0 | 7 | 0 | 9 | G4-T19 to T27 -09 tables Grass Cutting work completed
1007 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-14 | 3 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G4-T28 to T36 -09 tables Grass Cutting work completed
1008 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-15 | 3 | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 15 | G4-T37 to T50 -15 tables Grass Cutting work completed
1009 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-16 | 3 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G4-T51 to T59 -09 tables Grass Cutting work completed
1010 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-17 | [8 empty] | 0
1011 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-18 | 3 | 1 | 2 | 10 | 0 | 0 | 0 | 0 | 12 | G4-T60 to T71 -12 tables Grass Cutting work completed
1012 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-19 | 3 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 9 | G4-T72 to T80 -09 tables Grass Cutting work completed
1013 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-20 | 3 | 1 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | G4-T81 to T87 -07 tables Grass Cutting work completed
1014 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-21 | 3 | 1 | 0 | 0 | 18 | 0 | 0 | 0 | 18 | G4-T88 to T105 -18 tables Grass Cutting work completed
1015 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-22 | [8 empty] | 0
1016 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-23 | 3 | 1 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | G4-T106 to T125 -20 tables Grass Cutting work completed
1017 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-24 | 3 | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | G4-T126 to T131 -06 tables Grass Cutting work completed
1018 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-25 | [8 empty] | 0
1019 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-26 | 4 | 1 | 0 | 0 | 0 | 0 | 2 | 10 | 12 | G1- T41 to T52-12 Tables Grass Cutting Work completed
1020 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-27 | 4 | 1 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | G1- T36 to T40-05 Tables Grass Cutting Work completed
1021 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-28 | [8 empty] | 0
1022 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-29 | [8 empty] | 0
1023 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-30 | [8 empty] | 0
1024 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-31 | 4 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G1-T26 to T35-09 Tables Grass Cutting Work Completed
1025 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-01 | [8 empty] | 0
1026 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-02 | 4 | 1 | 0 | 0 | 0 | 0 | 14 | 0 | 14 | G1-T12 to T25-14 Tables Grass Cutting Work Completed
1027 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-03 | [8 empty] | 0
1028 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-04 | 4 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G1-T05 to T11-07 Tables Grass Cutting Work Completed
1029 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-05 | 4 | 1 | 0 | 0 | 0 | 0 | 4 | 0 | 4 | G1-T01 to T04-04 Tables Grass Cutting Work Completed
1030 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-06 | [8 empty] | 0
1031 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-07 | [8 empty] | 0
1032 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | 4 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G2-T35 to T41-07 Tables Grass Cutting Work Completed
1033 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-09 | [8 empty] | 0
1034 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-10 | 4 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G2-T28 to T34-07 Tables Grass Cutting Work Completed
1035 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-11 | 4 | 1 | 0 | 0 | 0 | 0 | 11 | 0 | 11 | G2-T18 to T27-11 Tables Grass Cutting Work Completed
1036 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-12 | 4 | 1 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | G2-T01 to T17-17 Tables Grass Cutting Work Completed
1037 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-13 | [8 empty] | 0
1038 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-14 | [8 empty] | 0
1039 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-15 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Spare Area Grass Cutting Completed
1040 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-16 | [8 empty] | 0
1041 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-17 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G2 Side Non PV Area Grass Cutting Work done
1042 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-18 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Spare Area Grass Cutting Completed
1043 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-19 | [8 empty] | 0
1044 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-20 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Spare Area Grass Cutting Completed
1045 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-21 | [8 empty] | 0
1046 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-22 | [8 empty] | 0
1047 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-23 | [8 empty] | 0
1048 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-24 | [8 empty] | 0
1049 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | [8 empty] | 0
1050 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-26 | [8 empty] | 0
1051 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-27 | [8 empty] | 0
1052 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | [8 empty] | 0
1053 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-29 | [8 empty] | 0
1054 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-30 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Fench Side Grass Cutting Work Done
1055 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-31 | [8 empty] | 0
1056 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-01 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Fench Side Grass Cutting Work Done
1057 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-02 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Fench Side Grass Cutting Work Done
1058 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-03 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Fench Side Grass Cutting Work Done
1059 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-04 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 Fence side area Grass cutting work done
1060 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-05 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 Fence side area Grass cutting work done
1061 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-06 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Fench Side Grass Cutting Work Done
1062 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-07 | [8 empty] | 0
1063 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-08 | [8 empty] | 0
1064 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-09 | [8 empty] | 0
1065 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-10 | [8 empty] | 0
1066 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-11 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 Fench Side Grass cutting Work Done
1067 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-12 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR Surrounding Area Grass Cutting Work Done
1068 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-13 | [8 empty] | 0
1069 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-14 | [8 empty] | 0
1070 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-15 | [8 empty] | 0
1071 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-16 | [8 empty] | 0
1072 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-17 | [8 empty] | 0
1073 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-18 | [8 empty] | 0
1074 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-19 | [8 empty] | 0
1075 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-20 | [8 empty] | 0
1076 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-21 | [8 empty] | 0
1077 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-22 | [8 empty] | 0
1078 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-23 | [8 empty] | 0
1079 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-24 | [8 empty] | 0
1080 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-25 | [8 empty] | 0
1081 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-26 | [8 empty] | 0
1082 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-27 | [8 empty] | 0
1083 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-28 | [8 empty] | 0
1084 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-01 | [8 empty] | 0
1085 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-02 | [8 empty] | 0
1086 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-03 | [8 empty] | 0
1087 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-04 | [8 empty] | 0
1088 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-05 | [8 empty] | 0
1089 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-06 | [8 empty] | 0
1090 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-07 | [8 empty] | 0
1091 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-08 | [8 empty] | 0
1092 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-09 | [8 empty] | 0
1093 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-10 | [8 empty] | 0
1094 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-11 | [8 empty] | 0
1095 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-12 | [8 empty] | 0
1096 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-13 | [8 empty] | 0
1097 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-14 | [8 empty] | 0
1098 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-15 | [8 empty] | 0
1099 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-16 | [8 empty] | 0
1100 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-17 | [8 empty] | 0
1101 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-18 | [8 empty] | 0
1102 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-19 | [8 empty] | 0
1103 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-20 | [8 empty] | 0
1104 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | [8 empty] | 0
1105 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-22 | [8 empty] | 0
1106 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-23 | [8 empty] | 0
1107 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-24 | [8 empty] | 0
1108 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-25 | [8 empty] | 0
1109 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-26 | [8 empty] | 0
1110 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-27 | [8 empty] | 0
1111 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-28 | [8 empty] | 0
1112 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | [8 empty] | 0
1113 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | [8 empty] | 0
1114 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | [8 empty] | 0
1115 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | [8 empty] | 0
1116 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | [8 empty] | 0
1117 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | [8 empty] | 0
1118 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | [8 empty] | 0
1119 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | [8 empty] | 0
1120 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | [8 empty] | 0
1121 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | [8 empty] | 0
1122 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | [8 empty] | 0
1123 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | [8 empty] | 0
1124 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | [8 empty] | 0
1125 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | [8 empty] | 0
1126 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | [8 empty] | 0
1127 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | [8 empty] | 0
1128 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | [8 empty] | 0
1129 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | [8 empty] | 0
1130 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | [8 empty] | 0
1131 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | [8 empty] | 0
1132 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | [8 empty] | 0
1133 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | [8 empty] | 0
1134 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | [8 empty] | 0
1135 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | [8 empty] | 0
1136 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | [8 empty] | 0
1137 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | [8 empty] | 0
1138 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | [8 empty] | 0
1139 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | [8 empty] | 0
1140 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | [8 empty] | 0
1141 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | [8 empty] | 0
1142 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | [8 empty] | 0
1143 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | [8 empty] | 0
1144 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | [8 empty] | 0
1145 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | [8 empty] | 0
1146 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 T1 TO T10-10 Tab;es Manual Grass Cutting Work Done
1147 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 T21 TO T42-10 Tab;es Manual Grass Cutting Work Done
1148 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 T43 TO T60-17 Tab;es Manual Grass Cutting Work Done
1149 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 T01 TO T20-20 Tables Manual Grass Cutting Work Done
1150 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 T21 TO T40-20 Tables Manual Grass Cutting Work Done
1151 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 T41 TO T60-20 Tables Manual Grass Cutting Work Done
1152 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 T61 TO T80-20 Tables Manual Grass Cutting Work Done
1153 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | [8 empty] | 0
1154 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 T81 TO T88-08 Tables Manual Grass Cutting Work Done
1155 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | [8 empty] | 0
1156 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | [8 empty] | 0
1157 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | [8 empty] | 0
1158 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | [8 empty] | 0
1159 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | [8 empty] | 0
1160 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | [8 empty] | 0
1161 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | [8 empty] | 0
1162 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | [8 empty] | 0
1163 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | [8 empty] | 0
1164 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | [8 empty] | 0
1165 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | [8 empty] | 0
1166 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | [8 empty] | 0
1167 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | [8 empty] | 0
1168 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | [8 empty] | 0
1169 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | [8 empty] | 0
1170 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | [8 empty] | 0
1171 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | [8 empty] | 0
1172 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | [8 empty] | 0
1173 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | [8 empty] | 0
1174 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | [8 empty] | 0
1175 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | [8 empty] | 0
1176 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | [8 empty] | 0
1177 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5-T01 TO T25 -Manual Grass cutting work completed
1178 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | [8 empty] | 0
1179 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5-T26 TO T50 -Manual Grass cutting work completed
1180 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5-T51 TO T70 -Manual Grass cutting work completed
1181 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5-T71 TO T89 -Manual Grass cutting work completed
1182 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5-T90 TO T120 -Manual Grass cutting work completed
1183 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5-T121 TO T140 -Manual Grass cutting work completed
1184 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5-T141 TO T155 -Manual Grass cutting work completed
1185 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 1 | 2 | 0 | 0 | 0 | 0 | 4 | 0 | 4 | G4 T01 TO T04 -04 Tables Grass Cutting Work Completed
1186 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 1 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G4 T05 TO T12 -08 Tables Grass Cutting Work Completed
1187 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4-T101 TO T135 -Manual Grass cutting work Completed
1188 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 1 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G4 T13 TO T20 -08 Tables Grass Cutting Work Completed
1189 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 1 | 2 | 3 | 0 | 0 | 0 | 4 | 0 | 7 | G4 T21 TO T27 -07 Tables Grass Cutting Work Completed
1190 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 1 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | G4 T28 TO T34 -07 Tables Grass Cutting Work Completed
1191 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 1 | 2 | 15 | 0 | 0 | 0 | 0 | 0 | 15 | G4 T35 TO T49 -15 Tables Grass Cutting Work Completed
1192 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 1 | 2 | 11 | 5 | 0 | 0 | 0 | 0 | 16 | G4 T50 TO T65 -16 Tables Grass Cutting Work Completed
1193 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 1 | 2 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | G4 T66 TO T73 -08 Tables Grass Cutting Work Completed
1194 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 1 | 2 | 0 | 0 | 14 | 0 | 0 | 0 | 14 | G4 T74 TO T87 -14 Tables Grass Cutting Work Completed
1195 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 1 | 2 | 0 | 0 | 18 | 0 | 0 | 0 | 18 | G4 T88 TO T105 -18 Tables Grass Cutting Work Completed
1196 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 1 | 2 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | G4-T106 to T114 -09 tables Grass Cutting work completed
1197 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 1 | 2 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | G4-T115 to T125 -11 tables Grass Cutting work completed
1198 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR Surrounding Area Grass Cutting Work Done
1199 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR Surrounding Area Grass Cutting Work Done
1200 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 1 | 2 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | G4-T126 to T140 -15 tables Grass Cutting work completed
1201 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 1 | 2 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | G4-T141 to T143 & G5-T146 TO T158 -16 tables Grass Cutting work completed
1202 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 1 | 2 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | G5-T131 TO T145 -15 tables Grass Cutting work completed
1203 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 1 | 2 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | G5-T118 TO T130 -13 tables Grass Cutting work completed
1204 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 1 | 2 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G5-T110 TO T117 -08 tables Grass Cutting work completed
1205 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 1 | 2 | 0 | 0 | 6 | 0 | 0 | 0 | 6 | G5-T105 TO T110A -06 tables Grass Cutting work completed
1206 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 1 | 2 | 0 | 0 | 0 | 0 | 13 | 0 | 13 | G3 TW1 TO TW5-5 Tables & T1 TO T8-13 Tables Grass Cutting work Completed
1207 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 1 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | G3 - T9 TO T13-05 Tables Grass Cutting work Completed
1208 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 1 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | G3 - T14 TO T 21-8 Tables Grass Cutting work Completed
1209 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 1 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | G3 - T22 TO T 31-10 Tables Grass Cutting work Completed
1210 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 1 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G3 - T32 TO T 37-06 Tables Grass Cutting work Completed
1211 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 1 | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | G3 - T38 TO T 44-08 Tables Grass Cutting work Completed
1212 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 1 | 2 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | G3 - T45 TO T49 -05 Tables Grass Cutting work Completed
1213 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 1 | 2 | 0 | 0 | 6 | 0 | 0 | 0 | 6 | G3 - T50 TO T56-06 Tables Grass Cutting work Completed
1214 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 1 | 2 | 0 | 0 | 9 | 0 | 0 | 0 | 9 | G3 - T57 TO T64-08 Tables Grass Cutting work Completed
1215 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 1 | 2 | 0 | 0 | 6 | 10 | 0 | 0 | 16 | G3 - T65 TO T68 & 63 G5 82 to 91 -16 Tables Grass Cutting work Completed
1216 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 1 | 2 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | G5 - T69 TO T81 -13 Tables Grass Cutting work Completed
1217 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 1 | 2 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | G5 - T62 TO T68 -7 Tables Grass Cutting work Completed
1218 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 1 | 2 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | G5 - T48 TO T61 -14 Tables Grass Cutting work Completed
1219 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 1 | 2 | [6 empty] | 0
Formulas:
Days = DAY(EOMONTH([Month Year],0))
Date = [Date, row above]+1

## Spare_Consumable
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Item Consumed | Qty Consumed | Place of Consumption | Ownership of Spare/Consumable | Remarks for the day
1 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | MC4 CONNECTORS | 1 | IC1_Inv4_SCB2_String9
2 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | +VE YCONNECTOR | 1 | IC1_Inv4_SCB3_String14
3 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | +VE YCONNECTOR | 1 | IC1_Inv4_SCB6_String4
4 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | MC4 CONNECTORS | 1 | IC2_Inv1_SCB1_String9
5 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | MC4 CONNECTORS | 1 | IC2_Inv1_SCB2_String1
6 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | +VE YCONNECTOR | 1 | IC2_Inv1_SCB10_String2
7 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-09 | Y CONNECTORS | 1 | IC1_Inv2_SCB1_String14
8 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-09 | No used | 1 | IC1_Inv2_SCB6_String10
9 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-11 | Y CONNECTORS | 1 | IC1_Inv2_SCB8_String5
10 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | Y CONNECTORS | 1 | IC1_Inv2_SCB5_String5
11 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | Mc4 connector Male | 1 | IC1_Inv2_SCB1_String9
12 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | Negative Y connector | 1 | IC1_Inv2_SCB6_String12
13 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | Positive Y connector | 1 | IC1_Inv1_SCB6_String12
14 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | Positive Y connector | 1 | IC1_Inv1_SCB5_String8
15 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | Positive Y connector | 1 | IC1_Inv1_SCB1_String5
16 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | Positive Y connector | 1 | IC1_Inv1_SCB8_String13
17 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | Positive Y connector | 1 | IC1_Inv3_SCB1_String1
18 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | Positive Y connector | 1 | IC1_Inv3_SCB1_String14
19 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | Mc4 connector Male & Female | 1 | IC1_Inv3_SCB7_String9
20 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-19 | Positive Y connector | 1 | IC1_Inv4_SCB4_String13
21 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-29 | Positive Y connector | 1 | IC1_Inv4_SCB6_String10
22 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-29 | Positive Y connector | 1 | IC2_Inv1_SCB1_String1
23 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-02 | Mc4 connector Male & Female | 1 | IC1_Inv4_SCB8_String6
24 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-07 | Positive Y connector | 1 | IC2_Inv6_SCB3_String7
25 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-07 | Positive Y connector | 1 | IC2_Inv5_SCB2_String8
26 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-16 | Tilt sensor add-04 installed | 1 | IC2_Inv1
27 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | pcb board replaced | 1 | IC1_Inv4
28 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
29 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
30 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
31 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-20 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
32 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-20 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
33 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-21 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
34 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-21 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv1
35 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-22 | Tilt sensor add-02 installed | 2 | IC1_Inv4
36 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-22 | New 2 Nos Battery Replaced | 2 | IC1_Inv4
37 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-23 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
38 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-25 | Positive Y connector | 1 | IC2_Inv5_SCB2_String 1
39 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-25 | Positive Y connector | 1 | IC2_Inv5_SCB4_String 4
40 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-25 | Positive Y connector | 1 | IC1_Inv2_SCB5_String 13
41 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-25 | Positive Y connector | 1 | IC1_Inv1_SCB3_String 6
42 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-25 | Positive Y connector | 1 | IC1_Inv3_SCB3_String 13
43 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-25 | Positive Y connector | 2 | IC1_Inv4_SCB3_String 7 & 14
44 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-27 | New 2 Nos Battery Replaced | 2 | IC2_Inv1
45 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-27 | Pcb board replaced | 1 | IC2_Inv2
46 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-27 | Add 002 tilt sensor installed | 2 | IC2_Inv2
47 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-27 | Y-Connector | 1 | IC1_Inv4_SCB3_String 3
48 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-27 | String Cable | 6 Metre | IC1_Inv4_SCB5_String 2
49 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-28 | Y-Connector | 1 | IC1_Inv4_SCB4_String 12
50 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-31 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
51 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-31 | MC4 Connector | 1 | IC2_Inv6_SCB4_String 7
52 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-03 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
53 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-03 | Actuator 1 small,1 medium gear wheel & Diode 2 Nos was replaced | Each 1 | IC1_Inv4
54 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-03 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Noswas replaced | Each 1 | IC2_Inv2
55 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
56 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC1_Inv2
57 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | Actuator 1 small,1 medium gear wheel & Diode 2 Nos was replaced | Each 1 | IC1_Inv3
58 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC1_Inv2
59 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-02 | 30 | 2022-09-07 | MC4 Connector | 1 | IC1_Inv4_SCB4_String 12
60 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-02 | 30 | 2022-09-07 | MC4 Connector | 1 | IC1_Inv4_SCB3_String 7
61 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-02 | 30 | 2022-09-07 | MC4 Connector | 1 | IC1_Inv4_SCB3_String 14
62 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-02 | 30 | 2022-09-07 | Y-Connector | 1 | IC1_Inv1_SCB7_String 9
63 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-02 | 30 | 2022-09-07 | Y-Connector | 1 | IC2_Inv6_SCB1_String 9
64 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-03 | 30 | 2022-09-09 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC1_Inv2
65 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-04 | 30 | 2022-09-09 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv3
66 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-05 | 30 | 2022-09-09 | Actuator 1 small,1 medium gear wheel & Diode 2 Nos was replaced | Each 1 | IC1_Inv 1
67 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-06 | 30 | 2022-09-09 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC1_Inv 4
68 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-07 | 30 | 2022-09-10 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB2_String 7
69 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-08 | 30 | 2022-09-10 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC1_Inv 3
70 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-09 | 30 | 2022-09-10 | Actuator 1 Big gear wheel & 1 motor& Diode 2 Nos was replaced | Each 1 | IC1_Inv 3
71 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-10 | 30 | 2022-09-10 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 3
72 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-11 | 30 | 2022-09-10 | Actuator 1 small,1 medium gear wheel & Diode 2 Nos was replaced | Each 1 | IC2_Inv 5
73 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-12 | 30 | 2022-09-10 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC2_Inv 5
74 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-13 | 30 | 2022-09-11 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC2_Inv 5
75 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-14 | 30 | 2022-09-11 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB2_String 7
76 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-15 | 30 | 2022-09-11 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB3_String 6
77 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-16 | 30 | 2022-09-12 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB3_String 6
78 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-17 | 30 | 2022-09-13 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB1_String 6
79 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-18 | 30 | 2022-09-13 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 5
80 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-19 | 30 | 2022-09-13 | Actuator 1 small,1 medium gear wheel & Diode 2 Nos was replaced | Each 1 | IC1_Inv 1
81 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-20 | 30 | 2022-09-13 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC2_Inv 6
82 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-21 | 30 | 2022-09-13 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 1
83 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-22 | 30 | 2022-09-14 | Actuator 1 small,1 medium gear wheel & Diode 2 Nos was replaced | Each 1 | IC1_Inv 2
84 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-23 | 30 | 2022-09-14 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 2
85 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-24 | 30 | 2022-09-14 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB1_String 6
86 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-25 | 30 | 2022-09-14 | Negative Y connector Replaced | 1 | IC1_Inv2_SCB10_String 7
87 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-25 | 30 | 2022-09-14 | Mc4 Connector replaced | 1 | IC1_Inv1_SCB7_String 13
88 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-25 | 30 | 2022-09-14 | Mc4 Connector replaced | 1 | IC1_Inv4_SCB8_String 9
89 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-26 | 30 | 2022-09-15 | Mc4 Connector replaced | 1 | IC1_Inv4_SCB5_String 14
90 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-27 | 30 | 2022-09-15 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB1_String 4
91 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-28 | 30 | 2022-09-15 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB1_String 3
92 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-29 | 30 | 2022-09-15 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 5
93 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-15 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 5
94 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-15 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 5
95 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-16 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB2_String 6
96 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-16 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB3_String 3
97 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-17 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB2_String 2
98 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-17 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 1
99 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB3_String 1
100 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 320 Watts module(1 No)104110100024 | 1 | IC2_Inv5_SCB7_String 1
101 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110101130 | 1 | IC2_Inv5_SCB7_String 8
102 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110101176 | 1 | IC1_Inv1_SCB3_String 13
103 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110101127 | 1 | IC1_Inv1_SCB4_String 12
104 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100753 | 1 | IC1_Inv1_SCB4_String 13
105 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110101014 | 1 | IC1_Inv1_SCB6_String 13
106 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110101023 | 1 | IC1_Inv1_SCB7_String 10
107 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100881 | 1 | IC1_Inv1_SCB8_String 14
108 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100791 | 1 | IC1_Inv1_SCB8_String 14
109 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100840 | 1 | IC1_Inv2_SCB2_String 13
110 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100877 | 1 | IC1_Inv3_SCB1_String 13
111 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100997 | 1 | IC1_Inv3_SCB1_String 13
112 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100805 | 1 | IC1_Inv3_SCB1_String 13
113 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100965 | 1 | IC1_Inv3_SCB1_String 13
114 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100986 | 1 | IC1_Inv3_SCB1_String 11
115 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100502 | 1 | IC1_Inv3_SCB8_String 1
116 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB3_String 3
117 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB1_String 3
118 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101192 | 1 | IC1_Inv2_SCB3_String 13
119 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101194 | 1 | IC1_Inv2_SCB3_String 13
120 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101198 | 1 | IC1_Inv2_SCB4_String 13
121 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101111 | 1 | IC1_Inv2_SCB7_String 9
122 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101245 | 1 | IC1_Inv2_SCB8_String 3
123 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101257 | 1 | IC1_Inv2_SCB8_String 2
124 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101258 | 1 | IC1_Inv2_SCB9_String 6
125 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101259 | 1 | IC1_Inv1_SCB9_String 7
126 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101290 | 1 | IC2_Inv6_SCB7_String 3
127 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101253 | 1 | IC2_Inv6_SCB7_String 3
128 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB4_String 1
129 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101123 | 1 | IC1_Inv3_SCB4_String 3
130 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101099 | 1 | IC1_Inv3_SCB4_String 3
131 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101210 | 1 | IC1_Inv3_SCB4_String 4
132 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101124 | 1 | IC1_Inv3_SCB4_String 9
133 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101252 | 1 | IC1_Inv3_SCB4_String 10
134 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101289 | 1 | IC1_Inv3_SCB5_String 10
135 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101097 | 1 | IC1_Inv3_SCB7_String 14
136 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101133 | 1 | IC1_Inv3_SCB5_String 8
137 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101375 | 1 | IC1_Inv3_SCB5_String 8
138 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101491 | 1 | IC1_Inv3_SCB4_String 7
139 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101040 | 1 | IC1_Inv3_SCB3_String 1
140 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101385 | 1 | IC1_Inv3_SCB2_String 2
141 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101342 | 1 | IC1_Inv3_SCB2_String 3
142 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101492 | 1 | IC1_Inv3_SCB1_String 2
143 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110100943 | 1 | IC1_Inv2_SCB2_String 2
144 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101013 | 1 | IC1_Inv2_SCB2_String 1
145 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110100355 | 1 | IC1_Inv2_SCB1_String 4
146 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB4_String 13
147 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104110101007 | 1 | IC1_Inv1_SCB8_String 2
148 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104110101009 | 1 | IC1_Inv1_SCB7_String 4
149 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104110101079 | 1 | IC1_Inv1_SCB7_String 1
150 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104110101077 | 1 | IC1_Inv1_SCB4_String 4
151 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104110101132 | 1 | IC1_Inv1_SCB4_String 5
152 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104110101246 | 1 | IC1_Inv4_SCB1_String 12
153 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104110101125 | 1 | IC1_Inv4_SCB6_String 2
154 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104111000463 | 1 | IC1_Inv4_SCB6_String 4
155 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-22 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB4_String 10
156 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101019 | 1 | IC1_Inv1_SCB6_String 4
157 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101128 | 1 | IC1_Inv1_SCB4_String 2
158 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101037 | 1 | IC1_Inv1_SCB3_String 4
159 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101056 | 1 | IC1_Inv1_SCB2_String 3
160 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101041 | 1 | IC1_Inv3_SCB3_String 9
161 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101044 | 1 | IC1_Inv4_SCB10_String 4
162 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101274 | 1 | IC1_Inv4_SCB10_String 4
163 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101251 | 1 | IC1_Inv4_SCB9_String 1
164 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101304 | 1 | IC1_Inv4_SCB9_String 4
165 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101286 | 1 | IC1_Inv4_SCB8_String 6
166 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101193 | 1 | IC1_Inv4_SCB6_String 13
167 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101195 | 1 | IC1_Inv3_SCB7_String 3
168 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101160 | 1 | IC1_Inv3_SCB6_String 14
169 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101061 | 1 | IC1_Inv3_SCB3_String 14
170 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110101118 | 1 | IC2_Inv6_SCB5_String 2
171 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110101063 | 1 | IC2_Inv6_SCB5_String 1
172 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110101177 | 1 | IC2_Inv6_SCB4_String 4
173 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 330 Watts module(1 No)104220900182 | 1 | IC2_Inv6_SCB4_String 1
174 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110101042 | 1 | IC2_Inv6_SCB2_String 12
175 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110100942 | 1 | IC2_Inv6_SCB2_String 11
176 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110100806 | 1 | IC2_Inv6_SCB6_String 12
177 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110100807 | 1 | IC2_Inv6_SCB6_String 13
178 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804577 | 1 | IC2_Inv6_SCB6_String 14
179 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804153 | 1 | IC2_Inv6_SCB7_String 12
180 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804766 | 1 | IC2_Inv6_SCB8_String 12
181 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104107202563 | 1 | IC1_Inv2_SCB9_String 4
182 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106605065 | 1 | IC1_Inv2_SCB8_String 9
183 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104107202470 | 1 | IC1_Inv2_SCB8_String 9
184 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804432 | 1 | IC1_Inv2_SCB7_String 7
185 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804315 | 1 | IC1_Inv2_SCB7_String 12
186 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804334 | 1 | IC1_Inv2_SCB7_String 12
187 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804467 | 1 | IC1_Inv2_SCB7_String 12
188 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804324 | 1 | IC1_Inv2_SCB7_String 12
189 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104107202533 | 1 | IC1_Inv2_SCB6_String 4
190 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104107201670 | 1 | IC1_Inv2_SCB6_String 4
191 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110401125 | 1 | IC1_Inv2_SCB6_String 3
192 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104107202165 | 1 | IC1_Inv2_SCB4_String 3
193 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-25 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 4
194 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-25 | Tilt sensor add-05 installed 1 No | 1 | IC1_Inv 3
195 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-25 | Tilt sensor add-01 installed 1 No | 1 | IC1_Inv 2
196 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101131 | 1 | IC2_Inv6_SCB9_String 4
197 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101271 | 1 | IC2_Inv5_SCB4_String 9
198 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101275 | 1 | IC2_Inv5_SCB2_String 10
199 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101217 | 1 | IC2_Inv5_SCB2_String 13
200 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101273 | 1 | IC2_Inv5_SCB2_String 13
201 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101276 | 1 | IC2_Inv5_SCB1_String 7
202 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101010 | 1 | IC2_Inv5_SCB1_String 5
203 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101008 | 1 | IC2_Inv5_SCB2_String 2
204 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101302 | 1 | IC2_Inv5_SCB4_String 2
205 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101219 | 1 | IC2_Inv5_SCB4_String 2
206 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101277 | 1 | IC2_Inv5_SCB4_String 2
207 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-27 | New 2 Nos Battery Replaced | 2 | IC2_Inv 5
208 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-27 | Tilt sensor add-01 installed 1 No | 1 | IC1_Inv 3
209 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-27 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 1
210 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-27 | Replaced old PV 325 Watts module(1 No)104110101163 | 1 | IC1_Inv2_SCB3_String 8
211 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-27 | Replaced New PV 330 Watts module(1 No)104249300044 | 1 | IC2_Inv6_SCB3_String 3
212 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-28 | Tilt sensor add-04 installed 1 No | 1 | IC1_Inv 4
213 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-28 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 2
214 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-29 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 1
215 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-30 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 1
216 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-30 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 6
217 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-01 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 1
218 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-03 | 1 No PCB Replaced | 1 | IC2_Inv 1
219 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-03 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 4
220 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv 1
221 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 2
222 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 3
223 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 3
224 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-09 | Positive Y-Connector | 1 | IC2_Inv6_SCB1_String 7
225 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-09 | Positive Y-Connector | 1 | IC2_Inv5_SCB2_String 1
226 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-10 | Positive Y-Connector | 1 | IC2_Inv5_SCB8_String 10
227 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv 1
228 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv 1
229 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 1
230 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 2
231 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | Tilt sensor add-03 installed 1 No | 1 | IC2_Inv 1
232 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | New 2 Nos Batteries Replaced | 2 | IC1_Inv 1
233 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB1_String 1
234 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-12 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv 4
235 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-12 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 3
236 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-15 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
237 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-15 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
238 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-18 | Charge control unit replaced | 1 | IC1_Inv2
239 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-21 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
240 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-21 | Actuator 1 No Motor was replaced | 1 | IC1_Inv3
241 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-23 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
242 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-24 | MC4 Connector(Male & Female) | 1 | IC2_Inv 1
243 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-26 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv3
244 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-28 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv 4
245 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-28 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv 4
246 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-28 | 1 no. Actuator Nylon Brass Bush replaced | 1 | IC1_Inv2
247 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-31 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 1
248 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-02 | 1 no. Actuator Nylon Brass Bush replaced | 1 | IC2_Inv 1
249 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-03 | New 2 Nos Batteries Replaced | 2 | IC2_Inv2
250 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-07 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
251 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-10 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
252 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-10 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv1
253 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-10 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv1
254 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-12 | New 2 Nos Batteries Replaced | 2 | IC1_Inv3
255 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-12 | New 2 Nos Batteries Replaced | 2 | IC1_Inv4
256 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-18 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
257 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-18 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv1
258 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-22 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv1
259 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-24 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv1
260 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-27 | New 2 Nos Batteries Replaced | 2 | IC2_Inv1
261 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-30 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
262 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-30 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
263 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-30 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv4
264 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-30 | New 2 Nos Batteries Replaced | 2 | IC1_Inv4
265 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-06 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
266 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-06 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
267 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-06 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv1
268 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-11 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
269 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-11 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv1
270 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-11 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
271 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-15 | 2 Nos MSAT box Batteries Replaced | 2 | IC2_Inv1
272 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-15 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
273 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-15 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
274 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-16 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
275 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-17 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
276 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-17 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
277 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-20 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
278 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-24 | Positive Y-Connector | 1 | IC1_Inv2_SCB5_String 1
279 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-25 | MC4 Connector(Male & Female) | 1 | IC1_Inv4_SCB3_String 9
280 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-25 | Positive Y-Connector | 1 | IC1_Inv4_SCB3_String 5
281 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-25 | Positive Y-Connector | 1 | IC1_Inv4_SCB4_String 9
282 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-26 | Positive Y-Connector | 1 | IC1_Inv4_SCB2_String 2
283 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-26 | Positive & Negative Y-Connector | 1 | IC1_Inv4_SCB2_String 11
284 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-26 | MC4 Connector(Male & Female) | 1 | IC1_Inv4_SCB4_String 12
285 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-29 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv1
286 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-29 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
287 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-29 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
288 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-03 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv2
289 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-03 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
290 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-04 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv2
291 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-05 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
292 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-05 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv2
293 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-05 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
294 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-06 | 1 no. Actuator Motor replaced | 1 | IC2_Inv2
295 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-07 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
296 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-07 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
297 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-08 | Y Connector(+ve & -ve) | 1 | IC1_Inv4_SCB4_String 11
298 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-08 | MC4 Connector(Male & Female) | 1 | IC1_Inv4_SCB4_String 11
299 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | 2 Nos MSAT box Batteries Replaced | 2 | IC2_Inv2
300 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | 2 Nos MSAT box Batteries Replaced | 2 | IC2_Inv2
301 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | 2 Nos MSAT box Batteries Replaced | 2 | IC2_Inv2
302 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | 2 Nos MSAT box Batteries Replaced | 2 | IC1_Inv2
303 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | 2 Nos MSAT box Batteries Replaced | 2 | IC1_Inv2
304 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
305 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
306 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | 2 Nos MSAT box Batteries Replaced | 2 | IC1_Inv2
307 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | 2 Nos MSAT box Batteries Replaced | 2 | IC1_Inv2
308 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | 2 Nos MSAT box Batteries Replaced | 2 | IC2_Inv2
309 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-17 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
310 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-18 | 2 Nos MSAT box Batteries Replaced | 2 | IC2_Inv2
311 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-20 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
312 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-20 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
313 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-20 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv4
314 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-21 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
315 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-22 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
316 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-22 | 1 No Actuator Small Gear Replaced | 1 | IC1_Inv2
317 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-23 | 1 No Actuator Motor Replaced | 1 | IC2_Inv2
318 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-23 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv1
319 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-24 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
320 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-25 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
321 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-26 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
322 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
323 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
324 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
325 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
326 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-29 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
327 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-29 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
328 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-30 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
329 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-30 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
330 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-31 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
331 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-02 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
332 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-02 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
333 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-02 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
334 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-03 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
335 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-03 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv1
336 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | 1 No Actuator Motor Replaced | 1 | IC1_Inv2
337 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
338 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
339 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | MC4 Connector(Male & Female) | 1 | IC1_Inv4_SCB4_String 10
340 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-07 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
341 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-07 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv4
342 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-07 | 1 No Medium Gear Replaced | 1 | IC1_Inv4
343 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-08 | 1 No Actuator Bearing Replaced | 1 | IC2_Inv2
344 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-08 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
345 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | 2 Nos MSAT box Batteries Replaced | 2 | IC1_Inv1
346 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv2
347 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
348 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | 1 No Actuator Bearing Replaced | 1 | IC1_Inv2
349 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-10 | 1 No Actuator Bearing Replaced | 1 | IC1_Inv4
350 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-10 | 1 No Actuator Motor Replaced | 1 | IC1_Inv2
351 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-11 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
352 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-11 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
353 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-12 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
354 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-12 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
355 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-13 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
356 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-14 | 2 Nos MSAT box Batteries Replaced | 2 | IC2_Inv1
357 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-14 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
358 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-14 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
359 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-15 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
360 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-16 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv4
361 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | Positive Y-Connector | 1 | IC1_Inv4_SCB4_String 5
362 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | Positive Y-Connector | 1 | IC1_Inv4_SCB4_String 13
363 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
364 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
365 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv1
366 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-18 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
367 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-19 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
368 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-19 | 1 No Actuator Bearing Replaced | 1 | IC2_Inv2
369 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-20 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
370 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-21 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
371 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-21 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
372 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-21 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
373 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-22 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
374 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-22 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
375 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-22 | Positive Y-Connector | 1 | IC1_Inv1_SCB2_String 1
376 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-23 | 1 No Actuator Motor Replaced | 1 | IC2_Inv2
377 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-24 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
378 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-24 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
379 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-24 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
380 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-25 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
381 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-25 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
382 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-25 | 1 No Big Gear Replaced | 1 | IC1_Inv4
383 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-26 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
384 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-26 | 1 No Big Gear Replaced | 1 | IC2_Inv2
385 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-26 | Charge control unit replaced | 1 | IC2_Inv1
386 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-27 | Charge control unit replaced | 1 | IC2_Inv1
387 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-01 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
388 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-02 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
389 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-02 | 1 No Actuator Motor Replaced | 1 | IC1_Inv2
390 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-02 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
391 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
392 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | 1 No Actuator Motor Replaced | 1 | IC2_Inv1
393 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
394 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
395 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-05 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
396 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-05 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
397 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-05 | 1 No Actuator Small Gear Replaced | 1 | IC2_Inv2
398 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-09 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
399 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-09 | 1 No Actuator Motor Replaced | 1 | IC1_Inv2
400 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-09 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv2
401 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-10 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv2
402 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-12 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
403 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-12 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
404 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-13 | 1 No Actuator Medium Gear Replaced | 1 | IC2_Inv2
405 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-16 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
406 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-16 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
407 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-18 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
408 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-18 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv2
409 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-19 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv3
410 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-22 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
411 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-23 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
412 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-24 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv1
413 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-24 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
414 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-24 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
415 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-25 | Negative Y connector Replaced | 1 | IC2_Inv5_SCB1_String 1
416 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-25 | Negative Y connector Replaced | 1 | IC2_Inv5_SCB1_String 2
417 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-25 | MC4 Connector(Male & Female) | 1 | IC2_Inv5_SCB2_String 2
418 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-26 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
419 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-26 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
420 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-26 | Charge control unit replaced | 1 | IC1_Inv4
421 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-27 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
422 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-30 | MC4 Connector(Male & Female) | 1 | IC1_Inv4_SCB3_String 7
423 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-30 | Positive Y-Connector | 1 | IC1_Inv4_SCB1_String 3
424 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-31 | Positive Y-Connector | 1 | IC1_Inv2_SCB6_String 14
425 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-31 | MC4 Connector(Male & Female) | 1 | IC1_Inv2_SCB7_String 12
426 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-31 | Positive Y-Connector | 1 | IC1_Inv2_SCB3_String 10
427 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-07 | Charge control unit replaced | 1 | IC2_Inv2
428 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-09 | MC4 Connector(Male & Female) | 1 | IC2_Inv2_SCB1_String 1
429 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-09 | Positive Y-Connector | 1 | IC2_Inv2_SCB6_String 6
430 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-09 | Positive Y-Connector | 1 | IC1_Inv4_SCB4_String 9
431 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-09 | Negative Y connector Replaced | 1 | IC1_Inv4_SCB4_String 9
432 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-10 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv2
433 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-10 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
434 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-10 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
435 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-10 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv3
436 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-11 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
437 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-11 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
438 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-11 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv4
439 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-11 | 1 No Actuator Motor Replaced | 1 | IC1_Inv2
440 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
441 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | 1 No Actuator Motor Replaced | 1 | IC1_Inv3
442 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | MC4 Connector(Male & Female) | 1 | IC1_Inv1_SCB7_String 10
443 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | Positive Y-Connector | 1 | IC1_Inv1_SCB7_String 5
444 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | SCB 30A Fuse | 1 | IC1_Inv4_SCB2_String 2
445 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | Positive Y-Connector | 1 | IC1_Inv4_SCB5_String 13
446 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-14 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv1
447 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-17 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
448 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-17 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
449 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-18 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
450 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-18 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
451 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-18 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
452 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-18 | 1 No Actuator Medium Gear Replaced | 1 | IC2_Inv2
453 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-19 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
454 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-19 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
455 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-20 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
456 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-20 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
457 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-21 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv2
458 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-21 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv3
459 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-21 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
460 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-23 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
461 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | 1 No Actuator Motor Replaced | 1 | IC2_Inv1
462 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
463 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | Actuator motor 2 no.s Carbon brushes are replaced | 2 | IC1_Inv2
464 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | 1 no Circlip replaced | 1 | IC1_Inv2
465 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
466 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-25 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
467 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-25 | 1 No Actuator Motor Replaced | 1 | IC1_Inv4
468 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-25 | 1 No Circlip Replaced | 1 | IC1_Inv4
469 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
470 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | 1 No Circlip Replaced | 1 | IC2_Inv2
471 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
472 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
473 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
474 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-27 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
475 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-27 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv2
476 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-27 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
477 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-27 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
478 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-28 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
479 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-28 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
480 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-29 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
481 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-29 | 1 No Circlip Replaced | 1 | IC2_Inv1
482 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-02 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
483 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-04 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
484 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-04 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
485 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-05 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
486 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-06 | 1 No Actuator Bearing Replaced | 1 | IC2_Inv1
487 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-06 | 1 No Circlip Replaced | 1 | IC2_Inv1
488 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-08 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
489 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-09 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
490 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-12 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
491 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-14 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
492 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-14 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv1
493 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-18 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
494 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-18 | 1 No Actuator Motor Replaced | 1 | IC1_Inv4
495 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-18 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
496 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | Positive Y-Connector | 1 | IC1_Inv1_SCB4_String 2
497 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | Positive Y-Connector | 1 | IC1_Inv3_SCB3_String 15
498 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | MC4 Connector(Male & Female) | 1 | IC1_Inv4_SCB1_String 8
499 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | Positive Y-Connector | 1 | IC1_Inv4_SCB1_String 10
500 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | MC4 Connector(Male & Female) | 2 | IC1_Inv3_SCB9_String 4
501 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
502 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-21 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
503 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-22 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv1
504 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | Main Moving Contact | 3 | MCR Power Trafo OLTC
505 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | Resistor Moving Contact Assembly | 3 | MCR Power Trafo OLTC
506 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | Fixed Contact Assembly | 15 | MCR Power Trafo OLTC
507 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | Copper Braided Wire | 4 | MCR Power Trafo OLTC
508 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | Top Cover Gasket | 1 | MCR Power Trafo OLTC
509 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | Transformer Mineral Oil | 210 | MCR Power Trafo OLTC
510 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | Transformer Mineral Oil | 105 | MCR Power Trafo OLTC
511 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-26 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv4
512 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-26 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
513 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-26 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
514 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-26 | Charge control unit replaced | 1 | IC1_Inv3
515 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-27 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
516 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-27 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
517 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-28 | 1 No MSAT 12V 65Ah Battery replaced | 1 | IC1_Inv3
518 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-30 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
519 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-31 | Replaced New PV 330 Watts module(1 No)104249300044 | 1 | IC1_Inv4_SCB3_String 6
520 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-02 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
521 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-03 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
522 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-04 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv4
523 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-08 | Tracker Relay & Relay Base | 10 | IC2_Inv2
524 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-08 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
525 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-08 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
526 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-08 | Charge control unit replaced | 1 | IC2_Inv1
527 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-09 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
528 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-11 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
529 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-12 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
530 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-14 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
531 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-16 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
532 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-18 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv3
533 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-18 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
534 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-21 | 1 No Actuator Motor Replaced | 1 | IC1_Inv3
535 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-21 | 1 No Actuator Small Gear Replaced | 1 | IC1_Inv3
536 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-21 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv3
537 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-26 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
538 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-26 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
539 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-26 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
540 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-27 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv1
541 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-29 | MICOM Relay (Line Differential Protection Relay) - GE(Alstom) make | 1 | Line CRP Solar Panel, 66/11 kV KPTCL Substation Chowdanakuppe
542 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-01 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
543 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-01 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv1
544 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | Positive Y-Connector | 1 | IC1_Inv3_SCB6_String 6
545 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | Positive Y-Connector | 1 | IC1_Inv3_SCB6_String 9
546 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | Positive Y-Connector | 1 | IC1_Inv3_SCB6_String 13
547 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | Positive Y-Connector | 1 | IC1_Inv1_SCB7_String 1
548 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | Positive Y-Connector | 1 | IC2_Inv5_SCB9_String 6
549 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
550 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-05 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
551 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-05 | 1 No Actuator Motor Replaced | 1 | IC1_Inv3
552 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-05 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
553 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-06 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv3
554 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-06 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
555 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-09 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
556 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-09 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
557 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-11 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv4
558 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-12 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
559 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-14 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
560 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-15 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
561 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-15 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
562 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-16 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
563 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-17 | 1 No Actuator Motor Replaced | 1 | IC2_Inv1
564 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-18 | 1 No Actuator Motor Replaced | 1 | IC2_Inv1
565 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-19 | PCB_100 Type | 1 | IC2_Inv2
566 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-20 | PCB_100 Type | 1 | IC2_Inv2
567 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-20 | PCB_100 Type | 1 | IC1_Inv3
568 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-20 | PCB_100 Type | 1 | IC2_Inv1
569 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-20 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
570 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-21 | PCB_100 Type | 1 | IC1_Inv2
571 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-22 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
572 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | 1 No Limit Switch was replaced | 1 | IC2_Inv2
573 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
574 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
575 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
576 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
577 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-27 | Memory unit | 1 | IC2_Inv2
578 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-27 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
579 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-27 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
580 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-27 | PCB_100 Type | 1 | IC2_Inv2
581 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
582 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
583 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | 1 No Limit Switch was replaced | 1 | IC1_Inv4
584 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | Charge control unit replaced | 1 | IC2_Inv2
585 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | 1 no 25v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv2
586 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-30 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
587 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-31 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
588 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-31 | PCB_100 Type | 1 | IC2_Inv2
589 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-31 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
590 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-04 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
591 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-04 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
592 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-04 | 1 N0. 2000A Fuse Replaced | 1 | IC1_Inv1
593 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-07 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
594 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-08 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
595 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-08 | 1 No Actuator Medium Gear Replaced | 1 | IC2_Inv2
596 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-09 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
597 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-11 | 1 No Actuator Medium Gear Replaced | 1 | IC2_Inv1
598 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-12 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
599 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-13 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
600 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-13 | 1 No Limit Switch was replaced | 1 | IC1_Inv4
601 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-14 | 2 Nos Actuator carbon brush replaced | 2 | IC1_Inv1
602 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-14 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
603 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-15 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
604 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-16 | 1 No Limit Switch was replaced | 1 | IC1_Inv1
605 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-21 | 1 No Limit Switch was replaced | 1 | IC1_Inv2
606 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-23 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
607 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-24 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
608 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-25 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
609 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-26 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
610 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-27 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
611 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-27 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
612 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-28 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
613 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-30 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
614 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-30 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
615 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-31 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
616 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-31 | Charge control unit replaced | 1 | IC2_Inv1
617 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-31 | 1 No Limit Switch was replaced | 1 | IC1_Inv4
618 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-04 | 1 No Limit Switch was replaced | 1 | IC2_Inv1
619 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-05 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
620 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-05 | 1 No Limit Switch was replaced | 1 | IC2_Inv1
621 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-05 | PCB_100 Type | 1 | IC1_Inv1
622 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-05 | PCB_100 Type | 1 | IC1_Inv2
623 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-07 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
624 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-07 | 1 No Actuator Motor Replaced | 1 | IC2_Inv2
625 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-07 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
626 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-08 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
627 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-10 | Charge control unit replaced | 1 | IC1_Inv4
628 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-11 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
629 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-12 | 1 No Actuator Motor Replaced | 1 | IC2_Inv2
630 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-13 | PCB_100 Type | 1 | IC2_Inv2
631 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-13 | PCB_100 Type | 1 | IC2_Inv2
632 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-13 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
633 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-13 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
634 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-13 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC2_Inv2
635 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-13 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
636 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | PCB_100 Type | 1 | IC2_Inv2
637 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | PCB_100 Type | 1 | IC2_Inv2
638 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | PCB_100 Type | 1 | IC2_Inv2
639 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | PCB_100 Type | 1 | IC2_Inv2
640 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC2_Inv2
641 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
642 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
643 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC2_Inv2
644 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
645 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
646 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC2_Inv2
647 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
648 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC2_Inv2
649 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
650 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
651 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
652 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
653 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-15 | PCB_100 Type | 1 | IC2_Inv2
654 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-15 | PCB_100 Type | 1 | IC2_Inv2
655 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-15 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC2_Inv2
656 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-15 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
657 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-15 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
658 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-15 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC2_Inv2
659 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-15 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
660 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-17 | 1 No Actuator Carbon Brush Replaced | 1 | IC1_Inv2
661 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-17 | PCB_100 Type | 1 | IC1_Inv1
662 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-18 | 1 No Limit Switch was replaced | 1 | IC2_Inv2
663 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-19 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
664 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-19 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
665 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-19 | 1 No Actuator Motor Replaced | 1 | IC2_Inv1
666 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-19 | Positive Y-Connector Replaced | 1 | IC1_Inv4
667 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-19 | Positive Y-Connector Replaced | 1 | IC1_Inv4
668 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-19 | Positive Y-Connector Replaced | 1 | IC1_Inv4
669 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-19 | MC4 Connector Replaced | 1 | IC1_Inv4
670 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-22 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
671 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-23 | 1 No Actuator Carbon Brush Replaced | 1 | IC1_Inv3
672 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-23 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC2_Inv2
673 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-24 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
674 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-24 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv2
675 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-25 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
676 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-25 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
677 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-26 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC2_Inv2
678 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-26 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
679 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-26 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
680 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-26 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
681 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-26 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv1
682 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
683 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
684 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
685 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
686 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
687 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
688 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
689 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
690 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
691 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
692 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 No Actuator Carbon Brush Replaced | 1 | IC2_Inv1
693 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv1
694 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv2
695 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv2
696 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv2
697 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv2
698 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv2
699 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv2
700 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv2
701 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv3
702 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv1
703 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
704 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
705 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv3
706 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv3
707 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
708 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv1
709 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv1
710 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv1
711 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv1
712 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv2
713 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv2
714 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv2
715 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv2
716 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv2
717 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
718 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv2
719 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv2
720 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
721 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv2
722 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
723 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv2
724 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
725 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv2
726 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
727 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv2
728 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv2
729 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv2
730 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | PCB_100 Type | 1 | IC1_Inv4
731 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No Actuator Carbon Brush Replaced | 1 | IC1_Inv2
732 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv2
733 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
734 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv2
735 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv2
736 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv3
737 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
738 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv3
739 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv3
740 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv3
741 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
742 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | PCB_200 Type | 1 | IC1_Inv3
743 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | New Actuator HB-DJ828 Installed | 1 | IC1_Inv2
744 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | New Actuator HB-DJ828 Installed | 1 | IC1_Inv3
745 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | New Actuator HB-DJ828 Installed | 1 | IC1_Inv3
746 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
747 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
748 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC2_Inv2
749 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv4
750 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv4
751 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | New Actuator HB-DJ828 Installed | 1 | IC2_Inv1
752 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | New Actuator HB-DJ828 Installed | 1 | IC1_Inv4
753 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | New Actuator HB-DJ828 Installed | 1 | IC2_Inv1
754 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | New Actuator HB-DJ828 Installed | 1 | IC2_Inv1
755 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | New Actuator HB-DJ828 Installed | 1 | IC2_Inv1
756 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | Charge control unit replaced | 1 | IC2_Inv1
757 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
758 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
759 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
760 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
761 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | 1 No Actuator Big Gear Replaced | 1 | IC2_Inv1
762 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
763 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | Charge control unit replaced | 1 | IC1_Inv3
764 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | New Actuator HB-DJ828 Installed | 1 | IC1_Inv2
765 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | Actuator 1 No Diode was replaced | 1 | IC2_Inv2
766 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | 1 No Actuator Big Gear Replaced | 1 | IC2_Inv2
767 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
768 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | Positive Y-Connector Replaced | 1 | IC1_Inv4
769 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | Positive Y-Connector Replaced | 1 | IC1_Inv2
770 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | Positive Y-Connector Replaced | 1 | IC1_Inv1_SCB2_String 1
771 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB5_String 11
772 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB9_String 9
773 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv1
774 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
775 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | Actuator motor 2 no.s Carbon brushes replaced | 2 | IC2_Inv2
776 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | Actuator Motor 1 no Circlip replaced | 1 | IC2_Inv2
777 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | Actuator 2 No.s Bearings replaced | 2 | IC2_Inv2
778 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | 1 No Limit Switch replaced | 1 | IC2_Inv2
779 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv3
780 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv4
781 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
782 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
783 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | PCB_100 Type | 1 | IC1_Inv4
784 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-07 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv2
785 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-07 | Charge control unit replaced | 1 | IC2_Inv1
786 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-07 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB1_String 8
787 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-08 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
788 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-08 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv3
789 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-08 | Positive Y-Connector Replaced | 1 | IC2_Inv1
790 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | Actuator 1 No Diode was replaced | 1 | IC2_Inv1
791 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
792 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
793 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv2
794 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC2_Inv1
795 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv3
796 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv2
797 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv2
798 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-11 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
799 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-12 | PCB_100 Type | 1 | IC1_Inv1
800 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-12 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
801 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-13 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
802 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-13 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv1
803 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-14 | Actuator 2 No.s Bearings replaced | 2 | IC1_Inv1
804 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-14 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
805 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-14 | MC4 Connector(Male & Female) | 1 | IC2_Inv2_SCB9_String 10
806 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-15 | 1 No Limit Switch replaced | 1 | IC1_Inv2
807 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-15 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
808 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-15 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB4_String 1
809 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv3
810 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
811 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv3
812 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
813 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB3_String 10
814 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | Actuator 2 No.s Bearings replaced | 2 | IC1_Inv4
815 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv4
816 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | Actuator motor 2 no.s Carbon brushes replaced | 2 | IC1_Inv1
817 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | Actuator Motor 1 no Circlip replaced | 1 | IC1_Inv1
818 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv3
819 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
820 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
821 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv4
822 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-19 | MC4 Connector Replaced | 1 | IC2_Inv2_SCB9_String 10
823 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-19 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB4_String 12
824 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-20 | Negative Y-Connector Replaced | 1 | IC2_Inv1_SCB5_String 3
825 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-20 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB3_String 14
826 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-21 | Actuator motor 1 no.s Carbon brushes replaced | 1 | IC2_Inv1
827 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-21 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
828 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-21 | Actuator 2 No.s Bearings replaced | 2 | IC1_Inv2
829 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-22 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
830 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-22 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv4
831 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB4_String 13
832 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | Negative Y-Connector Replaced | 1 | IC1_Inv4_SCB4_String 13
833 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | Negative Y-Connector Replaced | 1 | IC1_Inv4_SCB4_String 10
834 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
835 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-24 | MC4 Connector Replaced | 1 | IC1_Inv4_SCB4_String 13
836 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-25 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB9_String 10
837 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-25 | Actuator 1 No Diode was replaced | 1 | IC1_Inv4
838 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-26 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
839 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-26 | Negative Y-Connector Replaced | 1 | IC2_Inv1_SCB5_String 2
840 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-27 | Actuator motor 2 no.s Carbon brushes replaced | 2 | IC2_Inv1
841 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-27 | Actuator Motor 1 no Circlip replaced | 1 | IC2_Inv1
842 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-28 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
843 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-28 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
844 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-28 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
845 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-29 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
846 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-29 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv3
847 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-29 | New Actuator HB-DJ8289824-700 Installed | 1 | IC1_Inv1
848 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | PCB_100 Type | 1 | IC2_Inv1
849 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
850 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
851 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | Actuator 1 No Diode was replaced | 1 | IC1_Inv2
852 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-31 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
853 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-01 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
854 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-01 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
855 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-03 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
856 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-05 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
857 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-05 | PCB_100 Type | 1 | IC1_Inv1
858 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-06 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
859 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-06 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
860 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-07 | MC4 Connector Replaced | 1 | IC2_Inv2_SCB1_String 13
861 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-07 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB3_String 7
862 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-07 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
863 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-07 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
864 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-08 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB5_String 5
865 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-09 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
866 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-09 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
867 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-09 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
868 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-10 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
869 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-10 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv2
870 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-11 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
871 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-11 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv2
872 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-12 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
873 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-13 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
874 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-14 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
875 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-14 | Actuator 1 No Diode was replaced | 1 | IC1_Inv3
876 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-15 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
877 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-15 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
878 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-15 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
879 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-16 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv2
880 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-17 | Negative Y-Connector Replaced | 1 | IC2_Inv2_SCB1_String 13
881 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-18 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
882 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-18 | Negative Y-Connector Replaced | 1 | IC2_Inv2_SCB1_String 5
883 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-19 | Negative Y-Connector Replaced | 1 | IC1_Inv3_SCB7_String 5
884 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-20 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
885 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-20 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB8_String 11
886 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-20 | Negative Y-Connector Replaced | 1 | IC2_Inv1_SCB1_String 5
887 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-21 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv4
888 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-21 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
889 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-22 | Positive Y-Connector Replaced | 1 | IC2_Inv1_SCB2_String 7
890 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-22 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
891 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-23 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
892 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-24 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
893 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-26 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
894 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-27 | Positive Y-Connector Replaced | 1 | IC1_Inv1_SCB4_String 5
895 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-27 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
896 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-28 | MC4 Connector Replaced | 1 | IC1_Inv4_SCB8_String 7
897 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-28 | Negative Y-Connector Replaced | 1 | IC1_Inv1_SCB8_String 6
898 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-29 | Actuator 2 No.s Diode was replaced | 2 | IC1_Inv2
899 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-04 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
900 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-04 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
901 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-04 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
902 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-05 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv4
903 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-06 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB10_String 4
904 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-06 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
905 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-08 | Negative Y-Connector Replaced | 1 | IC1_Inv4_SCB1_String 9
906 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-08 | Negative Y-Connector Replaced | 1 | IC1_Inv4_SCB4_String 1
907 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-09 | MC4 Connector Replaced | 1 | IC1_Inv1_SCB3_String 12
908 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-10 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
909 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-10 | MC4 Connector Replaced | 1 | IC2_Inv2_SCB1_String 13
910 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-11 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
911 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-11 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
912 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-11 | MC4 Connector Replaced | 1 | IC2_Inv1_SCB8_String 9
913 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-12 | MC4 Connector Replaced | 1 | IC1_Inv1_SCB1_String 1
914 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-12 | Negative Y-Connector Replaced | 1 | IC1_Inv1_SCB1_String 3
915 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-14 | MC4 Connector Replaced | 2 | IC1_Inv2_SCB10_String 5
916 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB5_String 8
917 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | MC4 Connector Replaced | 1 | IC1_Inv1_SCB3_String 13
918 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
919 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
920 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-16 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
921 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-16 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
922 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-18 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv4
923 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-18 | Negative Y-Connector Replaced | 1 | IC1_Inv2_SCB8_String 8
924 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-19 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
925 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-20 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
926 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-20 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv4
927 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-21 | MC4 Connector Replaced | 1 | IC1_Inv3_SCB10_String 5
928 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB7_String 5
929 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | Positive Y-Connector Replaced | 1 | IC2_Inv1_SCB4_String 4
930 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
931 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
932 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-23 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv4
933 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-23 | PCB_100 Type | 1 | IC1_Inv4
934 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-26 | Charge control unit replaced | 1 | IC1_Inv4
935 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-27 | MC4 Connector Replaced | 1 | IC1_Inv4_SCB6_String 9
936 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-27 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
937 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-27 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
938 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-28 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB6_String 1
939 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-28 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
940 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-29 | MC4 Connector Replaced | 1 | IC2_Inv2_SCB5_String 5
941 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-29 | Charge control unit replaced | 1 | IC1_Inv4
942 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-30 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
943 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-30 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
944 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-31 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
945 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-31 | PCB_200 Type | 1 | IC2_Inv1
946 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-01 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
947 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-01 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
948 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-02 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB6_String 5
949 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-02 | Positive Y-Connector Replaced | 1 | IC2_Inv1_SCB6_String 7
950 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-03 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
951 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-04 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
952 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-05 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv4
953 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-06 | Actuator motor 2 no.s Carbon brushes | 1 | IC2_Inv1
954 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-06 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
955 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-06 | Replaced old PV 325 Watts module(1 No)104111000743 | 1 | IC1_Inv1
956 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-08 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
957 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-09 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
958 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-10 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
959 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-10 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
960 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | 1 No Actuator Medium Gear Replaced | 1 | IC2_Inv1
961 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
962 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
963 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | Actuator motor Bearing | 1 | IC2_Inv1
964 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | Actuator motor Bearing | 1 | IC1_Inv2
965 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-13 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB10_String 11
966 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-14 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
967 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-14 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
968 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-14 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
969 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-16 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
970 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-16 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
971 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-17 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
972 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-17 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
973 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-19 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv4
974 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-20 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
975 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-20 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv4
976 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-24 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
977 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-25 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB3_String 9
978 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-25 | MC4 Connector Replaced | 1 | IC1_Inv4_SCB6_String 12
979 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-26 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
980 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-26 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
981 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-26 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv1
982 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-27 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
983 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-27 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
984 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-28 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB7_String 14
985 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-29 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
986 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-29 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv2
987 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-30 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
988 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-31 | Positive Y-Connector Replaced | 1 | IC2_Inv2_SCB2_String 13
989 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-31 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB1_String 7
990 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-31 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB5_String 14
991 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-31 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
992 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-01 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
993 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-01 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
994 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-02 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
995 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-03 | Positive Y-Connector Replaced | 1 | IC1_Inv4
996 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-03 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
997 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-05 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv1
998 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-05 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv1
999 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-06 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
1000 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-06 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1001 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-08 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
1002 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-09 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
1003 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-09 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1004 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1005 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | Positive Y-Connector Replaced | 1 | IC2_Inv2
1006 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | Positive Y-Connector Replaced | 1 | IC2_Inv2
1007 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | Positive Y-Connector Replaced | 1 | IC1_Inv4
1008 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | Positive Y-Connector Replaced | 1 | IC1_Inv4
1009 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-12 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
1010 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-12 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1011 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-12 | Positive Y-Connector Replaced | 1 | IC1_Inv4
1012 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | PCB_100 Type | 1 | IC1_Inv2
1013 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | PCB_100 Type | 1 | IC1_Inv4
1014 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | PCB_100 Type | 1 | IC1_Inv3
1015 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | PCB_100 Type | 1 | IC2_Inv2
1016 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | PCB_100 Type | 1 | IC2_Inv2
1017 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | PCB_100 Type | 1 | IC2_Inv2
1018 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | IC1_Inv4_SCB3_String 3 | 1 | IC1_Inv1_SCB1_String 12
1019 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-14 | 1 No Actuator Medium Gear Replaced | 1 | IC2_Inv1
1020 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-16 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1021 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-16 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
1022 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-17 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1023 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-17 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
1024 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-19 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
1025 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-19 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
1026 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-19 | IC1_Inv4_SCB3_String 3 | 1 | IC1_Inv4_SCB3_String 3
1027 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-20 | IC1_Inv4_SCB10_String 5 | 1 | IC1_Inv4_SCB10_String 5
1028 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-21 | Positive Y-Connector Replaced | 1 | IC2_Inv2_SCB3_String 7
1029 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-21 | MC4 Connector Replaced | 1 | IC1_Inv2_SCB10_String 1
1030 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-22 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
1031 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-22 | Charge control unit replaced | 1 | IC1_Inv2
1032 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-23 | Positive Y-Connector Replaced | 1 | IC2_Inv1_SCB2_String 1
1033 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB1_String 3
1034 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB10_String 11
1035 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB10_String 04
1036 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB6_String 05
1037 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB5_String 5
1038 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB5_String 9
1039 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB7_String 5
1040 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | PCB_100 Type | 1 | PCB_100 Type
1041 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1042 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1043 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-28 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1044 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-01 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB10_String 1
1045 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-01 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB6_String 6
1046 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-01 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB9_String 10
1047 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-02 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB7_String 3
1048 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB6_String 10
1049 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB6_String 11
1050 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB2_String 8
1051 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB2_String 11
1052 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-08 | Positive Y-Connector Replaced | 1 | IC2_Inv5_SCB2_String 7
1053 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-11 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
1054 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-11 | 1 No Actuator Medium Gear Replaced | 1 | IC2_Inv2
1055 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-11 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
1056 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1057 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | 2 Nos Actuator Bearing Replaced | 1 | IC1_Inv3
1058 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB5_String 5
1059 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB5_String 8
1060 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB4_String 11
1061 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB9_String 5
1062 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-13 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB4_String 10
1063 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-13 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB6_String 11
1064 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-13 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB1_String 3
1065 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-15 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
1066 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-16 | 1 Nos Actuator Bearing Replaced | 1 | IC2_Inv2
1067 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-17 | Actuator motor 1 no.s Carbon brushes | 1 | IC2_Inv2
1068 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-18 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB3_String 13
1069 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-18 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB3_String 10
1070 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-20 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1071 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-20 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
1072 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-20 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv3
1073 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-24 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1074 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-24 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
1075 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-25 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1076 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-25 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1077 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-25 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1078 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-26 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB1_String 3
1079 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-26 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB9_String 12
1080 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-26 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB9_String 5
1081 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-26 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB6_String 5
1082 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-27 | PCB_200 Type | 1 | IC1_Inv2
1083 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-28 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB10_String 6
1084 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-28 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB10_String 8
1085 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-28 | PCB_100 Type | 1 | IC2_Inv1
1086 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-29 | PCB_200 Type | 1 | IC2_Inv2
1087 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-29 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
1088 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-01 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
1089 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-04 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
1090 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-05 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
1091 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-05 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1092 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-06 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1093 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-07 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1094 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-10 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1095 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-10 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1096 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-12 | Actuator motor 2 no.s Carbon brush | 2 | IC2_Inv2
1097 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-19 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB1_String 10
1098 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-20 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC2_Inv1
1099 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-21 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1100 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-21 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1101 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-22 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1102 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-22 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1103 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-22 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1104 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-24 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1105 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-24 | Positive Y-Connector Replaced | 1 | IC2_Inv1
1106 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-25 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
1107 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-26 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1108 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-26 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1109 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-26 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1110 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-02 | 1 No Actuator Big Gear Replaced | 1 | IC2_Inv1
1111 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-03 | Replaced old PV 325 Watts module(1 No)104249300393 | 1 | IC1_Inv4_SCB1_String 6
1112 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-03 | Replaced old PV 325 Watts module(1 No)104249300498 | 1 | IC1_Inv4_SCB1_String 6
1113 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-06 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
1114 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-07 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB2_String 11
1115 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-07 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB1_String 9
1116 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | 2 Nos Actuator Bearing Replaced | 1 | IC1_Inv2
1117 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104107202941 | 1 | IC1_Inv1_SCB1_String 2
1118 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104107204308 | 1 | IC1_Inv1_SCB2_String 2
1119 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104107204320 | 1 | IC1_Inv1_SCB6_String 3
1120 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104107204305 | 1 | IC1_Inv2_SCB1_String 2
1121 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)1041929035529 | 1 | IC1_Inv3_SCB3_String 5
1122 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000393 | 1 | IC1_Inv3_SCB3_String 15
1123 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000798 | 1 | IC2_Inv5_SCB8_String 11
1124 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000519 | 1 | IC1_Inv1_SCB1_String 13
1125 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000110 | 1 | IC1_Inv1_SCB5_String 13
1126 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000610 | 1 | IC1_Inv1_SCB7_String 11
1127 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000002 | 1 | IC1_Inv1_SCB8_String 13
1128 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104110401582 | 1 | IC1_Inv1_SCB8_String 13
1129 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000003 | 1 | IC1_Inv2_SCB2_String 11
1130 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000807 | 1 | IC1_Inv3_SCB3_String 13
1131 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104110101089 | 1 | IC2_Inv6_SCB6_String 1
1132 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000441 | 1 | IC2_Inv6_SCB8_String 1
1133 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000714 | 1 | IC2_Inv6_SCB8_String 2
1134 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000571 | 1 | IC1_Inv1_SCB9_String 12
1135 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000674 | 1 | IC1_Inv3_SCB8_String 11
1136 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000722 | 1 | IC1_Inv4_SCB9_String 1
1137 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv3
1138 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204503 | 1 | IC1_Inv3_SCB4_String 3
1139 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204719 | 1 | IC1_Inv3_SCB6_String 10
1140 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204634 | 1 | IC1_Inv3_SCB7_String 11
1141 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204717 | 1 | IC1_Inv3_SCB7_String 12
1142 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204716 | 1 | IC1_Inv3_SCB7_String 14
1143 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204718 | 1 | IC1_Inv4_SCB2_String 11
1144 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204651 | 1 | IC1_Inv4_SCB6_String 1
1145 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204586 | 1 | IC1_Inv4_SCB6_String 2
1146 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104110101114 | 1 | IC1_Inv4_SCB8_String 7
1147 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104110101200 | 1 | IC1_Inv4_SCB8_String 8
1148 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101712 | 1 | IC2_Inv5_SCB9_String 2
1149 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101708 | 1 | IC2_Inv5_SCB9_String 2
1150 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104111500999 | 1 | IC2_Inv5_SCB9_String 2
1151 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104111000432 | 1 | IC2_Inv5_SCB9_String 12
1152 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101709 | 1 | IC2_Inv5_SCB4_String 9
1153 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101737 | 1 | IC2_Inv5_SCB4_String 11
1154 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101621 | 1 | IC2_Inv5_SCB3_String 8
1155 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104111000309 | 1 | IC1_Inv2_SCB8_String 7
1156 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104111000433 | 1 | IC2_Inv6_SCB2_String 14
1157 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101108 | 1 | IC2_Inv6_SCB1_String 12
1158 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101135 | 1 | IC2_Inv6_SCB1_String 10
1159 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101445 | 1 | IC1_Inv1_SCB2_String 2
1160 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101774 | 1 | IC1_Inv3_SCB1_String 3
1161 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101475 | 1 | IC2_Inv5_SCB7_String 7
1162 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101623 | 1 | IC1_Inv1_SCB8_String 14
1163 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101729 | 1 | IC1_Inv2_SCB1_String 10
1164 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101736 | 1 | IC1_Inv2_SCB7_String 3
1165 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101691 | 1 | IC1_Inv2_SCB6_String 5
1166 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-11 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB3_String 8
1167 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-13 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
1168 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-13 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1169 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-14 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv2
1170 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-15 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1171 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-19 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
1172 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-20 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1173 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-21 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
1174 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-22 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
1175 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-22 | Iron Nut Replaced | 1 | IC1_Inv4
1176 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-22 | Vthread Rod Replaced | 1 | IC1_Inv4
1177 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-23 | Actuator Big Gear Replaced | 1 | IC1_Inv3
1178 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-24 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
1179 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-26 | Actuator motor 2 no.s Carbon brush | 2 | IC1_Inv1
1180 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-26 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1181 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-30 | Positive Y Connector Failure | 1 | IC1_Inv1_SCB4_String 7
1182 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-30 | Positive Y Connector Failure | 1 | IC1_Inv1_SCB2_String 1
1183 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-31 | Actuator motor 2 no.s Carbon brush | 2 | IC1_Inv4
1184 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-31 | PCB_100 Type | 1 | IC1_Inv4
1185 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-31 | PCB_100 Type | 1 | IC1_Inv2
1186 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-31 | PCB_100 Type | 1 | IC1_Inv2
1187 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-03 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1188 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-04 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv4
1189 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-05 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv4
1190 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-05 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv1
1191 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-05 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1192 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-05 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
1193 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-06 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv4
1194 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-07 | PCB_100 Type | 1 | IC1_Inv3
1195 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-07 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1196 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-07 | Actuator motor 2 no.s Carbon brush | 2 | IC1_Inv3
1197 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-08 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1198 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-08 | Actuator Big Gear Replaced | 1 | IC2_Inv1
1199 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-08 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1200 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-10 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
1201 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-10 | Iron Nut Replaced | 1 | IC2_Inv2
1202 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-10 | Vthread Rod Replaced | 1 | IC1_Inv4
1203 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-11 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1204 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-11 | 1 No Actuator Motor | 1 | IC1_Inv4
1205 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-13 | 1 No Actuator Motor | 1 | IC2_Inv1
1206 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-13 | Memory Unit Replaced | 1 | IC2_Inv1
1207 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-17 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1208 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-18 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
1209 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-18 | 1 No Actuator Motor | 1 | IC1_Inv2
1210 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-19 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1211 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-22 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv4
1212 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-22 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv4
1213 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-23 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
1214 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-25 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
1215 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-28 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1216 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-28 | Iron Nut Replaced | 1 | IC1_Inv1
1217 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-28 | Vthread Rod Replaced | 1 | IC1_Inv1
1218 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-28 | 2 No Battaries Replaced | 2 | IC1_Inv2
1219 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-28 | 2 No Battaries Replaced | 2 | IC1_Inv1
1220 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-28 | 2 No Battaries Replaced | 2 | IC1_Inv1
1221 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-29 | 2 No Battaries Replaced | 2 | IC2_Inv1
1222 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | 2 No Battaries Replaced | 2 | IC1_Inv4
1223 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | 2 No Battaries Replaced | 2 | IC1_Inv1
1224 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | 2 No Battaries Replaced | 2 | IC1_Inv1
1225 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | PCB_100 Type | 1 | IC1_Inv4
1226 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | PCB_100 Type | 1 | IC1_Inv1
1227 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | PCB_100 Type | 1 | IC1_Inv3
1228 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | Iron Nut & Vthread Rod Replaced | 1 | IC1_Inv3
1229 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
1230 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | Actuator Big Gear Replaced | 1 | IC1_Inv3
1231 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-02 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv3
1232 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-02 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1233 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-03 | 2 No Battaries Replaced | 2 | IC2_Inv1
1234 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-03 | 2 No Battaries Replaced | 2 | IC2_Inv1
1235 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-03 | PCB_100 Type | 1 | IC2_Inv1
1236 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-04 | 1 No Actuator Motor | 1 | IC2_Inv1
1237 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-07 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
1238 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-07 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
1239 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-07 | 2 No Battaries Replaced | 2 | IC1_Inv2
1240 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-09 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv4
1241 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-09 | 1 No Battaries Replaced | 1 | IC1_Inv1
1242 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-10 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
1243 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-10 | 1 No Actuator Motor | 1 | IC2_Inv1
1244 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-10 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1245 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-12 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
1246 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-12 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
1247 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-13 | 2 Nos Actuator Bearing Replaced | 1 | IC2_Inv2
1248 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-14 | 1 No Medium Gear Replaced | 1 | IC1_Inv3
1249 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-14 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
1250 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-16 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1251 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-16 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1252 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-16 | 1 No Medium Gear Replaced | 1 | IC1_Inv1
1253 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-21 | 1 No Actuator Motor | 1 | IC2_Inv1
1254 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-22 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1255 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-22 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1256 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-23 | 2 No Battaries Replaced | 2 | IC2_Inv1
1257 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-24 | Iron Nut & Vthread Rod Replaced | 1 | IC1_Inv2
1258 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-25 | 2 No Battaries Replaced | 2 | IC1_Inv4
1259 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-25 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv4
1260 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-25 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv4
1261 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-26 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv4
1262 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-26 | 1 No Actuator Motor | 1 | IC1_Inv3
1263 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-26 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1264 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-26 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
1265 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-27 | Iron Nut & Vthread Rod Replaced | 1 | IC2_Inv1
1266 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-27 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1267 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-29 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1268 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-30 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1269 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-30 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1270 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-30 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1271 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-01 | Iron Nut & Vthread Rod Replaced | 1 | IC1_Inv1
1272 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-01 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1273 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-02 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv2
1274 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-02 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1275 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-03 | 1 No Actuator Motor | 1 | IC1_Inv2
1276 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-04 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1277 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-07 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
1278 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-07 | 1 No Actuator Motor | 1 | IC2_Inv1
1279 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-07 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1280 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-09 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1281 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-09 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1282 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-12 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1283 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-12 | Iron Nut Replaced | 1 | IC1_Inv3
1284 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-12 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1285 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-13 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1286 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-13 | 1 No Medium Gear Replaced | 1 | IC1_Inv2
1287 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-14 | Iron Nut Replaced | 1 | IC2_Inv1
1288 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-16 | 1 No Actuator Motor | 1 | IC1_Inv2
1289 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-17 | Iron Nut Replaced | 1 | IC1_Inv3
1290 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-18 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1291 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-19 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1292 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-19 | Iron Nut Replaced | 1 | IC1_Inv2
1293 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-19 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
1294 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-22 | Iron Nut Replaced | 1 | IC1_Inv2
1295 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-23 | 1 No Actuator Motor | 1 | IC2_Inv1
1296 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-24 | 1 No Medium Gear Replaced | 1 | IC1_Inv2
1297 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-24 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
1298 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-25 | Iron Nut Replaced | 1 | IC2_Inv2
1299 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-25 | 1 No Actuator Motor | 1 | IC1_Inv2
1300 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-28 | PCB_200 Type | 1 | IC2_Inv1
1301 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-03 | 1 No Actuator Motor | 1 | IC1_Inv2
1302 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-03 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv2
1303 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-03 | 1 No Actuator Motor | 1 | IC1_Inv3
1304 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-03 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1305 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-04 | 1 No Actuator Motor | 1 | IC1_Inv2
1306 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-05 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1307 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-05 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
1308 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-05 | Charge control unit replaced | 1 | IC1_Inv2
1309 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-06 | Iron Nut Replaced | 1 | IC2_Inv1
1310 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-08 | PCB_200 Type | 1 | IC2_Inv2
1311 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-09 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1312 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-11 | Iron Nut Replaced | 1 | IC1_Inv4
1313 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-11 | 1 No Actuator Motor | 1 | IC1_Inv4
1314 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-12 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1315 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-14 | PCB_200 Type | 1 | IC2_Inv2
1316 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-16 | PCB_200 Type | 1 | IC1_Inv2
1317 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-16 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv2
1318 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-18 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1319 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-19 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1320 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-20 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1321 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-20 | PCB_200 Type | 1 | IC2_Inv2
1322 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-20 | PCB_200 Type | 1 | IC2_Inv1
1323 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-22 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1324 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-24 | 2 Nos Actuator Bearing Replaced | 1 | IC1_Inv4
1325 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-25 | 1 No Actuator Motor | 1 | IC2_Inv1
1326 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-26 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1327 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-27 | Iron Nut Replaced | 1 | IC2_Inv1
1328 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-29 | 1 No Big Gear Replaced | 1 | IC1_Inv3
1329 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-30 | Negative Y connector Replaced | 1 | IC1_Inv3_SCB9_String 7
1330 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-30 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB7_String 13
1331 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-03 | Iron Nut Replaced | 1 | IC1_Inv2
1332 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-03 | 2 Nos Actuator Bearing Replaced | 1 | IC1_Inv3
1333 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-03 | PCB_200 Type | 1 | IC1_Inv2
1334 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-04 | Actuator motor 2 no.s Carbon brushes | 1 | IC1_Inv3
1335 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-05 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1336 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-05 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
1337 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-07 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1338 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-07 | 1 No Actuator Motor | 1 | IC1_Inv2
1339 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-09 | 1 No Big Gear Replaced | 1 | IC2_Inv2
1340 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-10 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1341 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-12 | MC4 Connector Replaced | 1 | IC1_Inv4_SCB8_String 5
1342 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-16 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1343 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-16 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1344 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-18 | 1 No Big Gear Replaced | 1 | IC2_Inv2
1345 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-20 | 1 No Actuator Motor | 1 | IC2_Inv1
1346 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1347 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1348 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1349 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1350 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1351 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
1352 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
1353 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-25 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
1354 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-25 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
1355 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-25 | 1 No Big Gear Replaced | 1 | IC1_Inv4
1356 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-26 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1357 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-26 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1358 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-29 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1359 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-29 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1360 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-29 | 2 NO Diode Replaced | 2 | IC1_Inv1
1361 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-30 | Iron Rod Replaced | 1 | IC2_Inv1
1362 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-30 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1363 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-31 | 1 No Actuator Motor | 1 | IC1_Inv1
1364 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-31 | 1 No Actuator Motor | 1 | IC1_Inv1
1365 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-31 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1366 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-01 | 1 No Actuator Motor | 1 | IC1_Inv1
1367 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-02 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
1368 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-02 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1369 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-02 | 1 No Actuator Motor | 1 | IC1_Inv1
1370 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-03 | Iron Rod Replaced | 1 | IC2_Inv2
1371 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-04 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1372 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-04 | 1 No Actuator Motor | 1 | IC2_Inv1
1373 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-05 | Iron Nut Replaced | 1 | IC1_Inv1
1374 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-05 | Positive Y-Connector Replaced | 1 | IC1_Inv1_SCB8_String 3
1375 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-05 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB6_String 8
1376 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-06 | 1 No Actuator Motor | 1 | IC2_Inv2
1377 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-07 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
1378 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-08 | Actuator 2 No Limit Switch was replaced | 1 | IC1_Inv1
1379 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-08 | V thread Rod | 1 | IC1_Inv2
1380 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-10 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv2
1381 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-10 | 1 No Actuator Motor | 1 | IC2_Inv2
1382 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-12 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
1383 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-13 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1384 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-18 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv4
1385 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-18 | 1 No Actuator Motor | 1 | IC1_Inv2
1386 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-18 | Iron Rod Replaced | 1 | IC1_Inv1
1387 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-22 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1388 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-27 | Iron Nut Replaced | 1 | IC2_Inv2
1389 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-01 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1390 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-04 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1391 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-04 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
1392 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-05 | 1 No Actuator Motor | 1 | IC1_Inv2
1393 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-05 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1394 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-05 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1395 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-06 | Iron Rod Replaced | 1 | IC1_Inv4
1396 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-06 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
1397 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-07 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
1398 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-10 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1399 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-10 | 1 No Actuator Motor | 1 | IC1_Inv3
1400 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-13 | Iron Nut Replaced | 1 | IC1_Inv2
1401 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-13 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1402 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-15 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1403 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-16 | 1 No Actuator Motor | 1 | IC2_Inv2
1404 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-16 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
1405 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-17 | Iron Nut Replaced | 1 | IC1_Inv3
1406 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-18 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv2
1407 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-18 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv3
1408 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-20 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1409 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-21 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
1410 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-22 | Iron Nut Replaced | 1 | IC1_Inv4
1411 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-22 | 1 No Medium Gear Replaced | 1 | IC1_Inv4
1412 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-26 | 1 No Actuator Bearing Replaced | 1 | IC1_Inv1
1413 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-26 | 1 No Big Gear Replaced | 1 | IC2_Inv2
1414 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-28 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1415 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-28 | Iron nut Replaced | 1 | IC1_Inv1
1416 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-28 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1417 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-30 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1418 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-05 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1419 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-06 | PCB_100 Type | 1 | IC2_Inv1
1420 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-06 | PCB_100 Type | 1 | IC1_Inv2
1421 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-06 | PCB_100 Type | 1 | IC1_Inv3
1422 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-07 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1423 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1424 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | PCB_100 Type | 1 | IC1_Inv4
1425 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | CCU Replaced | 1 | IC1_Inv3
1426 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | CCU Replaced | 1 | IC1_Inv4
1427 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | Add 2 Tilt Sensor Replaced | 1 | IC1_Inv4
1428 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-09 | PCB_100 Type | 1 | IC1_Inv3
1429 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-09 | CCU Replaced | 1 | IC1_Inv3
1430 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-10 | Add 1 Tilt Sensor Replaced | 1 | IC2_Inv2
1431 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-10 | Add 1 Tilt Sensor Replaced | 1 | IC1_Inv3
1432 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-11 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1433 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-12 | 1 No Actuator Motor | 1 | IC1_Inv4
1434 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-12 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv2
1435 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-14 | 1 No Big Gear Replaced | 1 | IC1_Inv3
1436 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-15 | Add 1 Tilt Sensor Replaced | 1 | IC1_Inv3
1437 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-16 | Add 1 Tilt Sensor Replaced | 1 | IC1_Inv4
1438 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-16 | Add 4 Tilt Sensor Replaced | 1 | IC1_Inv4
1439 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-18 | 1 No Actuator Bearing Replaced | 1 | IC1_Inv3
1440 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-19 | Add 5 Tilt Sensor Replaced | 1 | IC2_Inv2
1441 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-21 | Actuator 2 No Limit Switch was replaced | 1 | IC1_Inv1
1442 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-21 | 1 No Medium Gear Replaced | 1 | IC1_Inv3
1443 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-23 | 1 No Actuator Motor | 1 | IC1_Inv1
1444 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-23 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1445 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-24 | 1 No Medium Gear Replaced | 1 | IC1_Inv2
1446 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-24 | 1 No Big Gear Replaced | 1 | IC1_Inv2
1447 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1448 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | Iron nut Replaced | 1 | IC1_Inv3
1449 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | PCB_100 Type | 1 | IC1_Inv4
1450 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | PCB_100 Type | 1 | IC1_Inv3
1451 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-26 | Iron nut Replaced | 1 | IC1_Inv3
1452 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
1453 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | 1 No Actuator Motor | 1 | IC1_Inv4
1454 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv4
1455 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | 1 No Big Gear Replaced | 1 | IC1_Inv4
1456 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-29 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1457 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-29 | 1 No Actuator Motor | 1 | IC1_Inv3
1458 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-30 | PCB_100 Type | 1 | IC1_Inv2
1459 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-03 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv2
1460 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-06 | PCB_100 Type | 1 | IC1_Inv3
1461 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-11 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1462 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-12 | 1 No Big Gear Replaced | 1 | IC2_Inv2
1463 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-13 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
1464 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-13 | 1 No Big Gear Replaced | 1 | IC1_Inv2
1465 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-14 | Iron nut Replaced | 1 | IC1_Inv2
1466 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-14 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1467 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-15 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1468 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-18 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1469 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-18 | Iron nut Replaced | 1 | IC2_Inv2
1470 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-18 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1471 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-18 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1472 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-19 | 1 No Big Gear Replaced | 1 | IC2_Inv2
1473 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-21 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
1474 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-22 | Actuator Limit Board Replaced | 1 | IC2_Inv1
1475 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-22 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
1476 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-25 | 1 No Actuator Motor Replaced | 2 | IC2_Inv1
1477 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-25 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1478 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-26 | 1 No Actuator Motor Replaced | 1 | IC1_Inv2
1479 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-26 | 1 No Big Gear Replaced | 1 | IC1_Inv3
1480 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-03 | 1 No Actuator Motor Replaced | 1 | IC1_Inv3
1481 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-04 | 1 No Actuator Motor Replaced | 1 | IC1_Inv3
1482 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-07 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1483 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-07 | Iron Nut Replaced | 1 | IC2_Inv1
1484 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-08 | 1 No Big Gear Replaced | 1 | IC2_Inv1
1485 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-08 | 1 No Actuator Motor Replaced | 1 | IC1_Inv3
1486 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-10 | Iron Nut Replaced | 1 | IC1_Inv3
1487 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-11 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1488 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-11 | 1 No Actuator Motor Replaced | 1 | IC1_Inv4
1489 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-15 | Iron nut Replaced | 1 | IC1_Inv1
1490 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-15 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1491 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-17 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1492 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-17 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1493 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-19 | EMC Filter | 1 | IC1_Inv1
1494 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-19 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
1495 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-20 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1496 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-20 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1497 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1498 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1499 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 1 No Actuator Motor | 1 | IC2_Inv1
1500 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1501 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | Iron Nut Replaced | 1 | IC2_Inv1
1502 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 1 No Big Gear Replaced | 1 | IC2_Inv1
1503 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-22 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1504 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-22 | 1 No Actuator Motor Replaced | 1 | IC2_Inv2
1505 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-26 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1506 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-26 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1507 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-27 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1508 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-27 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1509 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-27 | 1 No Big Gear Replaced | 1 | IC2_Inv1
1510 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv4
1511 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 1 No Medium Gear Replaced | 1 | IC1_Inv3
1512 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 1 No Actuator Motor | 1 | IC1_Inv2
1513 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1514 | FY2025-26 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1515 | FY2025-26 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 1 No Actuator Motor | 1 | IC1_Inv1
1516 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1517 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1518 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 1 No Big Gear Replaced | 1 | IC1_Inv1
1519 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
1520 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 1 No Big Gear Replaced | 1 | IC2_Inv1
1521 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv4
1522 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 1 No Actuator Motor | 1 | IC1_Inv4
1523 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 1 No Actuator Motor | 1 | IC2_Inv1
1524 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1525 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1526 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 2000A Replaced | 1 | IC1_Inv4
1527 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | LCL Filter Replaced | 1 | IC1_Inv4
1528 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC1_Inv3
1529 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC2_Inv2
1530 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC2_Inv2
1531 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC2_Inv2
1532 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC2_Inv2
1533 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC2_Inv2
1534 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC1_Inv4
1535 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC1_Inv1
1536 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC1_Inv4
1537 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 1 No Big Gear Replaced | 1 | IC1_Inv4
1538 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1539 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1540 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1541 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1542 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | PCB_100 Type | 1 | IC2_Inv1
1543 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1544 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 1 No Medium Gear Replaced | 1 | IC1_Inv1
1545 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 1 No Big Gear Replaced | 1 | IC1_Inv1
1546 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | Actuator 2 No Limit Switch was replaced | 1 | IC1_Inv3
1547 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 1 No Medium Gear Replaced | 1 | IC1_Inv4
1548 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 1 No Actuator Motor | 1 | IC1_Inv4
1549 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1550 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1551 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 1 No Medium Gear Replaced | 1 | IC1_Inv3
1552 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1553 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 1 No Medium Gear Replaced | 1 | IC1_Inv1
1554 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 2000A Fuse | 1 | IC1_Inv4
1555 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | CL18 Connector | 1 | IC1_Inv4
1556 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
1557 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1558 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1559 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
1560 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1561 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 1 No Small Gear Replaced | 1 | IC2_Inv2
1562 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1563 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1564 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 1 No Medium Gear Replaced | 1 | IC1_Inv1
1565 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
1566 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1567 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1568 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-03 | 1 No Actuator Motor | 1 | IC1_Inv1
1569 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-03 | 1 No Medium Gear Replaced | 1 | IC1_Inv2
1570 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-07 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
1571 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-10 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
1572 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-10 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1573 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-11 | 1 No Actuator Motor | 1 | IC1_Inv1
1574 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-11 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1575 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-12 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1576 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-13 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1577 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-13 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1578 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-14 | 1 No Actuator Motor | 1 | IC2_Inv2
1579 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-18 | 1 No Medium Gear Replaced | 1 | IC1_Inv2
1580 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-20 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1581 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-20 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1582 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-21 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1583 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-22 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1584 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-23 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
1585 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-23 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
1586 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-24 | AC Contactor | 1 | IC1_Inv4
1587 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-24 | AC Contactor Busbar | 1 | IC1_Inv4
1588 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-26 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1589 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-28 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
1590 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-28 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
1591 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-30 | 2 Nos Actuator Bearing Replaced | 1 | IC1_Inv4
1592 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-30 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1593 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1594 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1595 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1596 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
1597 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1598 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1599 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
1600 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
1601 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1602 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv2
1603 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
1604 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1605 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1606 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1607 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 1 No Actuator Motor | 1 | IC2_Inv1
1608 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1609 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
1610 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
1611 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
1612 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 2 Nos Actuator Bearing Replaced | 1 | IC1_Inv3
1613 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 1 No Medium Gear Replaced | 1 | IC1_Inv1
1614 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
1615 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 2 Nos Actuator Bearing Replaced | 1 | IC1_Inv1
1616 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | Actuator motor 2 no.s Carbon brushes | 1 | IC1_Inv2
1617 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1618 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
1619 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1620 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
1621 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | Actuator motor 2 no.s Carbon brushes | 1 | IC1_Inv2
1622 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1623 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 2 Nos Actuator Bearing Replaced | 1 | IC2_Inv1
1624 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
1625 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
Formulas:
Days = DAY(EOMONTH([Month Year],0))

## Basic Data (hidden)
Equipment | Affected DC Capacity | Plant Equivalent Weightage | Fault Category Plant BD sheet | Fault Category Tracker BD sheet | Tracker Equipment | Weightage of BD | Plant Equivalent Weightage | Status
IC1_Inv1 | 1669.29 | 15.89% | Module | MSAT100_PCB | MSAT_Type1 | 315 | 0.9665% | Open
IC1_Inv2 | 1833.3 | 17.45% | String Cable | MSAT200_PCB | MSAT_Type2 | 252 | 0.7732% | Close
IC1_Inv3 | 1785.84 | 17% | String Fuse | Tilt Sensor | MSAT_Type3 | 189 | 0.5799%
IC1_Inv4 | 1785.42 | 16.99% | SCB | Actuator | MSAT_Type4 | 210 | 0.6443%
IC2_Inv1 | 1763.16 | 16.78% | SCB Cable | Battery | MSAT_Type5 | 168 | 0.5155%
IC2_Inv2 | 1669.29 | 15.89% | SCB Fuse | Charge Controller | MSAT_Type6 | 126 | 0.3866%
IC1_Inv1_CB1 | 188.16 | 1.791% | Inverter | RTC | Tilt Sensor_Type1 | 63 | 0.1933%
IC1_Inv1_CB2 | 188.58 | 1.795% | InverterAC Cable | Gateway | Tilt Sensor_Type2 | 42 | 0.1289%
IC1_Inv1_CB3 | 188.79 | 1.797% | IDT | MMS | Baatery_Type1 | 315 | 0.9665%
IC1_Inv1_CB4 | 188.37 | 1.793% | IDT MV Cable |  | Baatery_Type2 | 252 | 0.7732%
IC1_Inv1_CB5 | 188.37 | 1.793% | IC MV Panel |  | Baatery_Type3 | 189 | 0.5799%
IC1_Inv1_CB6 | 188.16 | 1.791% | Incomer MV Cable |  | Baatery_Type4 | 210 | 0.6443%
IC1_Inv1_CB7 | 188.16 | 1.791% | Incomer MV Panel |  | Baatery_Type5 | 168 | 0.5155%
IC1_Inv1_CB8 | 188.16 | 1.791% | Metering System Plant |  | Baatery_Type6 | 126 | 0.3866%
IC1_Inv1_CB9 | 162.54 | 1.547% | Grid System |  | CCU_Type1 | 315 | 0.9665%
IC1_Inv1_CB10 | NA |  | Metering System Grid |  | CCU_Type2 | 252 | 0.7732%
IC1_Inv2_CB11 | NA |  | WMS |  | CCU_Type3 | 189 | 0.5799%
IC1_Inv2_CB1 | 188.16 | 1.791% | MMS |  | CCU_Type4 | 210 | 0.6443%
IC1_Inv2_CB2 | 188.16 | 1.791% | Battery Charger_MCR |  | CCU_Type5 | 168 | 0.5155%
IC1_Inv2_CB3 | 188.37 | 1.793% | IC_UPS |  | CCU_Type6 | 126 | 0.3866%
IC1_Inv2_CB4 | 188.37 | 1.793% | IC_Auxiliary Tranformer |  | Actuator Type1 | 63 | 0.1933%
IC1_Inv2_CB5 | 188.16 | 1.791% | IC_Auxiliary DB |  | Actuator Type2 | 42 | 0.1289%
IC1_Inv2_CB6 | 188.16 | 1.791% | IC_SCADA Panel |  | RTC
IC1_Inv2_CB7 | 190.05 | 1.809% | MC4 Connector |  | Gateway
IC1_Inv2_CB8 | 189.84 | 1.807% | Y-Connector |  | Repeater
IC1_Inv2_CB9 | 162.75 | 1.549% |  |  | Switch
IC1_Inv2_CB10 | 161.28 | 1.535%
IC1_Inv2_CB11 | NA
IC1_Inv3_CB1 | 188.16 | 1.791%
IC1_Inv3_CB2 | 188.16 | 1.791%
IC1_Inv3_CB3 | 201.81 | 1.921%
IC1_Inv3_CB4 | 189.21 | 1.801%
IC1_Inv3_CB5 | 190.05 | 1.809%
IC1_Inv3_CB6 | 190.47 | 1.813%
IC1_Inv3_CB7 | 190.26 | 1.811%
IC1_Inv3_CB8 | 191.1 | 1.819%
IC1_Inv3_CB9 | 95.34 | 0.9075%
IC1_Inv3_CB10 | 161.28 | 1.535%
IC1_Inv3_CB11 | NA
IC1_Inv4_CB1 | 204.54 | 1.947%
IC1_Inv4_CB2 | 191.1 | 1.819%
IC1_Inv4_CB3 | 191.1 | 1.819%
IC1_Inv4_CB4 | 191.1 | 1.819%
IC1_Inv4_CB5 | 191.1 | 1.819%
IC1_Inv4_CB6 | 191.1 | 1.819%
IC1_Inv4_CB7 | 204.54 | 1.947%
IC1_Inv4_CB8 | 191.1 | 1.819%
IC1_Inv4_CB9 | 81.9 | 0.7795%
IC1_Inv4_CB10 | 147.84 | 1.407%
IC1_Inv4_CB11 | NA
IC2_Inv1_CB1 | 201.6 | 1.919%
IC2_Inv1_CB2 | 188.16 | 1.791%
IC2_Inv1_CB3 | 188.16 | 1.791%
IC2_Inv1_CB4 | 188.16 | 1.791%
IC2_Inv1_CB5 | 188.37 | 1.793%
IC2_Inv1_CB6 | 188.58 | 1.795%
IC2_Inv1_CB7 | 188.16 | 1.791%
IC2_Inv1_CB8 | 190.05 | 1.809%
IC2_Inv1_CB9 | 161.28 | 1.535%
IC2_Inv1_CB10 | 80.64 | 0.7675%
IC2_Inv1_CB11 | NA
IC2_Inv2_CB1 | 191.73 | 1.825%
IC2_Inv2_CB2 | 192.57 | 1.833%
IC2_Inv2_CB3 | 192.57 | 1.833%
IC2_Inv2_CB4 | 191.94 | 1.827%
IC2_Inv2_CB5 | 191.1 | 1.819%
IC2_Inv2_CB6 | 191.1 | 1.819%
IC2_Inv2_CB7 | 191.1 | 1.819%
IC2_Inv2_CB8 | 191.1 | 1.819%
IC2_Inv2_CB9 | 136.08 | 1.295%
IC2_Inv2_CB10 | NA
IC2_Inv2_CB11 | NA
IC1_IDT | 7073.85 | 67.33%
IC2_IDT | 3432.45 | 32.67%
ICOG1_IC1 | 7073.85 | 67.33%
Incomer1 | 7073.85 | 67.33%
Incomer2 | 3432.45 | 32.67%
Outgoing1 | 10506.3 | 100%
Grid CB | 10506.3 | 100%
MV Cable_Incomer1 | 7073.85 | 67.33%
MV Cable INcomer2 | 3432.45 | 32.67%
MV Cable_IC1_IDT | 7073.85 | 67.33%
MV Cable_IC2_IDT | 3432.45 | 32.67%
IC1_UPS | 7073.85 | 67.33%
IC2_UPS | 3432.45 | 32.67%
IC1_Aux Tranfo. | 7073.85 | 67.33%
IC2_Aux Tranfo. | 3432.45 | 32.67%
IC1_AUX. DB | 7073.85 | 67.33%
IC2_AUX. DB | 3432.45 | 32.67%
IC1_SCADA Panel | 0 | 0%
IC2_SCADA Panel | 0 | 0%
MCR SCADA Panel | 0 | 0%
MCR_Aux Transfo. | 10506.3 | 100%
MCR_Battery Charger | 10506.3 | 100%
String_Type1_310 | 13.02 | 0.1239%
String_Type2_315 | 13.23 | 0.1259%
String_Type3_320 | 13.44 | 0.1279%
String_Type4_325 | 13.65 | 0.1299%
String_Type5_330 | 13.86 | 0.1319%
String_Type6_310/2 | 6.51 | 0.06196%
String_Type7_315/2 | 6.615 | 0.06296%
String_Type8_320/2 | 6.72 | 0.06396%
String_Type9_325/2 | 6.825 | 0.06496%
String_Type10_330/2 | 6.93 | 0.06596%