## O2Summary
Performance Summary PWEGPL
Month | 2025-07-01
Date | 2025-07-10
Financial Year | Year-3
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 585.7978 | 183.6 | -68.66%
| E_Grid MTD(MWh) | 5857.9782 | 6698.4 | 14.35%
| E_Grid YTD (MWh) | 48432.9328 | 45817.2 | -5.401%
2 | Wind Speed Daily | 7.1311 | 3.46 | -51.48%
| Wind Speed MTD | 7.1311 | 5.769 | -19.1%
| Wind Speed YTD | 6.2836 | 5.1814 | -17.54%
3 | PA Daily | 96.03% | 91.64% | -4.569%
| PA MTD | 96.03% | 91.4% | -4.816%
| PA YTD | 96.03% | 91.94% | -4.259%
4 | MA Daily | 97% | 91.64% | -5.523%
| MA MTD | 97% | 91.74% | -5.426%
| MA YTD | 97% | 92.51% | -4.628%
5 | EGA Daily | 99.5% | 100% | 0.5025%
| EGA MTD | 99.5% | 100% | 0.5025%
| EGA YTD | 99.5% | 100% | 0.5025%
6 | IGA Daily | 99% | 100% | 1.01%
| IGA MTD | 99% | 99.64% | 0.6451%
| IGA YTD | 99% | 99.38% | 0.3874%
7 | CUF Daily | 31.29% | 9.808% | -68.66%
| CUF MTD | 31.29% | 35.78% | 14.35%
| CUF YTD | 25.62% | 24.23% | -5.401%
8 | Line Loss Daily | 5% | 1.402% | 71.97%
| Line Loss MTD | 5% | 0.7163% | 85.67%
| Line Loss YTD | 5% | 1.885% | 62.29%
9 | Reactive Power Daily | 5% | 0.0006254% | 99.99%
| Reactive Power MTD | 5% | 0.0001211% | 100%
| Reactive Power YTD | 5% | 0.004617% | 99.91%
10 | Expected Energy Daily | 186.21 | 186.21 | 0%
| Expected Energy MTD | 6743.951 | 6743.95 | -1.483e-05%
| Expected Energy YTD | 46405.669 | 46578.287 | 0.372%

## AnnualKPI
Till Date | 2025-07-10 | 2025-07-01
PWEGPL Performance Summary-YTD
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA(%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | Expected Energy | Loss (%) | Reactive Power (%)
2026 | 101 | 6.2836 | 5.1814 | 48432.9328 | 45817.2 | 25.62% | 24.23% | 99.5% | 100% | 97% | 92.51% | 99% | 99.38% | 96.03% | 91.94% | 46405.669 | 1.885% | 0.004617%

## MonthlyKPI
Till Date | 2025-07-10 | 0 | 0 | 0 | 0
PWEGPL Performance Summary (MTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | WTG Total (MWh) | Line Losses(%) | E_WS_Corrected | Expected Energy | Loss (%) | Reactive Power (%)
2025-07-01 | 10 | 7.1311 | 5.769 | 5857.9782 | 6698.4 | 31.29% | 35.78% | 99.5% | 100% | 97% | 91.74% | 99% | 99.64% | 96.03% | 91.4% | 6743.95 | 0.68% | 6.744 | 6743.951 | 0.7163% | 0.0001211%
Start Date | 2025-07-04
End Date | 2025-07-10
PWEGPL Performance Summary (WTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | E_WS_Corrected
2025-07-01 | 7 | 7.1311 | 5.7172 | 4100.5847 | 4135.2 | 31.29% | 31.56% | 99.5% | 100% | 97% | 91.68% | 99% | 99.48% | 96.03% | 91.2% | 4.171
Start Date | 2025-06-11
End Date | 2025-07-10
PWEGPL Performance Summary (LTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%)
2025-07-01 | 30 | 7.1311 | 6.3512 | 15883.485 | 21148.8 | 28.28% | 37.66% | 99.5% | 100% | 97% | 91.75% | 99% | 99.75% | 96.03% | 91.52%
Formulas:
Days = [Days, row below]-6

## Analytices
Start Date | 2025-07-10
End Date | 2025-07-10 | 24 | 3.8
WTG No. | G01 | G02 | G03 | G04 | G05 | G06 | G07 | G08 | G09 | G10 | G11 | G12 | G13 | G14 | G15 | G16 | G17 | G18 | G19 | G20 | G21 | G22 | G23 | G25 | G26 | G27 | G28 | G29 | G30 | G31 | G32 | G33 | G34 | G35 | G36 | G37 | G38 | G39 | G40
MA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.001157% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 92.43% | 100% | 76.94% | 0.001157% | 100% | 0.06944% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WTG BD Hours | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.9997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8167 | 0 | 5.5333 | 23.9997 | 0 | 23.9833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IGA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
METERING YARD
FEEDER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OG
TRANSFER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
USS
EGA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
External Grid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Generation | 5933 | 5995 | 5680 | 6010 | 4589 | 5933 | 5930 | 5982 | 6600 | 5982 | 5933 | 6595 | 6605 | 6602 | 6398 | 6594 | 0 | 6420 | 6783 | 6932 | 4986 | 4865 | 4738 | 4680 | 3660 | 4580 | 3492 | 0 | 4510 | 0 | 3520 | 3665 | 3654 | 3654 | 3900 | 3850 | 3650 | 3650 | 3660
PA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.001157% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 92.43% | 100% | 76.94% | 0.001157% | 100% | 0.06944% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Sum of BD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.9997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8167 | 0 | 5.5333 | 23.9997 | 0 | 23.9833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Count of BD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MTTR WTG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.9997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8167 | 0 | 5.5333 | 23.9997 | 0 | 11.9917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MTBF WTG | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0.00027778 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22.1833 | 24 | 18.4667 | 0.00027778 | 24 | 0.0083333 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
WS (M/S) | 3.9 | 4 | 3.9 | 3.8 | 3.4 | 4.1 | 3.8 | 4.1 | 3.8 | 3.9 | 4.1 | 4 | 4 | 4 | 3.9 | 4.2 | 0 | 4.1 | 4.3 | 4.1 | 4.5 | 3.8 | 3.1 | 3.5 | 3 | 3.4 | 3.5 | 0 | 3.3 | 0 | 3.3 | 3.5 | 3.4 | 3.4 | 3.7 | 4 | 3.4 | 3.4 | 3.5
Fault Analysis
2023-04-01
|  |  | Put hour Here |  | Default hour for full Data
|  |  | 19944 |  | 19944
Finacial Year | (Multiple Items)
Row Labels | Sum of Breakdown Time | Count of Error Text | MTTR | MTBF
Active Crowbar Failure | 0.21667 | 1 | 0.21667 | 19944
Active Crowbar IGBT Errors | 9.3333 | 2 | 4.6667 | 9972
Analogue Card Failure | 6.0667 | 2 | 3.0333 | 9972
Automatic Secondaries Not OK Too Long | 33.9333 | 20 | 1.6967 | 997.2
Automatic Unwinding | 14.6167 | 7 | 2.0881 | 2849.1429
Blade Position Meas. Error | 22.4167 | 6 | 3.7361 | 3324
Bus Error - Interbus Failure | 325.7333 | 93 | 3.5025 | 214.4516
Bus Preload Protection Thermal Relay Failure | 31.2833 | 12 | 2.6069 | 1662
CAN Communication Failure | 30.95 | 19 | 1.6289 | 1049.6842
CCW Feedback Failure | 72.8167 | 10 | 7.2817 | 1994.4
Change Pause-Remote Control Reset | 5.1667 | 1 | 5.1667 | 19944
Controlled Emergency Series Battery Failure | 13.3167 | 5 | 2.6633 | 3988.8
Converter High Ambient Temperature Alarm | 0.41667 | 1 | 0.41667 | 19944
Coolant Of The Coolant Circuit Failure | 0.33333 | 2 | 0.16667 | 9972
CW Feedback Failure | 40.2667 | 13 | 3.0974 | 1534.1538
DTD Filter Alarm 1 | 9.9667 | 7 | 1.4238 | 2849.1429
Emergency Series HUB Trigger | 45.1333 | 18 | 2.5074 | 1108
Emergency Series Not OK | 1.9 | 2 | 0.95 | 9972
Error In Phase R Of The Inverter | 9.9833 | 4 | 2.4958 | 4986
Error In Phase S Of The Inverter | 13.5 | 2 | 6.75 | 9972
Error In Phase T Of The Inverter | 3.25 | 2 | 1.625 | 9972
Error In Phase T Of The Rectifier | 14.8667 | 4 | 3.7167 | 4986
Excess Current Phase R Of Stator | 1.5167 | 1 | 1.5167 | 19944
Excessive Temperature Of Coolant At The Input Of The Cooling Circuit | 0.36667 | 1 | 0.36667 | 19944
Excessive Temperature Of The Control Module | 7.0833 | 3 | 2.3611 | 6648
Failure Of The Contactor's Rotor Power | 13.0667 | 19 | 0.68772 | 1049.6842
Frequency Failure | 2.35 | 2 | 1.175 | 9972
Gearbox Fan Thermal Relays | 50.6833 | 11 | 4.6076 | 1813.0909
Gearbox Pump Thermal Relay Triggered and High Gearbox Oil Temperature | 6.6667 | 2 | 3.3333 | 9972
Generator Fans Thermal Relay Triggered Too Long | 8 | 7 | 1.1429 | 2849.1429
Generator NDE Bearing High Temperature Alarm | 7.0833 | 8 | 0.88542 | 2493
Generator Slipping Ring High Temperature | 45.05 | 18 | 2.5028 | 1108
Grid Voltage Failure | 169 | 71 | 2.3803 | 280.9014
Heating Protection Triggered | 3.6333 | 2 | 1.8167 | 9972
Heating/Coolant Thermal Magnetic Failure | 107.5833 | 18 | 5.9769 | 1108
High Gearbox Oil Temperature | 3.8833 | 2 | 1.9417 | 9972
High Generator Speed | 0.46667 | 1 | 0.46667 | 19944
High Generator Winding Temperature | 21.8833 | 11 | 1.9894 | 1813.0909
High Grid Harmonic Distortion | 3.55 | 3 | 1.1833 | 6648
High Temperature Of Coolant In The Input Of The Cooling Circuit | 10.4333 | 5 | 2.0867 | 3988.8
High Yaw Brake Pressure | 120.0833 | 23 | 5.221 | 867.1304
HU Pump Drive Failure | 48.4333 | 12 | 4.0361 | 1662
Hydraulic Oil High Temperature | 40.05 | 13 | 3.0808 | 1534.1538
Low Level Hydraulic Group Refrigeration Oil | 917.15 | 200 | 4.5858 | 99.72
Low Pitch Value In Stop Mode (1 Cylinder) | 147.4167 | 7 | 21.0595 | 2849.1429
Low Pressure Of Emergency Accumulators | 35.8 | 10 | 3.58 | 1994.4
Low Pressure On Hydraulic Group | 152.7167 | 47 | 3.2493 | 424.3404
Magnetothermic Of The Stator Protection Failure Or Door Open | 15.9167 | 4 | 3.9792 | 4986
Magnetothermic Trigger Of The Stator Protection | 74.6333 | 34 | 2.1951 | 586.5882
Manual Stop | 241.3161 | 69 | 3.4973 | 289.0435
Max. Pump time | 12.2333 | 4 | 3.0583 | 4986
OGS | 25.3333 | 6 | 4.2222 | 3324
Orienting and High Yaw Brake Pressure | 20.6833 | 5 | 4.1367 | 3988.8
Orienting and Low Yaw Brake Pressure | 4.9833 | 1 | 4.9833 | 19944
Overheating In The Grid's Inductance | 3.5167 | 3 | 1.1722 | 6648
Pitch Drive Error | 287.5333 | 50 | 5.7507 | 398.88
PLC Module Failure | 29.3833 | 12 | 2.4486 | 1662
PLC-Converter Communication Error | 420.55 | 64 | 6.5711 | 311.625
Preload Failure | 24.2833 | 8 | 3.0354 | 2493
Rotor Or Generator High Speed in STOP Or EMERGENCY | 9.15 | 3 | 3.05 | 6648
Rotor Protection Thermal Magnetic Failure | 3.6 | 1 | 3.6 | 19944
Rotor Speed Reading Failure | 7.2333 | 4 | 1.8083 | 4986
Speed Read Incorrectly | 92.7833 | 15 | 6.1856 | 1329.6
Temp. Measurement Module Failure | 4.2333 | 3 | 1.4111 | 6648
Top Emergency Button | 2.6833 | 4 | 0.67083 | 4986
Trafo Fan Thermal Relay Triggered Too Long | 8.5333 | 10 | 0.85333 | 1994.4
Very High Disalignment | 5.6667 | 1 | 5.6667 | 19944
Very Low Pressure On Hydraulic Unit | 33.9167 | 11 | 3.0833 | 1813.0909
Vibration Sensor | 22.5833 | 4 | 5.6458 | 4986
Wear Brushes Generator Triggered Too Long | 6.65 | 5 | 1.33 | 3988.8
Wind Vane Failure Alarm | 3.1667 | 1 | 3.1667 | 19944
Yaw Contactor Active | 12.0333 | 4 | 3.0083 | 4986
Yaw Motors Error | 74.65 | 24 | 3.1104 | 831
Yaw Motors Over Current Protection | 11.0833 | 5 | 2.2167 | 3988.8
Yaw Sensor Wiring Error | 79.4833 | 40 | 1.9871 | 498.6
Yawing Motor Thermal Relays | 9.8333 | 3 | 3.2778 | 6648
Yawing Sensor Failure | 9.2167 | 2 | 4.6083 | 9972
(blank) | 0 |  | #DIV/0! | #DIV/0!
Stator Contactor Failure | 4.9 | 1 | 4.9 | 19944
Hydraulic Filter Dirty | 1.5833 | 1
Slipping Rings Fan Or Heating Resistor Failure | 9.1667 | 3
Gearbox Oil High Temperature Warning | 46.4167 | 15
Difference Between 2 Blades Too High | 69.3167 | 12
Low Bus Voltage | 12.0833 | 1
Change Emergency-Local Reset | 7.5167 | 1
Trigger Of Overvoltage Protection | 8.05 | 1
Initialization Failure | 20.9167 | 3
Gearbox Oil Level Low | 97.3833 | 27
SF6 Breaker Fault | 751.8167 | 49
Low Pressure On Brake Circuit | 6.5 | 2
Transmission Line Related work | 141.1333 | 74
Manual Stop - Preventive Maintenance Activity | 1141.2667 | 151
Manual Stop - Audit | 626.25 | 174
Minimum Hydraulic Unit Temperature | 27.3831 | 8
Generator DE Bearing High Temperature Alarm | 19.45 | 2
Generator's Fans Failure Confirmation | 37.8667 | 19
Low Pressure In Gearbox | 7.55 | 4
Fault In 24v Power Supply | 0.61667 | 1
Out Of Range In Slippage | 6.6667 | 1
High Gearbox Bearing Temperature | 28.1167 | 8
Gearbox Pump Thermal Relay | 8.7167 | 5
Major BD - Transformer | 1528.415 | 65
Major BD - Blade | 3511.6667 | 148
Failure In The Gearbox Oil Particle Sensor | 61.5667 | 6
Rectifier Phase S Overcurrent | 86.9667 | 5
UPS breakdown | 3.3167 | 13
Maximum Synchronization Time | 2.4 | 1
Encoder Suynchronism Error | 16.7667 | 6
Transformer Fan Control Failure | 2.9 | 1
Encoder Not OK | 37.05 | 5
Maximum Time For Stator Disconnection | 2.9333 | 2
High Rotor Speed | 326.2167 | 16
Magnetothermic Trigger Of The Line Protection | 4.5667 | 1
Hydraulic Pump Protection | 25.15 | 4
Gearbox Bearing High Temperature Warning | 28.6 | 3
Max Orientation Time | 7.9667 | 2
General Work Stoppage | 85.9167 | 34
Gearbox Fan Feedback Failure | 3.4833 | 2
Automatics Not Ok | 0.45 | 1
Gearbox Fan Thermal Relays Triggered and High Gearbox Oil Temperature | 9.05 | 3
Wear Brushes Generator | 6.5 | 3
Hydraulic Unit Cooling Failure | 4.7667 | 1
SF6 and HV side | 230.8333 | 50
Fault In Analog Electronic Power Supply | 4.7 | 1
Very High Temperature Of Hydraulic Unit Oil | 2.3833 | 2
High Temperature Of The Control Module | 4.0667 | 1
Grand Total | 13265.5808 | 2069
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 3.5474 | 0 | [9 empty] | 125761 |  |  |  | 80 | 4.6 | 257758.0645 |  | 13.42% | 96.03% | 99.5% | 0 |  |  |  |  | 0% | 0% | 5% | 5% | 80
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 3.5682 | 0 | 92.81% | 92.81% | 100% | 100% |  |  |  |  | 4.938% | 111431 | 99600 | 4800 | 94800 | 80 | 4.6 | 257758.0645 |  | 13.42% | 96.03% | 99.5% | 0 |  |  |  |  | 10.62% | 0% | 5% | 5% | 80
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 4.391 | 0 | 88.58% | 88.79% | 99.77% | 100% |  |  |  |  | 12.94% | 258117 | 250800 | 2400 | 248400 | 80 | 4.6 | 257758.0645 |  | 13.42% | 96.03% | 99.5% | 0 |  |  |  |  | 2.835% | 0.01852% | 5% | 5% | 80
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.0569 | 0 | 83.81% | 85.33% | 98.22% | 100% |  |  |  |  | 10.64% | 216864 | 202800 | 3600 | 199200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 217.953 |  |  |  |  | 6.485% | 0.02213% | 5% | 5% | 78
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.5428 | 0 | 87.37% | 88.82% | 98.36% | 100% |  |  |  |  | 22.37% | 428910 | 418800 | 0 | 418800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 422.859 |  |  |  |  | 2.357% | 0.01541% | 5% | 5% | 78
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.391 | 0 | 90% | 90.31% | 99.65% | 100% |  |  |  |  | 13.21% | 257492 | 250800 | 3600 | 247200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 255.178 |  |  |  |  | 2.599% | 0.02012% | 5% | 5% | 78
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.0579 | 0 | 85.6% | 85.6% | 100% | 100% |  |  |  |  | 7.5% | 161561 | 144000 | 3600 | 140400 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 165.1 |  |  |  |  | 10.87% | 0.02802% | 5% | 5% | 78
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 2.9132 | 0 | 92.5% | 92.5% | 100% | 100% |  |  |  |  | 3.782% | 81163 | 75600 | 4800 | 70800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 77.212 |  |  |  |  | 6.854% | 0.09428% | 5% | 5% | 78
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 3.3879 | 0 | 91.34% | 91.34% | 100% | 100% |  |  |  |  | 5.385% | 111449 | 104400 | 3600 | 100800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 106.019 |  |  |  |  | 6.325% | 0.0396% | 5% | 5% | 78
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.1233 | 0 | 87.01% | 90.47% | 96.18% | 100% |  |  |  |  | 11.73% | 236100 | 222000 | 2400 | 219600 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 238.176 |  |  |  |  | 5.972% | 0.01324% | 5% | 5% | 78
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 3.4951 | 0 | 92.26% | 92.26% | 100% | 100% |  |  |  |  | 7.756% | 151284 | 150000 | 4800 | 145200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 149.33 |  |  |  |  | 0.8487% | 0.02619% | 5% | 5% | 78
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.8151 | 0 | 89.35% | 89.35% | 100% | 100% |  |  |  |  | 16.35% | 327786 | 308400 | 2400 | 306000 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 327.512 |  |  |  |  | 5.914% | 0.01299% | 5% | 5% | 78
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.5674 | 0 | 94.53% | 94.53% | 100% | 100% |  |  |  |  | 27.31% | 519730 | 513600 | 2400 | 511200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 511 |  |  |  |  | 1.179% | 0.0008926% | 5% | 5% | 78
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.5762 | 0 | 94.23% | 94.23% | 100% | 100% |  |  |  |  | 27.31% | 514588 | 511200 | 0 | 511200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 514 |  |  |  |  | 0.6584% | 0% | 5% | 5% | 78
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.4377 | 0 | 94.03% | 94.03% | 100% | 100% |  |  |  |  | 24.81% | 469515 | 465600 | 1200 | 464400 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 469.51 |  |  |  |  | 0.8338% | 0.0007802% | 5% | 5% | 78
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.8151 | 0 | 94.73% | 94.73% | 100% | 100% |  |  |  |  | 17.63% | 333663 | 331200 | 1200 | 330000 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 333.66 |  |  |  |  | 0.7382% | 0.00143% | 5% | 5% | 78
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.7597 | 0 | 94.68% | 94.68% | 100% | 100% |  |  |  |  | 31.92% | 601869 | 598800 | 1200 | 597600 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 601.869 |  |  |  |  | 0.5099% | 0.000793% | 5% | 5% | 78
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.9428 | 0 | 93.75% | 93.75% | 100% | 100% |  |  |  |  | 27.95% | 530337 | 526800 | 3600 | 523200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 530.337 |  |  |  |  | 0.6669% | 0.0009% | 5% | 5% | 78
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.5674 | 0 | 94.3% | 94.3% | 100% | 100% |  |  |  |  | 29.42% | 552581 | 550800 | 0 | 550800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 552.581 |  |  |  |  | 0.3223% | 0.0006495% | 5% | 5% | 78
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.5762 | 0 | 94.45% | 94.45% | 100% | 100% |  |  |  |  | 27.88% | 522462 | 522000 | 0 | 522000 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 522.462 |  |  |  |  | 0.08843% | 0.0006869% | 5% | 5% | 78
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.8151 | 0 | 93.84% | 93.84% | 100% | 100% |  |  |  |  | 16.86% | 320599 | 316800 | 1200 | 315600 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 320.59 |  |  |  |  | 1.185% | 0.002246% | 5% | 5% | 78
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.5097 | 0 | 94.17% | 94.17% | 100% | 100% |  |  |  |  | 21.54% | 407326 | 405600 | 2400 | 403200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 407.32 |  |  |  |  | 0.4237% | 0% | 5% | 5% | 78
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.721 | 0 | 94.18% | 94.18% | 100% | 100% |  |  |  |  | 40.13% | 752099 | 751200 | 0 | 751200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 752.09 |  |  |  |  | 0.1195% | 0% | 5% | 5% | 78
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.2598 | 0 | 94.29% | 94.29% | 100% | 100% |  |  |  |  | 15.45% | 299034 | 291600 | 2400 | 289200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 299.03 |  |  |  |  | 2.486% | 0.002809% | 5% | 5% | 78
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.0569 | 0 | 93.43% | 93.43% | 100% | 100% |  |  |  |  | 11.35% | 215096 | 213600 | 1200 | 212400 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 215.09 |  |  |  |  | 0.6955% | 0.003905% | 5% | 5% | 78
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 3.4903 | 0 | 94.25% | 94.25% | 100% | 100% |  |  |  |  | 6.474% | 128167 | 126000 | 4800 | 121200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 128.16 |  |  |  |  | 1.691% | 0.005618% | 5% | 5% | 78
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.2944 | 0 | 93.05% | 93.05% | 100% | 100% |  |  |  |  | 10.51% | 203962 | 198000 | 1200 | 196800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 203.96 |  |  |  |  | 2.923% | 0.004698% | 5% | 5% | 78
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.2262 | 0 | 93.13% | 93.13% | 100% | 100% |  |  |  |  | 12.76% | 243861 | 242400 | 3600 | 238800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 243.86 |  |  |  |  | 0.5991% | 0.0009862% | 5% | 5% | 78
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.8151 | 0 | 94.18% | 94.18% | 100% | 100% |  |  |  |  | 20.13% | 379529 | 376800 | 0 | 376800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 379.52 |  |  |  |  | 0.719% | 0.0006337% | 5% | 5% | 78
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.2369 | 0 | 93.4% | 93.4% | 100% | 100% |  |  |  |  | 9.744% | 190112 | 187200 | 4800 | 182400 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 190.11 |  |  |  |  | 1.532% | 0.004418% | 5% | 5% | 78
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.0569 | 0 | 93.92% | 93.92% | 100% | 100% |  |  |  |  | 14.36% | 271844 | 268800 | 0 | 268800 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 271.84 |  |  |  |  | 1.12% | 0.002205% | 5% | 5% | 78
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.0569 | 0 | 94.44% | 94.44% | 100% | 100% |  |  |  |  | 14.1% | 271570 | 268800 | 4800 | 264000 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 271.54 |  |  |  |  | 1.02% | 0.002657% | 5% | 5% | 78
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.9428 | 0 | 93% | 93% | 100% | 100% |  |  |  |  | 31.47% | 590942 | 589200 | 0 | 589200 | 78 | 5.6333 | 340888.4726 |  | 18.21% | 96.03% | 99.5% | 590.94 |  |  |  |  | 0.2948% | 0.000407% | 5% | 5% | 78
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.8867 | 0 | 90.99% | 92.87% | 97.98% | 100% |  |  |  |  | 31.22% | 588285 | 584400 | 0 | 584400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 588.28 |  |  |  |  | 0.6604% | 0% | 5% | 5% | 78
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.5097 | 0 | 92.56% | 92.56% | 100% | 100% |  |  |  |  | 25.06% | 491493 | 469200 | 0 | 469200 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 491.49 |  |  |  |  | 4.536% | 0.00122% | 5% | 5% | 78
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.9187 | 0 | 93.55% | 93.55% | 100% | 100% |  |  |  |  | 32.76% | 616130 | 614400 | 1200 | 613200 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 616.13 |  |  |  |  | 0.2808% | 0.0001922% | 5% | 5% | 78
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8151 | 0 | 92.91% | 92.91% | 100% | 100% |  |  |  |  | 21.03% | 404176 | 397200 | 3600 | 393600 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 404.17 |  |  |  |  | 1.726% | 0.000595% | 5% | 5% | 78
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.0569 | 0 | 91.08% | 91.08% | 100% | 100% |  |  |  |  | 14.04% | 266316 | 262800 | 0 | 262800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 266.31 |  |  |  |  | 1.32% | 0.00219% | 5% | 5% | 78
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.391 | 0 | 92.29% | 92.37% | 99.91% | 100% |  |  |  |  | 16.03% | 306808 | 304800 | 4800 | 300000 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 306.8 |  |  |  |  | 0.6545% | 0.001173% | 5% | 5% | 78
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8151 | 0 | 92.2% | 92.2% | 100% | 100% |  |  |  |  | 17.95% | 351123 | 336000 | 0 | 336000 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 351.12 |  |  |  |  | 4.307% | 0.00137% | 5% | 5% | 78
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.0569 | 0 | 93.78% | 93.78% | 100% | 100% |  |  |  |  | 16.6% | 315253 | 310800 | 0 | 310800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 315.25 |  |  |  |  | 1.413% | 0.001138% | 5% | 5% | 78
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.8852 | 0 | 93.01% | 93.01% | 100% | 100% |  |  |  |  | 7.308% | 144826 | 141600 | 4800 | 136800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 144.82 |  |  |  |  | 2.228% | 0.01078% | 5% | 5% | 78
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.2369 | 0 | 93.81% | 93.81% | 100% | 100% |  |  |  |  | 10.06% | 194224 | 192000 | 3600 | 188400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 194.22 |  |  |  |  | 1.145% | 0.005544% | 5% | 5% | 78
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8151 | 0 | 90.74% | 90.74% | 100% | 100% |  |  |  |  | 17.82% | 338208 | 334800 | 1200 | 333600 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 338.2 |  |  |  |  | 1.008% | 0.001772% | 5% | 5% | 78
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.5474 | 0 | 88.04% | 88.31% | 99.69% | 100% |  |  |  |  | 5.833% | 112662 | 111600 | 2400 | 109200 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 112.66 |  |  |  |  | 0.9426% | 0.005177% | 5% | 5% | 78
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8055 | 0 | 92.61% | 92.61% | 100% | 100% |  |  |  |  | 10.51% | 205550 | 201600 | 4800 | 196800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 205.55 |  |  |  |  | 1.922% | 0.004086% | 5% | 5% | 78
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.4951 | 0 | 89.49% | 89.49% | 100% | 100% |  |  |  |  | 6.987% | 139230 | 135600 | 4800 | 130800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 139.23 |  |  |  |  | 2.607% | 0.008378% | 5% | 5% | 78
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.5474 | 0 | 91.09% | 91.09% | 100% | 100% |  |  |  |  | 10.19% | 194666 | 192000 | 1200 | 190800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 194.66 |  |  |  |  | 1.37% | 0.003079% | 5% | 5% | 78
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.0569 | 0 | 91.41% | 92.21% | 99.13% | 100% |  |  |  |  | 16.99% | 321526 | 318000 | 0 | 318000 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 321.52 |  |  |  |  | 1.097% | 0.001496% | 5% | 5% | 78
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.8852 | 0 | 89.14% | 91.2% | 97.74% | 100% |  |  |  |  | 9.167% | 176988 | 174000 | 2400 | 171600 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 176.98 |  |  |  |  | 1.688% | 0.002049% | 5% | 5% | 78
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.5474 | 0 | 93.91% | 93.91% | 100% | 100% |  |  |  |  | 6.667% | 131285 | 127200 | 2400 | 124800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 131.28 |  |  |  |  | 3.112% | 0.006398% | 5% | 5% | 78
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.4951 | 0 | 88.47% | 92.89% | 95.24% | 100% |  |  |  |  | 7.179% | 141695 | 138000 | 3600 | 134400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 141.69 |  |  |  |  | 2.608% | 0.01355% | 5% | 5% | 78
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.8852 | 0 | 89.47% | 92.58% | 96.64% | 100% |  |  |  |  | 9.231% | 178470 | 176400 | 3600 | 172800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 178.47 |  |  |  |  | 1.16% | 0.004043% | 5% | 5% | 78
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.5474 | 0 | 91.58% | 92.78% | 98.7% | 100% |  |  |  |  | 9.744% | 191723 | 187200 | 4800 | 182400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 191.73 |  |  |  |  | 2.359% | 0.002509% | 5% | 5% | 78
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8055 | 0 | 92.91% | 92.91% | 100% | 100% |  |  |  |  | 15% | 286041 | 285600 | 4800 | 280800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 286.08 |  |  |  |  | 0.1542% | 0.00714% | 5% | 5% | 78
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 2.9906 | 0 | 87.14% | 93.58% | 93.11% | 100% |  |  |  |  | 4.231% | 87964 | 84000 | 4800 | 79200 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 87.96 |  |  |  |  | 4.506% | 0.02048% | 5% | 5% | 78
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.6823 | 0 | 92.52% | 93.17% | 99.31% | 100% |  |  |  |  | 13.59% | 261720 | 258000 | 3600 | 254400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 261.72 |  |  |  |  | 1.421% | 0.002304% | 5% | 5% | 78
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.8852 | 0 | 94.28% | 94.28% | 100% | 100% |  |  |  |  | 12.31% | 236447 | 231600 | 1200 | 230400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 236.44 |  |  |  |  | 2.05% | 0.002551% | 5% | 5% | 78
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.4951 | 0 | 92.83% | 92.83% | 100% | 100% |  |  |  |  | 7.179% | 140266 | 138000 | 3600 | 134400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 140.26 |  |  |  |  | 1.616% | 0.006858% | 5% | 5% | 78
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8151 | 0 | 88.22% | 92.92% | 94.95% | 100% |  |  |  |  | 23.21% | 436047 | 434400 | 0 | 434400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 436.04 |  |  |  |  | 0.3777% | 0% | 5% | 5% | 78
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.5097 | 0 | 91.79% | 91.84% | 99.95% | 100% |  |  |  |  | 22.24% | 424522 | 420000 | 3600 | 416400 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 424.52 |  |  |  |  | 1.065% | 0.001133% | 5% | 5% | 78
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.739 | 0 | 93.02% | 93.18% | 99.83% | 100% |  |  |  |  | 28.4% | 539046 | 531600 | 0 | 531600 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 539.04 |  |  |  |  | 1.381% | 0.0002265% | 5% | 5% | 78
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.2598 | 0 | 94.21% | 94.21% | 100% | 100% |  |  |  |  | 29.36% | 552531 | 549600 | 0 | 549600 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 552.53 |  |  |  |  | 0.5305% | 0.000221% | 5% | 5% | 78
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.7597 | 0 | 89.79% | 93.13% | 96.41% | 100% |  |  |  |  | 44.17% | 829710 | 826800 | 0 | 826800 | 78 | 6.5667 | 558388.3927 |  | 29.83% | 96.03% | 99.5% | 829.71 |  |  |  |  | 0.3507% | 0% | 5% | 5% | 78
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.6618 | 0 | 94.31% | 94.38% | 99.93% | 100% |  |  |  |  | 41.79% | 785959 | 782400 | 0 | 782400 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 785.95 |  |  |  |  | 0.4528% | 0% | 5% | 5% | 78
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 4.8151 | 0 | 92.56% | 93.46% | 99.03% | 100% |  |  |  |  | 20.26% | 381731 | 379200 | 0 | 379200 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 381.73 |  |  |  |  | 0.663% | 0% | 5% | 5% | 78
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.2598 | 0 | 93.6% | 93.81% | 99.77% | 100% |  |  |  |  | 38.85% | 730526 | 727200 | 0 | 727200 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 730.52 |  |  |  |  | 0.4553% | 0% | 5% | 5% | 78
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 3.8852 | 0 | 84.61% | 96.74% | 87.46% | 100% |  |  |  |  | 8.397% | 161209 | 157200 | 0 | 157200 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 161.2 |  |  |  |  | 2.487% | 0.001492% | 5% | 5% | 78
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 4.6823 | 0 | 93.77% | 93.77% | 100% | 100% |  |  |  |  | 14.42% | 275124 | 272400 | 2400 | 270000 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 275.12 |  |  |  |  | 0.9901% | 0.002192% | 5% | 5% | 78
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 4.8151 | 0 | 94.19% | 94.19% | 100% | 100% |  |  |  |  | 21.22% | 409156 | 397200 | 0 | 397200 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 409.15 |  |  |  |  | 2.922% | 0.0002984% | 5% | 5% | 78
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.2598 | 0 | 94.31% | 94.31% | 100% | 100% |  |  |  |  | 29.36% | 551667 | 549600 | 0 | 549600 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 551.66 |  |  |  |  | 0.3747% | 0% | 5% | 5% | 78
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.4377 | 0 | 93.82% | 95.68% | 98.06% | 100% |  |  |  |  | 30.19% | 567412 | 565200 | 0 | 565200 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 567.41 |  |  |  |  | 0.3898% | 0.0002152% | 5% | 5% | 78
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.9444 | 0 | 93.6% | 93.6% | 100% | 100% |  |  |  |  | 44.04% | 826022 | 824400 | 0 | 824400 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 826.02 |  |  |  |  | 0.1964% | 0% | 5% | 5% | 78
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.3749 | 0 | 93.11% | 93.11% | 100% | 100% |  |  |  |  | 29.36% | 554892 | 552000 | 2400 | 549600 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 554.89 |  |  |  |  | 0.5212% | 0.0006535% | 5% | 5% | 78
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 4.8151 | 0 | 92.61% | 92.71% | 99.89% | 100% |  |  |  |  | 25.9% | 491107 | 484800 | 0 | 484800 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 491.1 |  |  |  |  | 1.284% | 0.0002486% | 5% | 5% | 78
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 4.6823 | 0 | 94.32% | 94.32% | 100% | 100% |  |  |  |  | 22.44% | 428579 | 422400 | 2400 | 420000 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 428.57 |  |  |  |  | 1.442% | 0.001407% | 5% | 5% | 78
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 3.5474 | 0 | 93.01% | 93.39% | 99.59% | 100% |  |  |  |  | 5.705% | 116756 | 112800 | 6000 | 106800 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 116.75 |  |  |  |  | 3.388% | 0.01236% | 5% | 5% | 78
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 3.4951 | 0 | 90.46% | 90.46% | 100% | 100% |  |  |  |  | 3.526% | 93389 | 73200 | 7200 | 66000 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 76.68 |  |  |  |  | 21.62% | 0.01873% | 5% | 5% | 78
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 4.0569 | 0 | 91.37% | 91.37% | 100% | 100% |  |  |  |  | 15.19% | 318458 | 284400 | 0 | 284400 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 287.9 |  |  |  |  | 10.69% | 0.0007348% | 5% | 5% | 78
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.9444 | 0 | 92.25% | 92.31% | 99.93% | 100% |  |  |  |  | 42.5% | 810773 | 795600 | 0 | 795600 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 799.17 |  |  |  |  | 1.871% | 0.0001421% | 5% | 5% | 78
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.9797 | 0 | 90.63% | 90.63% | 100% | 100% |  |  |  |  | 47.88% | 911743 | 896400 | 0 | 896400 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 900.13 |  |  |  |  | 1.683% | 0% | 5% | 5% | 78
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 9.8669 | 0 | 91.41% | 91.5% | 99.91% | 100% |  |  |  |  | 55.19% | 1048241 | 1033200 | 0 | 1033200 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 1036.64 |  |  |  |  | 1.435% | 0% | 5% | 5% | 78
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.5603 | 0 | 91.46% | 91.46% | 100% | 100% |  |  |  |  | 49.1% | 933641 | 919200 | 0 | 919200 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 922.04 |  |  |  |  | 1.547% | 0% | 5% | 5% | 78
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 9.1527 | 0 | 92.08% | 92.08% | 100% | 100% |  |  |  |  | 54.74% | 1039356 | 1024800 | 0 | 1024800 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 1027.75 |  |  |  |  | 1.4% | 0% | 5% | 5% | 78
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 8.5607 | 0 | 90.8% | 90.8% | 100% | 100% |  |  |  |  | 50.58% | 961356 | 946800 | 0 | 946800 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 949.75 |  |  |  |  | 1.514% | 0% | 5% | 5% | 78
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.9797 | 0 | 91.68% | 91.68% | 100% | 100% |  |  |  |  | 48.91% | 930291 | 915600 | 0 | 915600 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 918.69 |  |  |  |  | 1.579% | 0% | 5% | 5% | 78
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 8.6467 | 0 | 91.79% | 91.79% | 100% | 100% |  |  |  |  | 58.91% | 1117630 | 1102800 | 0 | 1102800 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 1106.03 |  |  |  |  | 1.327% | 0% | 5% | 5% | 78
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.7649 | 0 | 91.9% | 91.9% | 100% | 100% |  |  |  |  | 56.99% | 1081503 | 1066800 | 0 | 1066800 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 1069.9 |  |  |  |  | 1.359% | 0% | 5% | 5% | 78
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.0985 | 0 | 88.96% | 91.92% | 96.78% | 100% |  |  |  |  | 35.64% | 655212 | 667200 | 0 | 667200 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 676.61 |  |  |  |  | -1.83% | 0% | 5% | 5% | 78
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 4.6851 | 0 | 90.87% | 90.87% | 100% | 100% |  |  |  |  | 19.36% | 366418 | 362400 | 0 | 362400 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 365.82 |  |  |  |  | 1.097% | 0% | 5% | 5% | 78
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.2874 | 0 | 91.26% | 91.26% | 100% | 100% |  |  |  |  | 31.79% | 583375 | 595200 | 0 | 595200 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 598.78 |  |  |  |  | -2.027% | 0% | 5% | 5% | 78
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.7295 | 0 | 90.9% | 90.9% | 100% | 100% |  |  |  |  | 44.74% | 851711 | 837600 | 0 | 837600 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 840.11 |  |  |  |  | 1.657% | 0.0002742% | 5% | 5% | 78
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 9.2621 | 0 | 91.84% | 91.84% | 100% | 100% |  |  |  |  | 60.19% | 1141646 | 1126800 | 0 | 1126800 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 1130.55 |  |  |  |  | 1.3% | 0% | 5% | 5% | 78
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.7295 | 0 | 92.03% | 92.03% | 100% | 100% |  |  |  |  | 42.63% | 813028 | 798000 | 0 | 798000 | 78 | 6.5667 | 501275.3421 |  | 26.78% | 96.03% | 99.5% | 801.43 |  |  |  |  | 1.848% | 0% | 5% | 5% | 78
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 5.1585 | 0 | 91.67% | 91.67% | 100% | 100% |  |  |  |  | 43.97% | 826509 | 823200 | 0 | 823200 | 78 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 826.51 |  |  |  |  | 0.4004% | 0% | 5% | 5% | 78
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 5.0007 | 0 | 91.11% | 91.11% | 100% | 100% |  |  |  |  | 41.22% | 774795 | 771600 | 0 | 771600 | 78 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 774.795 |  |  |  |  | 0.4124% | 0% | 5% | 5% | 78
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 7.5105 | 0 | 92.86% | 92.86% | 100% | 100% |  |  |  |  | 51.73% | 971643 | 968400 | 0 | 968400 | 78 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 971.643 |  |  |  |  | 0.3338% | 0% | 5% | 5% | 78
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 6.5364 | 0 | 91.04% | 91.04% | 100% | 100% |  |  |  |  | 42.82% | 804983 | 801600 | 0 | 801600 | 78 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 804.983 |  |  |  |  | 0.4203% | 0% | 5% | 5% | 78
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 6.6092 | 0 | 89.7% | 91.96% | 97.54% | 100% |  |  |  |  | 42.95% | 807243 | 804000 | 0 | 804000 | 78 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 807.243 |  |  |  |  | 0.4017% | 0% | 5% | 5% | 78
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 8.6467 | 0 | 91.2% | 91.2% | 100% | 100% |  |  |  |  | 56.15% | 1068626 | 1051200 | 0 | 1051200 | 78 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 1068.626 |  |  |  |  | 1.631% | 0% | 5% | 5% | 78
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 4.6705 | 0 | 92.03% | 92.23% | 99.79% | 100% |  |  |  |  | 21.15% | 398921 | 396000 | 0 | 396000 | 78 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 398.921 |  |  |  |  | 0.7322% | 0.0005854% | 5% | 5% | 78
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 5.4123 | 0 | 90.23% | 91.09% | 99.06% | 100% |  |  |  |  | 29.1% | 548000 | 544800 | 0 | 544800 | 78 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 548 |  |  |  |  | 0.5839% | 0% | 5% | 5% | 78
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 4.6851 | 0 | 92.57% | 92.57% | 100% | 100% |  |  |  |  | 18.91% | 357020 | 354000 | 0 | 354000 | 78 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 357.02 |  |  |  |  | 0.8459% | 0% | 5% | 5% | 78
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 3.46 | 0 | 91.64% | 91.64% | 100% | 100% |  |  |  |  | 9.808% | 186210 | 183600 | 0 | 183600 | 78 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 186.21 |  |  |  |  | 1.402% | 0.0006254% | 5% | 5% | 78
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 7.6 | 585797.8194 |  | 31.29% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [8 empty] | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 0 | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | 0 |  |  |  |  | 0% |  | 5% | 5% | 78
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 6.8667 | 616013.6335 |  | 32.91% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.0333 | 279529.7337 |  | 14.93% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 3.9667 | 164597.8603 |  | 8.793% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.0333 | 162550.4631 |  | 8.683% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.4333 | 183922.4143 |  | 9.825% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.8 | 128093.396 |  | 6.843% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 4.3 | 171913.6008 |  | 9.183% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.6 | 221156.2315 |  | 11.81% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 78
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Input_Raw
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106
[5 empty] | Energy Generated by individual Turbine | [38 empty] | Wind Speed (M/s) | [42 empty] | Meter Readings | [7 empty] | Calculated Energy Numbers
Date | Finacial Year | Calendor Year | Month Year | Days | G01 | G02 | G03 | G04 | G05 | G06 | G07 | G08 | G09 | G10 | G11 | G12 | G13 | G14 | G15 | G16 | G17 | G18 | G19 | G20 | G21 | G22 | G23 | G25 | G26 | G27 | G28 | G29 | G30 | G31 | G32 | G33 | G34 | G35 | G36 | G37 | G38 | G39 | G40 | WS_G01 | WS_G02 | WS_G03 | WS_G04 | WS_G05 | WS_G06 | WS_G07 | WS_G08 | WS_G09 | WS_G10 | WS_G11 | WS_G12 | WS_G13 | WS_G14 | WS_G15 | WS_G16 | WS_G17 | WS_G18 | WS_G19 | WS_G20 | WS_G21 | WS_G22 | WS_G23 | WS_G25 | WS_G26 | WS_G27 | WS_G28 | WS_G29 | WS_G30 | WS_G31 | WS_G32 | WS_G33 | WS_G34 | WS_G35 | WS_G36 | WS_G37 | WS_G38 | WS_G39 | WS_G40 | WTG Total Gneration (KWh) | Wind Speed Average cumulative (m/S)2 | Wind Speed Max (m/S) | Rain (mm) | 33 kV_Wind_F1_Export reading | 33 kV_Wind_F1_Import reading | 33 kV_Wind_F2_Export_reading | 33 kV_Wind_F2_Import_reading | 33 kV_Wind_F3_Export_Reading | 33 kV_Wind_F3_Import_Reading | 33 kV_Wind_F4_Export Reading | 33 kV_Wind_F4_Import Reading | 33 kV_F1_Total_Export (KWh) | 33 kV_Wind_F1_Import (KWh) | 33 kV_F2_Total_Export (KWh)2 | 33 kV_Wind_F2_Import (KWh) | 33 kV_Wind_F3_Export (KWh) | 33 kV_Wind_F3_Import (KWh)2 | 33 kV_Wind_F4_Export (KWh) | 33 kV_Wind_F4_Import (KWh)2 | 33 kV_Wind_Total_Export (KWh) | 33 kV_Wind_Total_Import (KWh) | 33 kV Line Loss (%) | Forecasting Data count received on Forecasting Portal | Forecasting Penalties (INR) | Expected Energy As Per Power Curve (MWh) | Reactive Energy (MVArH) | Operational Capacity | Column1
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 3576 | 5244 | 3376 | 3992 | 2114 | 3446 | 4316 | 4376 | 3336 | 2784 | 3724 | 4284 | 4556 | 5446 | 4725 | 3332 | 3446 | 3780 | 4017 | 5100 | 4216 | 2780 | 1846 | 2882 | 2546 | 3164 | 2420 | 0 | 2614 | 0 | 2684 | 2107 | 2688 | 2976 | 2792 | 2818 | 2858 | 2612 | 2788 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 4.05 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 4.18 | 3.41 | 4.09 | 4.29 | 4.06 | 4.5 | 3.75 | 3.14 | 3.53 | 3.02 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 125761 | 3.5474 |  |  | 237611 | 2156 | 278009 | 2188 | 253479 | 1795 | 289037 | 1839 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0% | 0 | 0 |  |  | 80
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 2552 | 3752 | 2170 | 3336 | 2196 | 2804 | 3645 | 3288 | 3376 | 3000 | 2864 | 3892 | 3398 | 3550 | 3998 | 3892 | 3980 | 3348 | 3505 | 3775 | 3630 | 2556 | 1802 | 2822 | 2672 | 2662 | 1552 | 0 | 2712 | 0 | 2760 | 2289 | 2512 | 2838 | 3150 | 2882 | 2772 | 2708 | 2791 | 3.21 | 3.42 | 3.52 | 3.63 | 3.23 | 3.53 | 3.4 | 3.17 | 3.02 | 3.2 | 3.52 | 3.17 | 4.36 | 4.09 | 4.46 | 4.36 | 4.67 | 4.28 | 4.44 | 4.5 | 4.11 | 3.93 | 4.13 | 4.08 | 3.47 | 3.92 | 3.89 | 0 | 3.8 | 0 | 3.61 | 3.69 | 3.51 | 3.72 | 3.87 | 3.73 | 3.54 | 3.45 | 3.53 | 111431 | 3.5682 |  |  | 237629 | 2157 | 278030 | 2189 | 253501 | 1796 | 289059 | 1840 | 21600 | 1200 | 25200 | 1200 | 26400 | 1200 | 26400 | 1200 | 99600 | 4800 | 10.62% | 96 | 2931 |  |  | 80
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 9436 | 10444 | 8994 | 7992 | 5532 | 8810 | 6040 | 8864 | 8552 | 7384 | 9876 | 5883 | 7698 | 7408 | 6173 | 7064 | 8016 | 6908 | 8564 | 10477 | 6850 | 3920 | 4886 | 7082 | 5480 | 6348 | 6006 | 0 | 4162 | 0 | 5080 | 6703 | 7996 | 4764 | 4792 | 5596 | 6680 | 7552 | 4105 | 4.76 | 4.88 | 4.8 | 4.65 | 4.27 | 5.04 | 5.09 | 4.76 | 4.82 | 4.8 | 4.93 | 4.74 | 4.55 | 4.63 | 4.57 | 4.63 | 4.82 | 4.84 | 4.83 | 5.1 | 4.76 | 4.34 | 4.24 | 4.48 | 4.55 | 4.34 | 4.26 | 0 | 3.79 | 0 | 4.37 | 4.3 | 4.48 | 4.78 | 4.74 | 4.25 | 4.44 | 4.59 | 5.03 | 258117 | 4.391 |  |  | 237670 | 2158 | 278051 | 2189 | 253571 | 1796 | 289136 | 1841 | 49200 | 1200 | 25200 | 0 | 84000 | 0 | 92400 | 1200 | 250800 | 2400 | 2.835% | 96 | 17068 |  |  | 80
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 3664 | 7960 | 5356 | 5976 | 4726 | 7228 | 6951 | 6252 | 5836 | 6356 | 6456 | 6719 | 5686 | 4942 | 4039 | 5316 | 6766 | 6572 | 6788 | 7386 | 5148 | 4276 | 5832 | 7202 | 5834 | 6752 | 6260 | 0 | 3918 | 0 | 5518 | 6091 | 7280 | 5474 | 3390 | 7150 | 5240 | 6772 | 3752 | 4.58 | 4.46 | 3.97 | 4.15 | 3.78 | 4.38 | 4.4 | 4.13 | 4.08 | 3.95 | 4.01 | 4.04 | 3.98 | 3.84 | 3.92 | 3.95 | 4.15 | 4.01 | 3.99 | 4.01 | 3.76 | 3.87 | 3.95 | 4.26 | 4.2 | 4.22 | 4.21 | 0 | 5.44 | 0 | 4.17 | 4.15 | 4.32 | 4.55 | 6.32 | 4.45 | 4.87 | 4.31 | 5.39 | 216864 | 4.0569 |  |  | 237715 | 2159 | 278085 | 2190 | 253615 | 1797 | 289182 | 1841 | 54000 | 1200 | 40800 | 1200 | 52800 | 1200 | 55200 | 0 | 202800 | 3600 | 6.485% | 96 | 12280 | 217.953 |  | 78
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 12200 | 10784 | 10570 | 5956 | 11540 | 12082 | 12510 | 12108 | 14236 | 10960 | 14128 | 14485 | 11088 | 12636 | 14796 | 7036 | 15820 | 16424 | 17394 | 17007 | 14520 | 1916 | 11964 | 11672 | 12938 | 10732 | 10142 | 0 | 10722 | 0 | 2722 | 10250 | 11038 | 10894 | 13146 | 11114 | 11404 | 11460 | 8516 | 5.59 | 6.18 | 5.43 | 5.42 | 5.97 | 6.06 | 5.51 | 5.15 | 5.98 | 5.33 | 6.31 | 5.92 | 5.96 | 5.77 | 5.83 | 5.9 | 6.05 | 5.8 | 5.74 | 6.66 | 5.05 | 6.2 | 6.1 | 5.88 | 6 | 5.88 | 5.94 | 0 | 5.74 | 0 | 5.52 | 5.76 | 6.04 | 6.02 | 5.85 | 6.03 | 5.99 | 5.42 | 6.19 | 428910 | 5.5428 |  |  | 237798 | 2159 | 278152 | 2190 | 253699 | 1797 | 289297 | 1841 | 99600 | 0 | 80400 | 0 | 100800 | 0 | 138000 | 0 | 418800 | 0 | 2.357% | 96 | 47311 | 422.859 |  | 78
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 7048 | 9292 | 6462 | 6772 | 7822 | 2735 | 3420 | 6800 | 8864 | 6280 | 7464 | 8930 | 8852 | 8384 | 8346 | 6660 | 10152 | 6368 | 10280 | 9239 | 7800 | 6952 | 7522 | 6640 | 7248 | 6588 | 6354 | 0 | 6816 | 0 | 4938 | 5908 | 3472 | 6490 | 7198 | 6498 | 4518 | 6232 | 6148 | 4.76 | 4.88 | 4.8 | 4.65 | 4.27 | 5.04 | 5.09 | 4.76 | 4.82 | 4.8 | 4.93 | 4.74 | 4.55 | 4.63 | 4.57 | 4.63 | 4.82 | 4.84 | 4.83 | 5.1 | 4.76 | 4.34 | 4.24 | 4.48 | 4.55 | 4.34 | 4.26 | 0 | 3.79 | 0 | 4.37 | 4.3 | 4.48 | 4.78 | 4.74 | 4.25 | 4.44 | 4.59 | 5.03 | 257492 | 4.391 |  |  | 237846 | 2160 | 278199 | 2190 | 253740 | 1798 | 289370 | 1842 | 57600 | 1200 | 56400 | 0 | 49200 | 1200 | 87600 | 1200 | 250800 | 3600 | 2.599% | 96 | 16092 | 255.178 |  | 78
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 5220 | 3700 | 4436 | 884 | 4908 | 879 | 3033 | 4092 | 4356 | 5040 | 5292 | 4980 | 4190 | 5796 | 4270 | 4 | 5176 | 5752 | 5103 | 6702 | 5566 | 5420 | 4696 | 5078 | 4574 | 4378 | 4658 | 0 | 5344 | 0 | 4332 | 4113 | 972 | 5000 | 5438 | 5268 | 4266 | 4168 | 4477 | 4.2 | 4.48 | 4.15 | 4.23 | 4.09 | 4.41 | 4.2 | 4.38 | 4.25 | 4.12 | 4.51 | 4.56 | 4.66 | 4.58 | 4.72 | 4.72 | 4.38 | 4.61 | 4.79 | 4.5 | 4.21 | 4.3 | 4 | 4.35 | 3.93 | 4.2 | 4.18 | 0 | 4.02 | 0 | 4 | 4.03 | 4.05 | 4.25 | 4.25 | 3.98 | 4.05 | 4.03 | 3.89 | 161561 | 4.0579 |  |  | 237878 | 2161 | 278228 | 2191 | 253768 | 1798 | 289401 | 1843 | 38400 | 1200 | 34800 | 1200 | 33600 | 0 | 37200 | 1200 | 144000 | 3600 | 10.87% | 96 | 38147 | 165.1 |  | 78
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 1960 | 2540 | 1912 | 2284 | 1866 | 1710 | 1956 | 2084 | 1724 | 1448 | 1816 | 1786 | 1928 | 1700 | 1532 | 0 | 2102 | 2172 | 2177 | 2192 | 2750 | 2576 | 2268 | 1934 | 2976 | 1682 | 2572 | 0 | 2976 | 0 | 2664 | 2373 | 2528 | 3056 | 2968 | 3038 | 2406 | 2536 | 2971 | 3.1605 | 3.5608 | 3.1151 | 3.3498 | 3.3269 | 3.1994 | 3.1127 | 3.3075 | 3.3208 | 2.8659 | 3.1959 | 3.2102 | 3.4381 | 3.1364 | 3.1875 | 0 | 3.2244 | 3.1802 | 3.1785 | 3.0892 | 3.3397 | 3.33 | 3.1537 | 2.9716 | 3.1007 | 2.7795 | 3.1705 | 0 | 3.0811 | 0 | 3.1179 | 2.8482 | 2.909 | 3.1531 | 3.0024 | 3.149 | 3.0592 | 3.2 | 3.0888 | 81163 | 2.9132 |  |  | 237901 | 2162 | 278244 | 2192 | 253780 | 1799 | 289413 | 1844 | 27600 | 1200 | 19200 | 1200 | 14400 | 1200 | 14400 | 1200 | 75600 | 4800 | 6.854% | 96 | 5488 | 77.212 |  | 78
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 3220 | 3560 | 2644 | 3256 | 3041 | 3480 | 3428 | 3332 | 2736 | 3352 | 3412 | 2747 | 3356 | 3212 | 2079 | 0 | 3500 | 3472 | 3023 | 4229 | 3275 | 3188 | 2686 | 3736 | 2808 | 2780 | 2824 | 0 | 3354 | 0 | 2450 | 2918 | 3590 | 3136 | 3438 | 2096 | 2330 | 2992 | 2769 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 3.5 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 0 | 3.41 | 4.09 | 4.29 | 4.06 | 3.02 | 3.75 | 3.14 | 3.53 | 3.01 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 111449 | 3.3879 |  |  | 237924 | 2163 | 278263 | 2193 | 253803 | 1800 | 289435 | 1844 | 27600 | 1200 | 22800 | 1200 | 27600 | 1200 | 26400 | 0 | 104400 | 3600 | 6.325% | 96 | 233 | 106.019 |  | 78
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 5128 | 6280 | 5516 | 5776 | 5745 | 5410 | 4061 | 6316 | 4348 | 6676 | 7840 | 5758 | 6856 | 6352 | 5989 | 0 | 5120 | 7232 | 6608 | 9324 | 7629 | 7949 | 7329 | 7206 | 7220 | 7025 | 7807 | 0 | 7195 | 0 | 7223 | 5906 | 6153 | 7858 | 6181 | 6848 | 6891 | 6523 | 6822 | 4.61 | 4.84 | 4.6 | 4.69 | 3.8 | 4.82 | 4.78 | 4.8 | 4.38 | 4.71 | 5.09 | 4.76 | 4.95 | 4.85 | 4.66 | 0 | 4.6 | 5.05 | 4.8 | 5.43 | 4.22 | 4.18 | 4.05 | 4.57 | 3.71 | 4.35 | 4.49 | 0 | 4.12 | 0 | 3.89 | 4.17 | 4.26 | 4.16 | 4.38 | 4.16 | 3.8 | 4.04 | 4.04 | 236100 | 4.1233 |  |  | 237977 | 2163 | 278309 | 2193 | 253844 | 1801 | 289480 | 1845 | 63600 | 0 | 55200 | 0 | 49200 | 1200 | 54000 | 1200 | 222000 | 2400 | 5.972% | 96 | 5005 | 238.176 |  | 78
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 4316 | 3696 | 3986 | 2420 | 4046 | 5079 | 4140 | 4684 | 1744 | 4112 | 4460 | 4310 | 4204 | 4472 | 1155 | 0 | 5408 | 5168 | 5578 | 6118 | 4592 | 4328 | 4704 | 4450 | 3958 | 4076 | 3910 | 0 | 5106 | 0 | 3788 | 3435 | 3696 | 4568 | 5094 | 4896 | 3666 | 3596 | 4325 | 3.74 | 3.74 | 3.75 | 3.66 | 3.58 | 4.01 | 3.68 | 3.94 | 3.7 | 3.66 | 3.85 | 3.83 | 3.84 | 3.92 | 3.11 | 0 | 4.02 | 3.98 | 4.12 | 4.16 | 3.79 | 3.68 | 3.68 | 3.85 | 3.49 | 3.7 | 3.67 | 0 | 3.9 | 0 | 3.66 | 3.57 | 3.7 | 3.91 | 4.05 | 3.93 | 3.61 | 4.13 | 3.7 | 151284 | 3.4951 |  |  | 238011 | 2164 | 278337 | 2194 | 253876 | 1802 | 289511 | 1846 | 40800 | 1200 | 33600 | 1200 | 38400 | 1200 | 37200 | 1200 | 150000 | 4800 | 0.8487% | 96 | 4615 | 149.33 |  | 78
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 11140 | 7480 | 9628 | 2232 | 9056 | 7947 | 9460 | 9688 | 6482 | 3688 | 12444 | 9350 | 8102 | 10392 | 9464 | 1112 | 12968 | 12416 | 11728 | 12297 | 8994 | 8152 | 10714 | 10910 | 8828 | 9116 | 8908 | 0 | 9794 | 0 | 7086 | 7543 | 8482 | 8556 | 9864 | 10140 | 7702 | 7590 | 8333 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 327786 | 4.8151 |  |  | 238080 | 2165 | 278399 | 2195 | 253934 | 1802 | 289579 | 1846 | 82800 | 1200 | 74400 | 1200 | 69600 | 0 | 81600 | 0 | 308400 | 2400 | 5.914% | 96 | 91469 | 327.512 |  | 78
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 14750 | 13334 | 13120 | 12895 | 13940 | 14632 | 15060 | 14658 | 14103 | 13510 | 16678 | 14261 | 11088 | 10532 | 14296 | 8036 | 15320 | 16124 | 16394 | 16007 | 16920 | 16264 | 14364 | 14072 | 15618 | 13132 | 12542 | 0 | 13122 | 0 | 12891 | 12930 | 13718 | 13574 | 15826 | 13794 | 14084 | 14140 | 14001 | 5.59 | 6.18 | 5.43 | 5.42 | 5.97 | 6.06 | 5.51 | 5.15 | 5.98 | 5.33 | 6.31 | 5.92 | 5.96 | 5.77 | 5.83 | 5.9 | 6.05 | 5.8 | 5.74 | 6.66 | 6.01 | 6.2 | 6.1 | 5.88 | 6 | 5.88 | 5.94 | 0 | 5.74 | 0 | 5.52 | 5.76 | 6.04 | 6.02 | 5.85 | 6.03 | 5.99 | 5.42 | 6.19 | 519730 | 5.5674 |  |  | 238197 | 2165 | 278494 | 2195 | 254041 | 1803 | 289688 | 1847 | 140400 | 0 | 114000 | 0 | 128400 | 1200 | 130800 | 1200 | 513600 | 2400 | 1.179% | 96 | 97193 | 511 |  | 78 | No scada available server OS failed
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 14293 | 14793 | 14285 | 14379 | 13985 | 14594 | 14284 | 14594 | 14159 | 14743 | 14852 | 14273 | 14184 | 14221 | 14457 | 9475 | 14263 | 14282 | 14291 | 14296 | 14704 | 14790 | 14721 | 14894 | 12720 | 14974 | 14802 | 0 | 14964 | 0 | 12790 | 12748 | 12742 | 12973 | 12785 | 12790 | 12863 | 12830 | 12795 | 5.83 | 5.9 | 6.05 | 5.8 | 5.74 | 6.21 | 6.01 | 6.2 | 6.1 | 6.1 | 5.88 | 6 | 5.88 | 5.94 | 6.2 | 5.74 | 6.23 | 5.52 | 5.76 | 6.04 | 6.02 | 5.85 | 6.03 | 5.42 | 6.19 | 5.59 | 6.01 | 0 | 5.42 | 0 | 6 | 5.51 | 5.15 | 5.98 | 5.33 | 6.1 | 5.92 | 5.92 | 5.9 | 514588 | 5.5762 |  |  | 238303 | 2165 | 278592 | 2195 | 254150 | 1803 | 289801 | 1847 | 127200 | 0 | 117600 | 0 | 130800 | 0 | 135600 | 0 | 511200 | 0 | 0.6584% | 96 | 79804 | 514 |  | 78 | No scada available server OS failed
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 14925 | 15604 | 15395 | 15942 | 10932 | 15953 | 15693 | 15831 | 12593 | 15603 | 15493 | 12862 | 12749 | 12852 | 12784 | 8839 | 12860 | 10527 | 12949 | 12973 | 12692 | 12639 | 11302 | 12842 | 10937 | 12706 | 12852 | 0 | 12793 | 0 | 11295 | 10183 | 10962 | 10981 | 10939 | 10926 | 10969 | 10210 | 10928 | 5.63 | 6.04 | 5.55 | 5.6 | 6.19 | 6.25 | 5.75 | 5.53 | 5.55 | 5.54 | 5.96 | 5.74 | 5.9 | 5.75 | 5.91 | 5.82 | 5.86 | 6.15 | 6.47 | 6.22 | 5.08 | 6.26 | 5.87 | 5.93 | 5.43 | 5.57 | 5.63 | 0 | 5.51 | 0 | 5.16 | 5.45 | 5.48 | 5.59 | 5.63 | 5.54 | 5.55 | 5.62 | 5.36 | 469515 | 5.4377 |  |  | 238392 | 2166 | 278675 | 2195 | 254265 | 1803 | 289902 | 1847 | 106800 | 1200 | 99600 | 0 | 138000 | 0 | 121200 | 0 | 465600 | 1200 | 0.8338% | 96 | 83785 | 469.51 |  | 78 | No scada available server OS failed
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 9219 | 9742 | 9769 | 9731 | 7948 | 9727 | 9768 | 9759 | 8864 | 9742 | 9749 | 8846 | 8790 | 8732 | 8759 | 6190 | 8742 | 8756 | 8796 | 8789 | 7939 | 8268 | 8179 | 8264 | 9214 | 8280 | 8264 | 0 | 8295 | 0 | 9627 | 9637 | 9695 | 9635 | 9637 | 9678 | 9629 | 9317 | 9687 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 333663 | 4.8151 |  |  | 238471 | 2166 | 278729 | 2196 | 254337 | 1803 | 289973 | 1847 | 94800 | 0 | 64800 | 1200 | 86400 | 0 | 85200 | 0 | 331200 | 1200 | 0.7382% | 96 | 38289 | 333.66 |  | 78 | No scada available server OS failed
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 17456 | 18268 | 18198 | 18467 | 14740 | 18104 | 18132 | 18105 | 17283 | 16001 | 16100 | 17426 | 17421 | 17056 | 17528 | 8943 | 17354 | 17965 | 17954 | 17695 | 14846 | 14749 | 14769 | 14754 | 15738 | 14803 | 14824 | 0 | 14795 | 0 | 15796 | 15740 | 15791 | 15846 | 15846 | 15825 | 15742 | 15962 | 15847 | 7.28 | 7.74 | 7.38 | 7.5 | 6.95 | 6.64 | 0 | 7.59 | 7.79 | 7.37 | 7.73 | 7.52 | 7.72 | 7.67 | 7.75 | 7.66 | 8.38 | 7.44 | 8.44 | 7.02 | 6.9 | 7.2 | 7.24 | 7.4 | 7.39 | 7.05 | 6.74 | 0 | 7.37 | 0 | 6.79 | 6.65 | 6.54 | 7.02 | 7.65 | 7.66 | 6.74 | 6.53 | 7.19 | 601869 | 6.7597 |  |  | 238602 | 2166 | 278827 | 2196 | 254472 | 1803 | 290108 | 1848 | 157200 | 0 | 117600 | 0 | 162000 | 0 | 162000 | 1200 | 598800 | 1200 | 0.5099% | 96 | 33860 | 601.869 |  | 78 | No scada available server OS failed
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 14297 | 14921 | 14963 | 14367 | 15592 | 14874 | 14853 | 14869 | 15102 | 14848 | 14863 | 15107 | 15111 | 15123 | 15143 | 9457 | 15132 | 15164 | 15179 | 15189 | 15853 | 15895 | 15867 | 15874 | 12759 | 15842 | 15896 | 0 | 15862 | 0 | 12796 | 12706 | 12759 | 12749 | 12796 | 12793 | 12795 | 10236 | 12705 | 6.04 | 6.55 | 6.01 | 5.72 | 6.71 | 6.27 | 6 | 5.79 | 6 | 6.65 | 6.61 | 6.36 | 6.31 | 6.18 | 6.29 | 6.5 | 6.63 | 6.48 | 6.75 | 6.78 | 6.72 | 6.39 | 5.76 | 5.9 | 6.3 | 5.66 | 5.5 | 5.76 | 5.28 | 0 | 5.85 | 5.65 | 5.63 | 5.65 | 5.94 | 5.56 | 5.81 | 5.84 | 5.94 | 530337 | 5.9428 |  |  | 238704 | 2167 | 278932 | 2197 | 254583 | 1804 | 290229 | 1848 | 122400 | 1200 | 126000 | 1200 | 133200 | 1200 | 145200 | 0 | 526800 | 3600 | 0.6669% | 96 | 145066 | 530.337 |  | 78 | No scada available server OS failed
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 16756 | 16731 | 16721 | 16734 | 12150 | 16742 | 16732 | 16749 | 16196 | 16742 | 16782 | 16187 | 16186 | 16164 | 16184 | 9321 | 16189 | 16147 | 16197 | 16169 | 12169 | 12189 | 12190 | 12185 | 14915 | 12169 | 12185 | 0 | 12168 | 0 | 14925 | 14952 | 14958 | 14952 | 14984 | 14984 | 14952 | 14963 | 14962 | 5.59 | 6.18 | 5.43 | 5.42 | 5.97 | 6.06 | 5.51 | 5.15 | 5.98 | 5.33 | 6.31 | 5.92 | 5.96 | 5.77 | 5.83 | 5.9 | 6.05 | 5.8 | 5.74 | 6.66 | 6.01 | 6.2 | 6.1 | 5.88 | 6 | 5.88 | 5.94 | 0 | 5.74 | 0 | 5.52 | 5.76 | 6.04 | 6.02 | 5.85 | 6.03 | 5.99 | 5.42 | 6.19 | 552581 | 5.5674 |  |  | 238828 | 2167 | 279013 | 2197 | 254708 | 1804 | 290358 | 1848 | 148800 | 0 | 97200 | 0 | 150000 | 0 | 154800 | 0 | 550800 | 0 | 0.3223% | 96 | 160779 | 552.581 |  | 78 | No scada available server OS failed
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 15153 | 15183 | 16583 | 16584 | 13650 | 16573 | 15190 | 16587 | 13458 | 16784 | 16596 | 14923 | 14937 | 14976 | 14979 | 9674 | 14979 | 14943 | 14943 | 14964 | 13687 | 13696 | 13674 | 13653 | 12556 | 13687 | 13659 | 0 | 13653 | 0 | 12562 | 12547 | 12589 | 12538 | 12565 | 12567 | 12564 | 12032 | 12574 | 5.83 | 5.9 | 6.05 | 5.8 | 5.74 | 6.21 | 6.01 | 6.2 | 6.1 | 6.1 | 5.88 | 6 | 5.88 | 5.94 | 6.2 | 5.74 | 6.23 | 5.52 | 5.76 | 6.04 | 6.02 | 5.85 | 6.03 | 5.42 | 6.19 | 5.59 | 6.01 | 0 | 5.42 | 0 | 6 | 5.51 | 5.15 | 5.98 | 5.33 | 6.1 | 5.92 | 5.92 | 5.9 | 522462 | 5.5762 |  |  | 238932 | 2167 | 279104 | 2197 | 254829 | 1804 | 290477 | 1848 | 124800 | 0 | 109200 | 0 | 145200 | 0 | 142800 | 0 | 522000 | 0 | 0.08843% | 96 | 182469 | 522.462 |  | 78 | No scada available server OS failed
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 9986 | 9964 | 9942 | 9960 | 8859 | 9936 | 9962 | 9967 | 8168 | 9997 | 9989 | 8164 | 8196 | 8164 | 8153 | 5639 | 8169 | 8176 | 8148 | 8243 | 8895 | 8858 | 8853 | 8857 | 8106 | 8895 | 8824 | 0 | 8852 | 0 | 8165 | 8169 | 8158 | 7963 | 7584 | 8139 | 8147 | 8163 | 8189 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 320599 | 4.8151 |  |  | 238998 | 2167 | 279163 | 2197 | 254903 | 1804 | 290542 | 1849 | 79200 | 0 | 70800 | 0 | 88800 | 0 | 78000 | 1200 | 316800 | 1200 | 1.185% | 96 | 88227 | 320.59 |  | 78 | No scada available server OS failed
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 12321 | 12334 | 12353 | 12327 | 10590 | 12358 | 12364 | 12387 | 11389 | 12389 | 12393 | 11358 | 10948 | 11378 | 11385 | 8429 | 11364 | 11398 | 11428 | 11463 | 10569 | 10595 | 8792 | 10563 | 10352 | 10585 | 10567 | 0 | 10589 | 0 | 10274 | 9590 | 10290 | 10363 | 10368 | 10374 | 10387 | 10338 | 10374 | 4.73 | 5.25 | 4.97 | 4.56 | 4.53 | 5.13 | 4.74 | 4.54 | 5.04 | 4.65 | 5.08 | 5.09 | 5.15 | 6.01 | 4.79 | 4.63 | 4.4 | 4.69 | 5.17 | 5.05 | 4.8 | 4.95 | 4.57 | 4.87 | 4.67 | 4.45 | 4.48 | 0 | 4.42 | 0 | 4.25 | 4.37 | 4.48 | 4.63 | 4.57 | 4.44 | 4.53 | 4.53 | 4.67 | 407326 | 4.5097 |  |  | 239083 | 2168 | 279232 | 2197 | 254995 | 1805 | 290634 | 1849 | 102000 | 1200 | 82800 | 0 | 110400 | 1200 | 110400 | 0 | 405600 | 2400 | 0.4237% | 96 | 87932 | 407.32 |  | 78 | No scada available server OS failed
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 20358 | 20376 | 20321 | 19585 | 20876 | 20387 | 20341 | 20365 | 21187 | 20369 | 20385 | 21179 | 19457 | 21178 | 21190 | 21179 | 21187 | 21185 | 21189 | 21254 | 20854 | 20862 | 20832 | 20858 | 19245 | 20835 | 20863 | 0 | 20851 | 0 | 19254 | 19276 | 19267 | 19259 | 19274 | 19248 | 19256 | 19289 | 19228 | 7.13 | 7.22 | 7.2 | 7.2 | 6.86 | 6.84 | 7.63 | 7.38 | 7.33 | 7.21 | 7.65 | 7.19 | 7.34 | 7.41 | 7.49 | 7.4 | 7.65 | 7.28 | 8.03 | 7.54 | 6.5 | 7.13 | 7.11 | 7.2 | 6.69 | 6.89 | 6.85 | 0 | 7.3 | 0 | 6.26 | 6.56 | 6.37 | 6.77 | 7.26 | 7.17 | 6.41 | 6.12 | 6.55 | 752099 | 6.721 |  |  | 239243 | 2168 | 279371 | 2197 | 255147 | 1805 | 290809 | 1849 | 192000 | 0 | 166800 | 0 | 182400 | 0 | 210000 | 0 | 751200 | 0 | 0.1195% | 96 | 191708 | 752.09 |  | 78 | No scada available server OS failed
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 8279 | 8290 | 8289 | 8278 | 8013 | 8268 | 8242 | 8281 | 7742 | 8284 | 8295 | 7748 | 7732 | 7753 | 7759 | 6349 | 7749 | 7736 | 7782 | 7793 | 8051 | 8057 | 8003 | 8042 | 8284 | 8073 | 8034 | 0 | 8055 | 0 | 8241 | 8417 | 8486 | 8494 | 8496 | 8452 | 8467 | 8463 | 8257 | 5.8621 | 6.3056 | 5.2877 | 5.3705 | 5.0465 | 5.8957 | 5.8957 | 5.8117 | 6.2648 | 4.8664 | 5.6272 | 5.7042 | 5.5212 | 5.7344 | 6.0185 | 5.5628 | 6.2912 | 5.9452 | 6.1094 | 6.4611 | 5.9728 | 4.9143 | 5.1145 | 5.336 | 5.0755 | 5.3435 | 5.0553 | 0 | 5 | 0 | 4.943 | 4.9765 | 5.2576 | 5.6703 | 5.5863 | 5.4673 | 5.2684 | 5.2848 | 5.2838 | 299034 | 5.2598 |  |  | 239312 | 2169 | 279424 | 2198 | 255208 | 1805 | 290869 | 1849 | 82800 | 1200 | 63600 | 1200 | 73200 | 0 | 72000 | 0 | 291600 | 2400 | 2.486% | 95 | 78346 | 299.03 |  | 78 | No scada available server OS failed
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 4363 | 4335 | 4367 | 4342 | 6344 | 4051 | 4375 | 4365 | 6342 | 4379 | 4395 | 6356 | 5538 | 6342 | 6367 | 6321 | 6376 | 6372 | 6398 | 6392 | 6356 | 5989 | 6347 | 6375 | 6450 | 6358 | 6332 | 0 | 6349 | 0 | 5579 | 5595 | 6487 | 6431 | 6458 | 6435 | 6479 | 6482 | 6474 | 4.58 | 4.46 | 3.97 | 4.15 | 3.78 | 4.38 | 4.4 | 4.13 | 4.08 | 3.95 | 4.01 | 4.04 | 3.98 | 3.84 | 3.92 | 3.95 | 4.15 | 4.01 | 3.99 | 4.01 | 3.76 | 3.87 | 3.95 | 4.26 | 4.2 | 4.22 | 4.21 | 0 | 5.44 | 0 | 4.17 | 4.15 | 4.32 | 4.55 | 6.32 | 4.45 | 4.87 | 4.31 | 5.39 | 215096 | 4.0569 |  |  | 239364 | 2169 | 279466 | 2198 | 255240 | 1805 | 290921 | 1850 | 62400 | 0 | 50400 | 0 | 38400 | 0 | 62400 | 1200 | 213600 | 1200 | 0.6955% | 96 | 29652 | 215.09 |  | 78 | No scada available server OS failed
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 3742 | 3758 | 3745 | 3742 | 3153 | 3164 | 3746 | 3789 | 3923 | 3754 | 3784 | 3942 | 3956 | 3932 | 3951 | 3956 | 3973 | 3957 | 3521 | 3989 | 3158 | 3021 | 3153 | 2680 | 3102 | 3157 | 3178 | 0 | 3167 | 0 | 2859 | 3123 | 3124 | 3154 | 3157 | 3185 | 3136 | 3174 | 3162 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 3.5 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 3.99 | 3.41 | 4.09 | 4.29 | 4.06 | 3.02 | 3.75 | 3.14 | 3.53 | 3.01 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 128167 | 3.4903 |  |  | 239389 | 2170 | 279486 | 2199 | 255268 | 1806 | 290953 | 1851 | 30000 | 1200 | 24000 | 1200 | 33600 | 1200 | 38400 | 1200 | 126000 | 4800 | 1.691% | 90 | 5922 | 128.16 |  | 78 | No scada available server OS failed
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 5021 | 5279 | 5297 | 5278 | 5423 | 5289 | 5267 | 5243 | 4434 | 5276 | 5292 | 4432 | 4452 | 4457 | 4432 | 4475 | 4478 | 4472 | 4489 | 4498 | 5490 | 5289 | 5489 | 5467 | 6041 | 5472 | 5484 | 0 | 5479 | 0 | 7158 | 7169 | 7184 | 7167 | 7172 | 7182 | 7156 | 6258 | 6021 | 4.33 | 4.54 | 4.49 | 4.18 | 4.27 | 4.89 | 4.38 | 4.32 | 4.44 | 4.47 | 4.89 | 4.48 | 4.5 | 4.5 | 4.37 | 4.5 | 4.41 | 4.67 | 5.98 | 5.16 | 4.2 | 4.72 | 4.05 | 4.62 | 4.45 | 4.26 | 4.37 | 0 | 4.93 | 0 | 4.07 | 4.82 | 4.43 | 4.27 | 4.59 | 4.5 | 4.33 | 4.5 | 4.6 | 203962 | 4.2944 |  |  | 239445 | 2170 | 279521 | 2200 | 255306 | 1806 | 290989 | 1851 | 67200 | 0 | 42000 | 1200 | 45600 | 0 | 43200 | 0 | 198000 | 1200 | 2.923% | 96 | 7484 | 203.96 |  | 78 | No scada available server OS failed
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 7021 | 7056 | 7041 | 6563 | 6587 | 7053 | 7069 | 6690 | 6032 | 7059 | 7089 | 6063 | 6321 | 6345 | 6356 | 6332 | 6341 | 6345 | 6347 | 6389 | 6583 | 6021 | 6545 | 6564 | 6832 | 6527 | 6544 | 0 | 6575 | 0 | 6853 | 6842 | 6021 | 6829 | 6839 | 6869 | 6882 | 5587 | 6849 | 4.61 | 4.84 | 4.6 | 4.69 | 3.8 | 4.82 | 4.78 | 4.8 | 4.38 | 4.71 | 5.09 | 4.76 | 4.95 | 4.85 | 4.66 | 4.01 | 4.6 | 5.05 | 4.8 | 5.43 | 4.22 | 4.18 | 4.05 | 4.57 | 3.71 | 4.35 | 4.49 | 0 | 4.12 | 0 | 3.89 | 4.17 | 4.26 | 4.16 | 4.38 | 4.16 | 3.8 | 4.04 | 4.04 | 243861 | 4.2262 |  |  | 239500 | 2171 | 279564 | 2200 | 255358 | 1807 | 291041 | 1852 | 66000 | 1200 | 51600 | 0 | 62400 | 1200 | 62400 | 1200 | 242400 | 3600 | 0.5991% | 96 | 6052 | 243.86 |  | 78 | No scada available server OS failed
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 10931 | 10952 | 10932 | 10921 | 8845 | 10210 | 10953 | 10959 | 11852 | 10944 | 10965 | 11856 | 11862 | 11832 | 11842 | 11857 | 11843 | 11853 | 11869 | 11897 | 8363 | 8563 | 8856 | 8842 | 9321 | 8858 | 8839 | 0 | 8849 | 0 | 9323 | 9342 | 9354 | 9344 | 9063 | 9340 | 9356 | 9376 | 9365 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 379529 | 4.8151 |  |  | 239577 | 2171 | 279622 | 2200 | 255439 | 1807 | 291139 | 1852 | 92400 | 0 | 69600 | 0 | 97200 | 0 | 117600 | 0 | 376800 | 0 | 0.719% | 96 | 53692 | 379.52 |  | 78 | No scada available server OS failed
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 5801 | 5823 | 5812 | 5824 | 4832 | 5849 | 5365 | 5859 | 5634 | 5864 | 5879 | 5641 | 5623 | 5321 | 5642 | 5648 | 5645 | 5649 | 5672 | 5679 | 4845 | 4265 | 4823 | 4854 | 4532 | 4210 | 4867 | 0 | 4879 | 0 | 4565 | 4521 | 4526 | 4556 | 4021 | 4537 | 4539 | 4567 | 3943 | 4.23 | 4.33 | 4.21 | 4.28 | 4.21 | 4.48 | 4.23 | 4.35 | 4.35 | 4.18 | 4.62 | 4.31 | 4.42 | 4.46 | 4.3 | 4.5 | 5.8 | 4.68 | 4.85 | 4.97 | 4.72 | 4.43 | 4.49 | 4.62 | 4.33 | 4.36 | 4.24 | 0 | 4.44 | 0 | 4.26 | 4.44 | 4.44 | 4.44 | 4.48 | 4.54 | 4.25 | 4.41 | 4.59 | 190112 | 4.2369 |  |  | 239613 | 2172 | 279653 | 2201 | 255482 | 1808 | 291185 | 1853 | 43200 | 1200 | 37200 | 1200 | 51600 | 1200 | 55200 | 1200 | 187200 | 4800 | 1.532% | 96 | 17621 | 190.11 |  | 78 | No scada available server OS failed
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 8035 | 8042 | 8051 | 7521 | 6672 | 8044 | 8020 | 8047 | 7821 | 8053 | 8059 | 7844 | 7856 | 7842 | 7823 | 7834 | 7818 | 7820 | 7853 | 7280 | 6632 | 6640 | 6621 | 6644 | 7021 | 6635 | 6654 | 0 | 5521 | 0 | 7034 | 7056 | 7045 | 7062 | 6760 | 7052 | 7044 | 7041 | 7047 | 4.58 | 4.46 | 3.97 | 4.15 | 3.78 | 4.38 | 4.4 | 4.13 | 4.08 | 3.95 | 4.01 | 4.04 | 3.98 | 3.84 | 3.92 | 3.95 | 4.15 | 4.01 | 3.99 | 4.01 | 3.76 | 3.87 | 3.95 | 4.26 | 4.2 | 4.22 | 4.21 | 0 | 5.44 | 0 | 4.17 | 4.15 | 4.32 | 4.55 | 6.32 | 4.45 | 4.87 | 4.31 | 5.39 | 271844 | 4.0569 |  |  | 239671 | 2172 | 279696 | 2201 | 255541 | 1808 | 291249 | 1853 | 69600 | 0 | 51600 | 0 | 70800 | 0 | 76800 | 0 | 268800 | 0 | 1.12% | 96 | 49821 | 271.84 |  | 78 | No scada available server OS failed
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 6459 | 6487 | 6443 | 6473 | 6742 | 6452 | 6401 | 6459 | 8098 | 6453 | 6467 | 8073 | 8068 | 8079 | 8082 | 8061 | 8013 | 8047 | 8056 | 8067 | 6755 | 5210 | 6776 | 6785 | 8124 | 6778 | 5567 | 0 | 6792 | 0 | 8135 | 8122 | 8132 | 8184 | 8157 | 8162 | 8151 | 8121 | 8139 | 4.58 | 4.46 | 3.97 | 4.15 | 3.78 | 4.38 | 4.4 | 4.13 | 4.08 | 3.95 | 4.01 | 4.04 | 3.98 | 3.84 | 3.92 | 3.95 | 4.15 | 4.01 | 3.99 | 4.01 | 3.76 | 3.87 | 3.95 | 4.26 | 4.2 | 4.22 | 4.21 | 0 | 5.44 | 0 | 4.17 | 4.15 | 4.32 | 4.55 | 6.32 | 4.45 | 4.87 | 4.31 | 5.39 | 271570 | 4.0569 |  |  | 239738 | 2173 | 279738 | 2202 | 255589 | 1809 | 291316 | 1854 | 80400 | 1200 | 50400 | 1200 | 57600 | 1200 | 80400 | 1200 | 268800 | 4800 | 1.02% | 96 | 39915 | 271.54 |  | 78 | No scada available server OS failed
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 16089 | 16078 | 16042 | 14467 | 15425 | 16059 | 16042 | 16072 | 17489 | 16079 | 14989 | 17467 | 17482 | 17421 | 17429 | 17435 | 17445 | 17466 | 17487 | 17501 | 15456 | 12641 | 13935 | 15467 | 15921 | 15432 | 12782 | 0 | 15469 | 0 | 15934 | 15954 | 14263 | 15967 | 15945 | 15932 | 15957 | 15955 | 15968 | 6.04 | 6.55 | 6.01 | 5.72 | 6.71 | 6.27 | 6 | 5.79 | 6 | 6.65 | 6.61 | 6.36 | 6.31 | 6.18 | 6.29 | 6.5 | 6.63 | 6.48 | 6.75 | 6.78 | 6.72 | 6.39 | 5.76 | 5.9 | 6.3 | 5.66 | 5.5 | 5.76 | 5.28 | 0 | 5.85 | 5.65 | 5.63 | 5.65 | 5.94 | 5.56 | 5.81 | 5.84 | 5.94 | 590942 | 5.9428 |  |  | 239869 | 2173 | 279835 | 2202 | 255707 | 1809 | 291461 | 1854 | 157200 | 0 | 116400 | 0 | 141600 | 0 | 174000 | 0 | 589200 | 0 | 0.2948% | 96 | 129769 | 590.94 |  | 78 | No scada available server OS failed
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 16821 | 16852 | 16832 | 16825 | 15121 | 16832 | 16844 | 16842 | 16583 | 16845 | 16858 | 16574 | 16587 | 16537 | 16573 | 16001 | 16529 | 16542 | 16584 | 16578 | 15124 | 13052 | 15142 | 15152 | 15528 | 15562 | 15526 | 0 | 13531 | 0 | 15532 | 13574 | 15535 | 15534 | 15565 | 15546 | 15537 | 15542 | 15543 | 5.58 | 6.55 | 5.67 | 5.72 | 6.71 | 6.27 | 6 | 5.79 | 6 | 6.65 | 5.98 | 6.36 | 6.31 | 5.42 | 6.29 | 6.5 | 6.63 | 6.48 | 6.75 | 6.78 | 6.72 | 6.39 | 5.76 | 5.9 | 6.3 | 5.66 | 5.5 | 5.76 | 5.28 | 0 | 5.85 | 5.65 | 5.63 | 5.65 | 5.94 | 5.56 | 5.81 | 5.84 | 5.94 | 588285 | 5.8867 |  |  | 239996 | 2173 | 279932 | 2202 | 255833 | 1809 | 291598 | 1854 | 152400 | 0 | 116400 | 0 | 151200 | 0 | 164400 | 0 | 584400 | 0 | 0.6604% | 96 | 139458 | 588.28 |  | 78 | No scada available server OS failed
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 14538 | 14554 | 14576 | 14574 | 12967 | 14573 | 11052 | 14576 | 13721 | 14621 | 14678 | 13753 | 14749 | 14756 | 14732 | 14765 | 14768 | 12952 | 14789 | 14799 | 12888 | 12863 | 12877 | 12889 | 11834 | 11750 | 12844 | 0 | 12856 | 0 | 11453 | 11842 | 11849 | 11832 | 11854 | 11844 | 11824 | 11856 | 11845 | 4.73 | 5.25 | 4.97 | 4.56 | 4.53 | 5.13 | 4.74 | 4.54 | 5.04 | 4.65 | 5.08 | 5.09 | 5.15 | 6.01 | 4.79 | 4.63 | 4.4 | 4.69 | 5.17 | 5.05 | 4.8 | 4.95 | 4.57 | 4.87 | 4.67 | 4.45 | 4.48 | 0 | 4.42 | 0 | 4.25 | 4.37 | 4.48 | 4.63 | 4.57 | 4.44 | 4.53 | 4.53 | 4.67 | 491493 | 4.5097 |  |  | 240094 | 2173 | 280017 | 2202 | 255927 | 1809 | 291712 | 1854 | 117600 | 0 | 102000 | 0 | 112800 | 0 | 136800 | 0 | 469200 | 0 | 4.536% | 96 | 152479 | 491.49 |  | 78 | No scada available server OS failed
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 17432 | 17421 | 17434 | 17442 | 16349 | 17435 | 17425 | 17443 | 17731 | 17456 | 17489 | 17727 | 18239 | 18211 | 18234 | 18242 | 18222 | 18234 | 17248 | 18221 | 16595 | 16548 | 16531 | 16523 | 14845 | 16543 | 16562 | 0 | 16569 | 0 | 14321 | 14856 | 14842 | 13521 | 14847 | 14834 | 14841 | 14865 | 14852 | 7.28 | 7.74 | 7.38 | 7.5 | 6.95 | 6.64 | 6.2 | 7.59 | 7.79 | 7.37 | 7.73 | 7.52 | 7.72 | 7.67 | 7.75 | 7.66 | 8.38 | 7.44 | 8.44 | 7.02 | 6.9 | 7.2 | 7.24 | 7.4 | 7.39 | 7.05 | 6.74 | 0 | 7.37 | 0 | 6.79 | 6.65 | 6.54 | 7.02 | 7.65 | 7.66 | 6.74 | 6.53 | 7.19 | 616130 | 6.9187 |  |  | 240216 | 2173 | 280127 | 2203 | 256057 | 1809 | 291862 | 1854 | 146400 | 0 | 132000 | 1200 | 156000 | 0 | 180000 | 0 | 614400 | 1200 | 0.2808% | 96 | 208104 | 616.13 |  | 78 | No scada available server OS failed
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 10932 | 10952 | 10976 | 10967 | 11167 | 10974 | 10953 | 10963 | 13230 | 10963 | 10977 | 13571 | 13578 | 13064 | 13853 | 13852 | 13674 | 13569 | 13863 | 13761 | 11153 | 11012 | 11145 | 11147 | 5192 | 11151 | 11152 | 0 | 11164 | 0 | 8752 | 8732 | 8758 | 8787 | 5147 | 8759 | 8742 | 8795 | 8749 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 404176 | 4.8151 |  |  | 240282 | 2174 | 280201 | 2203 | 256139 | 1810 | 291971 | 1855 | 79200 | 1200 | 88800 | 0 | 98400 | 1200 | 130800 | 1200 | 397200 | 3600 | 1.726% | 96 | 7564 | 404.17 |  | 78 | No scada available server OS failed
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 6172 | 8301 | 8352 | 8341 | 6500 | 8346 | 8346 | 8323 | 8289 | 8356 | 8367 | 8021 | 8240 | 8026 | 8256 | 8254 | 8562 | 8267 | 8287 | 8299 | 6521 | 6524 | 7721 | 7752 | 0 | 7767 | 7756 | 0 | 7741 | 0 | 5832 | 5847 | 5831 | 5867 | 5844 | 5821 | 5853 | 5849 | 5885 | 4.58 | 4.46 | 3.97 | 4.15 | 3.78 | 4.38 | 4.4 | 4.13 | 4.08 | 3.95 | 4.01 | 4.04 | 3.98 | 3.84 | 3.92 | 3.95 | 4.15 | 4.01 | 3.99 | 4.01 | 3.76 | 3.87 | 3.95 | 4.26 | 4.2 | 4.22 | 4.21 | 0 | 5.44 | 0 | 4.17 | 4.15 | 4.32 | 4.55 | 6.32 | 4.45 | 4.87 | 4.31 | 5.39 | 266316 | 4.0569 |  |  | 240325 | 2174 | 280249 | 2203 | 256199 | 1810 | 292039 | 1855 | 51600 | 0 | 57600 | 0 | 72000 | 0 | 81600 | 0 | 262800 | 0 | 1.32% | 96 | 53090 | 266.31 |  | 78 | No scada available server OS failed
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 9263 | 9255 | 9241 | 9245 | 8301 | 9247 | 9251 | 9053 | 9673 | 9249 | 9287 | 9681 | 9657 | 9652 | 9645 | 8562 | 9644 | 9640 | 8361 | 9688 | 8321 | 7531 | 7542 | 8367 | 3521 | 8356 | 8376 | 0 | 8364 | 0 | 6972 | 6964 | 6977 | 6952 | 6953 | 5128 | 6945 | 6983 | 6961 | 4.76 | 4.88 | 4.8 | 4.65 | 4.27 | 5.04 | 5.09 | 4.76 | 4.82 | 4.8 | 4.93 | 4.74 | 4.55 | 4.63 | 4.57 | 4.63 | 4.82 | 4.84 | 4.83 | 5.1 | 4.76 | 4.34 | 4.24 | 4.48 | 4.55 | 4.34 | 4.26 | 0 | 3.79 | 0 | 4.37 | 4.3 | 4.48 | 4.78 | 4.74 | 4.25 | 4.44 | 4.59 | 5.03 | 306808 | 4.391 |  |  | 240378 | 2175 | 280303 | 2204 | 256268 | 1811 | 292117 | 1856 | 63600 | 1200 | 64800 | 1200 | 82800 | 1200 | 93600 | 1200 | 304800 | 4800 | 0.6545% | 96 | 42452 | 306.8 |  | 78 | No scada available server OS failed
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 10973 | 12685 | 12694 | 11052 | 8461 | 11205 | 10989 | 12648 | 14478 | 12686 | 12734 | 14484 | 14476 | 14467 | 14489 | 13963 | 14472 | 13735 | 14535 | 14599 | 4731 | 4538 | 4634 | 4587 | 4742 | 9472 | 9453 | 0 | 4967 | 0 | 4739 | 4790 | 4021 | 4783 | 4762 | 3904 | 3632 | 6794 | 6749 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 351123 | 4.8151 |  |  | 240415 | 2175 | 280338 | 2204 | 256357 | 1811 | 292236 | 1856 | 44400 | 0 | 42000 | 0 | 106800 | 0 | 142800 | 0 | 336000 | 0 | 4.307% | 96 | 45221 | 351.12 |  | 78 | No scada available server OS failed
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 8876 | 8856 | 8467 | 8849 | 7901 | 8860 | 8872 | 8893 | 10832 | 8401 | 8890 | 10821 | 10846 | 10849 | 10850 | 10842 | 10856 | 10847 | 10879 | 10876 | 7949 | 7251 | 7934 | 7373 | 6841 | 7921 | 7369 | 0 | 7942 | 0 | 6837 | 6845 | 6867 | 6287 | 6856 | 5639 | 6859 | 6263 | 6857 | 4.58 | 4.46 | 3.97 | 4.15 | 3.78 | 4.38 | 4.4 | 4.13 | 4.08 | 3.95 | 4.01 | 4.04 | 3.98 | 3.84 | 3.92 | 3.95 | 4.15 | 4.01 | 3.99 | 4.01 | 3.76 | 3.87 | 3.95 | 4.26 | 4.2 | 4.22 | 4.21 | 0 | 5.44 | 0 | 4.17 | 4.15 | 4.32 | 4.55 | 6.32 | 4.45 | 4.87 | 4.31 | 5.39 | 315253 | 4.0569 |  |  | 240469 | 2175 | 280388 | 2204 | 256422 | 1811 | 292326 | 1856 | 64800 | 0 | 60000 | 0 | 78000 | 0 | 108000 | 0 | 310800 | 0 | 1.413% | 96 | 53455 | 315.25 |  | 78 | No scada available server OS failed
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 4021 | 4032 | 3562 | 3583 | 4562 | 3521 | 4024 | 3536 | 3832 | 3543 | 4026 | 4056 | 4059 | 4062 | 4053 | 4059 | 4055 | 4062 | 4067 | 4072 | 4531 | 4564 | 4521 | 4562 | 3587 | 4537 | 4526 | 0 | 4555 | 0 | 3579 | 3593 | 3061 | 3582 | 3578 | 3072 | 3569 | 3056 | 3566 | 4.0641 | 4.0593 | 4.0183 | 3.9908 | 3.9708 | 4.1533 | 4.1533 | 4.3953 | 4.0946 | 4.1891 | 4.5516 | 4.0448 | 4.0977 | 4.1514 | 4.115 | 4.1475 | 4.3757 | 4.3612 | 4.2471 | 4.3102 | 4.1 | 4.0657 | 3.9718 | 4.168 | 3.8945 | 3.9962 | 4.0166 | 0 | 4.1 | 0 | 3.8082 | 3.9238 | 4.0072 | 4.0677 | 4.0488 | 4.1113 | 3.861 | 3.9457 | 3.9454 | 144826 | 3.8852 |  |  | 240497 | 2176 | 280418 | 2205 | 256450 | 1812 | 292358 | 1857 | 33600 | 1200 | 36000 | 1200 | 33600 | 1200 | 38400 | 1200 | 141600 | 4800 | 2.228% | 44 | 3437 | 144.82 |  | 78 | No scada available server OS failed
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 6650 | 6658 | 6673 | 3206 | 4055 | 6692 | 6703 | 6698 | 6300 | 6712 | 6693 | 7043 | 6965 | 6923 | 7206 | 7190 | 7205 | 6965 | 6942 | 7164 | 4052 | 4048 | 4060 | 4048 | 3590 | 4083 | 4032 | 0 | 4116 | 0 | 3476 | 3598 | 3056 | 3587 | 3573 | 3577 | 3563 | 3561 | 3561 | 4.23 | 4.33 | 4.21 | 4.28 | 4.21 | 4.48 | 4.23 | 4.35 | 4.35 | 4.18 | 4.62 | 4.31 | 4.42 | 4.46 | 4.3 | 4.5 | 5.8 | 4.68 | 4.85 | 4.97 | 4.72 | 4.43 | 4.49 | 4.62 | 4.33 | 4.36 | 4.24 | 0 | 4.44 | 0 | 4.26 | 4.44 | 4.44 | 4.44 | 4.48 | 4.54 | 4.25 | 4.41 | 4.59 | 194224 | 4.2369 |  |  | 240525 | 2177 | 280445 | 2205 | 256497 | 1813 | 292416 | 1858 | 33600 | 1200 | 32400 | 0 | 56400 | 1200 | 69600 | 1200 | 192000 | 3600 | 1.145% | 0 | 0 | 194.22 |  | 78 | No scada available server OS failed
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 12206 | 12243 | 12116 | 5892 | 8608 | 12178 | 12998 | 12208 | 11345 | 12064 | 12092 | 11236 | 11299 | 11376 | 11407 | 11348 | 11369 | 11272 | 11454 | 11344 | 3206 | 8658 | 3569 | 8533 | 6275 | 8712 | 8517 | 0 | 8653 | 0 | 6087 | 6225 | 6105 | 6275 | 6260 | 6235 | 6273 | 6308 | 6262 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 338208 | 4.8151 |  |  | 240577 | 2177 | 280494 | 2206 | 256583 | 1813 | 292508 | 1858 | 62400 | 0 | 58800 | 1200 | 103200 | 0 | 110400 | 0 | 334800 | 1200 | 1.008% | 0 | 0 | 338.2 |  | 78 | No scada available server OS failed
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 3065 | 3066 | 2784 | 2259 | 4032 | 3086 | 3109 | 3046 | 3381 | 3125 | 3110 | 3357 | 3392 | 3347 | 3362 | 3317 | 3327 | 3465 | 3456 | 3408 | 758 | 2856 | 1102 | 4157 | 2670 | 4213 | 4215 | 0 | 4167 | 0 | 2699 | 2567 | 2607 | 2743 | 2736 | 2687 | 2673 | 2676 | 2642 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 4.05 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 4.18 | 3.41 | 4.09 | 4.29 | 4.06 | 4.5 | 3.75 | 3.14 | 3.53 | 3.02 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 112662 | 3.5474 |  |  | 240599 | 2178 | 280515 | 2206 | 256605 | 1813 | 292536 | 1859 | 26400 | 1200 | 25200 | 0 | 26400 | 0 | 33600 | 1200 | 111600 | 2400 | 0.9426% | 0 | 0 | 112.66 |  | 78 | No scada available server OS failed
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 6782 | 6734 | 6789 | 5976 | 4621 | 6821 | 6345 | 6599 | 7324 | 6759 | 6775 | 7344 | 7354 | 6898 | 7344 | 7256 | 7299 | 7378 | 7359 | 7387 | 4108 | 4516 | 4598 | 4588 | 3825 | 4576 | 4414 | 0 | 4579 | 0 | 3978 | 3996 | 3987 | 4116 | 4112 | 4022 | 4056 | 4008 | 927 | 4.85 | 5.26 | 4.68 | 5.05 | 5 | 5.11 | 4.84 | 4.48 | 5.09 | 4.83 | 5.29 | 5.04 | 5.15 | 5.24 | 4.99 | 5.44 | 4.96 | 5.48 | 5.43 | 5.67 | 0 | 5.29 | 4.82 | 5.04 | 5.32 | 5.01 | 5.03 | 0,0 | 4.81 | 0 | 4.95 | 5.01 | 4.99 | 5.16 | 5.21 | 4.87 | 5.18 | 4.85 | 5.19 | 205550 | 4.8055 |  |  | 240629 | 2179 | 280544 | 2207 | 256654 | 1814 | 292596 | 1860 | 36000 | 1200 | 34800 | 1200 | 58800 | 1200 | 72000 | 1200 | 201600 | 4800 | 1.922% | 0 | 0 | 205.55 |  | 78 | No scada available server OS failed
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 4822 | 4843 | 4845 | 4423 | 3239 | 4812 | 4878 | 4780 | 5060 | 4796 | 4821 | 5012 | 4749 | 1056 | 5076 | 5064 | 5096 | 5013 | 5043 | 5024 | 1998 | 3256 | 3212 | 3197 | 2911 | 3243 | 2368 | 0 | 3268 | 0 | 2943 | 2879 | 2867 | 2976 | 2913 | 2945 | 2901 | 2901 | 0 | 3.74 | 3.74 | 3.75 | 3.66 | 3.58 | 4.01 | 3.68 | 3.94 | 3.7 | 3.66 | 3.85 | 3.83 | 3.84 | 3.92 | 3.11 | 0 | 4.02 | 3.98 | 4.12 | 4.16 | 3.79 | 3.68 | 3.68 | 3.85 | 3.49 | 3.7 | 3.67 | 0 | 3.9 | 0 | 3.66 | 3.57 | 3.7 | 3.91 | 4.05 | 3.93 | 3.61 | 4.13 | 3.7 | 139230 | 3.4951 |  |  | 240650 | 2180 | 280563 | 2208 | 256689 | 1815 | 292634 | 1861 | 25200 | 1200 | 22800 | 1200 | 42000 | 1200 | 45600 | 1200 | 135600 | 4800 | 2.607% | 96 | 34850 | 139.23 |  | 78 | No scada available server OS failed
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 6421 | 6453 | 6423 | 6431 | 5032 | 6021 | 6023 | 6452 | 5890 | 6464 | 6479 | 5859 | 5867 | 5858 | 5842 | 5854 | 5875 | 5879 | 5870 | 5848 | 5067 | 5058 | 5022 | 4596 | 4572 | 5056 | 5042 | 0 | 5074 | 0 | 4529 | 3021 | 4572 | 4556 | 4581 | 4549 | 4588 | 2677 | 1265 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 4.05 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 4.18 | 3.41 | 4.09 | 4.29 | 4.06 | 4.5 | 3.75 | 3.14 | 3.53 | 3.02 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 194666 | 3.5474 |  |  | 240682 | 2180 | 280596 | 2208 | 256736 | 1816 | 292682 | 1861 | 38400 | 0 | 39600 | 0 | 56400 | 1200 | 57600 | 0 | 192000 | 1200 | 1.37% | 96 | 708 | 194.66 |  | 78 | No scada available server OS failed
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 9898 | 9872 | 10542 | 9888 | 8169 | 9874 | 10576 | 10587 | 8749 | 10556 | 10578 | 8787 | 8764 | 8769 | 8760 | 9946 | 9984 | 9966 | 7253 | 9989 | 8166 | 8152 | 8121 | 8176 | 7376 | 8162 | 8165 | 0 | 8175 | 0 | 7365 | 7370 | 7342 | 7359 | 7383 | 7376 | 7369 | 7388 | 6574 | 4.58 | 4.46 | 3.97 | 4.15 | 3.78 | 4.38 | 4.4 | 4.13 | 4.08 | 3.95 | 4.01 | 4.04 | 3.98 | 3.84 | 3.92 | 3.95 | 4.15 | 4.01 | 3.99 | 4.01 | 3.76 | 3.87 | 3.95 | 4.26 | 4.2 | 4.22 | 4.21 | 0 | 5.44 | 0 | 4.17 | 4.15 | 4.32 | 4.55 | 6.32 | 4.45 | 4.87 | 4.31 | 5.39 | 321526 | 4.0569 |  |  | 240740 | 2180 | 280655 | 2208 | 256811 | 1816 | 292755 | 1861 | 69600 | 0 | 70800 | 0 | 90000 | 0 | 87600 | 0 | 318000 | 0 | 1.097% | 96 | 1873 | 321.52 |  | 78 | No scada available server OS failed
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 5673 | 5132 | 5684 | 5681 | 4123 | 5424 | 5163 | 5642 | 6458 | 5635 | 5673 | 6475 | 6438 | 6473 | 6451 | 6423 | 6446 | 6475 | 1297 | 6452 | 4135 | 4154 | 4111 | 4156 | 2867 | 4127 | 4123 | 0 | 4145 | 0 | 3521 | 3536 | 3573 | 3557 | 3564 | 3535 | 3547 | 3550 | 3569 | 4.0641 | 4.0593 | 4.0183 | 3.9908 | 3.9708 | 4.1533 | 4.1533 | 4.3953 | 4.0946 | 4.1891 | 4.5516 | 4.0448 | 4.0977 | 4.1514 | 4.115 | 4.1475 | 4.3757 | 4.3612 | 4.2471 | 4.3102 | 4.1 | 4.0657 | 3.9718 | 4.168 | 3.8945 | 3.9962 | 4.0166 | 0 | 4.1 | 0 | 3.8082 | 3.9238 | 4.0072 | 4.0677 | 4.0488 | 4.1113 | 3.861 | 3.9457 | 3.9454 | 176988 | 3.8852 |  |  | 240768 | 2181 | 280682 | 2208 | 256852 | 1816 | 292804 | 1862 | 33600 | 1200 | 32400 | 0 | 49200 | 0 | 58800 | 1200 | 174000 | 2400 | 1.688% | 96 | 15134 | 176.98 |  | 78 | No scada available server OS failed
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 3466 | 3564 | 3552 | 3546 | 3521 | 3576 | 3537 | 3551 | 4056 | 3532 | 3543 | 4052 | 4033 | 4042 | 4034 | 4011 | 4047 | 4052 | 4040 | 4057 | 3523 | 3511 | 3525 | 3514 | 3162 | 3515 | 3543 | 0 | 3548 | 0 | 2487 | 3145 | 3121 | 3154 | 3132 | 3136 | 3156 | 3149 | 3152 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 4.05 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 4.18 | 3.41 | 4.09 | 4.29 | 4.06 | 4.5 | 3.75 | 3.14 | 3.53 | 3.02 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 131285 | 3.5474 |  |  | 240792 | 2181 | 280705 | 2209 | 256878 | 1817 | 292837 | 1862 | 28800 | 0 | 27600 | 1200 | 31200 | 1200 | 39600 | 0 | 127200 | 2400 | 3.112% | 96 | 55 | 131.28 |  | 78 | No scada available server OS failed
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 3821 | 3824 | 3809 | 3815 | 3190 | 3821 | 3829 | 3825 | 3550 | 3839 | 3852 | 3523 | 3522 | 3556 | 3528 | 3542 | 3541 | 3540 | 3559 | 3567 | 4102 | 2789 | 4115 | 4136 | 4021 | 4140 | 4109 | 0 | 4121 | 0 | 4101 | 4111 | 4116 | 4121 | 4119 | 4153 | 4132 | 4127 | 4129 | 3.74 | 3.74 | 3.75 | 3.66 | 3.58 | 4.01 | 3.68 | 3.94 | 3.7 | 3.66 | 3.85 | 3.83 | 3.84 | 3.92 | 3.11 | 0 | 4.02 | 3.98 | 4.12 | 4.16 | 3.79 | 3.68 | 3.68 | 3.85 | 3.49 | 3.7 | 3.67 | 0 | 3.9 | 0 | 3.66 | 3.57 | 3.7 | 3.91 | 4.05 | 3.93 | 3.61 | 4.13 | 3.7 | 141695 | 3.4951 |  |  | 240825 | 2182 | 280730 | 2210 | 256906 | 1817 | 292866 | 1863 | 39600 | 1200 | 30000 | 1200 | 33600 | 0 | 34800 | 1200 | 138000 | 3600 | 2.608% | 96 | 5662 | 141.69 |  | 78 | No scada available server OS failed
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 5587 | 5267 | 5278 | 5575 | 5201 | 5562 | 5579 | 5565 | 5321 | 5032 | 5543 | 5342 | 5347 | 5352 | 5353 | 5021 | 5042 | 5034 | 5045 | 5067 | 4693 | 5205 | 5200 | 5215 | 3501 | 5210 | 5242 | 0 | 5245 | 0 | 3515 | 3690 | 3692 | 3679 | 3698 | 3678 | 3682 | 3516 | 3696 | 4.0641 | 4.0593 | 4.0183 | 3.9908 | 3.9708 | 4.1533 | 4.1533 | 4.3953 | 4.0946 | 4.1891 | 4.5516 | 4.0448 | 4.0977 | 4.1514 | 4.115 | 4.1475 | 4.3757 | 4.3612 | 4.2471 | 4.3102 | 4.1 | 4.0657 | 3.9718 | 4.168 | 3.8945 | 3.9962 | 4.0166 | 0 | 4.1 | 0 | 3.8082 | 3.9238 | 4.0072 | 4.0677 | 4.0488 | 4.1113 | 3.861 | 3.9457 | 3.9454 | 178470 | 3.8852 |  |  | 240855 | 2183 | 280764 | 2210 | 256946 | 1818 | 292909 | 1864 | 36000 | 1200 | 40800 | 0 | 48000 | 1200 | 51600 | 1200 | 176400 | 3600 | 1.16% | 96 | 2876 | 178.47 |  | 78 | No scada available server OS failed
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 5618 | 5628 | 5632 | 5640 | 5601 | 5079 | 5633 | 5622 | 5173 | 5656 | 5674 | 5174 | 5164 | 5156 | 5177 | 5148 | 5142 | 5156 | 5176 | 5178 | 5632 | 5621 | 4621 | 5637 | 4021 | 5636 | 5644 | 0 | 5654 | 0 | 4631 | 4637 | 4645 | 4642 | 4666 | 4665 | 4633 | 4647 | 4664 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 4.05 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 4.18 | 3.41 | 4.09 | 4.29 | 4.06 | 4.5 | 3.75 | 3.14 | 3.53 | 3.02 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 191723 | 3.5474 |  |  | 240892 | 2184 | 280800 | 2211 | 256987 | 1819 | 292951 | 1865 | 44400 | 1200 | 43200 | 1200 | 49200 | 1200 | 50400 | 1200 | 187200 | 4800 | 2.359% | 96 | 9688 | 191.73 |  | 78 | No scada available server OS failed
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 6537 | 6585 | 6279 | 6263 | 8296 | 6578 | 6542 | 6545 | 9753 | 6567 | 6582 | 9745 | 9746 | 9723 | 9748 | 9752 | 9758 | 9742 | 9772 | 9784 | 8833 | 8842 | 8829 | 8835 | 6041 | 8846 | 8852 | 0 | 8853 | 0 | 5885 | 6046 | 6042 | 6055 | 6057 | 6048 | 5564 | 6049 | 6067 | 4.85 | 5.26 | 4.68 | 5.05 | 5 | 5.11 | 4.84 | 4.48 | 5.09 | 4.83 | 5.29 | 5.04 | 5.15 | 5.24 | 4.99 | 5.44 | 4.96 | 5.48 | 5.43 | 5.67 | 0 | 5.29 | 4.82 | 5.04 | 5.32 | 5.01 | 5.03 | 0,0 | 4.81 | 0 | 4.95 | 5.01 | 4.99 | 5.16 | 5.21 | 4.87 | 5.18 | 4.85 | 5.19 | 286041 | 4.8055 |  |  | 240941 | 2185 | 280858 | 2212 | 257037 | 1820 | 293032 | 1866 | 58800 | 1200 | 69600 | 1200 | 60000 | 1200 | 97200 | 1200 | 285600 | 4800 | 0.1542% | 96 | 3218 | 286.08 |  | 78 | No scada available server OS failed
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 2801 | 2812 | 2817 | 2814 | 2032 | 2801 | 2809 | 2816 | 3103 | 2832 | 2840 | 3108 | 3107 | 3118 | 3001 | 3109 | 3111 | 3104 | 3128 | 3135 | 2045 | 2042 | 2007 | 2021 | 1521 | 2014 | 2038 | 0 | 2042 | 0 | 1532 | 1542 | 1526 | 1535 | 1542 | 1540 | 1538 | 1539 | 1542 | 3.1605 | 3.5608 | 3.1151 | 3.3498 | 3.3269 | 3.1994 | 3.1127 | 3.3075 | 3.3208 | 2.8659 | 3.1959 | 3.2102 | 3.4381 | 3.1364 | 3.1875 | 3.02 | 3.2244 | 3.1802 | 3.1785 | 3.0892 | 3.3397 | 3.33 | 3.1537 | 2.9716 | 3.1007 | 2.7795 | 3.1705 | 0 | 3.0811 | 0 | 3.1179 | 2.8482 | 2.909 | 3.1531 | 3.0024 | 3.149 | 3.0592 | 3.2 | 3.0888 | 87964 | 2.9906 |  |  | 240953 | 2186 | 280871 | 2213 | 257057 | 1821 | 293057 | 1867 | 14400 | 1200 | 15600 | 1200 | 24000 | 1200 | 30000 | 1200 | 84000 | 4800 | 4.506% | 96 | 45073 | 87.96 |  | 78 | No scada available server OS failed
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 7042 | 7032 | 7021 | 7022 | 7732 | 7053 | 7043 | 7033 | 7342 | 7057 | 7069 | 7352 | 7347 | 7349 | 7354 | 6521 | 7365 | 7359 | 7387 | 7395 | 7768 | 7758 | 7743 | 7728 | 5831 | 7721 | 7772 | 0 | 7787 | 0 | 6467 | 6457 | 6043 | 6452 | 6456 | 6451 | 6458 | 6487 | 6466 | 4.85 | 5.26 | 4.68 | 5.05 | 5 | 5.11 | 4.84 | 4.48 | 5.09 | 4.83 | 5.29 | 5.04 | 5.15 | 5.24 | 4.99 | 5.44 | 4.96 | 5.48 | 5.43 | 5.67 | 0 | 5.29 | 4.82 | 5.04 | 5.32 | 5.01 | 5.03 | 0 | 4.81 | 0 | 4.95 | 5.01 | 4.99 | 5.16 | 5.21 | 4.87 | 5.18 | 4.85 | 5.19 | 261720 | 4.6823 |  |  | 241005 | 2187 | 280922 | 2214 | 257109 | 1822 | 293117 | 1867 | 62400 | 1200 | 61200 | 1200 | 62400 | 1200 | 72000 | 0 | 258000 | 3600 | 1.421% | 96 | 54003 | 261.72 |  | 78 | No scada available server OS failed
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 7125 | 7129 | 7132 | 7136 | 5501 | 7142 | 7122 | 7126 | 7109 | 6749 | 7164 | 7110 | 7118 | 7126 | 7129 | 6898 | 6473 | 7108 | 7142 | 7149 | 5521 | 5518 | 5509 | 5524 | 5842 | 5516 | 5528 | 0 | 5532 | 0 | 5589 | 5822 | 5821 | 5842 | 5846 | 5844 | 5824 | 5839 | 5842 | 4.0641 | 4.0593 | 4.0183 | 3.9908 | 3.9708 | 4.1533 | 4.1533 | 4.3953 | 4.0946 | 4.1891 | 4.5516 | 4.0448 | 4.0977 | 4.1514 | 4.115 | 4.1475 | 4.3757 | 4.3612 | 4.2471 | 4.3102 | 4.1 | 4.0657 | 3.9718 | 4.168 | 3.8945 | 3.9962 | 4.0166 | 0 | 4.1 | 0 | 3.8082 | 3.9238 | 4.0072 | 4.0677 | 4.0488 | 4.1113 | 3.861 | 3.9457 | 3.9454 | 236447 | 3.8852 |  |  | 241053 | 2187 | 280958 | 2214 | 257161 | 1822 | 293174 | 1868 | 57600 | 0 | 43200 | 0 | 62400 | 0 | 68400 | 1200 | 231600 | 1200 | 2.05% | 96 | 64981 | 236.44 |  | 78 | No scada available server OS failed
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 4453 | 4458 | 4421 | 4290 | 3602 | 4456 | 4434 | 4426 | 3729 | 4456 | 4467 | 3742 | 3745 | 3749 | 3752 | 3750 | 3753 | 3321 | 3356 | 3758 | 3656 | 3643 | 3622 | 3234 | 3552 | 3652 | 3649 | 0 | 3424 | 0 | 3553 | 3572 | 3522 | 3562 | 3565 | 3560 | 3532 | 3529 | 3321 | 3.74 | 3.74 | 3.75 | 3.66 | 3.58 | 4.01 | 3.68 | 3.94 | 3.7 | 3.66 | 3.85 | 3.83 | 3.84 | 3.92 | 3.11 | 0 | 4.02 | 3.98 | 4.12 | 4.16 | 3.79 | 3.68 | 3.68 | 3.85 | 3.49 | 3.7 | 3.67 | 0 | 3.9 | 0 | 3.66 | 3.57 | 3.7 | 3.91 | 4.05 | 3.93 | 3.61 | 4.13 | 3.7 | 140266 | 3.4951 |  |  | 241082 | 2188 | 280981 | 2215 | 257194 | 1823 | 293204 | 1868 | 34800 | 1200 | 27600 | 1200 | 39600 | 1200 | 36000 | 0 | 138000 | 3600 | 1.616% | 94 | 14022 | 140.26 |  | 78 | No scada available server OS failed
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 8741 | 10621 | 10623 | 10219 | 11850 | 10227 | 10615 | 10632 | 14750 | 10645 | 10658 | 14755 | 14752 | 14749 | 14754 | 14758 | 14762 | 14742 | 14782 | 12689 | 11856 | 11852 | 11811 | 11861 | 10450 | 11852 | 11859 | 0 | 10981 | 0 | 10452 | 9572 | 10421 | 10465 | 10459 | 10456 | 10448 | 10463 | 10465 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 436047 | 4.8151 |  |  | 241168 | 2188 | 281059 | 2215 | 257271 | 1823 | 293325 | 1868 | 103200 | 0 | 93600 | 0 | 92400 | 0 | 145200 | 0 | 434400 | 0 | 0.3777% | 96 | 86461 | 436.04 |  | 78 | No scada available server OS failed
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 5219 | 16389 | 16385 | 16380 | 9901 | 16374 | 15953 | 16387 | 13721 | 16382 | 16389 | 13750 | 13752 | 12032 | 13759 | 13021 | 13752 | 13744 | 13759 | 13782 | 9957 | 9952 | 9932 | 9967 | 7450 | 9962 | 9969 | 0 | 9974 | 0 | 7432 | 7021 | 7422 | 7437 | 7442 | 7445 | 7431 | 7447 | 7451 | 4.73 | 5.25 | 4.97 | 4.56 | 4.53 | 5.13 | 4.74 | 4.54 | 5.04 | 4.65 | 5.08 | 5.09 | 5.15 | 6.01 | 4.79 | 4.63 | 4.4 | 4.69 | 5.17 | 5.05 | 4.8 | 4.95 | 4.57 | 4.87 | 4.67 | 4.45 | 4.48 | 0 | 4.42 | 0 | 4.25 | 4.37 | 4.48 | 4.63 | 4.57 | 4.44 | 4.53 | 4.53 | 4.67 | 424522 | 4.5097 |  |  | 241229 | 2189 | 281125 | 2216 | 257382 | 1823 | 293437 | 1869 | 73200 | 1200 | 79200 | 1200 | 133200 | 0 | 134400 | 1200 | 420000 | 3600 | 1.065% | 96 | 167998 | 424.52 |  | 78 | No scada available server OS failed
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 16456 | 16445 | 16454 | 16001 | 16466 | 16423 | 16427 | 16421 | 16001 | 16456 | 16467 | 16467 | 12578 | 14842 | 16061 | 16032 | 16034 | 16027 | 16072 | 16085 | 12252 | 12256 | 12235 | 11021 | 13852 | 12264 | 12268 | 0 | 12276 | 0 | 13863 | 10521 | 13853 | 13845 | 12853 | 13857 | 13839 | 13879 | 13897 | 5.58 | 6.55 | 5.67 | 5.72 | 6.71 | 6.27 | 6 | 5.79 | 6 | 6.65 | 5.98 | 6.36 | 6.31 | 5.42 | 6.29 | 6.5 | 6.63 | 6.48 | 6.75 | 6.78 | 6.72 | 6.39 | 5.76 | 5.9 | 6.3 | 5.66 | 5.5 | 0 | 5.28 | 0 | 5.85 | 5.65 | 5.63 | 5.65 | 5.94 | 5.56 | 5.81 | 5.84 | 5.94 | 539046 | 5.739 |  |  | 241340 | 2189 | 281205 | 2216 | 257505 | 1823 | 293566 | 1869 | 133200 | 0 | 96000 | 0 | 147600 | 0 | 154800 | 0 | 531600 | 0 | 1.381% | 96 | 52674 | 539.04 |  | 78 | No scada available server OS failed
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 15835 | 14321 | 15869 | 14797 | 11790 | 15894 | 15864 | 15892 | 18652 | 15889 | 15896 | 18632 | 18643 | 18645 | 18665 | 17521 | 18675 | 18653 | 18678 | 18692 | 11789 | 11797 | 11735 | 8749 | 13604 | 11795 | 10990 | 0 | 11786 | 0 | 13631 | 13656 | 13621 | 13645 | 13652 | 13642 | 13625 | 13647 | 13664 | 5.8621 | 6.3056 | 5.2877 | 5.3705 | 5.0465 | 5.8957 | 5.8957 | 5.8117 | 6.2648 | 4.8664 | 5.6272 | 5.7042 | 5.5212 | 5.7344 | 6.0185 | 5.5628 | 6.2912 | 5.9452 | 6.1094 | 6.4611 | 5.9728 | 4.9143 | 5.1145 | 5.336 | 5.0755 | 5.3435 | 5.0553 | 0 | 5 | 0 | 4.943 | 4.9765 | 5.2576 | 5.6703 | 5.5863 | 5.4673 | 5.2684 | 5.2848 | 5.2838 | 552531 | 5.2598 |  |  | 241453 | 2189 | 281280 | 2216 | 257621 | 1823 | 293720 | 1869 | 135600 | 0 | 90000 | 0 | 139200 | 0 | 184800 | 0 | 549600 | 0 | 0.5305% | 96 | 111665 | 552.53 |  | 78 | No scada available server OS failed
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 27801 | 27807 | 27806 | 27819 | 17106 | 27841 | 27854 | 27867 | 26901 | 27878 | 27897 | 24649 | 26906 | 26909 | 26945 | 26942 | 26963 | 26942 | 26983 | 26997 | 17115 | 17167 | 17109 | 15902 | 15980 | 17190 | 17189 | 0 | 17192 | 0 | 17851 | 17832 | 17842 | 17821 | 17300 | 17839 | 17847 | 17852 | 17869 | 7.28 | 7.74 | 7.38 | 7.5 | 6.95 | 6.64 | 0 | 7.59 | 7.79 | 7.37 | 7.73 | 7.52 | 7.72 | 7.67 | 7.75 | 7.66 | 8.38 | 7.44 | 8.44 | 7.02 | 6.9 | 7.2 | 7.24 | 7.4 | 7.39 | 7.05 | 6.74 | 0 | 7.37 | 0 | 6.79 | 6.65 | 6.54 | 7.02 | 7.65 | 7.66 | 6.74 | 6.53 | 7.19 | 829710 | 6.7597 |  |  | 241599 | 2189 | 281393 | 2216 | 257829 | 1823 | 293942 | 1869 | 175200 | 0 | 135600 | 0 | 249600 | 0 | 266400 | 0 | 826800 | 0 | 0.3507% | 96 | 291053 | 829.71 |  | 78 | No scada available server OS failed
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 25119 | 25121 | 25115 | 25122 | 19223 | 25134 | 25123 | 25131 | 20263 | 25165 | 25172 | 23119 | 23112 | 23132 | 23145 | 23144 | 23151 | 23134 | 23167 | 23178 | 19243 | 18521 | 18501 | 18509 | 17921 | 19245 | 19252 | 0 | 19267 | 0 | 17945 | 17924 | 17952 | 17946 | 17956 | 17949 | 17932 | 17967 | 17959 | 7.13 | 7.22 | 7.2 | 7.2 | 6.86 | 6.84 | 7.52 | 7.38 | 7.33 | 7.21 | 7.51 | 7.19 | 7.34 | 7.41 | 7.21 | 7.4 | 7.01 | 7.28 | 7.58 | 7.54 | 6.5 | 7.13 | 7.11 | 7.2 | 6.69 | 6.89 | 6.85 | 0 | 7.02 | 0 | 6.26 | 6.56 | 6.37 | 6.77 | 7.01 | 7.01 | 6.41 | 6.12 | 6.55 | 785959 | 6.6618 |  |  | 241748 | 2189 | 281518 | 2216 | 258017 | 1823 | 294132 | 1869 | 178800 | 0 | 150000 | 0 | 225600 | 0 | 228000 | 0 | 782400 | 0 | 0.4528% | 96 | 247411 | 785.95 |  | 78 | No scada available server OS failed
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 10401 | 10407 | 10402 | 9518 | 9544 | 10409 | 10399 | 8107 | 12223 | 10456 | 10467 | 12232 | 12234 | 12245 | 12256 | 12252 | 12254 | 12233 | 12267 | 11499 | 9556 | 9552 | 9545 | 10260 | 9102 | 10256 | 10267 | 0 | 10278 | 0 | 9105 | 8664 | 9109 | 8678 | 9111 | 9110 | 9103 | 9114 | 9116 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 381731 | 4.8151 |  |  | 241822 | 2189 | 281584 | 2216 | 258092 | 1823 | 294233 | 1869 | 88800 | 0 | 79200 | 0 | 90000 | 0 | 121200 | 0 | 379200 | 0 | 0.663% | 96 | 14431 | 381.73 |  | 78 | No scada available server OS failed
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 21256 | 21262 | 21242 | 21234 | 18241 | 21265 | 21254 | 21262 | 21621 | 21268 | 19969 | 21632 | 21634 | 21638 | 21642 | 21640 | 21652 | 21657 | 21647 | 20782 | 18242 | 18236 | 18230 | 18256 | 18022 | 18251 | 18276 | 0 | 18280 | 0 | 18067 | 18065 | 18046 | 17021 | 18037 | 18069 | 18065 | 17489 | 18076 | 5.8621 | 6.3056 | 5.2877 | 5.3705 | 5.0465 | 5.8957 | 5.8957 | 5.8117 | 6.2648 | 4.8664 | 5.6272 | 5.7042 | 5.5212 | 5.7344 | 6.0185 | 5.5628 | 6.2912 | 5.9452 | 6.1094 | 6.4611 | 5.9728 | 4.9143 | 5.1145 | 5.336 | 5.0755 | 5.3435 | 5.0553 | 0 | 5 | 0 | 4.943 | 4.9765 | 5.2576 | 5.6703 | 5.5863 | 5.4673 | 5.2684 | 5.2848 | 5.2838 | 730526 | 5.2598 |  |  | 241970 | 2189 | 281705 | 2216 | 258250 | 1823 | 294412 | 1869 | 177600 | 0 | 145200 | 0 | 189600 | 0 | 214800 | 0 | 727200 | 0 | 0.4553% | 96 | 118681 | 730.52 |  | 78 | No scada available server OS failed
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 5742 | 5721 | 5723 | 5734 | 2321 | 5728 | 5722 | 5719 | 6001 | 5732 | 5747 | 6021 | 6025 | 6030 | 6045 | 6023 | 6033 | 6021 | 6038 | 6039 | 2345 | 2356 | 2342 | 2365 | 3050 | 2362 | 2356 | 0 | 2372 | 0 | 3059 | 3069 | 3054 | 3059 | 3051 | 3055 | 3034 | 3059 | 3056 | 4.0641 | 4.0593 | 4.0183 | 3.9908 | 3.9708 | 4.1533 | 4.1533 | 4.3953 | 4.0946 | 4.1891 | 4.5516 | 4.0448 | 4.0977 | 4.1514 | 4.115 | 4.1475 | 4.3757 | 4.3612 | 4.2471 | 4.3102 | 4.1 | 4.0657 | 3.9718 | 4.168 | 3.8945 | 3.9962 | 4.0166 | 0 | 4.1 | 0 | 3.8082 | 3.9238 | 4.0072 | 4.0677 | 4.0488 | 4.1113 | 3.861 | 3.9457 | 3.9454 | 161209 | 3.8852 |  |  | 241995 | 2189 | 281720 | 2216 | 258292 | 1823 | 294461 | 1869 | 30000 | 0 | 18000 | 0 | 50400 | 0 | 58800 | 0 | 157200 | 0 | 2.487% | 96 | 19160 | 161.2 |  | 78 | No scada available server OS failed
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 9011 | 9018 | 9015 | 8627 | 6821 | 7959 | 9009 | 9012 | 8001 | 9019 | 8644 | 8012 | 8015 | 8012 | 8021 | 8016 | 8025 | 8019 | 7778 | 8078 | 6832 | 6828 | 6809 | 6845 | 6215 | 6840 | 6856 | 0 | 6862 | 0 | 6218 | 6221 | 6224 | 6232 | 5589 | 5753 | 6211 | 6232 | 6245 | 4.85 | 5.26 | 4.68 | 5.05 | 5 | 5.11 | 4.84 | 4.48 | 5.09 | 4.83 | 5.29 | 5.04 | 5.15 | 5.24 | 4.99 | 5.44 | 4.96 | 5.48 | 5.43 | 5.67 | 0 | 5.29 | 4.82 | 5.04 | 5.32 | 5.01 | 5.03 | 0 | 4.81 | 0 | 4.95 | 5.01 | 4.99 | 5.16 | 5.21 | 4.87 | 5.18 | 4.85 | 5.19 | 275124 | 4.6823 |  |  | 242045 | 2190 | 281765 | 2216 | 258358 | 1824 | 294527 | 1869 | 60000 | 1200 | 54000 | 0 | 79200 | 1200 | 79200 | 0 | 272400 | 2400 | 0.9901% | 96 | 8433 | 275.12 |  | 78 | No scada available server OS failed
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 14601 | 14605 | 12264 | 14606 | 9321 | 14611 | 14608 | 14615 | 12801 | 14632 | 14640 | 12857 | 12846 | 12852 | 12845 | 12843 | 12842 | 12847 | 12867 | 12876 | 9354 | 9352 | 9345 | 9359 | 7790 | 9355 | 9362 | 0 | 9365 | 0 | 7756 | 7759 | 7784 | 7787 | 7780 | 6689 | 7769 | 7782 | 7789 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 409156 | 4.8151 |  |  | 242109 | 2190 | 281828 | 2216 | 258466 | 1824 | 294623 | 1869 | 76800 | 0 | 75600 | 0 | 129600 | 0 | 115200 | 0 | 397200 | 0 | 2.922% | 96 | 35674 | 409.15 |  | 78 | No scada available server OS failed
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 19801 | 19807 | 19809 | 18098 | 13021 | 19815 | 19801 | 19811 | 16321 | 19819 | 19821 | 16342 | 16345 | 16347 | 16344 | 16332 | 16322 | 16329 | 16345 | 16352 | 13051 | 13042 | 13038 | 13045 | 10821 | 13042 | 12590 | 0 | 12542 | 0 | 10829 | 10824 | 10832 | 10835 | 10838 | 10840 | 10831 | 10841 | 10844 | 5.8621 | 6.3056 | 5.2877 | 5.3705 | 5.0465 | 5.8957 | 5.8957 | 5.8117 | 6.2648 | 4.8664 | 5.6272 | 5.7042 | 5.5212 | 5.7344 | 6.0185 | 5.5628 | 6.2912 | 5.9452 | 6.1094 | 6.4611 | 5.9728 | 4.9143 | 5.1145 | 5.336 | 5.0755 | 5.3435 | 5.0553 | 0 | 5 | 0 | 4.943 | 4.9765 | 5.2576 | 5.6703 | 5.5863 | 5.4673 | 5.2684 | 5.2848 | 5.2838 | 551667 | 5.2598 |  |  | 242199 | 2190 | 281913 | 2216 | 258613 | 1824 | 294759 | 1869 | 108000 | 0 | 102000 | 0 | 176400 | 0 | 163200 | 0 | 549600 | 0 | 0.3747% | 96 | 70776 | 551.66 |  | 78 | No scada available server OS failed
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 20601 | 20609 | 20611 | 20615 | 12000 | 20619 | 20605 | 20621 | 18150 | 20626 | 20632 | 18154 | 18159 | 18162 | 18167 | 18165 | 18169 | 18159 | 18176 | 18184 | 12012 | 12015 | 12001 | 12145 | 10350 | 12121 | 12125 | 0 | 12132 | 0 | 10379 | 10372 | 10376 | 10374 | 10362 | 10368 | 10359 | 10367 | 10370 | 5.63 | 6.04 | 5.55 | 5.6 | 6.19 | 6.25 | 5.75 | 5.53 | 5.55 | 5.54 | 5.96 | 5.74 | 5.9 | 5.75 | 5.91 | 5.82 | 5.86 | 6.15 | 6.47 | 6.22 | 5.08 | 6.26 | 5.87 | 5.93 | 5.43 | 5.57 | 5.63 | 0 | 5.51 | 0 | 5.16 | 5.45 | 5.48 | 5.59 | 5.63 | 5.54 | 5.55 | 5.62 | 5.36 | 567412 | 5.4377 |  |  | 242285 | 2190 | 281993 | 2216 | 258767 | 1824 | 294910 | 1869 | 103200 | 0 | 96000 | 0 | 184800 | 0 | 181200 | 0 | 565200 | 0 | 0.3898% | 96 | 100593 | 567.41 |  | 78 | No scada available server OS failed
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 24750 | 24757 | 24743 | 24298 | 23401 | 24756 | 24732 | 24745 | 21821 | 24775 | 24789 | 21850 | 21856 | 21520 | 21860 | 21845 | 21861 | 21848 | 21878 | 21250 | 23422 | 23419 | 23411 | 23421 | 20121 | 21998 | 23434 | 0 | 22789 | 0 | 20114 | 20124 | 20128 | 20135 | 20138 | 20140 | 20119 | 19629 | 20145 | 7.28 | 7.74 | 7.38 | 7.5 | 6.95 | 6.64 | 7.2 | 7.59 | 7.79 | 7.37 | 7.73 | 7.52 | 7.72 | 7.67 | 7.75 | 7.66 | 8.38 | 7.44 | 8.44 | 7.02 | 6.9 | 7.2 | 7.24 | 7.4 | 7.39 | 7.05 | 6.74 | 0 | 7.37 | 0 | 6.79 | 6.65 | 6.54 | 7.02 | 7.65 | 7.66 | 6.74 | 6.53 | 7.19 | 826022 | 6.9444 |  |  | 242452 | 2190 | 282147 | 2216 | 258952 | 1824 | 295091 | 1869 | 200400 | 0 | 184800 | 0 | 222000 | 0 | 217200 | 0 | 824400 | 0 | 0.1964% | 96 | 186028 | 826.02 |  | 78 | No scada available server OS failed
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 13301 | 11520 | 13323 | 13335 | 12629 | 13346 | 13337 | 13364 | 22332 | 13372 | 13378 | 22326 | 22342 | 20987 | 21535 | 21522 | 22321 | 22316 | 22345 | 21452 | 12672 | 12662 | 11201 | 12678 | 11701 | 12672 | 12689 | 0 | 12692 | 0 | 11711 | 11723 | 11721 | 11723 | 11732 | 11734 | 11721 | 11735 | 11742 | 5.63 | 6.04 | 5.55 | 5.6 | 6.19 | 6.25 | 5.75 | 5.53 | 5.55 | 5.54 | 5.96 | 5.74 | 5.4 | 5.5 | 5.41 | 5.42 | 5.86 | 6.15 | 6.47 | 6.22 | 5.08 | 6.26 | 5.87 | 5.93 | 5.43 | 5.57 | 5.63 | 0 | 5.51 | 0 | 5.16 | 5.35 | 5.38 | 5.49 | 5.43 | 5.44 | 5.45 | 5.52 | 5.36 | 554892 | 5.3749 |  |  | 242550 | 2190 | 282231 | 2217 | 259051 | 1824 | 295270 | 1870 | 117600 | 0 | 100800 | 1200 | 118800 | 0 | 214800 | 1200 | 552000 | 2400 | 0.5212% | 96 | 137294 | 554.89 |  | 78 | No scada available server OS failed
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 17911 | 17915 | 17919 | 17913 | 14410 | 17917 | 15631 | 17921 | 9561 | 17934 | 17938 | 9565 | 9566 | 9568 | 9572 | 9522 | 9539 | 9542 | 9578 | 9582 | 14472 | 14474 | 14458 | 14462 | 12111 | 14457 | 14454 | 0 | 14468 | 0 | 11598 | 12132 | 12135 | 12142 | 12148 | 12145 | 12139 | 12152 | 12156 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 5.07 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 491107 | 4.8151 |  |  | 242649 | 2190 | 282326 | 2217 | 259182 | 1824 | 295349 | 1870 | 118800 | 0 | 114000 | 0 | 157200 | 0 | 94800 | 0 | 484800 | 0 | 1.284% | 96 | 100851 | 491.1 |  | 78 | No scada available server OS failed
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 12983 | 14968 | 14951 | 14966 | 9811 | 14959 | 14931 | 14967 | 12731 | 14972 | 14981 | 12735 | 12738 | 12741 | 12762 | 12758 | 12764 | 12760 | 12772 | 12775 | 9837 | 9831 | 9828 | 9855 | 8970 | 9850 | 9862 | 0 | 9868 | 0 | 8985 | 8957 | 8958 | 8951 | 8962 | 8959 | 8948 | 8964 | 8969 | 4.85 | 5.26 | 4.68 | 5.05 | 5 | 5.11 | 4.84 | 4.48 | 5.09 | 4.83 | 5.29 | 5.04 | 5.15 | 5.24 | 4.99 | 5.44 | 4.96 | 5.48 | 5.43 | 5.67 | 0 | 5.29 | 4.82 | 5.04 | 5.32 | 5.01 | 5.03 | 0 | 4.81 | 0 | 4.95 | 5.01 | 4.99 | 5.16 | 5.21 | 4.87 | 5.18 | 4.85 | 5.19 | 428579 | 4.6823 |  |  | 242722 | 2191 | 282390 | 2217 | 259292 | 1825 | 295454 | 1870 | 87600 | 1200 | 76800 | 0 | 132000 | 1200 | 126000 | 0 | 422400 | 2400 | 1.442% | 70 | 115200 | 428.57 |  | 78 | No scada available server OS failed
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 4102 | 4109 | 4104 | 4111 | 2479 | 4121 | 4112 | 4123 | 3621 | 3267 | 4167 | 3610 | 3616 | 3618 | 3620 | 3618 | 2021 | 3628 | 3642 | 3645 | 2487 | 2474 | 2468 | 2118 | 2742 | 2111 | 2121 | 0 | 2123 | 0 | 2745 | 2752 | 2753 | 2755 | 2758 | 2746 | 2742 | 2762 | 2765 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 4.05 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 4.18 | 3.41 | 4.09 | 4.29 | 4.06 | 4.5 | 3.75 | 3.14 | 3.53 | 3.02 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 116756 | 3.5474 |  |  | 242744 | 2192 | 282405 | 2218 | 259321 | 1826 | 295482 | 1872 | 26400 | 1200 | 18000 | 1200 | 34800 | 1200 | 33600 | 2400 | 112800 | 6000 | 3.388% | 86 | 4123 | 116.75 |  | 78 | No scada available server OS failed
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 3227 | 3234 | 3220 | 3107 | 2130 | 3220 | 3227 | 3375 | 5096 | 3208 | 3210 | 4318 | 4320 | 4327 | 4332 | 4256 | 0 | 4143 | 4134 | 4293 | 1484 | 1698 | 1595 | 1610 | 1600 | 1502 | 1553 | 0 | 1323 | 0 | 1273 | 1264 | 1189 | 1286 | 1249 | 1172 | 1156 | 932 | 1126 | 3.74 | 3.74 | 3.75 | 3.66 | 3.58 | 4.01 | 3.68 | 3.94 | 3.7 | 3.66 | 3.85 | 3.83 | 3.84 | 3.92 | 3.11 | 0 | 4.02 | 3.98 | 4.12 | 4.16 | 3.79 | 3.68 | 3.68 | 3.85 | 3.49 | 3.7 | 3.67 | 0 | 3.9 | 0 | 3.66 | 3.57 | 3.7 | 3.91 | 4.05 | 3.93 | 3.61 | 4.13 | 3.7 | 93389 | 3.4951 |  |  | 242757 | 2194 | 282417 | 2220 | 259340 | 1827 | 295499 | 1873 | 15600 | 2400 | 14400 | 2400 | 22800 | 1200 | 20400 | 1200 | 73200 | 7200 | 21.62% | 96 | 129 | 76.68 |  | 78 | No scada available server OS failed
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 9098 | 9102 | 8921 | 9121 | 7893 | 9157 | 9229 | 9095 | 11061 | 9199 | 8703 | 10307 | 10350 | 10217 | 10203 | 10136 | 0 | 10056 | 10165 | 9776 | 8109 | 7878 | 8085 | 7905 | 7945 | 8076 | 7948 | 0 | 7645 | 0 | 8128 | 8073 | 8174 | 8189 | 8110 | 8021 | 8137 | 8183 | 8063 | 4.58 | 4.46 | 3.97 | 4.15 | 3.78 | 4.38 | 4.4 | 4.13 | 4.08 | 3.95 | 4.01 | 4.04 | 3.98 | 3.84 | 3.92 | 3.95 | 4.15 | 4.01 | 3.99 | 4.01 | 3.76 | 3.87 | 3.95 | 4.26 | 4.2 | 4.22 | 4.21 | 0 | 5.44 | 0 | 4.17 | 4.15 | 4.32 | 4.55 | 6.32 | 4.45 | 4.87 | 4.31 | 5.39 | 318458 | 4.0569 |  |  | 242817 | 2194 | 282475 | 2220 | 259398 | 1827 | 295560 | 1873 | 72000 | 0 | 69600 | 0 | 69600 | 0 | 73200 | 0 | 284400 | 0 | 10.69% | 96 | 7611 | 287.9 |  | 78 | No scada available server OS failed
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 23205 | 23305 | 23032 | 22992 | 22197 | 22500 | 23295 | 23308 | 25219 | 23295 | 23292 | 24410 | 24390 | 24398 | 24410 | 24123 | 0 | 24397 | 24398 | 24394 | 22199 | 22189 | 22890 | 22790 | 22379 | 22907 | 22297 | 0 | 20213 | 0 | 20098 | 20403 | 20200 | 20149 | 20056 | 20690 | 20090 | 19910 | 20753 | 7.28 | 7.74 | 7.38 | 7.5 | 6.95 | 6.64 | 7.2 | 7.59 | 7.79 | 7.37 | 7.73 | 7.52 | 7.72 | 7.67 | 7.75 | 7.66 | 8.38 | 7.44 | 8.44 | 7.02 | 6.9 | 7.2 | 7.24 | 7.4 | 7.39 | 7.05 | 6.74 | 0 | 7.37 | 0 | 6.79 | 6.65 | 6.54 | 7.02 | 7.65 | 7.66 | 6.74 | 6.53 | 7.19 | 810773 | 6.9444 |  |  | 242988 | 2194 | 282611 | 2220 | 259578 | 1827 | 295736 | 1873 | 205200 | 0 | 163200 | 0 | 216000 | 0 | 211200 | 0 | 795600 | 0 | 1.871% | 96 | 307215 | 799.17 |  | 78 | No scada available server OS failed
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 26111 | 26117 | 24950 | 26000 | 25901 | 27198 | 27943 | 27943 | 27970 | 26953 | 27021 | 26400 | 28743 | 27211 | 24273 | 27211 | 0 | 26322 | 27210 | 28210 | 25762 | 25199 | 24765 | 24945 | 25012 | 25032 | 13093 | 0 | 24110 | 0 | 23992 | 20764 | 22421 | 23887 | 24652 | 24752 | 23882 | 24889 | 24899 | 8.9 | 7.74 | 9.1 | 7.5 | 9.3 | 6.64 | 9.5 | 9.5 | 9.2 | 7.37 | 9.4 | 7.52 | 9.5 | 7.67 | 7.75 | 9.78 | 8.38 | 9.5 | 8.44 | 9.3 | 6.9 | 9.1 | 7.24 | 7.4 | 7.39 | 9.4 | 6.74 | 0 | 9.6 | 0 | 9.7 | 6.65 | 6.54 | 7.02 | 9.8 | 9.8 | 6.74 | 9.5 | 9.7 | 911743 | 7.9797 |  |  | 243190 | 2194 | 282761 | 2220 | 259777 | 1827 | 295932 | 1873 | 242400 | 0 | 180000 | 0 | 238800 | 0 | 235200 | 0 | 896400 | 0 | 1.683% | 96 | 347383 | 900.13 |  | 78 | No scada available server OS failed
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 29903 | 30897 | 30873 | 31001 | 29882 | 31032 | 28206 | 30904 | 31593 | 31145 | 31117 | 30803 | 31797 | 30959 | 29590 | 30132 | 0 | 31101 | 30999 | 31252 | 29509 | 29971 | 29672 | 29267 | 26312 | 29781 | 23621 | 0 | 27943 | 0 | 26331 | 27692 | 28815 | 25651 | 26632 | 26845 | 26817 | 23915 | 26281 | 11.02 | 11.37 | 10.51 | 10.62 | 9.47 | 11.61 | 10.28 | 10.6 | 10.77 | 11.68 | 12.36 | 9.53 | 10.37 | 10.66 | 10.77 | 10.39 | 10.02 | 11.57 | 12.25 | 11.76 | 9.7 | 10.81 | 9.89 | 9 | 10.24 | 9.95 | 9.94 | 0 | 10.13 | 0 | 10.74 | 9.3 | 9.31 | 9.29 | 9.97 | 9.38 | 9.79 | 9.55 | 10.21 | 1048241 | 9.8669 |  |  | 243402 | 2194 | 282948 | 2220 | 260007 | 1827 | 296164 | 1873 | 254400 | 0 | 224400 | 0 | 276000 | 0 | 278400 | 0 | 1033200 | 0 | 1.435% | 96 | 385829 | 1036.64 |  | 78 | No scada available server OS failed
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 26714 | 26663 | 25426 | 25951 | 26940 | 26923 | 28123 | 28457 | 28623 | 28018 | 27012 | 27590 | 27811 | 27683 | 27589 | 27918 | 0 | 27485 | 27658 | 27034 | 26134 | 25472 | 25731 | 25631 | 24273 | 25373 | 22452 | 0 | 24823 | 0 | 22620 | 23521 | 24317 | 23551 | 23268 | 24483 | 23614 | 24541 | 24219 | 8.16 | 8.53 | 8.52 | 8.33 | 8.06 | 7.29 | 8.26 | 8.84 | 9.14 | 8.25 | 8.46 | 8.72 | 8.81 | 8.84 | 8.93 | 8.7 | 0 | 7.81 | 9.46 | 7.58 | 7.3 | 8.39 | 8.02 | 8.3 | 8.2 | 7.84 | 7.75 | 0 | 8.06 | 0 | 8.19 | 7.25 | 7.54 | 7.49 | 7.96 | 8.32 | 8.57 | 7.51 | 7.47 | 933641 | 7.5603 |  |  | 243585 | 2194 | 283114 | 2220 | 260211 | 1827 | 296377 | 1873 | 219600 | 0 | 199200 | 0 | 244800 | 0 | 255600 | 0 | 919200 | 0 | 1.547% | 96 | 389661 | 922.04 |  | 78 | No scada available server OS failed
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 29650 | 31065 | 29572 | 30143 | 28124 | 29853 | 30087 | 30043 | 31110 | 28964 | 28021 | 30212 | 30310 | 30310 | 30733 | 30012 | 0 | 30321 | 30323 | 30750 | 27642 | 27345 | 28545 | 28511 | 28567 | 29265 | 29432 | 0 | 27810 | 0 | 27022 | 26243 | 27010 | 26123 | 26443 | 27432 | 27411 | 27120 | 27832 | 9.6441 | 9.3889 | 9.4898 | 9.4367 | 9.9 | 10.2554 | 10.497 | 9.5987 | 10.6 | 9.876 | 10.5 | 9.9846 | 10.209 | 10.8 | 9.6 | 10.4 | 0 | 10.3 | 10.5 | 10.0016 | 9.9 | 10.4 | 9.5017 | 10.3 | 9.3 | 9.8 | 10.6 | 0 | 9.8445 | 0 | 9.3 | 10.2 | 9.2412 | 10.3 | 9.9281 | 9.8 | 8.6328 | 9.3267 | 9.6 | 1039356 | 9.1527 |  |  | 243808 | 2194 | 283305 | 2220 | 260422 | 1827 | 296606 | 1873 | 267600 | 0 | 229200 | 0 | 253200 | 0 | 274800 | 0 | 1024800 | 0 | 1.4% | 95 | 424174 | 1027.75 |  | 78 | No scada available server OS failed
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 28485 | 29073 | 27330 | 27532 | 26843 | 27963 | 27532 | 26313 | 29763 | 26832 | 20745 | 20832 | 26556 | 30063 | 30092 | 28711 | 0 | 28585 | 28510 | 30093 | 27853 | 25573 | 26110 | 26383 | 27874 | 26384 | 26899 | 0 | 25110 | 0 | 25898 | 21740 | 22736 | 25883 | 26888 | 26862 | 25892 | 25655 | 25763 | 9.1 | 8.3 | 8.1 | 9.3 | 9.9 | 8.1 | 9.5017 | 9.9 | 9.3 | 9.8 | 8.5 | 8.72 | 9.8445 | 9.6 | 9.3 | 8.3 | 0 | 8.5 | 9.9281 | 9.8 | 9.9 | 8.5 | 8.7 | 9.5987 | 9.1 | 9.876 | 9.1 | 0 | 9 | 0 | 9.6 | 10.4 | 9.2 | 9.4 | 9.7 | 9.3 | 9.1 | 9.7 | 9.9 | 961356 | 8.5607 |  |  | 244011 | 2194 | 283474 | 2220 | 260624 | 1827 | 296821 | 1873 | 243600 | 0 | 202800 | 0 | 242400 | 0 | 258000 |  | 946800 | 0 | 1.514% | 96 | 395248 | 949.75 |  | 78 | No scada available server OS failed
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 26621 | 25462 | 26723 | 26087 | 25512 | 26578 | 26821 | 26781 | 28475 | 26598 | 26836 | 21524 | 26823 | 27931 | 28012 | 27612 | 0 | 27842 | 27812 | 26474 | 26231 | 26383 | 26543 | 26843 | 26342 | 26123 | 25432 | 0 | 24532 | 0 | 23543 | 24248 | 24319 | 24023 | 24023 | 24361 | 23221 | 23372 | 24228 | 8.9 | 7.74 | 9.1 | 7.5 | 9.3 | 6.64 | 9.5 | 9.5 | 9.2 | 7.37 | 9.4 | 7.52 | 9.5 | 7.67 | 7.75 | 9.78 | 8.38 | 9.5 | 8.44 | 9.3 | 6.9 | 9.1 | 7.24 | 7.4 | 7.39 | 9.4 | 6.74 | 0 | 9.6 | 0 | 9.7 | 6.65 | 6.54 | 7.02 | 9.8 | 9.8 | 6.74 | 9.5 | 9.7 | 930291 | 7.9797 |  |  | 244194 | 2194 | 283641 | 2220 | 260828 | 1827 | 297030 | 1873 | 219600 | 0 | 200400 | 0 | 244800 | 0 | 250800 |  | 915600 | 0 | 1.579% | 96 | 409644 | 918.69 |  | 78 | No scada available server OS failed
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 31829 | 33032 | 32371 | 32041 | 31529 | 33041 | 32702 | 32738 | 34754 | 32395 | 33123 | 29739 | 30351 | 31472 | 33023 | 32572 | 0 | 32943 | 32132 | 29523 | 29903 | 30231 | 30531 | 30741 | 30848 | 30812 | 30715 | 0 | 29732 | 0 | 28617 | 28428 | 29664 | 28843 | 29590 | 29810 | 29641 | 28701 | 29513 | 10.0091 | 9.6441 | 9.3889 | 9.4898 | 9.4367 | 9.4367 | 10.2554 | 10.497 | 9.5987 | 9.5464 | 9.876 | 9.8914 | 9.9846 | 10.209 | 9.7197 | 10.53 | 0 | 10.7129 | 9.7111 | 9.9885 | 10.0016 | 9.2499 | 0 | 9.5017 | 9.6424 | 9.4144 | 8.8698 | 0 | 9.4438 | 0 | 9.7017 | 8.829 | 8.7997 | 9.2412 | 9.4702 | 9.9281 | 8.7421 | 8.6328 | 9.8267 | 1117630 | 8.6467 |  |  | 244437 | 2194 | 283846 | 2220 | 261070 | 1827 | 297259 | 1873 | 291600 | 0 | 246000 | 0 | 290400 | 0 | 274800 |  | 1102800 | 0 | 1.327% | 96 | 465575 | 1106.03 |  | 78 | No scada available server OS failed
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 30827 | 30953 | 30752 | 31051 | 29492 | 31010 | 30831 | 30829 | 30327 | 30778 | 30556 | 31076 | 31309 | 31934 | 32031 | 32112 | 0 | 31891 | 31792 | 31668 | 29984 | 29874 | 29727 | 29965 | 29718 | 29691 | 29582 | 0 | 29408 | 0 | 28462 | 28218 | 27085 | 28083 | 28514 | 27892 | 27713 | 28227 | 28141 | 8.9 | 7.74 | 9.1 | 7.5 | 9.3 | 6.64 | 9.5 | 9.5 | 9.2 | 7.37 | 9.4 | 7.52 | 9.5 | 7.67 | 7.75 | 9.78 | 0 | 9.5 | 8.44 | 9.3 | 6.9 | 9.1 | 7.24 | 7.4 | 7.39 | 9.4 | 6.74 | 0 | 9.6 | 0 | 9.7 | 6.65 | 6.54 | 7.02 | 9.8 | 9.8 | 6.74 | 9.5 | 9.7 | 1081503 | 7.7649 |  |  | 244677 | 2194 | 284036 | 2220 | 261301 | 1827 | 297487 | 1873 | 288000 | 0 | 228000 | 0 | 277200 | 0 | 273600 |  | 1066800 | 0 | 1.359% | 0 | 0 | 1069.9 |  | 78 | No scada available server OS failed
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 19727 | 19023 | 20023 | 19045 | 15624 | 19823 | 19774 | 20043 | 21453 | 20223 | 20421 | 20541 | 21212 | 20832 | 21154 | 19032 | 0 | 21081 | 20791 | 20545 | 15943 | 16231 | 15943 | 15900 | 15749 | 15840 | 15456 | 0 | 15453 | 0 | 16745 | 16350 | 16817 | 16469 | 16743 | 16721 | 15521 | 16332 | 16632 | 5.8621 | 6.3056 | 5.2877 | 5.3705 | 5.0465 | 5.8957 | 5.8957 | 5.8117 | 6.2648 | 4.8664 | 5.6272 | 5.7042 | 5.5212 | 5.7344 | 6.0185 | 5.5628 | 0 | 5.9452 | 6.1094 | 6.4611 | 5.9728 | 4.9143 | 5.1145 | 5.336 | 5.0755 | 5.3435 | 5.0553 | 0 | 5 | 0 | 4.943 | 4.9765 | 5.2576 | 5.6703 | 5.5863 | 5.4673 | 5.2684 | 5.2848 | 5.2838 | 655212 | 5.0985 |  |  | 244812 | 2194 | 284145 | 2220 | 261454 | 1827 | 297646 | 1873 | 162000 | 0 | 130800 | 0 | 183600 | 0 | 190800 |  | 667200 | 0 | -1.83% | 0 | 0 | 676.61 |  | 78 | No scada available server OS failed
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 11261 | 10482 | 11052 | 11137 | 7172 | 11627 | 11932 | 11732 | 13735 | 11452 | 11112 | 12431 | 11521 | 12329 | 12431 | 12410 | 0 | 12323 | 12521 | 12382 | 9027 | 9210 | 9319 | 9321 | 8230 | 9421 | 7945 | 0 | 9021 | 0 | 8332 | 8432 | 8253 | 8443 | 8393 | 7532 | 8027 | 8138 | 8332 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 0 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 366418 | 4.6851 |  |  | 244868 | 2194 | 284205 | 2220 | 261539 | 1827 | 297747 | 1873 | 67200 | 0 | 72000 | 0 | 102000 | 0 | 121200 |  | 362400 | 0 | 1.097% | 0 | 0 | 365.82 |  | 78 | No scada available server OS failed
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 16930 | 17730 | 17832 | 17892 | 13712 | 17819 | 17115 | 17852 | 19862 | 17723 | 17791 | 19102 | 18882 | 19192 | 18723 | 19124 | 0 | 18243 | 19082 | 18884 | 13731 | 13702 | 13636 | 13639 | 13590 | 13616 | 13651 | 0 | 13041 | 0 | 14767 | 14592 | 14601 | 14568 | 14541 | 14504 | 14364 | 14610 | 14732 | 5.63 | 6.04 | 5.55 | 5.6 | 6.19 | 6.25 | 5.75 | 5.53 | 5.55 | 5.54 | 5.96 | 5.74 | 5.9 | 5.75 | 5.91 | 5.82 | 0 | 6.15 | 6.47 | 6.22 | 5.08 | 6.26 | 5.87 | 5.93 | 5.43 | 5.57 | 5.63 | 0 | 5.51 | 0 | 5.16 | 5.45 | 5.48 | 5.59 | 5.63 | 5.54 | 5.55 | 5.62 | 5.36 | 583375 | 5.2874 |  |  | 244991 | 2194 | 284300 | 2220 | 261668 | 1827 | 297896 | 1873 | 147600 | 0 | 114000 | 0 | 154800 | 0 | 178800 |  | 595200 | 0 | -2.027% | 1 | 4353 | 598.78 |  | 78 | No scada available server OS failed
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 25663 | 20943 | 24454 | 24435 | 24432 | 25265 | 25672 | 25636 | 25303 | 25332 | 25832 | 23653 | 25621 | 25762 | 25920 | 25612 | 0 | 25309 | 25630 | 25434 | 22276 | 23276 | 22376 | 23754 | 22487 | 23486 | 23354 | 0 | 23418 | 0 | 21298 | 21316 | 21276 | 21264 | 21176 | 21254 | 21285 | 21217 | 21290 | 7.28 | 7.74 | 7.38 | 7.5 | 6.95 | 6.64 | 7.2 | 7.59 | 7.79 | 7.37 | 7.73 | 7.52 | 7.72 | 7.67 | 7.75 | 7.66 | 0 | 7.44 | 8.44 | 7.02 | 6.9 | 7.2 | 7.24 | 7.4 | 7.39 | 7.05 | 6.74 | 0 | 7.37 | 0 | 6.79 | 6.65 | 6.54 | 7.02 | 7.65 | 7.66 | 6.74 | 6.53 | 7.19 | 851711 | 6.7295 |  |  | 245178 | 2194 | 284447 | 2220 | 261843 | 1827 | 298085 | 1873 | 224400 | 0 | 176400 | 0 | 210000 | 0 | 226800 |  | 837600 | 0 | 1.657% | 96 | 288903 | 840.11 |  | 78 | No scada available server OS failed
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 32497 | 26743 | 33083 | 31234 | 32456 | 33975 | 33976 | 32509 | 35763 | 32865 | 33008 | 34187 | 33764 | 33653 | 33857 | 33743 | 0 | 32632 | 33764 | 33798 | 31176 | 31498 | 31241 | 31211 | 31542 | 31323 | 31230 | 0 | 31102 | 0 | 29353 | 29554 | 29513 | 28990 | 29448 | 29151 | 29334 | 29313 | 29160 | 10.0091 | 11.6441 | 11.3889 | 11.4898 | 11.4367 | 11.4367 | 10.2554 | 10.497 | 9.5987 | 11.5464 | 9.876 | 9.8914 | 9.9846 | 10.209 | 9.7197 | 10.53 | 0 | 10.7129 | 9.7111 | 9.9885 | 10.0016 | 11.2499 | 0 | 9.5017 | 9.6424 | 11.4144 | 8.8698 | 0 | 10.4438 | 0 | 9.7017 | 8.829 | 10.7997 | 10.2412 | 9.4702 | 9.9281 | 10.7421 | 10.6328 | 9.8267 | 1141646 | 9.2621 |  |  | 245423 | 2194 | 284644 | 2220 | 262076 | 1827 | 298349 | 1873 | 294000 | 0 | 236400 | 0 | 279600 | 0 | 316800 |  | 1126800 | 0 | 1.3% | 96 | 503826 | 1130.55 |  | 78 | No scada available server OS failed
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 23365 | 23351 | 23379 | 23421 | 22372 | 23113 | 23409 | 23341 | 25214 | 23326 | 23406 | 24354 | 24254 | 24260 | 24350 | 24309 | 0 | 24213 | 24265 | 24871 | 22310 | 22442 | 22364 | 22432 | 22345 | 22312 | 22323 | 0 | 22127 | 0 | 20262 | 20183 | 20131 | 20324 | 20212 | 20164 | 20178 | 20134 | 20212 | 7.28 | 7.74 | 7.38 | 7.5 | 6.95 | 6.64 | 7.2 | 7.59 | 7.79 | 7.37 | 7.73 | 7.52 | 7.72 | 7.67 | 7.75 | 7.66 | 0 | 7.44 | 8.44 | 7.02 | 6.9 | 7.2 | 7.24 | 7.4 | 7.39 | 7.05 | 6.74 | 0 | 7.37 | 0 | 6.79 | 6.65 | 6.54 | 7.02 | 7.65 | 7.66 | 6.74 | 6.53 | 7.19 | 813028 | 6.7295 |  |  | 245577 | 2194 | 284780 | 2220 | 262255 | 1827 | 298545 | 1873 | 184800 | 0 | 163200 | 0 | 214800 | 0 | 235200 |  | 798000 | 0 | 1.848% | 96 | 262228 | 801.43 |  | 78 | No scada available server OS failed
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | 23955 | 23954 | 23950 | 24000 | 21100 | 23955 | 23954 | 23956 | 27822 | 24000 | 23955 | 27822 | 27820 | 27824 | 27822 | 27824 | 0 | 27820 | 27822 | 27822 | 21150 | 19050 | 22110 | 22090 | 20160 | 21100 | 21101 | 0 | 21100 | 0 | 17260 | 19181 | 19230 | 19380 | 19220 | 19151 | 19239 | 19350 | 19460 | 6.3056 | 5.2877 | 5.3705 | 5.0465 | 5.8957 | 5.8957 | 5.8117 | 6.2648 | 4.8664 | 5.6272 | 5.7042 | 5.5212 | 5.7344 | 6.0185 | 5.5628 | 6.2912 | 0 | 6.1094 | 6.4611 | 5.9728 | 4.9143 | 5.1145 | 5.336 | 5.0755 | 5.3435 | 5.0553 | 5.4 | 0 | 5.5 | 0 | 4.9765 | 5.2576 | 5.6703 | 5.5863 | 5.4673 | 5.2684 | 5.2848 | 5.2838 | 6.9 | 826509 | 5.1585 |  |  | 245736 | 2194 | 284920 | 2220 | 262434 | 1827 | 298753 | 1873 | 190800 | 0 | 168000 | 0 | 214800 | 0 | 249600 |  | 823200 | 0 | 0.4004% | 93 | 271409 | 826.51 |  | 78 | No scada available server OS failed
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | 21422 | 21420 | 21424 | 21418 | 24240 | 21424 | 21430 | 21414 | 25021 | 21423 | 21422 | 25030 | 25014 | 25022 | 25025 | 25019 | 0 | 25020 | 25024 | 25022 | 24260 | 24252 | 24248 | 24250 | 16280 | 24550 | 24200 | 0 | 24001 | 0 | 16279 | 16281 | 16278 | 16282 | 16270 | 16290 | 16285 | 16275 | 16280 | 5.0755 | 5.3435 | 5.0553 | 5.8 | 5 | 5.4 | 4.943 | 4.9765 | 5.2576 | 5.6703 | 5.5863 | 5.4673 | 5.2684 | 5.2848 | 5.2838 | 5.0755 | 0 | 5.0553 | 5.8 | 5.3 | 5.9 | 4.943 | 4.9765 | 5.2576 | 5.6703 | 5.5863 | 5.4673 | 0 | 5.2848 | 0 | 5.5 | 5.3 | 6.7 | 6.1 | 5.2 | 5.7 | 5.2 | 5.9 | 5.7 | 774795 | 5.0007 |  |  | 245871 | 2194 | 285081 | 2220 | 262594 | 1827 | 298940 | 1873 | 162000 | 0 | 193200 | 0 | 192000 | 0 | 224400 |  | 771600 | 0 | 0.4124% | 96 | 203118 | 774.795 |  | 78 | No scada available server OS failed
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | 27690 | 27684 | 27693 | 27683 | 21300 | 27695 | 27684 | 27688 | 29000 | 27689 | 27683 | 29855 | 29855 | 29852 | 29580 | 29855 | 0 | 28360 | 29841 | 29845 | 20964 | 20876 | 20850 | 21242 | 29001 | 18876 | 21902 | 0 | 20400 | 0 | 29005 | 28995 | 28985 | 29015 | 28988 | 29012 | 29010 | 28990 | 29000 | 9.1 | 7.24 | 7.4 | 7.39 | 9.4 | 6.74 | 6.5 | 9.6 | 6.3 | 9.7 | 6.65 | 6.54 | 7.02 | 9.8 | 9.8 | 6.74 | 0 | 9.7 | 7.74 | 9.1 | 7.5 | 9.3 | 6.64 | 9.5 | 9.5 | 9.2 | 7.37 | 0 | 7.52 | 0 | 7.67 | 7.75 | 9.78 | 8.38 | 9.5 | 8.44 | 9.3 | 6.9 | 6.2 | 971643 | 7.5105 |  |  | 246112 | 2194 | 285219 | 2220 | 262801 | 1827 | 299161 | 1873 | 289200 | 0 | 165600 | 0 | 248400 | 0 | 265200 |  | 968400 | 0 | 0.3338% | 96 | 362922 | 971.643 |  | 78 | No scada available server OS failed
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | 23910 | 24850 | 23114 | 17850 | 21550 | 23822 | 24818 | 25424 | 23009 | 24600 | 26280 | 24924 | 26910 | 26920 | 26800 | 22430 | 0 | 24505 | 26702 | 26515 | 21570 | 21530 | 21555 | 21545 | 18930 | 21560 | 21540 | 0 | 21550 | 0 | 18910 | 18920 | 18935 | 18905 | 18925 | 18915 | 18930 | 18910 | 18920 | 6.9 | 7.2 | 7.24 | 7.4 | 7.39 | 7.05 | 6.74 | 7.1 | 7.37 | 6.9 | 6.79 | 6.65 | 6.54 | 7.02 | 7.65 | 7.66 | 0 | 6.53 | 7.19 | 6.9 | 7.2 | 7.24 | 7.4 | 7.39 | 7.05 | 6.74 | 7.1 | 0 | 6.8 | 0 | 6.65 | 6.54 | 7.02 | 7.65 | 7.66 | 6.74 | 6.53 | 7.19 | 7.8 | 804983 | 6.5364 |  |  | 246269 | 2194 | 285362 | 2220 | 262979 | 1827 | 299351 | 1873 | 188400 | 0 | 171600 | 0 | 213600 | 0 | 228000 |  | 801600 | 0 | 0.4203% | 96 | 328624 | 804.983 |  | 78 | No scada available server OS failed
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | 22232 | 22220 | 22218 | 22614 | 24101 | 22226 | 22964 | 22230 | 22488 | 21814 | 21480 | 22482 | 22489 | 22460 | 22497 | 22483 | 0 | 22499 | 22502 | 22501 | 24550 | 24452 | 24600 | 24102 | 20625 | 24099 | 24400 | 0 | 22500 | 0 | 19450 | 22175 | 21605 | 21195 | 21350 | 21250 | 22010 | 21180 | 21200 | 7.2 | 7.1 | 7.37 | 6.9 | 7.2 | 6.65 | 7.2 | 7.3 | 6.74 | 7.1 | 7.37 | 6.9 | 7.2 | 6.65 | 7.8 | 7.2 | 0 | 7.1 | 7.37 | 7.2 | 6.79 | 7.6 | 7.2 | 6.2 | 7.2 | 7.3 | 7.2 | 0 | 7 | 0 | 6.9 | 7.5 | 7.02 | 7.65 | 7.66 | 7 | 7.4 | 7.19 | 7.4 | 807243 | 6.6092 |  |  | 246445 | 2194 | 285522 | 2220 | 263145 | 1827 | 299519 | 1873 | 211200 | 0 | 192000 | 0 | 199200 | 0 | 201600 |  | 804000 | 0 | 0.4017% | 96 | 287329 | 807.243 |  | 78 | No scada available server OS failed
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | 30933 | 30912 | 31052 | 30936 | 33246 | 31546 | 30913 | 30932 | 30066 | 30937 | 30964 | 30989 | 31002 | 32056 | 31089 | 27505 | 0 | 32045 | 32013 | 32019 | 34031 | 34033 | 33218 | 33231 | 25421 | 33252 | 33200 | 0 | 33225 | 0 | 24434 | 24422 | 24411 | 22503 | 24441 | 24408 | 24400 | 24434 | 24407 | 10.0091 | 9.6441 | 9.3889 | 9.4898 | 9.4367 | 9.4367 | 10.2554 | 10.497 | 9.5987 | 9.5464 | 9.876 | 9.8914 | 9.9846 | 10.209 | 9.7197 | 10.53 | 0 | 10.7129 | 9.7111 | 9.9885 | 10.0016 | 9.2499 | 0 | 9.5017 | 9.6424 | 9.4144 | 8.8698 | 0 | 9.4438 | 0 | 9.7017 | 8.829 | 8.7997 | 9.2412 | 9.4702 | 9.9281 | 8.7421 | 8.6328 | 9.8267 | 1068626 | 8.6467 |  |  | 246654 | 2194 | 285712 | 2220 | 263383 | 1827 | 299758 | 1873 | 250800 | 0 | 228000 | 0 | 285600 | 0 | 286800 |  | 1051200 | 0 | 1.631% | 96 | 450779 | 1068.626 |  | 78 | No scada available server OS failed
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | 12488 | 12499 | 12502 | 12452 | 9293 | 12498 | 12456 | 12385 | 14622 | 12480 | 12640 | 14687 | 14676 | 14623 | 14828 | 14599 | 0 | 13935 | 14789 | 14741 | 9348 | 9289 | 8953 | 9202 | 8100 | 9255 | 9235 | 0 | 9225 | 0 | 8120 | 7901 | 8006 | 8311 | 8298 | 8142 | 8133 | 8090 | 8120 | 4.85 | 5.26 | 4.68 | 5.05 | 5 | 5.11 | 4.84 | 4.48 | 5.09 | 4.83 | 5.29 | 5.04 | 5.15 | 5.24 | 4.99 | 5.44 | 0 | 5.48 | 5.43 | 5.67 | 4.5 | 5.29 | 4.82 | 5.04 | 5.32 | 5.01 | 5.03 | 0 | 4.81 | 0 | 4.95 | 5.01 | 4.99 | 5.16 | 5.21 | 4.87 | 5.18 | 4.85 | 5.19 | 398921 | 4.6705 |  |  | 246721 | 2194 | 285773 | 2220 | 263476 | 1827 | 299867 | 1873 | 80400 | 0 | 73200 | 0 | 111600 | 0 | 130800 |  | 396000 | 0 | 0.7322% | 96 | 51198 | 398.921 |  | 78 | No scada available server OS failed
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | 12245 | 16569 | 16602 | 16549 | 13458 | 16623 | 16576 | 16612 | 20622 | 16511 | 16513 | 20698 | 20623 | 20612 | 20586 | 20699 | 0 | 20689 | 20530 | 20541 | 13450 | 13623 | 13277 | 13427 | 10015 | 13473 | 13442 | 0 | 13450 | 0 | 9978 | 11985 | 12022 | 11942 | 11966 | 11888 | 10058 | 10034 | 10112 | 5.59 | 6.18 | 5.43 | 5.42 | 5.97 | 6.06 | 5.51 | 5.15 | 5.98 | 5.33 | 6.31 | 5.92 | 5.96 | 5.77 | 5.83 | 5.9 | 0 | 5.8 | 5.74 | 6.66 | 6.01 | 6.2 | 6.1 | 5.88 | 6 | 5.88 | 5.94 | 0 | 5.74 | 0 | 5.52 | 5.76 | 6.04 | 6.02 | 5.85 | 6.03 | 5.99 | 5.42 | 6.19 | 548000 | 5.4123 |  |  | 246812 | 2194 | 285862 | 2220 | 263596 | 1827 | 300021 | 1873 | 109200 | 0 | 106800 | 0 | 144000 | 0 | 184800 |  | 544800 | 0 | 0.5839% | 96 | 228131 | 548 |  | 78 | No scada available server OS failed
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | 11475 | 11523 | 11498 | 10813 | 9135 | 11568 | 11467 | 11485 | 12355 | 11453 | 11515 | 12398 | 12314 | 12316 | 12403 | 12369 | 0 | 12355 | 12334 | 12356 | 9131 | 9157 | 9005 | 9006 | 7490 | 9025 | 8987 | 0 | 6877 | 0 | 6267 | 7370 | 7345 | 7397 | 7402 | 7389 | 7362 | 7312 | 7366 | 4.85 | 5.37 | 4.76 | 4.77 | 5.09 | 5.19 | 4.8 | 4.87 | 5.25 | 4.98 | 5.45 | 5.28 | 5.32 | 5.14 | 5.09 | 5.27 | 0 | 5.36 | 6.59 | 5.63 | 5.4 | 5.44 | 4.66 | 4.98 | 4.95 | 4.71 | 4.88 | 0 | 4.86 | 0 | 4.59 | 4.73 | 4.88 | 4.88 | 5.07 | 5.05 | 4.83 | 4.74 | 5.01 | 357020 | 4.6851 |  |  | 246872 | 2194 | 285920 | 2220 | 263681 | 1827 | 300113 | 1873 | 72000 | 0 | 69600 | 0 | 102000 | 0 | 110400 |  | 354000 | 0 | 0.8459% | 96 | 58822 | 357.02 |  | 78 | No scada available server OS failed
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | 5933 | 5995 | 5680 | 6010 | 4589 | 5933 | 5930 | 5982 | 6600 | 5982 | 5933 | 6595 | 6605 | 6602 | 6398 | 6594 | 0 | 6420 | 6783 | 6932 | 4986 | 4865 | 4738 | 4680 | 3660 | 4580 | 3492 | 0 | 4510 | 0 | 3520 | 3665 | 3654 | 3654 | 3900 | 3850 | 3650 | 3650 | 3660 | 3.93 | 3.99 | 3.9 | 3.78 | 3.4 | 4.13 | 3.8 | 4.05 | 3.76 | 3.86 | 4.06 | 3.98 | 4.04 | 4.03 | 3.88 | 4.18 | 0 | 4.09 | 4.29 | 4.06 | 4.5 | 3.75 | 3.14 | 3.53 | 3.02 | 3.42 | 3.48 | 0 | 3.31 | 0 | 3.29 | 3.51 | 3.38 | 3.42 | 3.69 | 3.98 | 3.43 | 3.41 | 3.47 | 186210 | 3.46 |  |  | 246902 | 2194 | 285950 | 2220 | 263725 | 1827 | 300162 | 1873 | 36000 | 0 | 36000 | 0 | 52800 | 0 | 58800 |  | 183600 | 0 | 1.402% | 96 | 21904 | 186.21 |  | 78 | No scada available server OS failed
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [78 empty] | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
Formulas:
Month Year = [Date]-DAY([Date])+1
Days = DAY(EOMONTH([1]!Input_Raw[[#This Row],[Date]],0))
Date = [Date, row above]+1

## Modelling New (hidden)
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | Bugt Capacity | CC*Bugt | Capacity | 78
1 | April | 4 | 2021-04-01 | 2021 | FY22 | 30 |  |  | 5.6333 |  |  | 11863.8432 | 80 |  |  | 0 |  |  | 395.4614 | 0 | 0 | 20.6% | [5 empty] | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5% |  |  | Hourly reactive power bugt | 3.9
2 | May | 5 | 2021-05-01 | 2021 | FY22 | 31 |  |  | 6.5667 |  |  | 20092.2163 | 80 |  |  | 0 |  |  | 648.136 | 0 | 0 | 33.76% | [5 empty] | 5.9682 | 6.1861 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5% |  |  | Day | 93.6
3 | June | 6 | 2021-06-01 | 2021 | FY22 | 30 |  |  | 6.5667 |  |  | 17455.8067 | 80 |  |  | 0 |  |  | 581.8602 | 0 | 0 | 30.31% | [5 empty] | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
4 | July | 7 | 2021-07-01 | 2021 | FY22 | 31 |  |  | 7.6 |  |  | 21077.401 | 80 |  |  | 0 |  |  | 679.9162 | 0 | 0 | 35.41% | [5 empty] | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
5 | August | 8 | 2021-08-01 | 2021 | FY22 | 31 |  |  | 6.8667 |  |  | 22159.7165 | 80 |  |  | 0 |  |  | 714.8296 | 0 | 0 | 37.23% | [5 empty] | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
6 | September | 9 | 2021-09-01 | 2021 | FY22 | 30 |  |  | 5.0333 |  |  | 9726.9638 | 80 |  |  | 0 |  |  | 324.2321 | 0 | 0 | 16.89% | [5 empty] | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
7 | October | 10 | 2021-10-01 | 2021 | FY22 | 31 |  |  | 3.9667 |  |  | 5924.9837 | 80 |  |  | 0 |  |  | 191.1285 | 0 | 0 | 9.955% | [5 empty] | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
8 | November | 11 | 2021-11-01 | 2021 | FY22 | 30 |  |  | 4.0333 |  |  | 5661.3427 | 80 |  |  | 0 |  |  | 188.7114 | 0 | 0 | 9.829% | [5 empty] | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
9 | December | 12 | 2021-12-01 | 2021 | FY22 | 31 |  |  | 4.4333 |  |  | 6618.7757 | 80 |  |  | 0 |  |  | 213.5089 | 0 | 0 | 11.12% | [5 empty] | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
10 | January | 1 | 2022-01-01 | 2022 | FY22 | 31 |  |  | 3.8 |  |  | 4606.7789 | 80 |  |  | 0 |  |  | 148.6058 | 0 | 0 | 7.74% | [5 empty] | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
11 | February | 2 | 2022-02-01 | 2022 | FY22 | 28 |  |  | 4.3 |  |  | 5619.7152 | 80 |  |  | 0 |  |  | 200.7041 | 0 | 0 | 10.45% | [5 empty] | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
12 | March | 3 | 2022-03-01 | 2022 | FY22 | 31 |  |  | 4.6 |  |  | 7950.8563 | 80 |  |  | 0 |  |  | 256.4792 | 0 | 0 | 13.36% | [5 empty] | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
13 | April | 4 | 2022-04-01 | 2022 | FY23 | 30 |  |  | 5.6333 |  |  | 11863.8432 | 80 |  |  | 0 |  |  | 395.4614 | 0 | 0 | 20.6% | [5 empty] | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
14 | May | 5 | 2022-05-01 | 2022 | FY23 | 31 |  |  | 6.5667 |  |  | 20092.2163 | 80 |  |  | 0 |  |  | 648.136 | 0 | 0 | 33.76% | [5 empty] | 5.9682 | 6.1861 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
15 | June | 6 | 2022-06-01 | 2022 | FY23 | 30 |  |  | 6.5667 |  |  | 17455.8067 | 80 |  |  | 0 |  |  | 581.8602 | 0 | 0 | 30.31% | [5 empty] | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
16 | July | 7 | 2022-07-01 | 2022 | FY23 | 31 |  |  | 7.6 |  |  | 21077.401 | 80 |  |  | 0 |  |  | 679.9162 | 0 | 0 | 35.41% | [5 empty] | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
17 | August | 8 | 2022-08-01 | 2022 | FY23 | 31 |  |  | 6.8667 |  |  | 22159.7165 | 80 |  |  | 0 |  |  | 714.8296 | 0 | 0 | 37.23% | [5 empty] | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
18 | September | 9 | 2022-09-01 | 2022 | FY23 | 30 |  |  | 5.0333 |  |  | 9726.9638 | 80 |  |  | 0 |  |  | 324.2321 | 0 | 0 | 16.89% | [5 empty] | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
19 | October | 10 | 2022-10-01 | 2022 | FY23 | 31 |  |  | 3.9667 |  |  | 5924.9837 | 80 |  |  | 0 |  |  | 191.1285 | 0 | 0 | 9.955% | [5 empty] | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
20 | November | 11 | 2022-11-01 | 2022 | FY23 | 30 |  |  | 4.0333 |  |  | 5661.3427 | 80 |  |  | 0 |  |  | 188.7114 | 0 | 0 | 9.829% | [5 empty] | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
21 | December | 12 | 2022-12-01 | 2022 | FY23 | 31 |  |  | 4.4333 |  |  | 6618.7757 | 80 |  |  | 0 |  |  | 213.5089 | 0 | 0 | 11.12% | [5 empty] | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
22 | January | 1 | 2023-01-01 | 2023 | FY23 | 31 |  |  | 3.8 |  |  | 4606.7789 | 80 |  |  | 0 |  |  | 148.6058 | 0 | 0 | 7.74% | [5 empty] | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
23 | February | 2 | 2023-02-01 | 2023 | FY23 | 28 |  |  | 4.3 |  |  | 5619.7152 | 80 |  |  | 0 |  |  | 200.7041 | 0 | 0 | 10.45% | [5 empty] | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
24 | March | 3 | 2023-03-01 | 2023 | FY23 | 31 |  |  | 4.6 |  |  | 7950.8563 | 80 |  |  | 0 |  |  | 256.4792 | 0 | 0 | 13.36% | [5 empty] | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
25 | April | 4 | 2023-04-01 | 2023 | FY24 | 30 |  |  | 5.6333 |  |  | 11000 | 80 |  |  | 0 |  |  | 366.6667 | 0 | 0 | 19.1% | [5 empty] | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
26 | May | 5 | 2023-05-01 | 2023 | FY24 | 31 |  |  | 6.5667 |  |  | 19240 | 80 |  |  | 0 |  |  | 620.6452 | 0 | 0 | 32.33% | [5 empty] | 5.9682 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
27 | June | 6 | 2023-06-01 | 2023 | FY24 | 30 |  |  | 6.5667 |  |  | 16180 | 80 |  |  | 0 |  |  | 539.3333 | 0 | 0 | 28.09% | [5 empty] | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
28 | July | 7 | 2023-07-01 | 2023 | FY24 | 31 |  |  | 7.6 |  |  | 20190 | 80 |  |  | 0 |  |  | 651.2903 | 0 | 0 | 33.92% | [5 empty] | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
29 | August | 8 | 2023-08-01 | 2023 | FY24 | 31 |  |  | 6.8667 |  |  | 21230 | 80 |  |  | 0 |  |  | 684.8387 | 0 | 0 | 35.67% | [5 empty] | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
30 | September | 9 | 2023-09-01 | 2023 | FY24 | 30 |  |  | 5.0333 |  |  | 9020 | 80 |  |  | 0 |  |  | 300.6667 | 0 | 0 | 15.66% | [5 empty] | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
31 | October | 10 | 2023-10-01 | 2023 | FY24 | 31 |  |  | 3.9667 |  |  | 6030 | 80 |  |  | 0 |  |  | 194.5161 | 0 | 0 | 10.13% | [5 empty] | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
32 | November | 11 | 2023-11-01 | 2023 | FY24 | 30 |  |  | 4.0333 |  |  | 5580 | 80 |  |  | 0 |  |  | 186 | 0 | 0 | 9.688% | [5 empty] | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
33 | December | 12 | 2023-12-01 | 2023 | FY24 | 31 |  |  | 4.4333 |  |  | 6740 | 80 |  |  | 0 |  |  | 217.4194 | 0 | 0 | 11.32% | [5 empty] | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
34 | January | 1 | 2024-01-01 | 2024 | FY24 | 31 |  |  | 3.8 |  |  | 4700 | 80 |  |  | 0 |  |  | 151.6129 | 0 | 0 | 7.897% | [5 empty] | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
35 | February | 2 | 2024-02-01 | 2024 | FY24 | 29 |  |  | 4.3 |  |  | 5360 | 80 |  |  | 0 |  |  | 184.8276 | 0 | 0 | 9.626% | [5 empty] | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
36 | March | 3 | 2024-03-01 | 2024 | FY24 | 31 |  |  | 4.6 |  |  | 8110 | 80 |  |  | 0 |  |  | 261.6129 | 0 | 0 | 13.63% | [5 empty] | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
37 | April | 4 | 2024-04-01 | 2024 | FY25 | 30 |  |  | 5.6333 |  |  | 11919.2 | 80 |  |  | 0 |  |  | 397.3067 | 0 | 0 | 20.69% | [5 empty] | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
38 | May | 5 | 2024-05-01 | 2024 | FY25 | 31 |  |  | 6.5667 |  |  | 20174.9 | 80 |  |  | 0 |  |  | 650.8032 | 0 | 773.2742 | 33.9% | [5 empty] | 5.9682 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
39 | June | 6 | 2024-06-01 | 2024 | FY25 | 30 |  |  | 6.5667 |  |  | 17527.1 | 80 |  |  | 0 |  |  | 584.2367 | 0 | 0 | 30.43% | [5 empty] | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
40 | July | 7 | 2024-07-01 | 2024 | FY25 | 31 |  |  | 7.6 |  |  | 21165.2 | 80 |  |  | 0 |  |  | 682.7484 | 0 | 0 | 35.56% | [5 empty] | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
41 | August | 8 | 2024-08-01 | 2024 | FY25 | 31 |  |  | 6.8667 |  |  | 22256.9 | 80 |  |  | 0 |  |  | 717.9645 | 0 | 0 | 37.39% | [5 empty] | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
42 | September | 9 | 2024-09-01 | 2024 | FY25 | 30 |  |  | 5.0333 |  |  | 9773.8 | 80 |  |  | 0 |  |  | 325.7933 | 0 | 0 | 16.97% | [5 empty] | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
43 | October | 10 | 2024-10-01 | 2024 | FY25 | 31 |  |  | 3.9667 |  |  | 5947 | 80 |  |  | 0 |  |  | 191.8387 | 0 | 0 | 9.992% | [5 empty] | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
44 | November | 11 | 2024-11-01 | 2024 | FY25 | 30 |  |  | 4.0333 |  |  | 5683.6 | 80 |  |  | 0 |  |  | 189.4533 | 0 | 0 | 9.867% | [5 empty] | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
45 | December | 12 | 2024-12-01 | 2024 | FY25 | 31 |  |  | 4.4333 |  |  | 6645.2 | 80 |  |  | 0 |  |  | 214.3613 | 0 | 0 | 11.16% | [5 empty] | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
46 | January | 1 | 2025-01-01 | 2025 | FY25 | 31 |  |  | 3.8 |  |  | 4628.1 | 80 |  |  | 0 |  |  | 149.2935 | 0 | 0 | 7.776% | [5 empty] | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
47 | February | 2 | 2025-02-01 | 2025 | FY25 | 28 |  |  | 4.3 |  |  | 5610.2 | 80 |  |  | 0 |  |  | 200.3643 | 0 | 0 | 10.44% | [5 empty] | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
48 | March | 3 | 2025-03-01 | 2025 | FY25 | 31 |  |  | 4.6 |  |  | 7990.5 | 80 |  |  | 3 |  |  | 257.7581 | 773.2742 | 773.2742 | 13.42% | 13.42% | 13.42% | 80 | 80 |  | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
49 | April | 4 | 2025-04-01 | 2025 | FY26 | 30 |  |  | 5.6333 |  |  | 10226.6542 | 78 |  |  | 30 |  |  | 340.8885 | 10226.6542 | 10226.6542 | 18.21% | 18.21% | 18.21% | 78 | 78 |  | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
50 | May | 5 | 2025-05-01 | 2025 | FY26 | 31 |  |  | 6.5667 |  |  | 17310.0402 | 78 |  |  | 31 |  |  | 558.3884 | 17310.0402 | 27536.6944 | 29.83% | 29.83% | 24.11% | 78 | 78 |  | 5.9682 | 6.1861 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
51 | June | 6 | 2025-06-01 | 2025 | FY26 | 30 |  |  | 6.5667 |  |  | 15038.2603 | 78 |  |  | 30 |  |  | 501.2753 | 15038.2603 | 42574.9546 | 26.78% | 26.78% | 24.99% | 78 | 78 |  | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
52 | July | 7 | 2025-07-01 | 2025 | FY26 | 31 |  |  | 7.6 |  |  | 18159.7324 | 78 |  |  | 10 |  |  | 585.7978 | 5857.9782 | 48432.9328 | 31.29% | 31.29% | 25.62% | 25.1613 | 64.7903 |  | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
53 | August | 8 | 2025-08-01 | 2025 | FY26 | 31 |  |  | 6.8667 |  |  | 19096.4226 | 78 |  |  | 0 |  |  | 616.0136 | 0 | 48432.9328 | 32.91% |  | 25.62% | 0 | 51.8323 |  | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
54 | September | 9 | 2025-09-01 | 2025 | FY26 | 30 |  |  | 5.0333 |  |  | 8385.892 | 78 |  |  | 0 |  |  | 279.5297 | 0 | 48432.9328 | 14.93% |  | 25.62% |  | 51.8323 |  | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
55 | October | 10 | 2025-10-01 | 2025 | FY26 | 31 |  |  | 3.9667 |  |  | 5102.5337 | 78 |  |  | 0 |  |  | 164.5979 | 0 | 48432.9328 | 8.793% |  | 25.62% |  | 51.8323 |  | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
56 | November | 11 | 2025-11-01 | 2025 | FY26 | 30 |  |  | 4.0333 |  |  | 4876.5139 | 78 |  |  | 0 |  |  | 162.5505 | 0 | 48432.9328 | 8.683% |  | 25.62% |  | 51.8323 |  | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
57 | December | 12 | 2025-12-01 | 2025 | FY26 | 31 |  |  | 4.4333 |  |  | 5701.5948 | 78 |  |  | 0 |  |  | 183.9224 | 0 | 48432.9328 | 9.825% |  | 25.62% |  | 51.8323 |  | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
58 | January | 1 | 2026-01-01 | 2026 | FY26 | 31 |  |  | 3.8 |  |  | 3970.8953 | 78 |  |  | 0 |  |  | 128.0934 | 0 | 48432.9328 | 6.843% |  | 25.62% |  | 51.8323 |  | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
59 | February | 2 | 2026-02-01 | 2026 | FY26 | 28 |  |  | 4.3 |  |  | 4813.5808 | 78 |  |  | 0 |  |  | 171.9136 | 0 | 48432.9328 | 9.183% |  | 25.62% |  | 51.8323 |  | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
60 | March | 3 | 2026-03-01 | 2026 | FY26 | 31 |  |  | 4.6 |  |  | 6855.8432 | 78 |  |  | 0 |  |  | 221.1562 | 0 | 48432.9328 | 11.81% |  | 25.62% |  | 51.8323 |  | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## WTG_BD
Sr. No. | Financial Year | Calendar Year | Operating Year | Month | Date | Affected WTG | SPV | Consumer | Plant Equivalent Weightage | Error Code | Error Text | Breakdown Description | Stoppage Type | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Fault Category | Paired WTG for Enegy based MA | Paired WTG Generation for loss calculation | Estimated Energy Loss (kWh) | Special Remarks | PTW No. | Job Card No.
1 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeure | G28 | 2420 | 2418.3194 | None
2 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeure | G28 | 2420 | 2418.3194 | None
3 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 16:05 | 16:05 | 16:19 | 0 | 0.23333 | 0.23333 | Reset then restore wtg. | Close | 0.0059829 | WTG Breakdown Maintenance | G03 | 3376 | 32.8222 | None
4 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 20:21 | 20:21 | 20:26 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G03 | 3376 | 11.7222 | None
5 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G05 | PWEGPL | MSEDCL | 2.564% | 5204 | Emergency Series Not OK | BD |  | 20:16 | 20:16 | 20:21 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G22 | 2780 | 9.6528 | None
6 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G06 | PWEGPL | MSEDCL | 2.564% | 700 | PLC-Converter Communication Error | BD |  | 10:50 | 11:40 | 12:29 | 0.83333 | 0.81667 | 1.65 | CCU reset then restore wtg. | Close | 0.042308 | WTG Breakdown Maintenance | G03 | 3376 | 232.1 | None
7 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G21 | PWEGPL | MSEDCL | 2.564% | 202 | Low Pressure On Brake Circuit | BD |  | 20:17 | 20:17 | 20:22 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G22 | 2780 | 9.6528 | None
8 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G22 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 20:18 | 20:18 | 20:23 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G21 | 4216 | 14.6389 | None
9 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G33 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 8:34 | 14:14 | 17:06 | 5.6667 | 2.8667 | 8.5333 | Checked related circuit found ok the restore wtg. | Close | 0.2188 | WTG Breakdown Maintenance | G34 | 2688 | 955.7333 | None
10 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G34 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 9:03 | 9:03 | 9:08 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G35 | 2976 | 10.3333 | None
11 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G34 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 17:26 | 17:26 | 17:35 | 0 | 0.15 | 0.15 | Reset then restore wtg. | Close | 0.0038462 | WTG Breakdown Maintenance | G35 | 2976 | 18.6 | None
12 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 9:15 | 9:15 | 9:20 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G37 | 2818 | 9.7847 | None
13 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 10:16 | 10:16 | 10:21 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G37 | 2818 | 9.7847 | None
14 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 10:54 | 10:54 | 10:59 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G37 | 2818 | 9.7847 | None
15 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 11:44 | 11:44 | 13:29 | 0 | 1.75 | 1.75 | Reset then restore wtg. | Close | 0.044872 | WTG Breakdown Maintenance | G37 | 2818 | 205.4792 | None
16 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-29 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 15:04 | 15:28 | 17:43 | 0.4 | 2.25 | 2.65 | Checked related circuit found ok then restore wtg. | Close | 0.067949 | WTG Breakdown Maintenance | G37 | 2818 | 311.1542 | None
17 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-30 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeure | G28 | 1552 | 1550.9222 | None
18 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-30 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeure | G28 | 1552 | 1550.9222 | None
19 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-30 | G01 | PWEGPL | MSEDCL | 2.564% | 125 | Yaw Motors Over Current Protection | BD |  | 11:46 | 14:08 | 18:42 | 2.3667 | 4.5667 | 6.9333 | Checked related circuit found yaw motor failure so replaced yaw motor with new one then restore wtg. | Close | 0.17778 | WTG Breakdown Maintenance | G07 | 3645 | 1053 | None
20 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-30 | G02 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 2:18 | 3:03 | 7:49 | 0.75 | 4.7667 | 5.5167 | Checked related circuit found CCU coolant cooling motor failure so replaced then start wtg. | Close | 0.14145 | WTG Breakdown Maintenance | G04 | 3336 | 766.8167 | None
21 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-30 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 14:49 | 14:49 | 15:00 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0047009 | WTG Breakdown Maintenance | G03 | 2170 | 16.5764 | None
22 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-30 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 16:22 | 18:56 | 18:59 | 2.5667 | 0.05 | 2.6167 | Reboot then restore wtg. | Close | 0.067094 | WTG Breakdown Maintenance | G03 | 2170 | 236.5903 | None
23 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-30 | G27 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 12:21 | 12:21 | 17:04 | 0 | 4.7167 | 4.7167 | Manual stop for blade bush gap inspection work. | Close | 0.12094 | WTG Force Majeaure | G25 | 2822 | 554.6014 | None
24 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-30 | G28 | PWEGPL | MSEDCL | 2.564% | 524 | High Temperature Of The Control Module | BD |  | 0:45 | 1:50 | 1:58 | 1.0833 | 0.13333 | 1.2167 | Reboot then restore wtg. | Close | 0.031197 | WTG Breakdown Maintenance | G30 | 2712 | 137.4833 | None
25 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-30 | G28 | PWEGPL | MSEDCL | 2.564% | 524 | High Temperature Of The Control Module | BD |  | 11:28 | 17:24 | 17:42 | 5.9333 | 0.3 | 6.2333 | Check related circuit found ok then restore wtg. | Close | 0.15983 | WTG Breakdown Maintenance | G30 | 2712 | 704.3667 | None
26 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-30 | G35 | PWEGPL | MSEDCL | 2.564% | 103 | CCW Feedback Failure | BD |  | 10:06 | 10:06 | 10:16 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0042735 | WTG Breakdown Maintenance | G36 | 3150 | 21.875 | None
27 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-30 | G35 | PWEGPL | MSEDCL | 2.564% | 103 | CCW Feedback Failure | BD |  | 10:22 | 12:31 | 16:00 | 2.15 | 3.4833 | 5.6333 | Check related circuit found yaw motor failure so replace with new one then restore wtg. | Close | 0.14444 | WTG Breakdown Maintenance | G36 | 3150 | 739.375 | None
28 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-30 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 12:21 | 12:21 | 12:26 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G39 | 2708 | 9.4028 | None
29 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 6006 | 6001.8292 | None
30 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 6006 | 6001.8292 | None
31 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G01 | PWEGPL | MSEDCL | 2.564% | 5205 | Magnetothermic Of The Stator Protection Failure Or Door Open | BD |  | 13:13 | 13:13 | 13:17 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0017094 | WTG Breakdown Maintenance | G07 | 6040 | 16.7778 | None
32 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G01 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 13:31 | 13:31 | 13:41 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0042735 | WTG Breakdown Maintenance | G07 | 6040 | 41.9444 | None
33 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G03 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 11:10 | 11:10 | 13:10 | 0 | 2 | 2 | Manual stop for blade bush gap inspection work. | Close | 0.051282 | WTG Force Majeaure | G04 | 7992 | 666 | None
34 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G04 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | BD |  | 15:46 | 15:46 | 15:51 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G03 | 8994 | 31.2292 | None
35 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 16:13 | 16:13 | 16:35 | 0 | 0.36667 | 0.36667 | Auto reset | Close | 0.0094017 | WTG Breakdown Maintenance | G03 | 8994 | 137.4083 | None
36 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G06 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD |  | 16:32 | 16:32 | 16:37 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G03 | 8994 | 31.2292 | None
37 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G07 | PWEGPL | MSEDCL | 2.564% | 2102 | PLC Module Failure | BD |  | 16:31 | 19:28 | 19:31 | 2.95 | 0.05 | 3 | Reboot then restore wtg. | Close | 0.076923 | WTG Breakdown Maintenance | G01 | 9436 | 1179.5 | None
38 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G07 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 20:18 | 20:18 | 20:23 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G01 | 9436 | 32.7639 | None
39 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G09 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 19:20 | 19:46 | 19:46 | 0.43333 | 0 | 0.43333 | Reset then restore wtg. | Close | 0.011111 | WTG Breakdown Maintenance | G12 | 5883 | 106.2208 | None
40 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G10 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD |  | 16:34 | 16:34 | 16:39 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G11 | 9876 | 34.2917 | None
41 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G10 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD |  | 17:13 | 17:13 | 17:18 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G11 | 9876 | 34.2917 | None
42 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G10 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD |  | 17:30 | 17:30 | 17:35 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G11 | 9876 | 34.2917 | None
43 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G10 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD |  | 18:54 | 19:45 | 19:45 | 0.85 | 0 | 0.85 | Reset then restore wtg. | Close | 0.021795 | WTG Breakdown Maintenance | G11 | 9876 | 349.775 | None
44 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G11 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD |  | 16:38 | 16:38 | 16:43 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G10 | 7384 | 25.6389 | None
45 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 16:25 | 16:25 | 16:29 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0017094 | WTG Breakdown Maintenance | G13 | 7698 | 21.3833 | None
46 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G12 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 16:31 | 16:31 | 16:50 | 0 | 0.31667 | 0.31667 | Reset then restore wtg. | Close | 0.0081197 | WTG Breakdown Maintenance | G13 | 7698 | 101.5708 | None
47 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 16:52 | 16:52 | 18:05 | 0 | 1.2167 | 1.2167 | Reset then restore wtg. | Close | 0.031197 | WTG Breakdown Maintenance | G13 | 7698 | 390.2458 | None
48 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G12 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 18:20 | 18:20 | 18:30 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0042735 | WTG Breakdown Maintenance | G13 | 7698 | 53.4583 | None
49 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 20:17 | 21:57 | 22:16 | 1.6667 | 0.31667 | 1.9833 | Reboot then restore wtg. | Close | 0.050855 | WTG Breakdown Maintenance | G13 | 7698 | 636.1542 | None
50 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G13 | PWEGPL | MSEDCL | 2.564% | 550 | Generator Fans Thermal Relay Triggered Too Long | BD |  | 15:10 | 15:50 | 16:02 | 0.66667 | 0.2 | 0.86667 | Reset then restore wtg. | Close | 0.022222 | WTG Breakdown Maintenance | G14 | 7408 | 267.5111 | None
51 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G13 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD |  | 20:34 | 20:34 | 20:45 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0047009 | WTG Breakdown Maintenance | G14 | 7408 | 56.5889 | None
52 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G14 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 8:30 | 11:11 | 13:00 | 2.6833 | 1.8167 | 4.5 | Check related circuit found ok then restore wtg. | Close | 0.11538 | WTG Breakdown Maintenance | G15 | 6173 | 1157.4375 | None
53 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G14 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 16:27 | 16:27 | 16:37 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0042735 | WTG Breakdown Maintenance | G15 | 6173 | 42.8681 | None
54 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G15 | PWEGPL | MSEDCL | 2.564% | 722 | Wind Vane Failure Alarm | BD |  | 16:24 | 17:56 | 17:56 | 1.5333 | 0 | 1.5333 | Reset then restore wtg. | Close | 0.039316 | WTG Breakdown Maintenance | G14 | 7408 | 473.2889 | None
55 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G16 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 16:31 | 16:31 | 16:36 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G17 | 8016 | 27.8333 | None
56 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G16 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD |  | 17:55 | 17:55 | 18:00 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G17 | 8016 | 27.8333 | None
57 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G16 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 18:12 | 18:27 | 18:45 | 0.25 | 0.3 | 0.55 | Auto reset | Close | 0.014103 | WTG Breakdown Maintenance | G17 | 8016 | 183.7 | None
58 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G16 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD |  | 20:41 | 20:41 | 20:46 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G17 | 8016 | 27.8333 | None
59 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G16 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 21:21 | 21:28 | 21:33 | 0.11667 | 0.083333 | 0.2 | Auto reset | Close | 0.0051282 | WTG Breakdown Maintenance | G17 | 8016 | 66.8 | None
60 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G17 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 18:22 | 18:22 | 18:39 | 0 | 0.28333 | 0.28333 | Reboot then restore wtg. | Close | 0.007265 | WTG Breakdown Maintenance | G16 | 7064 | 83.3944 | None
61 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G18 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 16:31 | 16:31 | 16:47 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.0068376 | WTG Breakdown Maintenance | G19 | 8564 | 95.1556 | None
62 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G18 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 18:12 | 18:12 | 18:35 | 0 | 0.38333 | 0.38333 | Auto reset | Close | 0.0098291 | WTG Breakdown Maintenance | G19 | 8564 | 136.7861 | None
63 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G18 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 20:38 | 21:29 | 21:30 | 0.85 | 0.016667 | 0.86667 | Auto reset | Close | 0.022222 | WTG Breakdown Maintenance | G19 | 8564 | 309.2556 | None
64 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G21 | PWEGPL | MSEDCL | 2.564% | 5228 | Preload Failure | BD |  | 19:38 | 23:50 | 23:54 | 4.2 | 0.066667 | 4.2667 | Reboot then restore wtg. | Close | 0.1094 | WTG Breakdown Maintenance | G22 | 3920 | 696.8889 | None
65 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G22 | PWEGPL | MSEDCL | 2.564% | 402 | Gearbox Oil Level Low | BD |  | 19:37 | 23:36 | 23:59 | 3.9833 | 0.38333 | 4.3667 | work in progress | Open | 0.11197 | WTG Breakdown Maintenance | G21 | 6850 | 1246.3194 | None
66 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G23 | PWEGPL | MSEDCL | 2.564% | 2102 | PLC Module Failure | BD |  | 14:11 | 14:45 | 17:26 | 0.56667 | 2.6833 | 3.25 | Check related circuit found RTD module failure so repalced with new one then restore wtg. | Close | 0.083333 | WTG Breakdown Maintenance | G22 | 3920 | 530.8333 | None
67 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G23 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 21:07 | 21:28 | 21:29 | 0.35 | 0.016667 | 0.36667 | Reset then restore wtg. | Close | 0.0094017 | WTG Breakdown Maintenance | G22 | 3920 | 59.8889 | None
68 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G26 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 3:27 | 3:27 | 4:21 | 0 | 0.9 | 0.9 | Reset then restore wtg. | Close | 0.023077 | WTG Breakdown Maintenance | G32 | 5080 | 190.5 | None
69 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G26 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 9:10 | 11:32 | 16:53 | 2.3667 | 5.35 | 7.7167 | Checked related circuit found no leakage then top-up 5 liter HU oil then restore wtg. | Close | 0.19786 | WTG Breakdown Maintenance | G32 | 5080 | 1633.3611 | None
70 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G26 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 19:20 | 19:20 | 19:50 | 0 | 0.5 | 0.5 | Reset then restore wtg. | Close | 0.012821 | WTG Breakdown Maintenance | G32 | 5080 | 105.8333 | None
71 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G27 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD |  | 21:02 | 21:02 | 21:07 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G25 | 7082 | 24.5903 | None
72 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G30 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 19:37 | 19:37 | 23:59 | 0 | 4.3667 | 4.3667 | work in progress | Open | 0.11197 | WTG Breakdown Maintenance | G28 | 6006 | 1092.7583 | None
73 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G32 | PWEGPL | MSEDCL | 2.564% | 2102 | PLC Module Failure | BD |  | 17:55 | 19:35 | 19:39 | 1.6667 | 0.066667 | 1.7333 | Reboot then restore wtg. | Close | 0.044444 | WTG Breakdown Maintenance | G26 | 5480 | 395.7778 | None
74 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G33 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 20:18 | 20:18 | 20:23 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G34 | 7996 | 27.7639 | None
75 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G34 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 17:54 | 17:54 | 17:59 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G33 | 6703 | 23.2743 | None
76 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G35 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 19:20 | 19:20 | 23:59 | 0 | 4.65 | 4.65 | work in progress | Open | 0.11923 | WTG Breakdown Maintenance | G36 | 4792 | 928.45 | None
77 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 8:34 | 8:34 | 8:39 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G35 | 4764 | 16.5417 | None
78 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G36 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD |  | 9:21 | 9:21 | 9:26 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G35 | 4764 | 16.5417 | None
79 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G36 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD |  | 10:43 | 10:48 | 10:48 | 0.083333 | 0 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G35 | 4764 | 16.5417 | None
80 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 11:32 | 11:32 | 11:37 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G35 | 4764 | 16.5417 | None
81 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 12:15 | 12:15 | 13:08 | 0 | 0.88333 | 0.88333 | Reset then restore wtg. | Close | 0.02265 | WTG Breakdown Maintenance | G35 | 4764 | 175.3417 | None
82 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G36 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD |  | 13:42 | 13:42 | 14:11 | 0 | 0.48333 | 0.48333 | Reset then restore wtg. | Close | 0.012393 | WTG Breakdown Maintenance | G35 | 4764 | 95.9417 | None
83 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G36 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 19:20 | 19:20 | 23:59 | 0 | 4.65 | 4.65 | work in progress | Open | 0.11923 | WTG Breakdown Maintenance | G35 | 4764 | 923.025 | None
84 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G37 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 8:35 | 14:10 | 19:07 | 5.5833 | 4.95 | 10.5333 | Checked related circuit found leakage form yaw caliper so replaced yaw caliper seal then top-up 30 liter oil then restore wtg. | Close | 0.27009 | WTG Breakdown Maintenance | G36 | 4792 | 2103.1556 | None
85 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G38 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 19:20 | 19:20 | 19:52 | 0 | 0.53333 | 0.53333 | Reset then restore wtg. | Close | 0.013675 | WTG Breakdown Maintenance | G39 | 7552 | 167.8222 | None
86 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G39 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 19:20 | 19:20 | 19:52 | 0 | 0.53333 | 0.53333 | Reset then restore wtg. | Close | 0.013675 | WTG Breakdown Maintenance | G38 | 6680 | 148.4444 | None
87 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G40 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD |  | 7:06 | 7:06 | 7:11 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G39 | 7552 | 26.2222 | None
88 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 14:45 | 14:45 | 14:50 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G39 | 7552 | 26.2222 | None
89 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 15:40 | 15:40 | 15:45 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G39 | 7552 | 26.2222 | None
90 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 17:53 | 17:53 | 17:58 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G39 | 7552 | 26.2222 | None
91 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G40 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD |  | 18:24 | 19:19 | 19:35 | 0.91667 | 0.26667 | 1.1833 | Reboot then restore wtg. | Close | 0.030342 | WTG Breakdown Maintenance | G39 | 7552 | 372.3556 | None
92 | 2025 | 2025 | Year_3 | 2025-03-01 | 2025-03-31 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 19:39 | 19:39 | 23:59 | 0 | 4.3333 | 4.3333 | work in progress | Open | 0.11111 | WTG Breakdown Maintenance | G39 | 7552 | 1363.5556 | None
93 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 6260 | 6255.6528 | None
94 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 6260 | 6255.6528 | None
95 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G01 | PWEGPL | MSEDCL | 2.564% | 107 | Yawing Motor Thermal Relays | BD |  | 9:27 | 9:27 | 9:49 | 0 | 0.36667 | 0.36667 | Auto reset | Close | 0.0094017 | WTG Breakdown Maintenance | G07 | 6951 | 106.1958 | None
96 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G01 | PWEGPL | MSEDCL | 2.564% | 125 | Yaw Motors Over Current Protection | BD |  | 11:22 | 15:30 | 17:17 | 4.1333 | 1.7833 | 5.9167 | Checked and found MPCB tripped so recorrect it then restore wtg. | Close | 0.15171 | WTG Breakdown Maintenance | G07 | 6951 | 1713.6146 | None
97 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G01 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD |  | 17:18 | 17:18 | 20:22 | 0 | 3.0667 | 3.0667 | Checked and found Balde A proportional valve failure so replaced with new one then restore wtg | Close | 0.078632 | WTG Breakdown Maintenance | G07 | 6951 | 888.1833 | None
98 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G04 | PWEGPL | MSEDCL | 2.564% | 5202 | Stator Contactor Failure | BD |  | 22:09 | 22:09 | 22:14 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G03 | 5356 | 18.5972 | None
99 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G08 | PWEGPL | MSEDCL | 2.564% | 110 | Yaw Sensor Wiring Error | BD |  | 4:44 | 7:12 | 7:28 | 2.4667 | 0.26667 | 2.7333 | Untwist then restore wtg. | Close | 0.070085 | WTG Breakdown Maintenance | G08 | 6252 | 712.0333 | None
100 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G12 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 2:44 | 2:44 | 2:49 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G13 | 5686 | 19.7431 | None
101 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 12:50 | 12:50 | 12:55 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G13 | 5686 | 19.7431 | None
102 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G13 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 22:35 | 22:35 | 23:59 | 0 | 1.4 | 1.4 | work in progress | Open | 0.035897 | WTG Breakdown Maintenance | G14 | 4942 | 288.2833 | None
103 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G14 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 22:19 | 22:19 | 22:24 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G15 | 4039 | 14.0243 | None
104 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G14 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 23:03 | 23:59 | 23:59 | 0.93333 | 0 | 0.93333 | work in progress | Open | 0.023932 | WTG Breakdown Maintenance | G15 | 4039 | 157.0722 | None
105 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G15 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 22:35 | 22:35 | 23:18 | 0 | 0.71667 | 0.71667 | Auto reset | Close | 0.018376 | WTG Breakdown Maintenance | G16 | 5316 | 158.7417 | None
106 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G16 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 4:58 | 4:58 | 5:03 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G17 | 6766 | 23.4931 | None
107 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G16 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 22:56 | 23:52 | 23:59 | 0.93333 | 0.11667 | 1.05 | Reboot then restore wtg. | Close | 0.026923 | WTG Breakdown Maintenance | G17 | 6766 | 296.0125 | None
108 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G17 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 23:13 | 23:13 | 23:59 | 0 | 0.76667 | 0.76667 | work in progress | Open | 0.019658 | WTG Breakdown Maintenance | G16 | 5316 | 169.8167 | None
109 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G18 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 22:23 | 22:23 | 23:59 | 0 | 1.6 | 1.6 | Auto reset | Close | 0.041026 | WTG Breakdown Maintenance | G19 | 6788 | 452.5333 | None
110 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G19 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 23:11 | 23:11 | 23:59 | 0 | 0.8 | 0.8 | work in progress | Open | 0.020513 | WTG Breakdown Maintenance | G18 | 6572 | 219.0667 | None
111 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G20 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 23:03 | 23:15 | 23:59 | 0.2 | 0.73333 | 0.93333 | work in progress | Open | 0.023932 | WTG Breakdown Maintenance | G19 | 6788 | 263.9778 | None
112 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G22 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 22:35 | 23:11 | 23:59 | 0.6 | 0.8 | 1.4 | work in progress | Close | 0.035897 | WTG Breakdown Maintenance | G05 | 4726 | 275.6833 | None
113 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G30 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 2:29 | 13:56 | 2.4833 | 11.45 | 13.9333 | Checked and found Netural relay failure so rplaced with new one then restore wtg. | Close | 0.35726 | WTG Breakdown Maintenance | G28 | 6260 | 3634.2778 | None
114 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G32 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 4:37 | 4:37 | 5:10 | 0 | 0.55 | 0.55 | Reboot then restore wtg. | Close | 0.014103 | WTG Breakdown Maintenance | G26 | 5834 | 133.6958 | None
115 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G32 | PWEGPL | MSEDCL | 2.564% | 700 | PLC-Converter Communication Error | BD |  | 13:25 | 15:37 | 15:44 | 2.2 | 0.11667 | 2.3167 | Reboot then restore wtg. | Close | 0.059402 | WTG Breakdown Maintenance | G26 | 5834 | 563.1431 | None
116 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G32 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 23:04 | 23:04 | 23:59 | 0 | 0.91667 | 0.91667 | work in progress | Close | 0.023504 | WTG Breakdown Maintenance | G26 | 5834 | 222.8264 | None
117 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G33 | PWEGPL | MSEDCL | 2.564% | 907 | Emergency Series HUB Trigger | BD |  | 23:21 | 23:21 | 23:26 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G34 | 7280 | 25.2778 | None
118 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G35 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 0:00 | 1:26 | 3:11 | 1.4333 | 1.75 | 3.1833 | Reboot then restore wtg. | Close | 0.081624 | WTG Breakdown Maintenance | G36 | 3390 | 449.6458 | None
119 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G36 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 0:00 | 3:59 | 15:59 | 3.9833 | 12 | 15.9833 | Checked and found balluf sensor cable failure so replaced with new one then restore then restore | Close | 0.40983 | WTG Breakdown Maintenance | G37 | 7150 | 4761.7014 | None
120 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G38 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 4:44 | 5:23 | 5:23 | 0.65 | 0 | 0.65 | Reset then restore wtg. | Close | 0.016667 | WTG Breakdown Maintenance | G39 | 6772 | 183.4083 | None
121 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G38 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 6:18 | 6:18 | 11:49 | 0 | 5.5167 | 5.5167 | Checked and found no leakage then tou-up 5 litre oil then restore wtg. | Close | 0.14145 | WTG Breakdown Maintenance | G39 | 6772 | 1556.6194 | None
122 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G38 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | Manual stop |  | 11:49 | 11:49 | 15:32 | 0 | 3.7167 | 3.7167 | Manual stop for blade bush gap inspection work | Close | 0.095299 | WTG Unscheduled Maintenance | G39 | 6772 | 1048.7194 | None
123 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 23:26 | 23:36 | 23:36 | 0.16667 | 0 | 0.16667 | Auto reset | Close | 0.0042735 | WTG Breakdown Maintenance | G40 | 3752 | 26.0556 | None
124 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 0:00 | 4:42 | 5:19 | 4.7 | 0.61667 | 5.3167 | Auto reset | Close | 0.13632 | WTG Breakdown Maintenance | G39 | 6772 | 1500.1861 | None
125 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 6:00 | 11:13 | 11:24 | 5.2167 | 0.18333 | 5.4 | Reboot then restore wtg. | Close | 0.13846 | WTG Breakdown Maintenance | G39 | 6772 | 1523.7 | None
126 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 15:49 | 16:13 | 16:15 | 0.4 | 0.033333 | 0.43333 | Reboot then restore wtg. | Close | 0.011111 | WTG Breakdown Maintenance | G39 | 6772 | 122.2722 | None
127 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 22:23 | 22:39 | 23:04 | 0.26667 | 0.41667 | 0.68333 | Reboot then restore wtg. | Close | 0.017521 | WTG Breakdown Maintenance | G39 | 6772 | 192.8139 | None
128 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 10142 | 10134.9569 | None
129 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 10142 | 10134.9569 | None
130 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G02 | PWEGPL | MSEDCL | 2.564% | 5225 | Fault In Analog Electronic Power Supply | BD |  | 1:21 | 3:58 | 4:36 | 2.6167 | 0.63333 | 3.25 | Reset CCU tchen restore wtg. | Close | 0.083333 | WTG Breakdown Maintenance | G04 | 5956 | 806.5417 | None
131 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G04 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 4:13 | 5:25 | 8:30 | 1.2 | 3.0833 | 4.2833 | Checked related circuit found MPCB failure so replaced with new one then restore wtg. | Close | 0.10983 | WTG Breakdown Maintenance | G03 | 10570 | 1886.4514 | None
132 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G04 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 8:30 | 11:59 | 11:59 | 3.4833 | 0 | 3.4833 | Reset then restore wtg. | Close | 0.089316 | WTG Breakdown Maintenance | G03 | 10570 | 1534.1181 | None
133 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G12 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 3:18 | 3:18 | 3:38 | 0 | 0.33333 | 0.33333 | Auto reset | Close | 0.008547 | WTG Breakdown Maintenance | G13 | 11088 | 154 | None
134 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G12 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 13:16 | 13:26 | 13:27 | 0.16667 | 0.016667 | 0.18333 | Reset then restore wtg. | Close | 0.0047009 | WTG Breakdown Maintenance | G13 | 11088 | 84.7 | None
135 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G13 | PWEGPL | MSEDCL | 2.564% | 5228 | Preload Failure | BD |  | 1:57 | 2:30 | 3:26 | 0.55 | 0.93333 | 1.4833 | Found addon block loose so tight it then restore wtg. | Close | 0.038034 | WTG Breakdown Maintenance | G14 | 12636 | 780.975 | None
136 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD |  | 7:04 | 7:04 | 7:09 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G14 | 12636 | 43.875 | None
137 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD |  | 7:20 | 7:20 | 7:25 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G14 | 12636 | 43.875 | None
138 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD |  | 7:47 | 7:47 | 7:52 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G14 | 12636 | 43.875 | None
139 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD |  | 8:21 | 8:21 | 8:46 | 0 | 0.41667 | 0.41667 | Reset then restore wtg. | Close | 0.010684 | WTG Breakdown Maintenance | G14 | 12636 | 219.375 | None
140 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD |  | 10:17 | 10:17 | 10:22 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G14 | 12636 | 43.875 | None
141 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD |  | 10:40 | 10:40 | 10:45 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G14 | 12636 | 43.875 | None
142 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G14 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 0:00 | 2:07 | 2:19 | 2.1167 | 0.2 | 2.3167 | Reset then restore wtg. | Close | 0.059402 | WTG Breakdown Maintenance | G15 | 14796 | 1428.225 | None
143 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G16 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 0:00 | 0:18 | 0:28 | 0.3 | 0.16667 | 0.46667 | Reboot then restore wtg. | Close | 0.011966 | WTG Breakdown Maintenance | G17 | 15820 | 307.6111 | None
144 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G16 | PWEGPL | MSEDCL | 2.564% | 444 | Gearbox Pump Thermal Relay Triggered and High Gearbox Oil Temperature | BD |  | 3:24 | 3:24 | 9:08 | 0 | 5.7333 | 5.7333 | Reset then restore wtg. | Close | 0.14701 | WTG Breakdown Maintenance | G17 | 15820 | 3779.2222 | None
145 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G16 | PWEGPL | MSEDCL | 2.564% | 412 | Gearbox Fan Thermal Relays | BD |  | 9:13 | 9:13 | 12:01 | 0 | 2.8 | 2.8 | Reset then restore wtg. | Close | 0.071795 | WTG Breakdown Maintenance | G17 | 15820 | 1845.6667 | None
146 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G17 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 0:00 | 0:39 | 1:01 | 0.65 | 0.36667 | 1.0167 | Reboot then restore wtg. | Close | 0.026068 | WTG Breakdown Maintenance | G16 | 7036 | 298.0528 | None
147 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G17 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 8:04 | 8:04 | 8:09 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G16 | 7036 | 24.4306 | None
148 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G18 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 8:09 | 8:09 | 8:14 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G19 | 17394 | 60.3958 | None
149 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G22 | PWEGPL | MSEDCL | 2.564% | 5228 | Preload Failure | BD |  | 0:00 | 10:26 | 10:54 | 10.4333 | 0.46667 | 10.9 | Found addon block malfunction so replaced it then restore wtg. | Close | 0.27949 | WTG Breakdown Maintenance | G05 | 11540 | 5241.0833 | None
150 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G22 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD |  | 12:14 | 12:14 | 12:24 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0042735 | WTG Breakdown Maintenance | G05 | 11540 | 80.1389 | None
151 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G22 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 13:39 | 13:39 | 14:49 | 0 | 1.1667 | 1.1667 | Reset then restore wtg. | Close | 0.029915 | WTG Breakdown Maintenance | G05 | 11540 | 560.9722 | None
152 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G22 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 14:49 | 14:49 | 17:52 | 0 | 3.05 | 3.05 | Manual stop for Blade bush gap inspection work | Close | 0.078205 | WTG Force Majeaure | G05 | 11540 | 1466.5417 | None
153 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G22 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD |  | 18:53 | 22:29 | 22:35 | 3.6 | 0.1 | 3.7 | Reboot then restore wtg. | Close | 0.094872 | WTG Breakdown Maintenance | G05 | 11540 | 1779.0833 | None
154 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G26 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 5:33 | 5:33 | 5:38 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G32 | 2722 | 9.4514 | None
155 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G26 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 10:48 | 10:48 | 10:53 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G32 | 2722 | 9.4514 | None
156 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G26 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 12:49 | 12:49 | 12:54 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G32 | 2722 | 9.4514 | None
157 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G32 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 0:00 | 10:45 | 10:50 | 10.75 | 0.083333 | 10.8333 | Reboot then restore wtg. | Close | 0.27778 | WTG Breakdown Maintenance | G26 | 12938 | 5840.0694 | None
158 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G32 | PWEGPL | MSEDCL | 2.564% | 700 | PLC-Converter Communication Error | BD |  | 19:39 | 23:10 | 23:11 | 3.5167 | 0.016667 | 3.5333 | Reset then restore wtg. | Close | 0.090598 | WTG Breakdown Maintenance | G26 | 12938 | 1904.7611 | None
159 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G32 | PWEGPL | MSEDCL | 2.564% | 700 | PLC-Converter Communication Error | BD |  | 23:20 | 23:23 | 23:59 | 0.05 | 0.6 | 0.65 | work in progress | Close | 0.016667 | WTG Breakdown Maintenance | G26 | 12938 | 350.4042 | None
160 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 8:11 | 8:11 | 8:16 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G38 | 11404 | 39.5972 | None
161 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 11:51 | 11:51 | 11:56 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G38 | 11404 | 39.5972 | None
162 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 19:46 | 19:46 | 19:57 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0047009 | WTG Breakdown Maintenance | G38 | 11404 | 87.1139 | None
163 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | G40 | PWEGPL | MSEDCL | 2.564% | 812 | Blade Position Meas. Error | BD |  | 7:40 | 10:58 | 10:58 | 3.3 | 0 | 3.3 | Reset then restore wtg. | Close | 0.084615 | WTG Breakdown Maintenance | G39 | 11460 | 1575.75 | None
164 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 6354 | 6349.5875 | None
165 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 6354 | 6349.5875 | None
166 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G04 | PWEGPL | MSEDCL | 2.564% | 1825 | Automatics Not Ok | BD |  | 6:16 | 6:16 | 6:21 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G03 | 6462 | 22.4375 | None
167 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G04 | PWEGPL | MSEDCL | 2.564% | 1825 | Automatics Not Ok | BD |  | 7:58 | 7:58 | 8:03 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G03 | 6462 | 22.4375 | None
168 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G04 | PWEGPL | MSEDCL | 2.564% | 1825 | Automatics Not Ok | BD |  | 16:14 | 16:14 | 16:19 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G03 | 6462 | 22.4375 | None
169 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G06 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 18:10 | 19:00 | 19:32 | 0.83333 | 0.53333 | 1.3667 | Checked and found SF-6 breaker tripped so charge SF-6 breaker then chen all motor found ok then restore wtg. | Close | 0.035043 | WTG Breakdown Maintenance | G03 | 6462 | 367.975 | None
170 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G06 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 20:01 | 21:47 | 23:59 | 1.7667 | 2.2 | 3.9667 | work in progress | Open | 0.10171 | WTG Breakdown Maintenance | G03 | 6462 | 1068.025 | None
171 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G07 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 3:43 | 3:43 | 6:53 | 0 | 3.1667 | 3.1667 | Reset then restore wtg. | Close | 0.081197 | WTG Breakdown Maintenance | G01 | 7048 | 929.9444 | None
172 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G07 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 18:42 | 19:50 | 19:50 | 1.1333 | 0 | 1.1333 | Reset then restore wtg. | Close | 0.02906 | WTG Breakdown Maintenance | G01 | 7048 | 332.8222 | None
173 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G07 | PWEGPL | MSEDCL | 2.564% | 2102 | PLC Module Failure | BD |  | 20:38 | 20:38 | 23:59 | 0 | 3.35 | 3.35 | work in progress | Close | 0.085897 | WTG Breakdown Maintenance | G01 | 7048 | 983.7833 | None
174 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD |  | 11:31 | 11:31 | 11:36 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G12 | 8930 | 31.0069 | None
175 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G16 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 19:40 | 22:08 | 22:40 | 2.4667 | 0.53333 | 3 | Reboot then restore wtg. | Close | 0.076923 | WTG Breakdown Maintenance | G17 | 10152 | 1269 | None
176 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G16 | PWEGPL | MSEDCL | 2.564% | 5248 | Active Crowbar IGBT Errors | BD |  | 23:51 | 23:51 | 23:59 | 0 | 0.13333 | 0.13333 | work in progress | Close | 0.0034188 | WTG Breakdown Maintenance | G17 | 10152 | 56.4 | None
177 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G18 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 19:46 | 19:46 | 19:51 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G19 | 10280 | 35.6944 | None
178 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G18 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 20:11 | 22:52 | 22:54 | 2.6833 | 0.033333 | 2.7167 | Reset then restore wtg. | Close | 0.069658 | WTG Breakdown Maintenance | G19 | 10280 | 1163.6389 | None
179 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G25 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 12:01 | 14:11 | 15:25 | 2.1667 | 1.2333 | 3.4 | Checked related circuit found no leakage then restore wtg. | Close | 0.087179 | WTG Breakdown Maintenance | G27 | 6588 | 933.3 | None
180 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G32 | PWEGPL | MSEDCL | 2.564% | 700 | PLC-Converter Communication Error | BD |  | 0:07 | 1:35 | 1:45 | 1.4667 | 0.16667 | 1.6333 | Reset then restore wtg. | Close | 0.04188 | WTG Breakdown Maintenance | G26 | 7248 | 493.2667 | None
181 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G32 | PWEGPL | MSEDCL | 2.564% | 700 | PLC-Converter Communication Error | BD |  | 6:12 | 7:21 | 12:06 | 1.15 | 4.75 | 5.9 | Checked related circuit found module failure so replace module then found nacelle to hub cable one core failure so used spare cable core then restore wtg. | Close | 0.15128 | WTG Breakdown Maintenance | G26 | 7248 | 1781.8 | None
182 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G33 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 11:59 | 13:04 | 13:11 | 1.0833 | 0.11667 | 1.2 | Reboot then restore wtg. | Close | 0.030769 | WTG Breakdown Maintenance | G34 | 3472 | 173.6 | None
183 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G33 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 13:13 | 13:49 | 15:17 | 0.6 | 1.4667 | 2.0667 | Checked related circuit found pressure switch and solenid valve cable failure so replaced with new one the restore wtg. | Close | 0.052991 | WTG Breakdown Maintenance | G34 | 6772 | 583.1444 | None
184 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G34 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 20:31 | 23:59 | 23:59 | 3.4667 | 0 | 3.4667 | work in progress | Close | 0.088889 | WTG Breakdown Maintenance | G33 | 5908 | 853.3778 | None
185 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G36 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | BD |  | 15:39 | 15:39 | 17:07 | 0 | 1.4667 | 1.4667 | Manual stop for blade bush gap inspection work | Close | 0.037607 | WTG Breakdown Maintenance | G37 | 6498 | 397.1 | None
186 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G38 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 1:36 | 11:09 | 12:23 | 9.55 | 1.2333 | 10.7833 | checked related circuit found MPCB tripped so correct it then restore wtg. | Close | 0.2765 | WTG Breakdown Maintenance | G39 | 4518 | 2029.9625 | None
187 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G39 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD |  | 20:31 | 20:31 | 20:48 | 0 | 0.28333 | 0.28333 | Auto reset | Close | 0.007265 | WTG Breakdown Maintenance | G38 | 6232 | 73.5722 | None
188 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G40 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD |  | 14:32 | 14:32 | 14:37 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G40 | 6148 | 21.3472 | None
189 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G40 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 20:07 | 20:07 | 20:42 | 0 | 0.58333 | 0.58333 | Auto reset | Close | 0.014957 | WTG Breakdown Maintenance | G40 | 6148 | 149.4306 | None
190 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | G40 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 21:53 | 21:53 | 21:58 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G40 | 6148 | 21.3472 | None
191 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 4658 | 4654.7653 | None
192 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 4658 | 4654.7653 | None
193 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G03 | PWEGPL | MSEDCL | 2.564% | 110 | Yaw Sensor Wiring Error | BD |  | 12:18 | 14:00 | 14:24 | 1.7 | 0.4 | 2.1 | Untwist then restore wtg. | Close | 0.053846 | WTG Breakdown Maintenance | G04 | 884 | 77.35 | None
194 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G04 | PWEGPL | MSEDCL | 2.564% | 1825 | Automatics Not Ok | BD |  | 0:43 | 1:46 | 11:06 | 1.05 | 9.3333 | 10.3833 | Check related circuit found loose connection so tight it then update software then restore wtg. | Close | 0.26624 | WTG Breakdown Maintenance | G03 | 4436 | 1919.1861 | None
195 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 19:30 | 22:17 | 22:17 | 2.7833 | 0 | 2.7833 | Reset then restore wtg. | Close | 0.071368 | WTG Breakdown Maintenance | G03 | 4436 | 514.4528 | None
196 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G06 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 0:00 | 13:47 | 0 | 13.7833 | 13.7833 | Checked related circuit found SF-6 breaker tripped so we checked T connector found ok then checked power cable then checked transformer then restore wtg. | Close | 0.35342 | WTG Breakdown Maintenance | G03 | 4436 | 2547.6194 | None
197 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G07 | PWEGPL | MSEDCL | 2.564% | 2102 | PLC Module Failure | BD |  | 0:00 | 4:03 | 4:30 | 4.05 | 0.45 | 4.5 | Reboot then restore wtg. | Close | 0.11538 | WTG Breakdown Maintenance | G01 | 5220 | 978.75 | None
198 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G08 | PWEGPL | MSEDCL | 2.564% | 125 | Yaw Motors Over Current Protection | BD |  | 14:40 | 15:47 | 24:00 | 1.1167 | 8.2167 | 9.3333 | Check related circuit found yaw motor failure so replace with new one then restore wtg. | Close | 0.23932 | WTG Breakdown Maintenance | G03 | 4436 | 1725.1111 | None
199 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G11 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD |  | 12:06 | 12:06 | 12:11 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G10 | 5040 | 17.5 | None
200 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G11 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD |  | 12:47 | 12:47 | 12:52 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G10 | 5040 | 17.5 | None
201 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G12 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 13:32 | 13:42 | 13:42 | 0.16667 | 0 | 0.16667 | Reset then restore wtg. | Close | 0.0042735 | WTG Breakdown Maintenance | G09 | 4356 | 30.25 | None
202 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD |  | 0:09 | 0:09 | 0:14 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G12 | 4980 | 17.2917 | None
203 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G14 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 15:42 | 15:42 | 15:56 | 0 | 0.23333 | 0.23333 | Reset then restore wtg. | Close | 0.0059829 | WTG Breakdown Maintenance | G13 | 4190 | 40.7361 | None
204 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G16 | PWEGPL | MSEDCL | 2.564% | 5248 | Active Crowbar IGBT Errors | BD |  | 0:00 | 0:00 | 9:50 | 0 | 9.8333 | 9.8333 | work in progress | Open | 0.25214 | WTG Breakdown Maintenance | G17 | 5176 | 2120.7222 | None
205 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G16 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 9:50 | 9:50 | 14:10 | 0 | 4.3333 | 4.3333 | manual stop for blade bush gap inspection work | Close | 0.11111 | WTG Force Majeaure | G17 | 5176 | 934.5556 | None
206 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G16 | PWEGPL | MSEDCL | 2.564% | 5248 | Active Crowbar IGBT Errors | BD |  | 14:10 | 14:10 | 23:59 | 0 | 9.8167 | 9.8167 | work in progress | Open | 0.25171 | WTG Breakdown Maintenance | G17 | 5176 | 2117.1278 | None
207 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G23 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 0:43 | 0:43 | 1:05 | 0 | 0.36667 | 0.36667 | Reset then restore wtg. | Close | 0.0094017 | WTG Breakdown Maintenance | G05 | 4908 | 74.9833 | None
208 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G25 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 10:03 | 10:03 | 10:50 | 0 | 0.78333 | 0.78333 | Reset then restore wtg. | Close | 0.020085 | WTG Breakdown Maintenance | G27 | 4378 | 142.8931 | None
209 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | G34 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 0:00 | 6:04 | 6:04 | 6.0667 | 0 | 6.0667 | Reset then restore wtg. | Close | 0.15556 | WTG Breakdown Maintenance | G33 | 4113 | 1039.675 | None
210 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 2572 | 2570.2139 | None
211 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 2572 | 2570.2139 | None
212 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 11:22 | 11:22 | 11:38 | 0 | 0.26667 | 0.26667 | Reset then restore wtg. | Close | 0.0068376 | WTG Breakdown Maintenance | G03 | 1912 | 21.2444 | None
213 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 23:53 | 23:53 | 23:57 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0017094 | WTG Breakdown Maintenance | G03 | 1912 | 5.3111 | None
214 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | G11 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD |  | 3:46 | 3:46 | 3:51 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G10 | 1448 | 5.0278 | None
215 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | G11 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD |  | 12:37 | 12:37 | 12:42 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G10 | 1448 | 5.0278 | None
216 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | G13 | PWEGPL | MSEDCL | 2.564% | 550 | Generator Fans Thermal Relay Triggered Too Long | BD |  | 17:47 | 18:11 | 18:16 | 0.4 | 0.083333 | 0.48333 | Reboot then restore wtg. | Close | 0.012393 | WTG Breakdown Maintenance | G14 | 1700 | 34.2361 | None
217 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | G22 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD |  | 16:23 | 16:23 | 16:28 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G21 | 2750 | 9.5486 | None
218 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | G33 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 11:40 | 11:40 | 16:38 | 0 | 4.9667 | 4.9667 | manual stop for blade bush gap inspection work | Close | 0.12735 | WTG Breakdown Maintenance | G34 | 2528 | 523.1556 | None
219 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 2824 | 2822.0389 | None
220 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 2824 | 2822.0389 | None
221 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | G01 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 14:35 | 14:35 | 14:40 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G07 | 3428 | 11.9028 | None
222 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | G15 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 10:45 | 10:45 | 13:44 | 0 | 2.9833 | 2.9833 | Manual stop for blade bush gap inspection work. | Close | 0.076496 | WTG Force Majeaure | G14 | 3212 | 399.2694 | None
223 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | G16 | PWEGPL | MSEDCL | 2.564% | 5248 | Active Crowbar IGBT Errors | BD |  | 0:00 | 0:00 | 23:59 | 0 | 23.9833 | 23.9833 | work in progress | Open | 0.61496 | WTG Breakdown Maintenance | G17 | 3500 | 3497.5694 | None
224 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 7807 | 7801.5785 | None
225 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 7807 | 7801.5785 | None
226 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | G01 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 2:25 | 2:25 | 2:30 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G07 | 4061 | 14.1007 | None
227 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | G01 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD |  | 17:43 | 17:43 | 17:48 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G07 | 4061 | 14.1007 | None
228 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 16:29 | 16:29 | 16:31 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0008547 | WTG Breakdown Maintenance | G03 | 5516 | 7.6611 | None
229 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | G06 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 1:24 | 1:29 | 2:35 | 0.083333 | 1.1 | 1.1833 | check and found SF-6 breaker tripped so charge it then checked all motors then restore wtg. | Close | 0.030342 | WTG Breakdown Maintenance | G03 | 5516 | 271.9694 | None
230 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | G07 | PWEGPL | MSEDCL | 2.564% | 227 | Hydraulic HUB Filter Dirty Too Long | BD |  | 4:37 | 7:27 | 7:27 | 2.8333 | 0 | 2.8333 | Reset then restore wtg. | Close | 0.07265 | WTG Breakdown Maintenance | G01 | 5128 | 605.3889 | None
231 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | G16 | PWEGPL | MSEDCL | 2.564% | 5248 | Active Crowbar IGBT Errors | BD |  | 0:00 | 0:00 | 23:59 | 0 | 23.9833 | 23.9833 | work in progress | Close | 0.61496 | WTG Breakdown Maintenance | G17 | 5120 | 5116.4444 | None
232 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | G28 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | BD |  | 14:18 | 14:18 | 14:23 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G30 | 7195 | 24.9826 | None
233 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | G28 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | BD |  | 16:06 | 16:06 | 16:17 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0047009 | WTG Breakdown Maintenance | G30 | 7195 | 54.9618 | None
234 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | G28 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | BD |  | 16:38 | 16:38 | 16:48 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0042735 | WTG Breakdown Maintenance | G30 | 7195 | 49.9653 | None
235 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | G28 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | BD |  | 19:44 | 19:44 | 19:49 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G30 | 7195 | 24.9826 | None
236 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | G28 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | BD |  | 20:07 | 20:07 | 20:12 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G30 | 7195 | 24.9826 | None
237 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | G33 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | BD |  | 12:10 | 12:10 | 17:16 | 0 | 5.1 | 5.1 | Manual stop for Blade A pitch seal replacement work | Close | 0.13077 | WTG Unscheduled Maintenance | G34 | 6153 | 1307.5125 | None
238 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | G38 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 14:24 | 14:24 | 14:29 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G40 | 6822 | 23.6875 | None
239 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 3910 | 3907.2847 | None
240 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 3910 | 3907.2847 | None
241 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G01 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 12:59 | 12:59 | 13:04 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G07 | 4140 | 14.375 | None
242 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G03 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD |  | 4:33 | 4:33 | 4:38 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G04 | 2420 | 8.4028 | None
243 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 13:42 | 13:42 | 13:47 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G03 | 3986 | 13.8403 | None
244 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G04 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | BD |  | 13:59 | 13:59 | 14:04 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G03 | 3986 | 13.8403 | None
245 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 22:49 | 23:59 | 23:59 | 1.1667 | 0 | 1.1667 | work in progress | Open | 0.029915 | WTG Breakdown Maintenance | G03 | 3986 | 193.7639 | None
246 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G09 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 19:19 | 23:09 | 23:59 | 3.8333 | 0.83333 | 4.6667 | work in progress | Open | 0.11966 | WTG Breakdown Maintenance | G12 | 4310 | 838.0556 | None
247 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G10 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD |  | 23:45 | 23:45 | 23:50 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G11 | 4460 | 15.4861 | None
248 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G11 | PWEGPL | MSEDCL | 2.564% | 577 | Slipping Rings Fan Or Heating Resistor Failure | BD |  | 9:14 | 11:24 | 13:26 | 2.1667 | 2.0333 | 4.2 | Checked related circuit found relay failure so replaced reley then restore wtg. | Close | 0.10769 | WTG Breakdown Maintenance | G10 | 4112 | 719.6 | None
249 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD |  | 23:53 | 23:53 | 23:58 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G12 | 4310 | 14.9653 | None
250 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G14 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 13:08 | 13:08 | 13:19 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0047009 | WTG Breakdown Maintenance | G15 | 1155 | 8.8229 | None
251 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G16 | PWEGPL | MSEDCL | 2.564% | 5248 | Active Crowbar IGBT Errors | BD |  | 0:00 | 0:00 | 23:59 | 0 | 23.9833 | 23.9833 | work in progress | Open | 0.61496 | WTG Breakdown Maintenance | G15 | 1155 | 1154.1979 | None
252 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G23 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD |  | 4:19 | 4:19 | 4:24 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G05 | 4046 | 14.0486 | None
253 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G23 | PWEGPL | MSEDCL | 2.564% | 501 | Generator DE Bearing High Temperature Alarm | BD |  | 4:30 | 4:30 | 4:35 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G05 | 4046 | 14.0486 | None
254 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G23 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD |  | 6:14 | 6:14 | 6:34 | 0 | 0.33333 | 0.33333 | Auto reset | Close | 0.008547 | WTG Breakdown Maintenance | G05 | 4046 | 56.1944 | None
255 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G23 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD |  | 9:10 | 9:10 | 9:18 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0034188 | WTG Breakdown Maintenance | G05 | 4046 | 22.4778 | None
256 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G26 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD |  | 23:57 | 23:57 | 23:59 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0008547 | WTG Breakdown Maintenance | G32 | 3788 | 5.2611 | None
257 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G28 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | Manual stop |  | 11:18 | 11:18 | 12:26 | 0 | 1.1333 | 1.1333 | Coolant cooling rediator clean then restore wtg. | Close | 0.02906 | WTG Unscheduled Maintenance | G30 | 5106 | 241.1167 | None
258 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G30 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD |  | 8:07 | 8:07 | 8:12 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G28 | 3910 | 13.5764 | None
259 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G30 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD |  | 9:02 | 9:02 | 9:07 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G28 | 3910 | 13.5764 | None
260 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G30 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD |  | 9:24 | 9:24 | 9:29 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G28 | 3910 | 13.5764 | None
261 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G33 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 15:34 | 15:34 | 16:49 | 0 | 1.25 | 1.25 | Gear box oil leakage arrest then top-up 15 liter gear oil then start wtg. | Close | 0.032051 | WTG Unscheduled Maintenance | G34 | 3696 | 192.5 | None
262 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | G37 | PWEGPL | MSEDCL | 2.564% | 402 | Gearbox Oil Level Low | BD |  | 5:40 | 5:40 | 9:20 | 0 | 3.6667 | 3.6667 | Reset then restore wtg. | Close | 0.094017 | WTG Breakdown Maintenance | G36 | 5094 | 778.25 | None
263 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8908 | 8901.8139 | None
264 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8908 | 8901.8139 | None
265 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G01 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 10:25 | 10:25 | 10:30 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G07 | 9460 | 32.8472 | None
266 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 0:00 | 0:00 | 0:42 | 0 | 0.7 | 0.7 | Reset then restore wtg. | Close | 0.017949 | WTG Breakdown Maintenance | G03 | 9628 | 280.8167 | None
267 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G04 | PWEGPL | MSEDCL | 2.564% | 208 | HU Pump Drive Failure | BD |  | 7:40 | 11:19 | 11:35 | 3.65 | 0.26667 | 3.9167 | Checked related circuit found contactor straked so replaced with new one then restore wtg. | Close | 0.10043 | WTG Breakdown Maintenance | G03 | 9628 | 1571.2361 | None
268 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G09 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 0:00 | 0:00 | 2:14 | 0 | 2.2333 | 2.2333 | Checked related circuit found ccU coolant cooling motor & MPCB failure so replaced with new one then restore wtg. then start wtg. | Close | 0.057265 | WTG Breakdown Maintenance | G12 | 9350 | 870.0694 | None
269 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G10 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD |  | 0:38 | 0:38 | 0:43 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G11 | 12444 | 43.2083 | None
270 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G10 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 7:40 | 11:19 | 11:22 | 3.65 | 0.05 | 3.7 | Reset then restore wtg. | Close | 0.094872 | WTG Breakdown Maintenance | G11 | 12444 | 1918.45 | None
271 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 13:53 | 13:53 | 14:03 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0042735 | WTG Breakdown Maintenance | G13 | 8102 | 56.2639 | None
272 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G15 | PWEGPL | MSEDCL | 2.564% | 502 | Generator NDE Bearing High Temperature Alarm | BD |  | 5:02 | 5:02 | 5:07 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G14 | 10392 | 36.0833 | None
273 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G16 | PWEGPL | MSEDCL | 2.564% | 5248 | Active Crowbar IGBT Errors | BD |  | 0:00 | 0:00 | 18:54 | 0 | 18.9 | 18.9 | Replaced Carbon brush and holder then restore wtg and power set to 500 kw | Close | 0.48462 | WTG Breakdown Maintenance | G17 | 12986 | 10226.475 | Due to material shortage power set on 500 kw
274 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G18 | PWEGPL | MSEDCL | 2.564% | 502 | Generator NDE Bearing High Temperature Alarm | BD |  | 1:40 | 1:40 | 1:45 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G19 | 11728 | 40.7222 | None
275 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G18 | PWEGPL | MSEDCL | 2.564% | 502 | Generator NDE Bearing High Temperature Alarm | BD |  | 5:20 | 5:20 | 5:25 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G19 | 11728 | 40.7222 | None
276 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G19 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 9:31 | 13:52 | 13:52 | 4.35 | 0 | 4.35 | Reset then restore wtg. | Close | 0.11154 | WTG Breakdown Maintenance | G20 | 12297 | 2228.8312 | None
277 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G22 | PWEGPL | MSEDCL | 2.564% | 402 | Gearbox Oil Level Low | BD |  | 5:40 | 5:40 | 8:30 | 0 | 2.8333 | 2.8333 | Reset then restore wtg. | Close | 0.07265 | WTG Breakdown Maintenance | G21 | 8994 | 1061.7917 | None
278 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G26 | PWEGPL | MSEDCL | 2.564% | 527 | High Temperature Of Upper Radiator | BD |  | 3:02 | 3:02 | 3:07 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G32 | 7086 | 24.6042 | None
279 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G26 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 13:17 | 13:17 | 13:22 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G32 | 7086 | 24.6042 | None
280 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | G37 | PWEGPL | MSEDCL | 2.564% | 5219 | Coolant Of The Coolant Circuit Failure | BD |  | 14:24 | 14:52 | 14:54 | 0.46667 | 0.033333 | 0.5 | Reset then restore wtg. | Close | 0.012821 | WTG Breakdown Maintenance | G36 | 9864 | 205.5 | None
281 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 12542 | 12533.2903 | None
282 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 12542 | 12533.2903 | None
283 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | G04 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 14:35 | 15:32 | 15:36 | 0.95 | 0.066667 | 1.0167 | Reboot then restore wtg. | Close | 0.026068 | WTG Breakdown Maintenance | G03 | 13120 | 555.7778 | None
284 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | G07 | PWEGPL | MSEDCL | 2.564% | 211 | Hydraulic HUB Filter Dirty | BD |  | 14:45 | 16:03 | 16:05 | 1.3 | 0.033333 | 1.3333 | Reset then restore wtg. | Close | 0.034188 | WTG Breakdown Maintenance | G01 | 14750 | 819.4444 | None
285 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 14:02 | 14:35 | 14:45 | 0.55 | 0.16667 | 0.71667 | Reboot then restore wtg. | Close | 0.018376 | WTG Breakdown Maintenance | G13 | 11088 | 331.1 | None
286 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | G14 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 12:22 | 12:22 | 17:05 | 0 | 4.7167 | 4.7167 | Manual stop for Blade A pitch seal replacement work | Close | 0.12094 | WTG Unscheduled Maintenance | G15 | 14296 | 2809.5611 | None
287 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 14802 | 14791.7208 | None
288 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 14802 | 14791.7208 | None
289 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | G03 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 11:50 | 11:50 | 13:15 | 0 | 1.4167 | 1.4167 | Manual stop for gear box hose replacement work | Close | 0.036325 | WTG Unscheduled Maintenance | G04 | 14379 | 848.7604 | None
290 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | G04 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 13:30 | 13:30 | 14:15 | 0 | 0.75 | 0.75 | Manual stop for CCU raditor cleaning work | Close | 0.019231 | WTG Unscheduled Maintenance | G03 | 14285 | 446.4062 | None
291 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | G07 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 15:18 | 15:18 | 16:02 | 0 | 0.73333 | 0.73333 | Manual stop for CCU raditor cleaning work | Close | 0.018803 | WTG Unscheduled Maintenance | G01 | 14293 | 436.7306 | None
292 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 12852 | 12843.075 | None
293 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 12852 | 12843.075 | None
294 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | G01 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 11:11 | 12:19 | 12:20 | 1.1333 | 0.016667 | 1.15 | Reset then restore wtg. | Close | 0.029487 | WTG Breakdown Maintenance | G07 | 15693 | 751.9562 | None
295 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | G18 | PWEGPL | MSEDCL | 2.564% | 5205 | Magnetothermic Of The Stator Protection Failure Or Door Open | BD |  | 10:10 | 10:35 | 12:26 | 0.41667 | 1.85 | 2.2667 | check related circuit found ACB relay malfuction so replace with new one then restore wtg. | Close | 0.05812 | WTG Breakdown Maintenance | G19 | 12949 | 1222.9611 | None
296 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | G23 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 9:20 | 10:02 | 11:15 | 0.7 | 1.2167 | 1.9167 | Check related circuit found no leakage then restore wtg. | Close | 0.049145 | WTG Breakdown Maintenance | G22 | 12639 | 1009.3646 | None
297 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | G33 | PWEGPL | MSEDCL | 2.564% | 907 | Emergency Series HUB Trigger | BD |  | 14:10 | 15:02 | 15:05 | 0.86667 | 0.05 | 0.91667 | Reset then restore wtg. | Close | 0.023504 | WTG Breakdown Maintenance | G34 | 10962 | 418.6875 | None
298 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 14:45 | 15:38 | 15:40 | 0.88333 | 0.033333 | 0.91667 | Reboot then restore wtg. | Close | 0.023504 | WTG Breakdown Maintenance | G40 | 10928 | 417.3889 | None
299 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8264 | 8258.2611 | None
300 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8264 | 8258.2611 | None
301 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | G01 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 13:01 | 14:05 | 14:07 | 1.0667 | 0.033333 | 1.1 | Reboot then restore wtg. | Close | 0.028205 | WTG Breakdown Maintenance | G07 | 9768 | 447.7 | None
302 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | G05 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 15:05 | 15:30 | 15:32 | 0.41667 | 0.033333 | 0.45 | Reboot then restore wtg. | Close | 0.011538 | WTG Breakdown Maintenance | G22 | 8268 | 155.025 | None
303 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | G21 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 15:05 | 15:45 | 15:47 | 0.66667 | 0.033333 | 0.7 | Reboot then restore wtg. | Close | 0.017949 | WTG Breakdown Maintenance | G22 | 8268 | 241.15 | None
304 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | G26 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 11:56 | 11:56 | 13:37 | 0 | 1.6833 | 1.6833 | Manual stop for gear box hose replacement work | Close | 0.043162 | WTG Unscheduled Maintenance | G32 | 9627 | 675.2271 | None
305 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-13 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 10:42 | 11:30 | 11:32 | 0.8 | 0.033333 | 0.83333 | Reboot then restore wtg. | Close | 0.021368 | WTG Breakdown Maintenance | G40 | 9687 | 336.3542 | None
306 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 14824 | 14813.7056 | None
307 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 14824 | 14813.7056 | None
308 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | G10 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 12:10 | 12:10 | 15:30 | 0 | 3.3333 | 3.3333 | Manual stop for Lift supporting & plateform guide clamp replaced then clean CCU radiator then restore wyg. | Close | 0.08547 | WTG Breakdown Maintenance | G11 | 16100 | 2236.1111 | None
309 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | G11 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 16:15 | 16:15 | 17:20 | 0 | 1.0833 | 1.0833 | Manual stop for CCU raditor cleaning work | Close | 0.027778 | WTG Breakdown Maintenance | G10 | 16001 | 722.2674 | None
310 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | G01 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 14:09 | 14:39 | 15:30 | 0.5 | 0.85 | 1.35 | Checked related circuit found ok then interchange addon then restore wtg. | Close | 0.034615 | WTG Breakdown Maintenance | G07 | 18132 | 1019.925 | None
311 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 15896 | 15884.9611 | None
312 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 15896 | 15884.9611 | None
313 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | G01 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 10:47 | 11:32 | 11:34 | 0.75 | 0.033333 | 0.78333 | Reset then restore wtg. | Close | 0.020085 | WTG Breakdown Maintenance | G07 | 14853 | 484.7854 | None
314 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | G04 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 15:35 | 16:10 | 16:12 | 0.58333 | 0.033333 | 0.61667 | Reboot then restore wtg. | Close | 0.015812 | WTG Breakdown Maintenance | G03 | 14963 | 384.466 | None
315 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | G39 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:30 | 11:30 | 15:45 | 0 | 4.25 | 4.25 | Blade C Pitch seal replaced then start wtg. | Close | 0.10897 | WTG Unscheduled Maintenance | G40 | 12705 | 2249.8438 | None
316 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 15884.9611 | 15873.9299 | None
317 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 15884.9611 | 15873.9299 | None
318 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | G21 | PWEGPL | MSEDCL | 2.564% | 5228 | Preload Failure | BD |  | 15:12 | 15:41 | 15:58 | 0.48333 | 0.28333 | 0.76667 | Checked related circuit found addon loose so tight it then restore wtg. | Close | 0.019658 | WTG Breakdown Maintenance | G22 | 12169 | 388.7319 | None
319 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | G25 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 15:12 | 16:05 | 16:07 | 0.88333 | 0.033333 | 0.91667 | Reset then restore wtg. | Close | 0.023504 | WTG Breakdown Maintenance | G27 | 12185 | 465.3993 | None
320 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | G38 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 15:12 | 16:15 | 16:18 | 1.05 | 0.05 | 1.1 | Reset then restore wtg. | Close | 0.028205 | WTG Breakdown Maintenance | G40 | 14952 | 685.3 | None
321 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 12176.5382 | 12168.0823 | None
322 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 12176.5382 | 12168.0823 | None
323 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | G01 | PWEGPL | MSEDCL | 2.564% | 207 | Hydraulic Oil High Temperature | BD |  | 4:02 | 4:50 | 4:52 | 0.8 | 0.033333 | 0.83333 | Reboot then restore wtg. | Close | 0.021368 | WTG Breakdown Maintenance | G07 | 15190 | 527.4306 | None
324 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | G01 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:20 | 11:20 | 13:10 | 0 | 1.8333 | 1.8333 | Check related circuit found internal leakage from proportional valve so replaced with new one then restore wtg. | Close | 0.047009 | WTG Unscheduled Maintenance | G07 | 15190 | 1160.3472 | None
325 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | G02 | PWEGPL | MSEDCL | 2.564% | 502 | Generator NDE Bearing High Temperature Alarm | BD |  | 4:16 | 5:10 | 5:12 | 0.9 | 0.033333 | 0.93333 | Reboot then restore wtg. | Close | 0.023932 | WTG Breakdown Maintenance | G04 | 16584 | 644.9333 | None
326 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | G02 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 13:22 | 13:22 | 14:35 | 0 | 1.2167 | 1.2167 | check related circuit found generator earthing brush wear out then replace it then restore wtg. | Close | 0.031197 | WTG Unscheduled Maintenance | G04 | 16584 | 840.7167 | None
327 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | G07 | PWEGPL | MSEDCL | 2.564% | 403 | High Gearbox Oil Temperature | BD |  | 3:25 | 4:02 | 4:05 | 0.61667 | 0.05 | 0.66667 | Reboot then restore wtg. | Close | 0.017094 | WTG Breakdown Maintenance | G01 | 15153 | 420.9167 | None
328 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | G07 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:19 | 11:19 | 13:06 | 0 | 1.7833 | 1.7833 | Check related circuit found MPCB tripped so correct it then check motor found ok then check connection then restore wtg. | Close | 0.045726 | WTG Unscheduled Maintenance | G01 | 15153 | 1125.9521 | None
329 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | G09 | PWEGPL | MSEDCL | 2.564% | 416 | Vibration Sensor | BD |  | 7:45 | 9:25 | 9:26 | 1.6667 | 0.016667 | 1.6833 | Reset then restore wtg. | Close | 0.043162 | WTG Breakdown Maintenance | G12 | 14923 | 1046.6826 | None
330 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | G39 | PWEGPL | MSEDCL | 2.564% | 5200 | Magnetothermic Trigger Of The Line Protection | BD |  | 8:45 | 9:48 | 9:50 | 1.05 | 0.033333 | 1.0833 | Reboot then restore wtg. | Close | 0.027778 | WTG Breakdown Maintenance | G40 | 12574 | 567.5764 | None
331 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8824 | 8817.8722 | None
332 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8824 | 8817.8722 | None
333 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | G23 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD |  | 9:35 | 9:35 | 9:40 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G22 | 8858 | 30.7569 | None
334 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | G23 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD |  | 10:12 | 10:12 | 10:17 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G22 | 8858 | 30.7569 | None
335 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | G23 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD |  | 12:15 | 12:32 | 12:35 | 0.28333 | 0.05 | 0.33333 | Reboot then restore wtg. | Close | 0.008547 | WTG Breakdown Maintenance | G22 | 8858 | 123.0278 | None
336 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | G30 | PWEGPL | MSEDCL | 2.564% | 426 | Rotor Speed Reading Failure | BD |  | 11:05 | 11:05 | 11:54 | 0 | 0.81667 | 0.81667 | check related circuit found rotor sensor connection loose so tight it | Close | 0.02094 | WTG Breakdown Maintenance | G28 | 8824 | 300.2611 | None
337 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | G36 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD |  | 9:45 | 11:55 | 15:05 | 2.1667 | 3.1667 | 5.3333 | Check related circuit found proportion valve cable connector loose so tight it then restore wtg. | Close | 0.13675 | WTG Breakdown Maintenance | G35 | 7963 | 1769.5556 | None
338 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | G35 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 16:48 | 17:35 | 17:38 | 0.78333 | 0.05 | 0.83333 | Reset then restore wtg. | Close | 0.021368 | WTG Breakdown Maintenance | G33 | 8169 | 283.6458 | None
339 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | G23 | PWEGPL | MSEDCL | 2.564% | 2106 | Temp. Measurement Module Failure | BD |  | 16:20 | 16:45 | 17:47 | 0.41667 | 1.0333 | 1.45 | Checked related circuit found Sensor ok then replaced module | Close | 0.037179 | WTG Breakdown Maintenance | G22 | 8824 | 533.1167 | None
340 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-19 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 10567 | 10559.6618 | None
341 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-19 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 10567 | 10559.6618 | None
342 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-19 | G13 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 14:58 | 15:15 | 15:18 | 0.28333 | 0.05 | 0.33333 | Reboot then restore wtg. | Close | 0.008547 | WTG Breakdown Maintenance | G14 | 11378 | 158.0278 | None
343 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-19 | G23 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 11:15 | 11:15 | 18:03 | 0 | 6.8 | 6.8 | Manual stop for Blade A pitch seal replacement work | Close | 0.17436 | WTG Unscheduled Maintenance | G05 | 10590 | 3000.5 | None
344 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-19 | G33 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 14:37 | 15:13 | 16:10 | 0.6 | 0.95 | 1.55 | Check related circuit found loose connection so tight it then restore wtg. | Close | 0.039744 | WTG Breakdown Maintenance | G34 | 10290 | 664.5625 | None
345 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 20863 | 20848.5118 | None
346 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 20863 | 20848.5118 | None
347 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | G04 | PWEGPL | MSEDCL | 2.564% | 719 | Cup Anemometer Failure Warning | BD |  | 11:30 | 12:12 | 12:13 | 0.7 | 0.016667 | 0.71667 | Reset then restore wtg. | Close | 0.018376 | WTG Breakdown Maintenance | G03 | 20321 | 606.8076 | None
348 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD |  | 4:05 | 4:05 | 4:10 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G14 | 21178 | 73.5347 | None
349 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD |  | 5:34 | 5:34 | 5:39 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G14 | 21178 | 73.5347 | None
350 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | G13 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD |  | 6:45 | 6:45 | 6:50 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G14 | 21178 | 73.5347 | None
351 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | G13 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:25 | 11:25 | 15:23 | 0 | 3.9667 | 3.9667 | Manual stop for generator cooling motor inspection and rectification work | Close | 0.10171 | WTG Unscheduled Maintenance | G14 | 21178 | 3500.2528 | None
352 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | G22 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 16:24 | 16:52 | 16:54 | 0.46667 | 0.033333 | 0.5 | Reset then restore wtg. | Close | 0.012821 | WTG Breakdown Maintenance | G05 | 20876 | 434.9167 | None
353 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8034 | 8028.4208 | None
354 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8034 | 8028.4208 | None
355 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | G16 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 15:52 | 15:52 | 17:30 | 0 | 1.6333 | 1.6333 | Manual stop for Slipring carbon brush & spring replacement and power set to 2000kw max. | Close | 0.04188 | WTG Unscheduled Maintenance | G17 | 7749 | 527.3625 | None
356 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | G32 | PWEGPL | MSEDCL | 2.564% | 1824 | Trafo Fan Thermal Relay | BD |  | 13:53 | 14:35 | 14:36 | 0.7 | 0.016667 | 0.71667 | Reset then restore wtg. | Close | 0.018376 | WTG Breakdown Maintenance | G26 | 8284 | 247.3694 | None
357 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | G26 | PWEGPL | MSEDCL | 2.564% | 1824 | Trafo Fan Thermal Relay | BD |  | 13:32 | 14:42 | 14:43 | 1.1667 | 0.016667 | 1.1833 | Reset then restore wtg. | Close | 0.030342 | WTG Breakdown Maintenance | G40 | 8257 | 407.116 | None
358 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | G40 | PWEGPL | MSEDCL | 2.564% | 1824 | Trafo Fan Thermal Relay | BD |  | 14:05 | 14:51 | 14:52 | 0.76667 | 0.016667 | 0.78333 | Reset then restore wtg. | Close | 0.020085 | WTG Breakdown Maintenance | G39 | 8463 | 276.2229 | None
359 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 6332 | 6327.6028 | None
360 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 6332 | 6327.6028 | None
361 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | G06 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 7:14 | 8:01 | 8:03 | 0.78333 | 0.033333 | 0.81667 | Reboot then restore wtg. | Close | 0.02094 | WTG Breakdown Maintenance | G03 | 4367 | 148.5993 | None
362 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | G06 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 14:10 | 14:43 | 14:45 | 0.55 | 0.033333 | 0.58333 | Reboot then restore wtg. | Close | 0.014957 | WTG Breakdown Maintenance | G03 | 4367 | 106.1424 | None
363 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | G13 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 10:38 | 10:38 | 12:22 | 0 | 1.7333 | 1.7333 | Manual stop for CCU motor replaced then restore wtg. | Close | 0.044444 | WTG Unscheduled Maintenance | G14 | 6342 | 458.0333 | None
364 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | G32 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:06 | 11:06 | 16:14 | 0 | 5.1333 | 5.1333 | Manual stop for transformer fan replacement work | Close | 0.13162 | WTG Unscheduled Maintenance | G26 | 6450 | 1379.5833 | None
365 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | G33 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 17:10 | 17:45 | 17:50 | 0.58333 | 0.083333 | 0.66667 | Reboot then restore wtg. | Close | 0.017094 | WTG Breakdown Maintenance | G34 | 6487 | 180.1944 | None
366 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 3178 | 3175.7931 | None
367 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 3178 | 3175.7931 | None
368 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | G19 | PWEGPL | MSEDCL | 2.564% | 118 | Yaw Motors Error | BD |  | 18:15 | 18:49 | 18:50 | 0.56667 | 0.016667 | 0.58333 | Reset then restore wtg. | Close | 0.014957 | WTG Breakdown Maintenance | G18 | 3957 | 96.1771 | None
369 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | G22 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 18:02 | 18:55 | 18:56 | 0.88333 | 0.016667 | 0.9 | Reset then restore wtg. | Close | 0.023077 | WTG Breakdown Maintenance | G05 | 3153 | 118.2375 | None
370 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | G25 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 10:55 | 10:55 | 16:30 | 0 | 5.5833 | 5.5833 | Manual stop for transformer fan replacement work | Close | 0.14316 | WTG Unscheduled Maintenance | G27 | 3157 | 734.441 | None
371 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | G32 | PWEGPL | MSEDCL | 2.564% | 525 | High Ambient Temperature In The Converter | BD |  | 16:18 | 17:01 | 17:03 | 0.71667 | 0.033333 | 0.75 | Reboot then restore wtg. | Close | 0.019231 | WTG Breakdown Maintenance | G26 | 3102 | 96.9375 | None
372 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 5484 | 5480.1917 | None
373 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 5484 | 5480.1917 | None
374 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | G01 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 17:23 | 18:25 | 18:27 | 1.0333 | 0.033333 | 1.0667 | Reboot then restore wtg. | Close | 0.02735 | WTG Breakdown Maintenance | G07 | 5267 | 234.0889 | None
375 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | G22 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 17:48 | 18:23 | 18:25 | 0.58333 | 0.033333 | 0.61667 | Reset then restore wtg. | Close | 0.015812 | WTG Breakdown Maintenance | G05 | 5423 | 139.341 | None
376 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | G26 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:50 | 11:50 | 16:18 | 0 | 4.4667 | 4.4667 | Manual stop for transformer fan replacement work | Close | 0.11453 | WTG Unscheduled Maintenance | G32 | 7158 | 1332.1833 | None
377 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | G39 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 15:00 | 15:00 | 17:07 | 0 | 2.1167 | 2.1167 | Manual stop for Blade bush gap inspection work | Close | 0.054274 | IG Force Majeaure | G38 | 7156 | 631.1194 | None
378 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | G40 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:40 | 11:40 | 16:20 | 0 | 4.6667 | 4.6667 | Manual stop for transformer fan replacement work | Close | 0.11966 | WTG Unscheduled Maintenance | G38 | 7156 | 1391.4444 | None
379 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 6544 | 6539.4556 | None
380 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 6544 | 6539.4556 | None
381 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | G04 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 14:28 | 15:10 | 15:12 | 0.7 | 0.033333 | 0.73333 | Reset then restore wtg. | Close | 0.018803 | WTG Breakdown Maintenance | G03 | 7041 | 215.1417 | None
382 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | G08 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 18:40 | 18:40 | 19:30 | 0 | 0.83333 | 0.83333 | Manual stop for generator temp. Apply grease and connections checking | Close | 0.021368 | WTG Unscheduled Maintenance | G03 | 7041 | 244.4792 | None
383 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | G09 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 9:40 | 10:32 | 10:33 | 0.86667 | 0.016667 | 0.88333 | Reset then restore wtg. | Close | 0.02265 | WTG Breakdown Maintenance | G12 | 6063 | 223.1521 | None
384 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | G12 | PWEGPL | MSEDCL | 2.564% | 2119 | CTRL Error - Processor Stopped | BD |  | 9:25 | 10:32 | 11:45 | 1.1167 | 1.2167 | 2.3333 | Check and found PLC card failure so replaced card then update softwear then restore wtg. | Close | 0.059829 | WTG Breakdown Maintenance | G09 | 6032 | 586.4444 | None
385 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | G22 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 13:38 | 13:38 | 15:02 | 0 | 1.4 | 1.4 | Manual stop for repeted error found pressure switch loose connection so tight it then restore wtg. | Close | 0.035897 | WTG Unscheduled Maintenance | G05 | 6587 | 384.2417 | None
386 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | G34 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 14:50 | 14:50 | 16:45 | 0 | 1.9167 | 1.9167 | Manual stop for Blade bush gap inspection work | Close | 0.049145 | IG Force Majeaure | G33 | 6842 | 546.4097 | None
387 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | G39 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:33 | 11:33 | 18:35 | 0 | 7.0333 | 7.0333 | Manual stop for Blade B pitch seal replacement work | Close | 0.18034 | WTG Unscheduled Maintenance | G40 | 6849 | 2007.1375 | None
388 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | G19 | PWEGPL | MSEDCL | 2.564% | 110 | Yaw Sensor Wiring Error | BD |  | 6:20 | 6:54 | 7:35 | 0.56667 | 0.68333 | 1.25 | Check and found yaw encoder failure so replaced with new one then restore wtg. | Close | 0.032051 | WTG Breakdown Maintenance | G18 | 6345 | 330.4687 | None
389 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8839 | 8832.8618 | None
390 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8839 | 8832.8618 | None
391 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | G06 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:05 | 11:05 | 14:25 | 0 | 3.3333 | 3.3333 | Manual stop for transformer fan replacement work | Close | 0.08547 | WTG Unscheduled Maintenance | G03 | 10932 | 1518.3333 | None
392 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | G21 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 11:15 | 11:15 | 14:10 | 0 | 2.9167 | 2.9167 | Manual stop for Blade bush gap inspection work | Close | 0.074786 | WTG Force Majeaure | G22 | 8563 | 1040.6424 | None
393 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | G22 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD |  | 13:05 | 13:05 | 13:10 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G21 | 8363 | 29.0382 | None
394 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | G22 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD |  | 16:10 | 16:10 | 16:15 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G21 | 8363 | 29.0382 | None
395 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | G25 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:55 | 11:55 | 19:20 | 0 | 7.4167 | 7.4167 | Manual stop for HYPM work | Close | 0.19017 | WTG Scheduled Maintenance | G27 | 8858 | 2737.3681 | None
396 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | G36 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 16:10 | 16:47 | 16:49 | 0.61667 | 0.033333 | 0.65 | Reboot then restore wtg. | Close | 0.016667 | WTG Breakdown Maintenance | G35 | 9344 | 253.0667 | None
397 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 4867 | 4863.6201 | None
398 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 4867 | 4863.6201 | None
399 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | G04 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 12:58 | 13:30 | 13:32 | 0.53333 | 0.033333 | 0.56667 | Reset then restore wtg. | Close | 0.01453 | WTG Breakdown Maintenance | G03 | 5812 | 137.2278 | None
400 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | G07 | PWEGPL | MSEDCL | 2.564% | 410 | OGS | BD |  | 16:50 | 17:36 | 17:38 | 0.76667 | 0.033333 | 0.8 | OGS reset then restore wg. | Close | 0.020513 | WTG Breakdown Maintenance | G01 | 5801 | 193.3667 | None
401 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | G14 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 15:32 | 16:10 | 17:02 | 0.63333 | 0.86667 | 1.5 | Slip ring clean then restore wtg. | Close | 0.038462 | WTG Breakdown Maintenance | G15 | 5642 | 352.625 | None
402 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | G27 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:16 | 11:16 | 17:50 | 0 | 6.5667 | 6.5667 | HYPM done then restore wtg. | Close | 0.16838 | WTG Scheduled Maintenance | G25 | 4854 | 1328.1083 | None
403 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | G36 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 7:10 | 8:06 | 8:08 | 0.93333 | 0.033333 | 0.96667 | Reset then restore wtg. | Close | 0.024786 | WTG Breakdown Maintenance | G35 | 4556 | 183.5056 | None
404 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | G40 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 11:02 | 11:02 | 14:20 | 0 | 3.3 | 3.3 | Manual stop for Blade bush gap inspection work | Close | 0.084615 | WTG Force Majeaure | G39 | 4567 | 627.9625 | None
405 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | G22 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD |  | 17:05 | 18:45 | 18:48 | 1.6667 | 0.05 | 1.7167 | Reboot then restore wtg. | Close | 0.044017 | WTG Breakdown Maintenance | G21 | 4845 | 346.5521 | None
406 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 6654 | 6649.3792 | None
407 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 6654 | 6649.3792 | None
408 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | G04 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 11:02 | 11:02 | 14:25 | 0 | 3.3833 | 3.3833 | Manual stop for Blade bush gap inspection work | Close | 0.086752 | WTG Force Majeaure | G03 | 8051 | 1134.9674 | None
409 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | G20 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 12:04 | 12:38 | 15:39 | 0.56667 | 3.0167 | 3.5833 | Check related circuit found Hub main accumulator failure so replaced with new one then restore wtg. | Close | 0.09188 | WTG Breakdown Maintenance | G19 | 7853 | 1172.4965 | None
410 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | G30 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:15 | 11:15 | 17:05 | 0 | 5.8333 | 5.8333 | HYPM done then restore wtg. | Close | 0.14957 | WTG Scheduled Maintenance | G28 | 6654 | 1617.2917 | None
411 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | G36 | PWEGPL | MSEDCL | 2.564% | 110 | Yaw Sensor Wiring Error | BD |  | 15:05 | 15:42 | 15:43 | 0.61667 | 0.016667 | 0.63333 | Reset then restore wtg. | Close | 0.016239 | WTG Breakdown Maintenance | G35 | 7062 | 186.3583 | None
412 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 5567 | 5563.134 | None
413 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 5567 | 5563.134 | None
414 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | G07 | PWEGPL | MSEDCL | 2.564% | 410 | OGS | BD |  | 15:20 | 16:07 | 16:30 | 0.78333 | 0.38333 | 1.1667 | Check OGS sensor Replaced OGS guard then restore wtg. | Close | 0.029915 | WTG Breakdown Maintenance | G01 | 6459 | 313.9792 | None
415 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | G22 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 9:10 | 10:12 | 17:09 | 1.0333 | 6.95 | 7.9833 | Check related circuit found hub main accumulator failure so replaced accumulator then found gear box oil leakage from hose so replaced GB hose then restore wtg. | Close | 0.2047 | WTG Breakdown Maintenance | G05 | 6742 | 2242.6514 | None
416 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | G28 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 8:12 | 8:12 | 14:45 | 0 | 6.55 | 6.55 | HYPM done then restore wtg. | Close | 0.16795 | WTG Scheduled Maintenance | G30 | 6792 | 1853.65 | None
417 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 12782 | 12773.1236 | None
418 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 12782 | 12773.1236 | None
419 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | G04 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 6:21 | 8:01 | 15:32 | 1.6667 | 7.5167 | 9.1833 | Check related circuit found HU pressure drop continuous so check HU pump then check NRV valve then replaced RV 8-10 & Break Valve restore wtg. | Close | 0.23547 | WTG Breakdown Maintenance | G03 | 16042 | 6138.2931 | None
420 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | G11 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 7:09 | 8:10 | 8:12 | 1.0167 | 0.033333 | 1.05 | Reboot then restore wtg. | Close | 0.026923 | WTG Breakdown Maintenance | G10 | 16079 | 703.4563 | None
421 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | G22 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 8:20 | 12:07 | 12:10 | 3.7833 | 0.05 | 3.8333 | Reboot then restore wtg. | Close | 0.098291 | WTG Breakdown Maintenance | G05 | 15425 | 2463.7153 | None
422 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | G22 | PWEGPL | MSEDCL | 2.564% | 500 | High Generator Winding Temperature | BD |  | 14:10 | 14:35 | 15:21 | 0.41667 | 0.76667 | 1.1833 | Check related circuit found single winding temp. high so check sensor then used spare sensor then restore wtg. | Close | 0.030342 | WTG Breakdown Maintenance | G05 | 15425 | 760.5382 | None
423 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | G23 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 14:07 | 15:45 | 15:47 | 1.6333 | 0.033333 | 1.6667 | Reboot then restore wtg. | Close | 0.042735 | WTG Breakdown Maintenance | G05 | 15425 | 1071.1806 | None
424 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | G28 | PWEGPL | MSEDCL | 2.564% | 5212 | Bus Preload Protection Thermal Relay Failure | BD |  | 6:40 | 10:12 | 12:32 | 3.5333 | 2.3333 | 5.8667 | Check related circuit found MPCB tripped so correct it then restore wtg. | Close | 0.15043 | WTG Breakdown Maintenance | G30 | 15469 | 3781.3111 | None
425 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | G34 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 12:40 | 12:40 | 18:30 | 0 | 5.8333 | 5.8333 | HYPM done then restore wtg. | Close | 0.14957 | WTG Scheduled Maintenance | G33 | 15954 | 3877.7083 | None
426 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 15526 | 15515.2181 | None
427 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 15526 | 15515.2181 | None
428 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | G16 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 8:20 | 9:15 | 9:16 | 0.91667 | 0.016667 | 0.93333 | Reset then restore wtg. | Close | 0.023932 | WTG Breakdown Maintenance | G17 | 16529 | 642.7944 | None
429 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | G22 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 8:32 | 9:45 | 12:40 | 1.2167 | 2.9167 | 4.1333 | Check related circuit found loose connection so tigh it then restore wtg. | Close | 0.10598 | WTG Breakdown Maintenance | G05 | 15121 | 2604.1722 | None
430 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | G22 | PWEGPL | MSEDCL | 2.564% | 208 | HU Pump Drive Failure | BD |  | 13:10 | 13:11 | 14:20 | 0.016667 | 1.15 | 1.1667 | Checked related circuit found HU contactor failure so replaced with new one then restore wtg. | Close | 0.029915 | WTG Breakdown Maintenance | G05 | 15121 | 735.0486 | None
431 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | G22 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 15:12 | 15:13 | 16:05 | 0.016667 | 0.86667 | 0.88333 | Checked related circuit found relay malfuction so interchage reley then restore wtg. | Close | 0.02265 | WTG Breakdown Maintenance | G05 | 15121 | 556.5368 | None
432 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | G30 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 14:25 | 14:25 | 17:07 | 0 | 2.7 | 2.7 | Manual stop for Blade bush gap inspection work | Close | 0.069231 | WTG Force Majeaure | G28 | 15526 | 1746.675 | None
433 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | G33 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:21 | 11:21 | 17:25 | 0 | 6.0667 | 6.0667 | HYPM done then restore wtg. | Close | 0.15556 | WTG Scheduled Maintenance | G34 | 15535 | 3926.9028 | None
434 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | G07 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 8:21 | 8:21 | 13:32 | 0 | 5.1833 | 5.1833 | Manual stop for oil leakage inspection work. Found oil leakage from Blade C so replaced pitch seal then restore wtg. | Close | 0.13291 | WTG Unscheduled Maintenance | G01 | 16821 | 3632.8688 | None
435 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-02 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 12844 | 12835.0806 | None
436 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-02 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 12844 | 12835.0806 | None
437 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-02 | G07 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 4:30 | 8:25 | 15:02 | 3.9167 | 6.6167 | 10.5333 | Check related circuit found oil leakage from Blade B. So replaced pitch seal then top-up 15 liter oil then restore wtg. | Close | 0.27009 | WTG Unscheduled Maintenance | G01 | 14789 | 5956.6806 | None
438 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-02 | G18 | PWEGPL | MSEDCL | 2.564% | 5236 | Error In Phase R Of The Inverter | BD |  | 9:10 | 9:32 | 15:21 | 0.36667 | 5.8167 | 6.1833 | Checked related circuit found carbon brush spring and holder failure so replaced with new one then restore wtg. | Close | 0.15855 | WTG Breakdown Maintenance | G19 | 14789 | 3810.2215 | None
439 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-02 | G22 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 16:05 | 16:05 | 16:10 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0021368 | WTG Breakdown Maintenance | G05 | 14538 | 50.4792 | None
440 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-02 | G27 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 11:54 | 11:54 | 15:24 | 0 | 3.5 | 3.5 | Manual stop for Blade bush gap inspection work | Close | 0.089744 | WTG Breakdown Maintenance | G25 | 12889 | 1879.6458 | None
441 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-02 | G32 | PWEGPL | MSEDCL | 2.564% | 119 | Yaw Contactor Active | BD |  | 15:56 | 16:35 | 16:37 | 0.65 | 0.033333 | 0.68333 | Reboot then restore wtg. | Close | 0.017521 | WTG Breakdown Maintenance | G26 | 11834 | 336.9403 | None
442 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 16562 | 16550.4986 | None
443 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 16562 | 16550.4986 | None
444 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | G09 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 15:10 | 15:35 | 15:36 | 0.41667 | 0.016667 | 0.43333 | Reset then restore wtg. | Close | 0.011111 | WTG Breakdown Maintenance | G12 | 17727 | 320.0708 | None
445 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 14:42 | 15:02 | 15:03 | 0.33333 | 0.016667 | 0.35 | Reset then restore wtg. | Close | 0.0089744 | WTG Breakdown Maintenance | G13 | 18239 | 265.9854 | None
446 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | G19 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 8:30 | 8:30 | 13:21 | 0 | 4.85 | 4.85 | Manual stop for oil leakage inspection & rectification found oil leak for Blade B pitch seal so replaced pith seal then restore wtg. | Close | 0.12436 | WTG Unscheduled Maintenance | G18 | 18234 | 3684.7875 | None
447 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | G32 | PWEGPL | MSEDCL | 2.564% | 102 | CW Feedback Failure | BD |  | 9:45 | 10:20 | 10:21 | 0.58333 | 0.016667 | 0.6 | Reset then restore wtg. | Close | 0.015385 | WTG Breakdown Maintenance | G26 | 14845 | 371.125 | None
448 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | G35 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:21 | 11:21 | 17:25 | 0 | 6.0667 | 6.0667 | HYPM done then checked blade bush gap inspection then restore wtg. | Close | 0.15556 | WTG Scheduled Maintenance | G36 | 14847 | 3752.9917 | None
449 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | G37 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 13:21 | 14:32 | 14:35 | 1.1833 | 0.05 | 1.2333 | Reboot then restore wtg. | Close | 0.031624 | WTG Breakdown Maintenance | G36 | 14847 | 762.9708 | None
450 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-04 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 11152 | 11144.2556 | None
451 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-04 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 11152 | 11144.2556 | None
452 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-04 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 13:56 | 14:20 | 14:21 | 0.4 | 0.016667 | 0.41667 | Reset then restore wtg. | Close | 0.010684 | WTG Breakdown Maintenance | G13 | 13578 | 235.7292 | None
453 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-04 | G22 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 18:05 | 18:42 | 18:43 | 0.61667 | 0.016667 | 0.63333 | Reset then restore wtg. | Close | 0.016239 | WTG Breakdown Maintenance | G05 | 11167 | 294.6847 | None
454 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-04 | G26 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 10:45 | 10:45 | 23:59 | 0 | 13.2333 | 13.2333 | Manual stop for pitch seal replacement work (work in progress) | Open | 0.33932 | WTG Unscheduled Maintenance | G32 | 8752 | 4825.7556 | None
455 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-04 | G36 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 10:35 | 10:35 | 17:10 | 0 | 6.5833 | 6.5833 | HYPM done then then restore wtg. | Close | 0.1688 | WTG Scheduled Maintenance | G37 | 8759 | 2402.6424 | None
456 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 7756 | 7750.6139 | None
457 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 7756 | 7750.6139 | None
458 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | G01 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 9:42 | 9:42 | 17:09 | 0 | 7.45 | 7.45 | Manual stop for Yaw caliper seal replacement work. | Close | 0.19103 | WTG Unscheduled Maintenance | G07 | 8346 | 2590.7375 | None
459 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | G05 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 17:01 | 17:01 | 18:05 | 0 | 1.0667 | 1.0667 | SEM meter Pole CT & PT installation work | Close | 0.02735 | WTG Unscheduled Maintenance | G22 | 6524 | 289.9556 | None
460 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 17:08 | 17:40 | 17:41 | 0.53333 | 0.016667 | 0.55 | Reset then restore wtg. | Close | 0.014103 | WTG Breakdown Maintenance | G09 | 8289 | 189.9563 | None
461 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | G14 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 17:05 | 17:30 | 17:31 | 0.41667 | 0.016667 | 0.43333 | Reset then restore wtg. | Close | 0.011111 | WTG Breakdown Maintenance | G15 | 8256 | 149.0667 | None
462 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | G21 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 12:00 | 12:00 | 12:24 | 0 | 0.4 | 0.4 | SEM meter Pole CT & PT installation work | Close | 0.010256 | WTG Unscheduled Maintenance | G22 | 6524 | 108.7333 | None
463 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | G22 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 12:37 | 12:37 | 13:20 | 0 | 0.71667 | 0.71667 | SEM meter Pole CT & PT installation work | Close | 0.018376 | WTG Unscheduled Maintenance | G05 | 6500 | 194.0972 | None
464 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | G26 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 0:00 | 0:00 | 23:59 | 0 | 23.9833 | 23.9833 | Manual stop for pitch seal replacement work (work in progress) | Open | 0.61496 | WTG Breakdown Maintenance | G32 | 5832 | 5827.95 | None
465 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | G28 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 13:58 | 13:58 | 16:45 | 0 | 2.7833 | 2.7833 | Manual stop for Blade bush gap inspection work | Close | 0.071368 | WTG Force Majeaure | G30 | 7741 | 897.741 | None
466 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-06 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8376 | 8370.1833 | None
467 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-06 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8376 | 8370.1833 | None
468 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-06 | G16 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 14:02 | 14:37 | 14:38 | 0.58333 | 0.016667 | 0.6 | Reset then restore wtg. | Close | 0.015385 | WTG Breakdown Maintenance | G17 | 9644 | 241.1 | None
469 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-06 | G19 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 12:32 | 13:10 | 14:12 | 0.63333 | 1.0333 | 1.6667 | Check related circuit check all motor found ok then restore wtg. | Close | 0.042735 | WTG Breakdown Maintenance | G18 | 9640 | 669.4444 | None
470 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-06 | G22 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 13:05 | 13:52 | 13:53 | 0.78333 | 0.016667 | 0.8 | Reset then restore wtg. | Close | 0.020513 | WTG Breakdown Maintenance | G05 | 8301 | 276.7 | None
471 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-06 | G23 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 15:20 | 16:02 | 16:04 | 0.7 | 0.033333 | 0.73333 | Reboot then restore wtg. | Close | 0.018803 | WTG Breakdown Maintenance | G05 | 8301 | 253.6417 | None
472 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-06 | G26 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 0:00 | 0:00 | 15:43 | 0 | 15.7167 | 15.7167 | Replaced Blade B pitch cylinder then top up 22 liter HU oil then restore wtg. | Close | 0.40299 | WTG Unscheduled Maintenance | G32 | 6972 | 4565.6917 | None
473 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-06 | G37 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:22 | 11:22 | 18:21 | 0 | 6.9833 | 6.9833 | HYPM done then checked blade bush gap inspection then restore wtg. | Close | 0.17906 | WTG Scheduled Maintenance | G36 | 6953 | 2023.1299 | None
474 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 9453 | 9446.4354 | None
475 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 9453 | 9446.4354 | None
476 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | G01 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 15:53 | 16:35 | 16:37 | 0.7 | 0.033333 | 0.73333 | Reboot then restore wtg. | Close | 0.018803 | WTG Breakdown Maintenance | G07 | 10989 | 335.775 | None
477 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | G06 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 15:53 | 16:30 | 16:32 | 0.61667 | 0.033333 | 0.65 | Reboot then restore wtg. | Close | 0.016667 | WTG Breakdown Maintenance | G03 | 12694 | 343.7958 | None
478 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | G07 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 15:54 | 16:45 | 16:47 | 0.85 | 0.033333 | 0.88333 | Reboot then restore wtg. | Close | 0.02265 | WTG Breakdown Maintenance | G01 | 10973 | 403.8674 | None
479 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | G16 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 15:59 | 16:20 | 16:22 | 0.35 | 0.033333 | 0.38333 | Reboot then restore wtg. | Close | 0.0098291 | WTG Breakdown Maintenance | G17 | 14472 | 231.15 | None
480 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | G18 | PWEGPL | MSEDCL | 2.564% | 5205 | Magnetothermic Of The Stator Protection Failure Or Door Open | BD |  | 15:55 | 16:35 | 16:44 | 0.66667 | 0.15 | 0.81667 | Reboot then restore wtg. | Close | 0.02094 | WTG Breakdown Maintenance | G19 | 14535 | 494.5937 | None
481 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | G21 | PWEGPL | MSEDCL | 2.564% | 5219 | Coolant Of The Coolant Circuit Failure | BD |  | 16:34 | 18:50 | 18:52 | 2.2667 | 0.033333 | 2.3 | Reboot then restore wtg. | Close | 0.058974 | WTG Breakdown Maintenance | G22 | 4538 | 434.8917 | None
482 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | G22 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 15:30 | 16:42 | 19:12 | 1.2 | 2.5 | 3.7 | Checked related circuit found MPCB tripped so checked motor resistance then restore wtg. | Close | 0.094872 | WTG Breakdown Maintenance | G05 | 8461 | 1304.4042 | None
483 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | G23 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 15:50 | 18:59 | 19:01 | 3.15 | 0.033333 | 3.1833 | Reboot then restore wtg. | Close | 0.081624 | WTG Breakdown Maintenance | G05 | 8461 | 1122.2576 | None
484 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | G25 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 11:30 | 11:30 | 14:47 | 0 | 3.2833 | 3.2833 | Manual stop for Blade bush gap inspection work | Close | 0.084188 | WTG Force Majeaure | G27 | 9472 | 1295.8222 | None
485 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | G30 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 16:50 | 18:45 | 18:47 | 1.9167 | 0.033333 | 1.95 | Reboot then restore wtg. | Close | 0.05 | WTG Breakdown Maintenance | G28 | 9453 | 768.0563 | None
486 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | G34 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 16:58 | 19:00 | 19:02 | 2.0333 | 0.033333 | 2.0667 | Reboot then restore wtg. | Close | 0.052991 | WTG Breakdown Maintenance | G33 | 4790 | 412.4722 | None
487 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | G37 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 16:18 | 19:15 | 19:17 | 2.95 | 0.033333 | 2.9833 | Reset then restore wtg. | Close | 0.076496 | WTG Breakdown Maintenance | G36 | 4762 | 591.9431 | None
488 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-07 | G38 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:30 | 11:30 | 17:48 | 0 | 6.3 | 6.3 | HYPM done then restore wtg. | Close | 0.16154 | WTG Scheduled Maintenance | G39 | 6794 | 1783.425 | None
489 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 7369 | 7363.8826 | None
490 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 7369 | 7363.8826 | None
491 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | G03 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 13:02 | 15:30 | 15:32 | 2.4667 | 0.033333 | 2.5 | Reboot then restore wtg. | Close | 0.064103 | WTG Breakdown Maintenance | G04 | 8849 | 921.7708 | None
492 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | G10 | PWEGPL | MSEDCL | 2.564% | 1899 | Automatic Secondaries Not OK | BD |  | 13:15 | 15:02 | 15:03 | 1.7833 | 0.016667 | 1.8 | Reset then restore wtg. | Close | 0.046154 | WTG Breakdown Maintenance | G11 | 8890 | 666.75 | None
493 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | G22 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 9:10 | 9:42 | 13:30 | 0.53333 | 3.8 | 4.3333 | Check related circuit found MPCB & Contactor failure so replaced with new one then restore wtg. | Close | 0.11111 | WTG Breakdown Maintenance | G05 | 7901 | 1426.5694 | None
494 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | G25 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 12:18 | 12:18 | 12:34 | 0 | 0.26667 | 0.26667 | SEM meter Pole CT & PT installation work | Close | 0.0068376 | WTG Unscheduled Maintenance | G27 | 7921 | 88.0111 | None
495 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | G28 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 11:42 | 11:42 | 12:01 | 0 | 0.31667 | 0.31667 | SEM meter Pole CT & PT installation work | Close | 0.0081197 | WTG Unscheduled Maintenance | G30 | 7942 | 104.7903 | None
496 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | G35 | PWEGPL | MSEDCL | 2.564% | 5220 | Encoder Not OK | BD |  | 9:48 | 10:07 | 10:08 | 0.31667 | 0.016667 | 0.33333 | Reset then restore wtg. | Close | 0.008547 | WTG Breakdown Maintenance | G36 | 6856 | 95.2222 | None
497 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | G35 | PWEGPL | MSEDCL | 2.564% | 5220 | Encoder Not OK | BD |  | 13:10 | 14:08 | 14:10 | 0.96667 | 0.033333 | 1 | Reboot then restore wtg. | Close | 0.025641 | WTG Breakdown Maintenance | G36 | 6856 | 285.6667 | None
498 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | G37 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 9:51 | 10:15 | 16:37 | 0.4 | 6.3667 | 6.7667 | Checked related circuit found oil leakage from Blade A. so replaced pitch seal then restore wtg. | Close | 0.1735 | WTG Breakdown Maintenance | G36 | 6856 | 1933.0111 | None
499 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 10:12 | 10:34 | 10:36 | 0.36667 | 0.033333 | 0.4 | Reset then restore wtg. | Close | 0.010256 | WTG Breakdown Maintenance | G40 | 6857 | 114.2833 | None
500 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 13:02 | 13:55 | 13:57 | 0.88333 | 0.033333 | 0.91667 | Reboot then restore wtg. | Close | 0.023504 | WTG Breakdown Maintenance | G40 | 6857 | 261.8993 | None
501 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 4526 | 4522.8569 | None
502 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 4526 | 4522.8569 | None
503 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | G03 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 12:07 | 12:07 | 12:30 | 0 | 0.38333 | 0.38333 | SEM meter Pole CT & PT installation work | Close | 0.0098291 | WTG Unscheduled Maintenance | G04 | 3583 | 57.2285 | None
504 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | G04 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 12:57 | 12:57 | 13:20 | 0 | 0.38333 | 0.38333 | SEM meter Pole CT & PT installation work | Close | 0.0098291 | WTG Unscheduled Maintenance | G03 | 3562 | 56.8931 | None
505 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | G06 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 16:57 | 16:57 | 17:16 | 0 | 0.31667 | 0.31667 | SEM meter Pole CT & PT installation work | Close | 0.0081197 | WTG Unscheduled Maintenance | G03 | 3562 | 46.9986 | None
506 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | G08 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 11:18 | 11:18 | 11:53 | 0 | 0.58333 | 0.58333 | SEM meter Pole CT & PT installation work | Close | 0.014957 | WTG Unscheduled Maintenance | G03 | 3562 | 86.5764 | None
507 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | G09 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 15:32 | 15:32 | 15:55 | 0 | 0.38333 | 0.38333 | SEM meter Pole CT & PT installation work | Close | 0.0098291 | WTG Unscheduled Maintenance | G12 | 4056 | 64.7833 | None
508 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | G10 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 16:16 | 16:16 | 16:36 | 0 | 0.33333 | 0.33333 | SEM meter Pole CT & PT installation work | Close | 0.008547 | WTG Unscheduled Maintenance | G11 | 4026 | 55.9167 | None
509 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | G34 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 11:10 | 11:10 | 12:30 | 0 | 1.3333 | 1.3333 | Manual stop for oil leakage inspection work | Close | 0.034188 | WTG Unscheduled Maintenance | G33 | 3593 | 199.6111 | None
510 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | G37 | PWEGPL | MSEDCL | 2.564% | 1819 | RC Filter Failure | BD |  | 14:27 | 15:01 | 17:30 | 0.56667 | 2.4833 | 3.05 | Check related circuit found 33k resistor and RC filter card failure so replaced both with new one then restore wtg. | Close | 0.078205 | WTG Breakdown Maintenance | G36 | 3578 | 454.7042 | None
511 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | G39 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 11:20 | 11:20 | 12:45 | 0 | 1.4167 | 1.4167 | Manual stop for oil leakage inspection work | Close | 0.036325 | WTG Unscheduled Maintenance | G40 | 3566 | 210.4931 | None
512 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 4032 | 4029.2 | None
513 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 4032 | 4029.2 | None
514 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | G04 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 10:58 | 11:50 | 23:59 | 0.86667 | 12.15 | 13.0167 | work in progress | Open | 0.33376 | WTG Breakdown Maintenance | G03 | 6673 | 3619.1757 | None
515 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | G09 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD |  | 16:26 | 16:55 | 18:58 | 0.48333 | 2.05 | 2.5333 | Checked related circuit found propotional valve failure then replaced . | Close | 0.064957 | WTG Breakdown Maintenance | G12 | 7043 | 743.4278 | None
516 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8517 | 8511.0854 | None
517 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8517 | 8511.0854 | None
518 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | G04 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 0:00 | 12:18 | 13:42 | 12.3 | 1.4 | 13.7 | Change PRV-10 & RV 8-10 Valve than start the WTG | Close | 0.35128 | WTG Breakdown Maintenance | G03 | 12116 | 6916.2167 | None
519 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | G21 | PWEGPL | MSEDCL | 2.564% | 5228 | Preload Failure | BD |  | 8:30 | 10:10 | 23:59 | 1.6667 | 13.8167 | 15.4833 | Checked related circuit found KC004 Contactor replace | Open | 0.39701 | WTG Breakdown Maintenance | G22 | 8658 | 5585.6125 | None
520 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | G23 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 10:30 | 11:15 | 23:04 | 0.75 | 11.8167 | 12.5667 | Checked related circuit & replace slipring and CAP module than start WTG | Close | 0.32222 | WTG Breakdown Maintenance | G22 | 8658 | 4533.425 | None
521 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 4215 | 4212.0729 | None
522 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 4215 | 4212.0729 | None
523 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | G04 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 9:16 | 11:57 | 13:42 | 2.6833 | 1.75 | 4.4333 | Checked related circuit found niddel valve failure than replace . | Close | 0.11368 | WTG Breakdown Maintenance | G07 | 3109 | 574.3014 | None
524 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | G03 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 11:20 | 11:20 | 13:35 | 0 | 2.25 | 2.25 | Manual stop for Blade bush gap inspection work | Close | 0.057692 | WTG Force Majeaure | G06 | 3086 | 289.3125 | None
525 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | G23 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 9:15 | 11:21 | 17:21 | 2.1 | 6 | 8.1 | Checked related circuit found Cab module failure then replace. | Close | 0.20769 | WTG Force Majeaure | G05 | 4032 | 1360.8 | None
526 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | G22 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 11:32 | 11:32 | 13:35 | 0 | 2.05 | 2.05 | SEM Yard Earthing work done then restore wtg. | Close | 0.052564 | WTG Unscheduled Maintenance | G05 | 4032 | 344.4 | None
527 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | G21 | PWEGPL | MSEDCL | 2.564% | 5228 | Preload Failure | BD |  | 0:00 | 0:00 | 20:36 | 0 | 20.6 | 20.6 | Checked related circuit found KC004 Contactor addon replace | Close | 0.52821 | WTG Breakdown Maintenance | G05 | 4032 | 3460.8 | None
528 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G30 | 4579 | 4575.8201 | None
529 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G30 | 4579 | 4575.8201 | None
530 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | G04 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 12:04 | 12:38 | 15:19 | 0.56667 | 2.6833 | 3.25 | No leakage fond than start WTG | Close | 0.083333 | WTG Breakdown Maintenance | G02 | 6734 | 911.8958 | None
531 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | G07 | PWEGPL | MSEDCL | 2.564% | 5236 | Error In Phase R Of The Inverter | BD |  | 20:14 | 20:43 | 21:32 | 0.48333 | 0.81667 | 1.3 | Checked related circuit no any obsarvation than start WTG | Close | 0.033333 | WTG Breakdown Maintenance | G01 | 6782 | 367.3583 | None
532 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | G14 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 17:30 | 17:30 | 21:48 | 0 | 4.3 | 4.3 | Manual stop for Blade bush gap inspection work | Close | 0.11026 | WTG Force Majeaure | G15 | 7344 | 1315.8 | None
533 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | G40 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 5:45 | 12:45 | 23:59 | 7 | 11.2333 | 18.2333 | checked T connector failure (work in progress) | Open | 0.46752 | WTG Breakdown Maintenance | G39 | 4008 | 3044.9667 | Material shotage Tee connector.
534 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | G28 | PWEGPL | MSEDCL | 2.564% | 2114 | Analogue Card Failure | BD |  | 12:17 | 12:38 | 13:01 | 0.35 | 0.38333 | 0.73333 | Reset then restore wtg. | Close | 0.018803 | WTG Breakdown Maintenance | G30 | 4579 | 139.9139 | None
535 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | G21 | PWEGPL | MSEDCL | 2.564% | 5228 | Preload Failure | BD |  | 6:14 | 10:12 | 10:18 | 3.9667 | 0.1 | 4.0667 | Reset then restore wtg. | Close | 0.10427 | WTG Breakdown Maintenance | G22 | 4516 | 765.2111 | None
536 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G30 | 3268 | 3265.7306 | None
537 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G30 | 3268 | 3265.7306 | None
538 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | G28 | PWEGPL | MSEDCL | 2.564% | 803 | Low Pitch Value In Stop Mode (1 Cylinder) | BD |  | 11:10 | 11:55 | 14:24 | 0.75 | 2.4833 | 3.2333 | Check related ckt found bulluf sensor failure then replaced & restore WTG. | Close | 0.082906 | WTG Breakdown Maintenance | G30 | 3268 | 440.2722 | None
539 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | G40 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | checked T connector failure (work in progress) | Open | 0.61496 | WTG Breakdown Maintenance | G39 | 2901 | 2898.9854 | Material shotage Tee connector.
540 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | G14 | PWEGPL | MSEDCL | 2.564% | 5232 | Error In Phase R Of The Rectifier | BD |  | 6:30 | 8:11 | 22:10 | 1.6833 | 13.9833 | 15.6667 | Check related ckt found Component failure then replace Rectifire Side 3 IGBT,Fuse ,KC002 Contactor ,800 HC resistor and check capacitor bank then restore WTG. | Close | 0.40171 | WTG Breakdown Maintenance | G15 | 5076 | 3313.5 | None
541 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | G04 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 17:55 | 19:02 | 20:29 | 1.1167 | 1.45 | 2.5667 | Check related ckt found hose damaged then replaced and restore WTG. | Close | 0.065812 | WTG Breakdown Maintenance | G02 | 4843 | 517.9319 | None
542 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | G13 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 15:15 | 15:15 | 18:30 | 0 | 3.25 | 3.25 | Manual stop for Blade bush gap inspection work | Close | 0.083333 | WTG Force Majeaure | G12 | 5012 | 678.7083 | None
543 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | G21 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 7:34 | 11:34 | 13:30 | 4 | 1.9333 | 5.9333 | Manual stop for Blade bush gap inspection work | Close | 0.15214 | WTG Force Majeaure | G22 | 3256 | 804.9556 | None
544 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | G21 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | FM |  | 2:02 | 2:02 | 3:18 | 0 | 1.2667 | 1.2667 | Transformer inspection work. | Close | 0.032479 | WTG Unscheduled Maintenance | G22 | 3256 | 171.8444 | None
545 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 5042 | 5038.4986 | None
546 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 5042 | 5038.4986 | None
547 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | G06 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 11:28 | 11:28 | 14:26 | 0 | 2.9667 | 2.9667 | SEM meter Pole CT & PT installation work | Close | 0.076068 | WTG Unscheduled Maintenance | G03 | 6423 | 793.9542 | None
548 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | G07 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 14:15 | 14:15 | 16:00 | 0 | 1.75 | 1.75 | SEM meter Pole CT & PT installation work | Close | 0.044872 | WTG Unscheduled Maintenance | G01 | 6421 | 468.1979 | None
549 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | G12 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 11:15 | 11:15 | 14:40 | 0 | 3.4167 | 3.4167 | Manual stop for Blade bush gap inspection work | Close | 0.087607 | WTG Force Majeaure | G13 | 5867 | 835.2326 | None
550 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | G25 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 13:20 | 14:02 | 15:46 | 0.7 | 1.7333 | 2.4333 | Check related circuit found no leakage then restore wtg. | Close | 0.062393 | WTG Breakdown Maintenance | G27 | 5056 | 512.6222 | None
551 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | G33 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 12:28 | 12:28 | 16:27 | 0 | 3.9833 | 3.9833 | Manual stop for Gearbox fan motor replaced then restore wtg. | Close | 0.10214 | WTG Unscheduled Maintenance | G34 | 4572 | 758.825 | None
552 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | G39 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 12:07 | 12:07 | 18:58 | 0 | 6.85 | 6.85 | HYPM done then then restore wtg. | Close | 0.17564 | WTG Scheduled Maintenance | G38 | 4588 | 1309.4917 | None
553 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | G40 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 19:40 | 20:33 | 19.6667 | 0.88333 | 20.55 | Check related circuit found B Phase Tee connector failure so replaced with new one then restore wtg. | Close | 0.52692 | WTG Breakdown Maintenance | G26 | 4572 | 3914.775 | Material shotage Tee connector.
554 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8165 | 8159.3299 | None
555 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8165 | 8159.3299 | None
556 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | G01 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD |  | 12:01 | 12:35 | 15:14 | 0.56667 | 2.65 | 3.2167 | Checked related circuit found loose connection so tight it then restore wtg. | Close | 0.082479 | WTG Unscheduled Maintenance | G07 | 10576 | 1417.4778 | None
557 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | G02 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 12:30 | 12:30 | 14:10 | 0 | 1.6667 | 1.6667 | Manual stop for SEM meter CT/PT istallation work | Close | 0.042735 | WTG Unscheduled Maintenance | G04 | 9888 | 686.6667 | None
558 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | G04 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 16:21 | 16:41 | 18:35 | 0.33333 | 1.9 | 2.2333 | Check related circuit found ok then set PRV 8-10 Valve then replaced Gearbox cooling fan motor replaced then restore wtg. | Close | 0.057265 | WTG Unscheduled Maintenance | G03 | 10542 | 980.9917 | None
559 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | G06 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 16:30 | 17:45 | 17:50 | 1.25 | 0.083333 | 1.3333 | Reset then restore wtg. | Close | 0.034188 | WTG Breakdown Maintenance | G03 | 10542 | 585.6667 | None
560 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | G19 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:40 | 11:40 | 23:59 | 0 | 12.3167 | 12.3167 | Manual stop for pitch seal replacement work (Pitch cylinder head sturcked work in progress) | Open | 0.31581 | WTG Breakdown Maintenance | G18 | 9966 | 5114.4958 | None
561 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | G40 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:46 | 11:46 | 17:28 | 0 | 5.7 | 5.7 | HYPM done then then restore wtg. | Close | 0.14615 | WTG Scheduled Maintenance | G39 | 7388 | 1754.65 | None
562 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 4123 | 4120.1368 | None
563 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 23.9833 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 4123 | 4120.1368 | None
564 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | G06 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 11:33 | 11:33 | 14:40 | 0 | 1900-01-02 02:48 | 1900-01-02 02:48 | Checked related circuit found ok then replaced smoke sensor then restore wtg. | Close | 0.079915 | WTG Unscheduled Maintenance | G03 | 5684 | 738.1306 | None
565 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | G19 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 0:00 | 0:00 | 22:45 | 0 | 1900-01-21 18:00 | 1900-01-21 18:00 | Manual stop for Blade B pitch cylinder replaced then restore wtg. | Close | 0.58333 | WTG Unscheduled Maintenance | G18 | 6475 | 6137.7604 | None
566 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | G26 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 12:16 | 12:16 | 19:46 | 0 | 7.5 | 7.5 | HYPM done then then restore wtg. | Close | 0.19231 | WTG Scheduled Maintenance | G32 | 3521 | 1100.3125 | None
567 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | G02 | PWEGPL | MSEDCL | 2.564% | 5225 | Fault In Analog Electronic Power Supply | BD |  | 14:48 | 15:20 | 15:22 | 0.53333 | 0.033333 | 0.56667 | Reset then restore wtg. | Close | 0.01453 | WTG Breakdown Maintenance | G04 | 5681 | 134.1347 | None
568 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | G07 | PWEGPL | MSEDCL | 2.564% | 5225 | Fault In Analog Electronic Power Supply | BD |  | 14:48 | 15:37 | 15:39 | 0.81667 | 0.033333 | 0.85 | Reset then restore wtg. | Close | 0.021795 | WTG Breakdown Maintenance | G01 | 5673 | 200.9187 | None
569 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 3543 | 3540.5396 | None
570 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 3572 | 3569.5194 | None
571 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | G01 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 12:55 | 13:17 | 14:05 | 0.36667 | 0.8 | 1899-12-31 04:00 | Slipring clean then restore wtg | Close | 0.029915 | WTG Breakdown Maintenance | G07 | 3537 | 171.9375 | None
572 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | G32 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 12:26 | 12:26 | 18:03 | 0 | 5.6167 | 5.6167 | HYPM done then then restore wtg. | Close | 0.14402 | WTG Scheduled Maintenance | G26 | 3162 | 739.9958 | None
573 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | G33 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 16:10 | 16:42 | 16:45 | 0.53333 | 0.05 | 0.58333 | Reboot then restore wtg. | Close | 0.014957 | WTG Breakdown Maintenance | G34 | 3121 | 75.8576 | None
574 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 4109 | 4106.1465 | None
575 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 4109 | 4106.1465 | None
576 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | G05 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 11:16 | 11:16 | 12:20 | 0 | 1899-12-31 01:36 | 1899-12-31 01:36 | Manual stop for SEM meter CT/PT istallation work | Close | 0.02735 | WTG Unscheduled Maintenance | G23 | 4115 | 868.7222 | None
577 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | G22 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:04 | 11:04 | 17:30 | 0 | 6.4333 | 6.4333 | HYPM done then then restore wtg. | Close | 0.16496 | WTG Scheduled Maintenance | G21 | 4102 | 1099.5639 | None
578 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | G28 | PWEGPL | MSEDCL | 2.564% | 2102 | PLC Module Failure | BD |  | 16:22 | 16:58 | 17:01 | 0.6 | 0.05 | 0.65 | Reboot then restore wtg. | Close | 0.016667 | WTG Breakdown Maintenance | G30 | 4121 | 111.6104 | None
579 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 5242 | 5238.3597 | None
580 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 5242 | 5238.3597 | None
581 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | G02 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 16:02 | 16:35 | 16:37 | 0.55 | 0.033333 | 0.58333 | Reset then restore wtg. | Close | 0.014957 | WTG Breakdown Maintenance | G04 | 5575 | 135.5035 | None
582 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | G03 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 16:15 | 16:52 | 16:54 | 0.61667 | 0.033333 | 0.65 | Reset then restore wtg. | Close | 0.016667 | WTG Breakdown Maintenance | G04 | 5575 | 150.9896 | None
583 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | G09 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 16:15 | 17:02 | 17:04 | 0.78333 | 0.033333 | 0.81667 | Reset then restore wtg. | Close | 0.02094 | WTG Breakdown Maintenance | G12 | 5342 | 181.7764 | None
584 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | G10 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 11:20 | 11:20 | 16:10 | 0 | 1900-01-03 20:00 | 1900-01-03 20:00 | Manual stop for lift clamp replacement work | Close | 0.12393 | WTG Unscheduled Maintenance | G11 | 5543 | 1116.2986 | None
585 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | G21 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:40 | 11:40 | 17:41 | 0 | 6.0167 | 6.0167 | HYPM done then then restore wtg. | Close | 0.15427 | WTG Scheduled Maintenance | G22 | 5200 | 1303.6111 | None
586 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | G32 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 14:25 | 15:10 | 15:12 | 0.75 | 0.033333 | 0.78333 | Reset then restore wtg. | Close | 0.020085 | WTG Breakdown Maintenance | G26 | 3501 | 114.2687 | None
587 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | G26 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 14:25 | 15:25 | 15:27 | 1 | 0.033333 | 1899-12-31 00:48 | Reset then restore wtg. | Close | 0.026496 | WTG Breakdown Maintenance | G40 | 3696 | 159.1333 | None
588 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 14:25 | 15:44 | 15:46 | 1.3167 | 0.033333 | 1899-12-31 08:24 | Reset then restore wtg. | Close | 0.034615 | WTG Breakdown Maintenance | G40 | 3696 | 207.9 | None
589 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-21 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 5644 | 5640.0806 | None
590 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-21 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 5644 | 5640.0806 | None
591 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-21 | G01 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 11:53 | 11:53 | 12:45 | 0 | 0.86667 | 0.86667 | Manual stop for SEM meter CT/PT istallation work | Close | 0.022222 | WTG Unscheduled Maintenance | G07 | 5633 | 203.4139 | None
592 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-21 | G06 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 14:07 | 14:51 | 15:55 | 0.73333 | 1899-12-31 01:36 | 1899-12-31 19:12 | Checked related circuit found ok then restore wtg. | Close | 0.046154 | WTG Breakdown Maintenance | G03 | 5632 | 422.4 | None
593 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-21 | G23 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 12:10 | 12:10 | 19:00 | 0 | 6.8333 | 6.8333 | HYPM done then then restore wtg. | Close | 0.17521 | WTG Scheduled Maintenance | G05 | 5601 | 1594.7292 | None
594 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-21 | G33 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 18:07 | 18:42 | 21:39 | 0.58333 | 1900-01-01 22:48 | 1900-01-02 12:48 | checked related circuit found no leakage then top-up 10 liter HU oil then restore wtg. | Close | 0.090598 | WTG Breakdown Maintenance | G34 | 4645 | 683.8472 | None
595 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8852 | 8845.8528 | None
596 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 8852 | 8845.8528 | None
597 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | G03 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 15:37 | 15:37 | 17:05 | 0 | 1899-12-31 11:12 | 1899-12-31 11:12 | Manual stop for SEM meter CT/PT istallation work | Close | 0.037607 | WTG Unscheduled Maintenance | G04 | 6263 | 382.7389 | None
598 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | G04 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 14:35 | 14:35 | 15:25 | 0 | 0.83333 | 0.83333 | Manual stop for SEM meter CT/PT istallation work | Close | 0.021368 | WTG Unscheduled Maintenance | G03 | 6279 | 218.0208 | None
599 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | G05 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:51 | 11:51 | 18:11 | 0 | 6.3333 | 6.3333 | HYPM done then then restore wtg. | Close | 0.16239 | WTG Scheduled Maintenance | G22 | 8842 | 2333.3056 | None
600 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | G32 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 12:30 | 13:30 | 13:32 | 1 | 0.033333 | 1899-12-31 00:48 | Reset then restore wtg. | Close | 0.026496 | WTG Breakdown Maintenance | G26 | 6041 | 260.0986 | None
601 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | G38 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:04 | 11:04 | 13:14 | 0 | 1900-01-01 04:00 | 1900-01-01 04:00 | Manual stop for Carbon brush replacement work. | Close | 0.055556 | WTG Unscheduled Maintenance | G39 | 6049 | 546.0903 | None
602 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 2038 | 2036.5847 | None
603 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 2038 | 2036.5847 | None
604 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | G11 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 14:57 | 15:42 | 15:45 | 0.75 | 0.05 | 0.8 | Reset then restore wtg. | Close | 0.020513 | WTG Breakdown Maintenance | G10 | 2830 | 94.3333 | None
605 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | G12 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | Manual stop |  | 11:20 | 11:20 | 13:30 | 0 | 1900-01-01 04:00 | 1900-01-01 04:00 | Manual stop for repeted error (low pressure on hydraulic group and failure of the rotor power supply failure) found losse connection and set RV8-10 valve then restore wtg. | Close | 0.055556 | WTG Unscheduled Maintenance | G13 | 3107 | 280.4931 | None
606 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | G15 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:17 | 11:17 | 17:57 | 0 | 6.6667 | 6.6667 | HYPM done then then restore wtg. | Close | 0.17094 | WTG Scheduled Maintenance | G16 | 3109 | 863.6111 | None
607 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | G16 | PWEGPL | MSEDCL | 2.564% | 5225 | Fault In Analog Electronic Power Supply | BD |  | 16:01 | 16:25 | 16:27 | 0.4 | 0.033333 | 0.43333 | Reset then restore wtg. | Close | 0.011111 | WTG Breakdown Maintenance | G17 | 3111 | 56.1708 | None
608 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | G25 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 14:15 | 14:15 | 15:00 | 0 | 0.75 | 0.75 | Manual stop for SEM meter CT/PT earthing istallation work | Close | 0.019231 | WTG Unscheduled Maintenance | G27 | 2014 | 62.9375 | None
609 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-24 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 7772 | 7766.6028 | None
610 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-24 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 7772 | 7766.6028 | None
611 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-24 | G16 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 12:10 | 12:10 | 19:55 | 0 | 7.75 | 7.75 | HYPM done then then restore wtg. | Close | 0.19872 | WTG Scheduled Maintenance | G17 | 7365 | 2378.2813 | None
612 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-24 | G26 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 13:55 | 13:55 | 16:01 | 0 | 2.1 | 2.1 | Manual stop for HU main accumulator replacement work | Close | 0.053846 | WTG Unscheduled Maintenance | G32 | 6467 | 565.8625 | None
613 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-24 | G34 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 12:20 | 12:58 | 13:00 | 0.63333 | 0.033333 | 0.66667 | Reset then restore wtg. | Close | 0.017094 | WTG Breakdown Maintenance | G33 | 6457 | 179.3611 | None
614 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 5528 | 5524.1611 | None
615 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 5528 | 5524.1611 | None
616 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | G10 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 11:00 | 11:30 | 11:31 | 0.5 | 0.016667 | 0.51667 | Reset then restore wtg. | Close | 0.013248 | WTG Breakdown Maintenance | G11 | 7164 | 154.225 | None
617 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | G16 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 5:23 | 6:43 | 6:45 | 1.3333 | 0.033333 | 1899-12-31 08:48 | Reboot then restore wtg. | Close | 0.035043 | WTG Breakdown Maintenance | G15 | 7129 | 405.9569 | None
618 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | G17 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 10:58 | 10:58 | 17:59 | 0 | 7.0167 | 7.0167 | HYPM done then then restore wtg. | Close | 0.17991 | WTG Scheduled Maintenance | G16 | 6898 | 2016.7069 | None
619 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | G32 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 12:36 | 12:36 | 14:05 | 0 | 1899-12-31 11:36 | 1899-12-31 11:36 | Manual stop for Blade bush gap inspection work | Close | 0.038034 | WTG Force Majeaure | G26 | 5842 | 361.0681 | None
620 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 3649 | 3646.466 | None
621 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 3649 | 3646.466 | None
622 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | G04 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 20:00 | 20:58 | 21:00 | 0.96667 | 0.033333 | 1 | Reset then restore wtg. | Close | 0.025641 | WTG Breakdown Maintenance | G03 | 4421 | 184.2083 | None
623 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | G18 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 13:05 | 13:05 | 19:51 | 0 | 6.7667 | 6.7667 | HYPM done then then restore wtg. | Close | 0.1735 | WTG Scheduled Maintenance | G17 | 3753 | 1058.1375 | None
624 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | G19 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:21 | 11:21 | 18:15 | 0 | 6.9 | 6.9 | HYPM done then then restore wtg. | Close | 0.17692 | WTG Scheduled Maintenance | G20 | 3758 | 1080.425 | None
625 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | G25 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 13:02 | 13:35 | 15:10 | 0.55 | 1899-12-31 14:00 | 1900-01-01 03:12 | Checked and found FG780 MPCB tripped so correct it then checked motor and connections then restore wtg. | Close | 0.054701 | WTG Breakdown Maintenance | G27 | 3652 | 324.6222 | None
626 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | G25 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 23:16 | 23:40 | 23:59 | 0.4 | 0.31667 | 0.71667 | work in progress | Open | 0.018376 | WTG Breakdown Maintenance | G27 | 3652 | 109.0528 | None
627 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | G30 | PWEGPL | MSEDCL | 2.564% | 208 | HU Pump Drive Failure | BD |  | 16:15 | 16:53 | 17:30 | 0.63333 | 0.61667 | 1899-12-31 06:00 | Checked related circuit found HU contactor failure so replaced with new one then restore wtg. | Close | 0.032051 | WTG Breakdown Maintenance | G28 | 3649 | 190.0521 | None
628 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | G40 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 17:00 | 17:58 | 18:00 | 0.96667 | 0.033333 | 1 | Reset then restore wtg. | Close | 0.025641 | WTG Breakdown Maintenance | G39 | 3529 | 147.0417 | None
629 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 11859 | 11850.7646 | None
630 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 11859 | 11850.7646 | None
631 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | G01 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 19:50 | 19:50 | 23:59 | 0 | 1900-01-03 03:36 | 1900-01-03 03:36 | (work in progress) Tee-connector failure wtg side. | Close | 0.10641 | WTG Breakdown Maintenance | G07 | 10615 | 1835.5104 | None
632 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | G04 | PWEGPL | MSEDCL | 2.564% | CE100014 | Manual Stop - Audit | Manual stop/Customer |  | 13:30 | 13:30 | 15:00 | 0 | 1899-12-31 12:00 | 1899-12-31 12:00 | Manual stop for Customer audit work | Close | 0.038462 | WTG Unscheduled Maintenance | G03 | 10623 | 663.9375 | None
633 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | G06 | PWEGPL | MSEDCL | 2.564% | CE100014 | Manual Stop - Audit | Manual stop/Customer |  | 11:10 | 11:10 | 13:00 | 0 | 1899-12-31 20:00 | 1899-12-31 20:00 | Manual stop for Customer audit work | Close | 0.047009 | WTG Unscheduled Maintenance | G03 | 10623 | 811.4792 | None
634 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | G20 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:39 | 11:39 | 18:36 | 0 | 6.95 | 6.95 | HYPM done then then restore wtg. | Close | 0.17821 | WTG Scheduled Maintenance | G19 | 14782 | 4280.6208 | None
635 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | G25 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 0:00 | 0:00 | 1:18 | 0 | 1899-12-31 07:12 | 1899-12-31 07:12 | Checked related circuit found MPCB failure so replaced with new one then restore wtg. | Close | 0.033333 | WTG Breakdown Maintenance | G27 | 11852 | 641.9833 | None
636 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | G30 | PWEGPL | MSEDCL | 2.564% | CE100014 | Manual Stop - Audit | Manual stop/Customer |  | 11:20 | 11:20 | 12:40 | 0 | 1899-12-31 08:00 | 1899-12-31 08:00 | Manual stop for Customer audit work | Close | 0.034188 | WTG Unscheduled Maintenance | G28 | 11859 | 658.8333 | None
637 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-27 | G33 | PWEGPL | MSEDCL | 2.564% | CE100014 | Manual Stop - Audit | Manual stop/Customer |  | 13:10 | 13:10 | 14:20 | 0 | 1899-12-31 04:00 | 1899-12-31 04:00 | Manual stop for Customer audit work | Close | 0.029915 | WTG Unscheduled Maintenance | G34 | 10421 | 506.5764 | None
638 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 9969 | 9962.0771 | None
639 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 9969 | 9962.0771 | None
640 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | G01 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 0:00 | 16:10 | 0 | 1900-01-15 04:00 | 1900-01-15 04:00 | Checked related circuit found Tee connector failure so replaced Tee connector with new one then restore wtg. | Close | 0.41453 | WTG Breakdown Maintenance | G07 | 15953 | 10746.1181 | None
641 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | G07 | PWEGPL | MSEDCL | 2.564% | 5225 | Fault In Analog Electronic Power Supply | BD |  | 1:18 | 1:48 | 1:50 | 0.5 | 0.033333 | 0.53333 | Reset then restore wtg. | Close | 0.013675 | WTG Breakdown Maintenance | G03 | 16385 | 364.1111 | None
642 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | G14 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 10:15 | 10:15 | 17:36 | 0 | 7.35 | 7.35 | HYPM done then then restore wtg. | Close | 0.18846 | WTG Scheduled Maintenance | G15 | 13759 | 4213.6937 | None
643 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | G16 | PWEGPL | MSEDCL | 2.564% | 5225 | Fault In Analog Electronic Power Supply | BD |  | 11:04 | 11:35 | 11:45 | 0.51667 | 0.16667 | 0.68333 | CCU reset then restore wtg. | Close | 0.017521 | WTG Breakdown Maintenance | G17 | 13752 | 391.55 | None
644 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | G33 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD |  | 15:12 | 15:52 | 19:38 | 0.66667 | 1900-01-02 18:24 | 1900-01-03 10:24 | Checked related circuit found TA033 power supply failure so replaced with new one then restore wtg. | Close | 0.11368 | WTG Breakdown Maintenance | G34 | 7422 | 1371.0083 | None
645 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-29 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 12268 | 12259.4806 | None
646 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-29 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 12268 | 12259.4806 | None
647 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-29 | G04 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 17:35 | 18:20 | 18:22 | 0.75 | 0.033333 | 0.78333 | Reset then restore wtg. | Close | 0.020085 | WTG Breakdown Maintenance | G03 | 16454 | 537.0403 | None
648 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-29 | G13 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:30 | 11:30 | 18:45 | 0 | 7.25 | 7.25 | HYPM done then then restore wtg. | Close | 0.1859 | WTG Scheduled Maintenance | G12 | 16467 | 4974.4062 | None
649 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-29 | G14 | PWEGPL | MSEDCL | 2.564% | 5238 | Error In Phase T Of The Inverter | BD |  | 11:00 | 11:35 | 14:20 | 0.58333 | 1900-01-01 18:00 | 1900-01-02 08:00 | Checked related circuit found Diode failure so replaced with new one then restore wtg. | Close | 0.08547 | WTG Breakdown Maintenance | G15 | 16061 | 2230.6944 | None
650 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-29 | G25 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 15:15 | 18:32 | 18:35 | 3.2833 | 0.05 | 1900-01-02 08:00 | Reset then restore wtg. | Close | 0.08547 | WTG Breakdown Maintenance | G27 | 12264 | 1703.3333 | None
651 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-29 | G33 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 12:55 | 12:55 | 20:10 | 0 | 1900-01-06 06:00 | 1900-01-06 06:00 | Manual stop for Customer audit point rectification and Gear box damper replacement work. | Close | 0.1859 | WTG Unscheduled Maintenance | G34 | 13853 | 4184.7604 | None
652 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-29 | G36 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 17:01 | 18:15 | 18:18 | 1.2333 | 0.05 | 1899-12-31 06:48 | Reboot then restore wtg. | Close | 0.032906 | WTG Breakdown Maintenance | G37 | 13857 | 740.9646 | None
653 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-30 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 10990 | 10982.3681 | None
654 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-30 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 10990 | 10982.3681 | None
655 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-30 | G02 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop/Customer |  | 16:22 | 16:22 | 19:30 | 0 | 1900-01-02 03:12 | 1900-01-02 03:12 | Manual stop for SEM meter CT/PT connection work | Close | 0.080342 | WTG Unscheduled Maintenance | G04 | 14797 | 1931.8306 | None
656 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-30 | G04 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 13:47 | 14:15 | 14:55 | 0.46667 | 0.66667 | 1899-12-31 03:12 | Checked reslsted circuit found PRV valve failure so replaced with new one then restore wtg. | Close | 0.02906 | WTG Breakdown Maintenance | G03 | 15869 | 749.3694 | None
657 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-30 | G16 | PWEGPL | MSEDCL | 2.564% | 5202 | Stator Contactor Failure | BD |  | 9:45 | 11:31 | 14:01 | 1.7667 | 1900-01-01 12:00 | 1900-01-03 06:24 | Check related circuit found Addon and CCU malfunction so replaced addon and reset CCU then restore wtg. | Close | 0.1094 | WTG Breakdown Maintenance | G17 | 18675 | 3320 | None
658 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-30 | G25 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD |  | 10:50 | 12:24 | 20:50 | 1.5667 | 1900-01-07 10:24 | 1900-01-09 | Check related circuit found Proportion valve cable damage form connecter side so replaced it then take tail after that error occurred heating /coolant thermal relay failure so checked and found Coolant pump and motor failure so replaced with new one then restore wtg. | Close | 0.25641 | WTG Breakdown Maintenance | G27 | 11795 | 4914.5833 | None
659 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-30 | G28 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD |  | 10:15 | 10:56 | 12:05 | 0.68333 | 1899-12-31 03:36 | 1899-12-31 20:00 | Checked releated circuit found proportional valve failure so replaced with new one then restore wtg. | Close | 0.047009 | WTG Breakdown Maintenance | G30 | 11786 | 900.3194 | None
660 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 17189 | 17177.0632 | None
661 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 17189 | 17177.0632 | None
662 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G12 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:10 | 11:10 | 18:16 | 0 | 7.1 | 7.1 | HYPM done then then restore wtg. | Close | 0.18205 | WTG Scheduled Maintenance | G13 | 26906 | 7959.6917 | None
663 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G05 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 12:45 | 13:40 | 13:42 | 0.91667 | 0.033333 | 0.95 | Reset then restore wtg. | Close | 0.024359 | WTG Breakdown Maintenance | G22 | 17167 | 679.5271 | None
664 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G21 | PWEGPL | MSEDCL | 2.564% | 5219 | Coolant Of The Coolant Circuit Failure | BD |  | 12:45 | 13:00 | 14:20 | 0.25 | 1899-12-31 08:00 | 1899-12-31 14:00 | Checked related circuit found ok then restore wtg. | Close | 0.040598 | WTG Breakdown Maintenance | G22 | 17167 | 1132.5451 | None
665 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G22 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 12:45 | 13:10 | 13:12 | 0.41667 | 0.033333 | 0.45 | Reset then restore wtg. | Close | 0.011538 | WTG Breakdown Maintenance | G21 | 17115 | 320.9063 | None
666 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G23 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 12:45 | 13:30 | 13:32 | 0.75 | 0.033333 | 0.78333 | Reset then restore wtg. | Close | 0.020085 | WTG Breakdown Maintenance | G05 | 17106 | 558.3208 | None
667 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G25 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 4:30 | 5:20 | 5:22 | 0.83333 | 0.033333 | 0.86667 | Reset then restore wtg. | Close | 0.022222 | WTG Breakdown Maintenance | G27 | 17190 | 620.75 | None
668 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G25 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 9:47 | 11:44 | 14:40 | 1.95 | 1900-01-01 22:24 | 1900-01-03 21:12 | Checked related circuit found Coolant motor failure so replaced with new one then restore wtg. | Close | 0.12521 | WTG Breakdown Maintenance | G27 | 17190 | 3497.6875 | None
669 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G26 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 8:40 | 9:22 | 13:35 | 0.7 | 1900-01-03 05:12 | 1900-01-03 22:00 | Slip ring clean then restore wtg. | Close | 0.12607 | WTG Breakdown Maintenance | G32 | 17851 | 3656.9757 | None
670 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G26 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 14:25 | 14:35 | 16:20 | 0.16667 | 1899-12-31 18:00 | 1899-12-31 22:00 | Checked related circuit found cab module malfunction so interchange then restore wtg. | Close | 0.049145 | WTG Breakdown Maintenance | G32 | 17851 | 1425.6007 | None
671 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G26 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 17:01 | 17:01 | 19:30 | 0 | 1900-01-01 11:36 | 1900-01-01 11:36 | Checked related circuit found slip ring TB damage so replaced TB then reconnection done then restore wtg. | Close | 0.063675 | WTG Breakdown Maintenance | G32 | 17851 | 1847.0826 | None
672 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G27 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 11:38 | 12:05 | 12:06 | 0.45 | 0.016667 | 0.46667 | Reset then restore wtg. | Close | 0.011966 | WTG Breakdown Maintenance | G25 | 15901 | 309.1861 | None
673 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G28 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 11:38 | 12:30 | 12:31 | 0.86667 | 0.016667 | 0.88333 | Reset then restore wtg. | Close | 0.02265 | WTG Breakdown Maintenance | G30 | 17192 | 632.7611 | None
674 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G35 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 11:38 | 12:45 | 12:46 | 1.1167 | 0.016667 | 1899-12-31 03:12 | Reset then restore wtg. | Close | 0.02906 | WTG Breakdown Maintenance | G36 | 17300 | 816.9444 | None
675 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G35 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 15:10 | 16:01 | 16:02 | 0.85 | 0.016667 | 0.86667 | Reset then restore wtg. | Close | 0.022222 | WTG Breakdown Maintenance | G36 | 17300 | 624.7222 | None
676 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G36 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 11:38 | 13:10 | 13:11 | 1.5333 | 0.016667 | 1899-12-31 13:12 | Reboot then restore wtg. | Close | 0.039744 | WTG Breakdown Maintenance | G37 | 17839 | 1152.1021 | None
677 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | G38 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 11:38 | 13:30 | 13:31 | 1.8667 | 0.016667 | 1899-12-31 21:12 | Reset then restore wtg. | Close | 0.048291 | WTG Breakdown Maintenance | G39 | 17852 | 1400.8861 | None
678 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-01 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 19252 | 19238.6306 | None
679 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-01 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 19252 | 19238.6306 | None
680 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-01 | G09 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:15 | 11:15 | 18:10 | 0 | 6.9167 | 6.9167 | HYPM done then then restore wtg. | Close | 0.17735 | WTG Scheduled Maintenance | G12 | 23119 | 6662.7674 | None
681 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-01 | G22 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 12:33 | 13:01 | 13:02 | 0.46667 | 0.016667 | 0.48333 | Reset then restore wtg. | Close | 0.012393 | WTG Breakdown Maintenance | G21 | 19243 | 387.5326 | None
682 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-01 | G23 | PWEGPL | MSEDCL | 2.564% | 5210 | Failure Of The Contactor's Rotor Power | BD |  | 12:33 | 13:15 | 13:16 | 0.7 | 0.016667 | 0.71667 | Reset then restore wtg. | Close | 0.018376 | WTG Breakdown Maintenance | G05 | 19223 | 574.0201 | None
683 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-01 | G25 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 12:33 | 13:10 | 13:11 | 0.61667 | 0.016667 | 0.63333 | Reset then restore wtg. | Close | 0.016239 | WTG Breakdown Maintenance | G27 | 19245 | 507.8542 | None
684 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 10267 | 10259.8701 | None
685 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 10267 | 10259.8701 | None
686 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | G04 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 10:30 | 11:04 | 13:20 | 0.56667 | 1900-01-01 06:24 | 1900-01-01 20:00 | Checked related circuit found HU hose failure so replaced with new one then restore wtg. | Close | 0.07265 | WTG Breakdown Maintenance | G03 | 10402 | 1228.0139 | None
687 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | G08 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:20 | 11:20 | 17:45 | 0 | 6.4167 | 6.4167 | HYPM done then then restore wtg. | Close | 0.16453 | WTG Scheduled Maintenance | G03 | 10402 | 2781.0903 | None
688 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | G20 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 18:55 | 19:38 | 21:01 | 0.71667 | 1899-12-31 09:12 | 1900-01-01 02:24 | Checked related circuit found ccU coolant cooling motor failure so replaced with new one then restore wtg. then start wtg. | Close | 0.053846 | WTG Breakdown Maintenance | G19 | 12267 | 1073.3625 | None
689 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | G33 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 11:27 | 11:27 | 12:30 | 0 | 1899-12-31 01:12 | 1899-12-31 01:12 | Manual stop for HYPM pending point rectification and radaitor clening work | Close | 0.026923 | WTG Unscheduled Maintenance | G34 | 9109 | 398.5188 | None
690 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | G35 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 13:05 | 13:05 | 14:02 | 0 | 0.95 | 0.95 | Manual stop for HYPM pending piont rectification work | Close | 0.024359 | WTG Unscheduled Maintenance | G36 | 9111 | 360.6438 | None
691 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | G33 | PWEGPL | MSEDCL | 2.564% | 509 | Generator Slipping Ring High Temperature | BD |  | 17:45 | 18:12 | 18:13 | 0.45 | 0.016667 | 0.46667 | Reset then restore wtg. | Close | 0.011966 | WTG Breakdown Maintenance | G34 | 9109 | 177.1194 | None
692 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-03 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 18276 | 18263.3083 | None
693 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-03 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 23:59 | 23:59 | 23.9833 | 0 | 1900-01-22 23:36 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61496 | WTG Force Majeaure | G28 | 18276 | 18263.3083 | None
694 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-03 | G11 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 10:21 | 12:11 | 12:12 | 1.8333 | 0.016667 | 1899-12-31 20:24 | Reset then restore wtg. | Close | 0.047436 | WTG Breakdown Maintenance | G10 | 21268 | 1639.4083 | None
695 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-03 | G11 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 12:12 | 12:12 | 18:30 | 0 | 1900-01-05 07:12 | 1900-01-05 07:12 | HYPM done then then restore wtg. | Close | 0.16154 | WTG Scheduled Maintenance | G10 | 21268 | 5582.85 | None
696 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-03 | G19 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 11:20 | 11:37 | 11:39 | 0.28333 | 0.033333 | 0.31667 | Reboot then restore wtg. | Close | 0.0081197 | WTG Breakdown Maintenance | G18 | 21657 | 285.7521 | None
697 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-03 | G20 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 9:45 | 11:01 | 12:12 | 1.2667 | 1899-12-31 04:24 | 1900-01-01 10:48 | Checked releated circuit found MPCB failure so replaced with new one then restore wtg. | Close | 0.062821 | WTG Breakdown Maintenance | G18 | 21657 | 2210.8187 | None
698 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-03 | G35 | PWEGPL | MSEDCL | 2.564% | 118 | Yaw Motors Error | BD |  | 14:45 | 15:30 | 16:15 | 0.75 | 0.75 | 1899-12-31 12:00 | Checked related circuit found losse connection in yaw sensor so tight it then restore wtg. | Close | 0.038462 | WTG Breakdown Maintenance | G36 | 18037 | 1127.3125 | None
699 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-03 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 15:45 | 16:30 | 16:31 | 0.75 | 0.016667 | 0.76667 | Reset then restore wtg. | Close | 0.019658 | WTG Breakdown Maintenance | G40 | 18076 | 577.4278 | None
700 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 1900-01-23 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 2356 | 2355.9727 | None
701 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 1900-01-23 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 2356 | 2355.9727 | None
702 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | G27 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:15 | 11:15 | 12:10 | 0 | 0.91667 | 0.91667 | Manual stop for HYPM pending piont rectification work | Close | 0.023504 | WTG Unscheduled Maintenance | G25 | 2365 | 90.3299 | None
703 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | G34 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:18 | 11:18 | 12:10 | 0 | 0.86667 | 0.86667 | Manual stop for HYPM pending piont rectification work | Close | 0.022222 | WTG Unscheduled Maintenance | G34 | 3054 | 110.2833 | None
704 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | G21 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 20:55 | 21:15 | 21:16 | 0.33333 | 0.016667 | 0.35 | Reset then restore wtg. | Close | 0.0089744 | WTG Breakdown Maintenance | G22 | 2356 | 34.3583 | None
705 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | G23 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 20:55 | 21:30 | 21:31 | 0.58333 | 0.016667 | 0.6 | Reset then restore wtg. | Close | 0.015385 | WTG Breakdown Maintenance | G22 | 2356 | 58.9 | None
706 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | G27 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 20:55 | 21:45 | 21:46 | 0.83333 | 0.016667 | 0.85 | Reset then restore wtg. | Close | 0.021795 | WTG Breakdown Maintenance | G25 | 2365 | 83.7604 | None
707 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | G25 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 20:55 | 21:50 | 21:51 | 0.91667 | 0.016667 | 0.93333 | Reset then restore wtg. | Close | 0.023932 | WTG Breakdown Maintenance | G27 | 2362 | 91.8556 | None
708 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | G28 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 20:55 | 22:00 | 22:01 | 1.0833 | 0.016667 | 1899-12-31 02:24 | Reset then restore wtg. | Close | 0.028205 | WTG Breakdown Maintenance | G30 | 2372 | 108.7167 | None
709 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 6856 | 6855.9206 | None
710 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 6856 | 6855.9206 | None
711 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | G04 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 11:01 | 11:38 | 12:07 | 0.61667 | 0.48333 | 1.1 | Slip ring clean then restore wtg. | Close | 0.028205 | WTG Breakdown Maintenance | G03 | 9015 | 413.1875 | None
712 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | G06 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:27 | 11:27 | 18:20 | 0 | 6.8833 | 6.8833 | HYPM done then then restore wtg. | Close | 0.1765 | WTG Scheduled Maintenance | G03 | 9015 | 2585.5521 | None
713 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | G11 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD |  | 16:58 | 17:29 | 17:30 | 0.51667 | 0.016667 | 0.53333 | Reset then restore wtg. | Close | 0.013675 | WTG Breakdown Maintenance | G10 | 9019 | 200.4222 | None
714 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | G14 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD |  | 11:15 | 11:32 | 11:33 | 0.28333 | 0.016667 | 0.3 | Reset then restore wtg. | Close | 0.0076923 | WTG Breakdown Maintenance | G15 | 8021 | 100.2625 | None
715 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | G19 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 15:30 | 15:50 | 16:20 | 0.33333 | 0.5 | 0.83333 | Slip ring clean then restore wtg. | Close | 0.021368 | WTG Breakdown Maintenance | G18 | 8019 | 278.4375 | None
716 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | G36 | PWEGPL | MSEDCL | 2.564% | CE100008 | General Work Stoppage | Manual stop |  | 12:15 | 12:15 | 13:45 | 0 | 1899-12-31 12:00 | 1.5 | Manual stop for HYPM pending piont rectification work | Close | 0.038462 | WTG Unscheduled Maintenance | G35 | 6232 | 389.5 | None
717 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | G37 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 11:00 | 11:27 | 12:05 | 0.45 | 0.63333 | 1.0833 | Slip ring clean then restore wtg. | Close | 0.027778 | WTG Breakdown Maintenance | G36 | 5589 | 252.2813 | None
718 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-06 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 9362 | 9361.8916 | None
719 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-06 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 9362 | 9361.8916 | None
720 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-06 | G03 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:36 | 11:36 | 18:12 | 0 | 6.6 | 6.6 | HYPM done then then restore wtg. | Close | 0.16923 | WTG Scheduled Maintenance | G04 | 14606 | 4016.65 | None
721 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-06 | G14 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 10:50 | 10:50 | 11:45 | 0 | 0.91667 | 0.91667 | Manual stop for repeated error found valve malfunction so replaced with new one then restore wtg. | Close | 0.023504 | WTG Breakdown Maintenance | G15 | 12845 | 490.6076 | None
722 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-06 | G37 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 17:30 | 18:01 | 21:29 | 0.51667 | 1900-01-02 11:12 | 3.9833 | Checked related circuit found oil leakage from Blade C Accumulator so replaced with new one then N2 refilling done then restore wtg. | Close | 0.10214 | WTG Unscheduled Maintenance | G36 | 7780 | 1291.2639 | None
723 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 12590 | 12589.8543 | None
724 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 12590 | 12589.8543 | None
725 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | G04 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:10 | 11:10 | 18:05 | 0 | 6.9167 | 6.9167 | HYPM done then then restore wtg. | Close | 0.17735 | WTG Scheduled Maintenance | G03 | 19809 | 5708.8437 | None
726 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | G28 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:09 | 11:09 | 13:35 | 0 | 1900-01-01 10:24 | 2.4333 | Manual stop for HYPM pending piont rectification work | Close | 0.062393 | WTG Unscheduled Maintenance | G30 | 12542 | 1271.6194 | None
727 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | G30 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 14:24 | 14:24 | 16:20 | 0 | 1899-12-31 22:24 | 1.9333 | Manual stop for HYPM pending piont rectification work | Close | 0.049573 | WTG Unscheduled Maintenance | G28 | 12590 | 1014.1944 | None
728 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 12125 | 12124.8597 | None
729 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 12125 | 12124.8597 | None
730 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | G21 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 21:05 | 21:18 | 21:19 | 0.21667 | 0.016667 | 0.23333 | Reset then restore wtg. | Close | 0.0059829 | WTG Breakdown Maintenance | G22 | 12015 | 116.8125 | None
731 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | G22 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 21:05 | 21:15 | 21:16 | 0.16667 | 0.016667 | 0.18333 | Reset then restore wtg. | Close | 0.0047009 | WTG Breakdown Maintenance | G23 | 12001 | 91.6743 | None
732 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | G25 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 21:05 | 21:35 | 21:36 | 0.5 | 0.016667 | 0.51667 | Reset then restore wtg. | Close | 0.013248 | WTG Breakdown Maintenance | G27 | 12121 | 260.9382 | None
733 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | G28 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 21:05 | 21:48 | 21:49 | 0.71667 | 0.016667 | 0.73333 | Reset then restore wtg. | Close | 0.018803 | WTG Breakdown Maintenance | G30 | 12132 | 370.7 | None
734 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | G30 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 21:05 | 21:55 | 21:56 | 0.83333 | 0.016667 | 0.85 | Reset then restore wtg. | Close | 0.021795 | WTG Breakdown Maintenance | G28 | 12125 | 429.4271 | None
735 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 23434 | 23433.7288 | None
736 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 23434 | 23433.7288 | None
737 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | G04 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 17:45 | 18:10 | 18:12 | 0.41667 | 0.033333 | 0.45 | Reboot then restore wtg. | Close | 0.011538 | WTG Breakdown Maintenance | G03 | 24743 | 463.9312 | None
738 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 11:30 | 11:55 | 13:10 | 0.41667 | 1899-12-31 06:00 | 1.6667 | Checked related coircuit found HU main accumulator pressure low so refilled N2 then restore wtg. | Close | 0.042735 | WTG Breakdown Maintenance | G13 | 21856 | 1517.7778 | None
739 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | G14 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 16:05 | 16:30 | 16:32 | 0.41667 | 0.033333 | 0.45 | Reboot then restore wtg. | Close | 0.011538 | WTG Breakdown Maintenance | G13 | 21856 | 409.8 | None
740 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | G20 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 10:45 | 11:11 | 12:05 | 0.43333 | 0.9 | 1.3333 | Slip ring clean then restore wtg. | Close | 0.034188 | WTG Breakdown Maintenance | G19 | 21878 | 1215.4444 | None
741 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | G30 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 17:00 | 17:25 | 18:20 | 0.41667 | 0.91667 | 1.3333 | Inspection done then restore wtg. | Close | 0.034188 | WTG Breakdown Maintenance | G28 | 23434 | 1301.8889 | None
742 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | G39 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 10:42 | 11:24 | 12:30 | 0.7 | 1899-12-31 02:24 | 1.8 | Checked related circuit found KR003 relay in loose condition so tight it then restore wtg | Close | 0.046154 | WTG Breakdown Maintenance | G40 | 20145 | 1510.875 | None
743 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | G27 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 14:05 | 14:05 | 17:15 | 0 | 1900-01-02 04:00 | 3.1667 | Manual stop for Blade bush gap inspection work | Close | 0.081197 | WTG Force Majeaure | G25 | 23421 | 3090.2708 | None
744 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 12689 | 12688.8531 | None
745 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 12689 | 12688.8531 | None
746 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | G02 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 11:55 | 11:55 | 18:44 | 0 | 6.8167 | 6.8167 | HYPM done then then restore wtg. | Close | 0.17479 | WTG Scheduled Maintenance | G04 | 13335 | 3787.5104 | None
747 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | G14 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 15:30 | 16:05 | 19:50 | 0.58333 | 1900-01-02 18:00 | 4.3333 | Checked related circuit found PRV -8 Valve failure so replaced with new one then restore wtg. | Close | 0.11111 | WTG Breakdown Maintenance | G13 | 22342 | 4033.9722 | None
748 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | G15 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 16:15 | 16:15 | 17:50 | 0 | 1899-12-31 14:00 | 1.5833 | Manual stop for yaw abnormal sound rectification work | Close | 0.040598 | WTG Unscheduled Maintenance | G16 | 21522 | 1419.8542 | None
749 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | G16 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:28 | 11:28 | 12:50 | 0 | 1899-12-31 08:48 | 1.3667 | Manual stop for yaw abnormal sound rectification work | Close | 0.035043 | WTG Unscheduled Maintenance | G17 | 22321 | 1271.0569 | None
750 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | G20 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 11:50 | 12:20 | 14:23 | 0.5 | 1900-01-01 01:12 | 2.55 | checked related circuit found loose connection so tight it then apply sealant then restore wtg. | Close | 0.065385 | WTG Breakdown Maintenance | G19 | 22345 | 2374.1562 | None
751 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | G23 | PWEGPL | MSEDCL | 2.564% | 502 | Generator NDE Bearing High Temperature Alarm | BD |  | 9:35 | 11:48 | 14:10 | 2.2167 | 1900-01-01 08:48 | 4.5833 | Replaced lift guide clamp then checked related circuit found generator carbon brush wear out and spring damage so replaced with new one then restore wtg. | Close | 0.11752 | WTG Breakdown Maintenance | G05 | 12629 | 2411.7882 | None
752 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 14454 | 14453.8327 | None
753 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 14454 | 14453.8327 | None
754 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | G02 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 16:45 | 17:27 | 17:28 | 0.7 | 0.016667 | 0.71667 | Reset then restore wtg. | Close | 0.018376 | WTG Breakdown Maintenance | G03 | 17919 | 535.0813 | None
755 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | G03 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 16:45 | 17:07 | 17:08 | 0.36667 | 0.016667 | 0.38333 | Reset then restore wtg. | Close | 0.0098291 | WTG Breakdown Maintenance | G04 | 17913 | 286.1104 | None
756 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | G04 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 16:45 | 17:14 | 17:15 | 0.48333 | 0.016667 | 0.5 | Reset then restore wtg. | Close | 0.012821 | WTG Breakdown Maintenance | G03 | 17919 | 373.3125 | None
757 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | G06 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 16:45 | 17:01 | 17:02 | 0.26667 | 0.016667 | 0.28333 | Reset then restore wtg. | Close | 0.007265 | WTG Breakdown Maintenance | G03 | 17919 | 211.5438 | None
758 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | G07 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 10:44 | 10:44 | 18:45 | 0 | 8.0167 | 8.0167 | HYPM done then then restore wtg. | Close | 0.20556 | WTG Scheduled Maintenance | G01 | 17911 | 5982.7715 | None
759 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | G10 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 16:45 | 18:10 | 18:11 | 1.4167 | 0.016667 | 1.4333 | Reset then restore wtg. | Close | 0.036752 | WTG Breakdown Maintenance | G11 | 17938 | 1071.2972 | None
760 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | G16 | PWEGPL | MSEDCL | 2.564% | 116 | Orienting and High Yaw Brake Pressure | BD |  | 16:30 | 17:15 | 17:16 | 0.75 | 0.016667 | 0.76667 | Reset then restore wtg. | Close | 0.019658 | WTG Breakdown Maintenance | G17 | 9539 | 304.7181 | None
761 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | G32 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 17:10 | 17:59 | 18:02 | 0.81667 | 0.05 | 0.86667 | Reboot then restore wtg. | Close | 0.022222 | WTG Breakdown Maintenance | G26 | 12111 | 437.3417 | None
762 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-12 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 9862 | 9861.8859 | None
763 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-12 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 9862 | 9861.8859 | None
764 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-12 | G01 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 10:59 | 10:59 | 18:20 | 0 | 7.35 | 7.35 | HYPM done then then restore wtg. | Close | 0.18846 | WTG Scheduled Maintenance | G07 | 14931 | 4572.6187 | None
765 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-12 | G40 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:45 | 11:45 | 12:32 | 0 | 0.78333 | 0.78333 | Manual stop for HYPM pending point rectification work | Close | 0.020085 | WTG Unscheduled Maintenance | G39 | 8964 | 292.575 | None
766 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-12 | G12 | PWEGPL | MSEDCL | 2.564% | 550 | Generator Fans Thermal Relay Triggered Too Long | BD |  | 22:35 | 23:22 | 23:55 | 0.78333 | 0.55 | 1.3333 | Checked related circuit found cable connection loose so tight it then restore wtg | Close | 0.034188 | WTG Breakdown Maintenance | G13 | 12738 | 707.6667 | None
767 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-13 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 2121 | 2120.9755 | None
768 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-13 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 2121 | 2120.9755 | None
769 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-13 | G10 | PWEGPL | MSEDCL | 2.564% | CE100010 | Manual Stop - Preventive Maintenance Activity | PM |  | 10:52 | 10:52 | 18:02 | 0 | 7.1667 | 7.1667 | HYPM done then then restore wtg. | Close | 0.18376 | WTG Scheduled Maintenance | G11 | 4167 | 1244.3125 | None
770 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-13 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 12:10 | 13:15 | 24:00 | 1.0833 | 1900-01-09 18:00 | 11.8331 | Checked related circuit checked SF-6 breaker & Transformer (work in progress) | Open | 0.30341 | WTG Breakdown Maintenance | G16 | 3618 | 1783.8331 | None
771 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-13 | G27 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 16:45 | 17:10 | 17:11 | 0.41667 | 0.016667 | 0.43333 | Reset then restore wtg. | Close | 0.011111 | WTG Breakdown Maintenance | G25 | 2118 | 38.2417 | None
772 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-13 | G28 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 16:45 | 17:20 | 17:21 | 0.58333 | 0.016667 | 0.6 | Reset then restore wtg. | Close | 0.015385 | WTG Breakdown Maintenance | G30 | 2123 | 53.075 | None
773 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-13 | G30 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 16:45 | 17:30 | 17:31 | 0.75 | 0.016667 | 0.76667 | Reset then restore wtg. | Close | 0.019658 | WTG Breakdown Maintenance | G28 | 2121 | 67.7542 | None
774 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-13 | G38 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 12:49 | 12:49 | 13:58 | 0 | 1899-12-31 03:36 | 1.15 | Manual stop for HYPM pending piont rectification work | Close | 0.029487 | WTG Unscheduled Maintenance | G39 | 2762 | 132.3458 | None
775 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-14 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 2153 | 2152.9751 | None
776 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-14 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 2153 | 2152.9751 | None
777 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-14 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 1943 | 1942.9775 | Material arrangement in progress
778 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-14 | G16 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 10:56 | 11:35 | 12:06 | 0.65 | 0.51667 | 1.1667 | Slipring cleaned Then Start WTG. | Close | 0.029915 | WTG Breakdown Maintenance | G18 | 1943 | 94.4514 | None
779 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-14 | G39 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 12:06 | 14:30 | 16:01 | 2.4 | 1899-12-31 12:24 | 3.9167 | Check related ckt found connection loose then tighted properly & Reatore | Close | 0.10043 | WTG Breakdown Maintenance | G40 | 2126 | 346.9514 | None
780 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-14 | G19 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 14:02 | 14:02 | 16:30 | 0 | 1900-01-01 11:12 | 2.4667 | Manual stop for Trf Temperature high trouble shooting work | Close | 0.063248 | WTG Unscheduled Maintenance | G18 | 1943 | 199.6972 | None
781 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-14 | G04 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 13:10 | 13:49 | 13:58 | 0.65 | 0.15 | 0.8 | Reset then restore wtg. | Close | 0.020513 | WTG Breakdown Maintenance | G03 | 2120 | 70.6667 | None
782 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-15 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 7948 | 7947.908 | None
783 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-15 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G28 | 7948 | 7947.908 | None
784 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-15 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 7856 | 7855.9091 | Material arrangement in progress
785 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-15 | G03 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 10:23 | 11:35 | 13:15 | 1.2 | 1899-12-31 16:00 | 2.8667 | As per error check & found B blade pressure switch cable disconnected so reconnect it then restore WTG. | Close | 0.073504 | WTG Breakdown Maintenance | G04 | 8021 | 958.0639 | None
786 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-15 | G11 | PWEGPL | MSEDCL | 2.564% | 5228 | Preload Failure | BD |  | 14:37 | 16:00 | 16:39 | 1.3833 | 0.65 | 2.0333 | Checked related ckt found kroo2 relay found malfunctional so cleaned and interchanged relay then restore | Close | 0.052137 | WTG Breakdown Maintenance | G10 | 8099 | 686.1653 | None
787 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-15 | G20 | PWEGPL | MSEDCL | 2.564% | 905 | Controlled Emergency Series Battery Failure | BD |  | 10:11 | 10:49 | 13:22 | 0.63333 | 1900-01-01 13:12 | 3.1833 | Check related ckt found brake power supply battery failure so replace it & also transformer inspected then restore WTG. | Close | 0.081624 | WTG Breakdown Maintenance | G19 | 7965 | 1056.4688 | None
788 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-15 | G05 | PWEGPL | MSEDCL | 2.564% | 5201 | Magnetothermic Trigger Of The Stator Protection | BD |  | 10:09 | 10:32 | 10:35 | 0.38333 | 0.05 | 0.43333 | Reset then restore wtg. | Close | 0.011111 | WTG Breakdown Maintenance | G22 | 7878 | 142.2417 | None
789 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-15 | G20 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 0:35 | 1:08 | 1:24 | 0.55 | 0.26667 | 0.81667 | chack related circuit, found mcb triped. So, on it and start the wtg | Close | 0.02094 | WTG Breakdown Maintenance | G19 | 7965 | 271.0313 | None
790 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-16 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G30 | 20213 | 20212.7661 | None
791 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-16 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G30 | 20213 | 20212.7661 | None
792 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-16 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G16 | 21923 | 21922.7463 | Material arrangement in progress
793 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-16 | G03 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 3:00 | 3:12 | 3:40 | 0.2 | 0.46667 | 0.66667 | Check related ckt found MCB tripped ,on it then restore WTG. | Close | 0.017094 | WTG Breakdown Maintenance | G06 | 21400 | 594.4444 | None
794 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-16 | G28 | PWEGPL | MSEDCL | 2.564% | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit | BD |  | 11:14 | 11:39 | 12:51 | 0.41667 | 1899-12-31 04:48 | 1.6167 | Found radiator dust then CCU Cooling radiatir cleaned & coolant sensor cleaned then restore. | Close | 0.041453 | WTG Breakdown Maintenance | G30 | 20213 | 1361.5701 | None
795 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-16 | G04 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 10:45 | 11:12 | 12:05 | 0.45 | 0.88333 | 1.3333 | Slipring cleaned Then Start WTG. | Close | 0.034188 | WTG Breakdown Maintenance | G06 | 21400 | 1188.8889 | None
796 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-16 | G21 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 6:38 | 6:58 | 6:59 | 0.33333 | 0.016667 | 0.35 | Reset then restore wtg. | Close | 0.0089744 | WTG Breakdown Maintenance | G22 | 22189 | 323.5896 | None
797 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-16 | G23 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 6:38 | 7:05 | 7:06 | 0.45 | 0.016667 | 0.46667 | Reset then restore wtg. | Close | 0.011966 | WTG Breakdown Maintenance | G22 | 22189 | 431.4528 | None
798 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G30 | 24110 | 24109.7209 | None
799 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G30 | 24110 | 24109.7209 | None
800 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 24122 | 24121.7208 | Material arrangement in progress
801 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | G15 | PWEGPL | MSEDCL | 2.564% | 502 | Generator NDE Bearing High Temperature Alarm | BD |  | 13:44 | 13:57 | 14:55 | 0.21667 | 0.96667 | 1.1833 | Check related ckt, sensor checked & grease applied & adjusted air exit cover then restored wtg. | Close | 0.030342 | WTG Breakdown Maintenance | G14 | 25011 | 1233.1813 | None
802 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | G28 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 10:40 | 11:20 | 23:59 | 0.66667 | 1900-01-11 15:36 | 13.3167 | Check pressure switch connection, KR919 Relay,TA 031 Power supply .(work in progress) | Open | 0.34145 | WTG Breakdown Maintenance | G30 | 24110 | 13377.7014 | None
803 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | G33 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 11:12 | 11:12 | 14:22 | 0 | 1900-01-02 04:00 | 3.1667 | Manual stop for Blade bush gap inspection work | Close | 0.081197 | WTG Force Majeure | G34 | 24521 | 3235.4097 | None
804 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | G15 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 14:59 | 14:59 | 16:40 | 0 | 1899-12-31 16:24 | 1.6833 | Manual stop for Blade bush gap inspection work | Close | 0.043162 | WTG Force Majeure | G14 | 25011 | 1754.2437 | None
805 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | G03 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD |  | 11:23 | 11:47 | 11:51 | 0.4 | 0.066667 | 0.46667 | Reset then restore wtg. | Close | 0.011966 | WTG Breakdown Maintenance | G04 | 24900 | 484.1667 | None
806 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 12:25 | 12:37 | 12:39 | 0.2 | 0.033333 | 0.23333 | Reset then restore wtg. | Close | 0.0059829 | WTG Breakdown Maintenance | G13 | 26543 | 258.0569 | None
807 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G30 | 27943 | 27942.6766 | None
808 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G30 | 27943 | 27942.6766 | None
809 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 28901 | 28900.6655 | Material arrangement in progress
810 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | G39 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 14:22 | 15:07 | 16:58 | 0.75 | 1899-12-31 20:24 | 2.6 | Check related ckt found WS220B cable loose conection so proper tightened then restore WTG | Close | 0.066667 | WTG Breakdown Maintenance | G40 | 28381 | 3074.6083 | None
811 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | G07 | PWEGPL | MSEDCL | 2.564% | 403 | High Gearbox Oil Temperature | BD |  | 16:59 | 17:25 | 19:28 | 0.43333 | 1900-01-01 01:12 | 2.4833 | Check related ckt found fg480 mpcb failure then replaced it then found hose leakage then hose replaced then restore WTG. | Close | 0.063675 | WTG Breakdown Maintenance | G01 | 28803 | 2980.3104 | None
812 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | G28 | PWEGPL | MSEDCL | 2.564% | 404 | High Gearbox Bearing Temperature | BD |  | 17:31 | 17:48 | 18:40 | 0.28333 | 0.86667 | 1.15 | Check temperature sensor & gb oil level & cooling motor found everything ok then restore wtg. | Close | 0.029487 | WTG Breakdown Maintenance | G30 | 27943 | 1338.9354 | None
813 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | G35 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 12:49 | 12:57 | 12:59 | 0.13333 | 0.033333 | 0.16667 | Reset then restore wtg. | Close | 0.0042735 | WTG Breakdown Maintenance | G36 | 28732 | 199.5278 | None
814 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | G37 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 12:49 | 13:07 | 13:10 | 0.3 | 0.05 | 0.35 | Reset then restore wtg. | Close | 0.0089744 | WTG Breakdown Maintenance | G36 | 28732 | 419.0083 | None
815 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | G38 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 12:49 | 13:17 | 13:18 | 0.46667 | 0.016667 | 0.48333 | Reset then restore wtg. | Close | 0.012393 | WTG Breakdown Maintenance | G40 | 28381 | 571.5618 | None
816 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | G26 | PWEGPL | MSEDCL | 2.564% | 2100 | PLC Voltage Recovery | BD |  | 12:49 | 13:25 | 13:26 | 0.6 | 0.016667 | 0.61667 | Reset then restore wtg. | Close | 0.015812 | WTG Breakdown Maintenance | G40 | 28381 | 729.234 | None
817 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | G28 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 0:00 | 0:00 | 1:40 | 0 | 1899-12-31 16:00 | 1.6667 | Check pressure switch connection, KR919 Relay,TA 031 Power supply output cable was short circuit,in hub pressure switch.so, corrected the circuit and restore the wtg | Close | 0.042735 | WTG Breakdown Maintenance | G30 | 27943 | 1940.4861 | None
818 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G30 | 24823 | 24822.7127 | None
819 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G30 | 24823 | 24822.7127 | None
820 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G19 | 25458 | 25457.7053 | None
821 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | G28 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 1:03 | 1:03 | 3:36 | 0 | 1900-01-01 13:12 | 2.55 | Mnaual stop for hub leak sensor warning attending work | Close | 0.065385 | WTG Unscheduled Maintenance | G30 | 24823 | 2637.4437 | None
822 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | G32 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 12:30 | 12:30 | 13:15 | 0 | 0.75 | 0.75 | Manual stop for Upper rediator high temp warning rectification work | Close | 0.019231 | WTG Unscheduled Maintenance | G26 | 24273 | 758.5312 | None
823 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | G04 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 11:22 | 12:14 | 13:00 | 0.86667 | 0.76667 | 1.6333 | Slipring cleaned Then Start WTG. | Close | 0.04188 | WTG Breakdown Maintenance | G02 | 25563 | 1739.7042 | None
824 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | G03 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD |  | 13:25 | 13:53 | 14:56 | 0.46667 | 1899-12-31 01:12 | 1.5167 | check ckt found C blade proportional Valve failure Replaced it then restore WTG. | Close | 0.038889 | WTG Breakdown Maintenance | G06 | 25823 | 1631.8701 | None
825 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | G20 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 14:02 | 16:34 | 17:23 | 2.5333 | 0.81667 | 3.35 | Check ckt found communication cable connection loosen so fixed it then restore WTG. | Close | 0.085897 | WTG Breakdown Maintenance | G19 | 25458 | 3553.5125 | None
826 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 13:10 | 13:32 | 13:34 | 0.36667 | 0.033333 | 0.4 | Reset then restore wtg. | Close | 0.010256 | WTG Breakdown Maintenance | G09 | 25623 | 427.05 | None
827 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Breakdown Maintenance | G30 | 27810 | 27809.6781 | None
828 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Breakdown Maintenance | G30 | 27810 | 27809.6781 | None
829 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G16 | 27812 | 27811.6781 | None
830 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | G11 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 9:54 | 10:51 | 12:27 | 0.95 | 1899-12-31 14:24 | 2.55 | Slipring cleaned & Post PM inspection done Then Start WTG. | Close | 0.065385 | WTG Breakdown Maintenance | G10 | 27864 | 2960.55 | None
831 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | G21 | PWEGPL | MSEDCL | 2.564% | 403 | High Gearbox Oil Temperature | BD |  | 12:55 | 13:31 | 14:26 | 0.6 | 0.91667 | 1.5167 | Check related ckt found fg480 mpcb failure then replaced it then restore WTG. | Close | 0.038889 | WTG Breakdown Maintenance | G22 | 27345 | 1728.0521 | None
832 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-21 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G30 | 25110 | 25109.7094 | None
833 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-21 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G30 | 25110 | 25109.7094 | None
834 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-21 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G16 | 26511 | 26510.6932 | None
835 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-21 | G23 | PWEGPL | MSEDCL | 2.564% | 222 | Very Low Pressure On Hydraulic Unit | BD |  | 17:45 | 18:06 | 18:50 | 0.35 | 0.73333 | 1.0833 | Adjusted PRV8 or RV10 Valve then restore WTG. | Close | 0.027778 | WTG Breakdown Maintenance | G22 | 25573 | 1154.3368 | None
836 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-21 | G10 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 12:20 | 12:20 | 13:30 | 0 | 1899-12-31 04:00 | 1.1667 | Manually stop for generator winding temperature high | Close | 0.029915 | WTG Unscheduled Maintenance | G08 | 25213 | 1225.6319 | None
837 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-21 | G33 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD |  | 13:45 | 14:14 | 16:16 | 0.48333 | 1900-01-01 00:48 | 2.5167 | Check related ckt found A blade propotional valve failure then replaced & start WTG. | Close | 0.06453 | WTG Breakdown Maintenance | G34 | 24836 | 2604.3306 | None
838 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-21 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 11:42 | 11:42 | 19:16 | 0 | 1900-01-06 13:36 | 7.5667 | Resolved warning rectification work | Close | 0.19402 | WTG Unscheduled Maintenance | G13 | 24356 | 7678.9056 | None
839 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-21 | G11 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 12:34 | 12:34 | 19:02 | 0 | 1900-01-05 11:12 | 6.4667 | Manually stop for HYPM audit pending point closing work & Nose cone DM Work | Close | 0.16581 | WTG Unscheduled Maintenance | G13 | 24356 | 6562.5889 | None
840 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G30 | 24532 | 24531.7161 | None
841 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G30 | 24532 | 24531.7161 | None
842 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G16 | 25412 | 25411.7059 | None
843 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 10:58 | 11:25 | 13:38 | 0.45 | 1900-01-01 05:12 | 2.6667 | Replaced HU main Accumulator,then start the WTG | Close | 0.068376 | WTG Breakdown Maintenance | G13 | 24623 | 2735.8889 | None
844 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | G20 | PWEGPL | MSEDCL | 2.564% | 102 | CW Feedback Failure | BD |  | 17:27 | 17:59 | 18:35 | 0.53333 | 0.6 | 1.1333 | Chacked and found yaw contactor was stuck,after removing stuck started the WTG | Close | 0.02906 | WTG Breakdown Maintenance | G19 | 25612 | 1209.4556 | None
845 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | G02 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 11:03 | 11:34 | 12:49 | 0.51667 | 1899-12-31 06:00 | 1.7667 | Slipring cleaned Then Start WTG. | Close | 0.045299 | WTG Breakdown Maintenance | G04 | 24987 | 1839.3208 | None
846 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | G38 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 10:35 | 10:58 | 11:01 | 0.38333 | 0.05 | 0.43333 | Reset then restore wtg. | Close | 0.011111 | WTG Breakdown Maintenance | G39 | 25472 | 459.9111 | None
847 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 1:22 | 1:53 | 3:40 | 0.51667 | 1899-12-31 18:48 | 2.3 | Interchange the RV-8-10 valve,then started the WTG | Close | 0.058974 | WTG Breakdown Maintenance | G13 | 24623 | 2359.7042 | None
848 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | G31 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G30 | 29732 | 29731.6559 | None
849 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeaure | G30 | 29732 | 29731.6559 | None
850 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | G17 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G16 | 30372 | 30371.6485 | None
851 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | G20 | PWEGPL | MSEDCL | 2.564% | 102 | CW Feedback Failure | FM |  | 12:08 | 14:20 | 14:20 | 2.2 | 0 | 2.2 | ROW issue | Close | 0.05641 | WTG Force Majeure | G19 | 29932 | 2743.7667 | None
852 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | G14 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 14:30 | 14:37 | 14:40 | 0.11667 | 0.05 | 0.16667 | Reset then restore wtg. | Close | 0.0042735 | WTG Breakdown Maintenance | G13 | 28151 | 195.4931 | None
853 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | FM |  | 12:08 | 14:20 | 14:20 | 2.2 | 0 | 2.2 | ROW issue | Close | 0.05641 | WTG Force Majeure | G13 | 28151 | 2580.5083 | None
854 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | G20 | PWEGPL | MSEDCL | 2.564% | 102 | CW Feedback Failure | BD |  | 17:50 | 18:03 | 19:01 | 0.21667 | 0.96667 | 1.1833 | Replaced yaw contactor,then started the WTG | Close | 0.030342 | WTG Breakdown Maintenance | G19 | 29932 | 1475.8139 | None
855 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | G05 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 17:58 | 18:25 | 18:30 | 0.45 | 0.083333 | 0.53333 | Reset then restore wtg. | Close | 0.013675 | WTG Breakdown Maintenance | G22 | 30231 | 671.8 | None
856 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | G20 | PWEGPL | MSEDCL | 2.564% | 102 | CW Feedback Failure | BD |  | 14:20 | 14:45 | 14:50 | 0.41667 | 0.083333 | 0.5 | Reset then restore wtg. | Close | 0.012821 | WTG Breakdown Maintenance | G19 | 29932 | 623.5833 | None
857 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 14:20 | 14:43 | 14:45 | 0.38333 | 0.033333 | 0.41667 | Reset then restore wtg. | Close | 0.010684 | WTG Breakdown Maintenance | G13 | 28151 | 488.7326 | None
858 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 29408 | 29407.6596 | None
859 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 29408 | 29407.6596 | None
860 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | G17 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G16 | 29912 | 29911.6538 | None
861 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | G09 | PWEGPL | MSEDCL | 2.564% | 804 | Difference Between 2 Blades Too High | BD |  | 12:07 | 12:39 | 15:25 | 0.53333 | 1900-01-01 18:24 | 3.3 | Checked and found WS243C cable was faulty so,replaced it. | Close | 0.084615 | WTG Breakdown Maintenance | G13 | 29109 | 4002.4875 | None
862 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 14:41 | 15:05 | 15:45 | 0.4 | 0.66667 | 1.0667 | RV-8-10 valve setting done,then started the WTG | Close | 0.02735 | WTG Breakdown Maintenance | G13 | 29109 | 1293.7333 | None
863 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 18453 | 18452.7864 | None
864 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 18453 | 18452.7864 | None
865 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | G17 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 18881 | 18880.7815 | None
866 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | G16 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 13:50 | 13:50 | 15:04 | 0 | 1899-12-31 05:36 | 1.2333 | Replaced 2nos. Trafo fan(R-HV,B-LV) | Close | 0.031624 | WTG Unscheduled Maintenance | G18 | 18881 | 970.2736 | None
867 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | G38 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 15:00 | 15:46 | 16:52 | 0.76667 | 1899-12-31 02:24 | 1.8667 | Slipring cleaned Then Start WTG. | Close | 0.047863 | WTG Breakdown Maintenance | G39 | 18432 | 1433.6 | None
868 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | G02 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 17:25 | 17:56 | 17:59 | 0.51667 | 0.05 | 0.56667 | Reset then restore wtg. | Close | 0.01453 | WTG Breakdown Maintenance | G04 | 17945 | 423.7014 | None
869 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 10021 | 10020.884 | None
870 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 10021 | 10020.884 | None
871 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | G17 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 10123 | 10122.8828 | None
872 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | G13 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 11:03 | 11:03 | 15:15 | 0 | 1900-01-03 04:48 | 4.2 | Replaced 4nos. Trafo fan(B-HV,R,Y&B-LV) | Close | 0.10769 | WTG Unscheduled Maintenance | G12 | 10231 | 1790.425 | None
873 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | G02 | PWEGPL | MSEDCL | 2.564% | 700 | PLC-Converter Communication Error | BD |  | 14:03 | 14:17 | 17:15 | 0.23333 | 1900-01-01 23:12 | 3.2 | chacked and found slipring connection cable loose, so,fixed it. Then replaced a 80w panel fan | Close | 0.082051 | WTG Breakdown Maintenance | G04 | 10037 | 1338.2667 | None
874 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | G03 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | Manual stop |  | 12:58 | 12:58 | 13:45 | 0 | 0.78333 | 0.78333 | 3 nos.L A Hammer replaced,sealant applied | Close | 0.020085 | WTG Unscheduled Maintenance | G04 | 10037 | 327.5965 | None
875 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | G37 | PWEGPL | MSEDCL | 2.564% | 402 | Gearbox Oil Level Low | BD |  | 16:58 | 17:22 | 19:00 | 0.4 | 1899-12-31 15:12 | 2.0333 | Chacked and found gearbox hose leakage so,replaced it. Top up 90 lit GB Oil | Close | 0.052137 | WTG Breakdown Maintenance | G36 | 10493 | 888.9903 | None
876 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | G28 | PWEGPL | MSEDCL | 2.564% | 907 | Emergency Series HUB Trigger | BD |  | 16:47 | 17:13 | 20:37 | 0.43333 | 1900-01-02 09:36 | 3.8333 | chack related circuit found cable loose,after fixing cable start the wtg | Close | 0.098291 | WTG Breakdown Maintenance | G30 | 10021 | 1600.5764 | None
877 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | G03 | PWEGPL | MSEDCL | 2.564% | CE100014 | Manual Stop - Audit | Manual stop/Customer |  | 13:45 | 13:45 | 14:30 | 0 | 0.75 | 0.75 | Post PM audit done | Close | 0.019231 | WTG Unscheduled Maintenance | G04 | 10037 | 313.6562 | None
878 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-27 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 16041 | 16040.8143 | None
879 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-27 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 16041 | 16040.8143 | None
880 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-27 | G17 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 16043 | 16042.8143 | None
881 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-27 | G01 | PWEGPL | MSEDCL | 2.564% | 401 | Low Pressure In Gearbox | BD |  | 10:45 | 11:09 | 12:16 | 0.4 | 1899-12-31 02:48 | 1.5167 | chack and found Gearbox manifold to metal hose connecting hose leakage,so replaced it. And also fond 2 nos. 80w fan failure. So,replaced it. | Close | 0.038889 | WTG Breakdown Maintenance | G07 | 16015 | 1012.059 | None
882 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-27 | G28 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 9:15 | 10:57 | 21:00 | 1.7 | 1900-01-09 01:12 | 11.75 | chacked and found hu motor side coupler and spidex failure,so replaced it. During run trial found KR240A relay base failure so, replaced it.then start the WTG. | Close | 0.30128 | WTG Breakdown Maintenance | G30 | 16041 | 7853.4062 | None
883 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 23418 | 23417.729 | None
884 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 23418 | 23417.729 | None
885 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | G17 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 23109 | 23108.7325 | None
886 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | G02 | PWEGPL | MSEDCL | 2.564% | 700 | PLC-Converter Communication Error | BD |  | 14:10 | 14:45 | 19:45 | 0.58333 | 1900-01-04 | 5.5833 | chack slipring connection,module, found cab module failure, so,replaced it. | Close | 0.14316 | WTG Breakdown Maintenance | G04 | 23335 | 5428.6285 | None
887 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 15:20 | 15:53 | 19:00 | 0.55 | 1900-01-02 02:48 | 3.6667 | chacked electrovalves,pressure switch connection,pressure valves setting then fix them again and start the WTG | Close | 0.094017 | WTG Breakdown Maintenance | G13 | 23421 | 3578.2083 | None
888 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | G09 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 15:40 | 15:56 | 18:30 | 0.26667 | 1900-01-01 13:36 | 2.8333 | found pressure switch connection cable faulty,so rejoin it and start the WTG | Close | 0.07265 | WTG Breakdown Maintenance | G13 | 23421 | 2764.9792 | None
889 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | G03 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 12:15 | 12:25 | 13:30 | 0.16667 | 1899-12-31 02:00 | 1.25 | clean slipring,and pm pending poins closed | Close | 0.032051 | WTG Breakdown Maintenance | G04 | 23335 | 1215.3646 | None
890 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | G23 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 18:20 | 19:15 | 19:18 | 0.91667 | 0.05 | 0.96667 | Reset then restore wtg. | Close | 0.024786 | WTG Breakdown Maintenance | G22 | 23276 | 937.5056 | None
891 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 31102 | 31101.64 | None
892 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 31102 | 31101.64 | None
893 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | G17 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 30432 | 30431.6478 | None
894 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | G02 | PWEGPL | MSEDCL | 2.564% | 5222 | Speed Read Incorrectly | BD |  | 10:10 | 11:46 | 14:25 | 1.6 | 1900-01-01 15:36 | 4.25 | Chacked ccu,encoder connection,corrected encoder cable connection,then started the WTG | Close | 0.10897 | WTG Breakdown Maintenance | G04 | 30134 | 5336.2292 | None
895 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | G02 | PWEGPL | MSEDCL | 2.564% | 2119 | CTRL Error - Processor Stopped | BD |  | 16:21 | 16:47 | 17:08 | 0.43333 | 0.35 | 0.78333 | updated PLC software | Close | 0.020085 | WTG Breakdown Maintenance | G04 | 30134 | 983.5403 | None
896 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | G09 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 15:26 | 15:39 | 15:40 | 0.21667 | 0.016667 | 0.23333 | Reset then restore wtg. | Close | 0.0059829 | WTG Breakdown Maintenance | G13 | 31564 | 306.8722 | None
897 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | G12 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 15:20 | 15:32 | 15:33 | 0.2 | 0.016667 | 0.21667 | Reset then restore wtg. | Close | 0.0055556 | WTG Breakdown Maintenance | G13 | 31564 | 284.9528 | None
898 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | G39 | PWEGPL | MSEDCL | 2.564% | 117 | Orienting and Low Yaw Brake Pressure | BD |  | 15:20 | 15:44 | 15:46 | 0.4 | 0.033333 | 0.43333 | Reset then restore wtg. | Close | 0.011111 | WTG Breakdown Maintenance | G40 | 31260 | 564.4167 | None
899 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-30 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 22127 | 22126.7439 | None
900 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-30 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 22127 | 22126.7439 | None
901 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-30 | G17 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 22013 | 22012.7452 | None
902 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-30 | G38 | PWEGPL | MSEDCL | 2.564% | CE100001 | Manual Stop | FM |  | 12:50 | 12:50 | 15:05 | 0 | 1900-01-01 06:00 | 2.25 | Blade inspection done | Close | 0.057692 | WTG Force Majeure | G39 | 22234 | 2084.4375 | None
903 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-30 | G38 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | Manual stop/Customer |  | 15:05 | 15:05 | 15:55 | 0 | 0.83333 | 0.83333 | Post PM audit done | Close | 0.021368 | WTG Force Majeure | G39 | 22234 | 772.0139 | None
904 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 21100 | 21099.7558 | None
905 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 21100 | 21099.7558 | None
906 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | G17 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 27820 | 27819.678 | None
907 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | G32 | PWEGPL | MSEDCL | 2.564% | 552 | Wear Brushes Generator Triggered Too Long | BD |  | 11:40 | 12:10 | 13:02 | 0.5 | 0.86667 | 1.3667 | Check slipring carbon brush found all are ok then check feedback ckt found ok then restore wtg | Close | 0.035043 | WTG Breakdown Maintenance | G26 | 20160 | 1148 | None
908 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | G32 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 16:25 | 17:02 | 17:04 | 0.61667 | 0.033333 | 0.65 | Reset then restore wtg. | Close | 0.016667 | WTG Breakdown Maintenance | G26 | 20160 | 546 | None
909 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | G22 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 13:15 | 13:15 | 16:44 | 0 | 3.4833 | 3.4833 | Manual stop for blade bush gap inspection work | Close | 0.089316 | WTG Force Majeure | G21 | 21150 | 3069.6875 | None
910 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 24001 | 24000.7222 | None
911 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 24001 | 24000.7222 | None
912 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 25020 | 25019.7104 | None
913 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | G36 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 13:52 | 13:52 | 17:14 | 0 | 3.3667 | 3.3667 | Manual stop for blade bush gap inspection work | Close | 0.086325 | WTG Force Majeure | G35 | 16282 | 2284.0028 | None
914 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 20400 | 20399.7639 | None
915 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 20400 | 20399.7639 | None
916 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 28360 | 28359.6718 | None
917 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | G27 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 11:32 | 11:32 | 16:30 | 0 | 4.9667 | 4.9667 | Manual stop for blade bush gap inspection work | Close | 0.12735 | WTG Force Majeure | G25 | 21242 | 4395.9139 | None
918 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | G23 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 16:54 | 17:26 | 17:28 | 0.53333 | 0.033333 | 0.56667 | Reset then restore wtg. | Close | 0.01453 | WTG Breakdown Maintenance | G22 | 20876 | 492.9056 | None
919 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | G09 | PWEGPL | MSEDCL | 2.564% | 813 | Low Pressure Of Emergency Accumulators | BD |  | 17:02 | 17:21 | 17:23 | 0.31667 | 0.033333 | 0.35 | Reset then restore wtg. | Close | 0.0089744 | WTG Breakdown Maintenance | G12 | 29855 | 435.3854 | None
920 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-04 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 21550 | 21549.7506 | None
921 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-04 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 21550 | 21549.7506 | None
922 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-04 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 24505 | 24504.7164 | None
923 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-04 | G16 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 11:19 | 11:19 | 13:55 | 0 | 2.6 | 2.6 | Manual stop for blade bush gap inspection work | Close | 0.066667 | WTG Force Majeure | G18 | 24505 | 2654.7083 | None
924 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-04 | G09 | PWEGPL | MSEDCL | 2.564% | 208 | HU Pump Drive Failure | BD |  | 15:08 | 15:24 | 16:15 | 0.26667 | 0.85 | 1.1167 | Check related ckt found HU contactor failure so replaced then restore WTG | Close | 0.028632 | WTG Breakdown Maintenance | G12 | 24924 | 1159.6583 | None
925 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-04 | G04 | PWEGPL | MSEDCL | 2.564% | 203 | Low Pressure On Hydraulic Group | BD |  | 9:32 | 10:34 | 17:20 | 1.0333 | 6.7667 | 7.8 | Check related circuit we found PRV 1-10 valve issue so replaced it &found hydraulic main hose damage so we replaced the hose | Close | 0.2 | WTG Breakdown Maintenance | G03 | 23114 | 7512.05 | None
926 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-05 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 22500 | 22499.7396 | None
927 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-05 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 22500 | 22499.7396 | None
928 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-05 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 22499 | 22498.7396 | None
929 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-05 | G32 | PWEGPL | MSEDCL | 2.564% | 552 | Wear Brushes Generator Triggered Too Long | BD |  | 10:45 | 11:18 | 13:16 | 0.55 | 1.9667 | 2.5167 | Check related ckt found ground brush feedback failure so replaced. | Close | 0.06453 | WTG Breakdown Maintenance | G26 | 20625 | 2162.7604 | None
930 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-05 | G11 | PWEGPL | MSEDCL | 2.564% | 5263 | CAN Communication Failure | BD |  | 14:03 | 14:40 | 14:45 | 0.61667 | 0.083333 | 0.7 | Reset then restore wtg. | Close | 0.017949 | WTG Breakdown Maintenance | G10 | 21814 | 636.2417 | None
931 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-06 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 33225 | 33224.6155 | None
932 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-06 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 33225 | 33224.6155 | None
933 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-06 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 32045 | 32044.6291 | None
934 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-06 | G35 | PWEGPL | MSEDCL | 2.564% | 711 | Sonic Error.NRG Operates | BD |  | 12:40 | 13:01 | 14:15 | 0.35 | 1.2333 | 1.5833 | Check releted circuit found Cap anemometer connection loose so tighed than start WTG | Close | 0.040598 | WTG Breakdown Maintenance | G36 | 24441 | 1612.4271 | None
935 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-06 | G16 | PWEGPL | MSEDCL | 2.564% | 502 | Generator NDE Bearing High Temperature Alarm | BD |  | 17:10 | 17:20 | 18:10 | 0.16667 | 0.83333 | 1 | Generator bearing apply grease slipring 4 carbon brush change than start WTG | Close | 0.025641 | WTG Breakdown Maintenance | G18 | 32045 | 1335.2083 | None
936 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 9225 | 9224.8932 | None
937 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 9225 | 9224.8932 | None
938 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 13935 | 13934.8387 | None
939 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | G23 | PWEGPL | MSEDCL | 2.564% | 205 | Low Level Hydraulic Group Refrigeration Oil | BD |  | 15:00 | 15:39 | 17:00 | 0.65 | 1.35 | 2 | Checked leakage, no leakage found then restore wtg. | Close | 0.051282 | WTG Breakdown Maintenance | G22 | 9289 | 774.0833 | None
940 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | G33 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 17:45 | 18:20 | 18:22 | 0.58333 | 0.033333 | 0.61667 | Reset then restore wtg. | Close | 0.015812 | WTG Breakdown Maintenance | G34 | 8006 | 205.7097 | None
941 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 13450 | 13449.8443 | None
942 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 13450 | 13449.8443 | None
943 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 20689 | 20688.7605 | None
944 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | G01 | PWEGPL | MSEDCL | 2.564% | 800 | Pitch Drive Error | BD |  | 11:00 | 11:22 | 17:46 | 0.36667 | 6.4 | 6.7667 | Check releted circuit found proportional valve failure so replace it, than start WTG | Close | 0.1735 | WTG Breakdown Maintenance | G07 | 16576 | 4673.5111 | None
945 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | G32 | PWEGPL | MSEDCL | 2.564% | 1821 | Heating Protection Triggered | BD |  | 17:00 | 17:15 | 19:30 | 0.25 | 2.25 | 2.5 | Check releted circuit found MPCB failure so replace it, than start WTG | Close | 0.064103 | WTG Breakdown Maintenance | G26 | 10015 | 1043.2292 | None
946 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-09 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 6877 | 6876.9204 | None
947 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-09 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 6877 | 6876.9204 | None
948 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-09 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 12355 | 12354.857 | None
949 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-09 | G04 | PWEGPL | MSEDCL | 2.564% | 2118 | Bus Error - Interbus Failure | BD |  | 10:30 | 11:15 | 12:30 | 0.75 | 1.25 | 2 | Clean slipring than start WTG | Close | 0.051282 | WTG Breakdown Maintenance | G07 | 11467 | 955.5833 | None
950 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-09 | G32 | PWEGPL | MSEDCL | 2.564% | 5203 | Heating/Coolant Thermal Magnetic Failure | BD |  | 11:46 | 12:11 | 16:04 | 0.41667 | 3.8833 | 4.3 | Check releted circuit found FG781A connection loose so tighed than start WTG | Close | 0.11026 | WTG Breakdown Maintenance | G26 | 7490 | 1341.9583 | None
951 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-10 | G31 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 20:00 | 20:00 | 20 | 0 | 20 | Manual stop for blade bush gap issue retrofitting work | Open | 0.51282 | WTG Force Majeure | G30 | 4510 | 3758.3333 | None
952 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-10 | G29 | PWEGPL | MSEDCL | 2.564% | CE100015 | Manual Stop - Safety Related | FM |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Manual stop for blade bush gap issue retrofitting work | Open | 0.61538 | WTG Force Majeure | G30 | 4510 | 4509.9478 | None
953 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-10 | G17 | PWEGPL | MSEDCL | 2.564% | 5216 | Grid Voltage Failure | BD |  | 0:00 | 24:00 | 24:00 | 23.9997 | 0 | 23.9997 | Take meggering & MBT test found trf failure (Work in progress) | Open | 0.61538 | WTG Breakdown Maintenance | G18 | 6420 | 6419.9257 | None
954 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-10 | G26 | PWEGPL | MSEDCL | 2.564% | 213 | Hydraulic Pump Protection | BD |  | 10:25 | 10:50 | 12:14 | 0.41667 | 1.4 | 1.8167 | Check related ckt found connection loose , connection tighten properly & trail taken then FG280 MPCB Tripped so stand mpcb then restore wtg. | Close | 0.046581 | WTG Breakdown Maintenance | G32 | 3520 | 266.4444 | None
955 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-10 | G28 | PWEGPL | MSEDCL | 2.564% | 213 | Hydraulic Pump Protection | BD |  | 12:38 | 13:02 | 18:10 | 0.4 | 5.1333 | 5.5333 | Check related ckt found fg280 mpcb tripped so mpcb stand & connection checked then trail taken again mpcb trip so check KM004 Contactor connection found connection loose then tighten properly then restore wtg. | Close | 0.14188 | WTG Breakdown Maintenance | G30 | 4510 | 1039.8056 | None
956 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-10 | G31 | PWEGPL | MSEDCL | 2.564% | 700 | PLC-Converter Communication Error | BD |  | 20:00 | 20:00 | 23:59 | 0 | 3.9833 | 3.9833 | Removed materials arrangment in progress | Open | 0.10214 | WTG Breakdown Maintenance | G30 | 4510 | 748.5347 | Material shortage
Formulas:
Month = Table6[[#This Row],[Date]]-DAY(Table6[[#This Row],[Date]])+1
Resolution Time = (Table6[[#This Row],[Fault Clearance time]]-Table6[[#This Row],[Work Start TimeStamp]])*24
Breakdown Time = (Table6[[#This Row],[Fault Clearance time]]-Table6[[#This Row],[Fault Start TimeStamp]])*24

## IGA_BD
Sr. No. | Financial Year | Calendar Year | Operating Year | Month | Date | Affected Feeder | SPV | Consumer | Plant Equivalent Weightage | Breakdown Description | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Fault Category | Estimated Energy Loss (kWh) | Scope | PTW No. | Job Card No.
1 | 2025 | 2025 | Year_1 | 2025-03-01 | 2025-03-31 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 19:20 | 19:20 | 19:37 | 0 | 0.28333 | 0.28333 | Test charged & stood ok | Close | 0.07265 | IG Breakdown Maintenance | 580 | SGSL
2 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-01 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 tripped due to Earth fault / Over current | 22:35 | 22:35 | 23:59 | 0 | 1.4 | 1.4 | Test charged & stood ok | Open | 0.32308 | IG Breakdown Maintenance | 2898 | SGSL
3 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-01 | Wind_F1 | PWEGPL | MSEDCL | 25.64% | F-1 tripped due to Earth fault / Over current | 22:38 | 22:38 | 23:03 | 0 | 0.41667 | 0.41667 | Test charged & stood ok | Close | 0.10684 | IG Breakdown Maintenance | 708.3333 | SGSL
4 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-02 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 tripped due to Earth fault / Over current | 0:00 | 0:00 | 1:21 | 0 | 1.35 | 1.35 | Circuit open then close one by one | Close | 0.31154 | IG Breakdown Maintenance | 6986.25 | SGSL
5 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-03 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 21:24 | 21:24 | 21:45 | 0 | 0.35 | 0.35 | Test charged & stood ok | Close | 0.089744 | IG Breakdown Maintenance | 857.5 | SGSL
6 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-07 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 Shutdown taken for scada cable rectification work | 12:37 | 12:37 | 14:38 | 0 | 2.0167 | 2.0167 | Scada cable rejoint then restore feeder | Close | 0.46538 | IG Unscheduled Maintenance | 4083.75 | SGSL
7 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-07 | Wind_F4 | PWEGPL | MSEDCL | 25.64% | F-4 Shutdown taken for scada cable rectification work | 12:37 | 12:37 | 14:39 | 0 | 2.0333 | 2.0333 | Scada cable rejoint then restore feeder | Close | 0.52137 | IG Unscheduled Maintenance | 4631.4815 | SGSL
8 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-01 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 Shutdown taken for 11Kv line restoration work. | 17:05 | 17:05 | 18:00 | 0 | 0.91667 | 0.91667 | 11 Kv line restore then restore feeder | Close | 0.21154 | IG Unscheduled Maintenance | 5651.25 | SGSL
9 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-01 | Wind_F4 | PWEGPL | MSEDCL | 25.64% | F-4 Shutdown taken for 11Kv line restoration work. | 17:05 | 17:05 | 18:00 | 0 | 0.91667 | 0.91667 | 11 Kv line restore then restore feeder | Close | 0.23504 | IG Unscheduled Maintenance | 6416.6667 | SGSL
10 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-06 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 16:26 | 16:26 | 16:32 | 0 | 0.1 | 0.1 | Test charged & stood ok | Close | 0.025641 | IG Breakdown Maintenance | 265 | SGSL
11 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-12 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 tripped due to Earth fault | 15:02 | 15:02 | 15:12 | 0 | 0.16667 | 0.16667 | Test charged & stood ok | Close | 0.038462 | IG Breakdown Maintenance | 214 | SGSL
12 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-12 | Wind_F1 | PWEGPL | MSEDCL | 25.64% | F-1 tripped due to Earth fault | 15:21 | 15:21 | 15:28 | 0 | 0.11667 | 0.11667 | Test charged & stood ok | Close | 0.029915 | IG Breakdown Maintenance | 126 | SGSL
13 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-16 | Wind_F4_Ckt2 | PWEGPL | MSEDCL | 12.82% | F-4 Shutdown taken for line & HT yard preventive maintenance work | 14:00 | 14:00 | 15:20 | 0 | 1.3333 | 1.3333 | Line & HT yard maintenance work done then restore circuit | Close | 0.17094 | IG Scheduled Maintenance | 2777.7778 | SGSL
14 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-17 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 Shutdown taken for line & HT yard preventive maintenance work | 13:00 | 13:00 | 14:48 | 0 | 1.8 | 1.8 | Line & HT yard maintenance work done then restore feeder | Close | 0.41538 | IG Scheduled Maintenance | 3969 | SGSL
15 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-19 | Wind_F1 | PWEGPL | MSEDCL | 25.64% | F-1 tripped due to Earth fault | 20:44 | 20:44 | 21:00 | 0 | 0.26667 | 0.26667 | Test charged & stood ok | Close | 0.068376 | IG Breakdown Maintenance | 333.3333 | SGSL
16 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-19 | Wind_F4_Ckt1 | PWEGPL | MSEDCL | 12.82% | F-4 tripped due to Earth fault | 21:12 | 21:12 | 22:07 | 0 | 0.91667 | 0.91667 | Circuit 2 isolator open then closed | Close | 0.11752 | IG Breakdown Maintenance | 1283.3333 | SGSL
17 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-19 | Wind_F4_Ckt2 | PWEGPL | MSEDCL | 12.82% | F-4 tripped due to Earth fault | 21:12 | 21:12 | 23:59 | 0 | 2.7833 | 2.7833 | work in progress | Open | 0.35684 | IG Breakdown Maintenance | 4035.8333 | SGSL
18 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-19 | Wind_F4_Ckt2 | PWEGPL | MSEDCL | 12.82% | F-4 tripped due to Earth fault | 0:00 | 0:00 | 0:44 | 0 | 0.73333 | 0.73333 | LA failure in G12 HT yard so replaced it then restore feeder | Close | 0.094017 | IG Breakdown Maintenance | 1063.3333 | SGSL
19 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-20 | Wind_F4_Ckt1 | PWEGPL | MSEDCL | 12.82% | F-4 Ckt-1 Shutdown taken for line & HT yard preventive maintenance work | 10:35 | 10:35 | 11:47 | 0 | 1.2 | 1.2 | Line & HT yard maintenance work done then restore feeder | Close | 0.15385 | IG Scheduled Maintenance | 2580 | SGSL
20 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-20 | Wind_F1 | PWEGPL | MSEDCL | 25.64% | F-1 Shutdown taken for line & HT yard preventive maintenance work | 12:30 | 12:30 | 14:00 | 0 | 1.5 | 1.5 | Line & HT yard maintenance work done then restore feeder | Close | 0.38462 | IG Scheduled Maintenance | 2550 | SGSL
21 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-20 | Wind_F1 | PWEGPL | MSEDCL | 25.64% | F-1 tripped due to Earth fault | 18:17 | 18:17 | 18:48 | 0 | 0.51667 | 0.51667 | Test charged & stood ok | Close | 0.13248 | IG Breakdown Maintenance | 878.3333 | SGSL
22 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-21 | Wind_F2_Ckt2 | PWEGPL | MSEDCL | 15.38% | F-2 Shutdown taken for line & HT yard preventive maintenance work | 11:20 | 11:20 | 12:40 | 0 | 1.3333 | 1.3333 | Line & HT yard maintenance work done then restore feeder | Close | 0.20513 | IG Breakdown Maintenance | 2400 | SGSL
23 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-23 | Wind_F1 | PWEGPL | MSEDCL | 25.64% | F-1 Shutdown taken for line & VCB yard preventive maintenance work | 10:52 | 10:52 | 14:18 | 0 | 3.4333 | 3.4333 | Line & VCB yard maintenance work done then restore feeder | Close | 0.88034 | IG Scheduled Maintenance | 2231.6667 | SGSL
24 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-23 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 Shutdown taken for line & VCB yard preventive maintenance work | 10:52 | 10:52 | 14:18 | 0 | 3.4333 | 3.4333 | Line & VCB yard maintenance work done then restore feeder | Close | 0.88034 | IG Scheduled Maintenance | 2060 | SGSL
25 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-23 | Wind_F4_Ckt2 | PWEGPL | MSEDCL | 12.82% | F-4 Shutdown taken for container movement work | 14:48 | 14:48 | 16:01 | 0 | 1.2167 | 1.2167 | Container movement then restore feeder | Close | 0.15598 | IG Unscheduled Maintenance | 1216.6667 | O2 power
26 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-23 | Wind_F4_Ckt1 | PWEGPL | MSEDCL | 12.82% | F-4 Shutdown taken for PT replacement work . | 15:40 | 15:40 | 16:01 | 0 | 0.35 | 0.35 | PT replaced then restore feeder | Close | 0.044872 | IG Unscheduled Maintenance | 350 | SGSL
27 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-24 | Wind_F4 | PWEGPL | MSEDCL | 25.64% | F-4 shutdown taken for Protection PT replaced | 14:24 | 14:24 | 15:05 | 0 | 0.68333 | 0.68333 | PT replaced then restore feeder | Close | 0.17521 | IG Unscheduled Maintenance | 1777 | SGSL
28 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-27 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 11:30 | 11:30 | 11:36 | 0 | 0.1 | 0.1 | Test charged & stood ok | Close | 0.025641 | IG Unscheduled Maintenance | 430 | SGSL
29 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-27 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 tripped due to Earth fault | 15:40 | 15:40 | 19:50 | 0 | 4.1667 | 4.1667 | G01 Isolator open then restore feeder | Close | 0.96154 | IG Unscheduled Maintenance | 22687.5 | SGSL
30 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-28 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 14:21 | 14:21 | 14:25 | 0 | 0.066667 | 0.066667 | Test charged & stood ok | Close | 0.017094 | IG Unscheduled Maintenance | 203 | SGSL
31 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-29 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 8:26 | 8:26 | 8:32 | 0 | 0.1 | 0.1 | Test charged & stood ok | Close | 0.025641 | IG Unscheduled Maintenance | 555 | SGSL
32 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-29 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 9:26 | 9:26 | 9:30 | 0 | 0.066667 | 0.066667 | Test charged & stood ok | Close | 0.017094 | IG Breakdown Maintenance | 370 | SGSL
33 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-31 | Wind_F2_Ckt1 | PWEGPL | MSEDCL | 10.26% | F-2 tripped due to Earth fault | 10:05 | 10:05 | 11:38 | 0 | 1.55 | 1.55 | Circuit 2 isolator open then charge feeder circuit 1 | Close | 0.15897 | IG Unscheduled Maintenance | 11315 | SGSL
34 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-31 | Wind_F2_Ckt2 | PWEGPL | MSEDCL | 15.38% | F-2 tripped due to Earth fault | 10:05 | 10:05 | 12:45 | 0 | 2.6667 | 2.6667 | Circuit 2 petorling done then charge circuit 2 | Close | 0.41026 | IG Unscheduled Maintenance | 19466.6667 | SGSL
35 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-01 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 12:31 | 12:31 | 12:33 | 0 | 0.033333 | 0.033333 | Test charged & stood ok | Close | 0.008547 | IG Breakdown Maintenance | 248.3333 | SGSL
36 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-01 | Wind_F1 | PWEGPL | MSEDCL | 25.64% | F-1 tripped due to Earth fault | 16:45 | 16:45 | 16:48 | 0 | 0.05 | 0.05 | Test charged & stood ok | Close | 0.012821 | IG Breakdown Maintenance | 312.5 | SGSL
37 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-02 | Wind_F2_Ckt1 | PWEGPL | MSEDCL | 10.26% | F-2 Shutdown taken for line & HT yard preventive maintenance work | 14:55 | 14:55 | 15:55 | 0 | 1 | 1 | Line & HT yard maintenance work done then restore circuit | Close | 0.10256 | IG Scheduled Maintenance | 3700 | SGSL
38 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-03 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 4:40 | 4:40 | 4:54 | 0 | 0.23333 | 0.23333 | Test charged & stood ok | Close | 0.059829 | IG Breakdown Maintenance | 1702 | SGSL
39 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-04 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 Shutdown taken for line & VCB yard preventive maintenance work | 10:30 | 10:30 | 14:11 | 0 | 3.6833 | 3.6833 | Line & VCB yard maintenance work done then restore feeder | Close | 0.85 | IG Scheduled Maintenance | 8121.75 | SGSL
40 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-04 | Wind_F4 | PWEGPL | MSEDCL | 25.64% | F-4 Shutdown taken for line & VCB yard preventive maintenance work | 10:30 | 10:30 | 14:11 | 0 | 3.6833 | 3.6833 | Line & VCB yard maintenance work done then restore feeder | Close | 0.94444 | IG Scheduled Maintenance | 8594.4444 | SGSL
41 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-04 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 14:35 | 14:35 | 14:50 | 0 | 0.25 | 0.25 | Test charged & stood ok | Close | 0.064103 | IG Unscheduled Maintenance | 312.5 | SGSL
42 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-04 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 Shutdown taken for Protection CT replacement work | 16:30 | 16:30 | 20:55 | 0 | 4.4167 | 4.4167 | Portection CT replaced then restore feeder | Close | 1.1325 | IG Unscheduled Maintenance | 5520.8333 | SGSL
43 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-08 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 6:49 | 6:49 | 6:51 | 0 | 0.033333 | 0.033333 | Test charged & stood ok | Close | 0.008547 | IG Breakdown Maintenance | 179.1667 | SGSL
44 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-08 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Over current | 19:02 | 19:02 | 21:05 | 0 | 2.05 | 2.05 | Line petroling done then charged feeder | Close | 0.52564 | IG Breakdown Maintenance | 11018.75 | SGSL
45 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-11 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | F-3 tripped due to Over current | 16:37 | 16:37 | 16:45 | 0 | 0.13333 | 0.13333 | Test charged & stood ok | Close | 0.030769 | IG Breakdown Maintenance | 527 | SGSL
46 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-13 | Wind_F2_Ckt2 | PWEGPL | MSEDCL | 15.38% | F-2 Shutdown taken for PG connector sparking rectification work | 16:10 | 16:10 | 16:45 | 0 | 0.58333 | 0.58333 | PG connector replaced then restore circuit | Close | 0.089744 | IG Unscheduled Maintenance | 437 | SGSL
47 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-16 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | F-2 tripped due to Earth fault | 6:34 | 6:34 | 6:38 | 0 | 0.066667 | 0.066667 | Test charged & stood ok | Close | 0.017094 | IG Breakdown Maintenance | 539 | SGSL
48 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-18 | Wind_F1 | PWEGPL | MSEDCL | 25.64% | F-1 tripped due to Earth fault/ Over Current | 12:44 | 12:44 | 12:49 | 0 | 0.083333 | 0.083333 | Test charged & stood ok | Close | 0.021368 | IG Breakdown Maintenance | 935 | SGSL
49 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-25 | Wind_F4 | PWEGPL | MSEDCL | 25.64% | Shutdown taken for External line LT conductor rejoin work | 12:25 | 12:25 | 13:50 | 0 | 1.4167 | 1.4167 | After the work feeder charged | Close | 0.36325 | IG Unscheduled Maintenance | 12070 | O2 power
50 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-25 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | Shutdown taken for External line LT conductor rejoin work | 12:25 | 12:25 | 13:50 | 0 | 1.4167 | 1.4167 | After the work feeder charged | Close | 0.32692 | IG Unscheduled Maintenance | 10160 | O2 power
51 | 2026 | 2025 | Year_1 | 2025-07-01 | 2025-07-05 | Wind_F3 | PWEGPL | MSEDCL | 23.08% | Shutdown taken for scada cable rejoined work . | 11:34 | 11:34 | 12:54 | 0 | 1.3333 | 1.3333 | Scada cable rejoint then restore feeder | Close | 0.30769 | IG Unscheduled Maintenance | 9600 | SGSL
52 | 2026 | 2025 | Year_1 | 2025-07-01 | 2025-07-05 | Wind_F4 | PWEGPL | MSEDCL | 25.64% | Shutdown taken for scada cable rejoined work . | 11:34 | 11:34 | 12:54 | 0 | 1.3333 | 1.3333 | Scada cable rejoint then restore feeder | Close | 0.34188 | IG Unscheduled Maintenance | 10667 | SGSL
53 | 2026 | 2025 | Year_1 | 2025-07-01 | 2025-07-07 | Wind_F2 | PWEGPL | MSEDCL | 25.64% | line clearance for crane | 13:25 | 13:25 | 13:40 | 0 | 0.25 | 0.25 | crane passed then restore feeder | Close | 0.064103 | IG Unscheduled Maintenance | 838 | O2 power
54 | 2026 | 2025 | Year_1 | 2025-07-01 | 2025-07-08 | Wind_F1_Ckt2 | PWEGPL | MSEDCL | 12.82% | Shutdown taken for scada cable rejoined work . | 13:30 | 13:30 | 14:10 | 0 | 0.66667 | 0.66667 | Scada cable rejoint then restore feeder | Close | 0.08547 | IG Unscheduled Maintenance | 5191.6667 | SGSL
Formulas:
Month = Table8[[#This Row],[Date]]-DAY(Table8[[#This Row],[Date]])+1

## Grid_BD
Sr. No. | Financial Year | Calendar Year | Operating Year | Month | Date | Affected Feeder | SPV | Concumaer | Plant Equivalent Weightage | Breakdown Description | Breakdown Type | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Fault Category | Paired WTG for Enegy based MA | Estimated Energy Loss (kWh) | Curtailment Order imit. | EGA_Including_CurtailmentOrder | PTW No. | Job Card No.
1 | 2023 | 2025 | Year_1 | 2023-02-01 | 2023-02-01 | Line1 | PWEGPL | MSEDCL | 100% | Grid Failure |  | 17:33 | 0.73472 | 0.76528 | 0.083333 | 0.73333 | 0.81667 | Charged feeders post Grid resume | Close | 0.81667 |  |  |  |  | 100%
Formulas:
Month = Table9[[#This Row],[Date]]-DAY(Table9[[#This Row],[Date]])+1

## Basic Data (hidden)
[12 empty] | Major Breakdown | 100 | Yawing Sensor Failure | Fault Category
| Generator | Consumer | Capacity | % Plant Equiva. Weightage | Feeder | TX | USS | MY |  |  |  | Breakdown | 101 | Maximum Winding Error | WTG Unscheduled Maintenance | IG Unscheduled Maintenance | EG Unscheduled Maintenance
G01 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G01 |  | Total Capacity | 78 | Open | Manual Stop | 102 | CW Feedback Failure | WTG Breakdown Maintenance | IG Breakdown Maintenance | EG Breakdown Maintenance
G02 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G02 |  |  |  | Close | ROW | 103 | CCW Feedback Failure | WTG Scheduled Maintenance | IG Scheduled Maintenance | EG Scheduled Maintenance
G03 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G03 | [5 empty] | 104 | Max Orientation Time | WTG Environmental | IG Force Majeure | EG Force Majeure
G04 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G04 | [5 empty] | 105 | Maximum Unwinding Time | WTG Force Majeure
G05 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G05 | [5 empty] | 106 | Unwinding Error
G06 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G06 | [5 empty] | 107 | Yawing Motor Thermal Relays
G07 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G07 | [5 empty] | 108 | Automatic Unwinding
G08 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G08 | [5 empty] | 110 | Yaw Sensor Wiring Error
G09 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G09 | [5 empty] | 112 | Yaw Beak Wear
G10 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G10 | [5 empty] | 114 | Low Yaw Brake Pressure
G11 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F3 | TX2 | G11 | [5 empty] | 115 | High Yaw Brake Pressure
G12 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G12 | [5 empty] | 116 | Orienting and High Yaw Brake Pressure
G13 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G13 | [5 empty] | 117 | Orienting and Low Yaw Brake Pressure
G14 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G14 | [5 empty] | 118 | Yaw Motors Error
G15 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G15 | [5 empty] | 119 | Yaw Contactor Active
G16 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G16 | [5 empty] | 121 | Low Grease Level for Yaw Plates
G17 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G17 | [5 empty] | 122 | Yaw Plate Lubrication Failure
G18 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G18 | [5 empty] | 123 | Low Grease Level For Yaw Pinion
G19 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G19 | [5 empty] | 124 | Yaw Pinion Lubrication Failure
G20 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F4 | TX2 | G20 | [5 empty] | 125 | Yaw Motors Over Current Protection
G21 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G21 | [5 empty] | 126 | Excessive Yaw Drag
G22 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G22 | [5 empty] | 127 | Possible Yaw Circuit Leakages
G23 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G23 | [5 empty] | 128 | Auto Yaw Not Possible
G25 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G25 | [5 empty] | 130 | Yaw Pinion Lubrication Failure Too Long
G26 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G26 | [5 empty] | 200 | Minimum Hydraulic Unit Temperature
G27 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G27 | [5 empty] | 201 | Max. Pump time
G28 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G28 | [5 empty] | 202 | Low Pressure On Brake Circuit
G29 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G29 | [5 empty] | 203 | Low Pressure On Hydraulic Group
G30 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G30 | [5 empty] | 204 | Hydraulic Filter Dirty
G31 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F2 | TX1 | G31 | [5 empty] | 205 | Low Level Hydraulic Group Refrigeration Oil
G32 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G32 | [5 empty] | 207 | Hydraulic Oil High Temperature
G33 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G33 | [5 empty] | 208 | HU Pump Drive Failure
G34 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G34 | [5 empty] | 211 | Hydraulic HUB Filter Dirty
G35 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G35 | [5 empty] | 212 | Leakage In The HUB
G36 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G36 | [5 empty] | 213 | Hydraulic Pump Protection
G37 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G37 | [5 empty] | 214 | Maximum HU Preheating Time
G38 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G38 | [5 empty] | 217 | Warning Load Control valve Malfunction
G39 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G39 | [5 empty] | 218 | Low Oil Temperature : Heating Procedure Request
G40 | PWEGPL | MSEDCL | 2 | 2.564% | Wind_F1 | TX1 | G40 | [5 empty] | 219 | Hydraulic Unit Alarm Temperature
Wind_F1 | PWEGPL | MSEDCL | 20 | 25.64% | [8 empty] | 221 | Hydraulic Unit Cooling Failure
Wind_F1_Ckt1 | PWEGPL | MSEDCL | 10 | 12.82%
Wind_F1_Ckt2 | PWEGPL | MSEDCL | 10 | 12.82%
Wind_F2 | PWEGPL | MSEDCL | 20 | 25.64% | [8 empty] | 222 | Very Low Pressure On Hydraulic Unit
Wind_F2_Ckt1 | PWEGPL | MSEDCL | 8 | 10.26%
Wind_F2_Ckt2 | PWEGPL | MSEDCL | 12 | 15.38%
Wind_F3 | PWEGPL | MSEDCL | 18 | 23.08% | [8 empty] | 223 | Very High Temperature Of Hydraulic Unit Oil
Wind_F3_Ckt1 | PWEGPL | MSEDCL | 10 | 12.82%
Wind_F3_Ckt2 | PWEGPL | MSEDCL | 8 | 10.26%
Wind_F4 | PWEGPL | MSEDCL | 20 | 25.64% | [8 empty] | 226 | Hydraulic Filter Dirty Too Long
Wind_F4_Ckt1 | PWEGPL | MSEDCL | 10 | 12.82%
Wind_F4_Ckt2 | PWEGPL | MSEDCL | 10 | 12.82%
TX1 | PWEGPL | MSEDCL | 40 | 51.28% | [8 empty] | 227 | Hydraulic HUB Filter Dirty Too Long
TX2 | PWEGPL | MSEDCL | 38 | 48.72% | [8 empty] | 228 | Time Out For Oil Heating In Operation
Line1 | PWEGPL | MSEDCL | 78 | 100% | [8 empty] | 300 | Anemo Failure
[13 empty] | 302 | High Wind Speed
[13 empty] | 303 | TOP Zero Degrees
[13 empty] | 304 | Ambient Temperature Low
[13 empty] | 305 | Ambient Temperature High
[13 empty] | 306 | High Temperature On Trafo Winding
[13 empty] | 307 | Overheating On Trafo Winding
[13 empty] | 309 | Smoke Sensor
[13 empty] | 310 | Machine On Preheating
[13 empty] | 312 | Zero Degrees HUB
[13 empty] | 313 | Very High Disalignment
[13 empty] | 314 | High Misalignment and Orienting Badly
[13 empty] | 315 | Beacon Failure
[13 empty] | 317 | Low Nacelle Temperature
[13 empty] | 318 | High Nacelle Temperature
[13 empty] | 319 | Ice On Nacelle
[13 empty] | 320 | Ice Sensor Error
[13 empty] | 321 | Low Ground Cabinet Temperature
[13 empty] | 324 | High Temperature Kit System Failure
[13 empty] | 325 | High Temperature Kit Feedback Failure
[13 empty] | 326 | Low Temperature Kit System Failure
[13 empty] | 327 | Low Temperature Kit Feedback Error
[13 empty] | 341 | Ice Shake
[13 empty] | 343 | Turbine Under Ice Operation
[13 empty] | 344 | High Temperature In Auxiliary Transformer
[13 empty] | 345 | Very High Temperature In Auxiliary Transformer
[13 empty] | 347 | GUYS Functionality Active
[13 empty] | 349 | Transformer Winding High Temperature Warning
[13 empty] | 352 | Converter Water Pressure High
[13 empty] | 354 | Converter Water Pressure Low
[13 empty] | 356 | Auxiliary Transformer Windings High Temperature Warning
[13 empty] | 357 | SADEI System Failure
[13 empty] | 360 | High Wind Turbulence Intensity Alarm
[13 empty] | 361 | VHT - Top Cabinet Maximum Temperature
[13 empty] | 362 | VHT - Ground Cabinet Maximum Temperature
[13 empty] | 363 | VHT - HUB Cabinet Maximum Temperature
[13 empty] | 364 | VHT - Air Conditioning Top Cabinet Feedback
[13 empty] | 365 | VHT - Air Conditioning Ground Cabinet Feedback
[13 empty] | 366 | VHT - Air Conditioning HUB Cabinet Feedback
[13 empty] | 400 | Maximum Generator - Rotor Discrepancy
[13 empty] | 401 | Low Pressure In Gearbox
[13 empty] | 402 | Gearbox Oil Level Low
[13 empty] | 403 | High Gearbox Oil Temperature
[13 empty] | 404 | High Gearbox Bearing Temperature
[13 empty] | 405 | Rotor Or Generator High Speed in STOP Or EMERGENCY
[13 empty] | 406 | High Generator Speed
[13 empty] | 407 | High Rotor Speed
[13 empty] | 408 | Rotor Or Generator High Speed In Pause
[13 empty] | 409 | Generator - Rotor Discrepancy
[13 empty] | 410 | OGS
[13 empty] | 411 | High Brake Temperature
[13 empty] | 412 | Gearbox Fan Thermal Relays
[13 empty] | 413 | Gearbox Fan Feedback Failure
[13 empty] | 414 | Gearbox Fans Active
[13 empty] | 415 | Low Gearbox Oil Temperature
[13 empty] | 416 | Vibration Sensor
[13 empty] | 417 | Gearbox Main Filter Dirty
[13 empty] | 418 | Auxiliary Gearbox Filter Dirty
[13 empty] | 419 | Gearbox Pump Feedback Failure
[13 empty] | 421 | Gearbox Pump Thermal Relay
[13 empty] | 422 | Gearbox Pump Auxiliary Filter Thermal Relay
[13 empty] | 423 | Gearbox Main Filter Dirty Warning
[13 empty] | 424 | Gearbox Oil Heating Thermal Circuit Breaker
[13 empty] | 425 | Gearbox Heating Resistors Feedback Failure
[13 empty] | 426 | Rotor Speed Reading Failure
[13 empty] | 427 | Gearbox Auxiliary Filter Dirty Warning
[13 empty] | 429 | Gearbox Oil High Temperature Warning
[13 empty] | 430 | Gearbox Bearing High Temperature Warning
[13 empty] | 431 | Vibration Sensor After Switching To STOP Or EMERGENCY Mode
[13 empty] | 432 | Metal Particles In Gearbox Oil
[13 empty] | 433 | Failure In The Gearbox Oil Particle Sensor
[13 empty] | 434 | Low Grease Level for Main Shaft Bearing
[13 empty] | 435 | Main Shaft Bearing Lubrication Failure
[13 empty] | 441 | Gearbox Fan Thermal Relays Triggered and High Gearbox Oil Temperature
[13 empty] | 442 | Gearbox Pump Contactor Feedback Failure and High Gearbox Oil Temperature
[13 empty] | 444 | Gearbox Pump Thermal Relay Triggered and High Gearbox Oil Temperature
[13 empty] | 445 | Gearbox Pump Auxiliary Filter Thermal Relay Triggered Too Long
[13 empty] | 446 | Gearbox Fan Feedback Failure and High Gearbox Oil Temperature
[13 empty] | 447 | Gearbox Heating Resistor Feedback Failure and High Gearbox Oil Temperature
[13 empty] | 448 | Main Shaft Bearing Lubrication Failure Too Long
[13 empty] | 500 | High Generator Winding Temperature
[13 empty] | 501 | Generator DE Bearing High Temperature Alarm
[13 empty] | 502 | Generator NDE Bearing High Temperature Alarm
[13 empty] | 506 | Generator Thermal Relay Fans
[13 empty] | 507 | Generator's Fans Failure Confirmation
[13 empty] | 509 | Generator Slipping Ring High Temperature
[13 empty] | 514 | Grid Voltage Dip Warning
[13 empty] | 515 | Active Crowbar On Warning
[13 empty] | 516 | Generator Winding High Temperature Warning
[13 empty] | 517 | Generator DE Bearing High Temperature Warning
[13 empty] | 518 | Generator NDE Bearing High Temperature Warning
[13 empty] | 519 | Nacelle Temperature
[13 empty] | 523 | High Temperature Of Coolant In The Input Of The Cooling Circuit
[13 empty] | 524 | High Temperature Of The Control Module
[13 empty] | 525 | High Ambient Temperature In The Converter
[13 empty] | 526 | High Ambient Temperature In The Stator Thermo-Magnet
[13 empty] | 527 | High Temperature Of Upper Radiator
[13 empty] | 528 | High Temperature Of Lower Radiator
[13 empty] | 530 | High Temperature Of Inver Inductance
[13 empty] | 532 | Low Grease Level For Generator Bearings
[13 empty] | 533 | Generator Bearing Lubrication Failure
[13 empty] | 534 | Maximum Slip Rings Heating Time
[13 empty] | 537 | Wear Brushes Generator
[13 empty] | 538 | Converter High Ambient Temperature Alarm
[13 empty] | 539 | Converter Inlet Ambient Temperature Sensor Failure
[13 empty] | 550 | Generator Fans Thermal Relay Triggered Too Long
[13 empty] | 551 | Generator Bearing Lubrication Failure Too Long
[13 empty] | 552 | Wear Brushes Generator Triggered Too Long
[13 empty] | 565 | Main Shaft Front Bearing Extreme Temperature
[13 empty] | 566 | Main Shaft Front Bearing High Temperature Warning
[13 empty] | 567 | Main Shaft Rear Bearing Extreme Temperature
[13 empty] | 568 | Main Shaft Rear Bearing High Temperature Warning
[13 empty] | 571 | Generator Slip Rings High Temperature Warning
[13 empty] | 572 | Converter Coolant In The Input Of The Cooling Circuit High Temperature Warning
[13 empty] | 573 | Converter Control Module High Temperature Warning
[13 empty] | 574 | Converter Upper Radiator High Temperature Warning
[13 empty] | 575 | Converter Lower Radiator High Temperature Warning
[13 empty] | 576 | Generator Fans Failure Too Long
[13 empty] | 577 | Slipping Rings Fan Or Heating Resistor Failure
[13 empty] | 600 | ATD Filters Out Of Range
[13 empty] | 601 | ATD Saturation Alarm
[13 empty] | 602 | Maximum Time For Stator Connection
[13 empty] | 603 | Maximum Time For Stator Disconnection
[13 empty] | 609 | Speed Reference Not Allowed
[13 empty] | 610 | Permission Denied For Star and Delta Connection
[13 empty] | 611 | Maximum Time To Make A Connection Change In The Stator
[13 empty] | 612 | Maximum Time For Connection In Star
[13 empty] | 613 | Maximum Time For Connection In Delta
[13 empty] | 615 | Accelerometer Vibration Alarm
[13 empty] | 616 | Rotor Block
[13 empty] | 619 | Calibration Test Not Executed Or NO OK
[13 empty] | 621 | Maximum Synchronization Time
[13 empty] | 622 | Non-Consecutive Accelerometer Reading Error
[13 empty] | 623 | Accelerometer Measurement Error
[13 empty] | 624 | LTD Saturation Alarm
[13 empty] | 625 | LTD Filters Out Of Range
[13 empty] | 626 | Azimuth Inductive Sensor Failure
[13 empty] | 627 | Grid Frequency Disturbance - Inertia Emulation Activation
[13 empty] | 628 | Pitch LTD Saturation Alarm
[13 empty] | 629 | Pitch LTD Filters Out Of Range
[13 empty] | 700 | PLC-Converter Communication Error
[13 empty] | 702 | Sonic Communication Failure
[13 empty] | 703 | Remote Control Com Failure
[13 empty] | 707 | SMP Communication Failure
[13 empty] | 708 | Pause Due To Remote Control Communications Failure
[13 empty] | 711 | Sonic Error.NRG Operates
[13 empty] | 715 | Wattmeter Failure
[13 empty] | 716 | NRG.Error Sonic Operates
[13 empty] | 717 | NRG Failure
[13 empty] | 718 | 24 Hours With NRG Or Too Many Sonic-NRG Changes
[13 empty] | 719 | Cup Anemometer Failure Warning
[13 empty] | 720 | Sonic Failure, Cup Anemometer Operates Warning
[13 empty] | 721 | Wind Vane Failure Warning
[13 empty] | 722 | Wind Vane Failure Alarm
[13 empty] | 728 | WTG PLC-GENSET Communication Failure
[13 empty] | 800 | Pitch Drive Error
[13 empty] | 802 | Low Pitch Value In Stop Mode (2 Cylinders)
[13 empty] | 803 | Low Pitch Value In Stop Mode (1 Cylinder)
[13 empty] | 804 | Difference Between 2 Blades Too High
[13 empty] | 806 | Possible Ice On Blades
[13 empty] | 811 | Non-Consecutive Pitch Reading Errors
[13 empty] | 812 | Blade Position Meas. Error
[13 empty] | 813 | Low Pressure Of Emergency Accumulators
[13 empty] | 814 | ACP Alarm
[13 empty] | 816 | Blade Bearing Lubrication System Problem
[13 empty] | 817 | Blade Bearing Lubrication System Error
[13 empty] | 819 | Low Grease Level For Blade Bearings
[13 empty] | 820 | Blade Bearing Lubrication Failure
[13 empty] | 823 | Incorrect Emergency Speed
[13 empty] | 825 | Blade Bearing Lubrication Failure Too Long
[13 empty] | 828 | Pitch Rate Error During TPR Shutdown
[13 empty] | 829 | Pitch Electrovalves Power Supply Failure
[13 empty] | 900 | Top Emergency Button
[13 empty] | 901 | Emergency Series Feedback Error
[13 empty] | 902 | Opening Series For Test
[13 empty] | 903 | Authoriz Person In Turbine
[13 empty] | 904 | Presence Of Unauth. Person In Turbine
[13 empty] | 905 | Controlled Emergency Series Battery Failure
[13 empty] | 906 | Trigger Of FG230 Or FM230
[13 empty] | 907 | Emergency Series HUB Trigger
[13 empty] | 908 | Ground Emergency Button
[13 empty] | 911 | Change Emergency-Local Reset
[13 empty] | 912 | Change Emergency-Remote Control Reset
[13 empty] | 913 | Change Stop Local Reset
[13 empty] | 914 | Change Stop-Remote Control Reset
[13 empty] | 915 | Change Pause-Local Reset
[13 empty] | 916 | Change Pause-Remote Control Reset
[13 empty] | 917 | Basic Data Incorrectly Entered
[13 empty] | 932 | WTG Shutdown Requested By Flight Manager
[13 empty] | 1800 | Not Performing Pole Trial
[13 empty] | 1801 | Pole Test Missing
[13 empty] | 1812 | Lock And Send To Run: Frequency Out Of Range
[13 empty] | 1813 | DTD Filter Alarm 1
[13 empty] | 1814 | DTD Filter Alarm 2
[13 empty] | 1816 | Speed Filters Alarm Torque Loop
[13 empty] | 1817 | Speed Filters Alarm Speed Loop
[13 empty] | 1818 | Switchgear Contactor Trigger
[13 empty] | 1819 | RC Filter Failure
[13 empty] | 1820 | RC Filter
[13 empty] | 1821 | Heating Protection Triggered
[13 empty] | 1822 | Discussion Due To Low Temperature
[13 empty] | 1823 | Coolant Confirmation Failure
[13 empty] | 1824 | Trafo Fan Thermal Relay
[13 empty] | 1825 | Automatics Not Ok
[13 empty] | 1828 | Trigger Of Overvoltage Protection
[13 empty] | 1832 | Reactive Power Production By The Converter Is Limited
[13 empty] | 1833 | Transformer Fan Control Failure
[13 empty] | 1834 | MV Switch Trip From Arc Detector
[13 empty] | 1835 | MV Switch Trip From Neutral Detector
[13 empty] | 1836 | MV Switch Trip From Transformer Fuses
[13 empty] | 1835 | MV Switch Trip From CCU
[13 empty] | 1838 | Lock And Send To Run: Voltage Out Of Range
[13 empty] | 1840 | Transformer Over Voltage Operation Time Exceeded
[13 empty] | 1874 | Latched Control Relay Fault Alarm
[13 empty] | 1875 | MV Switch Trip From TOP Cabinet Button Or Latched Control Relay Handle
[13 empty] | 1876 | The MV Switch Gear Has Not Tripped
[13 empty] | 1878 | Smoke Sensor In Ground
[13 empty] | 1879 | Warning Auxiliary Leakage Current
[13 empty] | 1880 | Alarm Auxiliary Leakage Current
[13 empty] | 1882 | Transformer Auxiliary Services Fuses
[13 empty] | 1885 | External Temperature Multiplexer Failure
[13 empty] | 1893 | Trafo Fan Thermal Relay Triggered Too Long
[13 empty] | 1894 | Automatic Secondaries Not OK Too Long
[13 empty] | 1895 | Auxiliary Leakage Current Too Long
[13 empty] | 1896 | Low Grid Voltage
[13 empty] | 1899 | Automatic Secondaries Not OK
[13 empty] | 1909 | WT UY Ground Power Supply Circuit Breaker Tripped
[13 empty] | 1910 | WT UY Top Power Supply Circuit Breaker Tripped
[13 empty] | 1911 | WT UY Ground KMGS1 Contactor Failure
[13 empty] | 1912 | WT UY Top KMGS2 Contactor Failure
[13 empty] | 1913 | WT UY Ground Switch Selector Active
[13 empty] | 1914 | WT UY Impulse Relay activation (TL) Failure
[13 empty] | 1915 | WT UY System Is Initializing
[13 empty] | 1917 | Discrepancy Between Emergency Indicators
[13 empty] | 2100 | PLC Voltage Recovery
[13 empty] | 2101 | Counter Card Failure
[13 empty] | 2102 | PLC Module Failure
[13 empty] | 2106 | Temp. Measurement Module Failure
[13 empty] | 2107 | Initialization Failure
[13 empty] | 2113 | Cycle Time Exceeded
[13 empty] | 2114 | Analogue Card Failure
[13 empty] | 2115 | Change Auto Reset->Remote
[13 empty] | 2116 | Change Remote Reset->Local
[13 empty] | 2117 | PLC Internal Error Warning
[13 empty] | 2118 | Bus Error - Interbus Failure
[13 empty] | 2119 | CTRL Error - Processor Stopped
[13 empty] | 2120 | Optical Fiber Low Quality
[13 empty] | 2124 | Flash Writing Error
[13 empty] | 2125 | Flash Writing Limit Exveeded
[13 empty] | 2129 | PLC Data Incorrect
[13 empty] | 2130 | GATEWAY Configuration Error
[13 empty] | 2131 | UPS Fail
[13 empty] | 2198 | Temperature Measurement Module Failure
[13 empty] | 5200 | Magnetothermic Trigger Of The Line Protection
[13 empty] | 5201 | Magnetothermic Trigger Of The Stator Protection
[13 empty] | 5202 | Stator Contactor Failure
[13 empty] | 5203 | Heating/Coolant Thermal Magnetic Failure
[13 empty] | 5204 | Emergency Series Not OK
[13 empty] | 5205 | Magnetothermic Of The Stator Protection Failure Or Door Open
[13 empty] | 5206 | Brake Chopper Failure
[13 empty] | 5207 | Excessive Temperature Of Coolant At The Input Of The Cooling Circuit
[13 empty] | 5208 | Brake Chopper IGBT 2 Failure
[13 empty] | 5209 | Brake Chopper Driver 2 Failure
[13 empty] | 5210 | Failure Of The Contactor's Rotor Power
[13 empty] | 5212 | Bus Preload Protection Thermal Relay Failure
[13 empty] | 5213 | Crowbar Overvoltage
[13 empty] | 5213 | Crowbar Not OK
[13 empty] | 5215 | Rotor Protection Thermal Magnetic Failure
[13 empty] | 5216 | Grid Voltage Failure
[13 empty] | 5217 | Frequency Failure
[13 empty] | 5218 | Phase Rotation Failure
[13 empty] | 5219 | Coolant Of The Coolant Circuit Failure
[13 empty] | 5220 | Encoder Not OK
[13 empty] | 5221 | Encoder Suynchronism Error
[13 empty] | 5222 | Speed Read Incorrectly
[13 empty] | 5223 | Brake Chopper Driver 1 Failure
[13 empty] | 5224 | Out Of Range In Slippage
[13 empty] | 5225 | Fault In Analog Electronic Power Supply
[13 empty] | 5227 | Fault In 24v Power Supply
[13 empty] | 5228 | Preload Failure
[13 empty] | 5229 | Data Capture Failure In Test
[13 empty] | 5230 | Test Rotor Movement
[13 empty] | 5231 | Discrepancy In power Regulation
[13 empty] | 5232 | Error In Phase R Of The Rectifier
[13 empty] | 5233 | Error In Phase S Of The Rectifier
[13 empty] | 5234 | Error In Phase T Of The Rectifier
[13 empty] | 5235 | Rectifier Driver Error (Edriver) Or Of The Inverter (Edriver I)
[13 empty] | 5236 | Error In Phase R Of The Inverter
[13 empty] | 5237 | Error In Phase S Of The Inverter
[13 empty] | 5238 | Error In Phase T Of The Inverter
[13 empty] | 5239 | Rectifier Phase R Overcurrent
[13 empty] | 5240 | Rectifier Phase S Overcurrent
[13 empty] | 5241 | Excess Current Phase R Of Rotor
[13 empty] | 5242 | Excess Current Phasse S Of Rotor
[13 empty] | 5243 | Excess Current Phase R Of Stator
[13 empty] | 5244 | Excess Current Phase S Of Stator
[13 empty] | 5245 | Bus Over Voltage Detected By Hardware
[13 empty] | 5246 | Bus Over Voltage Detected By Software
[13 empty] | 5247 | Low Bus Voltage
[13 empty] | 5248 | Active Crowbar IGBT Errors
[13 empty] | 5249 | Earth Leakage In The Stator
[13 empty] | 5250 | Brake Chopper IGBT 1 Failure
[13 empty] | 5251 | Active Crowbar Failure
[13 empty] | 5252 | Actuator Of The Coolant Circuit Failure
[13 empty] | 5253 | Excess Temperature In The Radiator's Hardware
[13 empty] | 5254 | Excessive Temperature Of The Control Module
[13 empty] | 5255 | Overtemperature Thermostats Of The Cabinet Cubicle
[13 empty] | 5256 | Excessive Ambient Temperature Of The Converter
[13 empty] | 5257 | Excess Ambient Temperature In The Stator Thermo-Magnet
[13 empty] | 5258 | Excessive Temperature Of The Upper Radiator
[13 empty] | 5259 | Excessive Temperature Of The Lower Radiator
[13 empty] | 5260 | Overheating In The Grid's Inductance
[13 empty] | 5261 | Overheating In The Rectifiers Inductance
[13 empty] | 5262 | Overheating In The Inverter's Inductance
[13 empty] | 5263 | CAN Communication Failure
[13 empty] | 5264 | High Transient Grid Harmonic Distortion
[13 empty] | 5265 | High Grid Harmonic Voltage Distortion
[13 empty] | 5266 | Power Transformer Internal Failure
[13 empty] | 5267 | 690V Circuits Ground Faults
[13 empty] | 5268 | High Grid Harmonic Distortion
[13 empty] | 5269 | High Grid Harmonic Distortion Warning
[13 empty] | 5270 | Earth Leakage In The Rotor
[13 empty] | 2509 | SF6 Breaker Fault
[13 empty] | CE100001 | Manual Stop
[13 empty] | CE100002 | Major BD - Blade
[13 empty] | CE100003 | Major BD - Transformer
[13 empty] | CE100004 | Major BD - Generator
[13 empty] | CE100005 | Major BD - Gearbox
[13 empty] | CE100006 | Major BD - Main Bearing
[13 empty] | CE100007 | Transmission Line Related work
[13 empty] | CE100008 | General Work Stoppage
[13 empty] | CE100009 | Major BD - Power Cable
[13 empty] | CE100011 | Major BD - DFIG
[13 empty] | CE100012 | Major BD - Foundation
[13 empty] | CE100013 | Theft
[13 empty] | CE100010 | Manual Stop - Preventive Maintenance Activity
[13 empty] | CE100014 | Manual Stop - Audit
[13 empty] | CE100015 | Manual Stop - Safety Related
[13 empty] | CE100016 | Manual Stop - Blade Cleaning
[13 empty] | CE100017 | UPS breakdown
[13 empty] | CE100018 | SF6 and HV side

## WTG Reactive Power
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44
Date | Financial Year | Calendar Year | Month Year | G01 | G02 | G03 | G04 | G05 | G06 | G07 | G08 | G09 | G10 | G11 | G12 | G13 | G14 | G15 | G16 | G17 | G18 | G19 | G20 | G21 | G22 | G23 | G25 | G26 | G27 | G28 | G29 | G30 | G31 | G32 | G33 | G34 | G35 | G36 | G37 | G38 | G39 | G40 | Total Reactive Power (kVArh) | Column1
2025-03-29 | 2025 | 2025 | 2025-03-01 | [39 empty] | 0
2025-03-30 | 2025 | 2025 | 2025-03-01 | [39 empty] | 0
2025-03-31 | 2025 | 2025 | 2025-03-01 | 2411.487 | 891.6197 | 1879.9699 | 874.2626 | 880.4713 | 636.2265 | 372.8833 | 641.519 | 906.0887 | 2260.394 | 383.091 | 377.6865 | 2175.7978 | 1993.9216 | 1758.4657 | 2234.1107 | 1964.6707 | 2190.6098 | 441.9792 | 670.5095 | 1570.8376 | 1180.1707 | 1761.4244 | 999.7058 | 1757.046 | 677.2118 | 333.82 | 0 | 1635.0767 | 0 | 1909.0221 | 573.7749 | 742.5826 | 1713.1288 | 1709.3145 | -8.1559 | 2496.8774 | 783.4712 | 2020.958 | 47802.0313
2025-04-01 | 2026 | 2025 | 2025-04-01 | 2322.1235 | 880.1081 | 2078.5867 | 914.5695 | 945.8455 | 637.9924 | 748.219 | 777.1361 | 722.7967 | 2126.2865 | 729.4575 | 657.0716 | 2115.474 | 1806.1052 | 1979.2855 | 2123.0251 | 2192.0195 | 2109.1038 | 708.9222 | 620.7477 | 1738.0668 | 1166.9419 | 1782.3727 | 1210.9576 | 1935.1739 | 703.6288 | 551.5907 | 0 | 1232.2376 | 0 | 1843.691 | 697.056 | 823.1135 | 1362.145 | 1053.6383 | -3.8062 | 2338.3736 | 824.4841 | 1543.8372 | 47998.3787
2025-04-02 | 2026 | 2025 | 2025-04-01 | 2637.2192 | 1097.0692 | 2227.8404 | 923.7416 | 938.2683 | 1297.9406 | 808.4993 | 1289.6567 | 1427.063 | 2544.821 | 855.7841 | 904.2495 | 2402.8842 | 2695.9843 | 2431.9187 | 2122.2456 | 2309.7017 | 3275.5917 | 852.7877 | 1820.6796 | 2426.154 | 491.6329 | 2794.5914 | 1860.9447 | 2885.9037 | 1148.8614 | 1083.9293 | 0 | 2614.3132 | 0 | 823.2844 | 1097.612 | 1182.3387 | 2677.0025 | 2930.4442 | -5.806 | 3280.2777 | 1180.1252 | 2777.1324 | 66112.6877
2025-04-03 | 2026 | 2025 | 2025-04-01 | 2246.2058 | 999.8763 | 2226.0732 | 964.8013 | 886.5267 | 310.4275 | 434.6387 | 696.4918 | 942.5248 | 2164.418 | 725.648 | 756.4623 | 2369.339 | 2369.0812 | 2227.3578 | 2284.8013 | 2242.396 | 2133.4678 | 722.128 | 931.433 | 2229.9002 | 1362.7018 | 2262.5322 | 1064.164 | 2218.1311 | 670.9676 | 487.7805 | 0 | 1891.0717 | 0 | 1266.729 | 571.0981 | 344.8436 | 2159.9289 | 2167.4363 | -0.62418 | 1525.8424 | 613.2425 | 2334.2306 | 51804.0749
2025-04-04 | 2026 | 2025 | 2025-04-01 | 2041.9638 | 388.9551 | 2124.023 | 127.742 | 918.1217 | 83.6738 | 539.6643 | 499.3578 | 465.2299 | 2022.4022 | 707.9753 | 724.6901 | 1884.747 | 2115.7314 | 2050.154 | 111.5131 | 2221.5963 | 2113.498 | 747.0538 | 736.9155 | 2084.2164 | 1478.5472 | 1975.4358 | 888.9653 | 2010.7748 | 476.8457 | 507.5768 | 0 | 2028.1925 | 0 | 1944.1858 | 451.6692 | 93.7413 | 1857.9228 | 2067.6373 | -2.4657 | 2138.7909 | 441.671 | 2200.4018 | 45269.1172
2025-04-05 | 2026 | 2025 | 2025-04-01 | 1876.6226 | 2453.1843 | 1792.9483 | 2211.351 | 1764.4128 | 1666.3205 | 1910.9348 | 2018.7832 | 1635.8613 | 1357.6993 | 1716.0805 | 1716.427 | 1822.3371 | 1593.3717 | 1444.4012 | 0 | 2021.6525 | 2078.9627 | 2082.5695 | 2121.1535 | 2701.0488 | 2515.4811 | 2220.8267 | 1930.8067 | 2949.735 | 1640.4508 | 2557.8496 | 0 | 2950.7668 | 0 | 2629.0589 | 2369.3689 | 2486.7691 | 3025.3162 | 2939.6089 | 3016.1374 | 2372.7201 | 0 | 2927.9752 | 76518.994
2025-04-06 | 2026 | 2025 | 2025-04-01 | 1810.3475 | 373.706 | 2124.0686 | 120.3521 | 0 | 372.111 | 634.795 | 349.298 | 288.821 | 1822.0809 | 624.6403 | 638.458 | 1762.0523 | 1807.978 | 1542.3584 | 0 | 2143.8435 | 1837.3247 | 647.149 | 444.1512 | 2084.2164 | 1478.5472 | 1975.4358 | 888.9653 | 2010.7748 | 476.8457 | 507.5768 | 0 | 2028.1925 | 0 | 1944.1858 | 451.6692 | 93.7413 | 1857.9228 | 2067.6373 | 2145 | 2138.7909 | 441.671 | 2200.4018 | 44135.1102
2025-04-07 | 2026 | 2025 | 2025-04-01 | 1891.7158 | 673.008 | 2044.8962 | 479.9239 | 258.3903 | 586.396 | 540.2957 | 662.5477 | 457.5581 | 2060.9708 | 700.0054 | 762.4624 | 2042.7492 | 2029.6797 | 1694.1446 | 0 | 2094.7339 | 2125.3133 | 720.4764 | 1004.4539 | 944.4695 | 597.1967 | 720.9387 | 16.8658 | 702.9906 | 165.7304 | -68.1872 | 0 | 725.9068 | 0 | 702.3264 | 85.5696 | 155.8761 | 729.0436 | 764.1744 | -1.6386 | 720.3451 | 710 | 759.7323 | 31261.0615
2025-04-08 | 2026 | 2025 | 2025-04-01 | 1910.5437 | 389.2763 | 2048.9178 | -47.8144 | 623.8795 | 358.6271 | 561.9942 | 296.7837 | 178.8487 | 1892.529 | 266.9529 | 603.1785 | 1810.7305 | 1934.8088 | 1567.0379 | 0 | 2093.95 | 2007.1697 | 428.6528 | 384.5257 | 2064.975 | 1452.7388 | 1940.4757 | 51.5167 | 1888.164 | 376.72 | 142.9288 | 0 | 1956.1253 | 0 | 1867.137 | 107.2599 | 385.3045 | 1937.8512 | 2011.0095 | -9.7052 | 2026.7745 | 15.593 | 2099.0948 | 39624.5559
2025-04-09 | 2026 | 2025 | 2025-04-01 | 616.5324 | 137.0467 | 567.342 | 36.0524 | 752.842 | 203.4382 | 198.4896 | 242.9161 | 0 | 437.3383 | 202.867 | 495.0081 | 941.903 | 2566.5919 | 1891.3042 | 427.4053 | 2182.9024 | 2428.2554 | 393.7 | 582.7216 | 2179.2963 | 1444.5757 | 2370.1045 | 687.6252 | 2398.027 | 874.1103 | 818.9967 | 0 | 2465.8407 | 0 | 2208.1021 | 636.8648 | 906.724 | 2368.0593 | 2513.1359 | -4.2376 | 2640.5093 | 0 | 2760.133 | 42572.5238
2025-04-10 | 2026 | 2025 | 2025-04-01 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 0 | 129 | 0 | 129 | 129 | 129 | 129 | 129 | -5 | 129 | 129 | 129 | 4639 | No scada available server OS failed-reading as per billing meter
2025-04-11 | 2026 | 2025 | 2025-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-04-12 | 2026 | 2025 | 2025-04-01 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 0 | 99 | 0 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 3663 | No scada available server OS failed-reading as per billing meter
2025-04-13 | 2026 | 2025 | 2025-04-01 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 0 | 129 | 0 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 4773 | No scada available server OS failed-reading as per billing meter
2025-04-14 | 2026 | 2025 | 2025-04-01 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 0 | 129 | 0 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 4773 | No scada available server OS failed-reading as per billing meter
2025-04-15 | 2026 | 2025 | 2025-04-01 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 0 | 129 | 0 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 4773 | No scada available server OS failed-reading as per billing meter
2025-04-16 | 2026 | 2025 | 2025-04-01 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 0 | 97 | 0 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 3589 | No scada available server OS failed-reading as per billing meter
2025-04-17 | 2026 | 2025 | 2025-04-01 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 0 | 97 | 0 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 3589 | No scada available server OS failed-reading as per billing meter
2025-04-18 | 2026 | 2025 | 2025-04-01 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 0 | 194.5946 | 0 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 194.5946 | 7200 | No scada available server OS failed-reading as per billing meter
2025-04-19 | 2026 | 2025 | 2025-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-04-20 | 2026 | 2025 | 2025-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-04-21 | 2026 | 2025 | 2025-04-01 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 0 | 227 | 0 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 8399 | No scada available server OS failed-reading as per billing meter
2025-04-22 | 2026 | 2025 | 2025-04-01 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 0 | 227 | 0 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 8399 | No scada available server OS failed-reading as per billing meter
2025-04-23 | 2026 | 2025 | 2025-04-01 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 194 | 195 | 195 | 193 | 195 | 185 | 195 | 195 | 195 | 0 | 195 | 0 | 193 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 7200 | No scada available server OS failed-reading as per billing meter
2025-04-24 | 2026 | 2025 | 2025-04-01 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 0 | 259 | 0 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 9583 | No scada available server OS failed-reading as per billing meter
2025-04-25 | 2026 | 2025 | 2025-04-01 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 65 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 2405 | No scada available server OS failed-reading as per billing meter
2025-04-26 | 2026 | 2025 | 2025-04-01 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 65 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 2405 | No scada available server OS failed-reading as per billing meter
2025-04-27 | 2026 | 2025 | 2025-04-01 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 0 | 227 | 0 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 8399 | No scada available server OS failed-reading as per billing meter
2025-04-28 | 2026 | 2025 | 2025-04-01 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 0 | 162 | 0 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 5994 | No scada available server OS failed-reading as per billing meter
2025-04-29 | 2026 | 2025 | 2025-04-01 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 0 | 195 | 0 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 7215 | No scada available server OS failed-reading as per billing meter
2025-04-30 | 2026 | 2025 | 2025-04-01 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 65 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 2405 | No scada available server OS failed-reading as per billing meter
2025-05-01 | 2026 | 2025 | 2025-05-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-05-02 | 2026 | 2025 | 2025-05-01 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 0 | 162 | 0 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 5994 | No scada available server OS failed-reading as per billing meter
2025-05-03 | 2026 | 2025 | 2025-05-01 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 0 | 32 | 0 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 1184 | No scada available server OS failed-reading as per billing meter
2025-05-04 | 2026 | 2025 | 2025-05-01 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 65 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 2405 | No scada available server OS failed-reading as per billing meter
2025-05-05 | 2026 | 2025 | 2025-05-01 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 0 | 162 | 162 | 0 | 162 | 0 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 5832 | No scada available server OS failed-reading as per billing meter
2025-05-06 | 2026 | 2025 | 2025-05-01 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 72 | 98 | 98 | 0 | 98 | 0 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 3600 | No scada available server OS failed-reading as per billing meter
2025-05-07 | 2026 | 2025 | 2025-05-01 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 0 | 130 | 0 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 4810 | No scada available server OS failed-reading as per billing meter
2025-05-08 | 2026 | 2025 | 2025-05-01 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 0 | 97 | 0 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 3589 | No scada available server OS failed-reading as per billing meter
2025-05-09 | 2026 | 2025 | 2025-05-01 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 0 | 422 | 0 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 15614 | No scada available server OS failed-reading as per billing meter
2025-05-10 | 2026 | 2025 | 2025-05-01 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 0 | 291 | 0 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 291 | 10767 | No scada available server OS failed-reading as per billing meter
2025-05-11 | 2026 | 2025 | 2025-05-01 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 0 | 162 | 0 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 5994 | No scada available server OS failed-reading as per billing meter
2025-05-12 | 2026 | 2025 | 2025-05-01 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 0 | 162 | 162 | 0 | 162 | 0 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 5832 | No scada available server OS failed-reading as per billing meter
2025-05-13 | 2026 | 2025 | 2025-05-01 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 0 | 227 | 0 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 8399 | No scada available server OS failed-reading as per billing meter
2025-05-14 | 2026 | 2025 | 2025-05-01 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 0 | 324 | 0 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 324 | 0 | 11664 | No scada available server OS failed-reading as per billing meter
2025-05-15 | 2026 | 2025 | 2025-05-01 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 0 | 162 | 0 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 5994 | No scada available server OS failed-reading as per billing meter
2025-05-16 | 2026 | 2025 | 2025-05-01 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 0 | 130 | 0 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 4810 | No scada available server OS failed-reading as per billing meter
2025-05-17 | 2026 | 2025 | 2025-05-01 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 0 | 98 | 0 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 3626 | No scada available server OS failed-reading as per billing meter
2025-05-18 | 2026 | 2025 | 2025-05-01 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 0 | 227 | 0 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 8399 | No scada available server OS failed-reading as per billing meter
2025-05-19 | 2026 | 2025 | 2025-05-01 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 0 | 519 | 0 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 19203 | No scada available server OS failed-reading as per billing meter
2025-05-20 | 2026 | 2025 | 2025-05-01 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 0 | 195 | 0 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 7215 | No scada available server OS failed-reading as per billing meter
2025-05-21 | 2026 | 2025 | 2025-05-01 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 0 | 130 | 0 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 4810 | No scada available server OS failed-reading as per billing meter
2025-05-22 | 2026 | 2025 | 2025-05-01 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 0 | 552 | 0 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 552 | 20424 | No scada available server OS failed-reading as per billing meter
2025-05-23 | 2026 | 2025 | 2025-05-01 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 0 | 487 | 0 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 487 | 18019 | No scada available server OS failed-reading as per billing meter
2025-05-24 | 2026 | 2025 | 2025-05-01 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 0 | 163 | 0 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 6031 | No scada available server OS failed-reading as per billing meter
2025-05-25 | 2026 | 2025 | 2025-05-01 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 0 | 163 | 0 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 6031 | No scada available server OS failed-reading as per billing meter
2025-05-26 | 2026 | 2025 | 2025-05-01 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 0 | 260 | 0 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 9620 | No scada available server OS failed-reading as per billing meter
2025-05-27 | 2026 | 2025 | 2025-05-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-05-28 | 2026 | 2025 | 2025-05-01 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 0 | 130 | 0 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 4810 | No scada available server OS failed-reading as per billing meter
2025-05-29 | 2026 | 2025 | 2025-05-01 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 1221 | No scada available server OS failed-reading as per billing meter
2025-05-30 | 2026 | 2025 | 2025-05-01 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 1221 | No scada available server OS failed-reading as per billing meter
2025-05-31 | 2026 | 2025 | 2025-05-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-01 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-02 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-03 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-04 | 2026 | 2025 | 2025-06-01 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 65 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 2405 | No scada available server OS failed-reading as per billing meter
2025-06-05 | 2026 | 2025 | 2025-06-01 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 0 | 163 | 0 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 6031 | No scada available server OS failed-reading as per billing meter
2025-06-06 | 2026 | 2025 | 2025-06-01 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 1221 | No scada available server OS failed-reading as per billing meter
2025-06-07 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-08 | 2026 | 2025 | 2025-06-01 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 1221 | No scada available server OS failed-reading as per billing meter
2025-06-09 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-10 | 2026 | 2025 | 2025-06-01 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 0 | 98 | 0 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 3626 | No scada available server OS failed-reading as per billing meter
2025-06-11 | 2026 | 2025 | 2025-06-01 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 1221 | No scada available server OS failed-reading as per billing meter
2025-06-12 | 2026 | 2025 | 2025-06-01 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 0 | 163 | 0 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 6031 | No scada available server OS failed-reading as per billing meter
2025-06-13 | 2026 | 2025 | 2025-06-01 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 0 | 390 | 0 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 14430 | No scada available server OS failed-reading as per billing meter
2025-06-14 | 2026 | 2025 | 2025-06-01 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 0 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 0 | 486 | 0 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 486 | 17496 | No scada available server OS failed-reading as per billing meter
2025-06-15 | 2026 | 2025 | 2025-06-01 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 65 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 2340 | No scada available server OS failed-reading as per billing meter
2025-06-16 | 2026 | 2025 | 2025-06-01 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 0 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 0 | 32 | 0 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 1152 | No scada available server OS failed-reading as per billing meter
2025-06-17 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-18 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-19 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-20 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-21 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-22 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-23 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-24 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-25 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-26 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-27 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-28 | 2026 | 2025 | 2025-06-01 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 0 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 0 | 64.8649 | 0 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 2335.1351 | No scada available server OS failed-reading as per billing meter
2025-06-29 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-06-30 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-07-01 | 2026 | 2025 | 2025-07-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-07-02 | 2026 | 2025 | 2025-07-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-07-03 | 2026 | 2025 | 2025-07-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-07-04 | 2026 | 2025 | 2025-07-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-07-05 | 2026 | 2025 | 2025-07-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-07-06 | 2026 | 2025 | 2025-07-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-07-07 | 2026 | 2025 | 2025-07-01 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 0 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 0 | 64.8649 | 0 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 64.8649 | 2335.1351 | No scada available server OS failed-reading as per billing meter
2025-07-08 | 2026 | 2025 | 2025-07-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-07-09 | 2026 | 2025 | 2025-07-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No scada available server OS failed-reading as per billing meter
2025-07-10 | 2026 | 2025 | 2025-07-01 | 32.43 | 32.43 | 32.43 | 32.43 | 32.43 | 32.43 | 32.43 | 32.43 | 32 | 32.43 | 32.43 | 32.43 | 32.43 | 32.43 | 32.43 | 32.43 | 0 | 32.43 | 32.43 | 32.43 | 32.43 | 32.43 | 32.43 | 32.43 | 32.43 | 32 | 32.43 | 0 | 32.43 | 0 | 32.43 | 32.43 | 32.43 | 32.43 | 32 | 32 | 32 | 32 | 32 | 1164.47 | No scada available server OS failed-reading as per billing meter
2025-07-11 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-12 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-13 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-14 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-15 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-16 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-17 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-18 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-19 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-20 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-21 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-22 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-23 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-24 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-25 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-26 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-27 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-28 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-29 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-30 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-07-31 | 2026 | 2025 | 2025-07-01 | [39 empty] | 0
2025-08-01 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-02 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-03 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-04 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-05 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-06 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-07 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-08 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-09 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-10 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-11 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-12 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-13 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-14 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-15 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-16 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-17 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-18 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-19 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-20 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-21 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-22 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-23 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-24 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-25 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-26 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-27 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-28 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-29 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-30 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-08-31 | 2026 | 2025 | 2025-08-01 | [39 empty] | 0
2025-09-01 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-02 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-03 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-04 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-05 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-06 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-07 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-08 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-09 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-10 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-11 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-12 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-13 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-14 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-15 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-16 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-17 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-18 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-19 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-20 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-21 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-22 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-23 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-24 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-25 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-26 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-27 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-28 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-29 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-09-30 | 2026 | 2025 | 2025-09-01 | [39 empty] | 0
2025-10-01 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-02 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-03 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-04 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-05 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-06 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-07 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-08 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-09 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-10 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-11 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-12 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-13 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-14 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-15 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-16 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-17 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-18 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-19 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-20 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-21 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-22 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-23 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-24 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-25 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-26 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-27 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-28 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-29 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-30 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-10-31 | 2026 | 2025 | 2025-10-01 | [39 empty] | 0
2025-11-01 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-02 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-03 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-04 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-05 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-06 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-07 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-08 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-09 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-10 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-11 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-12 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-13 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-14 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-15 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-16 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-17 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-18 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-19 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-20 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-21 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-22 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-23 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-24 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-25 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-26 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-27 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-28 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-29 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-11-30 | 2026 | 2025 | 2025-11-01 | [39 empty] | 0
2025-12-01 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-02 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-03 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-04 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-05 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-06 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-07 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-08 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-09 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-10 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-11 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-12 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-13 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-14 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-15 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-16 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-17 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-18 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-19 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-20 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-21 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-22 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-23 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-24 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-25 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-26 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-27 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-28 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-29 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-30 | 2026 | 2025 | 2025-12-01 | [39 empty] | 0
2025-12-31 | 2026 | 2025 | 2025-12-01 | 2411.487 | 891.6197 | 1879.9699 | 874.2626 | 880.4713 | 636.2265 | 372.8833 | 641.519 | 906.0887 | 2260.394 | 383.091 | 377.6865 | 2175.7978 | 1993.9216 | 1758.4657 | 2234.1107 | 1964.6707 | 2190.6098 | 441.9792 | 670.5095 | 1570.8376 | 1180.1707 | 1761.4244 | 999.7058 | 1757.046 | 677.2118 | 333.82 | 0 | 1635.0767 | 0 | 1909.0221 | 573.7749 | 742.5826 | 1713.1288 | 1709.3145 | -8.1559 | 2496.8774 | 783.4712 | 2020.958 | 47802.0313
Formulas:
Month Year = [Date]-DAY([Date])+1
Date = [Date, row above]+1

## PM record
Suzlon Mirkala Yearly maintenance schedule Plan Vs Actual Year 2023-24
Sr No | Turbine No | Generator Make | Turbine ID | 6 Months Schedule Date | Completed Date | 12 Months Schedule Date | Completed Date | 18 Months Schedule Date | Completed Date | 24 Months Schedule Date | Completed Date | 30 Months Schedule Date | Completed Date | 36 Months Schedule Date | Completed Date | 42 Months Schedule Date | Completed Date | 48 Months Schedule Date | Completed Date | 54 Month PM Schedule Date | Completed Date | 60Month PM Schedule Date | Completed Date | 66 Month PM Schedule Date | Completed Date | 72 Month PM Schedule Date | Completed Date | 78 Month PM Schedule Date | Completed Date | 84 Month PM Schedule Date | Completed Date | 90 Month PM Schedule Date | Completed Date | 96 Month PM Schedule Date | Completed Date | Delay in Days | 102 Month PM Schedule Date | Completed Date | Delay in Days | 108 Month PM Schedule Date(Suzlon) Day-1 | 108 Month PM Schedule Date(Suzlon) Day-2 | Completed Date Day1 | Completed Date Day2 | Delay in Days | PM delay resons | 114 Month Half year PM Schedule Date | Completed Date | Delay in Days | 120 Month YPM Schedule Date (Day-01) | 120 Month YPM Schedule Date (Day-02) | 120 Month YPM Completed Date (Day-01) | 120 Month YPM Completed Date (Day-02) | Delay in Days | PM delay resons | WTG | 126 Month Plan Date HYPM | 126 Month Actual Date HYPM | Diff. Days | Adherence | Remarks
1 | G 24 | ABB | 100261368 | 2014-12-19 | 2014-12-19 | 2015-06-19 | 2015-06-22 | 2015-12-19 | 2015-12-19 | 2016-06-19 | 2016-07-14 | 2016-12-19 | 2016-12-26 | 2017-06-19 | 2017-06-23 | 2017-12-19 | 2018-01-11 | 2018-06-19 | 2018-08-06 | 2018-12-14 | 2019-01-28 | 2019-09-07 | 2019-09-04 | 2020-03-05 | 2020-04-25 | 2020-09-01 | 2020-12-22 | 2021-03-01 | 2021-03-26 | 2021-09-01 | 2022-05-19 | 2022-03-01 | 2022-05-19 | 2022-09-01 | 2022-09-24 | 23 | 2023-02-28 | 2023-03-14 | 14 | 2023-10-10 | 2023-10-11 | 2023-12-16 | 2023-12-18 | 68 |  | 2024-03-01 | 2024-03-04 | 3
2 | G 25 | ABB | 100261366 | 2014-12-21 | 2014-12-21 | 2015-06-21 | 2015-08-01 | 2015-12-21 | 2015-12-21 | 2016-06-21 | 2016-07-21 | 2016-12-21 | 2016-12-28 | 2017-06-21 | 2017-06-24 | 2017-12-21 | 2018-01-08 | 2018-06-21 | 2018-08-08 | 2018-12-16 | 2019-01-29 | 2019-09-08 | 2019-09-07 | 2020-03-06 | 2020-04-30 | 2020-09-02 | 2020-12-18 | 2021-03-02 | 2021-03-27 | 2021-09-01 | 2022-05-20 | 2022-03-02 | 2022-05-20 | 2022-09-01 | 2022-09-25 | 24 | 2023-02-28 | 2023-03-17 | 17 | 2023-10-12 | 2023-10-13 | 2023-10-10 | 2023-10-31 | 18 |  | 2024-03-02 | 2024-03-05 | 3 | 2024-11-05 | 2024-11-06 | 2024-11-06 | 2024-11-07 | 1 |  | PWEGPL25 | 2025-04-26 | 2025-04-26 | 0 | 100 | Delay due to payment issue
3 | G 27 | ABB | 100261367 | 2014-12-23 | 2014-12-23 | 2015-06-23 | 2015-06-17 | 2015-12-23 | 2015-12-22 | 2016-06-23 | 2016-07-22 | 2016-12-23 | 2016-12-27 | 2017-06-23 | 2017-07-07 | 2017-12-23 | 2018-01-09 | 2018-06-23 | 2018-08-14 | 2018-12-18 | 2019-01-30 | 2019-09-09 | 2019-09-16 | 2020-03-07 | 2020-05-01 | 2020-09-03 | 2020-12-17 | 2021-03-03 | 2021-03-28 | 2021-09-03 | 2022-05-19 | 2022-03-03 | 2022-05-19 | 2022-09-03 | 2022-09-26 | 23 | 2023-03-02 | 2023-03-21 | 19 | 2023-10-14 | 2023-10-15 | 2023-12-18 | 2023-12-16 | 62 |  | 2024-03-04 | 2024-03-06 | 2 | 2024-11-07 | 2024-11-08 | 2024-11-08 | 2024-11-09 | 1 |  | PWEGPL27 | 2025-04-27 | 2025-04-27 | 0 | 100
4 | G 31 | CANTERY | 100261341 | 2014-12-25 | 2014-12-25 | 2015-06-25 | 2015-06-21 | 2015-12-25 | 2015-12-26 | 2016-06-25 | 2016-07-23 | 2016-12-25 | 2017-01-02 | 2017-06-25 | 2017-07-19 | 2017-12-25 | 2018-01-12 | 2018-06-25 | 2018-08-24 | 2018-12-20 | 2019-02-02 | 2019-09-10 | 2019-09-17 | 2020-03-08 | 2020-05-02 | 2020-09-04 | 2020-12-25 | 2021-03-04 | 2021-03-29 | 2021-09-03 | 2022-05-21 | 2022-03-04 | 2022-05-21 | 2022-09-03 | 2022-09-27 | 24 | 2023-03-02 | 2023-03-24 | 22 | 2023-10-16 | 2023-10-17 | 2023-10-19 | 2023-11-18 | 32 | ROW at site office (11-10-23 to 16-10-23) for crane movement to G20 & Multiple activities at site BD & G20 restoration work.(20-10-23 to 27-10-2023) /limited manpower at site | 2024-03-05 | 2024-03-08 | 3 | 2024-11-09 | 2024-11-11 | 2024-11-18 | 2024-11-19 | 8 | Manual stop for blade bush gap issue retrofitting work on 14-Dec-24 @15:02 | PWEGPL31 | 2025-06-07 |  | -45815 | -50788.8889 | Major B.D Blade root bush gap issue in blade no 596
5 | G 30 | CANTERY | 100261340 | 2014-12-27 | 2014-12-27 | 2015-06-27 | 2015-06-27 | 2015-12-27 | 2015-12-28 | 2016-06-27 | 2016-07-25 | 2016-12-27 | 2017-01-03 | 2017-06-27 | 2017-07-08 | 2017-12-27 | 2018-01-13 | 2018-06-27 | 2018-08-17 | 2018-12-22 | 2019-02-01 | 2019-09-11 | 2019-09-18 | 2020-03-09 | 2020-05-03 | 2020-09-05 | 2020-12-24 | 2021-03-05 | 2021-03-30 | 2021-09-06 | 2022-05-23 | 2022-03-05 | 2022-05-23 | 2022-09-06 | 2022-09-28 | 22 | 2023-03-05 | 2023-03-27 | 22 | 2023-10-18 | 2023-10-19 | 2023-10-18 | 2023-11-07 | 19 | ROW at site office (11-10-23 to 16-10-23) for crane movement to G20 & Multiple activities at site BD & G20 restoration work.(20-10-23 to 27-10-2023) /limited manpower at site | 2024-03-06 | 2024-03-09 | 3 | 2024-11-12 | 2024-11-13 | 2024-11-23 | 2024-11-24 | 11 |  | PWEGPL30 | 2025-04-28 | 2025-04-28 | 0 | 100
6 | G 29 | CANTERY | 100261337 | 2015-01-01 | 2015-01-01 | 2015-07-01 | 2015-07-10 | 2016-01-01 | 2015-12-29 | 2016-07-01 | 2016-07-26 | 2017-01-01 | 2017-01-19 | 2017-07-01 | 2017-07-10 | 2018-01-01 | 2018-01-15 | 2018-07-01 | 2018-08-16 | 2018-12-27 | 2019-01-31 | 2019-09-12 | 2019-09-21 | 2020-03-10 | 2020-05-04 | 2020-09-06 | 2020-12-23 | 2021-03-08 | 2021-03-31 | 2021-09-06 | 2022-05-24 | 2022-03-07 | 2022-05-24 | 2022-09-06 | 2022-09-29 | 23 | 2023-03-05 | 2023-03-28 | 23 | 2023-10-20 | 2023-10-21 | 2023-10-17 | 2023-11-06 | 16 | ROW at site office (11-10-23 to 16-10-23) for crane movement to G20 & Multiple activities at site BD & G20 restoration work.(20-10-23 to 27-10-2023) /limited manpower at site | 2024-03-07 | 2024-03-11 | 4 | 2024-11-14 | 2024-11-15 | 2024-11-21 | 2024-11-22 | 7 |  | PWEGPL29 | 2025-06-08 |  | -45816 | -50790 | Major B.D Blade root bush gap issue blade 636 de erected
7 | G 34 | ABB | 100261333 | 2015-01-04 | 2015-01-04 | 2015-07-04 | 2015-08-01 | 2016-01-04 | 2016-01-04 | 2016-07-04 | 2016-07-30 | 2017-01-04 | 2017-01-23 | 2017-07-04 | 2017-08-02 | 2018-01-04 | 2018-01-16 | 2018-07-04 | 2018-08-18 | 2018-12-30 | 2019-02-04 | 2019-09-13 | 2019-09-23 | 2020-03-11 | 2020-05-13 | 2020-09-07 | 2020-12-26 | 2021-03-09 | 2021-04-01 | 2021-09-08 | 2022-06-02 | 2022-03-08 | 2022-06-02 | 2022-09-08 | 2022-10-01 | 23 | 2023-03-07 | 2023-03-30 | 23 | 2023-10-22 | 2023-10-23 | 2023-11-16 | 2023-11-17 | 25 |  | 2024-03-08 | 2024-03-12 | 4 | 2024-11-16 | 2024-11-18 | 2024-11-10 | 2024-11-11 | -7 |  | PWEGPL28 | 2025-04-29 | 2025-04-29 | 0 | 100
8 | G 33 | ABB | 100261334 | 2015-01-07 | 2015-01-07 | 2015-07-07 | 2015-07-20 | 2016-01-07 | 2016-01-06 | 2016-07-07 | 2016-08-01 | 2017-01-07 | 2017-01-24 | 2017-07-07 | 2017-08-04 | 2018-01-07 | 2018-01-17 | 2018-07-07 | 2018-08-20 | 2019-01-02 | 2019-02-06 | 2019-09-14 | 2019-09-25 | 2020-03-12 | 2020-05-14 | 2020-09-08 | 2020-12-27 | 2021-03-10 | 2021-04-02 | 2021-09-08 | 2022-06-03 | 2022-03-09 | 2022-06-03 | 2022-09-08 | 2022-10-02 | 24 | 2023-03-07 | 2023-03-31 | 24 | 2023-10-24 | 2023-10-25 | 2023-10-27 | 2023-11-08 | 14 | ROW at site office (11-10-23 to 16-10-23) for crane movement to G20 & Multiple activities at site BD & G20 restoration work.(20-10-23 to 27-10-2023) /limited manpower at site | 2024-03-09 | 2024-03-15 | 6 | 2024-11-19 | 2024-11-20 | 2024-11-12 | 2024-11-14 | -6 |  | PWEGPL34 | 2025-04-30 | 2025-04-30 | 0 | 100
9 | G 35 | ABB | 100261372 | 2015-01-08 | 2015-01-08 | 2015-07-08 | 2015-08-04 | 2016-01-08 | 2016-01-08 | 2016-07-08 | 2016-08-03 | 2017-01-08 | 2017-01-21 | 2017-07-08 | 2017-08-06 | 2018-01-08 | 2018-01-18 | 2018-07-08 | 2018-08-21 | 2019-01-03 | 2019-02-07 | 2019-09-15 | 2019-09-26 | 2020-03-13 | 2020-05-06 | 2020-09-09 | 2020-12-28 | 2021-03-11 | 2021-04-03 | 2021-09-10 | 2022-06-06 | 2022-03-10 | 2022-06-06 | 2022-09-10 | 2022-10-03 | 23 | 2023-03-09 | 2023-04-04 | 26 | 2023-10-26 | 2023-10-27 | 2023-11-20 | 2023-11-21 | 25 |  | 2024-03-11 | 2024-03-19 | 8 | 2024-11-21 | 2024-11-22 | 2024-11-25 | 2024-11-26 | 4 |  | PWEGPL33 | 2025-05-01 | 2025-05-01 | 0 | 100
10 | G 36 | ABB | 100261371 | 2015-01-10 | 2015-01-10 | 2015-07-10 | 2015-08-02 | 2016-01-10 | 2016-01-10 | 2016-07-10 | 2016-08-05 | 2017-01-10 | 2017-01-30 | 2017-07-10 | 2017-08-07 | 2018-01-10 | 2018-01-19 | 2018-07-10 | 2018-08-27 | 2019-01-05 | 2019-02-08 | 2019-09-16 | 2019-09-27 | 2020-03-14 | 2020-05-14 | 2020-09-10 | 2021-01-01 | 2021-03-12 | 2021-04-04 | 2021-09-10 | 2022-06-05 | 2022-03-11 | 2022-06-05 | 2022-09-10 | 2022-10-05 | 25 | 2023-03-09 | 2023-04-03 | 25 | 2023-10-28 | 2023-10-29 | 2023-11-22 | 2023-11-23 | 25 |  | 2024-03-12 | 2024-03-20 | 8 | 2024-11-23 | 2024-11-25 | 2024-11-28 | 2024-11-29 | 4 |  | PWEGPL35 | 2025-05-02 | 2025-05-03 | 1 | 100 | delay due to Pitch seal replaced in G-07
11 | G 37 | CANTERY | 100261338 | 2015-01-13 | 2015-01-13 | 2015-07-13 | 2015-08-05 | 2016-01-13 | 2016-01-13 | 2016-07-13 | 2016-08-12 | 2017-01-13 | 2017-01-25 | 2017-07-13 | 2017-08-08 | 2018-01-13 | 2018-01-20 | 2018-07-13 | 2018-08-22 | 2019-01-08 | 2019-02-09 | 2019-09-17 | 2019-09-28 | 2020-03-15 | 2020-05-15 | 2020-09-11 | 2020-12-29 | 2021-03-15 | 2021-04-06 | 2021-09-13 | 2022-06-09 | 2022-03-12 | 2022-06-09 | 2022-09-13 | 2022-10-06 | 23 | 2023-03-12 | 2023-04-05 | 24 | 2023-10-30 | 2023-10-31 | 2023-11-24 | 2023-11-25 | 25 |  | 2024-03-13 | 2024-03-21 | 8 | 2024-11-26 | 2024-11-27 | 2024-11-30 | 2024-12-01 | 4 |  | PWEGPL36 | 2025-05-03 | 2025-05-04 | 1 | 100
12 | G 38 | ABB | 100261403 | 2015-01-20 | 2015-01-20 | 2015-07-20 | 2015-07-20 | 2016-01-20 | 2016-01-17 | 2016-07-20 | 2016-08-13 | 2017-01-20 | 2017-02-02 | 2017-07-20 | 2017-08-09 | 2018-01-20 | 2018-01-25 | 2018-07-20 | 2018-09-01 | 2019-01-15 | 2019-02-11 | 2019-09-18 | 2019-09-29 | 2020-03-16 | 2020-05-15 | 2020-09-12 | 2020-12-30 | 2021-03-16 | 2021-04-08 | 2021-09-13 | 2022-06-10 | 2022-03-14 | 2022-06-10 | 2022-09-13 | 2022-10-08 | 25 | 2023-03-12 | 2023-04-06 | 25 | 2023-11-01 | 2023-11-02 | 2023-11-25 | 2023-11-24 | 22 |  | 2024-03-14 | 2024-03-23 | 9 | 2024-11-28 | 2024-11-29 | 2024-12-02 | 2024-12-03 | 4 |  | PWEGPL37 | 2025-05-04 | 2025-05-06 | 2 | 100 | Delay due to Pitch cylinder replacement work in G-26
13 | G 39 | ABB | 100261374 | 2015-01-22 | 2015-01-22 | 2015-07-22 | 2015-07-18 | 2016-01-22 | 2016-01-21 | 2016-07-22 | 2016-08-14 | 2017-01-22 | 2017-02-03 | 2017-07-22 | 2017-08-10 | 2018-01-22 | 2018-01-27 | 2018-07-22 | 2018-09-03 | 2019-01-17 | 2019-02-12 | 2019-09-19 | 2019-09-30 | 2020-03-17 | 2020-05-16 | 2020-09-13 | 2020-10-13 | 2021-03-17 | 2021-04-21 | 2021-09-15 | 2022-06-11 | 2022-03-15 | 2022-06-11 | 2022-09-15 | 2022-10-09 | 24 | 2023-03-14 | 2023-04-07 | 24 | 2023-11-03 | 2023-11-04 | 2023-11-27 | 2023-11-28 | 24 |  | 2024-03-15 | 2024-03-22 | 7 | 2024-11-30 | 2024-12-02 | 2024-12-06 | 2024-12-07 | 5 | 02 days Maint activity stopped for G-25 PM pending completion work. | PWEGPL38 | 2025-05-05 | 2025-05-07 | 2 | 100
14 | G 40 | CANTERY | 100261336 | 2015-01-28 | 2015-01-28 | 2015-07-28 | 2015-08-17 | 2016-01-28 | 2016-01-29 | 2016-07-28 | 2016-08-16 | 2017-01-28 | 2017-01-28 | 2017-07-28 | 2017-08-24 | 2018-01-28 | 2018-01-29 | 2018-07-28 | 2018-11-05 | 2019-01-23 | 2019-02-13 | 2019-09-20 | 2019-10-02 | 2020-03-18 | 2020-05-05 | 2020-09-14 | 2020-10-14 | 2021-03-18 | 2021-04-09 | 2021-09-15 | 2022-06-12 | 2022-03-16 | 2022-06-12 | 2022-09-15 | 2022-10-10 | 25 | 2023-03-14 | 2023-04-12 | 29 | 2023-11-05 | 2023-11-06 | 2023-11-29 | 2023-11-27 | 21 | PM team has taken weekly off and they continue to PM work on Sunday | 2024-03-16 | 2024-03-25 | 9 | 2024-12-03 | 2024-12-04 | 2024-12-08 | 2024-12-10 | 6 | PM postpone to 10-12-24 due to N2 Not avail. | PWEGPL39 | 2025-05-06 | 2025-05-15 | 9 | 100 | Delayed due to 8 employess GWO training(for 4days)
15 | G 26 | ABB | 100261404 | 2015-01-30 | 2015-01-30 | 2015-07-30 | 2015-08-19 | 2016-01-30 | 2016-01-30 | 2016-07-30 | 2016-08-18 | 2017-01-30 | 2017-02-04 | 2017-07-30 | 2017-08-11 | 2018-01-30 | 2018-01-30 | 2018-07-30 | 2018-11-06 | 2019-01-25 | 2019-02-20 | 2019-09-21 | 2019-10-03 | 2020-03-19 | 2020-05-16 | 2020-09-15 | 2020-10-20 | 2021-03-19 | 2021-04-19 | 2021-09-17 | 2022-06-13 | 2022-03-17 | 2022-06-13 | 2022-09-17 | 2022-10-11 | 24 | 2023-03-16 | 2023-04-14 | 29 | 2023-11-07 | 2023-11-08 | 2023-11-30 | 2023-12-01 | 23 | PM team-02 employees on leave. Date- 28-11-23 | 2024-03-18 | 2024-03-26 | 8 | 2024-12-05 | 2024-12-06 | 2024-12-12 | 2024-12-15 | 9 | PM Postpone 2day to 15-12-24 ,due to G-33 Pitch seal replacement work & team busy in 14-12-24 &G-26 B.D | PWEGPL40 | 2025-05-08 | 2025-05-16 | 8 | 100
16 | G 32 | ABB | 100261369 | 2015-02-03 | 2015-02-03 | 2015-08-03 | 2015-08-22 | 2016-02-03 | 2016-02-03 | 2016-08-03 | 2016-08-19 | 2017-02-03 | 2017-02-10 | 2017-08-03 | 2017-08-28 | 2018-02-03 | 2018-02-12 | 2018-08-03 | 2018-11-07 | 2019-01-29 | 2019-02-21 | 2019-09-22 | 2019-10-06 | 2020-03-20 | 2020-05-17 | 2020-09-16 | 2020-10-21 | 2021-03-22 | 2021-04-20 | 2021-09-17 | 2022-06-14 | 2022-03-18 | 2022-06-14 | 2022-09-17 | 2022-10-14 | 27 | 2023-03-16 | 2023-04-17 | 32 | 2023-11-09 | 2023-11-10 | 2023-12-01 | 2023-12-02 | 22 | PM team-02 employees on leave. Date- 29-11-23 | 2024-03-19 | 2024-03-16 | 3 | 2024-12-07 | 2024-12-09 | 2024-12-16 | 2024-12-17 | 8 | Delay due to G-26 ,pin ball hardware damaged from 12-dec-24 to 18-dec-24 | PWEGPL26 | 2025-05-09 | 2025-05-17 | 8 | 100
17 | G 28 | CANTERY | 100261339 | 2015-02-04 | 2015-02-04 | 2015-08-04 | 2015-08-28 | 2016-02-04 | 2016-02-04 | 2016-08-04 | 2016-08-23 | 2017-02-04 | 2017-02-09 | 2017-08-04 | 2017-09-01 | 2018-02-04 | 2018-03-07 | 2018-08-04 | 2018-11-08 | 2019-01-30 | 2019-02-26 | 2019-09-23 | 2019-10-07 | 2020-03-21 | 2020-05-12 | 2020-09-17 | 2020-12-20 | 2021-03-23 | 2021-04-10 | 2021-09-20 | 2022-05-28 | 2022-03-19 | 2022-05-28 | 2022-09-20 | 2022-09-30 | 10 | 2023-03-19 | 2023-03-29 | 10 | 2023-11-11 | 2023-11-12 | 2023-10-11 | 2023-11-04 | -8 | ROW at site office (11-10-23 to 16-10-23) for crane movement to G20 | 2024-03-20 | 2024-03-27 | 7 | 2024-12-10 | 2024-12-11 | 2024-12-20 | 2024-12-21 | 10 |  | PWEGPL32 | 2025-05-10 | 2025-05-18 | 8 | 100
18 | G 21 | CANTERY | 100261410 | 2015-03-30 | 2015-03-30 | 2015-09-30 | 2015-06-19 | 2016-03-30 | 2016-03-22 | 2016-09-30 | 2016-10-17 | 2017-03-30 | 2017-04-01 | 2017-09-29 | 2017-09-25 | 2018-03-30 | 2018-06-19 | 2018-09-29 | 2018-11-09 | 2019-03-25 | 2019-03-06 | 2019-09-24 | 2019-10-09 | 2020-03-22 | 2020-05-17 | 2020-09-18 | 2020-10-18 | 2021-03-24 | 2021-04-11 | 2021-09-20 | 2022-06-27 | 2022-03-21 | 2022-06-27 | 2022-09-20 | 2022-10-15 | 25 | 2023-03-19 | 2023-04-18 | 30 | 2023-11-13 | 2023-11-14 | 2023-12-05 | 2023-12-06 | 22 |  | 2024-03-22 | 2024-03-29 | 7 | 2024-12-12 | 2024-12-13 | 2025-03-11 | 2025-03-15 | 92 | Major B.D(Stopped due to Blade Root gap) on 15-July-24@12:51 ,Repair work completed on 15-Feb-25 | PWEGPL21 | 2025-05-11 | 2025-05-20 | 9 | 100
19 | G 22 | ABB | 100261399 | 2015-03-31 | 2015-03-31 | 2015-09-30 | 2015-09-03 | 2016-03-31 | 2016-03-29 | 2016-10-01 | 2016-10-04 | 2017-03-31 | 2017-04-04 | 2017-09-30 | 2017-09-26 | 2018-03-31 | 2018-06-21 | 2018-09-30 | 2018-11-10 | 2019-03-26 | 2019-03-07 | 2019-09-25 | 2019-10-12 | 2020-03-23 | 2020-05-19 | 2020-09-19 | 2020-12-15 | 2021-03-25 | 2021-04-22 | 2021-09-22 | 2022-07-05 | 2022-03-22 | 2022-07-05 | 2022-09-22 | 2022-10-16 | 24 | 2023-03-21 | 2023-04-19 | 29 | 2023-11-15 | 2023-11-16 | 2023-12-04 | 2023-12-05 | 19 |  | 2024-03-23 | 2024-03-30 | 7 | 2024-12-14 | 2024-12-16 | 2024-12-27 | 2024-12-28 | 12 |  | PWEGPL22 | 2025-05-12 | 2025-05-19 | 7 | 100
20 | G 23 | ABB | 100261392 | 2015-04-01 | 2015-04-01 | 2015-10-01 | 2015-06-22 | 2016-04-01 | 2016-03-31 | 2016-10-02 | 2016-10-18 | 2017-04-01 | 2017-04-07 | 2017-10-01 | 2017-11-14 | 2018-04-01 | 2018-06-22 | 2018-10-01 | 2018-11-12 | 2019-03-27 | 2019-02-15 | 2019-09-26 | 2019-10-13 | 2020-03-24 | 2020-05-18 | 2020-09-20 | 2020-12-16 | 2021-03-26 | 2021-04-24 | 2021-09-22 | 2022-06-28 | 2022-03-23 | 2022-06-28 | 2022-09-22 | 2022-12-20 | 89 | 2023-03-21 | 2023-05-06 | 46 | 2023-11-17 | 2023-11-18 | 2024-03-13 | 2024-03-14 | 117 | WTG under major BM blade crack | 2024-03-25 | 2024-03-14 | 11 | 2024-12-17 | 2024-12-18 | 2024-12-24 | 2024-12-26 | 8 |  | PWEGPL23 | 2025-05-13 | 2025-05-21 | 8 | 100
21 | G 05 | ABB | 100261396 | 2015-04-03 | 2015-04-03 | 2015-10-03 | 2015-10-03 | 2016-04-03 | 2016-04-25 | 2016-10-03 | 2016-10-03 | 2017-04-03 | 2017-04-08 | 2017-10-03 | 2017-11-15 | 2018-04-03 | 2018-06-27 | 2018-10-03 | 2018-11-14 | 2019-03-29 | 2019-03-08 | 2019-09-27 | 2019-10-14 | 2020-03-25 | 2020-04-25 | 2020-09-21 | 2020-12-11 | 2021-03-29 | 2021-04-25 | 2021-09-24 | 2022-06-24 | 2022-03-24 | 2022-06-24 | 2022-09-24 | 2022-12-21 | 88 | 2023-03-23 | 2023-05-07 | 45 | 2023-11-19 | 2023-11-20 | 2023-12-02 | 2023-12-04 | 14 |  | 2024-03-26 | 2024-04-01 | 6 | 2024-12-19 | 2024-12-20 | 2024-12-22 | 2024-12-23 | 3 | Little early taken due to HG temp error & resolved | PWEGPL05 | 2025-05-15 | 2025-05-22 | 7 | 100
22 | G 15 | ABB | 100261393 | 2015-04-05 | 2015-04-05 | 2015-10-05 | 2015-10-05 | 2016-04-05 | 2016-04-04 | 2016-10-05 | 2016-10-05 | 2017-04-05 | 2017-04-10 | 2017-10-05 | 2017-11-16 | 2018-04-05 | 2018-07-01 | 2018-10-05 | 2018-11-16 | 2019-03-31 | 2019-03-09 | 2019-09-28 | 2019-10-15 | 2020-03-26 | 2020-04-26 | 2020-09-22 | 2020-10-22 | 2021-03-30 | 2021-04-26 | 2021-09-24 | 2022-06-20 | 2022-03-25 | 2022-06-20 | 2022-09-24 | 2022-12-22 | 89 | 2023-03-23 | 2023-05-08 | 46 | 2023-11-21 | 2023-11-22 | 2023-12-12 | 2023-12-13 | 21 |  | 2024-03-27 | 2024-04-02 | 6 | 2024-12-21 | 2024-12-23 | 2024-12-29 | 2024-12-30 | 7 |  | PWEGPL15 | 2025-05-16 | 2025-05-23 | 7 | 100
23 | G 16 | ABB | 100261402 | 2015-04-06 | 2015-04-06 | 2015-10-06 | 2015-10-07 | 2016-04-06 | 2016-04-01 | 2016-10-06 | 2016-10-06 | 2017-04-06 | 2017-04-11 | 2017-10-06 | 2017-11-17 | 2018-04-06 | 2018-07-02 | 2018-10-06 | 2018-11-17 | 2019-04-01 | 2019-03-11 | 2019-09-29 | 2019-10-16 | 2020-03-27 | 2020-04-26 | 2020-09-23 | 2020-10-23 | 2021-03-31 | 2021-04-27 | 2021-09-27 | 2022-05-26 | 2022-03-26 | 2022-05-26 | 2022-09-27 | 2022-12-23 | 87 | 2023-03-26 | 2023-05-09 | 44 | 2023-11-23 | 2023-11-24 | 2023-12-13 | 2023-12-12 | 18 |  | 2024-03-29 | 2024-04-03 | 5 | 2024-12-24 | 2024-12-25 | 2025-01-02 | 2025-01-03 | 9 | PM team have taken off on 31/12/24 | PWEGPL16 | 2025-05-17 | 2025-05-24 | 7 | 100
24 | G 17 | ABB | 100261394 | 2015-04-07 | 2015-04-07 | 2015-10-07 | 2015-10-08 | 2016-04-07 | 2016-04-09 | 2016-10-07 | 2016-10-07 | 2017-04-07 | 2017-04-12 | 2017-10-07 | 2017-11-18 | 2018-04-07 | 2018-07-20 | 2018-10-07 | 2018-11-18 | 2019-04-02 | 2019-03-12 | 2019-09-30 | 2019-10-17 | 2020-03-28 | 2020-04-27 | 2020-09-24 | 2020-10-24 | 2021-04-01 | 2021-04-29 | 2021-09-27 | 2022-05-18 | 2022-03-28 | 2022-05-18 | 2022-09-27 | 2022-12-24 | 88 | 2023-03-26 | 2023-05-28 | 63 | 2023-11-25 | 2023-11-26 | 2023-12-10 | 2023-12-11 | 15 |  | 2024-03-30 | 2024-03-18 | 12 | 2024-12-26 | 2024-12-27 | 2025-01-04 | 2025-01-06 | 10 | PM team have taken off on 01/01/25 & on dated 05/01/25 PM cancelled due to vehicle issue | PWEGPL17 | 2025-05-18 | 2025-05-25 | 7 | 100
25 | G 18 | ABB | 100261254 | 2015-04-08 | 2015-04-08 | 2015-10-08 | 2015-10-09 | 2016-04-08 | 2016-04-15 | 2016-10-08 | 2016-10-08 | 2017-04-08 | 2017-04-13 | 2017-10-08 | 2017-11-20 | 2018-04-08 | 2018-07-16 | 2018-10-08 | 2018-11-19 | 2019-04-03 | 2019-03-13 | 2019-10-01 | 2019-10-18 | 2020-03-29 | 2020-04-27 | 2020-09-25 | 2020-12-07 | 2021-04-02 | 2021-04-30 | 2021-09-29 | 2022-07-01 | 2022-03-29 | 2022-07-01 | 2022-09-29 | 2022-12-25 | 87 | 2023-03-28 | 2023-05-29 | 62 | 2023-11-27 | 2023-11-28 | 2023-12-09 | 2023-12-11 | 13 | Team-01 assigned Yaw drive replacement work at G-15 | 2024-04-01 | 2024-04-04 | 3 | 2024-12-28 | 2024-12-30 | 2025-01-07 | 2025-01-08 | 9 |  | PWEGPL18 | 2025-05-19 | 2025-05-26 | 7 | 100
26 | G 19 | ABB | 100261400 | 2015-04-10 | 2015-04-10 | 2015-10-10 | 2015-10-10 | 2016-04-10 | 2016-04-16 | 2016-10-10 | 2016-10-09 | 2017-04-10 | 2017-04-17 | 2017-10-10 | 2017-11-21 | 2018-04-10 | 2018-07-19 | 2018-10-10 | 2018-11-20 | 2019-04-05 | 2019-03-14 | 2019-10-02 | 2019-10-20 | 2020-03-30 | 2020-04-28 | 2020-09-26 | 2020-12-04 | 2021-04-05 | 2021-05-04 | 2021-09-29 | 2022-06-17 | 2022-03-30 | 2022-06-17 | 2022-09-29 | 2022-12-26 | 88 | 2023-03-28 | 2023-05-29 | 62 | 2023-11-29 | 2023-11-30 | 2023-12-07 | 2023-12-08 | 8 |  | 2024-04-02 | 2024-04-05 | 3 | 2024-12-31 | 2025-01-01 | 2025-01-10 | 2025-01-11 | 10 | on dated 09-Jan-25 ,PM cancelled due to G-18 PM Pending point Closing work | PWEGPL19 | 2025-05-20 | 2025-05-26 | 6 | 100
27 | G 20 | ABB | 100261395 | 2015-04-27 | 2015-04-27 | 2015-10-27 | 2015-10-27 | 2016-04-27 | 2016-04-07 | 2016-10-27 | 2016-10-10 | 2017-04-27 | 2017-04-27 | 2017-10-27 | 2017-11-22 | 2018-04-27 | 2018-07-17 | 2018-10-27 | 2018-11-25 | 2019-04-22 | 2019-03-16 | 2019-10-03 | 2019-10-21 | 2020-03-31 | 2020-04-28 | 2020-09-27 | 2020-12-09 | 2021-04-06 | 2021-05-05 | 2021-10-01 | 2022-06-30 | 2022-03-31 | 2022-06-30 | 2022-10-01 | 2022-12-27 | 87 | 2023-03-30 | 2023-05-30 | 61 | 2023-12-01 | 2023-12-02 | 2023-12-06 | 2023-12-07 | 5 |  | 2024-04-03 | 2024-04-06 | 3 | 2025-01-02 | 2025-01-03 | 2025-01-12 | 2025-01-13 | 10 |  | PWEGPL20 | 2025-05-22 | 2025-05-27 | 5 | 100
28 | G 14 | CANTERY | 100261409 | 2015-04-29 | 2015-04-29 | 2015-10-29 | 2015-10-28 | 2016-04-29 | 2016-04-07 | 2016-10-29 | 2016-10-12 | 2017-04-29 | 2017-04-29 | 2017-10-29 | 2017-11-27 | 2018-04-29 | 2018-07-23 | 2018-10-29 | 2018-11-26 | 2019-04-24 | 2019-04-03 | 2019-10-04 | 2019-10-22 | 2020-04-01 | 2020-04-29 | 2020-09-28 | 2020-10-28 | 2021-04-07 | 2021-04-15 | 2021-10-01 | 2022-07-04 | 2022-04-01 | 2022-07-04 | 2022-10-01 | 2022-12-28 | 88 | 2023-03-30 | 2023-05-30 | 61 | 2023-12-03 | 2023-12-04 | 2023-12-15 | 2023-12-14 | 10 |  | 2024-04-04 | 2024-04-08 | 4 | 2025-01-04 | 2025-01-06 | 2025-01-14 | 2025-01-20 | 14 | on the date 15-01-25 PM Team Taken w-off | PWEGPL14 | 2025-05-23 | 2025-05-28 | 5 | 100
29 | G 13 | CANTERY | 100261219 | 2015-04-30 | 2015-04-30 | 2015-10-30 | 2015-10-29 | 2016-04-30 | 2016-04-11 | 2016-10-30 | 2016-11-25 | 2017-04-30 | 2017-04-30 | 2017-10-30 | 2017-11-28 | 2018-04-30 | 2018-07-24 | 2018-10-30 | 2018-11-27 | 2019-04-25 | 2019-04-04 | 2019-10-05 | 2019-10-23 | 2020-04-02 | 2020-04-29 | 2020-09-29 | 2020-12-02 | 2021-04-08 | 2021-05-06 | 2021-10-04 | 2022-07-03 | 2022-04-02 | 2022-07-03 | 2022-10-04 | 2022-12-29 | 86 | 2023-04-02 | 2023-05-31 | 59 | 2023-12-05 | 2023-12-06 | 2023-12-14 | 2023-12-15 | 9 |  | 2024-04-05 | 2024-04-09 | 4 | 2025-01-07 | 2025-01-08 | 2025-01-21 | 2025-01-22 | 14 | PM Postpone to 20-01-24,due to recreational(Sports) event as per sidhu's mail communication | PWEGPL13 | 2025-05-24 | 2025-05-29 | 5 | 100
30 | G 12 | ABB | 100261370 | 2015-05-04 | 2015-05-04 | 2015-11-04 | 2015-10-30 | 2016-05-04 | 2016-05-02 | 2016-11-04 | 2016-10-13 | 2017-05-04 | 2017-05-22 | 2017-11-04 | 2017-11-23 | 2018-05-04 | 2018-07-31 | 2018-11-04 | 2018-11-28 | 2019-04-29 | 2019-04-07 | 2019-10-06 | 2019-10-24 | 2020-04-03 | 2020-04-30 | 2020-09-30 | 2020-11-30 | 2021-04-09 | 2021-05-07 | 2021-10-04 | 2022-07-02 | 2022-04-04 | 2022-07-02 | 2022-10-04 | 2022-12-30 | 87 | 2023-04-02 | 2023-05-31 | 59 | 2023-12-07 | 2023-12-08 | 2023-12-20 | 2023-12-19 | 11 |  | 2024-04-06 | 2024-04-10 | 4 | 2025-01-09 | 2025-01-10 | 2025-01-23 | 2025-01-24 | 14 |  | PWEGPL12 | 2025-05-25 | 2025-05-31 | 6 | 100
31 | G 09 | ABB | 100261253 | 2015-05-05 | 2015-05-05 | 2015-11-05 | 2015-11-04 | 2016-05-05 | 2016-05-21 | 2016-11-05 | 2016-10-15 | 2017-05-05 | 2017-05-23 | 2017-11-05 | 2017-11-24 | 2018-05-05 | 2018-07-25 | 2018-11-05 | 2018-11-30 | 2019-04-30 | 2019-04-06 | 2019-10-07 | 2019-10-25 | 2020-04-04 | 2020-05-01 | 2020-10-01 | 2020-10-31 | 2021-04-12 | 2021-05-08 | 2021-10-06 | 2022-06-07 | 2022-04-05 | 2022-06-07 | 2022-10-06 | 2022-12-30 | 85 | 2023-04-04 | 2023-06-01 | 58 | 2023-12-09 | 2023-12-10 | 2023-12-19 | 2023-12-20 | 10 |  | 2024-04-08 | 2024-04-11 | 3 | 2025-01-11 | 2025-01-13 | 2025-01-25 | 2025-01-27 | 14 | PM Cancelled in 26th jan ,Republic day | PWEGPL09 | 2025-05-26 | 2025-06-01 | 6 | 100
32 | G 08 | ABB | 100261398 | 2015-05-07 | 2015-05-07 | 2015-11-07 | 2015-11-05 | 2016-05-07 | 2016-04-23 | 2016-11-07 | 2016-10-19 | 2017-05-07 | 2017-05-24 | 2017-11-07 | 2017-11-25 | 2018-05-07 | 2018-07-26 | 2018-11-07 | 2018-12-01 | 2019-05-02 | 2019-04-09 | 2019-10-08 | 2019-10-26 | 2020-04-05 | 2020-05-02 | 2020-10-02 | 2020-11-22 | 2021-04-13 | 2021-05-09 | 2021-10-06 | 2022-06-29 | 2022-04-06 | 2022-06-29 | 2022-10-06 | 2022-12-31 | 86 | 2023-04-04 | 2023-06-01 | 58 | 2023-12-11 | 2023-12-12 | 2023-12-22 | 2023-12-21 | 9 |  | 2024-04-09 | 2024-04-12 | 3 | 2025-01-14 | 2025-01-15 | 2025-01-28 | 2025-01-29 | 14 |  | PWEGPL08 | 2025-05-27 | 2025-06-02 | 6 | 100
33 | G 06 | CANTERY | 100261216 | 2015-05-08 | 2015-05-08 | 2015-11-08 | 2015-11-06 | 2016-05-08 | 2016-05-08 | 2016-11-08 | 2016-10-20 | 2017-05-08 | 2017-05-25 | 2017-11-08 | 2017-11-29 | 2018-05-08 | 2018-07-27 | 2018-11-08 | 2018-12-02 | 2019-05-03 | 2019-05-21 | 2019-10-09 | 2019-10-28 | 2020-04-06 | 2020-05-03 | 2020-10-03 | 2020-12-21 | 2021-04-14 | 2021-05-10 | 2021-10-08 | 2022-06-26 | 2022-04-07 | 2022-06-26 | 2022-10-08 | 2023-01-02 | 86 | 2023-04-06 | 2023-06-03 | 58 | 2023-12-13 | 2023-12-14 | 2023-12-21 | 2023-12-22 | 8 |  | 2024-04-10 | 2024-04-13 | 3 | 2025-01-16 | 2025-01-17 | 2025-01-30 | 2025-01-31 | 14 |  | PWEGPL06 | 2025-05-29 | 2025-06-05 | 7 | 100
34 | G 03 | ABB | 100261397 | 2015-05-09 | 2015-05-09 | 2015-11-09 | 2015-11-07 | 2016-05-09 | 2016-05-10 | 2016-11-09 | 2016-10-22 | 2017-05-09 | 2017-05-26 | 2017-11-09 | 2017-12-03 | 2018-05-09 | 2018-07-28 | 2018-11-09 | 2018-12-03 | 2019-05-04 | 2019-05-22 | 2019-10-10 | 2019-10-30 | 2020-04-07 | 2020-05-04 | 2020-10-04 | 2020-11-04 | 2021-04-15 | 2021-05-11 | 2021-10-08 | 2022-06-25 | 2022-04-08 | 2022-06-25 | 2022-10-08 | 2023-01-03 | 87 | 2023-04-06 | 2023-06-03 | 58 | 2023-12-15 | 2023-12-16 | 2023-12-25 | 2023-12-23 | 7 |  | 2024-04-11 | 2024-04-15 | 4 | 2025-01-18 | 2025-01-20 | 2025-02-01 | 2025-02-05 | 16 | Day-02 Activity not taken due to N2 Not avail.(& day-2 taken after G-04) | PWEGPL03 | 2025-05-30 | 2025-06-06 | 7 | 100
35 | G 04 | CANTERY | 100261342 | 2015-05-10 | 2015-05-10 | 2015-11-10 | 2015-11-25 | 2016-05-10 | 2016-05-12 | 2016-11-10 | 2016-10-23 | 2017-05-10 | 2017-05-29 | 2017-11-10 | 2017-12-10 | 2018-05-10 | 2018-08-02 | 2018-11-10 | 2018-12-04 | 2019-05-05 | 2019-05-26 | 2019-10-11 | 2019-10-31 | 2020-04-08 | 2020-05-05 | 2020-10-05 | 2020-11-20 | 2021-04-16 | 2021-05-25 | 2021-10-11 | 2022-06-22 | 2022-04-09 | 2022-06-22 | 2022-10-11 | 2023-01-04 | 85 | 2023-04-09 | 2023-06-04 | 56 | 2023-12-17 | 2023-12-18 | 2023-12-23 | 2023-12-25 | 7 |  | 2024-04-12 | 2024-04-16 | 4 | 2025-01-21 | 2025-01-22 | 2025-02-02 | 2025-02-04 | 13 | Day-02 not taken due to Annual Blood donation drive | PWEGPL04 | 2025-05-31 | 2025-06-07 | 7 | 100
36 | G 02 | ABB | 100261373 | 2015-05-11 | 2015-05-11 | 2015-11-11 | 2015-11-08 | 2016-05-11 | 2016-05-13 | 2016-11-11 | 2016-10-24 | 2017-05-11 | 2017-05-30 | 2017-11-11 | 2017-12-09 | 2018-05-11 | 2018-08-01 | 2018-11-11 | 2018-12-05 | 2019-05-06 | 2019-05-27 | 2019-10-12 | 2019-11-04 | 2020-04-09 | 2020-05-06 | 2020-10-06 | 2020-11-18 | 2021-04-19 | 2021-05-26 | 2021-10-11 | 2022-06-21 | 2022-04-11 | 2022-06-21 | 2022-10-11 | 2023-01-05 | 86 | 2023-04-09 | 2023-06-05 | 57 | 2023-12-19 | 2023-12-20 | 2023-12-28 | 2023-12-29 | 9 |  | 2024-04-13 | 2024-04-18 | 5 | 2025-01-23 | 2025-01-24 | 2025-02-06 | 2025-02-07 | 14 |  | PWEGPL02 | 2025-06-01 | 2025-06-10 | 9 | 100
37 | G 07 | CANTERY | 100261361 | 2015-05-16 | 2015-05-16 | 2015-11-16 | 2015-11-09 | 2016-05-16 | 2016-05-20 | 2016-11-16 | 2016-11-28 | 2017-05-16 | 2017-05-31 | 2017-11-16 | 2017-12-13 | 2018-05-16 | 2018-07-30 | 2018-11-16 | 2018-12-06 | 2019-05-11 | 2019-05-28 | 2019-10-13 | 2019-11-02 | 2020-04-10 | 2020-05-07 | 2020-10-07 | 2020-11-11 | 2021-04-20 | 2021-04-13 | 2021-10-13 | 2022-06-19 | 2022-04-12 | 2022-06-19 | 2022-10-13 | 2023-01-06 | 85 | 2023-04-11 | 2023-06-05 | 55 | 2023-12-21 | 2023-12-22 | 2023-12-27 | 2023-12-26 | 4 |  | 2024-04-15 | 2024-04-19 | 4 | 2025-01-25 | 2025-01-27 | 2025-02-08 | 2025-02-10 | 14 |  | PWEGPL07 | 2025-06-02 | 2025-06-11 | 9 | 100
38 | G 01 | CANTERY | 100261335 | 2015-05-17 | 2015-05-17 | 2015-11-17 | 2015-11-10 | 2016-05-17 | 2016-05-16 | 2016-11-17 | 2016-11-29 | 2017-05-17 | 2017-06-01 | 2017-11-17 | 2017-12-14 | 2018-05-17 | 2018-08-03 | 2018-11-17 | 2018-12-07 | 2019-05-12 | 2019-05-30 | 2019-10-14 | 2019-11-03 | 2020-04-11 | 2020-05-09 | 2020-10-08 | 2020-11-08 | 2021-04-21 | 2021-04-14 | 2021-10-13 | 2022-06-18 | 2022-04-13 | 2022-06-18 | 2022-10-13 | 2023-01-07 | 86 | 2023-04-11 | 2023-06-04 | 54 | 2023-12-23 | 2023-12-24 | 2023-12-26 | 2023-12-27 | 3 |  | 2024-04-16 | 2024-04-21 | 5 | 2025-01-28 | 2025-01-29 | 2025-02-11 | 2025-02-12 | 14 |  | PWEGPL01 | 2025-06-03 | 2025-06-12 | 9 | 100
39 | G 10 | ABB | 100261401 | 2015-05-20 | 2015-05-20 | 2015-11-20 | 2015-11-26 | 2016-05-20 | 2016-05-11 | 2016-11-20 | 2016-11-30 | 2017-05-20 | 2017-06-02 | 2017-11-20 | 2017-12-15 | 2018-05-20 | 2018-06-29 | 2018-11-20 | 2018-12-08 | 2019-05-15 | 2019-05-29 | 2019-10-15 | 2019-11-05 | 2020-04-12 | 2020-05-10 | 2020-10-09 | 2020-11-26 | 2021-04-22 | 2021-05-27 | 2021-10-15 | 2022-06-16 | 2022-04-14 | 2022-06-16 | 2022-10-15 | 2023-01-09 | 86 | 2023-04-13 | 2023-06-02 | 50 | 2023-12-25 | 2023-12-26 | 2024-01-02 | 2023-12-31 | 5 |  | 2024-04-17 | 2024-04-22 | 5 | 2025-01-30 | 2025-01-31 | 2025-02-13 | 2025-02-14 | 14 |  | PWEGPL10 | 2025-06-05 | 2025-06-13 | 8 | 100
40 | G 11 | ABB | 100261173 | 2015-05-21 | 2015-05-21 | 2015-11-21 | 2015-10-16 | 2016-05-21 | 2016-05-17 | 2016-11-21 | 2016-12-01 | 2017-05-21 | 2017-06-03 | 2017-11-21 | 2017-12-16 | 2018-05-21 | 2018-06-18 | 2018-11-21 | 2018-12-09 | 2019-05-16 | 2019-04-19 | 2019-10-16 | 2019-11-06 | 2020-04-13 | 2020-05-11 | 2020-10-10 | 2020-11-28 | 2021-04-23 | 2021-05-28 | 2021-10-15 | 2022-06-15 | 2022-04-15 | 2022-06-15 | 2022-10-15 | 2023-01-08 | 85 | 2023-04-13 | 2023-06-02 | 50 | 2023-12-27 | 2023-12-28 | 2023-12-29 | 2023-12-28 | 0 |  | 2024-04-18 | 2024-04-23 | 5 | 2025-02-01 | 2025-02-02 | 2025-02-15 | 2025-02-17 | 15 | PM 1day postpone due to G-37 B.D(HU oil level)so replaced 3nos accumulator | PWEGPL11 | 2025-06-06 | 2025-06-03 | -3 | 100

## Spar Parts Consumption
Sr. No. | Date | Location | Material Name | Quantity | UoM | Remark
1 | 2025-03-29 | G36 | shim (1mm) | 4 | pc
2 | 2025-03-29 | G36 | AI module | 2 | pc
3 | 2025-03-30 | G35 | Yaw motor (Bonifigoli) | 1 | pc
4 | 2025-03-30 | G35 | Yaw contactor (26-30-10) | 1 | pc
5 | 2025-03-30 | G35 | Addon (NC) | 1 | pc
6 | 2025-03-30 | G01 | Yaw motor (Bonifigoli) | 1 | pc
7 | 2025-04-01 | G01 | proportional valve | 1 | pc
8 | 2025-04-01 | G38 | Hydraulic Oil | 5 | liter
9 | 2025-04-01 | G36 | WS251 cable | 1 | pc
10 | 2025-04-01 | G30 | netural relay | 1 | pc
11 | 2025-04-03 | G32 | cab module 9 pin | 1 | pc
12 | 2025-04-03 | G33 | WS240 cable | 1 | pc
13 | 2025-04-04 | G08 | Yaw motor | 1 | pc
14 | 2025-04-07 | G33 | Pitch seal kit | 1 | set
15 | 2025-04-07 | G33 | Gear box oil | 15 | liter
16 | 2025-04-09 | G09 | CCU coolant motor | 1 | pc
17 | 2025-04-09 | G09 | MPCB | 1 | pc
18 | 2025-04-09 | G04 | HU contactor | 1 | pc
19 | 2025-04-10 | G14 | Pitch seal kit | 1 | set
20 | 2025-04-10 | G03 | Gear box hose | 1 | pc
21 | 2025-04-11 | G18 | ACB reley (F5103057) | 1 | set
22 | 2025-04-13 | G26 | Gear box hose | 1 | pc
23 | 2025-04-15 | G39 | Pitch seal kit | 1 | set
24 | 2025-04-15 | G39 | HU contactor (52-30-10) | 1 | pc
25 | 2025-04-15 | G39 | NO addon | 1 | pc
26 | 2025-04-17 | G15 | Proportional valve | 1 | pc
27 | 2025-04-19 | G23 | HU contactor (52-30-10) | 1 | pc
28 | 2025-04-19 | G23 | Pitch seal kit | 1 | pc
29 | 2025-04-19 | G23 | HU oil | 10 | liter
30 | 2025-04-21 | G16 | Brush holder | 3 | pc
31 | 2025-04-21 | G16 | Brush holder spring | 7 | pc
32 | 2025-04-22 | G32 | Transformer fan | 3 | pc
33 | 2025-04-22 | G13 | CCU coolant motor | 1 | pc
34 | 2025-04-23 | G25 | Transformer fan | 3 | pc
35 | 2025-04-24 | G26 | Transformer fan | 3 | pc
36 | 2025-04-24 | G40 | Transformer fan | 5 | pc
37 | 2025-04-25 | G19 | Yaw encoder | 1 | pc
38 | 2025-04-25 | G12 | Plc Flash card | 1 | pc
39 | 2025-04-25 | G39 | Pitch seal kit | 1 | pc
40 | 2025-04-26 | G06 | Transformer fan | 3 | pc
41 | 2025-04-28 | G20 | Accumulator (24 liter) 143 bar | 1 | pc
42 | 2025-04-29 | G07 | OGS garud | 1 | pc
43 | 2025-04-29 | G22 | Hub Main accumulator (143 bar) 24 liter | 1 | pc
44 | 2025-04-29 | G22 | Gear box hose | 1 | pc
45 | 2025-04-29 | G04 | RV 8-10 | 2 | pc
46 | 2025-04-29 | G04 | Electro operate valve | 2 | pc
47 | 2025-04-30 | G07 | Pitch seal kit | 1 | set
48 | 2025-04-30 | G22 | HU Contactor | 1 | pc
49 | 2025-04-30 | G22 | Addon (NO) | 1 | pc
50 | 2025-05-02 | G07 | Pitch seal kit | 1 | set
51 | 2025-05-02 | G07 | HU oil | 15 | liter
52 | 2025-05-02 | G18 | Brush holder | 3 | pc
53 | 2025-05-02 | G18 | Brush holder spring | 8 | pc
54 | 2025-05-03 | G19 | Pitch seal kit | 1 | set
55 | 2025-05-05 | G01 | Yaw Caliper Seal | 2 | set
56 | 2025-05-06 | G26 | Pitch cylinder | 1 | pc
57 | 2025-05-06 | G26 | HU oil | 22 | liter
58 | 2025-05-08 | G22 | MPCB (1.6 to 2.4) | 1 | pc
59 | 2025-05-08 | G22 | Contactor (12-30-10) | 1 | pc
60 | 2025-05-08 | G37 | Pitch seal kit | 1 | pc
61 | 2025-05-09 | G37 | 33k Resistor | 1 | pc
62 | 2025-05-09 | G37 | RC bus filter card | 1 | pc
63 | 2025-05-10 | G04 | PRV-10 valve | 1 | pc
64 | 2025-05-10 | G04 | RV 8-10 valve | 1 | pc
65 | 2025-05-10 | G09 | Propotional Valve | 1 | pc
66 | 2025-05-11 | G23 | Slipring unit | 1 | pc
67 | 2025-05-11 | G23 | CAB Module | 1 | pc
68 | 2025-05-11 | G21 | KC004 contactor | 1 | pc
69 | 2025-05-12 | G23 | CAB Module | 1 | pc
70 | 2025-05-12 | G04 | Needle Valve | 1 | pc
71 | 2025-05-14 | G14 | Single Drive card | 3 | pc
72 | 2025-05-14 | G14 | IGBT | 3 | pc
73 | 2025-05-14 | G14 | 125A Fuse | 2 | pc
74 | 2025-05-14 | G14 | KC002 Contactor | 1 | pc
75 | 2025-05-14 | G14 | 800 HC Resistor | 6 | pc
76 | 2025-05-14 | G04 | Hydraulic pump hose | 1 | pc
77 | 2025-05-15 | G33 | Power supply (10 Amp) | 1 | pc
78 | 2025-05-15 | G33 | Gearbox fan cooling motor | 1 | pc
79 | 2025-05-15 | G40 | Tee - Connector | 1 | set
80 | 2025-05-16 | G04 | Gear box fan cooling motor | 1 | pc
81 | 2025-05-17 | G19 | Pitch cylinder | 1 | pc
82 | 2025-05-17 | G06 | Sealant | 1 | pc
83 | 2025-05-20 | G10 | Lift guide clamp | 4 | pc
84 | 2025-05-21 | G33 | HU oil | 10 | liter
85 | 2025-05-22 | G38 | Carbon brush ABB | 26 | pc
86 | 2025-05-22 | G38 | Carbon brush Spring ABB | 4 | pc
87 | 2025-05-24 | G26 | HU main accumulator (32 liter) | 1 | pc
88 | 2025-05-26 | G25 | MPCB (1.6 to 2.4) | 1 | pc
89 | 2025-05-26 | G30 | HU contactor (52-30-10) | 1 | pc
90 | 2025-05-28 | G33 | Power supply (20 Amp) | 1 | pc
91 | 2025-05-29 | G33 | Gear box damper | 2 | pc
92 | 2025-05-30 | G28 | Proportional valve | 1 | pc
93 | 2025-05-30 | G25 | Coolant pump with motor | 1 | set
94 | 2025-05-30 | G16 | Addon | 1 | pc
95 | 2025-05-30 | G04 | PRV-10 valve | 1 | pc
96 | 2025-05-31 | G25 | Coolant motor | 1 | pc
97 | 2025-06-02 | G04 | HU hose (GP037088 | 1 | pc
98 | 2025-06-02 | G20 | CCU cooling motor | 1 | pc
99 | 2025-06-02 | G33 | Carbon brush | 8 | pc
100 | 2025-06-02 | G35 | carbon brush | 10 | pc
101 | 2025-06-03 | G20 | MPCB (1.6 to 2.4) | 1 | pc
102 | 2025-06-05 | G36 | Carbon brush | 18 | pc
103 | 2025-06-05 | G36 | Carbon brush Spring ABB | 4 | pc
104 | 2025-06-06 | G14 | PRV8-10 valve | 1 | pc
105 | 2025-06-06 | G37 | Accumulator (24 liter) 143 bar | 1 | pc
106 | 2025-06-10 | G23 | Lift guide clamp | 1 | pc
107 | 2025-06-10 | G23 | Carbon brush | 2 | pc
108 | 2025-06-10 | G23 | Carbon brush Spring ABB | 1 | pc
109 | 2025-06-10 | G15 | gadus | 1 | pc
110 | 2025-06-10 | G16 | gadus | 1 | pc
111 | 2025-06-10 | G14 | PRV1-10 valve | 2 | pc
112 | 2025-06-10 | G14 | RV8-10 valve | 2 | pc
113
114 | 2025-06-18 | G07 | MPCB (2.5 to 4.0) | 1 | pc
115 | 2025-06-18 | G07 | Gearbox Pump Hose | 1 | pc
116 | 2025-06-19 | G03 | propotional valve | 1 | pc
117 | 2025-06-19 | G28 | Multiwing fan | 1 | pc
118 | 2025-06-20 | G11 | Light | 1 | pc
119 | 2025-06-20 | G21 | MPCB | 1 | pc
120 | 2025-06-21 | G33 | propotional valve | 1 | pc
121 | 2025-06-21 | G12 | Rotor Handle | 1 | pc
122 | 2025-06-21 | G12 | sealant | 2 | pc
123 | 2025-06-21 | G12 | ABB internal Generator motor | 1 | pc
124 | 2025-06-21 | G10 | ABB carbon brush | 6 | pc
125 | 2025-06-22 | G12 | HU main accumulator (32 liter) | 1 | pc
126 | 2025-06-23 | G20 | Yaw contactor (26-30-10) | 1 | pc
127 | 2025-06-25 | G16 | Transformer fan | 2 | pc
128 | 2025-06-26 | G13 | Transformer fan | 4 | pc
129 | 2025-06-26 | G37 | gearbox manifold to metal hose connecting hose | 1 | pc
130 | 2025-06-26 | G37 | GB Oil | 90 | liter
131 | 2025-06-26 | G03 | LA hammer | 3 | pc
132 | 2025-06-26 | G03 | sealant | 2 | pc
133 | 2025-06-26 | G02 | sealant | 2 | pc
134 | 2025-06-26 | G02 | 80w fan | 1 | pc
135 | 2025-06-27 | G01 | 80w fan | 2 | pc
136 | 2025-06-27 | G01 | gearbox manifold to metal hose connecting hose | 1 | pc
137 | 2025-06-27 | G28 | motor side coupler | 1 | pc
138 | 2025-06-27 | G28 | spider | 1 | pc
139 | 2025-06-27 | G28 | relay base | 1 | pc
140 | 2025-06-28 | G03 | 127 w panel fan | 1 | pc
141 | 2025-06-28 | G02 | cab module | 1 | pc
142 | 2025-07-01 | G32 | 80 w panel fan | 1 | pc
143 | 2025-07-01 | G22 | 80 w panel fan | 2 | pc
144 | 2025-07-02 | G36 | 80 w panel fan | 2 | pc
145 | 2025-07-04 | G04 | HU Main Hose | 1 | pc
146 | 2025-07-04 | G09 | HU Contactor | 1 | pc
147 | 2025-07-06 | G16 | ABB carbon brush | 4 | pc
148 | 2025-07-06 | G16 | Kluberplex BEM 41-132 | 240 | gm
149 | 2025-07-08 | G01 | Proportional valve | 1 | pc
150 | 2025-07-08 | G32 | MPCB MS 132 (8A-12A) | 1 | pc