## O2Summary
Performance Summary PWEPL
Month | 2025-07-01
Date | 2025-07-09
Financial Year | Year-3
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 904.894 | 1226.163 | 35.5%
| E_Grid MTD(MWh) | 8144.046 | 13292.556 | 63.22%
| E_Grid YTD (MWh) | 41428.9983 | 58731.362 | 41.76%
2 | Wind Speed Daily | 9.8233 | 9.8275 | 0.04242%
| Wind Speed MTD | 9.8233 | 11.679 | 18.89%
| Wind Speed YTD | 6.2836 | 6.9091 | 9.954%
3 | PA Daily | 96.03% | 100% | 4.134%
| PA MTD | 96.03% | 99% | 3.092%
| PA YTD | 96.03% | 97.42% | 1.453%
4 | EGA Daily | 99.5% | 100% | 0.5025%
| EGA MTD | 99.5% | 100% | 0.5025%
| EGA YTD | 99.5% | 99.34% | -0.1619%
5 | IGA Daily | 99% | 100% | 1.01%
| IGA MTD | 99% | 99.65% | 0.6541%
| IGA YTD | 99% | 98.41% | -0.5995%
6 | MA Daily | 97% | 100% | 3.093%
| MA MTD | 97% | 99.65% | 2.729%
| MA YTD | 97% | 98.41% | 1.45%
7 | CUF Daily | 53.56% | 72.57% | 35.5%
| CUF MTD | 53.56% | 87.41% | 63.22%
| CUF YTD | 24.52% | 34.76% | 41.76%
8 | Line Loss Daily | 5% | 0% | 100%
| Line Loss MTD | 5% | -1.234e-15% | 100%
| Line Loss YTD | 5% | 9.992e-16% | 100%
9 | Reactive Power Daily | 5% | 0.01855% | 99.63%
| Reactive Power MTD | 5% | 0.01893% | 99.62%
| Reactive Power YTD | 5% | 0.01585% | 99.68%
10 | Expected Energy Daily | 1190.71 | 1226.163 | 2.977%
| Expected Energy MTD | 13570.93 | 13292.556 | -2.051%
| Expected Energy YTD | 59079.6 | 58731.362 | -0.5894%
Feeder4

## AnnualKPI
Till Date | 2025-07-09 | 2025-07-01
PWEPL Performance Summary-YTD
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA(%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | Expected Energy | Loss (%) | Reactive Power (%)
2026 | 100 | 6.2836 | 6.9091 | 41428.9983 | 58731.362 | 24.52% | 34.76% | 99.5% | 99.34% | 97% | 99% | 99% | 98.41% | 96.03% | 97.42% | 59079.6 | 9.992e-16% | 0.01585%

## MonthlyKPI
Till Date | 2025-07-09 | 0 | 0 | 0 | 0
PWEPL Performance Summary (MTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | WTG Total (MWh) | Line Losses(%) | E_WS_Corrected | Expected Energy | Loss (%) | Reactive Power (%)
2025-07-01 | 9 | 9.8233 | 11.679 | 8144.046 | 13292.556 | 53.56% | 87.41% | 99.5% | 100% | 97% | 99.35% | 99% | 99.65% | 96.03% | 99% | 13292.556 | 0% | 13570.93 | 13570.93 | -1.234e-15% | 0.01893%
Start Date | 2025-07-03
End Date | 2025-07-09
PWEPL Performance Summary (WTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | E_WS_Corrected
2025-07-01 | 7 | 9.8233 | 11.7742 | 6334.258 | 10380.662 | 53.56% | 87.77% | 99.5% | 100% | 97% | 99.49% | 99% | 99.87% | 96.03% | 99.36% | 10561.32
Start Date | 2025-06-10
End Date | 2025-07-09
PWEGPL Performance Summary (LTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%)
2025-07-01 | 30 | 7.1311 | 10.5491 | 19059.2076 | 37508.581 | 37.6% | 74% | 99.7% | 99.5% | 98.6% | 99.09% | 99.5% | 99.22% | 98.11% | 98.32%
Formulas:
Days = [Days, row below]-6

## Analytics
Start Date | 2025-06-12
End Date | 2025-07-09 | 648 | 10.4754
WTG No. | P-01 | P-02 | P-03 | P-04 | P-05 | P-06 | P-07 | P-08 | P-09 | P-10 | P-11 | P-12 | P-13 | P-14 | P-15 | P-16 | P-17 | P-18 | P-19 | P-20 | P-22 | P-23 | P-25 | P-26 | P-27 | P-28 | P-31 | P-32 | P-34 | P-37 | P-38 | P-40 | P-41 | P-42 | P-43 | P-45 | P-46 | P-47 | P-48 | P-50 | P-51 | P-52 | P-55 | P-56
MA | 98.96% | 99.51% | 95.45% | 94.71% | 99.99% | 99.32% | 99.96% | 99.68% | 99.57% | 99.82% | 98.91% | 99.99% | 96.33% | 99.82% | 97.61% | 99.17% | 99.89% | 99.99% | 98.99% | 99.58% | 99.85% | 99.41% | 99.76% | 97.54% | 99.99% | 99.31% | 99.98% | 99.69% | 97.29% | 98.8% | 99.9% | 98.2% | 98.77% | 99.42% | 99.72% | 99.94% | 99.99% | 99.99% | 99.99% | 97.98% | 99.27% | 99.7% | 99.99% | 97.78% | 99.08%
WTG BD Hours | 6.75 | 3.1833 | 29.4667 | 34.25 | 0.066667 | 4.4 | 0.23333 | 2.0667 | 2.7833 | 1.15 | 7.05 | 0.033333 | 23.7667 | 1.1667 | 15.4667 | 5.4 | 0.73333 | 0.05 | 6.5167 | 2.7167 | 0.95 | 3.8333 | 1.5667 | 15.9333 | 0.033333 | 4.4833 | 0.11667 | 2.0333 | 17.55 | 7.7833 | 0.66667 | 11.6667 | 7.9833 | 3.7333 | 1.7833 | 0.38333 | 0.083333 | 0.066667 | 0.066667 | 13.1167 | 4.7167 | 1.9167 | 0.066667 | 14.3833 | 0
IGA | 98.61% | 98.61% | 98.61% | 99.89% | 100% | 100% | 98.61% | 100% | 100% | 100% | 100% | 100% | 100% | 99.89% | 99.89% | 99.89% | 99.89% | 98.61% | 99.89% | 99.89% | 99.89% | 99.89% | 100% | 100% | 100% | 100% | 98.61% | 98.61% | 99.89% | 98.61% | 99.89% | 100% | 100% | 100% | 99.89% | 100% | 100% | 100% | 100% | 98.61% | 98.61% | 98.61% | 98.61% | 98.61% | 99.56%
METERING YARD | [44 empty] | #DIV/0!
FEEDER | 8.9833 | 8.9833 | 8.9833 | 0.68333 | 0 | 0 | 8.9833 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68333 | 0.68333 | 0.68333 | 0.68333 | 8.9833 | 0.68333 | 0.68333 | 0.68333 | 0.68333 | 0 | 0 | 0 | 0 | 8.9833 | 8.9833 | 0.68333 | 8.9833 | 0.68333 | 0 | 0 | 0 | 0.68333 | 0 | 0 | 0 | 0 | 8.9833 | 8.9833 | 8.9833 | 8.9833 | 8.9833 | 0
OG | [44 empty] | #DIV/0!
TRANSFER | [44 empty] | #DIV/0!
USS | [44 empty] | #DIV/0!
EGA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
External Grid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Generation | 887180 | 851680 | 746140 | 815110 | 866192 | 864288 | 863304 | 788256 | 663320 | 694564 | 786482 | 867960 | 855036 | 813078 | 759072 | 793688 | 818794 | 814012 | 797492 | 729511 | 861796 | 794032 | 799272 | 809920 | 850960 | 823488 | 697290 | 732842 | 840016 | 802052 | 791488 | 734396 | 852184 | 870252 | 753126 | 935644 | 928512 | 871756 | 912304 | 754254 | 833658 | 795260 | 898000 | 878236 | 35895897
PA | 97.57% | 98.12% | 94.07% | 94.61% | 99.99% | 99.32% | 98.58% | 99.68% | 99.57% | 99.82% | 98.91% | 99.99% | 96.33% | 99.71% | 97.51% | 99.06% | 99.78% | 98.61% | 98.89% | 99.48% | 99.75% | 99.3% | 99.76% | 97.54% | 99.99% | 99.31% | 98.6% | 98.3% | 97.19% | 97.41% | 99.79% | 98.2% | 98.77% | 99.42% | 99.62% | 99.94% | 99.99% | 99.99% | 99.99% | 96.59% | 97.89% | 98.32% | 98.6% | 96.39% | 98.64%
Sum of BD | 6.75 | 3.1833 | 29.4667 | 34.25 | 0.066667 | 4.4 | 0.23333 | 2.0667 | 2.7833 | 1.15 | 7.05 | 0.033333 | 23.7667 | 1.1667 | 15.4667 | 5.4 | 0.73333 | 0.05 | 6.5167 | 2.7167 | 0.95 | 3.8333 | 1.5667 | 15.9333 | 0.033333 | 4.4833 | 0.11667 | 2.0333 | 17.55 | 7.7833 | 0.66667 | 11.6667 | 7.9833 | 3.7333 | 1.7833 | 0.38333 | 0.083333 | 0.066667 | 0.066667 | 13.1167 | 4.7167 | 1.9167 | 0.066667 | 14.3833 | 0
Count of BD | 6 | 2 | 3 | 8 | 1 | 4 | 2 | 4 | 3 | 4 | 7 | 1 | 4 | 1 | 3 | 2 | 3 | 1 | 4 | 3 | 2 | 5 | 2 | 7 | 1 | 4 | 1 | 2 | 10 | 5 | 3 | 2 | 6 | 3 | 2 | 2 | 1 | 1 | 1 | 5 | 3 | 3 | 1 | 6 | 0
MTTR WTG | 1.125 | 1.5917 | 9.8222 | 4.2812 | 0.066667 | 1.1 | 0.11667 | 0.51667 | 0.92778 | 0.2875 | 1.0071 | 0.033333 | 5.9417 | 1.1667 | 5.1556 | 2.7 | 0.24444 | 0.05 | 1.6292 | 0.90556 | 0.475 | 0.76667 | 0.78333 | 2.2762 | 0.033333 | 1.1208 | 0.11667 | 1.0167 | 1.755 | 1.5567 | 0.22222 | 5.8333 | 1.3306 | 1.2444 | 0.89167 | 0.19167 | 0.083333 | 0.066667 | 0.066667 | 2.6233 | 1.5722 | 0.63889 | 0.066667 | 2.3972 | 1.4954
MTBF WTG | 106.875 | 322.4083 | 206.1778 | 76.7188 | 647.9333 | 160.9 | 323.8833 | 161.4833 | 215.0722 | 161.7125 | 91.5643 | 647.9667 | 156.0583 | 646.8333 | 210.8444 | 321.3 | 215.7556 | 647.95 | 160.3708 | 215.0944 | 323.525 | 128.8333 | 323.2167 | 90.2952 | 647.9667 | 160.8792 | 647.8833 | 322.9833 | 63.045 | 128.0433 | 215.7778 | 318.1667 | 106.6694 | 214.7556 | 323.1083 | 323.8083 | 647.9167 | 647.9333 | 647.9333 | 126.9767 | 214.4278 | 215.3611 | 647.9333 | 105.6028 | 302.0442
WS (M/S) | 11.1357 | 11.3043 | 10.205 | 11.1657 | 10.6446 | 11.3132 | 11.255 | 10.35 | 9.2468 | 9.6686 | 11.0161 | 11.9882 | 11.1771 | 10.3668 | 10.4754 | 10.1743 | 10.7993 | 10.3371 | 10.2007 | 9.1732 | 10.7093 | 10.0879 | 9.6596 | 11.0718 | 11.1271 | 10.4343 | 9.1404 | 9.6543 | 10.9543 | 10.3011 | 10.2229 | 9.8314 | 11.2904 | 11.1768 | 9.63 | 13.2136 | 12.0993 | 10.8257 | 11.6064 | 10.03 | 10.9918 | 11.01 | 12.7989 | 11.6593 | 10.7164
Line loss (%)
Corelation (%)
Reactive Power
Fault Analysis
|  |  | Put hour Here |  | Default hour for full Data
|  |  | #REF! |  | #REF!
Row Labels | Sum of Breakdown Time | Count of Error Text | MTTR | MTBF
Gearbox oil overtemperature | 289.1 | 73 | 3.9603 | #REF!
Line CCU collective faults | 207.0167 | 26 | 7.9622 | #REF!
PLC fault 24V Supply | 84.2253 | 12 | 7.0188 | #REF!
Anemometer defec | 65.85 | 8 | 8.2313 | #REF!
Line CCU fault current | 65.0833 | 7 | 9.2976 | #REF!
Pitch thyristor 3 fault | 58.0833 | 9 | 6.4537 | #REF!
Yaw tooth sensor 1 timeout | 40.3 | 20 | 2.015 | #REF!
Rotor speeds not plausible | 39.8 | 7 | 5.6857 | #REF!
Communication fault wind measurement device | 34.2167 | 5 | 6.8433 | #REF!
No communication Cu | 28.95 | 2 | 14.475 | #REF!
Pitch thyristor 1 fault | 26.9833 | 3 | 8.9944 | #REF!
Brake not released secondary brake | 20.25 | 2 | 10.125 | #REF!
CCU fault at abnormal grid condition | 18.5167 | 2 | 9.2583 | #REF!
Grid voltage drop CU | 18.0167 | 20 | 0.90083 | #REF!
Pitch thyristor 2 fault | 17.8833 | 4 | 4.4708 | #REF!
Communication fault pitch controller Axis 2 | 15.5833 | 4 | 3.8958 | #REF!
Gearbox oil level too low | 14.3833 | 9 | 1.5981 | #REF!
Line CCU fault voltage | 13.3667 | 3 | 4.4556 | #REF!
Timeout yaw counter | 6.5667 | 3 | 2.1889 | #REF!
Yaw tooth sensor 2 timeout | 6.5333 | 4 | 1.6333 | #REF!
axis 3 fault pitch controlle | 6.4667 | 5 | 1.2933 | #REF!
Yaw Brake Voltage 230Volt not OK | 6.0333 | 4 | 1.5083 | #REF!
Temp. sensor error (shut down) | 5.9 | 3 | 1.9667 | #REF!
System re-initialization after grid outage | 5.4167 | 13 | 0.41667 | #REF!
DTA DIN03 control breaker status | 5.3333 | 1 | 5.3333 | #REF!
Battery voltage not OK axis 1 | 4.6167 | 1 | 4.6167 | #REF!
axis 2 fault pitch controller | 4.3 | 2 | 2.15 | #REF!
Pitch control deviation Axis 3 | 4.25 | 2 | 2.125 | #REF!
Yaw Mapping | 3.8333 | 1 | 3.8333 | #REF!
Communication fault Pitch controller | 3.1833 | 1 | 3.1833 | #REF!
Internal Line VCB tripped in over current | 3.1167 | 2 | 1.5583 | #REF!
axis 1 fault pitch controller | 2.85 | 4 | 0.7125 | #REF!
TopBox DIN21 motor protection aux contact string | 2.8 | 4 | 0.7 | #REF!
Ratio generator-/rotor speed | 2.6833 | 1 | 2.6833 | #REF!
Line fault voltage | 2.25 | 1 | 2.25 | #REF!
Feedback error circuit breaker | 1.9333 | 1 | 1.9333 | #REF!
Shaft bearing overtemperature | 1.9 | 1 | 1.9 | #REF!
No speed reduction with secondary braking | 1.25 | 4 | 0.3125 | #REF!
Brake does not close | 1.0167 | 1 | 1.0167 | #REF!
Pitch control deviation axis 1 | 1 | 1 | 1 | #REF!
Limit switch 90deg-rotorblade defective | 0.66667 | 1 | 0.66667 | #REF!
Safety chain | 0.6 | 2 | 0.3 | #REF!
Pitch malfunction 2 or 3 blades | 0.58333 | 1 | 0.58333 | #REF!
Yaw runaway | 0.48333 | 1 | 0.48333 | #REF!
Yaw sensor error | 0.41667 | 1 | 0.41667 | #REF!
Secondary braking time too high | 0.38333 | 2 | 0.19167 | #REF!
Secondary brake test | 0.13333 | 1 | 0.13333 | #REF!
Incorrect Error Code | 0 | 12 | 0 | #REF!
Grand Total | 1144.1086 | 297 | 3.8522 | #REF!
|  |  | #DIV/0! | #REF!

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 4.6409 | 5.68 | 96.85% | 99.33% | 97.5% | 100% |  |  |  |  | 9.999% | 168935 | 168935 | 0 | 168935 | 70.4 | 4.565 | 177354.8387 |  | 10.5% | 96.03% | 99.5% | 156.79 |  |  |  |  | 0% | 0% | 5% | 5% | 70.4
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 4.9325 | 6.15 | 99.5% | 100% | 99.5% | 100% |  |  |  |  | 11.24% | 189877 | 189877 | 0 | 189877 | 70.4 | 4.565 | 177354.8387 |  | 10.5% | 96.03% | 99.5% | 162.74 |  |  |  |  | 0% | 0% | 5% | 5% | 70.4
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 3.7164 | 4.75 | 95.4% | 99.59% | 95.79% | 100% |  |  |  |  | 5.196% | 87784 | 87784 | 0 | 87784 | 70.4 | 4.565 | 177354.8387 |  | 10.5% | 96.03% | 99.5% | 66.47 |  |  |  |  | -1.11e-14% | 0% | 5% | 5% | 70.4
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.0677 | 6.47 | 85.43% | 98.56% | 86.68% | 100% |  |  |  |  | 14.47% | 244495 | 244495 | 0 | 244495 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 261.94 |  |  |  |  | -1.11e-14% | 0.01526% | 5% | 5% | 70.4
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.4718 | 6.87 | 96.84% | 99.12% | 97.71% | 100% |  |  |  |  | 18.69% | 315710 | 315710 | 0 | 315710 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 310.38 |  |  |  |  | 2.22e-14% | 0.02014% | 5% | 5% | 70.4
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 3.5082 | 4.18 | 94.45% | 98.41% | 95.98% | 100% |  |  |  |  | 4.559% | 77037 | 77037 | 0 | 77037 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 72.74 |  |  |  |  | 0% | 0.01943% | 5% | 5% | 70.4
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.1436 | 5.01 | 93.44% | 99.98% | 93.46% | 100% |  |  |  |  | 6.937% | 117205 | 117205 | 0 | 117205 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 115.35 |  |  |  |  | 0% | 0.01764% | 5% | 5% | 70.4
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.4491 | 5.5 | 93.03% | 94.99% | 97.94% | 100% |  |  |  |  | 7.543% | 127441 | 127441 | 0 | 127441 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 127.87 |  |  |  |  | 0% | 0.002704% | 5% | 5% | 70.4
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 3.8152 | 4.7 | 96.94% | 99.87% | 97.07% | 100% |  |  |  |  | 5.749% | 97130 | 97130 | 0 | 97130 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 89.31 |  |  |  |  | 0% | 0.0005914% | 5% | 5% | 70.4
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.3709 | 5.5 | 97.31% | 98.98% | 98.32% | 100% |  |  |  |  | 7.909% | 133637 | 133637 | 0 | 133637 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 120.74 |  |  |  |  | 0% | 0.01422% | 5% | 5% | 70.4
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.1109 | 4.86 | 96.65% | 97.86% | 98.76% | 83.44% |  |  |  |  | 5.49% | 92765 | 92765 | 0 | 92765 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 98.25 |  |  |  |  | 2.22e-14% | 0.008602% | 5% | 5% | 70.4
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.2959 | 5.39 | 96.56% | 98.81% | 97.72% | 100% |  |  |  |  | 8.27% | 139732 | 139732 | 0 | 139732 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 137.01 |  |  |  |  | 0% | 0.01468% | 5% | 5% | 70.4
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.3873 | 6.9 | 96.5% | 99.49% | 96.99% | 100% |  |  |  |  | 15.47% | 261367 | 261367 | 0 | 261367 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 246.08 |  |  |  |  | -2.22e-14% | 0.01973% | 5% | 5% | 70.4
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.1159 | 6.04 | 96.05% | 98.75% | 97.26% | 100% |  |  |  |  | 13.85% | 234033 | 234033 | 0 | 234033 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 228.85 |  |  |  |  | 0% | 0.02008% | 5% | 5% | 70.4
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.4291 | 6.85 | 98.98% | 99.13% | 99.85% | 100% |  |  |  |  | 15.97% | 269769 | 269769 | 0 | 269769 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 262.35 |  |  |  |  | 0% | 0.02021% | 5% | 5% | 70.4
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.9427 | 6.62 | 100% | 100% | 100% | 100% |  |  |  |  | 13.47% | 227580 | 227580 | 0 | 227580 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 219.75 |  |  |  |  | -1.11e-14% | 0.02016% | 5% | 5% | 70.4
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.9261 | 6.46 | 99.89% | 99.89% | 100% | 100% |  |  |  |  | 13.69% | 231240 | 231240 | 0 | 231240 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 223.32 |  |  |  |  | 0% | 0.02007% | 5% | 5% | 70.4
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.0939 | 6.81 | 99.15% | 99.15% | 100% | 83.04% |  |  |  |  | 15.08% | 254860 | 254860 | 0 | 254860 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 249.16 |  |  |  |  | -1.11e-14% | 0.008959% | 5% | 5% | 70.4
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.2598 | 6.18 | 99.17% | 99.17% | 100% | 100% |  |  |  |  | 17.85% | 301619 | 301619 | 0 | 301619 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 288.87 |  |  |  |  | 0% | 0.004154% | 5% | 5% | 70.4
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.2409 | 8.07 | 98.68% | 99.08% | 99.6% | 100% |  |  |  |  | 24.06% | 406593 | 406593 | 0 | 406593 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 398.35 |  |  |  |  | -1.11e-14% | 0.01305% | 5% | 5% | 70.4
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.7127 | 7.18 | 99.06% | 99.06% | 100% | 100% |  |  |  |  | 21.53% | 363733 | 363733 | 0 | 363733 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 353.43 |  |  |  |  | 0% | 0.01384% | 5% | 5% | 70.4
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.7152 | 7.01 | 99.08% | 99.08% | 100% | 100% |  |  |  |  | 18.73% | 316438 | 316438 | 0 | 316438 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 305.33 |  |  |  |  | 0% | 0.02% | 5% | 5% | 70.4
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.1234 | 6.58 | 100% | 100% | 100% | 100% |  |  |  |  | 18.02% | 304485 | 304485 | 0 | 304485 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 290.9 |  |  |  |  | 0% | 0.01992% | 5% | 5% | 70.4
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.4977 | 5.55 | 98.21% | 100% | 98.21% | 100% |  |  |  |  | 11.29% | 190695 | 190695 | 0 | 190695 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 186.07 |  |  |  |  | 0% | 0.02027% | 5% | 5% | 70.4
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.2566 | 5.27 | 97.95% | 99.56% | 98.39% | 85.19% |  |  |  |  | 7.189% | 121460 | 121460 | 0 | 121460 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 123.66 |  |  |  |  | 2.22e-14% | 0.01991% | 5% | 5% | 70.4
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.6352 | 5.79 | 93.98% | 98.42% | 95.5% | 100% |  |  |  |  | 10.98% | 185519 | 185519 | 0 | 185519 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 185.49 |  |  |  |  | 0% | 0.01848% | 5% | 5% | 70.4
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.6136 | 5.65 | 94.43% | 99.18% | 95.21% | 100% |  |  |  |  | 8.925% | 150802 | 150802 | 0 | 150802 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 152.06 |  |  |  |  | 2.22e-14% | 0.02274% | 5% | 5% | 70.4
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.542 | 5.76 | 97.24% | 98.56% | 98.66% | 100% |  |  |  |  | 10.07% | 170185 | 170185 | 0 | 170185 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 173.65 |  |  |  |  | 0% | 0.02027% | 5% | 5% | 70.4
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.3225 | 5.12 | 90.95% | 97.98% | 92.83% | 100% |  |  |  |  | 8.564% | 144697 | 144697 | 0 | 144697 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 143.45 |  |  |  |  | 0% | 0.02008% | 5% | 5% | 70.4
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 3.9584 | 4.59 | 98.98% | 98.98% | 100% | 100% |  |  |  |  | 6.724% | 113604 | 113604 | 0 | 113604 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 110.6 |  |  |  |  | -1.11e-14% | 0.02017% | 5% | 5% | 70.4
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.1516 | 5.13 | 98.36% | 98.36% | 100% | 100% |  |  |  |  | 7.795% | 131712 | 131712 | 0 | 131712 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 131.18 |  |  |  |  | 0% | 0.0174% | 5% | 5% | 70.4
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.8641 | 5.78 | 99.2% | 99.2% | 100% | 100% |  |  |  |  | 12.13% | 204908 | 204908 | 0 | 204908 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 201.28 |  |  |  |  | 0% | 0.02022% | 5% | 5% | 70.4
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.6725 | 7.02 | 99.32% | 99.32% | 100% | 100% |  |  |  |  | 17.99% | 304033 | 304033 | 0 | 304033 | 70.4 | 5.22 | 228113.2814 |  | 13.5% | 96.03% | 99.5% | 294.64 |  |  |  |  | 0% | 0.02023% | 5% | 5% | 70.4
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.5466 | 7.19 | 99.87% | 99.87% | 100% | 100% |  |  |  |  | 19.94% | 336843 | 336843 | 0 | 336843 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 324.42 |  |  |  |  | -2.22e-14% | 0.01989% | 5% | 5% | 70.4
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.2659 | 8.36 | 99.21% | 99.21% | 100% | 100% |  |  |  |  | 29.17% | 492802 | 492802 | 0 | 492802 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 481.71 |  |  |  |  | 0% | 0.02024% | 5% | 5% | 70.4
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.4045 | 8.31 | 95.88% | 99.86% | 96.02% | 100% |  |  |  |  | 28.25% | 477257 | 477257 | 0 | 477257 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 477.26 |  |  |  |  | 2.22e-14% | 0.02028% | 5% | 5% | 70.4
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.7609 | 9.13 | 100% | 100% | 100% | 100% |  |  |  |  | 29.44% | 497495 | 497495 | 0 | 497495 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 490.15 |  |  |  |  | 0% | 0.02027% | 5% | 5% | 70.4
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.318 | 7.96 | 99.47% | 99.47% | 100% | 100% |  |  |  |  | 27.24% | 460318 | 460318 | 0 | 460318 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 461.99 |  |  |  |  | 0% | 0.02025% | 5% | 5% | 70.4
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.9805 | 7.49 | 100% | 100% | 100% | 100% |  |  |  |  | 22.59% | 381718 | 381718 | 0 | 381718 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 378.83 |  |  |  |  | 0% | 0.0202% | 5% | 5% | 70.4
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.8957 | 8.71 | 100% | 100% | 100% | 100% |  |  |  |  | 31.09% | 525250 | 525250 | 0 | 525250 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 517.71 |  |  |  |  | 0% | 0.02028% | 5% | 5% | 70.4
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.2266 | 9.55 | 98.51% | 98.7% | 99.81% | 100% |  |  |  |  | 36.51% | 616955 | 616955 | 0 | 616955 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 589.61 |  |  |  |  | 0% | 0.0203% | 5% | 5% | 70.4
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.0366 | 6.73 | 93% | 95.48% | 97.4% | 100% |  |  |  |  | 12.42% | 209885 | 209885 | 0 | 209885 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 197.15 |  |  |  |  | 0% | 0.02018% | 5% | 5% | 70.4
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.4364 | 6.13 | 90.97% | 94.87% | 95.89% | 100% |  |  |  |  | 9.242% | 156148 | 156148 | 0 | 156148 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 148.4 |  |  |  |  | 2.22e-14% | 0.01931% | 5% | 5% | 70.4
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.907 | 4.99 | 96.57% | 96.57% | 100% | 100% |  |  |  |  | 6.398% | 108095 | 108095 | 0 | 108095 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 102.44 |  |  |  |  | 0% | 0.02001% | 5% | 5% | 70.4
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.5143 | 4.8 | 87.33% | 95.84% | 91.12% | 100% |  |  |  |  | 5.433% | 91789 | 91789 | 0 | 91789 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 97.92 |  |  |  |  | 0% | 0.02434% | 5% | 5% | 70.4
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.398 | 4.01 | 96.44% | 96.44% | 100% | 87.88% |  |  |  |  | 4.919% | 83105 | 83105 | 0 | 83105 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 82.79 |  |  |  |  | -2.22e-14% | 0.01851% | 5% | 5% | 70.4
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.7082 | 4.69 | 85.41% | 95.99% | 88.98% | 100% |  |  |  |  | 5.791% | 97848 | 97848 | 0 | 97848 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 104.47 |  |  |  |  | 0% | 0.01972% | 5% | 5% | 70.4
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.022 | 5.43 | 94.1% | 97.69% | 96.32% | 100% |  |  |  |  | 5.803% | 98053 | 98053 | 0 | 98053 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 98.72 |  |  |  |  | 0% | 0.02019% | 5% | 5% | 70.4
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.5484 | 4.28 | 99.22% | 99.96% | 99.27% | 100% |  |  |  |  | 4.409% | 74497 | 74497 | 0 | 74497 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 74.53 |  |  |  |  | 0% | 0.0009501% | 5% | 5% | 70.4
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8418 | 6.14 | 99.25% | 99.46% | 99.79% | 100% |  |  |  |  | 10.39% | 175607 | 175607 | 0 | 175607 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 167.61 |  |  |  |  | 0% | 0.008761% | 5% | 5% | 70.4
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.5184 | 6.98 | 96.91% | 100% | 96.91% | 100% |  |  |  |  | 8.093% | 136747 | 136747 | 0 | 136747 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 82.84 |  |  |  |  | 0% | 0.001875% | 5% | 5% | 70.4
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.9407 | 5.89 | 98.13% | 99.78% | 98.34% | 100% |  |  |  |  | 7.331% | 123872 | 123872 | 0 | 123872 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 13.38 |  |  |  |  | -1.11e-14% | 0.001307% | 5% | 5% | 70.4
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.4509 | 5.38 | 91.04% | 97.97% | 92.93% | 100% |  |  |  |  | 6.745% | 113971 | 113971 | 0 | 113971 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 114.6 |  |  |  |  | -1.11e-14% | 0.0003105% | 5% | 5% | 70.4
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.4891 | 6.25 | 100% | 100% | 100% | 100% |  |  |  |  | 9.291% | 156981 | 156981 | 0 | 156981 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 143.73 |  |  |  |  | 0% | 0% | 5% | 5% | 70.4
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.5873 | 6.51 | 98.39% | 100% | 98.39% | 100% |  |  |  |  | 9.733% | 164448 | 164448 | 0 | 164448 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 146.37 |  |  |  |  | 0% | 0.01091% | 5% | 5% | 70.4
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.4518 | 6.17 | 86.22% | 99.6% | 86.56% | 100% |  |  |  |  | 8.679% | 146641 | 146641 | 0 | 146641 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 140.63 |  |  |  |  | 0% | 0.01511% | 5% | 5% | 70.4
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 2.885 | 3.79 | 99.64% | 99.64% | 100% | 100% |  |  |  |  | 2.919% | 49311 | 49311 | 0 | 49311 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 45.49 |  |  |  |  | 0% | 0.04492% | 5% | 5% | 70.4
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.3202 | 8.55 | 99.01% | 99.25% | 99.77% | 100% |  |  |  |  | 29.4% | 496668 | 496668 | 0 | 496668 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 464.94 |  |  |  |  | 0% | 0.00446% | 5% | 5% | 70.4
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.1618 | 9.75 | 94.94% | 99.18% | 95.72% | 100% |  |  |  |  | 34.73% | 586779 | 586779 | 0 | 586779 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 576.94 |  |  |  |  | 0% | 0.003775% | 5% | 5% | 70.4
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.3984 | 8.17 | 100% | 100% | 100% | 100% |  |  |  |  | 29.87% | 504609 | 504609 | 0 | 504609 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 485.57 |  |  |  |  | 2.22e-14% | 0.00439% | 5% | 5% | 70.4
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.1457 | 8.91 | 96.68% | 99.74% | 96.93% | 100% |  |  |  |  | 34.25% | 578733 | 578733 | 0 | 578733 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 558.98 |  |  |  |  | 0% | 0.003828% | 5% | 5% | 70.4
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.6143 | 9.62 | 99.73% | 99.73% | 100% | 100% |  |  |  |  | 42.11% | 711533 | 711533 | 0 | 711533 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 691.97 |  |  |  |  | 0% | 0.003113% | 5% | 5% | 70.4
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 10.2359 | 12.39 | 99.55% | 99.66% | 99.88% | 100% |  |  |  |  | 75.98% | 1283785 | 1283785 | 0 | 1283785 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 1292.91 |  |  |  |  | 0% | 0.001726% | 5% | 5% | 70.4
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 8.8632 | 11.18 | 99.86% | 100% | 99.86% | 100% |  |  |  |  | 58.91% | 995423 | 995423 | 0 | 995423 | 70.4 | 5.7233 | 349950.5148 |  | 20.71% | 96.03% | 99.5% | 983.09 |  |  |  |  | 0% | 0.002225% | 5% | 5% | 70.4
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.5211 | 8.93 | 100% | 100% | 100% | 100% |  |  |  |  | 28.24% | 477059 | 477059 | 0 | 477059 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 430.77 |  |  |  |  | -1.11e-14% | 0.004643% | 5% | 5% | 70.4
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.645 | 8.89 | 98.01% | 98.77% | 99.23% | 100% |  |  |  |  | 29.03% | 490432 | 490432 | 0 | 490432 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 453.43 |  |  |  |  | 0% | 0.006864% | 5% | 5% | 70.4
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.7316 | 8.99 | 99.22% | 99.52% | 99.69% | 100% |  |  |  |  | 31.06% | 524861 | 524861 | 0 | 524861 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 482.41 |  |  |  |  | 0% | 0.01811% | 5% | 5% | 70.4
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.6355 | 9.1 | 98.76% | 98.8% | 99.96% | 100% |  |  |  |  | 30.21% | 510411 | 510411 | 0 | 510411 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 475.81 |  |  |  |  | 2.22e-14% | 0.01893% | 5% | 5% | 70.4
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.1284 | 7.6 | 98.5% | 99.37% | 99.13% | 100% |  |  |  |  | 22.4% | 378554 | 378554 | 0 | 378554 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 361.89 |  |  |  |  | 0% | 0.01788% | 5% | 5% | 70.4
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.317 | 6.84 | 98.67% | 98.67% | 100% | 100% |  |  |  |  | 14.4% | 243339 | 243339 | 0 | 243339 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 238.66 |  |  |  |  | 0% | 0.01778% | 5% | 5% | 70.4
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.6864 | 7.26 | 99.72% | 99.72% | 100% | 100% |  |  |  |  | 17.61% | 297459 | 297459 | 0 | 297459 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 290.06 |  |  |  |  | 0% | 0.01797% | 5% | 5% | 70.4
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.8177 | 8.57 | 99.88% | 99.88% | 100% | 100% |  |  |  |  | 29.71% | 501923 | 501923 | 0 | 501923 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 485.96 |  |  |  |  | 0% | 0.0188% | 5% | 5% | 70.4
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.3814 | 9.48 | 99.97% | 99.97% | 100% | 100% |  |  |  |  | 37.35% | 631093 | 631093 | 0 | 631093 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 615.65 |  |  |  |  | 2.22e-14% | 0.01868% | 5% | 5% | 70.4
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.9764 | 10.03 | 99.8% | 99.8% | 100% | 94.34% |  |  |  |  | 43.98% | 743030 | 743030 | 0 | 743030 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 754.1 |  |  |  |  | 0% | 0.009079% | 5% | 5% | 70.4
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 8.4359 | 10.56 | 99.65% | 99.65% | 100% | 100% |  |  |  |  | 51.47% | 869654 | 869654 | 0 | 869654 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 869.19 |  |  |  |  | 0% | 0.00756% | 5% | 5% | 70.4
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.3545 | 9.94 | 100% | 100% | 100% | 100% |  |  |  |  | 38.22% | 645773 | 645773 | 0 | 645773 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 630.85 |  |  |  |  | -2.22e-14% | 0.02017% | 5% | 5% | 70.4
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 2.4861 | 3.02 | 97.79% | 97.79% | 100% | 100% |  |  |  |  | 1.081% | 18268 | 18268 | 0 | 18268 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 15.97 |  |  |  |  | 0% | 0.01801% | 5% | 5% | 70.4
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 3.1107 | 3.77 | 99.42% | 99.42% | 100% | 100% |  |  |  |  | 4.22% | 71295 | 71295 | 0 | 71295 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 65.28 |  |  |  |  | 0% | 0.01932% | 5% | 5% | 70.4
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.2652 | 8.49 | 99.43% | 99.43% | 100% | 100% |  |  |  |  | 26.5% | 447815 | 447815 | 0 | 447815 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 413.48 |  |  |  |  | 0% | 0.01869% | 5% | 5% | 70.4
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 11.9716 | 14.99 | 97.9% | 97.9% | 100% | 100% |  |  |  |  | 85.26% | 1440479 | 1440479 | 0 | 1440479 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 1482.58 |  |  |  |  | 0% | 0.01825% | 5% | 5% | 70.4
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 11.7523 | 14.63 | 95.38% | 99.49% | 95.87% | 100% |  |  |  |  | 83.87% | 1417059 | 1417059 | 0 | 1417059 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 1496.89 |  |  |  |  | 0% | 0.007446% | 5% | 5% | 70.4
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 12.6909 | 15.89 | 95.97% | 97.29% | 98.65% | 100% |  |  |  |  | 90.45% | 1528311 | 1528311 | 0 | 1528311 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 1619.39 |  |  |  |  | 0% | 0.01913% | 5% | 5% | 70.4
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 12.5361 | 15.54 | 91.89% | 96.4% | 95.32% | 100% |  |  |  |  | 83.14% | 1404731 | 1404731 | 0 | 1404731 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 1534.29 |  |  |  |  | 2.22e-14% | 0.01927% | 5% | 5% | 70.4
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 11.053 | 13.77 | 94.94% | 98.94% | 95.95% | 100% |  |  |  |  | 77.74% | 1313437 | 1313437 | 0 | 1313437 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 1387.29 |  |  |  |  | 0% | 0.0206% | 5% | 5% | 70.4
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 10.3914 | 12.93 | 99.62% | 99.62% | 100% | 100% |  |  |  |  | 78.25% | 1322071 | 1322071 | 0 | 1322071 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 1337.29 |  |  |  |  | 0% | 0.01988% | 5% | 5% | 70.4
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 10.8091 | 13.14 | 99.62% | 99.62% | 100% | 100% |  |  |  |  | 81.59% | 1378618 | 1378618 | 0 | 1378618 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 1411.15 |  |  |  |  | 2.22e-14% | 0.0187% | 5% | 5% | 70.4
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 13.4457 | 16.41 | 96.12% | 99.18% | 96.91% | 100% |  |  |  |  | 88.7% | 1498655 | 1498655 | 0 | 1498655 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 1581.51 |  |  |  |  | 0% | 0.01801% | 5% | 5% | 70.4
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 13.3543 | 15.91 | 97.23% | 98.65% | 98.55% | 100% |  |  |  |  | 91.03% | 1538021 | 1538021 | 0 | 1538021 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 1618.54 |  |  |  |  | 2.22e-14% | 0.01986% | 5% | 5% | 70.4
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 12.2252 | 14.81 | 99.07% | 99.07% | 100% | 100% |  |  |  |  | 90.69% | 1532252 | 1532252 | 0 | 1532252 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 1590.42 |  |  |  |  | 2.22e-14% | 0.01834% | 5% | 5% | 70.4
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 11.6518 | 14.81 | 98.67% | 99.4% | 99.27% | 100% |  |  |  |  | 87.9% | 1485231 | 1485231 | 0 | 1485231 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 1539.71 |  |  |  |  | 0% | 0.01879% | 5% | 5% | 70.4
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 10.357 | 13.37 | 99.69% | 99.69% | 100% | 100% |  |  |  |  | 78.95% | 1333960 | 1333960 | 0 | 1333960 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 1342.98 |  |  |  |  | 0% | 0.02021% | 5% | 5% | 70.4
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 10.5777 | 13.4 | 99.62% | 99.62% | 100% | 100% |  |  |  |  | 80.3% | 1356811 | 1356811 | 0 | 1356811 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 1368.72 |  |  |  |  | 0% | 0.01995% | 5% | 5% | 70.4
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 10.848 | 13.28 | 98.73% | 99.22% | 99.51% | 100% |  |  |  |  | 80.42% | 1358717 | 1358717 | 0 | 1358717 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 1400.72 |  |  |  |  | 0% | 0.01986% | 5% | 5% | 70.4
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 12.0684 | 14.72 | 98.1% | 98.35% | 99.75% | 100% |  |  |  |  | 89.48% | 1511837 | 1511837 | 0 | 1511837 | 70.4 | 6.81 | 519769.5973 |  | 30.76% | 96.03% | 99.5% | 1574.47 |  |  |  |  | 0% | 0.01893% | 5% | 5% | 70.4
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 10.8366 | 12.97 | 97.77% | 98.2% | 99.56% | 100% |  |  |  |  | 82.73% | 1397865 | 1397865 | 0 | 1397865 | 70.4 | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | 1440.43 |  |  |  |  | 0% | 0.01968% | 5% | 5% | 70.4
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 11.8557 | 14.15 | 97.68% | 99.5% | 98.17% | 100% |  |  |  |  | 89.61% | 1514029 | 1514029 | 0 | 1514029 | 70.4 | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | 1569.18 |  |  |  |  | 0% | 0.01951% | 5% | 5% | 70.4
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 11.7511 | 14.58 | 99.58% | 99.77% | 99.81% | 100% |  |  |  |  | 89.26% | 1508194 | 1508194 | 0 | 1508194 | 70.4 | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | 1538.95 |  |  |  |  | 0% | 0.01938% | 5% | 5% | 70.4
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 11.6495 | 14.66 | 99.78% | 99.78% | 100% | 100% |  |  |  |  | 87.4% | 1476767 | 1476767 | 0 | 1476767 | 70.4 | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | 1498.97 |  |  |  |  | 0% | 0.01864% | 5% | 5% | 70.4
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 12.3727 | 15.35 | 97.77% | 97.77% | 100% | 100% |  |  |  |  | 91% | 1537523 | 1537523 | 0 | 1537523 | 70.4 | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | 1597.99 |  |  |  |  | 0% | 0.01933% | 5% | 5% | 70.4
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 13.3775 | 16.28 | 99.97% | 99.97% | 100% | 100% |  |  |  |  | 96.72% | 1634254 | 1634254 | 0 | 1634254 | 70.4 | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | 1671.39 |  |  |  |  | 0% | 0.01915% | 5% | 5% | 70.4
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 12.2432 | 14.69 | 99.15% | 99.55% | 99.6% | 100% |  |  |  |  | 90.62% | 1531057 | 1531057 | 0 | 1531057 | 70.4 | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | 1571.27 |  |  |  |  | -1.11e-14% | 0.01739% | 5% | 5% | 70.4
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 11.1975 | 13.29 | 99.3% | 99.61% | 99.68% | 100% |  |  |  |  | 86.81% | 1466704 | 1466704 | 0 | 1466704 | 70.4 | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | 1492.04 |  |  |  |  | 0% | 0.01876% | 5% | 5% | 70.4
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | [7 empty] | 9.8275 | 12.01 | 100% | 100% | 100% | 100% |  |  |  |  | 72.57% | 1226163 | 1226163 | 0 | 1226163 | 70.4 | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | 1190.71 |  |  |  |  | 0% | 0.01855% | 5% | 5% | 70.4
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 9.8233 | 904894.0022 |  | 53.56% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.1 | 1057470.4978 |  | 62.59% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.56 | 373388.4569 |  | 22.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 4.1733 | 150264.6274 |  | 8.894% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.4633 | 240102.5114 |  | 14.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.79 | 233936.5434 |  | 13.85% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 3.75 | 106720.0922 |  | 6.316% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 3.925 | 118578.5783 |  | 7.018% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 4.565 | 177355.297 |  | 10.5% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.4
Formulas:
Month Year = Daily_KPI[[#This Row],[Date]]-DAY(Daily_KPI[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Input_Raw
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117
[5 empty] | Energy Generated by individual Turbine | [43 empty] | Wind Speed (M/s) | [47 empty] | Meter Readings | [7 empty] | Calculated Energy Numbers
Date | Finacial Year | Calendor Year | Month Year | Days | P-01 | P-02 | P-03 | P-04 | P-05 | P-06 | P-07 | P-08 | P-09 | P-10 | P-11 | P-12 | P-13 | P-14 | P-15 | P-16 | P-17 | P-18 | P-19 | P-20 | P-22 | P-23 | P-25 | P-26 | P-27 | P-28 | P-31 | P-32 | P-34 | P-37 | P-38 | P-40 | P-41 | P-42 | P-43 | P-45 | P-46 | P-47 | P-48 | P-50 | P-51 | P-52 | P-55 | P-56 | WS_P-01 | WS_P-02 | WS_P-03 | WS_P-04 | WS_P-05 | WS_P-06 | WS_P-07 | WS_P-08 | WS_P-09 | WS_P-10 | WS_P-11 | WS_P-12 | WS_P-13 | WS_P-14 | WS_P-15 | WS_P-16 | WS_P-17 | WS_P-18 | WS_P-19 | WS_P-20 | WS_P-22 | WS_P-23 | WS_P-25 | WS_P-26 | WS_P-27 | WS_P-28 | WS_P-31 | WS_P-32 | WS_P-34 | WS_P-37 | WS_P-38 | WS_P-40 | WS_P-41 | WS_P-42 | WS_P-43 | WS_P-45 | WS_P-46 | WS_P-47 | WS_P-48 | WS_P-50 | WS_P-51 | WS_P-52 | WS_P-55 | WS_P-56 | WTG Total Gneration (MWh) | Wind Speed Average cumulative (m/S)2 | Wind Speed Max (m/S) | Rain (mm) | 33 kV_Wind_F1_Export reading | 33 kV_Wind_F1_Import reading | 33 kV_Wind_F2_Export_reading | 33 kV_Wind_F2_Import_reading | 33 kV_Wind_F3_Export_Reading | 33 kV_Wind_F3_Import_Reading | 33 kV_Wind_F4_Export Reading | 33 kV_Wind_F4_Import Reading | 33 kV_F1_Total_Export (MWh) | 33 kV_Wind_F1_Import (MWh) | 33 kV_F2_Total_Export (MWh)2 | 33 kV_Wind_F2_Import (MWh) | 33 kV_Wind_F3_Export (MWh) | 33 kV_Wind_F3_Import (MWh)2 | 33 kV_Wind_F4_Export (MWh) | 33 kV_Wind_F4_Import (MWh)2 | 33 kV_Wind_Total_Export (MWh) | 33 kV_Wind_Total_Import (MWh) | 33 kV Line Loss (%) | EbMA(%) | Forecasting Data count received on Forecasting Portal | Forecasting Penalties (INR) | Expected Energy As Per Power Curve (MWh) | Reactive Energy (MVArH) | Operational Capacity
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 6588 | 6752 | 7308 | 4560 | 4436 | 3156 | 4936 | 2472 | 1594 | 1536 | 1938 | 2062 | 2156 | 2066 | 1992 | 2430 | 2670 | 6332 | 2648 | 2525 | 4952 | 5652 | 3308 | 2956 | 3544 | 3264 | 7016 | 2540 | 4808 | 3862 | 3224 | 2220 | 3612 | 4604 | 3274 | 6072 | 4800 | 4032 | 4272 | 2936 | 2990 | 4564 | 5896 | 4380 | 5.01 | 5.26 | 5.33 | 5.18 | 4.52 | 4.41 | 4.94 | 4.26 | 3.85 | 4.11 | 3.96 | 4.15 | 4.18 | 4.34 | 4.37 | 4.53 | 4.61 | 5.17 | 4.65 | 4.3 | 5.46 | 5.6 | 4.2 | 4.48 | 4.73 | 4.71 | 4.99 | 3.82 | 5.2 | 4.61 | 4.51 | 4.11 | 4.72 | 4.53 | 4.69 | 5.68 | 4.91 | 4.35 | 4.67 | 4.05 | 4.09 | 4.75 | 5.16 | 5.05 | 168.935 | 4.6409 | 5.68 |  | 24830 |  | 40801 |  | 37204 |  | 66100 |  | 24.83 |  | 40.801 |  | 37.204 |  | 66.1 |  | 168.935 | 0 | 0% |  | 89 | 251.75 | 156.79 |  | 70.4
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 8936 | 7288 | 6868 | 6172 | 4268 | 3588 | 5354 | 2160 | 1444 | 1408 | 1792 | 2198 | 2320 | 2460 | 2208 | 2244 | 2764 | 6940 | 2756 | 2719 | 6344 | 6796 | 3068 | 3092 | 3684 | 3152 | 5592 | 2868 | 5300 | 4688 | 3244 | 1882 | 3968 | 5704 | 3516 | 6320 | 5152 | 4908 | 5504 | 3816 | 4472 | 5472 | 8544 | 6904 | 5.8 | 5.57 | 5.5 | 5.61 | 4.83 | 4.92 | 5.25 | 4.52 | 4.04 | 4.33 | 4 | 4.32 | 4.41 | 4.46 | 4.45 | 4.38 | 4.54 | 5.58 | 4.58 | 4.35 | 5.63 | 5.61 | 4.6 | 4.98 | 5.38 | 5.24 | 4.91 | 4.21 | 5.24 | 4.96 | 4.46 | 4.16 | 5.02 | 5.15 | 4.49 | 5.9 | 5.21 | 4.86 | 5.34 | 4.38 | 4.66 | 5.17 | 6.15 | 5.88 | 189.877 | 4.9325 | 6.15 |  | 24318 |  | 46523 |  | 41294 |  | 77742 |  | 24.318 |  | 46.523 |  | 41.294 |  | 77.742 |  | 189.877 | 0 | 0% |  | 90 | 884 | 162.74 |  | 70.4
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 3784 | 2960 | 2816 | 970 | 2856 | 1928 | 2996 | 1136 | 688 | 828 | 994 | 1212 | 1248 | 1368 | 1206 | 1338 | 1552 | 3472 | 1504 | 1374 | 1404 | 1652 | 1660 | 1740 | 2112 | 1848 | 2168 | 864 | 1232 | 1868 | 1724 | 1038 | 2564 | 3656 | 1132 | 3596 | 2932 | 2932 | 3200 | 1018 | 1536 | 1926 | 4148 | 3604 | 4.11 | 4.13 | 3.94 | 3.15 | 3.98 | 3.88 | 4.19 | 3.27 | 3.02 | 3.39 | 3.26 | 3.49 | 3.45 | 3.43 | 3.48 | 3.39 | 3.77 | 4.25 | 3.59 | 3.31 | 3.85 | 3.86 | 3.38 | 3.97 | 4.04 | 3.91 | 3.29 | 2.89 | 3.34 | 3.59 | 3.27 | 3.19 | 4.29 | 4.33 | 3.52 | 4.75 | 4.32 | 3.98 | 4.36 | 2.74 | 3.19 | 3.7 | 4.68 | 4.6 | 87.784 | 3.7164 | 4.75 |  | 13466 |  | 16456 |  | 24702 |  | 33160 |  | 13.466 |  | 16.456 |  | 24.702 |  | 33.16 |  | 87.784 | 0 | -1.11e-14% |  | 88 | 2257.38 | 66.47 |  | 70.4
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 4268 | 4068 | 3800 | 7152 | 6388 | 6152 | 2860 | 5052 | 4148 | 6102 | 7662 | 7860 | 7466 | 7150 | 5670 | 5514 | 5412 | 3300 | 6996 | 5745 | 7184 | 8632 | 7020 | 6844 | 4100 | 6952 | 3420 | 3056 | 5872 | 3422 | 6164 | 4716 | 6208 | 5104 | 8556 | 8624 | 6180 | 4920 | 5324 | 4338 | 3536 | 3794 | 4236 | 3528 | 4.52 | 4.61 | 4.6 | 5.2 | 5.11 | 5.17 | 4.42 | 5.73 | 4.86 | 5.41 | 5.49 | 5.61 | 5.42 | 5.37 | 5.08 | 4.85 | 4.87 | 4.29 | 5.26 | 4.81 | 5.4 | 5.55 | 5.94 | 6.34 | 5.5 | 6.47 | 4.09 | 4.37 | 4.82 | 4.79 | 4.75 | 4.52 | 5.61 | 4.8 | 5.37 | 5.88 | 5.2 | 4.57 | 4.92 | 4.29 | 4.61 | 4.8 | 4.98 | 4.73 | 244.495 | 5.0677 | 6.47 |  | 63206 |  | 80047 |  | 53616 |  | 47626 |  | 63.206 |  | 80.047 |  | 53.616 |  | 47.626 |  | 244.495 | 0 | -1.11e-14% |  | 89 | 25300 | 261.94 |  | 70.4
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 6296 | 4972 | 4080 | 5304 | 10732 | 9008 | 5052 | 4672 | 3214 | 4976 | 5884 | 7356 | 8586 | 8718 | 6402 | 7596 | 8356 | 5740 | 10008 | 8600 | 5096 | 5336 | 6688 | 8336 | 8316 | 8028 | 4244 | 5576 | 4028 | 7408 | 9640 | 5766 | 10360 | 7964 | 7744 | 11976 | 7700 | 8872 | 8504 | 6352 | 7568 | 7352 | 9220 | 8084 | 5.1 | 4.96 | 4.74 | 5 | 6.19 | 6.02 | 5.03 | 5.12 | 4.64 | 5.25 | 5.11 | 5.52 | 5.84 | 5.87 | 5.48 | 5.7 | 5.68 | 5.27 | 5.98 | 5.65 | 5.05 | 4.95 | 5.37 | 6.07 | 6.26 | 6.2 | 4.63 | 4.68 | 4.76 | 5.15 | 5.85 | 5.01 | 6.55 | 5.63 | 5.26 | 6.87 | 4.8 | 5.68 | 5.94 | 5.09 | 5.35 | 5.44 | 6.04 | 5.98 | 315.71 | 5.4718 | 6.87 |  | 66056 |  | 86828 |  | 80882 |  | 81944 |  | 66.056 |  | 86.828 |  | 80.882 |  | 81.944 |  | 315.71 | 0 | 2.22e-14% |  | 95 | 25676 | 310.38 |  | 70.4
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 2864 | 2514 | 2568 | 2582 | 2348 | 1772 | 2086 | 1076 | 770 | 922 | 942 | 1016 | 1002 | 546 | 562 | 706 | 894 | 2588 | 948 | 819 | 2296 | 2480 | 1360 | 1556 | 1696 | 1508 | 1344 | 1312 | 2600 | 1758 | 1100 | 1526 | 2160 | 2624 | 1444 | 2944 | 2740 | 2456 | 2628 | 1136 | 1716 | 1784 | 2800 | 2544 | 3.75 | 3.9 | 3.77 | 3.82 | 3.63 | 3.71 | 3.81 | 3.04 | 2.96 | 3.25 | 3.06 | 3.27 | 3.08 | 2.93 | 3.05 | 3.1 | 3.42 | 3.91 | 3.15 | 3.08 | 3.88 | 3.78 | 3.07 | 3.8 | 3.58 | 3.47 | 3.43 | 3.06 | 4 | 3.38 | 3 | 3.29 | 4.05 | 3.83 | 3.1 | 4.1 | 4.17 | 3.59 | 4.09 | 2.9 | 3.31 | 3.58 | 4.03 | 4.18 | 77.037 | 3.5082 | 4.18 |  | 11848 |  | 16977 |  | 21198 |  | 27014 |  | 11.848 |  | 16.977 |  | 21.198 |  | 27.014 |  | 77.037 | 0 | 0% |  | 94 | 7538.5 | 72.74 |  | 70.4
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 2716 | 2818 | 3052 | 3092 | 3528 | 2796 | 2618 | 2496 | 1856 | 2022 | 2102 | 2154 | 2434 | 1572 | 798 | 1024 | 1380 | 3196 | 1406 | 1083 | 3124 | 3560 | 3108 | 2848 | 3372 | 3032 | 3404 | 2240 | 2868 | 3262 | 1412 | 1696 | 3168 | 2904 | 3116 | 4976 | 4096 | 3300 | 3096 | 1672 | 2784 | 3192 | 3516 | 3316 | 3.96 | 4.34 | 4.27 | 3.99 | 4.15 | 4.29 | 4.33 | 3.96 | 3.8 | 4.17 | 3.88 | 4.03 | 4.02 | 4.03 | 3.52 | 3.7 | 4.02 | 4.42 | 3.89 | 3.63 | 4.3 | 4.34 | 3.96 | 4.35 | 4.3 | 4.22 | 3.98 | 3.89 | 4.03 | 4.39 | 3.61 | 3.66 | 4.53 | 4.07 | 4.04 | 5.01 | 4.83 | 4.02 | 4.4 | 3.65 | 4.19 | 4.59 | 4.67 | 4.89 | 117.205 | 4.1436 | 5.01 |  | 25424 |  | 24435 |  | 29560 |  | 37786 |  | 25.424 |  | 24.435 |  | 29.56 |  | 37.786 |  | 117.205 | 0 | 0% |  | 80 | 1459.87 | 115.35 |  | 70.4
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 2060 | 3368 | 3088 | 5440 | 2920 | 2352 | 2928 | 2116 | 2560 | 2424 | 2928 | 2598 | 2442 | 2302 | 1794 | 2010 | 1980 | 2884 | 2430 | 2109 | 5192 | 6060 | 4888 | 4600 | 3876 | 3448 | 932 | 1628 | 4012 | 3004 | 2596 | 1232 | 2628 | 2704 | 4318 | 4076 | 2524 | 2308 | 2484 | 1624 | 1794 | 2880 | 4144 | 1756 | 4.42 | 4.77 | 4.64 | 5.33 | 4.37 | 4.39 | 4.61 | 3.98 | 4.5 | 4.7 | 4.5 | 4.44 | 4.39 | 4.29 | 4.17 | 4.18 | 4.13 | 4.47 | 4.35 | 4.07 | 5.38 | 5.5 | 4.9 | 5.23 | 4.86 | 4.79 | 4.02 | 3.47 | 4.77 | 4.29 | 4.09 | 3.79 | 4.63 | 4.21 | 4.78 | 5.01 | 4.37 | 3.73 | 4.3 | 3.58 | 3.47 | 4.34 | 4.92 | 4.63 | 127.441 | 4.4491 | 5.5 |  | 31880 |  | 40243 |  | 23228 |  | 32090 |  | 31.88 |  | 40.243 |  | 23.228 |  | 32.09 |  | 127.441 | 0 | 0% |  | 93 | 0 | 127.87 |  | 70.4
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 3244 | 3292 | 3884 | 3042 | 2524 | 2080 | 2482 | 1488 | 976 | 926 | 1140 | 1108 | 1112 | 1008 | 936 | 1118 | 1250 | 2768 | 1508 | 1524 | 3800 | 4304 | 2012 | 1844 | 2212 | 1920 | 2236 | 1880 | 2572 | 2672 | 1566 | 1008 | 2348 | 2512 | 1958 | 3400 | 2372 | 1964 | 2248 | 2640 | 2660 | 3484 | 3868 | 2240 | 4.23 | 4.51 | 4.56 | 4.14 | 3.63 | 3.82 | 4.23 | 3.61 | 3.24 | 3.51 | 3.25 | 3.43 | 3.26 | 3.08 | 3.13 | 3.02 | 3.43 | 4.12 | 3.39 | 3.18 | 4.67 | 4.7 | 3.63 | 4.14 | 4 | 3.78 | 3.84 | 3.49 | 3.96 | 3.96 | 3.03 | 3.09 | 4.17 | 3.84 | 3.59 | 4.66 | 4.34 | 3.64 | 3.99 | 3.64 | 3.73 | 4.3 | 4.67 | 4.24 | 97.13 | 3.8152 | 4.7 |  | 14738 |  | 24586 |  | 20456 |  | 37350 |  | 14.738 |  | 24.586 |  | 20.456 |  | 37.35 |  | 97.13 | 0 | 0% |  | 42 | 0 | 89.31 |  | 70.4
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 4816 | 6158 | 6360 | 4018 | 2620 | 2224 | 3702 | 1354 | 864 | 940 | 1064 | 1380 | 1418 | 1652 | 1514 | 1754 | 1870 | 4848 | 2142 | 1905 | 3932 | 4732 | 2128 | 2264 | 2656 | 2448 | 6486 | 2492 | 3980 | 3524 | 1970 | 604 | 2424 | 3584 | 2560 | 4672 | 3496 | 3156 | 3300 | 2890 | 4412 | 4524 | 4924 | 3876 | 4.79 | 5.37 | 5.5 | 4.86 | 4.04 | 4.26 | 4.86 | 3.65 | 3.57 | 3.76 | 3.51 | 3.8 | 3.77 | 3.82 | 3.92 | 3.88 | 4 | 5.07 | 4.1 | 3.75 | 4.99 | 5.12 | 3.84 | 4.43 | 4.38 | 4.32 | 5.13 | 4.03 | 4.83 | 4.52 | 3.62 | 3.43 | 4.5 | 4.43 | 4.07 | 5.13 | 4.88 | 4.17 | 4.58 | 3.96 | 4.6 | 4.9 | 5.19 | 4.99 | 133.637 | 4.3709 | 5.5 |  | 16516 |  | 32029 |  | 26080 |  | 59012 |  | 16.516 |  | 32.029 |  | 26.08 |  | 59.012 |  | 133.637 | 0 | 0% |  | 88 | 753.5 | 120.74 |  | 70.4
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 3588 | 1666 | 2912 | 2518 | 2796 | 2304 | 3262 | 1310 | 772 | 796 | 884 | 1082 | 1258 | 1118 | 1130 | 1160 | 1552 | 3528 | 1812 | 1467 | 2608 | 2816 | 1656 | 1684 | 2024 | 1904 | 2276 | 1236 | 2236 | 2142 | 1766 | 1798 | 2904 | 3448 | 1660 | 3304 | 3252 | 1624 | 3272 | 1198 | 1706 | 2192 | 3764 | 3380 | 4.41 | 4.43 | 4.37 | 4.17 | 4.12 | 4.38 | 4.57 | 3.88 | 3.53 | 3.84 | 3.64 | 3.84 | 3.87 | 3.71 | 3.73 | 3.64 | 4 | 4.45 | 4.14 | 3.7 | 4.47 | 4.4 | 3.93 | 4.41 | 4.5 | 4.48 | 3.79 | 3.21 | 4.16 | 3.87 | 3.66 | 3.86 | 4.64 | 4.52 | 3.76 | 4.86 | 4.86 | 4.33 | 4.69 | 3.08 | 3.49 | 4.05 | 4.75 | 4.69 | 92.765 | 4.1109 | 4.86 |  | 13370 |  | 21843 |  | 24702 |  | 32850 |  | 13.37 |  | 21.843 |  | 24.702 |  | 32.85 |  | 92.765 | 0 | 2.22e-14% |  | 57 | 0 | 98.25 |  | 70.4
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 5684 | 5040 | 3864 | 4080 | 3472 | 3760 | 5310 | 2120 | 1412 | 1598 | 1914 | 2114 | 2158 | 2354 | 2188 | 2644 | 2842 | 3504 | 2940 | 2546 | 3968 | 3264 | 2184 | 2680 | 2864 | 2632 | 3202 | 1676 | 4084 | 2292 | 2702 | 2586 | 3384 | 3928 | 2786 | 4772 | 4544 | 3144 | 3176 | 2280 | 2364 | 2540 | 5452 | 5684 | 4.83 | 4.93 | 4.44 | 4.78 | 4.13 | 4.67 | 5.02 | 3.85 | 3.49 | 3.89 | 3.75 | 3.96 | 3.95 | 3.9 | 3.96 | 4.05 | 4.19 | 4.51 | 4.25 | 3.91 | 4.9 | 4.36 | 3.73 | 4.49 | 4.42 | 4.31 | 3.9 | 3.33 | 4.81 | 3.77 | 3.73 | 3.98 | 4.65 | 4.52 | 4.08 | 5.16 | 5.21 | 4.22 | 5.39 | 3.6 | 3.69 | 3.96 | 5.09 | 5.26 | 139.732 | 4.2959 | 5.39 |  | 21676 |  | 36398 |  | 32766 |  | 48892 |  | 21.676 |  | 36.398 |  | 32.766 |  | 48.892 |  | 139.732 | 0 | 0% |  | 57 | 786.88 | 137.01 |  | 70.4
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 10424 | 12190 | 6296 | 7670 | 7064 | 7756 | 11548 | 3632 | 2030 | 2106 | 2814 | 3628 | 4604 | 4408 | 4292 | 4496 | 4924 | 9236 | 5034 | 4201 | 6720 | 5204 | 3724 | 4296 | 4368 | 4048 | 4240 | 3476 | 7492 | 4094 | 4744 | 4258 | 6916 | 8448 | 3622 | 9128 | 9048 | 6536 | 8824 | 4904 | 2812 | 3112 | 10932 | 12068 | 6.35 | 6.56 | 5.27 | 5.94 | 5.41 | 6.01 | 6.63 | 4.67 | 4.11 | 4.51 | 4.41 | 4.8 | 5.12 | 5.06 | 5.16 | 5.16 | 5.07 | 5.98 | 5.27 | 4.78 | 5.77 | 5.06 | 4.41 | 5.11 | 5.05 | 4.95 | 4.4 | 4.63 | 5.88 | 4.84 | 4.72 | 5.02 | 5.88 | 5.85 | 4.42 | 6.56 | 6.41 | 5.24 | 6.21 | 5.1 | 5.67 | 5.9 | 6.79 | 6.9 | 261.367 | 5.3873 | 6.9 |  | 35250 |  | 62807 |  | 67978 |  | 95332 |  | 35.25 |  | 62.807 |  | 67.978 |  | 95.332 |  | 261.367 | 0 | -2.22e-14% |  | 96 | 559 | 246.08 |  | 70.4
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 8048 | 6866 | 6204 | 6172 | 8244 | 6180 | 4388 | 3544 | 2542 | 3226 | 3752 | 4476 | 4496 | 4530 | 4392 | 5048 | 5862 | 7580 | 5384 | 4687 | 6188 | 6220 | 4844 | 5336 | 5680 | 5264 | 4884 | 482 | 5216 | 820 | 6316 | 4034 | 7780 | 8520 | 4568 | 7112 | 7456 | 6608 | 7756 | 2994 | 3082 | 3576 | 6392 | 7284 | 5.51 | 5.34 | 5.21 | 5.4 | 5.59 | 5.55 | 5.36 | 4.69 | 4.41 | 4.92 | 4.84 | 4.96 | 5.01 | 5.03 | 5.11 | 5.25 | 5.29 | 5.57 | 5.2 | 4.8 | 5.51 | 5.26 | 4.77 | 5.29 | 5.29 | 5.18 | 4.43 | 3.14 | 5.21 | 3.73 | 5.14 | 4.93 | 6.01 | 5.7 | 4.66 | 6 | 6.04 | 5.17 | 5.83 | 4.21 | 4.34 | 4.72 | 5.67 | 5.83 | 234.033 | 5.1159 | 6.04 |  | 43160 |  | 64583 |  | 63690 |  | 62600 |  | 43.16 |  | 64.583 |  | 63.69 |  | 62.6 |  | 234.033 | 0 | 0% |  | 96 | 1616 | 228.85 |  | 70.4
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 9372 | 7640 | 7404 | 7204 | 6904 | 5168 | 7328 | 3656 | 2614 | 3416 | 3996 | 4676 | 4802 | 5186 | 4848 | 6084 | 6810 | 8040 | 6078 | 5279 | 6748 | 7992 | 4904 | 5392 | 6312 | 6128 | 5726 | 3162 | 6636 | 4012 | 7254 | 3960 | 6420 | 8160 | 5812 | 10452 | 10084 | 8388 | 8116 | 3196 | 2426 | 4840 | 9440 | 7704 | 6.03 | 5.74 | 5.79 | 5.84 | 5.39 | 5.26 | 5.84 | 4.79 | 4.39 | 4.92 | 4.78 | 5 | 5.17 | 5.35 | 5.38 | 5.72 | 5.63 | 6.01 | 5.5 | 5.08 | 5.87 | 5.88 | 4.96 | 5.5 | 5.78 | 5.79 | 4.92 | 4.06 | 5.85 | 4.61 | 5.47 | 4.9 | 5.72 | 5.86 | 5.19 | 6.85 | 6.72 | 5.82 | 6.07 | 3.83 | 4.36 | 4.86 | 6.38 | 6.02 | 269.769 | 5.4291 | 6.85 |  | 45896 |  | 75931 |  | 67652 |  | 80290 |  | 45.896 |  | 75.931 |  | 67.652 |  | 80.29 |  | 269.769 | 0 | 0% |  | 96 | 275 | 262.35 |  | 70.4
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 10252 | 8528 | 9040 | 5548 | 5512 | 4576 | 9688 | 1936 | 1346 | 1522 | 1848 | 2180 | 2054 | 2208 | 1996 | 2324 | 2952 | 9008 | 2884 | 2956 | 7852 | 8448 | 3824 | 3912 | 4724 | 3824 | 6906 | 3808 | 5404 | 5510 | 3404 | 2072 | 5196 | 7980 | 3836 | 7772 | 6076 | 6068 | 6396 | 3194 | 5612 | 7896 | 11188 | 8320 | 5.88 | 5.68 | 5.92 | 5.18 | 4.92 | 5.01 | 6.16 | 3.96 | 3.7 | 4 | 3.79 | 4.06 | 4.03 | 4.09 | 4.09 | 4.21 | 4.43 | 5.93 | 4.35 | 4.19 | 5.87 | 5.87 | 4.52 | 4.93 | 5.11 | 4.82 | 5.11 | 4.57 | 5.26 | 5.17 | 4.23 | 3.91 | 5.32 | 5.58 | 4.42 | 6.17 | 5.62 | 5.01 | 5.35 | 3.93 | 4.96 | 5.59 | 6.62 | 5.96 | 227.58 | 4.9427 | 6.62 |  | 27170 |  | 49812 |  | 51648 |  | 98950 |  | 27.17 |  | 49.812 |  | 51.648 |  | 98.95 |  | 227.58 | 0 | -1.11e-14% |  | 96 | 2148 | 219.75 |  | 70.4
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 8752 | 10494 | 11348 | 5314 | 5624 | 5428 | 6458 | 3284 | 2346 | 2432 | 2628 | 2916 | 2880 | 2448 | 2096 | 2540 | 2974 | 7524 | 2560 | 2070 | 5224 | 5896 | 3704 | 3560 | 4268 | 3784 | 10572 | 5176 | 5960 | 6360 | 2934 | 3408 | 5572 | 6320 | 3756 | 7904 | 7272 | 5684 | 6216 | 5606 | 7404 | 8664 | 7740 | 6140 | 5.61 | 6.22 | 6.46 | 5.16 | 4.56 | 5.12 | 5.53 | 4.56 | 4.31 | 4.57 | 4.21 | 4.34 | 4.28 | 4.06 | 4.1 | 4.08 | 4.3 | 5.69 | 4.21 | 3.71 | 5.17 | 5.15 | 4.33 | 4.79 | 4.85 | 4.67 | 6.02 | 4.74 | 5.28 | 5.11 | 3.74 | 4.43 | 5.18 | 5.13 | 4.36 | 5.93 | 5.75 | 4.82 | 5.3 | 4.59 | 5.34 | 5.7 | 5.78 | 5.51 | 231.24 | 4.9261 | 6.46 |  | 31802 |  | 43772 |  | 53428 |  | 102238 |  | 31.802 |  | 43.772 |  | 53.428 |  | 102.238 |  | 231.24 | 0 | 0% |  | 96 | 654 | 223.32 |  | 70.4
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 12860 | 14146 | 15412 | 4154 | 8044 | 6360 | 8280 | 1792 | 862 | 700 | 724 | 812 | 1028 | 1316 | 1186 | 1692 | 2434 | 11076 | 1606 | 1318 | 6200 | 7796 | 2760 | 2600 | 3512 | 2928 | 13956 | 6452 | 4752 | 7662 | 2122 | 3868 | 7772 | 8560 | 2872 | 8824 | 7508 | 7052 | 7100 | 9034 | 8356 | 10844 | 10088 | 6440 | 6.01 | 6.54 | 6.81 | 4.9 | 5.3 | 5.22 | 5.69 | 4.42 | 3.81 | 4 | 3.67 | 3.89 | 3.8 | 3.98 | 3.92 | 4.05 | 4.63 | 5.94 | 4.13 | 3.85 | 6.03 | 6.78 | 4.48 | 4.96 | 5.45 | 5.29 | 6.33 | 5.06 | 5.01 | 5.45 | 4.21 | 4.58 | 5.75 | 5.42 | 4.85 | 6.04 | 5.69 | 5.05 | 5.28 | 5.22 | 5.33 | 5.89 | 5.94 | 5.48 | 254.86 | 5.0939 | 6.81 |  | 17718 |  | 37448 |  | 65088 |  | 134606 |  | 17.718 |  | 37.448 |  | 65.088 |  | 134.606 |  | 254.86 | 0 | -1.11e-14% |  | 52 | 409 | 249.16 |  | 70.4
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 11848 | 9914 | 9336 | 7400 | 10516 | 7636 | 9334 | 3618 | 2236 | 3346 | 3888 | 4528 | 4960 | 4768 | 4528 | 5788 | 7052 | 9612 | 5256 | 4855 | 7872 | 8956 | 5040 | 5504 | 6236 | 5984 | 6604 | 4808 | 7580 | 5616 | 6358 | 4282 | 9732 | 11024 | 5388 | 7504 | 7832 | 7608 | 8672 | 7524 | 6680 | 8652 | 9644 | 6100 | 5.91 | 5.82 | 5.71 | 5.53 | 5.67 | 5.4 | 5.83 | 4.57 | 4.07 | 4.74 | 4.58 | 4.76 | 4.92 | 4.83 | 4.88 | 5.08 | 5.39 | 5.8 | 4.95 | 4.58 | 5.73 | 5.77 | 4.72 | 5.37 | 5.44 | 5.37 | 4.63 | 4.61 | 5.48 | 4.96 | 4.98 | 4.56 | 6.18 | 6.05 | 4.81 | 5.9 | 5.76 | 5.17 | 5.7 | 4.96 | 4.99 | 5.56 | 6.05 | 5.66 | 301.619 | 5.2598 | 6.18 |  | 45340 |  | 75801 |  | 74806 |  | 105672 |  | 45.34 |  | 75.801 |  | 74.806 |  | 105.672 |  | 301.619 | 0 | 0% |  | 54 | 1534 | 288.87 |  | 70.4
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 15284 | 11874 | 11896 | 8462 | 12948 | 13064 | 13038 | 4766 | 3500 | 4270 | 4484 | 4816 | 4888 | 5088 | 4234 | 5196 | 5596 | 13036 | 5816 | 4839 | 9548 | 10992 | 7196 | 7096 | 8764 | 7728 | 9738 | 5820 | 8528 | 8864 | 5484 | 5638 | 13948 | 17140 | 6798 | 14928 | 15268 | 14804 | 15024 | 6020 | 9376 | 12416 | 13312 | 15068 | 7.05 | 6.47 | 6.5 | 6.17 | 7 | 7.22 | 6.94 | 5.27 | 5.03 | 5.58 | 5.23 | 5.25 | 5.46 | 5.51 | 5.38 | 5.6 | 5.45 | 6.95 | 5.57 | 5.14 | 6.47 | 6.65 | 5.68 | 6.06 | 6.52 | 6.28 | 5.72 | 5.2 | 6.18 | 6.07 | 5.28 | 5.62 | 7.63 | 7.65 | 5.6 | 8.07 | 7.7 | 7.02 | 7.41 | 5.01 | 6.14 | 6.75 | 7.58 | 7.54 | 406.593 | 6.2409 | 8.07 |  | 57508 |  | 80581 |  | 122762 |  | 145742 |  | 57.508 |  | 80.581 |  | 122.762 |  | 145.742 |  | 406.593 | 0 | -1.11e-14% |  | 95 | 6832 | 398.35 |  | 70.4
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 15976 | 12770 | 12612 | 10010 | 11112 | 7176 | 14158 | 4776 | 3140 | 3936 | 4360 | 4548 | 4646 | 4580 | 4064 | 5096 | 5804 | 14696 | 5658 | 5017 | 11860 | 12088 | 7464 | 7344 | 8116 | 6556 | 8210 | 4848 | 8776 | 7210 | 6166 | 3616 | 9868 | 11124 | 6944 | 7432 | 9120 | 8864 | 9816 | 6288 | 8292 | 10952 | 15328 | 13316 | 6.84 | 6.52 | 6.52 | 6.15 | 6.17 | 5.58 | 6.93 | 5.05 | 4.6 | 5.11 | 4.86 | 4.88 | 4.96 | 4.94 | 4.94 | 5.09 | 5.2 | 6.94 | 5.16 | 4.81 | 6.54 | 6.51 | 5.42 | 5.84 | 6.02 | 5.61 | 5.44 | 4.81 | 5.96 | 5.52 | 5.02 | 4.55 | 6.4 | 6.15 | 5.25 | 6.46 | 6.17 | 5.57 | 6.12 | 4.91 | 5.65 | 6.16 | 7.18 | 6.85 | 363.733 | 5.7127 | 7.18 |  | 54886 |  | 86063 |  | 78128 |  | 144656 |  | 54.886 |  | 86.063 |  | 78.128 |  | 144.656 |  | 363.733 | 0 | 0% |  | 90 | 1677 | 353.43 |  | 70.4
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 13680 | 13158 | 13488 | 8300 | 10264 | 7384 | 10792 | 3822 | 2828 | 3448 | 3536 | 3702 | 3660 | 3876 | 3660 | 4466 | 4928 | 12576 | 4910 | 4344 | 9272 | 10664 | 5864 | 6008 | 6416 | 5564 | 11814 | 4048 | 7996 | 5792 | 5648 | 4340 | 9520 | 8880 | 5436 | 8876 | 5292 | 8108 | 8848 | 4104 | 6444 | 8614 | 11768 | 10300 | 6.71 | 6.79 | 7.01 | 5.94 | 6.38 | 6.03 | 6.49 | 4.85 | 4.65 | 5.16 | 4.78 | 4.81 | 4.88 | 4.95 | 4.99 | 5.26 | 5.18 | 6.83 | 5.23 | 4.9 | 6.23 | 6.42 | 5.22 | 5.66 | 5.81 | 5.58 | 6.52 | 4.7 | 6 | 5.39 | 5.18 | 5.29 | 6.63 | 5.98 | 4.95 | 6.56 | 6.19 | 5.74 | 6.28 | 4.51 | 5.5 | 5.98 | 6.74 | 6.59 | 316.438 | 5.7152 | 7.01 |  | 44848 |  | 73500 |  | 71512 |  | 126578 |  | 44.848 |  | 73.5 |  | 71.512 |  | 126.578 |  | 316.438 | 0 | 0% |  | 96 | 2198 | 305.33 |  | 70.4
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 14444 | 12916 | 12512 | 6832 | 7132 | 5584 | 12548 | 3418 | 2158 | 2478 | 2616 | 2986 | 2762 | 2916 | 2752 | 3098 | 3614 | 12772 | 3732 | 3553 | 9992 | 11776 | 5596 | 5596 | 6704 | 5404 | 10238 | 5266 | 6368 | 7618 | 4176 | 3340 | 6752 | 7816 | 5444 | 9800 | 7772 | 7272 | 7304 | 6668 | 7058 | 11286 | 13840 | 10576 | 6.32 | 6.31 | 6.23 | 5.04 | 4.93 | 4.91 | 6.3 | 4.52 | 4.13 | 4.42 | 4.13 | 4.3 | 4.2 | 4.16 | 4.19 | 4.17 | 4.49 | 6.27 | 4.4 | 4.18 | 5.93 | 6.19 | 4.84 | 5.3 | 5.5 | 5.16 | 5.58 | 4.71 | 5.07 | 5.41 | 4.21 | 4.28 | 5.42 | 5.2 | 4.76 | 6.22 | 5.65 | 5 | 5.26 | 4.57 | 5.01 | 5.95 | 6.58 | 6.03 | 304.485 | 5.1234 | 6.58 |  | 39718 |  | 64253 |  | 62772 |  | 137742 |  | 39.718 |  | 64.253 |  | 62.772 |  | 137.742 |  | 304.485 | 0 | 0% |  | 96 | 8829.63 | 290.9 |  | 70.4
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 7024 | 7886 | 8292 | 4064 | 3800 | 3248 | 6370 | 2004 | 1064 | 1256 | 1392 | 1772 | 1664 | 1800 | 1636 | 1796 | 1942 | 7492 | 2364 | 2073 | 6348 | 7508 | 3160 | 3128 | 3956 | 3272 | 7778 | 5382 | 3704 | 6804 | 2336 | 2038 | 3604 | 4900 | 4026 | 6560 | 4824 | 4476 | 4364 | 5864 | 5564 | 8416 | 7520 | 6224 | 4.9 | 5.48 | 5.52 | 4.23 | 4.18 | 4.42 | 5.14 | 3.96 | 3.54 | 3.9 | 3.6 | 3.89 | 3.72 | 3.68 | 3.67 | 3.66 | 3.84 | 5.33 | 3.93 | 3.61 | 5.22 | 5.27 | 4.22 | 4.69 | 4.82 | 4.56 | 5.08 | 4.65 | 4.16 | 5.18 | 3.47 | 3.79 | 4.67 | 4.64 | 4.33 | 5.55 | 5.1 | 4.44 | 4.75 | 4.36 | 4.54 | 5.43 | 5.48 | 5.3 | 190.695 | 4.4977 | 5.55 |  | 22668 |  | 39597 |  | 37814 |  | 90616 |  | 22.668 |  | 39.597 |  | 37.814 |  | 90.616 |  | 190.695 | 0 | 0% |  | 96 | 4696.13 | 186.07 |  | 70.4
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 3564 | 3242 | 2616 | 3462 | 2120 | 2144 | 3370 | 2470 | 1926 | 1778 | 3022 | 3280 | 3238 | 2876 | 2724 | 2960 | 3342 | 3552 | 3516 | 3202 | 4032 | 3948 | 3136 | 3496 | 3852 | 3564 | 2130 | 908 | 3192 | 1262 | 3684 | 1490 | 2092 | 1932 | 3240 | 3292 | 2560 | 1884 | 2156 | 1288 | 1178 | 1676 | 3784 | 3280 | 4.56 | 4.74 | 4.26 | 4.2 | 3.84 | 4.33 | 4.72 | 4.03 | 3.9 | 4.36 | 4.26 | 4.44 | 4.36 | 4.16 | 4.23 | 4.16 | 4.35 | 4.58 | 4.41 | 4.06 | 4.76 | 4.5 | 4.14 | 4.81 | 4.75 | 4.62 | 3.55 | 3.18 | 4.11 | 3.69 | 4.06 | 3.73 | 4.4 | 3.95 | 4.14 | 5.27 | 4.92 | 3.85 | 4.27 | 3.2 | 3.35 | 3.93 | 5.27 | 4.89 | 121.46 | 4.2566 | 5.27 |  | 29762 |  | 40178 |  | 19670 |  | 31850 |  | 29.762 |  | 40.178 |  | 19.67 |  | 31.85 |  | 121.46 | 0 | 2.22e-14% |  | 68 | 480 | 123.66 |  | 70.4
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 7452 | 5908 | 5648 | 5262 | 5500 | 4176 | 6712 | 994 | 1904 | 2586 | 3026 | 3416 | 3490 | 3348 | 3192 | 3524 | 3978 | 6956 | 3580 | 3241 | 6220 | 5972 | 1584 | 1536 | 1844 | 1308 | 4084 | 2696 | 4200 | 3742 | 3810 | 2596 | 5180 | 6252 | 4488 | 6128 | 6048 | 1312 | 5680 | 3648 | 3764 | 4762 | 7880 | 6892 | 5.2 | 5.09 | 5.11 | 4.88 | 4.64 | 4.77 | 5.37 | 3.89 | 3.8 | 4.35 | 4.19 | 4.4 | 4.33 | 4.3 | 4.34 | 4.28 | 4.51 | 5.36 | 4.37 | 4.02 | 5.36 | 5.16 | 3.96 | 4.34 | 4.56 | 4.27 | 4.22 | 3.85 | 4.6 | 4.5 | 4.02 | 3.96 | 5.2 | 5.03 | 4.52 | 5.65 | 5.41 | 4.71 | 5.06 | 4.01 | 4.26 | 4.73 | 5.79 | 5.58 | 185.519 | 4.6352 | 5.79 |  | 21688 |  | 50815 |  | 42872 |  | 70144 |  | 21.688 |  | 50.815 |  | 42.872 |  | 70.144 |  | 185.519 | 0 | 0% |  | 96 | 2995.5 | 185.49 |  | 70.4
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 5176 | 4024 | 3460 | 3884 | 5396 | 4756 | 4432 | 2468 | 720 | 710 | 780 | 852 | 894 | 2644 | 2464 | 2842 | 3594 | 4136 | 3436 | 3144 | 4168 | 3564 | 3216 | 3620 | 4344 | 3904 | 2804 | 1252 | 3132 | 1966 | 3540 | 2584 | 4984 | 6472 | 3216 | 5352 | 5860 | 3344 | 5456 | 1876 | 2046 | 2598 | 5744 | 5948 | 4.77 | 4.63 | 4.45 | 4.82 | 5.19 | 5.26 | 4.92 | 4.33 | 3.87 | 4.17 | 3.84 | 4.04 | 4 | 4.35 | 4.36 | 4.49 | 4.75 | 4.78 | 4.67 | 4.36 | 5.12 | 4.65 | 4.35 | 4.96 | 5.12 | 5 | 3.8 | 3.29 | 4.54 | 3.93 | 4.37 | 4.28 | 5.42 | 5.37 | 4.31 | 5.58 | 5.65 | 5.01 | 5.64 | 3.62 | 3.77 | 4.23 | 5.39 | 5.55 | 150.802 | 4.6136 | 5.65 |  | 21508 |  | 39628 |  | 44204 |  | 45462 |  | 21.508 |  | 39.628 |  | 44.204 |  | 45.462 |  | 150.802 | 0 | 2.22e-14% |  | 54 | 0 | 152.06 |  | 70.4
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 6648 | 4724 | 4068 | 5136 | 5292 | 3564 | 5910 | 2316 | 1188 | 1320 | 1536 | 1712 | 2030 | 2300 | 2200 | 2684 | 3294 | 6260 | 3364 | 2969 | 5980 | 6040 | 3576 | 3608 | 4272 | 3968 | 3424 | 1296 | 3976 | 2598 | 3710 | 1280 | 4612 | 5452 | 4040 | 5648 | 5228 | 4772 | 6416 | 1788 | 2118 | 3224 | 7256 | 7388 | 4.99 | 4.83 | 4.67 | 4.85 | 4.83 | 4.58 | 5.14 | 4.13 | 3.63 | 3.92 | 3.73 | 3.88 | 3.99 | 4.05 | 4.15 | 4.18 | 4.41 | 5.24 | 4.44 | 4.04 | 5.33 | 5.19 | 4.33 | 4.81 | 5 | 5.03 | 4.12 | 3.25 | 4.58 | 4.16 | 4.11 | 3.53 | 5.06 | 5.33 | 4.5 | 5.56 | 5.37 | 4.87 | 5.37 | 3.28 | 3.63 | 4.34 | 5.66 | 5.76 | 170.185 | 4.542 | 5.76 |  | 25526 |  | 45693 |  | 42264 |  | 56702 |  | 25.526 |  | 45.693 |  | 42.264 |  | 56.702 |  | 170.185 | 0 | 0% |  | 40 | 435.62 | 173.65 |  | 70.4
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 5692 | 4588 | 4000 | 4256 | 4616 | 1684 | 3182 | 2448 | 2012 | 2256 | 2516 | 2744 | 2988 | 824 | 882 | 954 | 900 | 5020 | 1124 | 897 | 4176 | 3892 | 3104 | 3336 | 3776 | 3280 | 4152 | 2010 | 3764 | 3298 | 746 | 2972 | 4552 | 5872 | 3396 | 4964 | 5152 | 4700 | 5328 | 1756 | 2548 | 3328 | 5704 | 5308 | 4.65 | 4.63 | 4.42 | 4.49 | 4.66 | 4.54 | 4.11 | 4.1 | 4.05 | 4.38 | 4.12 | 4.3 | 4.33 | 3.63 | 3.76 | 3.83 | 3.83 | 4.76 | 3.91 | 3.72 | 4.72 | 4.4 | 4.11 | 4.69 | 4.74 | 4.59 | 4.17 | 3.41 | 4.36 | 4.1 | 3.19 | 4.37 | 5.06 | 5.05 | 4.19 | 5.01 | 5.12 | 4.54 | 5.09 | 3.12 | 3.75 | 4.13 | 4.99 | 5.07 | 144.697 | 4.3225 | 5.12 |  | 28460 |  | 25811 |  | 39840 |  | 50586 |  | 28.46 |  | 25.811 |  | 39.84 |  | 50.586 |  | 144.697 | 0 | 0% |  | 96 | 1141.62 | 143.45 |  | 70.4
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 3824 | 2852 | 2860 | 2566 | 4008 | 2728 | 2960 | 1484 | 1076 | 1476 | 1724 | 2000 | 2148 | 1974 | 1918 | 2004 | 2308 | 3400 | 2150 | 2006 | 2892 | 2720 | 2244 | 2456 | 2752 | 2476 | 2416 | 1570 | 2600 | 2098 | 2384 | 1632 | 2252 | 4356 | 2390 | 3424 | 3552 | 3536 | 3944 | 1984 | 2172 | 2656 | 3792 | 3840 | 3.8 | 4.04 | 3.87 | 3.95 | 4.33 | 4.19 | 3.96 | 3.61 | 3.32 | 3.71 | 3.57 | 3.78 | 3.76 | 3.68 | 3.84 | 3.7 | 3.97 | 4.13 | 3.86 | 3.62 | 4.42 | 4.17 | 3.81 | 4.41 | 4.33 | 4.22 | 3.43 | 3.37 | 4.07 | 3.83 | 3.53 | 3.44 | 4.54 | 4.43 | 3.85 | 4.48 | 4.59 | 4.12 | 4.57 | 3.39 | 3.64 | 4.02 | 4.3 | 4.52 | 113.604 | 3.9584 | 4.59 |  | 19836 |  | 27912 |  | 29432 |  | 36424 |  | 19.836 |  | 27.912 |  | 29.432 |  | 36.424 |  | 113.604 | 0 | -1.11e-14% |  | 96 | 12 | 110.6 |  | 70.4
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 5012 | 3940 | 3304 | 3790 | 2020 | 3148 | 4404 | 1704 | 1252 | 1540 | 1584 | 1776 | 1728 | 1878 | 1862 | 2262 | 2504 | 5480 | 2750 | 2280 | 3716 | 3836 | 2540 | 2608 | 2948 | 2620 | 2988 | 1360 | 3320 | 2360 | 2912 | 1594 | 3948 | 5376 | 2382 | 4448 | 4116 | 4132 | 4752 | 1450 | 1628 | 2396 | 4856 | 5208 | 4.48 | 4.51 | 4.21 | 4.39 | 4.28 | 4.38 | 4.66 | 3.74 | 3.56 | 3.85 | 3.6 | 3.76 | 3.66 | 3.75 | 3.85 | 3.97 | 4.12 | 4.8 | 4.14 | 3.83 | 4.65 | 4.45 | 3.88 | 4.42 | 4.3 | 4.19 | 3.74 | 3.13 | 4.31 | 3.9 | 3.87 | 3.54 | 4.76 | 4.7 | 3.73 | 4.93 | 4.87 | 4.39 | 4.82 | 3.12 | 3.41 | 3.93 | 4.96 | 5.13 | 131.712 | 4.1516 | 5.13 |  | 20300 |  | 33492 |  | 33534 |  | 44386 |  | 20.3 |  | 33.492 |  | 33.534 |  | 44.386 |  | 131.712 | 0 | 0% |  | 96 | 88.62 | 131.18 |  | 70.4
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 7672 | 6560 | 5388 | 5362 | 6732 | 5172 | 6084 | 2736 | 2032 | 2700 | 2960 | 3348 | 3376 | 3416 | 3266 | 3874 | 4404 | 8060 | 4280 | 3542 | 5192 | 5880 | 4024 | 4624 | 5232 | 4500 | 3488 | 1818 | 4840 | 2784 | 4220 | 1238 | 6408 | 7940 | 3714 | 6600 | 6332 | 6240 | 7216 | 2018 | 2456 | 3264 | 6996 | 6920 | 5.26 | 5.18 | 4.9 | 5.1 | 5.31 | 5.2 | 5.18 | 4.35 | 4.16 | 4.67 | 4.43 | 4.6 | 4.7 | 4.68 | 4.76 | 4.9 | 4.96 | 5.57 | 4.88 | 4.45 | 5.25 | 5.21 | 4.54 | 5.2 | 5.38 | 5.19 | 3.99 | 3.48 | 5.05 | 4.13 | 4.45 | 3.88 | 5.73 | 5.61 | 4.39 | 5.78 | 5.65 | 5.13 | 5.68 | 3.67 | 3.87 | 4.36 | 5.56 | 5.6 | 204.908 | 4.8641 | 5.78 |  | 35532 |  | 51990 |  | 53878 |  | 63508 |  | 35.532 |  | 51.99 |  | 53.878 |  | 63.508 |  | 204.908 | 0 | 0% |  | 96 | 691.5 | 201.28 |  | 70.4
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 13028 | 10924 | 10548 | 8370 | 10156 | 7608 | 10324 | 3228 | 2502 | 3068 | 3256 | 3080 | 3508 | 3896 | 3744 | 4368 | 4804 | 11728 | 4580 | 3627 | 8504 | 9688 | 5688 | 6040 | 6752 | 5712 | 8652 | 4224 | 7912 | 5660 | 5072 | 3712 | 9692 | 10188 | 5342 | 8264 | 7652 | 8092 | 9060 | 3480 | 6956 | 8868 | 12284 | 10192 | 6.74 | 6.33 | 6.44 | 6.16 | 6.45 | 6.08 | 6.5 | 4.66 | 4.54 | 5.03 | 4.68 | 4.66 | 4.86 | 5 | 5.05 | 5.22 | 5.14 | 6.75 | 5.03 | 4.61 | 6.19 | 6.35 | 5.25 | 5.72 | 6.02 | 5.73 | 5.7 | 4.74 | 6.08 | 5.4 | 4.98 | 5.03 | 6.72 | 6.3 | 5.1 | 6.48 | 6.23 | 5.75 | 6.34 | 4.16 | 5.6 | 6.1 | 7.02 | 6.67 | 304.033 | 5.6725 | 7.02 |  | 42834 |  | 69907 |  | 74424 |  | 116868 |  | 42.834 |  | 69.907 |  | 74.424 |  | 116.868 |  | 304.033 | 0 | 0% |  | 96 | 1791.5 | 294.64 |  | 70.4
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 13832 | 13376 | 14452 | 9372 | 9904 | 7568 | 12124 | 3156 | 1902 | 2176 | 2252 | 2558 | 2572 | 2838 | 2744 | 3324 | 4656 | 12544 | 3830 | 3599 | 11508 | 12828 | 5552 | 5348 | 6376 | 4880 | 12474 | 5426 | 8352 | 7698 | 4700 | 3292 | 9248 | 10860 | 5350 | 11476 | 8976 | 8592 | 8848 | 8212 | 9652 | 12636 | 14936 | 10844 | 6.46 | 6.62 | 7.03 | 5.8 | 6.08 | 5.74 | 6.56 | 4.44 | 4.09 | 4.42 | 4.06 | 4.25 | 4.32 | 4.41 | 4.53 | 4.67 | 5 | 6.63 | 4.77 | 4.56 | 6.37 | 6.59 | 4.89 | 5.36 | 5.52 | 5.15 | 6.49 | 4.89 | 5.66 | 5.57 | 4.8 | 4.55 | 6.38 | 6.38 | 4.87 | 6.88 | 6.25 | 5.8 | 6.01 | 5.23 | 5.84 | 6.46 | 7.19 | 6.48 | 336.843 | 5.5466 | 7.19 |  | 36772 |  | 73101 |  | 78764 |  | 148206 |  | 36.772 |  | 73.101 |  | 78.764 |  | 148.206 |  | 336.843 | 0 | -2.22e-14% |  | 96 | 2155.12 | 324.42 |  | 70.4
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 18020 | 17608 | 19048 | 8728 | 13132 | 14480 | 15656 | 5320 | 3614 | 3892 | 4036 | 4582 | 4672 | 5434 | 5448 | 7740 | 8184 | 15788 | 6674 | 5142 | 10776 | 14108 | 7508 | 7524 | 8936 | 8368 | 18474 | 10368 | 9720 | 13502 | 6864 | 7212 | 14560 | 16928 | 7470 | 18648 | 17304 | 15660 | 15340 | 13326 | 14184 | 17244 | 17032 | 14548 | 7.21 | 7.43 | 7.87 | 5.59 | 6.43 | 7.01 | 7.03 | 5.16 | 4.79 | 5.14 | 4.74 | 4.9 | 4.96 | 5.09 | 5.31 | 5.66 | 5.72 | 7.01 | 5.43 | 4.85 | 6.22 | 6.81 | 5.36 | 5.89 | 6.1 | 5.96 | 7.53 | 5.83 | 5.94 | 6.62 | 5.26 | 5.75 | 7.44 | 7.45 | 5.39 | 8.36 | 7.69 | 6.89 | 7.2 | 6.08 | 6.51 | 7.22 | 7.75 | 7.12 | 492.802 | 6.2659 | 8.36 |  | 58452 |  | 96288 |  | 133264 |  | 204798 |  | 58.452 |  | 96.288 |  | 133.264 |  | 204.798 |  | 492.802 | 0 | 0% |  | 96 | 24622.5 | 481.71 |  | 70.4
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 15716 | 17084 | 17356 | 11444 | 13600 | 13264 | 12008 | 5496 | 4982 | 5174 | 5164 | 5080 | 5140 | 5152 | 4996 | 5632 | 6528 | 16004 | 6904 | 6407 | 11140 | 13568 | 7740 | 7620 | 8616 | 7728 | 16908 | 11180 | 13656 | 13958 | 7934 | 10306 | 14164 | 14648 | 7180 | 18688 | 17564 | 14524 | 14560 | 8952 | 12608 | 13816 | 14776 | 12292 | 6.83 | 7.57 | 7.8 | 7.62 | 6.63 | 6.84 | 6.38 | 5.06 | 5.12 | 5.53 | 5.15 | 5.11 | 5.18 | 5.17 | 5.28 | 5.36 | 5.49 | 7.12 | 5.61 | 5.28 | 7.39 | 7.96 | 5.39 | 5.84 | 6.09 | 5.89 | 7.66 | 6.12 | 7.99 | 6.86 | 5.62 | 6.41 | 7.39 | 7.05 | 6.47 | 8.31 | 7.78 | 6.68 | 7 | 5.13 | 6.33 | 6.66 | 7.03 | 6.62 | 477.257 | 6.4045 | 8.31 |  | 62740 |  | 100541 |  | 131318 |  | 182658 |  | 62.74 |  | 100.541 |  | 131.318 |  | 182.658 |  | 477.257 | 0 | 2.22e-14% |  | 69 | 7746 | 477.26 |  | 70.4
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 14352 | 13288 | 11716 | 14860 | 17652 | 16288 | 12356 | 5124 | 4816 | 5494 | 5934 | 6692 | 5780 | 6400 | 5688 | 6860 | 7276 | 16256 | 7222 | 6157 | 12688 | 15212 | 8520 | 8840 | 9612 | 8216 | 13100 | 10590 | 15708 | 14436 | 8374 | 10680 | 17832 | 17348 | 8648 | 20544 | 19712 | 17128 | 17040 | 4310 | 7964 | 10622 | 15308 | 14852 | 7.01 | 6.95 | 6.79 | 7.52 | 8.02 | 7.98 | 6.93 | 5.4 | 5.47 | 5.9 | 5.65 | 5.74 | 5.69 | 5.83 | 5.75 | 6.07 | 5.92 | 7.69 | 5.93 | 5.45 | 7.08 | 7.49 | 6.08 | 6.52 | 6.85 | 6.51 | 6.95 | 6.53 | 7.69 | 7.46 | 6.04 | 6.92 | 8.58 | 7.81 | 5.94 | 9.13 | 8.64 | 7.62 | 7.93 | 4.58 | 5.77 | 6.53 | 7.55 | 7.59 | 497.495 | 6.7609 | 9.13 |  | 69028 |  | 115093 |  | 154224 |  | 159150 |  | 69.028 |  | 115.093 |  | 154.224 |  | 159.15 |  | 497.495 | 0 | 0% |  | 96 | 3622.38 | 490.15 |  | 70.4
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 17148 | 18204 | 18376 | 13192 | 12208 | 10636 | 11940 | 3746 | 4100 | 4964 | 5506 | 6066 | 5740 | 5586 | 4976 | 5796 | 7168 | 16136 | 6516 | 5584 | 12876 | 15252 | 7888 | 8260 | 9404 | 7964 | 17476 | 9450 | 14124 | 12326 | 7880 | 7194 | 11960 | 13552 | 8452 | 15548 | 14264 | 12328 | 12232 | 6472 | 10642 | 13534 | 15336 | 12316 | 7.25 | 7.68 | 7.82 | 6.87 | 6.48 | 6.49 | 6.58 | 5.05 | 5.11 | 5.51 | 5.27 | 5.34 | 5.35 | 5.28 | 5.29 | 5.41 | 5.63 | 7.35 | 5.48 | 5.11 | 6.86 | 7.24 | 5.62 | 6.1 | 6.49 | 6.2 | 7.41 | 6.09 | 7.01 | 6.77 | 5.58 | 5.74 | 6.98 | 6.78 | 5.7 | 7.96 | 7.4 | 6.45 | 6.7 | 5 | 6.33 | 6.93 | 7.43 | 6.87 | 460.318 | 6.318 | 7.96 |  | 63638 |  | 107402 |  | 109922 |  | 179356 |  | 63.638 |  | 107.402 |  | 109.922 |  | 179.356 |  | 460.318 | 0 | 0% |  | 96 | 16139.25 | 461.99 |  | 70.4
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 12724 | 11808 | 9732 | 10200 | 10908 | 10264 | 8096 | 4692 | 5048 | 6168 | 6272 | 6490 | 6116 | 6118 | 5680 | 6452 | 7052 | 11428 | 6218 | 5318 | 9312 | 10224 | 6756 | 7192 | 7668 | 6868 | 10360 | 7212 | 10568 | 9600 | 7276 | 7360 | 10860 | 11512 | 7456 | 13728 | 13516 | 11944 | 11936 | 4010 | 7984 | 9128 | 12324 | 10140 | 6.43 | 6.44 | 6.13 | 6.2 | 6.3 | 6.5 | 5.75 | 5.04 | 5.45 | 6.01 | 5.68 | 5.63 | 5.64 | 5.62 | 5.65 | 5.74 | 5.69 | 6.41 | 5.48 | 5.08 | 6.1 | 6.18 | 5.34 | 5.93 | 6 | 5.8 | 6.05 | 5.5 | 6.29 | 6.12 | 5.49 | 6.06 | 6.78 | 6.41 | 5.43 | 7.49 | 7.21 | 6.32 | 6.73 | 4.28 | 5.69 | 5.97 | 6.73 | 6.37 | 381.718 | 5.9805 | 7.49 |  | 63270 |  | 91874 |  | 102028 |  | 124546 |  | 63.27 |  | 91.874 |  | 102.028 |  | 124.546 |  | 381.718 | 0 | 0% |  | 96 | 9466.5 | 378.83 |  | 70.4
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 15556 | 11464 | 12536 | 11760 | 16608 | 14096 | 11340 | 7702 | 6558 | 9432 | 10676 | 11802 | 10824 | 9760 | 8576 | 10026 | 9694 | 12484 | 9680 | 7998 | 10784 | 11380 | 9504 | 10364 | 11568 | 10112 | 11248 | 9784 | 11776 | 12156 | 9952 | 10540 | 16516 | 16304 | 8504 | 18732 | 19164 | 16176 | 16784 | 8618 | 12436 | 12840 | 16692 | 14744 | 7.26 | 6.46 | 6.92 | 6.77 | 7.64 | 7.42 | 6.71 | 6.11 | 5.97 | 6.97 | 6.95 | 7 | 6.91 | 6.62 | 6.52 | 6.75 | 6.41 | 6.88 | 6.5 | 5.89 | 6.65 | 6.6 | 6.09 | 6.72 | 7.07 | 6.83 | 6.47 | 6.26 | 6.77 | 6.89 | 6.33 | 6.92 | 8.19 | 7.63 | 5.85 | 8.71 | 8.5 | 7.41 | 7.88 | 5.74 | 6.9 | 6.92 | 7.92 | 7.5 | 525.25 | 6.8957 | 8.71 |  | 98542 |  | 119890 |  | 144920 |  | 161898 |  | 98.542 |  | 119.89 |  | 144.92 |  | 161.898 |  | 525.25 | 0 | 0% |  | 96 | 19096.63 | 517.71 |  | 70.4
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 20072 | 16952 | 13692 | 16204 | 18348 | 19744 | 18256 | 11024 | 6920 | 7492 | 8164 | 12246 | 12604 | 12044 | 9286 | 11726 | 11166 | 14280 | 10852 | 9423 | 15124 | 13020 | 11684 | 7128 | 12112 | 10112 | 11248 | 11560 | 15624 | 13880 | 10212 | 13932 | 18252 | 15400 | 10154 | 23244 | 21828 | 14108 | 19680 | 12836 | 14862 | 16376 | 22900 | 21184 | 8.08 | 7.52 | 7.01 | 7.75 | 7.82 | 8.45 | 8.06 | 6.77 | 5.83 | 6.26 | 6.05 | 7 | 7.07 | 6.9 | 6.66 | 6.9 | 6.46 | 7.14 | 6.76 | 6.07 | 7.55 | 6.87 | 6.31 | 6.33 | 6.97 | 6.46 | 6.24 | 6.7 | 7.74 | 7.36 | 6.12 | 7.52 | 8.44 | 7.22 | 6.19 | 9.55 | 8.93 | 6.79 | 8.34 | 6.91 | 7.45 | 7.66 | 9.09 | 8.67 | 616.955 | 7.2266 | 9.55 |  | 99486 |  | 144835 |  | 164536 |  | 208098 |  | 99.486 |  | 144.835 |  | 164.536 |  | 208.098 |  | 616.955 | 0 | 0% |  | 96 | 39098.5 | 589.61 |  | 70.4
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 8252 | 9048 | 6076 | 7410 | 4716 | 6952 | 7816 | 4492 | 2574 | 1788 | 1888 | 3718 | 3184 | 2534 | 2700 | 3532 | 3372 | 6588 | 5014 | 3393 | 7048 | 6200 | 1912 | 1372 | 2588 | 3776 | 4452 | 3106 | 7176 | 3766 | 3396 | 4548 | 5480 | 3768 | 4938 | 7624 | 6828 | 3472 | 6048 | 3112 | 3604 | 4584 | 8444 | 7596 | 5.73 | 5.97 | 5.23 | 5.83 | 4.8 | 5.8 | 5.92 | 4.98 | 4.36 | 4.25 | 3.94 | 4.69 | 4.57 | 4.49 | 4.54 | 4.83 | 4.47 | 5.38 | 5.16 | 4.42 | 5.88 | 5.36 | 4.31 | 4.59 | 4.83 | 4.73 | 4.32 | 4.28 | 5.89 | 4.69 | 4.14 | 5.24 | 5.4 | 4.61 | 4.87 | 6.73 | 6.38 | 4.47 | 5.84 | 4.2 | 4.49 | 4.97 | 6.13 | 5.9 | 209.885 | 5.0366 | 6.73 |  | 27292 |  | 56713 |  | 49436 |  | 76444 |  | 27.292 |  | 56.713 |  | 49.436 |  | 76.444 |  | 209.885 | 0 | 0% |  | 96 | 7684.87 | 197.15 |  | 70.4
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 5612 | 7000 | 5152 | 5546 | 3928 | 4968 | 5450 | 3156 | 2116 | 1588 | 1944 | 2486 | 2352 | 512 | 2462 | 2840 | 3168 | 5376 | 3910 | 3110 | 5148 | 1232 | 2832 | 3112 | 1792 | 2432 | 4132 | 1742 | 5540 | 1876 | 3020 | 3134 | 3524 | 4048 | 3402 | 5968 | 5200 | 3048 | 4728 | 1762 | 2132 | 2440 | 5904 | 5324 | 5.38 | 6.13 | 5.09 | 5.12 | 4.05 | 4.87 | 5.71 | 4.31 | 3.94 | 3.9 | 3.66 | 4.11 | 3.89 | 3.71 | 4.05 | 4.2 | 4.21 | 5.5 | 4.47 | 4.03 | 5.15 | 4.46 | 3.98 | 4.47 | 3.91 | 3.93 | 4.36 | 3.54 | 5.22 | 3.86 | 3.7 | 4.28 | 4.48 | 4.1 | 4.06 | 5.43 | 5.18 | 3.84 | 4.73 | 3.39 | 3.66 | 4.02 | 5.25 | 5.87 | 156.148 | 4.4364 | 6.13 |  | 23810 |  | 39890 |  | 38546 |  | 53902 |  | 23.81 |  | 39.89 |  | 38.546 |  | 53.902 |  | 156.148 | 0 | 2.22e-14% |  | 73 | 1948.87 | 148.4 |  | 70.4
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 4208 | 4344 | 2472 | 3128 | 2596 | 3528 | 3910 | 1794 | 1010 | 1012 | 1200 | 2002 | 1834 | 1918 | 1688 | 1948 | 1936 | 2804 | 2444 | 1849 | 2900 | 1724 | 1860 | 1836 | 2020 | 1716 | 2058 | 1940 | 3188 | 2542 | 1960 | 2352 | 3020 | 2640 | 1796 | 4616 | 4148 | 2524 | 3596 | 218 | 2428 | 756 | 4552 | 4080 | 4.25 | 4.56 | 3.81 | 4.14 | 3.73 | 4.56 | 4.51 | 3.64 | 3.39 | 3.6 | 3.4 | 3.86 | 3.61 | 3.66 | 3.67 | 3.75 | 3.79 | 4.01 | 3.85 | 3.5 | 4.29 | 3.78 | 3.43 | 3.97 | 3.73 | 3.44 | 3.18 | 3.57 | 4.34 | 3.98 | 3.34 | 4.03 | 4.37 | 3.67 | 3.43 | 4.99 | 4.83 | 3.62 | 4.42 | 3.18 | 3.73 | 3.82 | 4.74 | 4.74 | 108.095 | 3.907 | 4.99 |  | 16284 |  | 26479 |  | 29020 |  | 36312 |  | 16.284 |  | 26.479 |  | 29.02 |  | 36.312 |  | 108.095 | 0 | 0% |  | 92 | 455.87 | 102.44 |  | 70.4
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 4132 | 1424 | 3340 | 2600 | 2352 | 2704 | 3216 | 1290 | 838 | 1152 | 1148 | 1378 | 1378 | 1564 | 1500 | 1840 | 2200 | 3144 | 2080 | 2027 | 2524 | 2276 | 1452 | 1636 | 1836 | 1756 | 2846 | 776 | 2616 | 1516 | 2392 | 1706 | 496 | 2188 | 1738 | 3236 | 2996 | 1940 | 3192 | 984 | 1688 | 724 | 3940 | 4028 | 3.86 | 3.93 | 3.77 | 3.68 | 3.4 | 3.8 | 3.88 | 2.94 | 2.79 | 3.15 | 3.03 | 3.29 | 3.05 | 3.18 | 3.2 | 3.32 | 3.66 | 3.76 | 3.32 | 3.22 | 3.79 | 3.56 | 2.88 | 3.72 | 3.37 | 3.32 | 3.19 | 3.02 | 3.83 | 3.48 | 3.15 | 3.36 | 3.66 | 3.6 | 3.12 | 4.28 | 4.25 | 3.46 | 4.1 | 3.08 | 3.55 | 3.47 | 4.8 | 4.36 | 91.789 | 3.5143 | 4.8 |  | 13864 |  | 25357 |  | 20810 |  | 31758 |  | 13.864 |  | 25.357 |  | 20.81 |  | 31.758 |  | 91.789 | 0 | 0% |  | 96 | 7255.25 | 97.92 |  | 70.4
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 1696 | 1248 | 1436 | 3048 | 1980 | 1336 | 1092 | 1828 | 1360 | 2200 | 2632 | 2924 | 2690 | 2362 | 2092 | 2460 | 2708 | 1504 | 2418 | 2173 | 2976 | 2896 | 2448 | 2668 | 2724 | 2400 | 1260 | 880 | 2880 | 1062 | 2592 | 824 | 0 | 1752 | 554 | 1908 | 1648 | 1812 | 1864 | 1086 | 1324 | 1120 | 1728 | 1512 | 2.88 | 3.35 | 3.1 | 3.67 | 3.64 | 3.47 | 3.05 | 3.14 | 3.1 | 3.65 | 3.55 | 3.81 | 3.64 | 3.52 | 3.61 | 3.65 | 3.85 | 3.23 | 3.62 | 3.57 | 3.85 | 3.67 | 3.24 | 4.01 | 3.66 | 3.48 | 2.75 | 2.75 | 3.8 | 3.03 | 3.52 | 2.89 | 3.71 | 3.31 | 3.18 | 3.38 | 3.61 | 3.21 | 3.6 | 2.88 | 3.05 | 3.21 | 3.19 | 3.43 | 83.105 | 3.398 | 4.01 |  | 23874 |  | 29159 |  | 13124 |  | 16948 |  | 23.874 |  | 29.159 |  | 13.124 |  | 16.948 |  | 83.105 | 0 | -2.22e-14% |  | 69 | 0 | 82.79 |  | 70.4
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 3744 | 3488 | 3020 | 516 | 568 | 1648 | 2312 | 1476 | 1120 | 1276 | 1234 | 1440 | 1528 | 1532 | 1456 | 1696 | 1836 | 3576 | 2028 | 1838 | 3020 | 3168 | 2188 | 2112 | 2484 | 2260 | 3036 | 1606 | 3032 | 2858 | 1672 | 924 | 1140 | 3368 | 1106 | 3668 | 2912 | 2804 | 3104 | 1214 | 2032 | 2948 | 4096 | 3764 | 4.06 | 4.12 | 3.95 | 3.34 | 3.29 | 3.83 | 3.8 | 3.3 | 3.29 | 3.64 | 3.38 | 3.59 | 3.52 | 3.51 | 3.51 | 3.58 | 3.66 | 3.97 | 3.51 | 3.32 | 3.93 | 3.87 | 3.46 | 4.04 | 3.92 | 3.88 | 3.59 | 3.04 | 3.73 | 3.8 | 3.19 | 3.3 | 3.88 | 4.02 | 3.35 | 4.69 | 4.36 | 3.77 | 4.26 | 2.74 | 3.32 | 3.96 | 4.45 | 4.44 | 97.848 | 3.7082 | 4.69 |  | 17118 |  | 22900 |  | 20136 |  | 37694 |  | 17.118 |  | 22.9 |  | 20.136 |  | 37.694 |  | 97.848 | 0 | 0% |  | 96 | 0 | 104.47 |  | 70.4
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 3496 | 3012 | 2848 | 1124 | 1732 | 2348 | 2580 | 1212 | 680 | 754 | 910 | 1074 | 1058 | 1086 | 932 | 1198 | 1516 | 3500 | 1588 | 1499 | 3488 | 3676 | 2028 | 2132 | 2320 | 1868 | 2526 | 1338 | 3696 | 2508 | 1812 | 1216 | 2496 | 3928 | 2352 | 3500 | 3112 | 3064 | 3572 | 1104 | 1826 | 2620 | 3908 | 3816 | 4.51 | 4.67 | 4.45 | 3.83 | 4.19 | 4.6 | 4.37 | 3.24 | 2.95 | 3.22 | 3.04 | 3.23 | 2.99 | 3.04 | 3.12 | 3.16 | 3.51 | 5.1 | 3.35 | 3.24 | 4.39 | 4.33 | 3.5 | 4.08 | 3.94 | 3.72 | 4.11 | 3.64 | 4.36 | 4.58 | 3.19 | 3.6 | 4.86 | 4.93 | 3.65 | 5.3 | 5.19 | 4.43 | 5.07 | 3.18 | 3.99 | 4.43 | 5.26 | 5.43 | 98.053 | 4.022 | 5.43 |  | 14036 |  | 23967 |  | 24968 |  | 35082 |  | 14.036 |  | 23.967 |  | 24.968 |  | 35.082 |  | 98.053 | 0 | 0% |  | 71 | 2 | 98.72 |  | 70.4
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 2396 | 1696 | 1528 | 2138 | 2536 | 1856 | 1612 | 1172 | 716 | 974 | 1332 | 1582 | 1656 | 1336 | 1392 | 1594 | 1840 | 1844 | 1634 | 1279 | 2000 | 1872 | 1312 | 1412 | 1580 | 1472 | 1090 | 888 | 2020 | 1348 | 1728 | 1116 | 2228 | 2540 | 1224 | 2404 | 2436 | 2160 | 2588 | 1184 | 1522 | 1548 | 2596 | 2116 | 3.58 | 3.64 | 3.35 | 3.76 | 3.94 | 3.81 | 3.53 | 3.11 | 2.93 | 3.3 | 3.44 | 3.6 | 3.5 | 3.49 | 3.61 | 3.74 | 3.86 | 3.55 | 3.56 | 3.43 | 3.84 | 3.68 | 3.1 | 3.86 | 3.56 | 3.5 | 2.77 | 2.85 | 3.91 | 3.23 | 3.4 | 3.2 | 4.28 | 3.8 | 3.15 | 3.92 | 4.08 | 3.56 | 4.04 | 3.1 | 3.31 | 3.54 | 3.85 | 3.87 | 74.497 | 3.5484 | 4.28 |  | 13208 |  | 20057 |  | 19864 |  | 21368 |  | 13.208 |  | 20.057 |  | 19.864 |  | 21.368 |  | 74.497 | 0 | 0% |  | 44 | 0 | 74.53 |  | 70.4
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 6200 | 4356 | 3944 | 4634 | 5800 | 4880 | 4512 | 2636 | 1916 | 2364 | 2470 | 2664 | 2298 | 2564 | 1618 | 2870 | 3096 | 5188 | 3296 | 2663 | 4400 | 4152 | 3576 | 3580 | 3856 | 3200 | 4002 | 2168 | 4416 | 3526 | 3656 | 3488 | 5680 | 6552 | 2790 | 6528 | 6436 | 5672 | 6332 | 2316 | 3208 | 3712 | 6596 | 5796 | 5.2 | 4.71 | 4.57 | 5.15 | 5.31 | 5.35 | 5 | 4.38 | 4.28 | 4.73 | 4.31 | 4.4 | 4.28 | 4.46 | 4.37 | 4.65 | 4.6 | 5.17 | 4.56 | 4.2 | 5.21 | 4.9 | 4.53 | 4.93 | 4.97 | 4.75 | 4.38 | 4 | 5.22 | 4.73 | 4.51 | 4.83 | 5.69 | 5.44 | 4.11 | 6.14 | 5.92 | 5.16 | 5.67 | 3.82 | 4.33 | 4.74 | 5.77 | 5.61 | 175.607 | 4.8418 | 6.14 |  | 28560 |  | 40155 |  | 51368 |  | 55524 |  | 28.56 |  | 40.155 |  | 51.368 |  | 55.524 |  | 175.607 | 0 | 0% |  | 95 | 0 | 167.61 |  | 70.4
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 4628 | 4100 | 3848 | 3528 | 4424 | 4044 | 4378 | 1664 | 1364 | 1426 | 1436 | 1504 | 1530 | 1630 | 1608 | 1746 | 1932 | 4764 | 1880 | 1739 | 3204 | 3128 | 2504 | 2432 | 2616 | 2212 | 4434 | 3360 | 2084 | 3230 | 2146 | 2868 | 3360 | 4252 | 3612 | 4836 | 4672 | 4584 | 5108 | 2580 | 3268 | 2936 | 5068 | 5080 | 6.93 | 6.84 | 5.77 | 5.95 | 6.95 | 6.85 | 6.97 | 3.96 | 3.95 | 3.9 | 3.96 | 3.93 | 3.8 | 3.82 | 3.98 | 3.73 | 3.95 | 6.98 | 3.69 | 3.86 | 5.73 | 5.9 | 4.95 | 5.98 | 5.93 | 5.95 | 6.78 | 5.82 | 5.44 | 6.71 | 5.98 | 5.61 | 5.52 | 6.9 | 5.62 | 6.3 | 6.67 | 6.61 | 6.67 | 4.53 | 5.98 | 4.23 | 6.53 | 6.7 | 136.747 | 5.5184 | 6.98 |  | 18688 |  | 28237 |  | 38148 |  | 51674 |  | 18.688 |  | 28.237 |  | 38.148 |  | 51.674 |  | 136.747 | 0 | 0% |  | 86 | 0 | 82.84 |  | 70.4
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 3895 | 3718 | 3584 | 3310 | 3341 | 3703 | 2536 | 2236 | 2936 | 2282 | 2193 | 2824 | 2246 | 2112 | 2219 | 2025 | 2115 | 2258 | 2295 | 2355 | 2118 | 2123 | 2245 | 2456 | 2856 | 2456 | 2984 | 2569 | 3516 | 3025 | 2734 | 2854 | 2236 | 3136 | 2854 | 3456 | 2984 | 3135 | 3892 | 3168 | 3146 | 2980 | 3350 | 3416 | 5.56 | 5.74 | 5.26 | 5.2 | 4.84 | 4.83 | 4.72 | 4.83 | 4.9 | 4.86 | 4.76 | 5.44 | 4.86 | 4.96 | 4.73 | 4.66 | 4.85 | 4.98 | 4.91 | 4.66 | 4.76 | 4.9 | 4.84 | 5.31 | 5.75 | 5.62 | 4.55 | 4.18 | 5.11 | 4.69 | 4.06 | 4.73 | 4.9 | 4.95 | 4.14 | 5.27 | 4.92 | 4.85 | 5.27 | 5.2 | 4.35 | 4.33 | 5.27 | 5.89 | 123.872 | 4.9407 | 5.89 |  | 24730 |  | 29776 |  | 28737 |  | 40629 |  | 24.73 |  | 29.776 |  | 28.737 |  | 40.629 |  | 123.872 | 0 | -1.11e-14% |  | 96 | 0 | 13.38 |  | 70.4
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 3028 | 2600 | 2828 | 1354 | 3848 | 3504 | 2444 | 2270 | 1920 | 2288 | 2286 | 2420 | 2502 | 2560 | 2596 | 2996 | 2586 | 2420 | 3068 | 2951 | 1680 | 1324 | 2648 | 2896 | 2904 | 2920 | 2628 | 1052 | 944 | 1938 | 300 | 3148 | 3892 | 3820 | 2086 | 4392 | 3968 | 3260 | 3852 | 1852 | 1610 | 2356 | 3384 | 2648 | 4.45 | 4.38 | 4.04 | 4.29 | 4.51 | 4.3 | 4.55 | 4.15 | 4.15 | 4.84 | 4.57 | 4.81 | 4.5 | 4.8 | 4.71 | 4.67 | 4.6 | 4.07 | 4.94 | 4.85 | 4.51 | 4.34 | 4.46 | 5.06 | 5.1 | 5.35 | 3.81 | 3.32 | 3.68 | 3.99 | 4.12 | 4.13 | 4.82 | 4.3 | 4.57 | 5.38 | 4.91 | 4.26 | 4.57 | 3.62 | 3.65 | 4.32 | 4.83 | 4.56 | 113.971 | 4.4509 | 5.38 |  | 25054 |  | 24445 |  | 33684 |  | 30788 |  | 25.054 |  | 24.445 |  | 33.684 |  | 30.788 |  | 113.971 | 0 | -1.11e-14% |  | 69 | 0 | 114.6 |  | 70.4
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 4044 | 4228 | 4080 | 3650 | 4176 | 4856 | 3752 | 3302 | 1968 | 1974 | 2006 | 2636 | 2950 | 3196 | 2604 | 2596 | 3136 | 3060 | 4696 | 3501 | 3480 | 3360 | 4308 | 3540 | 3304 | 3260 | 3362 | 2004 | 3320 | 3466 | 3278 | 2888 | 4460 | 3184 | 3394 | 7604 | 6000 | 3668 | 3336 | 2592 | 3394 | 3912 | 5432 | 4024 | 4.35 | 4.72 | 4.62 | 4.52 | 4.69 | 5.13 | 4.64 | 4.49 | 4.49 | 4.03 | 4.3 | 3.88 | 4.06 | 3.86 | 4.47 | 4.38 | 4.29 | 4.39 | 4.32 | 4.84 | 4.5 | 4.57 | 4.42 | 4.52 | 4.69 | 4.48 | 4.51 | 4 | 3.64 | 4.43 | 4.36 | 4.18 | 4.31 | 5.15 | 4.29 | 4.21 | 6.25 | 5.54 | 4.46 | 4.63 | 3.88 | 4.25 | 4.62 | 5.16 | 156.981 | 4.4891 | 6.25 |  | 29248 |  | 40211 |  | 40172 |  | 47350 |  | 29.248 |  | 40.211 |  | 40.172 |  | 47.35 |  | 156.981 | 0 | 0% |  | 96 | 0 | 143.73 |  | 70.4
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 6036 | 5160 | 4416 | 3308 | 1224 | 3620 | 4346 | 5252 | 4544 | 3826 | 4124 | 3664 | 3658 | 3398 | 2648 | 2892 | 2992 | 4024 | 3546 | 2418 | 3804 | 3100 | 4864 | 4088 | 4736 | 5192 | 3130 | 1464 | 3088 | 2278 | 1890 | 3380 | 1900 | 4372 | 3124 | 8232 | 4428 | 4836 | 4556 | 1924 | 2400 | 2370 | 6704 | 3492 | 5.15 | 4.97 | 4.81 | 4.52 | 3.29 | 4.59 | 4.61 | 5.29 | 5.29 | 5.02 | 5.03 | 4.73 | 4.63 | 4.64 | 4.55 | 4.42 | 4.46 | 4.32 | 4.56 | 4.42 | 3.99 | 4.81 | 4.43 | 4.73 | 4.78 | 5.15 | 5.32 | 4.04 | 3.52 | 4.46 | 4 | 3.44 | 4.41 | 4.02 | 4.64 | 4.3 | 6.51 | 5 | 4.87 | 4.95 | 3.58 | 3.92 | 4.07 | 5.6 | 164.448 | 4.5873 | 6.51 |  | 43948 |  | 36208 |  | 36548 |  | 47744 |  | 43.948 |  | 36.208 |  | 36.548 |  | 47.744 |  | 164.448 | 0 | 0% |  | 71 | 0 | 146.37 |  | 70.4
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 2208 | 1744 | 1540 | 2852 | 2856 | 3280 | 1554 | 3876 | 2940 | 3632 | 4028 | 3908 | 4026 | 4702 | 3964 | 3550 | 2840 | 1328 | 3950 | 3067 | 3596 | 3796 | 5104 | 5524 | 5112 | 5628 | 1152 | 1792 | 2612 | 3340 | 3252 | 2658 | 3012 | 3236 | 4452 | 6012 | 4232 | 3300 | 3548 | 2894 | 2322 | 3682 | 2712 | 1828 | 4.26 | 4.08 | 4.01 | 4.22 | 4.14 | 4.63 | 4.08 | 4.37 | 4.37 | 4.16 | 4.66 | 4.59 | 4.71 | 4.79 | 5.01 | 4.75 | 4.68 | 4.16 | 3.8 | 4.46 | 4.3 | 4.39 | 4.38 | 4.45 | 4.98 | 5.08 | 5.48 | 3.4 | 3.52 | 4.11 | 4.51 | 4.15 | 4.18 | 4.55 | 4.39 | 4.7 | 6.17 | 4.94 | 4.4 | 4.6 | 4.17 | 3.83 | 4.82 | 4.45 | 146.641 | 4.4518 | 6.17 |  | 43778 |  | 42633 |  | 32134 |  | 28096 |  | 43.778 |  | 42.633 |  | 32.134 |  | 28.096 |  | 146.641 | 0 | 0% |  | 44 | 0 | 140.63 |  | 70.4
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 2332 | 1888 | 1648 | 1210 | 948 | 852 | 1692 | 1176 | 440 | 366 | 648 | 688 | 338 | 446 | 388 | 574 | 504 | 1408 | 544 | 609 | 2008 | 1996 | 1120 | 940 | 1176 | 1268 | 1212 | 476 | 1352 | 1636 | 588 | 642 | 820 | 1060 | 1336 | 2188 | 1588 | 828 | 1228 | 1112 | 828 | 1886 | 1780 | 1544 | 3.36 | 3.47 | 3.19 | 2.76 | 2.61 | 2.96 | 3.33 | 2.97 | 2.97 | 2.56 | 2.76 | 2.87 | 3.07 | 1.12 | 2.79 | 2.75 | 2.81 | 2.9 | 3.03 | 2.4 | 2.64 | 3.26 | 3.2 | 2.67 | 3.29 | 3.07 | 3.27 | 2.65 | 2.23 | 2.87 | 3.02 | 2.3 | 2.67 | 3.15 | 2.74 | 2.87 | 3.79 | 3.39 | 2.61 | 3.1 | 2.6 | 2.38 | 3.2 | 3.29 | 49.311 | 2.885 | 3.79 |  | 8160 |  | 11555 |  | 10154 |  | 19442 |  | 8.16 |  | 11.555 |  | 10.154 |  | 19.442 |  | 49.311 | 0 | 0% |  | 95 | 0 | 45.49 |  | 70.4
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 14740 | 17408 | 19836 | 9294 | 17940 | 16424 | 11696 | 6624 | 7212 | 7986 | 7742 | 7620 | 2584 | 7032 | 6596 | 7432 | 8484 | 16384 | 7716 | 7434 | 8976 | 9748 | 9088 | 8888 | 9160 | 8984 | 22106 | 6448 | 8784 | 8652 | 10076 | 12004 | 17844 | 17640 | 7280 | 18272 | 18772 | 16632 | 17720 | 5888 | 9124 | 9830 | 13356 | 13212 | 6.82 | 7.49 | 7.99 | 6.18 | 7.43 | 7.47 | 6.53 | 5.47 | 5.47 | 5.41 | 6.13 | 5.78 | 5.7 | 1.55 | 5.64 | 5.76 | 5.91 | 5.83 | 7.44 | 5.68 | 5.53 | 5.91 | 6.07 | 5.68 | 5.99 | 6.23 | 6.19 | 8.34 | 5.31 | 5.99 | 5.92 | 6.11 | 6.79 | 8.15 | 7.39 | 5.28 | 8.55 | 7.86 | 7.27 | 7.57 | 5.07 | 5.99 | 6.09 | 7.13 | 496.668 | 6.3202 | 8.55 |  | 75888 |  | 98852 |  | 153248 |  | 168680 |  | 75.888 |  | 98.852 |  | 153.248 |  | 168.68 |  | 496.668 | 0 | 0% |  | 86 | 0 | 464.94 |  | 70.4
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 13828 | 19344 | 19252 | 12348 | 19104 | 18768 | 12984 | 9124 | 8068 | 9656 | 10874 | 11520 | 10948 | 10310 | 8936 | 9758 | 10472 | 15864 | 10316 | 9153 | 12100 | 11320 | 11160 | 12288 | 12508 | 11848 | 17338 | 7484 | 12808 | 10426 | 11310 | 12680 | 18980 | 20196 | 9350 | 22004 | 21956 | 18428 | 21096 | 7600 | 12084 | 10804 | 16628 | 13756 | 7.71 | 8.23 | 8.51 | 7.19 | 7.85 | 8.17 | 7.28 | 6.32 | 6.32 | 6.22 | 6.83 | 6.74 | 6.71 | 6.67 | 6.53 | 6.53 | 6.57 | 6.53 | 7.76 | 6.43 | 6.08 | 6.76 | 6.57 | 6.36 | 6.87 | 7.27 | 7.02 | 8.35 | 5.91 | 7.02 | 6.65 | 6.56 | 7.22 | 8.55 | 8.13 | 5.95 | 9.75 | 8.71 | 7.82 | 8.46 | 5.76 | 7 | 7.01 | 8.24 | 586.779 | 7.1618 | 9.75 |  | 107994 |  | 128181 |  | 173212 |  | 177392 |  | 107.994 |  | 128.181 |  | 173.212 |  | 177.392 |  | 586.779 | 0 | 0% |  | 56 | 0 | 576.94 |  | 70.4
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 16900 | 17912 | 18488 | 11020 | 14748 | 13396 | 11540 | 7496 | 6914 | 8000 | 8776 | 8456 | 8212 | 7512 | 6778 | 7306 | 8000 | 15916 | 7900 | 6997 | 10364 | 10524 | 8744 | 9312 | 9760 | 9016 | 18168 | 8328 | 11540 | 10496 | 9080 | 9594 | 14792 | 16412 | 8822 | 16672 | 16672 | 15304 | 15900 | 8274 | 12684 | 12772 | 15240 | 13872 | 7.15 | 7.57 | 7.83 | 6.5 | 6.94 | 6.95 | 6.38 | 5.64 | 5.64 | 5.59 | 6.13 | 5.97 | 5.85 | 5.86 | 5.71 | 5.76 | 5.85 | 5.69 | 7.23 | 5.69 | 5.42 | 6.2 | 6.24 | 5.55 | 6.08 | 6.26 | 6.14 | 7.58 | 5.5 | 6.52 | 6.1 | 5.84 | 6.18 | 7.58 | 7.23 | 5.57 | 8.17 | 7.63 | 6.95 | 7.36 | 5.28 | 6.47 | 6.51 | 7.24 | 504.609 | 6.3984 | 8.17 |  | 84686 |  | 105843 |  | 133490 |  | 180590 |  | 84.686 |  | 105.843 |  | 133.49 |  | 180.59 |  | 504.609 | 0 | 2.22e-14% |  | 88 | 0 | 485.57 |  | 70.4
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 19200 | 19484 | 19456 | 14060 | 15200 | 13220 | 13824 | 8484 | 7742 | 9694 | 11008 | 11588 | 10704 | 10564 | 9540 | 10616 | 11026 | 17236 | 10306 | 8477 | 13516 | 14076 | 11832 | 12528 | 13080 | 12064 | 19470 | 10060 | 13880 | 13188 | 11066 | 8894 | 15392 | 15060 | 9840 | 15844 | 16320 | 14492 | 13560 | 9362 | 14840 | 15144 | 18092 | 15704 | 7.75 | 8.01 | 8.21 | 7.19 | 7.96 | 7.85 | 7.09 | 6.14 | 6.14 | 6.19 | 6.87 | 6.86 | 6.82 | 6.71 | 6.67 | 6.69 | 6.83 | 6.55 | 7.7 | 6.46 | 5.92 | 7 | 7.09 | 6.52 | 7.01 | 7.33 | 7.07 | 8.03 | 6.23 | 7.09 | 6.96 | 6.48 | 6.96 | 8.7 | 7.85 | 6.01 | 8.91 | 8.49 | 7.7 | 8.01 | 5.79 | 7.22 | 7.23 | 8.12 | 578.733 | 7.1457 | 8.91 |  | 108724 |  | 136967 |  | 127982 |  | 205060 |  | 108.724 |  | 136.967 |  | 127.982 |  | 205.06 |  | 578.733 | 0 | 0% |  | 88 | 0 | 558.98 |  | 70.4
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 21808 | 19588 | 20624 | 18064 | 22256 | 19816 | 17842 | 10276 | 9120 | 11372 | 13450 | 14380 | 13056 | 12428 | 11298 | 12500 | 12952 | 20192 | 11030 | 9101 | 15780 | 15296 | 13752 | 14488 | 12076 | 12468 | 21122 | 13012 | 18220 | 16318 | 13168 | 12604 | 21976 | 20844 | 10024 | 22780 | 22720 | 20724 | 22144 | 12936 | 17664 | 18176 | 21792 | 20296 | 8.23 | 7.99 | 8.35 | 8.06 | 8.54 | 8.46 | 7.85 | 6.5 | 6.5 | 6.49 | 7.29 | 7.51 | 7.48 | 7.32 | 7.14 | 7.11 | 7.24 | 7 | 8.24 | 6.67 | 6.07 | 7.46 | 7.27 | 6.87 | 7.44 | 7.46 | 7.12 | 8.27 | 6.93 | 7.95 | 7.62 | 6.99 | 7.35 | 9.27 | 8.18 | 6.03 | 9.62 | 8.96 | 8.19 | 8.74 | 6.76 | 7.84 | 7.84 | 8.83 | 711.533 | 7.6143 | 9.62 |  | 124438 |  | 159861 |  | 185864 |  | 241370 |  | 124.438 |  | 159.861 |  | 185.864 |  | 241.37 |  | 711.533 | 0 | 0% |  | 92 | 4874.5 | 691.97 |  | 70.4
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 35656 | 33632 | 34808 | 30400 | 34572 | 30552 | 32058 | 22420 | 17820 | 23602 | 28722 | 30596 | 23396 | 26542 | 24544 | 27144 | 28978 | 33564 | 24588 | 22509 | 28684 | 25508 | 23260 | 26384 | 28480 | 25668 | 32940 | 25160 | 31148 | 27908 | 27600 | 23250 | 33328 | 34156 | 22716 | 33712 | 33464 | 33800 | 34824 | 32008 | 33084 | 31156 | 35296 | 34148 | 11.32 | 11.49 | 11.73 | 10.36 | 11.1 | 10.45 | 10.52 | 8.91 | 8.91 | 8.16 | 9.48 | 10.74 | 10.78 | 9.91 | 9.58 | 9.66 | 9.8 | 10.14 | 11.08 | 9.21 | 8.47 | 9.69 | 9.19 | 8.35 | 9.74 | 10.12 | 9.46 | 10.92 | 9.14 | 10.36 | 9.64 | 9.61 | 9.25 | 12.39 | 11.27 | 8.55 | 12.36 | 11.79 | 11.06 | 11.63 | 10.76 | 11.06 | 10.28 | 11.96 | 1283.785 | 10.2359 | 12.39 |  | 250348 |  | 320361 |  | 291658 |  | 421418 |  | 250.348 |  | 320.361 |  | 291.658 |  | 421.418 |  | 1283.785 | 0 | 0% |  | 91 | 0 | 1292.91 |  | 70.4
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 27252 | 23100 | 18748 | 24224 | 27128 | 24928 | 24682 | 15502 | 11552 | 15596 | 20700 | 23420 | 24876 | 20098 | 18744 | 20982 | 23722 | 20412 | 20252 | 19493 | 23100 | 18644 | 16244 | 20308 | 22788 | 21964 | 16556 | 20740 | 23984 | 23962 | 23324 | 19384 | 25304 | 25788 | 19556 | 29928 | 29680 | 26152 | 29028 | 22492 | 26400 | 26198 | 30312 | 28176 | 9.3 | 8.77 | 8.01 | 9.17 | 9.45 | 9.52 | 9.21 | 7.53 | 6.89 | 7.99 | 8.85 | 9.18 | 9.36 | 8.37 | 8.51 | 8.66 | 8.99 | 8.29 | 8.36 | 7.9 | 8.82 | 7.74 | 7.07 | 8.56 | 8.94 | 8.78 | 7.18 | 8.44 | 9.08 | 8.94 | 8.66 | 8.64 | 10.16 | 9.38 | 7.85 | 11.18 | 10.63 | 9.21 | 10.25 | 8.67 | 9.61 | 9.37 | 10.56 | 9.95 | 995.423 | 8.8632 | 11.18 |  | 192950 |  | 256123 |  | 237320 |  | 309030 |  | 192.95 |  | 256.123 |  | 237.32 |  | 309.03 |  | 995.423 | 0 | 0% |  | 93 | 0 | 983.09 |  | 70.4
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 15156 | 13980 | 10136 | 12256 | 13160 | 15836 | 13966 | 8754 | 5878 | 5468 | 6048 | 10344 | 10024 | 10616 | 7802 | 9646 | 6878 | 10300 | 11804 | 6197 | 12060 | 11380 | 10016 | 9132 | 9412 | 7900 | 7812 | 8246 | 12156 | 11204 | 6796 | 10442 | 13916 | 7764 | 9062 | 19420 | 17524 | 8748 | 13164 | 9054 | 10492 | 12534 | 18468 | 16108 | 7.14 | 7.03 | 6.34 | 7.04 | 6.7 | 7.67 | 7.25 | 6.15 | 5.5 | 5.7 | 5.42 | 6.52 | 6.43 | 6.52 | 6.09 | 6.42 | 5.44 | 6.34 | 6.77 | 5.25 | 6.94 | 6.7 | 6.09 | 6.24 | 6.3 | 5.9 | 5.52 | 5.94 | 6.98 | 6.64 | 5.27 | 6.73 | 7.39 | 5.39 | 5.98 | 8.93 | 8.05 | 5.69 | 6.97 | 6.1 | 6.54 | 6.94 | 8.23 | 7.75 | 477.059 | 6.5211 | 8.93 |  | 82976 |  | 116653 |  | 119974 |  | 157456 |  | 82.976 |  | 116.653 |  | 119.974 |  | 157.456 |  | 477.059 | 0 | -1.11e-14% |  | 96 | 0 | 430.77 |  | 70.4
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 15232 | 14788 | 9096 | 13316 | 13948 | 15708 | 13944 | 8964 | 5886 | 5864 | 7046 | 11272 | 11496 | 10868 | 6060 | 10160 | 8212 | 9924 | 11298 | 8100 | 11764 | 9980 | 9548 | 9868 | 10312 | 8360 | 5360 | 8284 | 12992 | 11288 | 7428 | 11228 | 13424 | 9524 | 8172 | 19152 | 16712 | 9196 | 16224 | 10642 | 11620 | 13060 | 18144 | 16968 | 7.11 | 7.12 | 5.94 | 7.25 | 6.91 | 7.68 | 7.24 | 6.27 | 5.57 | 5.9 | 5.79 | 6.87 | 6.98 | 6.77 | 6.5 | 6.65 | 5.81 | 6.16 | 6.72 | 5.77 | 6.87 | 6.3 | 5.97 | 6.51 | 6.64 | 6.17 | 5.04 | 5.98 | 7.16 | 6.68 | 5.43 | 6.97 | 7.31 | 5.86 | 5.77 | 8.89 | 8.11 | 5.69 | 7.67 | 6.43 | 6.75 | 7.06 | 8.21 | 7.9 | 490.432 | 6.645 | 8.89 |  | 88616 |  | 118350 |  | 125116 |  | 158350 |  | 88.616 |  | 118.35 |  | 125.116 |  | 158.35 |  | 490.432 | 0 | 0% |  | 89 | 0 | 453.43 |  | 70.4
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 16708 | 14980 | 10180 | 12560 | 15444 | 16480 | 14758 | 9230 | 5654 | 6684 | 9466 | 13520 | 12872 | 11326 | 9026 | 9852 | 8440 | 10712 | 10548 | 6905 | 12236 | 10444 | 9924 | 10172 | 11360 | 7424 | 8328 | 9582 | 12824 | 12454 | 7860 | 11044 | 14872 | 12236 | 9042 | 19868 | 19060 | 11260 | 16940 | 10058 | 11864 | 14108 | 19088 | 17468 | 7.36 | 7.13 | 6.23 | 6.98 | 7.14 | 7.76 | 7.37 | 6.19 | 5.51 | 6.07 | 6.3 | 7.19 | 7.04 | 6.65 | 6.4 | 6.49 | 5.86 | 6.38 | 6.49 | 5.49 | 6.87 | 6.32 | 5.94 | 6.5 | 6.69 | 6.14 | 5.51 | 6.23 | 7.05 | 6.85 | 5.59 | 6.88 | 7.61 | 6.43 | 5.91 | 8.99 | 8.28 | 6.19 | 7.69 | 6.28 | 6.73 | 7.17 | 8.36 | 7.95 | 524.861 | 6.7316 | 8.99 |  | 96306 |  | 121063 |  | 137204 |  | 170288 |  | 96.306 |  | 121.063 |  | 137.204 |  | 170.288 |  | 524.861 | 0 | 0% |  | 54 | 5590.37 | 482.41 |  | 70.4
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 16388 | 15436 | 15280 | 12198 | 14272 | 15156 | 13570 | 9960 | 8726 | 7804 | 8440 | 9296 | 7972 | 8146 | 7360 | 8430 | 9472 | 11804 | 10834 | 7663 | 12604 | 11372 | 12616 | 9924 | 10664 | 5016 | 13916 | 9112 | 12120 | 10892 | 9556 | 10472 | 14152 | 11764 | 9968 | 19944 | 17600 | 13024 | 12444 | 9888 | 11808 | 11980 | 18100 | 13268 | 7.29 | 7.27 | 7.45 | 6.92 | 6.87 | 7.5 | 7.09 | 6.31 | 6.17 | 6.07 | 6.1 | 6.28 | 5.93 | 5.9 | 5.99 | 6.05 | 6.05 | 6.54 | 6.55 | 5.62 | 6.98 | 6.55 | 6.58 | 6.57 | 6.44 | 5.35 | 6.97 | 5.97 | 6.91 | 6.37 | 6.12 | 6.68 | 7.37 | 6.39 | 6.11 | 9.1 | 8 | 6.61 | 6.64 | 6.1 | 6.58 | 6.51 | 8.16 | 6.95 | 510.411 | 6.6355 | 9.1 |  | 90418 |  | 119723 |  | 128828 |  | 171442 |  | 90.418 |  | 119.723 |  | 128.828 |  | 171.442 |  | 510.411 | 0 | 2.22e-14% |  | 90 | 57457.88 | 475.81 |  | 70.4
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 11576 | 12092 | 12092 | 9480 | 12004 | 11220 | 8064 | 5290 | 6012 | 7048 | 6664 | 6660 | 5764 | 6416 | 5448 | 6106 | 6024 | 11316 | 5292 | 4342 | 8760 | 9120 | 8624 | 8096 | 7820 | 4616 | 14364 | 5776 | 9400 | 8040 | 6040 | 7230 | 12628 | 12280 | 5924 | 12760 | 12544 | 11340 | 12212 | 4854 | 8132 | 8996 | 10612 | 9476 | 6.34 | 6.59 | 6.78 | 6.37 | 6.82 | 7.11 | 5.93 | 5.14 | 5.81 | 6.35 | 5.9 | 5.79 | 5.7 | 5.74 | 5.65 | 5.8 | 5.5 | 6.69 | 5.29 | 4.91 | 6.14 | 6.16 | 5.85 | 6.14 | 6.14 | 5.38 | 7.11 | 5.3 | 6.34 | 5.97 | 5.38 | 6.24 | 7.43 | 6.77 | 5.11 | 7.6 | 7.22 | 6.47 | 7.04 | 4.71 | 5.86 | 6.09 | 6.58 | 6.41 | 378.554 | 6.1284 | 7.6 |  | 66594 |  | 82352 |  | 104218 |  | 125390 |  | 66.594 |  | 82.352 |  | 104.218 |  | 125.39 |  | 378.554 | 0 | 0% |  | 89 | 2043.25 | 361.89 |  | 70.4
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 11248 | 11184 | 9516 | 6566 | 6032 | 5708 | 6442 | 2692 | 1850 | 1872 | 1868 | 1828 | 1180 | 1980 | 1854 | 2162 | 2802 | 11256 | 2948 | 2595 | 6976 | 7904 | 4120 | 4084 | 4644 | 4064 | 8438 | 4328 | 7016 | 6764 | 3364 | 3776 | 6128 | 6332 | 5320 | 8832 | 7656 | 7068 | 7852 | 1816 | 6110 | 8092 | 9868 | 9204 | 6.36 | 6.58 | 6.38 | 5.61 | 5.53 | 5.76 | 5.47 | 4.38 | 4.27 | 4.51 | 4.11 | 4.14 | 4.08 | 4.21 | 4.29 | 4.44 | 4.54 | 6.79 | 4.49 | 4.3 | 5.75 | 5.98 | 4.75 | 5.13 | 5.35 | 5.2 | 6.03 | 4.89 | 5.85 | 5.73 | 4.51 | 5.09 | 5.78 | 5.97 | 5.07 | 6.84 | 6.27 | 5.58 | 6.13 | 3.48 | 5.34 | 5.91 | 6.54 | 6.54 | 243.339 | 5.317 | 6.84 |  | 28202 |  | 51487 |  | 59384 |  | 104266 |  | 28.202 |  | 51.487 |  | 59.384 |  | 104.266 |  | 243.339 | 0 | 0% |  | 89 | 1151.12 | 238.66 |  | 70.4
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 11992 | 11256 | 9040 | 9092 | 8084 | 7968 | 6868 | 3700 | 3134 | 3348 | 3264 | 3100 | 2816 | 3232 | 3002 | 3340 | 3930 | 12464 | 3848 | 3157 | 8748 | 9288 | 6160 | 5800 | 6288 | 5524 | 8826 | 3974 | 8060 | 6676 | 4476 | 5310 | 8368 | 11440 | 6666 | 10712 | 9800 | 9500 | 9852 | 1592 | 5158 | 7086 | 11176 | 10344 | 6.46 | 6.52 | 6.2 | 6.26 | 6.11 | 6.39 | 5.59 | 4.74 | 4.9 | 5.21 | 4.79 | 4.7 | 4.74 | 4.85 | 4.88 | 5.04 | 4.99 | 7.03 | 4.89 | 4.57 | 6.16 | 6.27 | 5.34 | 5.56 | 5.85 | 5.67 | 6 | 4.75 | 6.19 | 5.7 | 4.99 | 5.67 | 6.41 | 6.63 | 5.43 | 7.26 | 6.75 | 6.19 | 6.62 | 3.53 | 5.08 | 5.7 | 6.82 | 6.77 | 297.459 | 5.6864 | 7.26 |  | 43134 |  | 66839 |  | 81034 |  | 106452 |  | 43.134 |  | 66.839 |  | 81.034 |  | 106.452 |  | 297.459 | 0 | 0% |  | 88 | 58.37 | 290.06 |  | 70.4
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 16272 | 16412 | 14480 | 14668 | 15760 | 15420 | 10990 | 6340 | 6332 | 7096 | 7096 | 6940 | 6236 | 6836 | 6140 | 7030 | 7224 | 18304 | 7150 | 6097 | 13552 | 14848 | 10376 | 10516 | 10756 | 9288 | 15096 | 7022 | 14028 | 10336 | 8348 | 10592 | 16544 | 19176 | 10218 | 16776 | 16276 | 15704 | 16868 | 4310 | 8712 | 10746 | 14836 | 14176 | 7.33 | 7.57 | 7.34 | 7.5 | 7.61 | 7.93 | 6.6 | 5.64 | 5.97 | 6.42 | 6.09 | 5.9 | 5.93 | 6.03 | 6.04 | 6.2 | 5.91 | 8.08 | 5.96 | 5.5 | 7.16 | 7.41 | 6.4 | 6.81 | 7.01 | 6.66 | 7.36 | 5.66 | 7.4 | 6.61 | 6.11 | 7.07 | 8.24 | 8.07 | 6.31 | 8.57 | 7.97 | 7.4 | 8.06 | 4.48 | 6.02 | 6.56 | 7.62 | 7.47 | 501.923 | 6.8177 | 8.57 |  | 80976 |  | 116139 |  | 143116 |  | 161692 |  | 80.976 |  | 116.139 |  | 143.116 |  | 161.692 |  | 501.923 | 0 | 0% |  | 88 | 1277.87 | 485.96 |  | 70.4
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 16940 | 18236 | 16776 | 16532 | 20504 | 20520 | 12128 | 8652 | 9538 | 10458 | 10170 | 9840 | 8880 | 9484 | 8716 | 9292 | 9242 | 20004 | 9754 | 9209 | 16132 | 16792 | 13236 | 13472 | 14468 | 13176 | 17692 | 9324 | 15816 | 12992 | 11256 | 13448 | 21704 | 23956 | 13724 | 22036 | 21456 | 20508 | 22340 | 4666 | 10828 | 12460 | 17356 | 17380 | 7.42 | 7.85 | 7.75 | 7.83 | 8.39 | 8.74 | 6.75 | 6.18 | 6.82 | 7.26 | 6.91 | 6.63 | 6.62 | 6.63 | 6.69 | 6.71 | 6.37 | 8.34 | 6.56 | 6.26 | 7.57 | 7.73 | 6.94 | 7.39 | 7.69 | 7.48 | 7.79 | 6.16 | 7.7 | 7.01 | 6.71 | 7.61 | 9.24 | 8.83 | 6.97 | 9.48 | 8.76 | 8.17 | 8.88 | 4.63 | 6.48 | 6.82 | 8.04 | 7.99 | 631.093 | 7.3814 | 9.48 |  | 111890 |  | 145949 |  | 186472 |  | 186782 |  | 111.89 |  | 145.949 |  | 186.472 |  | 186.782 |  | 631.093 | 0 | 2.22e-14% |  | 88 | 7317.37 | 615.65 |  | 70.4
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 24196 | 25240 | 24932 | 19492 | 22920 | 21536 | 17028 | 9980 | 10090 | 10840 | 10442 | 9888 | 8660 | 9344 | 8536 | 8916 | 8990 | 25260 | 9608 | 8518 | 19384 | 20144 | 15308 | 13504 | 15072 | 13060 | 23764 | 14612 | 18956 | 18500 | 10694 | 14312 | 23096 | 26168 | 14422 | 24492 | 22780 | 22304 | 24300 | 8910 | 18918 | 20834 | 23140 | 21940 | 8.76 | 9.44 | 9.38 | 8.55 | 8.8 | 8.95 | 7.57 | 6.86 | 7.03 | 7.44 | 7.08 | 6.76 | 6.66 | 6.67 | 6.75 | 6.7 | 6.46 | 9.32 | 6.7 | 6.25 | 8.37 | 8.73 | 7.58 | 7.93 | 8.12 | 7.71 | 9.03 | 7.14 | 8.56 | 7.99 | 6.77 | 7.73 | 9.6 | 9.44 | 7.39 | 10.03 | 9.1 | 8.53 | 9.31 | 5.53 | 8 | 8.35 | 9.09 | 8.8 | 743.03 | 7.9764 | 10.03 |  | 116844 |  | 157004 |  | 201908 |  | 267274 |  | 116.844 |  | 157.004 |  | 201.908 |  | 267.274 |  | 743.03 | 0 | 0% |  | 46 | 30691.5 | 754.1 |  | 70.4
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 26848 | 29624 | 29888 | 22960 | 22984 | 22604 | 19756 | 13976 | 12856 | 13350 | 13108 | 12576 | 12416 | 12842 | 12008 | 12492 | 11744 | 27292 | 13188 | 12000 | 22824 | 25256 | 17560 | 18140 | 19120 | 18040 | 29972 | 17014 | 18836 | 21024 | 14360 | 16360 | 23972 | 27140 | 20686 | 25664 | 24512 | 23912 | 25080 | 10968 | 23360 | 24166 | 23932 | 23244 | 9.26 | 10.48 | 10.56 | 8.91 | 8.75 | 9.1 | 8.04 | 7.36 | 7.46 | 7.78 | 7.49 | 7.17 | 7.28 | 7.31 | 7.43 | 7.42 | 6.87 | 9.8 | 7.27 | 6.85 | 8.59 | 9.24 | 7.58 | 8.27 | 8.49 | 8.35 | 10.32 | 7.67 | 8.75 | 8.49 | 7.35 | 8.21 | 9.68 | 9.45 | 8.21 | 10.19 | 9.3 | 8.76 | 9.38 | 6.03 | 8.92 | 9 | 9.26 | 9.1 | 869.654 | 8.4359 | 10.56 |  | 151142 |  | 199196 |  | 212228 |  | 307088 |  | 151.142 |  | 199.196 |  | 212.228 |  | 307.088 |  | 869.654 | 0 | 0% |  | 46 | 13380.75 | 869.19 |  | 70.4
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 22828 | 27164 | 27808 | 14710 | 15188 | 15524 | 15484 | 10594 | 9624 | 9644 | 8592 | 7896 | 7740 | 8038 | 7424 | 7284 | 8218 | 22240 | 8612 | 7553 | 15504 | 18048 | 12244 | 12116 | 12872 | 12256 | 27744 | 10994 | 16284 | 14372 | 9026 | 10860 | 15924 | 20804 | 13654 | 20720 | 19632 | 17676 | 18500 | 8602 | 18210 | 19786 | 19344 | 18436 | 8.37 | 9.71 | 9.94 | 7.23 | 7.31 | 7.82 | 7.4 | 6.56 | 6.55 | 6.84 | 6.26 | 6.04 | 6.12 | 6.17 | 6.26 | 6.12 | 6.06 | 8.69 | 6.2 | 5.84 | 7.29 | 7.87 | 6.55 | 6.96 | 7.22 | 7.12 | 9.72 | 6.48 | 7.57 | 7.27 | 6.18 | 7.07 | 7.98 | 8.21 | 6.91 | 9.34 | 8.5 | 7.67 | 8.15 | 5.45 | 7.92 | 8.15 | 8.35 | 8.18 | 645.773 | 7.3545 | 9.94 |  | 103578 |  | 134355 |  | 154828 |  | 253012 |  | 103.578 |  | 134.355 |  | 154.828 |  | 253.012 |  | 645.773 | 0 | -2.22e-14% |  | 93 | 28400.5 | 630.85 |  | 70.4
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 648 | 704 | 756 | 498 | 276 | 280 | 618 | 302 | 200 | 172 | 280 | 256 | 268 | 280 | 44 | 170 | 122 | 560 | 236 | 256 | 752 | 424 | 424 | 348 | 388 | 424 | 606 | 304 | 236 | 686 | 284 | 156 | 180 | 400 | 458 | 968 | 512 | 376 | 444 | 350 | 430 | 672 | 936 | 584 | 2.35 | 2.97 | 2.7 | 2.45 | 2.26 | 2.49 | 2.71 | 2.23 | 2.2 | 2.42 | 2.42 | 2.65 | 2.4 | 2.31 | 2.43 | 2.25 | 2.64 | 2.64 | 2.16 | 2.26 | 2.78 | 2.74 | 2.26 | 3.02 | 2.47 | 2.49 | 2.3 | 2.2 | 2.36 | 2.58 | 2.01 | 2.05 | 2.77 | 2.41 | 2.41 | 2.94 | 2.85 | 2.26 | 2.7 | 2.21 | 2.29 | 2.71 | 2.75 | 2.89 | 18.268 | 2.4861 | 3.02 |  | 3062 |  | 3760 |  | 3592 |  | 7854 |  | 3.062 |  | 3.76 |  | 3.592 |  | 7.854 |  | 18.268 | 0 | 0% |  | 92 | 976.75 | 15.97 |  | 70.4
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 2480 | 2804 | 2964 | 1612 | 1908 | 2548 | 2274 | 1456 | 980 | 850 | 958 | 1032 | 1044 | 1062 | 580 | 1272 | 1540 | 2172 | 1608 | 1373 | 1576 | 1224 | 1336 | 1232 | 1388 | 1280 | 2834 | 550 | 1592 | 754 | 1524 | 2218 | 1872 | 2548 | 960 | 2848 | 2176 | 2044 | 2408 | 602 | 778 | 818 | 2624 | 1592 | 3.19 | 3.74 | 3.49 | 3.12 | 2.81 | 3.52 | 3.41 | 3.14 | 3.03 | 3.18 | 2.99 | 3.22 | 3 | 2.9 | 3.01 | 3.08 | 3.34 | 3.25 | 2.99 | 2.9 | 3.23 | 2.97 | 2.85 | 3.53 | 3.14 | 3.1 | 3.06 | 2.42 | 3.13 | 2.64 | 2.72 | 3.3 | 3.42 | 3.17 | 2.68 | 3.77 | 3.58 | 3.09 | 3.52 | 2.3 | 2.52 | 2.73 | 3.45 | 3.24 | 71.295 | 3.1107 | 3.77 |  | 11556 |  | 15923 |  | 20570 |  | 23246 |  | 11.556 |  | 15.923 |  | 20.57 |  | 23.246 |  | 71.295 | 0 | 0% |  | 92 | 3.25 | 65.28 |  | 70.4
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 13724 | 12936 | 10560 | 12372 | 9236 | 12700 | 12626 | 9906 | 7748 | 6614 | 8030 | 9108 | 6184 | 9206 | 7992 | 8828 | 9030 | 9548 | 11152 | 7733 | 12856 | 10272 | 10944 | 8680 | 9672 | 9968 | 8052 | 7542 | 12668 | 9060 | 8400 | 9266 | 9540 | 9700 | 9756 | 17016 | 13768 | 10384 | 10204 | 8312 | 9426 | 8980 | 16656 | 11460 | 6.89 | 6.7 | 6.47 | 7.02 | 5.63 | 6.87 | 6.86 | 6.41 | 5.84 | 5.74 | 5.75 | 5.96 | 5.84 | 6.06 | 6.07 | 6.07 | 5.84 | 6 | 6.45 | 5.55 | 6.97 | 6.2 | 6.15 | 5.89 | 6.18 | 6.23 | 5.56 | 5.64 | 6.97 | 5.78 | 5.71 | 6.25 | 6.1 | 5.88 | 6.09 | 8.49 | 7.17 | 6.14 | 6.08 | 5.83 | 6.23 | 5.85 | 7.92 | 6.34 | 447.815 | 6.2652 | 8.49 |  | 86854 |  | 120265 |  | 101814 |  | 138882 |  | 86.854 |  | 120.265 |  | 101.814 |  | 138.882 |  | 447.815 | 0 | 0% |  | 91 | 56256.63 | 413.48 |  | 70.4
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 36552 | 34760 | 32576 | 34444 | 35688 | 35648 | 35116 | 30966 | 26508 | 28724 | 31880 | 34828 | 12584 | 33536 | 31354 | 32550 | 32706 | 33384 | 33224 | 29763 | 33960 | 32112 | 32012 | 33396 | 33696 | 32716 | 28958 | 31428 | 26180 | 33976 | 31472 | 31448 | 35336 | 35308 | 30300 | 37048 | 36928 | 35064 | 36564 | 31868 | 34686 | 35748 | 37100 | 36384 | 12.74 | 12.86 | 11.44 | 12.51 | 12.25 | 12.79 | 12.67 | 11.37 | 10.04 | 10.72 | 12.37 | 13.31 | 9.53 | 11.81 | 11.76 | 11.3 | 11.82 | 11.6 | 11.63 | 10.31 | 11.75 | 11.25 | 10.76 | 12.33 | 12.31 | 11.35 | 10.18 | 10.83 | 11.96 | 11.53 | 11.39 | 11.16 | 13.93 | 12.66 | 10.68 | 14.99 | 13.63 | 12.24 | 13.08 | 11.2 | 12.31 | 12.53 | 14.66 | 13.21 | 1440.479 | 11.9716 | 14.99 |  | 297310 |  | 381601 |  | 319032 |  | 442536 |  | 297.31 |  | 381.601 |  | 319.032 |  | 442.536 |  | 1440.479 | 0 | 0% |  | 85 | 50539.5 | 1482.58 |  | 70.4
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 33308 | 32248 | 27628 | 28426 | 35712 | 37064 | 31428 | 32924 | 29168 | 28362 | 31910 | 35396 | 36792 | 35570 | 32546 | 33520 | 32982 | 29540 | 35650 | 32117 | 35632 | 34064 | 33652 | 34780 | 34800 | 32504 | 21566 | 25480 | 29992 | 27662 | 30784 | 32878 | 35552 | 34684 | 31866 | 37964 | 37628 | 34616 | 36976 | 24700 | 26272 | 27976 | 28880 | 33860 | 12.27 | 12.47 | 10.45 | 12.47 | 11.54 | 12.55 | 12.33 | 11.42 | 10.49 | 10.62 | 11.91 | 13.03 | 12.67 | 12.16 | 11.74 | 11.26 | 11.45 | 10.84 | 11.89 | 10.43 | 11.92 | 11.41 | 10.8 | 12.5 | 12.2 | 11.19 | 8.81 | 10.86 | 11.87 | 11.55 | 10.62 | 11.14 | 13.04 | 11.66 | 10.66 | 14.63 | 13.27 | 11.32 | 12.55 | 10.39 | 11.46 | 12.07 | 14.27 | 12.92 | 1417.059 | 11.7523 | 14.63 |  | 330288 |  | 393149 |  | 323074 |  | 370548 |  | 330.288 |  | 393.149 |  | 323.074 |  | 370.548 |  | 1417.059 | 0 | 0% |  | 70 | 3827.75 | 1496.89 |  | 70.4
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 37480 | 36332 | 33716 | 14582 | 37140 | 37872 | 36686 | 34520 | 30316 | 30690 | 33706 | 37028 | 37632 | 36490 | 34918 | 27354 | 35774 | 35016 | 36850 | 34341 | 37272 | 36064 | 35504 | 36484 | 36796 | 29400 | 29268 | 33140 | 37492 | 35074 | 34672 | 34842 | 37212 | 37216 | 34260 | 38616 | 38508 | 37312 | 38268 | 31984 | 33848 | 33916 | 36560 | 36160 | 13.4 | 13.87 | 11.83 | 11.53 | 12.52 | 13.58 | 13.54 | 12.16 | 10.98 | 11.1 | 12.64 | 14 | 13.26 | 12.52 | 12.43 | 11.56 | 12.64 | 12.2 | 12.58 | 11.14 | 12.74 | 12.33 | 11.56 | 13.43 | 12.99 | 11.84 | 10.23 | 11.62 | 13.26 | 12.35 | 11.78 | 12.08 | 14.61 | 13 | 11.6 | 15.89 | 14.51 | 12.62 | 13.73 | 11.46 | 12.59 | 13.15 | 15.49 | 14.06 | 1528.311 | 12.6909 | 15.89 |  | 342076 |  | 400069 |  | 336986 |  | 449180 |  | 342.076 |  | 400.069 |  | 336.986 |  | 449.18 |  | 1528.311 | 0 | 0% |  | 54 | 2657.25 | 1619.39 |  | 70.4
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 32792 | 32388 | 29648 | 18184 | 36872 | 36696 | 31748 | 33708 | 29716 | 29340 | 33832 | 33356 | 32020 | 34536 | 29202 | 34376 | 35066 | 31248 | 34828 | 31291 | 36256 | 32120 | 34020 | 34932 | 35584 | 34840 | 27094 | 22976 | 35804 | 24454 | 34754 | 33148 | 36588 | 36896 | 32518 | 37740 | 37824 | 36472 | 37716 | 23764 | 25776 | 24092 | 27288 | 21228 | 13.21 | 13.62 | 12.11 | 12.43 | 12.69 | 13.3 | 13.23 | 12.06 | 10.8 | 11.11 | 12.84 | 13.98 | 13.1 | 12.34 | 12.26 | 11.79 | 12.73 | 12.17 | 12.16 | 10.83 | 12.69 | 11.99 | 11.33 | 13.16 | 12.77 | 11.86 | 10.82 | 11.02 | 12.83 | 11.72 | 12.09 | 11.62 | 14.55 | 13.23 | 11.32 | 15.54 | 14.12 | 12.66 | 13.54 | 11.07 | 12.08 | 12.54 | 14.9 | 13.38 | 1404.731 | 12.5361 | 15.54 |  | 331348 |  | 388935 |  | 329952 |  | 354496 |  | 331.348 |  | 388.935 |  | 329.952 |  | 354.496 |  | 1404.731 | 0 | 2.22e-14% |  | 89 | 23087.63 | 1534.29 |  | 70.4
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 31544 | 30016 | 26188 | 30920 | 35096 | 34912 | 30624 | 26844 | 24360 | 26306 | 31160 | 34148 | 34860 | 31624 | 29750 | 30646 | 32440 | 28808 | 30916 | 27615 | 33320 | 30080 | 29972 | 31968 | 32924 | 31964 | 22670 | 18384 | 33068 | 22350 | 31422 | 29348 | 34212 | 34968 | 27714 | 37052 | 37116 | 34632 | 36456 | 18632 | 24404 | 20436 | 27680 | 23888 | 11.43 | 11.44 | 10.59 | 11.36 | 11.33 | 11.93 | 11.71 | 10.37 | 9.32 | 9.97 | 11.61 | 12.32 | 11.66 | 10.6 | 10.81 | 10.43 | 11.19 | 10.8 | 10.35 | 9.32 | 10.96 | 10.06 | 9.77 | 11.15 | 11.27 | 10.74 | 9.6 | 9.66 | 11.13 | 10.23 | 10.86 | 10.36 | 12.67 | 12 | 9.58 | 13.77 | 12.64 | 11.43 | 12.29 | 10.23 | 11.17 | 11.17 | 13.1 | 11.95 | 1313.437 | 11.053 | 13.77 |  | 304506 |  | 369515 |  | 313792 |  | 325624 |  | 304.506 |  | 369.515 |  | 313.792 |  | 325.624 |  | 1313.437 | 0 | 0% |  | 88 | 24565.62 | 1387.29 |  | 70.4
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 33160 | 32792 | 27180 | 32628 | 33900 | 32776 | 33436 | 27290 | 22320 | 23326 | 28306 | 32592 | 34160 | 30636 | 27646 | 28156 | 30542 | 29048 | 28496 | 24429 | 31340 | 26388 | 26896 | 30128 | 30628 | 28844 | 22328 | 27472 | 32596 | 27132 | 28632 | 27760 | 32960 | 33116 | 24482 | 34948 | 35936 | 31320 | 35384 | 29026 | 32780 | 26260 | 36908 | 35988 | 10.82 | 10.87 | 9.38 | 11.04 | 10.59 | 11.32 | 11.1 | 9.87 | 8.9 | 9.35 | 10.53 | 11.46 | 11.25 | 10.32 | 10.25 | 9.87 | 10.47 | 9.7 | 9.82 | 8.74 | 10.39 | 9.26 | 8.98 | 10.56 | 10.48 | 9.92 | 8.25 | 9.53 | 10.72 | 10.1 | 9.91 | 9.92 | 11.65 | 10.86 | 8.83 | 12.93 | 11.76 | 10.11 | 11.54 | 9.91 | 10.9 | 10.73 | 12.63 | 11.7 | 1322.071 | 10.3914 | 12.93 |  | 284490 |  | 345971 |  | 298100 |  | 393510 |  | 284.49 |  | 345.971 |  | 298.1 |  | 393.51 |  | 1322.071 | 0 | 0% |  | 88 | 19905.13 | 1337.29 |  | 70.4
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 35268 | 31376 | 28408 | 33820 | 33368 | 32752 | 33774 | 30090 | 22256 | 25796 | 28906 | 35872 | 36164 | 30960 | 29464 | 31010 | 33144 | 30088 | 27604 | 26036 | 33100 | 26816 | 29532 | 31144 | 33436 | 33180 | 24908 | 28364 | 31696 | 30752 | 30464 | 25338 | 32536 | 34532 | 27220 | 36376 | 36276 | 33948 | 35660 | 31874 | 34872 | 27490 | 36912 | 36036 | 11.07 | 10.62 | 9.86 | 11.34 | 10.57 | 11.13 | 11.25 | 10.48 | 9.09 | 9.97 | 11.68 | 12.67 | 11.97 | 10.35 | 10.73 | 10.46 | 11.3 | 10.08 | 9.89 | 9.05 | 10.76 | 9.59 | 9.51 | 11.05 | 11.23 | 10.99 | 8.91 | 9.74 | 11.15 | 10.35 | 10.68 | 9.6 | 11.79 | 11.48 | 9.39 | 13.14 | 12.16 | 11.05 | 11.74 | 10.61 | 11.52 | 11.01 | 12.74 | 11.85 | 1378.618 | 10.8091 | 13.14 |  | 306376 |  | 361334 |  | 300786 |  | 410122 |  | 306.376 |  | 361.334 |  | 300.786 |  | 410.122 |  | 1378.618 | 0 | 2.22e-14% |  | 88 | 12007.25 | 1411.15 |  | 70.4
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 31768 | 30844 | 29372 | 35934 | 38084 | 37928 | 31610 | 33912 | 27648 | 31576 | 35656 | 37360 | 37956 | 35964 | 34936 | 36106 | 36156 | 30916 | 37072 | 35571 | 37288 | 36084 | 36216 | 36684 | 37120 | 36656 | 26728 | 25442 | 33592 | 30044 | 36748 | 35492 | 35216 | 35360 | 35322 | 38592 | 38616 | 38140 | 38564 | 28652 | 29696 | 22890 | 31044 | 32100 | 13.81 | 14.11 | 12.49 | 14.06 | 13.32 | 14.28 | 13.99 | 12.83 | 11.39 | 11.77 | 14.07 | 15.21 | 14.11 | 12.99 | 13.24 | 12.6 | 13.91 | 12.8 | 13.01 | 11.7 | 13.19 | 12.74 | 12.23 | 14.36 | 13.79 | 12.99 | 11.18 | 11.75 | 13.49 | 12.71 | 13 | 12.41 | 15.61 | 14.29 | 12.34 | 16.41 | 15.2 | 13.78 | 14.55 | 12.41 | 13.44 | 13.62 | 15.84 | 14.59 | 1498.655 | 13.4457 | 16.41 |  | 350784 |  | 430773 |  | 335992 |  | 381106 |  | 350.784 |  | 430.773 |  | 335.992 |  | 381.106 |  | 1498.655 | 0 | 0% |  | 76 | 5714 | 1581.51 |  | 70.4
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 36304 | 34300 | 34904 | 36964 | 37444 | 36416 | 34906 | 35892 | 31096 | 33644 | 35304 | 37592 | 37912 | 33632 | 33916 | 36376 | 34668 | 35292 | 35668 | 33965 | 36664 | 35196 | 36272 | 35796 | 37600 | 37384 | 33520 | 31976 | 23564 | 33866 | 35908 | 32410 | 36244 | 37488 | 34862 | 38192 | 37640 | 37868 | 38044 | 27660 | 35100 | 26496 | 35840 | 36236 | 13.68 | 13.93 | 13.18 | 13.79 | 13.23 | 13.62 | 13.81 | 12.97 | 11.4 | 12.08 | 15.06 | 15.91 | 14.23 | 12.64 | 13.04 | 12.88 | 13.84 | 13.06 | 12.56 | 11.49 | 12.92 | 12.4 | 12.2 | 14.15 | 14.26 | 13.31 | 12.18 | 11.58 | 11.92 | 12.45 | 13.08 | 11.78 | 15.34 | 14.15 | 12.27 | 15.77 | 14.73 | 13.83 | 14.22 | 12.17 | 13.49 | 13.17 | 15.67 | 14.15 | 1538.021 | 13.3543 | 15.91 |  | 358492 |  | 411383 |  | 331746 |  | 436400 |  | 358.492 |  | 411.383 |  | 331.746 |  | 436.4 |  | 1538.021 | 0 | 2.22e-14% |  | 93 | 7554.13 | 1618.54 |  | 70.4
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 37872 | 37092 | 34608 | 35210 | 37056 | 37400 | 37636 | 33792 | 28304 | 28912 | 34046 | 36772 | 37316 | 34280 | 32652 | 34038 | 35184 | 35704 | 34296 | 31710 | 36544 | 34212 | 31528 | 30244 | 35360 | 35172 | 31352 | 34268 | 37284 | 36452 | 34288 | 33276 | 30556 | 37220 | 31930 | 38064 | 38040 | 36700 | 37964 | 35056 | 37404 | 28626 | 38540 | 38292 | 12.69 | 13.17 | 11.68 | 12.99 | 12.23 | 13.23 | 13.07 | 11.69 | 10.24 | 10.59 | 12.51 | 13.7 | 12.81 | 11.48 | 11.77 | 11.32 | 12.46 | 11.88 | 11.36 | 10.25 | 12.21 | 11.29 | 10.65 | 12.12 | 12.35 | 11.68 | 10.49 | 11.17 | 12.81 | 11.88 | 11.8 | 11.41 | 13.64 | 13.14 | 10.67 | 14.81 | 13.59 | 12.35 | 13.3 | 11.75 | 12.94 | 12.68 | 14.65 | 13.41 | 1532.252 | 12.2252 | 14.81 |  | 331446 |  | 411628 |  | 326276 |  | 462902 |  | 331.446 |  | 411.628 |  | 326.276 |  | 462.902 |  | 1532.252 | 0 | 2.22e-14% |  | 87 | 1780.62 | 1590.42 |  | 70.4
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 37344 | 36472 | 32720 | 36244 | 36904 | 36976 | 36652 | 31512 | 27164 | 27150 | 31396 | 34780 | 36268 | 34512 | 31148 | 31998 | 32468 | 34176 | 34478 | 31135 | 35816 | 33152 | 32360 | 34552 | 34144 | 32680 | 27046 | 32176 | 36552 | 35098 | 30896 | 33360 | 32052 | 35908 | 31036 | 38396 | 38124 | 35704 | 37672 | 28972 | 34848 | 28390 | 37600 | 37200 | 12.41 | 12.87 | 10.88 | 12.42 | 11.96 | 12.73 | 12.62 | 11.18 | 10.08 | 10.15 | 11.42 | 12.39 | 11.83 | 11.42 | 11.03 | 10.75 | 10.93 | 11.28 | 11.29 | 10.07 | 11.75 | 11.02 | 10.39 | 12.08 | 11.97 | 10.86 | 9.27 | 10.75 | 12.12 | 11.46 | 10.36 | 11.29 | 13.16 | 11.99 | 10.39 | 14.81 | 13.33 | 11.48 | 12.78 | 10.31 | 11.89 | 12.1 | 14.31 | 13.1 | 1485.231 | 11.6518 | 14.81 |  | 322006 |  | 399435 |  | 325096 |  | 438694 |  | 322.006 |  | 399.435 |  | 325.096 |  | 438.694 |  | 1485.231 | 0 | 0% |  | 90 | 7795.25 | 1539.71 |  | 70.4
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 35220 | 33256 | 25496 | 34184 | 32712 | 34388 | 33614 | 28690 | 25872 | 23298 | 26352 | 31248 | 33008 | 32300 | 27792 | 28472 | 26832 | 27508 | 31086 | 25514 | 33240 | 30976 | 29408 | 27580 | 30884 | 28948 | 18178 | 28242 | 33648 | 32484 | 23594 | 28706 | 32248 | 29660 | 27458 | 36856 | 36428 | 29920 | 34760 | 26418 | 30446 | 34060 | 37048 | 35928 | 10.87 | 10.87 | 9 | 11.4 | 10.31 | 11.3 | 10.91 | 10.12 | 9.57 | 9.41 | 10 | 11.06 | 10.78 | 10.67 | 10.16 | 9.92 | 9.43 | 9.36 | 10.3 | 8.9 | 10.74 | 10.24 | 9.59 | 10.8 | 10.79 | 9.89 | 7.42 | 9.63 | 11 | 10.41 | 8.75 | 10.14 | 11.53 | 9.84 | 9.44 | 13.37 | 11.98 | 9.67 | 11.27 | 9.35 | 10.33 | 10.93 | 12.67 | 11.59 | 1333.96 | 10.357 | 13.37 |  | 285288 |  | 355096 |  | 295678 |  | 397898 |  | 285.288 |  | 355.096 |  | 295.678 |  | 397.898 |  | 1333.96 | 0 | 0% |  | 76 | 8973 | 1342.98 |  | 70.4
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 34880 | 32804 | 25076 | 33318 | 33384 | 34728 | 33448 | 29282 | 24540 | 24036 | 28610 | 33344 | 35008 | 33028 | 29156 | 30232 | 30606 | 27236 | 31982 | 27725 | 33144 | 28476 | 28928 | 30284 | 31476 | 30432 | 18140 | 27820 | 34088 | 32090 | 28052 | 29682 | 32436 | 30764 | 24332 | 36924 | 36136 | 29888 | 35128 | 27690 | 31238 | 34060 | 37068 | 36112 | 10.95 | 10.92 | 8.94 | 11.46 | 10.61 | 11.47 | 10.96 | 10.27 | 9.42 | 9.51 | 10.67 | 11.72 | 11.37 | 10.95 | 10.59 | 10.34 | 10.43 | 9.36 | 10.64 | 9.36 | 10.92 | 10.06 | 9.48 | 11 | 11.04 | 10.28 | 7.4 | 9.67 | 11.32 | 10.44 | 9.73 | 10.36 | 11.62 | 10.17 | 9.46 | 13.4 | 12.09 | 9.79 | 11.46 | 9.6 | 10.59 | 11.06 | 12.76 | 11.78 | 1356.811 | 10.5777 | 13.4 |  | 295940 |  | 364139 |  | 299070 |  | 397662 |  | 295.94 |  | 364.139 |  | 299.07 |  | 397.662 |  | 1356.811 | 0 | 0% |  | 95 | 11966 | 1368.72 |  | 70.4
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 35320 | 32164 | 28848 | 33378 | 30180 | 31808 | 32784 | 30544 | 24688 | 26808 | 31576 | 33320 | 34776 | 28284 | 27910 | 29912 | 30918 | 30132 | 21022 | 25255 | 33000 | 29452 | 30284 | 28448 | 32492 | 31956 | 24704 | 28244 | 33532 | 31770 | 29454 | 25212 | 31528 | 33224 | 27730 | 33812 | 35516 | 32560 | 34788 | 31308 | 34148 | 33920 | 36624 | 35384 | 11.24 | 10.9 | 9.99 | 11.53 | 10.37 | 11.2 | 11.13 | 10.69 | 9.44 | 10.11 | 11.85 | 12.58 | 11.78 | 10.47 | 10.55 | 10.38 | 10.97 | 10.17 | 9.89 | 8.95 | 10.92 | 10.05 | 9.85 | 11.1 | 11.5 | 10.86 | 8.89 | 9.76 | 11.25 | 10.46 | 10.33 | 9.63 | 11.7 | 11.25 | 9.61 | 13.28 | 12.2 | 10.9 | 11.65 | 10.6 | 11.46 | 11.23 | 12.86 | 11.78 | 1358.717 | 10.848 | 13.28 |  | 304892 |  | 349847 |  | 288628 |  | 415350 |  | 304.892 |  | 349.847 |  | 288.628 |  | 415.35 |  | 1358.717 | 0 | 0% |  | 88 | 28273 | 1400.72 |  | 70.4
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 37604 | 35884 | 12572 | 36876 | 31768 | 35668 | 37002 | 34272 | 28488 | 30148 | 30524 | 37060 | 37416 | 33072 | 32390 | 33876 | 34820 | 35348 | 33448 | 30811 | 36332 | 34040 | 34332 | 35428 | 35700 | 35652 | 31666 | 33350 | 36996 | 35804 | 33860 | 30326 | 35624 | 36552 | 32542 | 38060 | 38036 | 36472 | 37476 | 34470 | 36576 | 37148 | 38404 | 37944 | 12.48 | 12.48 | 10.89 | 12.82 | 11.62 | 12.36 | 12.59 | 11.8 | 10.38 | 10.84 | 12.74 | 13.99 | 12.95 | 11.36 | 11.74 | 11.37 | 12.28 | 11.62 | 11.24 | 10.1 | 12.06 | 11.29 | 11.03 | 12.6 | 12.74 | 11.99 | 10.53 | 10.97 | 12.54 | 11.55 | 11.59 | 10.69 | 13.27 | 12.53 | 10.84 | 14.72 | 13.44 | 12.24 | 12.9 | 11.6 | 12.53 | 12.48 | 14.27 | 12.96 | 1511.837 | 12.0684 | 14.72 |  | 339020 |  | 409063 |  | 319982 |  | 443772 |  | 339.02 |  | 409.063 |  | 319.982 |  | 443.772 |  | 1511.837 | 0 | 0% |  | 90 | 1373 | 1574.47 |  | 70.4
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | 36472 | 33292 | 13552 | 34144 | 28088 | 29144 | 34354 | 31060 | 23538 | 27696 | 31092 | 35800 | 35112 | 30556 | 28654 | 31642 | 32864 | 33304 | 28902 | 25311 | 33084 | 29856 | 30888 | 32288 | 34216 | 32784 | 31244 | 29034 | 34136 | 32620 | 31438 | 24090 | 33348 | 34608 | 28492 | 36504 | 36668 | 34828 | 35684 | 33694 | 35508 | 34620 | 37488 | 36168 | 11.42 | 10.86 | 10.39 | 11.29 | 10.66 | 10.6 | 11.16 | 10.61 | 9.15 | 10.15 | 11.14 | 12.54 | 11.57 | 10.22 | 10.45 | 10.58 | 11.03 | 10.73 | 9.84 | 8.9 | 10.58 | 9.92 | 9.79 | 10.94 | 11.63 | 10.83 | 10.23 | 9.72 | 11.03 | 10.4 | 10.55 | 9.32 | 11.92 | 11.35 | 9.65 | 12.97 | 12.06 | 11.19 | 11.58 | 11.01 | 11.54 | 10.99 | 12.78 | 11.54 | 1397.865 | 10.8366 | 12.97 |  | 314474 |  | 369079 |  | 292962 |  | 421350 |  | 314.474 |  | 369.079 |  | 292.962 |  | 421.35 |  | 1397.865 | 0 | 0% |  | 93 | 8212 | 1440.43 |  | 70.4
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | 37752 | 35880 | 35608 | 32666 | 37248 | 30976 | 36232 | 33730 | 28294 | 32806 | 36482 | 37268 | 36064 | 32716 | 29540 | 33420 | 33058 | 35776 | 31122 | 27519 | 32568 | 30880 | 34340 | 35652 | 36896 | 35256 | 33378 | 32058 | 32908 | 34788 | 32170 | 29172 | 36872 | 36464 | 30852 | 37840 | 37948 | 37124 | 37508 | 36178 | 37008 | 36332 | 38268 | 37412 | 12.17 | 12.02 | 11.83 | 11.79 | 11.99 | 11.59 | 11.82 | 11.53 | 10.14 | 11.31 | 13.05 | 13.57 | 12.16 | 11.25 | 11.55 | 11.55 | 12.06 | 11.66 | 11.06 | 10.08 | 11.3 | 11.07 | 10.77 | 12.37 | 12.85 | 11.68 | 10.93 | 10.33 | 11.59 | 11.06 | 11.63 | 10.43 | 13.9 | 12.34 | 10.98 | 14.15 | 13.19 | 12.41 | 12.64 | 11.95 | 12.29 | 11.63 | 13.63 | 12.35 | 1514.029 | 11.8557 | 14.15 |  | 346788 |  | 379419 |  | 321152 |  | 466670 |  | 346.788 |  | 379.419 |  | 321.152 |  | 466.67 |  | 1514.029 | 0 | 0% |  | 93 | 3501 | 1569.18 |  | 70.4
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | 36900 | 35500 | 32824 | 35192 | 36888 | 36628 | 36700 | 32998 | 27708 | 28078 | 32450 | 35944 | 36484 | 33964 | 31570 | 33798 | 34116 | 34504 | 34416 | 31500 | 34492 | 32168 | 33228 | 34652 | 35172 | 34484 | 29288 | 31770 | 35160 | 34476 | 32768 | 32644 | 35360 | 32924 | 31460 | 37928 | 37940 | 35792 | 37348 | 33538 | 35384 | 36292 | 37992 | 37772 | 12.14 | 12.22 | 11.04 | 11.93 | 12.19 | 12.92 | 12.53 | 11.35 | 10.01 | 10.38 | 11.73 | 13.2 | 12.35 | 11.26 | 11.56 | 11.24 | 11.85 | 11.43 | 11.31 | 10.15 | 11.26 | 10.57 | 10.5 | 12 | 12.17 | 11.45 | 9.95 | 10.47 | 11.63 | 11.17 | 11.33 | 11.18 | 12.42 | 12.48 | 10.36 | 14.58 | 13.38 | 12.17 | 13.07 | 11.19 | 11.96 | 11.99 | 14.1 | 12.88 | 1508.194 | 11.7511 | 14.58 |  | 331198 |  | 400604 |  | 323452 |  | 452940 |  | 331.198 |  | 400.604 |  | 323.452 |  | 452.94 |  | 1508.194 | 0 | 0% |  | 92 | 7937 | 1538.95 |  | 70.4
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | 35668 | 34080 | 29796 | 34690 | 36300 | 34636 | 36536 | 31264 | 26244 | 26574 | 31336 | 34816 | 36120 | 33580 | 31088 | 32796 | 33334 | 34052 | 32736 | 30267 | 33132 | 31676 | 31496 | 33464 | 33976 | 33116 | 29114 | 32112 | 34696 | 34888 | 32380 | 30724 | 35604 | 36152 | 30126 | 37732 | 37400 | 35632 | 37356 | 32910 | 35348 | 36208 | 37988 | 37624 | 12.21 | 12.58 | 11.28 | 12.21 | 11.88 | 12.44 | 12.6 | 11.08 | 9.84 | 10.15 | 11.31 | 12.75 | 12.19 | 11.27 | 11.32 | 11.09 | 11.56 | 11.51 | 11.07 | 10.08 | 11.41 | 10.85 | 10.27 | 11.86 | 11.96 | 11.13 | 10.09 | 10.77 | 11.87 | 11.44 | 11.11 | 10.86 | 9.93 | 12.41 | 10.32 | 14.66 | 13.31 | 12.12 | 12.83 | 11.23 | 12.19 | 12.26 | 14.29 | 12.99 | 1476.767 | 11.6495 | 14.66 |  | 318406 |  | 390501 |  | 321536 |  | 446324 |  | 318.406 |  | 390.501 |  | 321.536 |  | 446.324 |  | 1476.767 | 0 | 0% |  | 89 | 11143.38 | 1498.97 |  | 70.4
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | 35240 | 31268 | 35336 | 36748 | 36860 | 35860 | 37536 | 34158 | 28976 | 29254 | 34244 | 37272 | 37444 | 35126 | 34076 | 34664 | 36328 | 36268 | 34880 | 32845 | 36376 | 34140 | 34648 | 25228 | 36188 | 35576 | 32316 | 34840 | 37060 | 36692 | 35336 | 16802 | 37048 | 37400 | 33938 | 38260 | 38220 | 37316 | 37952 | 35460 | 37612 | 37856 | 38620 | 38256 | 12.43 | 13.24 | 12.05 | 13.09 | 12.15 | 13.33 | 13.26 | 11.88 | 10.48 | 10.73 | 12.49 | 13.96 | 13.05 | 11.85 | 12.23 | 11.57 | 12.84 | 12.17 | 11.79 | 10.61 | 12.31 | 11.72 | 11.08 | 12.43 | 12.8 | 11.93 | 10.76 | 11.48 | 12.95 | 12.09 | 12.2 | 9.2 | 10.55 | 13.38 | 11.3 | 15.35 | 14.01 | 12.95 | 13.52 | 12.07 | 13.18 | 13.12 | 15.16 | 13.66 | 1537.523 | 12.3727 | 15.35 |  | 332988 |  | 421517 |  | 315718 |  | 467300 |  | 332.988 |  | 421.517 |  | 315.718 |  | 467.3 |  | 1537.523 | 0 | 0% |  | 96 | 12441.25 | 1597.99 |  | 70.4
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | 38572 | 38044 | 35844 | 38248 | 37784 | 38200 | 38456 | 35070 | 32300 | 32052 | 36096 | 38136 | 38480 | 36866 | 35136 | 36824 | 37512 | 36952 | 37628 | 36346 | 38068 | 37000 | 36700 | 37296 | 37636 | 37320 | 32080 | 37044 | 38244 | 38322 | 37708 | 36106 | 37116 | 38204 | 35734 | 38748 | 38708 | 38044 | 38576 | 36512 | 38370 | 38620 | 38836 | 38716 | 13.79 | 14.31 | 12.18 | 14.39 | 13 | 14.21 | 14.09 | 12.75 | 11.37 | 11.52 | 13.74 | 15.17 | 14.24 | 13.06 | 13.42 | 12.62 | 14.38 | 12.56 | 13.2 | 11.8 | 13.44 | 12.96 | 12.06 | 14.18 | 13.83 | 12.77 | 10.66 | 12.42 | 14.06 | 13.1 | 13.66 | 12.4 | 11.26 | 14 | 12.15 | 16.28 | 14.84 | 13.48 | 14.2 | 12.47 | 13.97 | 14.22 | 16.02 | 14.38 | 1634.254 | 13.3775 | 16.28 |  | 361086 |  | 445314 |  | 341486 |  | 486368 |  | 361.086 |  | 445.314 |  | 341.486 |  | 486.368 |  | 1634.254 | 0 | 0% |  | 79 | 0 | 1671.39 |  | 70.4
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | 34760 | 36072 | 33548 | 34498 | 35272 | 35316 | 36888 | 33674 | 29816 | 30748 | 35518 | 37360 | 37844 | 35166 | 33328 | 34546 | 35680 | 34836 | 34536 | 31975 | 36468 | 33784 | 34752 | 36100 | 36252 | 36036 | 30314 | 33144 | 34600 | 35380 | 34818 | 30664 | 34752 | 34328 | 30854 | 37868 | 36180 | 36376 | 36000 | 34140 | 36402 | 37172 | 35716 | 37576 | 12.41 | 12.59 | 11.48 | 12.87 | 12.07 | 12.75 | 12.82 | 12.02 | 10.69 | 11.13 | 13.58 | 14.56 | 13.57 | 11.84 | 12.25 | 11.66 | 13.05 | 11.67 | 11.56 | 10.38 | 12.21 | 11.34 | 11.14 | 12.89 | 13.05 | 12.26 | 10.24 | 10.94 | 12.37 | 11.6 | 12.28 | 11.07 | 10.22 | 12.94 | 10.94 | 14.69 | 13.6 | 12.47 | 13.27 | 11.58 | 12.62 | 12.6 | 14.41 | 13.02 | 1531.057 | 12.2432 | 14.69 |  | 348100 |  | 410253 |  | 316756 |  | 455948 |  | 348.1 |  | 410.253 |  | 316.756 |  | 455.948 |  | 1531.057 | 0 | -1.11e-14% |  | 83 | 14574.75 | 1571.27 |  | 70.4
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | 33664 | 34328 | 33636 | 34274 | 35412 | 32012 | 35722 | 32494 | 24894 | 28828 | 29606 | 36808 | 36428 | 31630 | 30410 | 33298 | 34596 | 34296 | 30608 | 28090 | 34332 | 30928 | 31704 | 33188 | 34940 | 34812 | 30536 | 30956 | 35252 | 33404 | 33740 | 27316 | 34904 | 33244 | 29276 | 36868 | 37208 | 35888 | 36632 | 34974 | 36544 | 36100 | 35768 | 37156 | 11.2 | 11.24 | 11.05 | 11.58 | 11.05 | 11.32 | 11.55 | 10.99 | 9.43 | 10.47 | 12.49 | 13.22 | 12.19 | 10.5 | 10.96 | 10.99 | 11.76 | 11 | 10.24 | 9.36 | 11.1 | 10.25 | 9.99 | 11.28 | 11.97 | 11.42 | 10.09 | 10.09 | 11.46 | 10.64 | 11.19 | 9.84 | 9.33 | 11.92 | 9.87 | 13.29 | 12.53 | 11.74 | 12.15 | 11.34 | 11.98 | 11.51 | 13.18 | 11.94 | 1466.704 | 11.1975 | 13.29 |  | 323702 |  | 386434 |  | 309484 |  | 447084 |  | 323.702 |  | 386.434 |  | 309.484 |  | 447.084 |  | 1466.704 | 0 | 0% |  | 89 | 8665.25 | 1492.04 |  | 70.4
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | 32056 | 26880 | 24968 | 30346 | 30424 | 27432 | 29414 | 27312 | 20554 | 23132 | 28634 | 31568 | 31952 | 26464 | 24450 | 26524 | 28090 | 26060 | 24436 | 21465 | 29680 | 24400 | 25652 | 27828 | 28724 | 27848 | 21658 | 23732 | 31096 | 27602 | 26896 | 21152 | 29364 | 30580 | 23994 | 33704 | 33400 | 29660 | 32272 | 26908 | 30544 | 30296 | 34268 | 32744 | 10.16 | 9.34 | 9.13 | 10.52 | 9.91 | 10.12 | 10.02 | 9.97 | 8.64 | 9.4 | 9.6 | 11.5 | 10.98 | 9.5 | 9.7 | 9.83 | 10.12 | 9.21 | 9.14 | 8.3 | 10.06 | 9.02 | 8.93 | 10.27 | 10.6 | 10 | 8.18 | 8.82 | 10.36 | 9.47 | 9.7 | 8.72 | 8.22 | 10.21 | 8.9 | 12.01 | 11.11 | 9.96 | 10.67 | 9.55 | 10.38 | 10.05 | 11.51 | 10.62 | 1226.163 | 9.8275 | 12.01 |  | 273204 |  | 317841 |  | 267988 |  | 367130 |  | 273.204 |  | 317.841 |  | 267.988 |  | 367.13 |  | 1226.163 | 0 | 0% |  | 88 | 10687.5 | 1190.71 |  | 70.4
Formulas:
Month Year = [Date]-DAY([Date])+1
Days = DAY(EOMONTH(Input_Raw[[#This Row],[Date]],0))
Date = [Date, row above]+1

## WTG_BD
Sr. No. | Financial Year | Calendar Year | Operating Year | Month | Date | Affected WTG | SPV | Consumer | Plant Equivalent Weightage | Error Code | Error Text | Breakdown Description | Stoppage Type | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Fault Category | Paired WTG for Enegy based MA | Paired WTG Generation for loss calculation | Estimated Energy Loss (kWh) | Special Remarks | PTW No. | Job Card No.
1 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | P-51 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.41111 | 0.41111 | 0.73958 | 0.32847 | 7.8833 | 7.8833 | 12th Annual Maintenance Activity completed | Close | 0.17917 | WTG Scheduled Maintenance | P-52 |  | 750
2 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | P-56 | PWEPL | MSEDCL | 2.273% | 86 | Braking pad of secondary brake worn out | Secondary brake pads worn |  | 0.69028 | 0.69028 | 0.80069 | 0.11042 | 2.65 | 2.65 | Hydraulic Brake Pad Replaced & wtg restored | Close | 0.060227 | WTG Breakdown Maintenance | P-56 |  | 388
3 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-52 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.40556 | 0.40556 | 0.75486 | 0.34931 | 8.3833 | 8.3833 | 12th Annual Maintenance Activity completed | Close | 0.19053 | WTG Scheduled Maintenance | P-51 |  | 357
4 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-09 | PWEPL | MSEDCL | 2.273% | 77 | Gearbox oil overtemperature | Radiator Motor Failure |  | 0.97569 | 0.97569 | 0.99931 | 0.023611 | 0.56667 | 0.56667 | Rediator Motor replaced | Close | 0.012879 | WTG Breakdown Maintenance | P-8 |  | 397
5 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-27 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.84236 | 0.84236 | 0.92569 | 0.083333 | 2 | 2 | Hard Rebooted Turbine from down tower assembly | Close | 0.045455 | WTG Breakdown Maintenance | P-28 |  | 3065
6 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-32 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.65486 | 0.65486 | 0.69306 | 0.038194 | 0.91667 | 0.91667 | DTA Maintenance activity completed | Close | 0.020833 | WTG Scheduled Maintenance | P-37 |  | 66
7 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-37 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.60417 | 0.60417 | 0.64792 | 0.04375 | 1.05 | 1.05 | DTA Maintenance activity completed | Close | 0.023864 | WTG Scheduled Maintenance | P-32 |  | 54
8 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-51 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.58333 | 0.58333 | 0.62222 | 0.038889 | 0.93333 | 0.93333 | DTA Maintenance activity completed | Close | 0.021212 | WTG Scheduled Maintenance | P-52 |  | 0
9 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-52 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.54167 | 0.54167 | 0.57361 | 0.031944 | 0.76667 | 0.76667 | DTA Maintenance activity completed | Close | 0.017424 | WTG Scheduled Maintenance | P-50 |  | 0
10 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-09 | PWEPL | MSEDCL | 2.273% | 77 | Gearbox oil overtemperature | Radiator Motor Failure |  | 0.046528 | 0.046528 | 0.25972 | 0.21319 | 5.1167 | 5.1167 | Radiator motor replaced | Close | 0.11629 | WTG Breakdown Maintenance | P-08 |  | 932
11 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-46 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.090972 | 0.090972 | 0.15069 | 0.059722 | 1.4333 | 1.4333 | Rebooted the PLC & reset at scada | Close | 0.032576 | WTG Breakdown Maintenance | P-47 |  | 163
12 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-46 | PWEPL | MSEDCL | 2.273% | 352 | Communication fault wind measurement device | FT Sensor failure |  | 0.17153 | 0.17153 | 0.33819 | 0.16667 | 4 | 4 | FT sensor replaced. | Close | 0.090909 | WTG Breakdown Maintenance | P-47 |  | 1720
13 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-31 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.4625 | 0.4625 | 0.72986 | 0.26736 | 6.4167 | 6.4167 | 12th Annual Maintenance Day 1 Activity completed | Close | 0.14583 | WTG Scheduled Maintenance | P-03 |  | 1202
14 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-51 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated |  | 0.89514 | 0.89514 | 0.96667 | 0.071528 | 1.7167 | 1.7167 | Cable Twist Release & Turbine Restored | Close | 0.039015 | WTG Breakdown Maintenance | P-52 |  | 44
15 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-05 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work |  | 0.45694 | 0.45694 | 0.48472 | 0.027778 | 0.66667 | 0.66667 | OIL & Grease sample collection work completed | Close | 0.015152 | WTG Scheduled Maintenance | P-41 |  | 2
16 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-06 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work |  | 0.53611 | 0.53611 | 0.56806 | 0.031944 | 0.76667 | 0.76667 | OIL & Grease sample collection work completed | Close | 0.017424 | WTG Scheduled Maintenance | P-41 |  | 0
17 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-40 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work |  | 0.47014 | 0.47014 | 0.5125 | 0.042361 | 1.0167 | 1.0167 | OIL & Grease sample collection work completed | Close | 0.023106 | WTG Scheduled Maintenance | P-46 |  | 0
18 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-41 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work |  | 0.52986 | 0.52986 | 0.55694 | 0.027083 | 0.65 | 0.65 | OIL & Grease sample collection work completed | Close | 0.014773 | WTG Scheduled Maintenance | P-05 |  | 0
19 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-42 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work |  | 0.64514 | 0.64514 | 0.68542 | 0.040278 | 0.96667 | 0.96667 | OIL & Grease sample collection work completed | Close | 0.02197 | WTG Scheduled Maintenance | P-12 |  | 12
20 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-48 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work |  | 0.63542 | 0.63542 | 0.6625 | 0.027083 | 0.65 | 0.65 | OIL & Grease sample collection work completed | Close | 0.014773 | WTG Scheduled Maintenance | P-47 |  | 14
21 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-31 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.4125 | 0.4125 | 0.72083 | 0.30833 | 7.4 | 7.4 | 12th Annual Maintenance Day 2 Activity completed | Close | 0.16818 | WTG Scheduled Maintenance | P-3 |  | 5340
22 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-56 | PWEPL | MSEDCL | 2.273% | 134 | Battery charging voltage not OK | Battery Voltage Not OK |  | 0.87083 | 0.87083 | 0.96667 | 0.095833 | 2.3 | 2.3 | Axis Box 5 Amp Fuse Replaced & wtg restored | Close | 0.052273 | WTG Breakdown Maintenance | P-55 |  | 904
23 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-27 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | WETB card failure |  | 0.85139 | 0.85139 | 0.99931 | 0.14792 | 3.55 | 3.55 | Replaced WETB card. | Close | 0.080682 | WTG Breakdown Maintenance | P-28 |  | 476
24 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-26 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated |  | 0.63403 | 0.63403 | 0.68403 | 0.05 | 1.2 | 1.2 | Cable Twist Release & Turbine Restored | Close | 0.027273 | WTG Breakdown Maintenance | P-25 |  | 58
25 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-47 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work |  | 0.89028 | 0.89028 | 0.92431 | 0.034028 | 0.81667 | 0.81667 | OIL & Grease sample collection work completed | Close | 0.018561 | WTG Breakdown Maintenance | P-48 |  | 72
26 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-03 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.39722 | 0.39722 | 0.71528 | 0.31806 | 7.6333 | 7.6333 | 12th Annual Maintenance Activity completed | Close | 0.17348 | WTG Scheduled Maintenance | P-02 |  | 905
27 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-07 | PWEPL | MSEDCL | 2.273% | 81 | Shaft bearing overtemperature | Shaft Bearing Over Tempreture |  | 0.6375 | 0.6375 | 0.76736 | 0.12986 | 3.1167 | 3.1167 | Tempreture sensor cable connection tight proparly & turbine restored | Close | 0.070833 | WTG Breakdown Maintenance | P-18 |  | 474
28 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | P-02 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.38472 | 0.38472 | 0.7125 | 0.32778 | 7.8667 | 7.8667 | 12th Annual Maintenance Activity completed | Close | 0.17879 | WTG Scheduled Maintenance | P-18 |  | 668
29 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | P-02 | PWEPL | MSEDCL | 2.273% | 86 | Braking pad of secondary brake worn out | Braking pad of secondary brake worn out |  | 0.85625 | 0.85625 | 0.99931 | 0.14306 | 3.4333 | 3.4333 | Hydralic Brake pad & Sensor replaced | Close | 0.07803 | WTG Breakdown Maintenance | P-18 |  | 1305
30 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | P-06 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout |  | 0.83958 | 0.83958 | 0.88889 | 0.049306 | 1.1833 | 1.1833 | Rebooted the PLC & reset at scada | Close | 0.026894 | WTG Breakdown Maintenance | P-41 |  | 53
31 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-06 | PWEPL | MSEDCL | 2.273% | 86 | Braking pad of secondary brake worn out | Braking pad of secondary brake worn out |  | 0.0041667 | 0.0041667 | 0.052778 | 0.048611 | 1.1667 | 1.1667 | Hydralic Brake pad & Sensor replaced | Close | 0.026515 | WTG Breakdown Maintenance | P-18 |  | 490
32 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-02 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout |  | 0 | 0 | 0.11528 | 0.11528 | 2.7667 | 2.7667 | Grease cleaned from yaw sensor, Yaw teeth, Pinion. | Close | 0.062879 | WTG Breakdown Maintenance | P-41 |  | 117
33 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-18 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.40486 | 0.40486 | 0.71667 | 0.31181 | 7.4833 | 7.4833 | 12th Annual Maintenance Activity completed | Close | 0.17008 | WTG Scheduled Maintenance | P-07 |  | 824
34 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-11 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault |  | 0.11667 | 0.11667 | 0.16528 | 0.048611 | 1.1667 | 1.1667 | Hard Rebooted Turbine from down tower assembly | Close | 0.026515 | WTG Breakdown Maintenance | P-10 |  | 21
35 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-13 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU Collective faults |  | 0.11667 | 0.11667 | 0.22361 | 0.10694 | 2.5667 | 2.5667 | Replaced WEMA card. | Close | 0.058333 | WTG Breakdown Maintenance | P-12 |  | 32
36 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-46 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work |  | 0.80903 | 0.80903 | 0.83333 | 0.024306 | 0.58333 | 0.58333 | OIL & Grease sample collection work completed | Close | 0.013258 | WTG Scheduled Maintenance | P-45 |  | 193
37 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-01 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.375 | 0.375 | 0.70903 | 0.33403 | 8.0167 | 8.0167 | 12th Annual Maintenance Activity completed | Close | 0.1822 | WTG Scheduled Maintenance | P-07 |  | 1327
38 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-07 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.40625 | 0.40625 | 0.77778 | 0.37153 | 8.9167 | 8.9167 | 12th Annual Maintenance Activity completed | Close | 0.20265 | WTG Scheduled Maintenance | P-18 |  | 2709
39 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-11 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated |  | 0.66042 | 0.66042 | 0.68403 | 0.023611 | 0.56667 | 0.56667 | Cable Twist Release & Turbine Restored | Close | 0.012879 | WTG Breakdown Maintenance | P-10 |  | 245
40 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | P-01 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.75347 | 0.75347 | 0.76875 | 0.015278 | 0.36667 | 0.36667 | DTA Maintenance activity completed | Close | 0.0083333 | WTG Scheduled Maintenance | P-07 |  | 240
41 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | P-02 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.53611 | 0.53611 | 0.60069 | 0.064583 | 1.55 | 1.55 | DTA Maintenance activity completed | Close | 0.035227 | WTG Scheduled Maintenance | P-18 |  | 393
42 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | P-03 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.72292 | 0.72292 | 0.74514 | 0.022222 | 0.53333 | 0.53333 | DTA Maintenance activity completed | Close | 0.012121 | WTG Scheduled Maintenance | P-02 |  | 261
43 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | P-18 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.63403 | 0.63403 | 0.66875 | 0.034722 | 0.83333 | 0.83333 | DTA Maintenance activity completed | Close | 0.018939 | WTG Scheduled Maintenance | P-07 |  | 377
44 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | P-51 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated |  | 0.69444 | 0.69444 | 0.82639 | 0.13194 | 3.1667 | 3.1667 | Cable Twist Release & Turbine Restored | Close | 0.07197 | WTG Breakdown Maintenance | P-52 |  | 1092
45 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | P-55 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work |  | 0.43889 | 0.43889 | 0.50556 | 0.066667 | 1.6 | 1.6 | OIL & Grease sample collection work completed | Close | 0.036364 | WTG Scheduled Maintenance | P-56 |  | 14
46 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-14 | P-45 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox Oil & Main Bering Grease Sample Collection work |  | 0.56389 | 0.56389 | 0.60833 | 0.044444 | 1.0667 | 1.0667 | OIL & Grease sample collection work completed | Close | 0.024242 | WTG Scheduled Maintenance | P-46 |  | 232
47 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | P-56 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.42292 | 0.42292 | 0.73611 | 0.31319 | 7.5167 | 7.5167 | 12th Annual Maintenance Day 1 Activity completed | Close | 0.17083 | WTG Scheduled Maintenance | P-55 |  | 1493
48 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | P-43 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Hub door open |  | 0.69375 | 0.69375 | 0.71736 | 0.023611 | 0.56667 | 0.56667 | hub door closing work complited | Close | 0.012879 | WTG Breakdown Maintenance | P-27 |  | 137
49 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | P-07 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout |  | 0.73819 | 0.73819 | 0.77083 | 0.032639 | 0.78333 | 0.78333 | Grease cleaned from yaw sensor, Yaw teeth, Pinion. | Close | 0.017803 | WTG Breakdown Maintenance | P-18 |  | 565
50 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | P-56 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.4375 | 0.4375 | 0.74375 | 0.30625 | 7.35 | 7.35 | 12th Annual Maintenance Day 2 Activity completed | Close | 0.16705 | WTG Scheduled Maintenance | P-55 |  | 2179
51 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-16 | P-38 | PWEPL | MSEDCL | 2.273% | 280 | Prepressure error, active brake | Hydraulic brake test Accumulater pressure error |  | 0.77778 | 0.77778 | 0.79306 | 0.015278 | 0.36667 | 0.36667 | Accumulater reaplaced & turbine restored | Close | 0.0083333 | WTG Breakdown Maintenance | P-17 |  | 338
52 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | P-55 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.42361 | 0.42361 | 0.81667 | 0.39306 | 9.4333 | 9.4333 | 12th Annual Maintenance Activity completed | Close | 0.21439 | WTG Scheduled Maintenance | P-56 |  | 3485
53 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | P-26 | PWEPL | MSEDCL | 2.273% | 123 | Generator carbon brush warn | Generator carbon brush warn |  | 0.70208 | 0.70208 | 0.73819 | 0.036111 | 0.86667 | 0.86667 | generator carbon brush limit switch connection tight properly | Close | 0.019697 | WTG Breakdown Maintenance | P-25 |  | 280
54 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | P-45 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.42292 | 0.42292 | 0.79583 | 0.37292 | 8.95 | 8.95 | 12th Annual Maintenance Activity completed | Close | 0.20341 | WTG Scheduled Maintenance | P-46 |  | 3194
55 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | P-51 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated |  | 0.44653 | 0.44653 | 0.55486 | 0.10833 | 2.6 | 2.6 | Cable Twist Release & Turbine Restored | Close | 0.059091 | WTG Breakdown Maintenance | P-52 |  | 81
56 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-18 | P-23 | PWEPL | MSEDCL | 2.273% | CE100017 | UPS breakdown | UPS fault |  | 0.70208 | 0.70208 | 0.70833 | 0.00625 | 0.15 | 0.15 | Replaced UPS Battery Bank | Close | 0.0034091 | WTG Breakdown Maintenance | P-22 |  | 164
57 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-19 | P-46 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.40833 | 0.40833 | 0.76389 | 0.35556 | 8.5333 | 8.5333 | 12th Annual Maintenance Activity completed | Close | 0.19394 | WTG Scheduled Maintenance | P-45 |  | 2942
58 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-20 | P-52 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | IO Card 28V power supply failed |  | 0.39861 | 0.39861 | 0.41736 | 0.01875 | 0.45 | 0.45 | Rebooted the PLC & reset at scada | Close | 0.010227 | WTG Breakdown Maintenance | P-51 |  | 0
59 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | P-10 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout |  | 0.52917 | 0.52917 | 0.53264 | 0.0034722 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | WTG Breakdown Maintenance | P-09 |  | 7
60 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | P-47 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Grease on sensor |  | 0.34236 | 0.34236 | 0.36181 | 0.019444 | 0.46667 | 0.46667 | Grease cleaned from yaw sensor, Yaw teeth, Pinion. | Close | 0.010606 | WTG Breakdown Maintenance | P-48 |  | 39
61 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | P-10 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Grease on sensor |  | 0.64861 | 0.64861 | 0.68681 | 0.038194 | 0.91667 | 0.91667 | Grease cleaned from yaw sensor, Yaw teeth, Pinion. | Close | 0.020833 | WTG Breakdown Maintenance | P-09 |  | 249
62 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | P-26 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.027778 | 0.027778 | 0.036806 | 0.0090278 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | WTG Breakdown Maintenance | P-25 |  | 0
63 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | P-47 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout |  | 0.27431 | 0.27431 | 0.29514 | 0.020833 | 0.5 | 0.5 | Rebooted the PLC & reset at scada | Close | 0.011364 | WTG Breakdown Maintenance | P-48 |  | 61
64 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | P-10 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout |  | 0.32431 | 0.32431 | 0.35903 | 0.034722 | 0.83333 | 0.83333 | Rebooted the PLC & reset at scada | Close | 0.018939 | WTG Breakdown Maintenance | P-09 |  | 188
65 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | P-47 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.42292 | 0.42292 | 0.80556 | 0.38264 | 9.1833 | 9.1833 | 12th Annual Maintenance Activity completed | Close | 0.20871 | WTG Scheduled Maintenance | P-48 |  | 2984
66 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | P-48 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.34514 | 0.34514 | 0.70139 | 0.35625 | 8.55 | 8.55 | 12th Annual Maintenance Activity completed | Close | 0.19432 | WTG Scheduled Maintenance | P-42 |  | 1251
67 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | P-07 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated |  | 0.39931 | 0.39931 | 0.53125 | 0.13194 | 3.1667 | 3.1667 | Cable Twist Release & Turbine Restored | Close | 0.07197 | WTG Breakdown Maintenance | P-18 |  | 52
68 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | P-26 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated |  | 0.37639 | 0.37639 | 0.42708 | 0.050694 | 1.2167 | 1.2167 | Cable Twist Release & Turbine Restored | Close | 0.027652 | WTG Breakdown Maintenance | P-25 |  | 0
69 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | P-51 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated |  | 0.40972 | 0.40972 | 0.42153 | 0.011806 | 0.28333 | 0.28333 | Cable Twist Release & Turbine Restored | Close | 0.0064394 | WTG Breakdown Maintenance | P-52 |  | 0
70 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | P-42 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.41875 | 0.41875 | 0.75486 | 0.33611 | 8.0667 | 8.0667 | 12th Annual Maintenance Activity completed | Close | 0.18333 | WTG Scheduled Maintenance | P-48 |  | 1670
71 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | P-47 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout |  | 0.59722 | 0.59722 | 0.68958 | 0.092361 | 2.2167 | 2.2167 | Yaw tooth sensor clean & Cable twist release & turbine restored | Close | 0.050379 | WTG Breakdown Maintenance | P-48 |  | 769
72 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-06 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.42292 | 0.42292 | 0.79444 | 0.37153 | 8.9167 | 8.9167 | 12th Annual Maintenance Activity completed | Close | 0.20265 | WTG Scheduled Maintenance | P-41 |  | 2809
73 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-07 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Turbine Ispection |  | 0.49653 | 0.49653 | 0.54653 | 0.05 | 1.2 | 1.2 | Turbine Inspection Completed | Close | 0.027273 | WTG Scheduled Maintenance | P-18 |  | 167
74 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-27 | P-41 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.42986 | 0.42986 | 0.71736 | 0.2875 | 6.9 | 6.9 | 12th Annual Maintenance Activity completed | Close | 0.15682 | WTG Scheduled Maintenance | P-05 |  | 1170
75 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | P-05 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.43125 | 0.43125 | 0.78958 | 0.35833 | 8.6 | 8.6 | 12th Annual Maintenance Activity completed | Close | 0.19545 | WTG Scheduled Maintenance | P-41 |  | 2101
76 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-28 | P-51 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated |  | 0.51389 | 0.51389 | 0.57639 | 0.0625 | 1.5 | 1.5 | Cable Twist Release & Turbine Restored | Close | 0.034091 | WTG Breakdown Maintenance | P-52 |  | 96
77 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | P-40 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | 12th Annual Maintenance Activity |  | 0.36181 | 0.36181 | 0.69653 | 0.33472 | 8.0333 | 8.0333 | 12th Annual Maintenance Activity completed | Close | 0.18258 | WTG Scheduled Maintenance | P-05 |  | 1659
78 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-29 | P-34 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | IO Card 28V power supply failed |  | 0.45903 | 0.45903 | 0.46319 | 0.0041667 | 0.1 | 0.1 | Rebooted the PLC & reset at scada | Close | 0.0022727 | WTG Breakdown Maintenance | P-04 |  | 0
79 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | P-12 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch Converter failure |  | 0.26389 | 0.26389 | 0.50417 | 0.24028 | 5.7667 | 5.7667 | Replaced Pitch converter | Close | 0.13106 | WTG Breakdown Maintenance | P-11 |  | 354
80 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | P-07 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.51042 | 0.51042 | 0.54514 | 0.034722 | 0.83333 | 0.83333 | DTA Maintenance activity completed | Close | 0.018939 | WTG Scheduled Maintenance | P-18 |  | 282
81 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | P-56 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.55208 | 0.55208 | 0.57778 | 0.025694 | 0.61667 | 0.61667 | DTA Maintenance activity completed | Close | 0.014015 | WTG Scheduled Maintenance | P-55 |  | 235
82 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | P-55 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.62569 | 0.62569 | 0.65139 | 0.025694 | 0.61667 | 0.61667 | DTA Maintenance activity completed | Close | 0.014015 | WTG Scheduled Maintenance | P-56 |  | 302
83 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | P-45 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.66319 | 0.66319 | 0.69375 | 0.030556 | 0.73333 | 0.73333 | DTA Maintenance activity completed | Close | 0.016667 | WTG Scheduled Maintenance | P-46 |  | 470
84 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-30 | P-46 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.69722 | 0.69722 | 0.72292 | 0.025694 | 0.61667 | 0.61667 | DTA Maintenance activity completed | Close | 0.014015 | WTG Scheduled Maintenance | P-45 |  | 425
85 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | P-23 | PWEPL | MSEDCL | 2.273% | 157 | Brake does not close | Secondary rotor brake does not close |  | 0.38611 | 0.38611 | 0.39306 | 0.0069444 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | WTG Breakdown Maintenance | P-22 |  | 0
86 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | P-47 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.44028 | 0.44028 | 0.50833 | 0.068056 | 1.6333 | 1.6333 | DTA Maintenance activity completed | Close | 0.037121 | WTG Scheduled Maintenance | P-48 |  | 23
87 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | P-48 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.51944 | 0.51944 | 0.55208 | 0.032639 | 0.78333 | 0.78333 | DTA Maintenance activity completed | Close | 0.017803 | WTG Scheduled Maintenance | P-47 |  | 125
88 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-01 | P-42 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.59792 | 0.59792 | 0.65139 | 0.053472 | 1.2833 | 1.2833 | DTA Maintenance activity completed | Close | 0.029167 | WTG Scheduled Maintenance | P-48 |  | 291
89 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-02 | P-18 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | A Q A Against PM Audit |  | 0.48472 | 0.48472 | 0.59167 | 0.10694 | 2.5667 | 2.5667 | Audit work completed | Close | 0.058333 | WTG Unscheduled Maintenance | P-07 |  | 196
90 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-02 | P-06 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.50347 | 0.50347 | 0.54792 | 0.044444 | 1.0667 | 1.0667 | DTA Maintenance activity completed | Close | 0.024242 | WTG Scheduled Maintenance | P-41 |  | 2025
91 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-02 | P-41 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.55278 | 0.55278 | 0.58958 | 0.036806 | 0.88333 | 0.88333 | DTA Maintenance activity completed | Close | 0.020076 | WTG Scheduled Maintenance | P-05 |  | 167
92 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-02 | P-05 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.63194 | 0.63194 | 0.66181 | 0.029861 | 0.71667 | 0.71667 | DTA Maintenance activity completed | Close | 0.016288 | WTG Scheduled Maintenance | P-41 |  | 385
93 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-02 | P-34 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | A Q A Against PM Audit |  | 0.65625 | 0.65625 | 0.73194 | 0.075694 | 1.8167 | 1.8167 | Audit work completed | Close | 0.041288 | WTG Unscheduled Maintenance | P-04 |  | 792
94 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-02 | P-40 | PWEPL | MSEDCL | 2.273% | CE100010 | Manual Stop - Preventive Maintenance Activity | DTA Maintenance |  | 0.66944 | 0.66944 | 0.69722 | 0.027778 | 0.66667 | 0.66667 | DTA Maintenance activity completed | Close | 0.015152 | WTG Scheduled Maintenance | P-05 |  | 377
95 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | P-42 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | A Q A Against PM Audit |  | 0.475 | 0.475 | 0.58542 | 0.11042 | 2.65 | 2.65 | Audit work completed | Close | 0.060227 | WTG Unscheduled Maintenance | P-48 |  | 591
96 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | P-04 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU Collective faults |  | 0.7375 | 0.7375 | 0.75 | 0.0125 | 0.3 | 0.3 | Hard Rebooted Turbine from down tower assembly | Close | 0.0068182 | WTG Breakdown Maintenance | P-22 |  | 102
97 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | P-20 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Pitch Drive Oil replacement work |  | 0.475 | 0.475 | 0.58889 | 0.11389 | 2.7333 | 2.7333 | Pitch Motor Oil replacement work done | Close | 0.062121 | WTG Unscheduled Maintenance | P-38 |  | 566
98 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | P-51 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | CBM Anomolies |  | 0.49653 | 0.49653 | 0.57083 | 0.074306 | 1.7833 | 1.7833 | CBM sensor interchange & turbine restored | Close | 0.04053 | WTG Unscheduled Maintenance | P-52 |  | 404
99 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-05 | P-08 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Pitch Drive Oil replacement work |  | 0.625 | 0.625 | 0.73056 | 0.10556 | 2.5333 | 2.5333 | Pitch Motor Oil replacement work done | Close | 0.057576 | WTG Unscheduled Maintenance | P-25 |  | 1483
100 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-06 | P-34 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Pitch Drive Oil replacement work |  | 0.425 | 0.425 | 0.49653 | 0.071528 | 1.7167 | 1.7167 | Pitch Motor Oil replacement work done | Close | 0.039015 | WTG Unscheduled Maintenance | P-04 |  | 3
101 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | P-26 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.35625 | 0.35625 | 0.42639 | 0.070139 | 1.6833 | 1.6833 | Manual stop for Foundation Pressure Grouting work | Close | 0.038258 | WTG Unscheduled Maintenance | P-25 |  | 983
102 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | P-37 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.39722 | 0.39722 | 0.44444 | 0.047222 | 1.1333 | 1.1333 | Q1 braker reset | Close | 0.025758 | WTG Breakdown Maintenance | P-32 |  | 715
103 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | P-15 | PWEPL | MSEDCL | 2.273% | 338 | Rotor CCU temperature warning | Rotor CCU temperature warning |  | 0.42847 | 0.42847 | 0.45972 | 0.03125 | 0.75 | 0.75 | Coolent Top up & turbine restored | Close | 0.017045 | WTG Breakdown Maintenance | P-14 |  | 1083
104 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | P-26 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.65972 | 0.65972 | 0.99931 | 0.33958 | 8.15 | 8.15 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.18523 | WTG Unscheduled Maintenance | P-25 |  | 4762
105 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | P-34 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Hub door open |  | 0.74514 | 0.74514 | 0.76111 | 0.015972 | 0.38333 | 0.38333 | hub door closing work completed | Close | 0.0087121 | WTG Unscheduled Maintenance | P-04 |  | 603
106 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | P-26 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0 | 0 | 0.67014 | 0.67014 | 16.0833 | 16.0833 | Foundation Pressure Grouting work completed | Close | 0.36553 | WTG Unscheduled Maintenance | P-27 |  | 3197
107 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | P-37 | PWEPL | MSEDCL | 2.273% | 431 | Yaw tooth sensor 2 timeout | Yaw tooth sensor 2 timeout |  | 0.29306 | 0.29306 | 0.32292 | 0.029861 | 0.71667 | 0.71667 | Yaw tooth sensor clean & turbine restored | Close | 0.016288 | WTG Breakdown Maintenance | P-32 |  | 219
108 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | P-25 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.36319 | 0.36319 | 0.99931 | 0.63611 | 15.2667 | 15.2667 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.34697 | WTG Unscheduled Maintenance | P-08 |  | 3034
109 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | P-27 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.53264 | 0.53264 | 0.99931 | 0.46667 | 11.2 | 11.2 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.25455 | WTG Unscheduled Maintenance | P-28 |  | 2226
110 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | P-14 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.73542 | 0.73542 | 0.99931 | 0.26389 | 6.3333 | 6.3333 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.14394 | WTG Unscheduled Maintenance | P-13 |  | 1259
111 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-25 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0 | 0 | 0.50972 | 0.50972 | 12.2333 | 12.2333 | Foundation Pressure Grouting work completed | Close | 0.27803 | WTG Unscheduled Maintenance | P-26 |  | 1809
112 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-27 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0 | 0 | 0.45764 | 0.45764 | 10.9833 | 10.9833 | Foundation Pressure Grouting work completed | Close | 0.24962 | WTG Unscheduled Maintenance | P-26 |  | 1624
113 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-14 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0 | 0 | 0.74375 | 0.74375 | 17.85 | 17.85 | Foundation Pressure Grouting work completed | Close | 0.40568 | WTG Unscheduled Maintenance | P-13 |  | 2639
114 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-23 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.37292 | 0.37292 | 0.99931 | 0.62639 | 15.0333 | 15.0333 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.34167 | WTG Unscheduled Maintenance | P-22 |  | 2223
115 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-40 | PWEPL | MSEDCL | 2.273% | 106 | Rotor CCU fault current | Converter rotor current fault |  | 0.56597 | 0.56597 | 0.64514 | 0.079167 | 1.9 | 1.9 | Replaced WEOR card | Close | 0.043182 | WTG Breakdown Maintenance | P-05 |  | 70
116 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-37 | PWEPL | MSEDCL | 2.273% | 431 | Yaw tooth sensor 2 timeout | Yaw tooth sensor 2 timeout |  | 0.77708 | 0.77708 | 0.82986 | 0.052778 | 1.2667 | 1.2667 | Yaw tooth sensor clean & Gap set & turbine restored | Close | 0.028788 | WTG Breakdown Maintenance | P-32 |  | 82
117 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | P-23 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0 | 0 | 0.52639 | 0.52639 | 12.6333 | 12.6333 | Foundation Pressure Grouting work completed | Close | 0.28712 | WTG Unscheduled Maintenance | P-22 |  | 1293
118 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | P-50 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.38958 | 0.38958 | 0.99931 | 0.60972 | 14.6333 | 14.6333 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.33258 | WTG Unscheduled Maintenance | P-51 |  | 1498
119 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-11 | P-52 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.57292 | 0.57292 | 0.99931 | 0.42639 | 10.2333 | 10.2333 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.23258 | WTG Unscheduled Maintenance | P-51 |  | 1048
120 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-50 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0 | 0 | 0.34444 | 0.34444 | 8.2667 | 8.2667 | Foundation Pressure Grouting work completed | Close | 0.18788 | WTG Unscheduled Maintenance | P-51 |  | 718
121 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-52 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0 | 0 | 0.34444 | 0.34444 | 8.2667 | 8.2667 | Foundation Pressure Grouting work completed | Close | 0.18788 | WTG Unscheduled Maintenance | P-51 |  | 719
122 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-52 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.60694 | 0.60694 | 0.67361 | 0.066667 | 1.6 | 1.6 | Foundation Pressure Grouting work completed | Close | 0.036364 | WTG Unscheduled Maintenance | P-51 |  | 139
123 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-02 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.37986 | 0.37986 | 0.99931 | 0.61944 | 14.8667 | 14.8667 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.33788 | WTG Unscheduled Maintenance | P-18 |  | 1292
124 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-13 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated |  | 0.41111 | 0.41111 | 0.50139 | 0.090278 | 2.1667 | 2.1667 | Cable Twist Release & Turbine Restored | Close | 0.049242 | WTG Breakdown Maintenance | P-12 |  | 0
125 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-26 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated |  | 0.38472 | 0.38472 | 0.41319 | 0.028472 | 0.68333 | 0.68333 | Cable Twist Release & Turbine Restored | Close | 0.01553 | WTG Breakdown Maintenance | P-25 |  | 0
126 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-41 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.64097 | 0.64097 | 0.67986 | 0.038889 | 0.93333 | 0.93333 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.021212 | WTG Unscheduled Maintenance | P-05 |  | 89
127 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-41 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.76389 | 0.76389 | 0.99931 | 0.23542 | 5.65 | 5.65 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.12841 | WTG Unscheduled Maintenance | P-05 |  | 483
128 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-47 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.65764 | 0.65764 | 0.67986 | 0.022222 | 0.53333 | 0.53333 | Circuit braker tripped so reset breaker | Close | 0.012121 | WTG Breakdown Maintenance | P-48 |  | 545
129 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-37 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.60694 | 0.60694 | 0.62639 | 0.019444 | 0.46667 | 0.46667 | Rebooted the PLC & reset at scada | Close | 0.010606 | WTG Breakdown Maintenance | P-32 |  | 0
130 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | P-02 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0 | 0 | 0.41667 | 0.41667 | 10 | 10 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.22727 | WTG Unscheduled Maintenance | P-18 |  | 787
131 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | P-02 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.69167 | 0.69167 | 0.70486 | 0.013194 | 0.31667 | 0.31667 | Foundation Pressure Grouting work completed | Close | 0.007197 | WTG Unscheduled Maintenance | P-18 |  | 25
132 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | P-41 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0 | 0 | 0.41667 | 0.41667 | 10 | 10 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.22727 | WTG Unscheduled Maintenance | P-05 |  | 787
133 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | P-41 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.69167 | 0.69167 | 0.99931 | 0.30764 | 7.3833 | 7.3833 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.1678 | WTG Unscheduled Maintenance | P-05 |  | 581
134 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | P-43 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.64375 | 0.64375 | 0.99931 | 0.35556 | 8.5333 | 8.5333 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.19394 | WTG Unscheduled Maintenance | P-27 |  | 672
135 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | P-46 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.69861 | 0.69861 | 0.71528 | 0.016667 | 0.4 | 0.4 | Rebooted the PLC & reset at scada | Close | 0.0090909 | WTG Breakdown Maintenance | P-45 |  | 213
136 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-41 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0 | 0 | 0.29167 | 0.29167 | 7 | 7 | Foundation Pressure Grouting work completed | Close | 0.15909 | WTG Unscheduled Maintenance | P-05 |  | 649
137 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-43 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0 | 0 | 0.79653 | 0.79653 | 19.1167 | 19.1167 | Foundation Pressure Grouting work completed | Close | 0.43447 | WTG Unscheduled Maintenance | P-27 |  | 1771
138 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-05 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.37569 | 0.37569 | 0.52014 | 0.14444 | 3.4667 | 3.4667 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.078788 | WTG Unscheduled Maintenance | P-41 |  | 322
139 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-05 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.75903 | 0.75903 | 0.99931 | 0.24028 | 5.7667 | 5.7667 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.13106 | WTG Unscheduled Maintenance | P-41 |  | 554
140 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-04 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0.64444 | 0.64444 | 0.99931 | 0.35486 | 8.5167 | 8.5167 | Foundation Pressure Grouting work completed,waiting for curing | Close | 0.19356 | WTG Unscheduled Maintenance | P-22 |  | 789
141 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-52 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.64722 | 0.64722 | 0.65694 | 0.0097222 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | WTG Breakdown Maintenance | P-51 |  | 0
142 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-26 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated |  | 0.40833 | 0.40833 | 0.49306 | 0.084722 | 2.0333 | 2.0333 | Cable Twist Release & Turbine Restored | Close | 0.046212 | WTG Breakdown Maintenance | P-27 |  | 0
143 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-05 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0 | 0 | 0.35278 | 0.35278 | 8.4667 | 8.4667 | Foundation Pressure Grouting work completed | Close | 0.19242 | WTG Unscheduled Maintenance | P-22 |  | 1504
144 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-04 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Foundation Pressure Grouting work |  | 0 | 0 | 0.675 | 0.675 | 16.2 | 16.2 | Foundation Pressure Grouting work completed | Close | 0.36818 | WTG Unscheduled Maintenance | P-41 |  | 786
145 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-18 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.65208 | 0.65208 | 0.66111 | 0.0090278 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | WTG Breakdown Maintenance | P-01 |  | 17
146 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-32 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.65208 | 0.65208 | 0.65903 | 0.0069444 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | WTG Breakdown Maintenance | P-37 |  | 15
147 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-28 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.66597 | 0.66597 | 0.67569 | 0.0097222 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | WTG Breakdown Maintenance | P-27 |  | 0
148 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-40 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.67361 | 0.67361 | 0.68333 | 0.0097222 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | WTG Breakdown Maintenance | P-05 |  | 33
149 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | P-15 | PWEPL | MSEDCL | 2.273% | 86 | Braking pad of secondary brake worn out | Secondary Brake Pad worn |  | 0.48958 | 0.48958 | 0.68819 | 0.19861 | 4.7667 | 4.7667 | Brake Pad replaced | Close | 0.10833 | WTG Breakdown Maintenance | P-16 |  | 949
150 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-27 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Slipring replacement work |  | 0.61111 | 0.61111 | 0.76458 | 0.15347 | 3.6833 | 3.6833 | Slipring replacement work completed | Close | 0.083712 | WTG Breakdown Maintenance | P-28 |  | 274
151 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-38 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault |  | 0.75347 | 0.75347 | 0.84306 | 0.089583 | 2.15 | 2.15 | Hard Rebooted Turbine from down tower assembly | Close | 0.048864 | WTG Breakdown Maintenance | P-17 |  | 2367
152 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-48 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | QHSE Turbine Audit |  | 0.56667 | 0.56667 | 0.65764 | 0.090972 | 2.1833 | 2.1833 | QHSE turbine audit completed | Close | 0.049621 | WTG Unscheduled Maintenance | P-47 |  | 227
153 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-34 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | QHSE Turbine Audit |  | 0.50069 | 0.50069 | 0.56806 | 0.067361 | 1.6167 | 1.6167 | QHSE turbine audit completed | Close | 0.036742 | WTG Unscheduled Maintenance | P-04 |  | 307
154 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-15 | PWEPL | MSEDCL | 2.273% | 41 | Vibrations sensor Defect | tower vibration sensor failure |  | 0.97778 | 0.97778 | 0.99931 | 0.021528 | 0.51667 | 0.51667 | Hard Rebooted Turbine from down tower assembly | Close | 0.011742 | WTG Breakdown Maintenance | P-14 |  | 48
155 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-56 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault |  | 0.62083 | 0.62083 | 0.62639 | 0.0055556 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | WTG Breakdown Maintenance | P-55 |  | 0
156 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-24 | P-14 | PWEPL | MSEDCL | 2.273% | 60 | Yaw limit switch activated | Yaw limit switch activated |  | 0.52708 | 0.52708 | 0.66111 | 0.13403 | 3.2167 | 3.2167 | Cable Twist Release & Turbine Restored | Close | 0.073106 | WTG Breakdown Maintenance | P-13 |  | 0
157 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-24 | P-19 | PWEPL | MSEDCL | 2.273% | 102 | DTA DIN03 control breaker status | Top box motor protection alarm |  | 0.58056 | 0.58056 | 0.65833 | 0.077778 | 1.8667 | 1.8667 | Replaced WETB card. | Close | 0.042424 | WTG Breakdown Maintenance | P-20 |  | 179
158 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | P-13 | PWEPL | MSEDCL | 2.273% | 54 | Anemometer defec | Anemometer failure |  | 0.42014 | 0.42014 | 0.82986 | 0.40972 | 9.8333 | 9.8333 | Anemometer signal communucating cable replaced | Close | 0.22348 | WTG Breakdown Maintenance | P-12 |  | 3776
159 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-31 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.27569 | 0.27569 | 0.38819 | 0.1125 | 2.7 | 2.7 | Hard Rebooted Turbine from down tower assembly | Close | 0.061364 | WTG Breakdown Maintenance | P-03 |  | 2018
160 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-52 | PWEPL | MSEDCL | 2.273% | 141 | Rotor CCU collective faults | Rotor CCU collective faults |  | 0.27569 | 0.27569 | 0.36458 | 0.088889 | 2.1333 | 2.1333 | Hard Rebooted Turbine from down tower assembly | Close | 0.048485 | WTG Breakdown Maintenance | P-51 |  | 1861
161 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-56 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.79861 | 0.79861 | 0.81944 | 0.020833 | 0.5 | 0.5 | Rebooted the PLC & reset at scada | Close | 0.011364 | WTG Breakdown Maintenance | P-55 |  | 667
162 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-17 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.90972 | 0.90972 | 0.95417 | 0.044444 | 1.0667 | 1.0667 | Replaced WEMA card. | Close | 0.024242 | WTG Breakdown Maintenance | P-16 |  | 290
163 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | P-48 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox inspection |  | 0.60833 | 0.60833 | 0.65486 | 0.046528 | 1.1167 | 1.1167 | Thermobypass valve replaced & gearbox inspection done. | Close | 0.025379 | WTG Breakdown Maintenance | P-47 |  | 973
164 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | P-09 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Gearbox inspection |  | 0.70347 | 0.70347 | 0.75139 | 0.047917 | 1.15 | 1.15 | Thermobypass valve replaced & gearbox inspection done. | Close | 0.026136 | WTG Breakdown Maintenance | P-8 |  | 544
165 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-29 | P-27 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault |  | 0.91736 | 0.91736 | 0.99653 | 0.079167 | 1.9 | 1.9 | Pitch Encoder clean properly & turbine restored | Close | 0.043182 | WTG Breakdown Maintenance | P-28 |  | 1947
166 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-30 | P-13 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault |  | 0.49861 | 0.49861 | 0.58333 | 0.084722 | 2.0333 | 2.0333 | Pitch Encoder clean properly & turbine restored | Close | 0.046212 | WTG Breakdown Maintenance | P-12 |  | 2769
167 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-30 | P-13 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.58333 | 0.58333 | 0.61458 | 0.03125 | 0.75 | 0.75 | Q1 braker reset | Close | 0.017045 | WTG Breakdown Maintenance | P-12 |  | 1184
168 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-30 | P-13 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.92014 | 0.92014 | 0.93472 | 0.014583 | 0.35 | 0.35 | Q1 braker reset | Close | 0.0079545 | WTG Breakdown Maintenance | P-12 |  | 412
169 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | P-15 | PWEPL | MSEDCL | 2.273% | 120 | Communication fault Pitch controller | Pitch controller communication fault |  | 0.25069 | 0.25069 | 0.57292 | 0.32222 | 7.7333 | 7.7333 | Replaced AEPC card & Top Box to Slipring Lane cable & turbine restored | Close | 0.17576 | WTG Breakdown Maintenance | P-14 |  | 3830
170 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | P-14 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.58264 | 0.58264 | 0.59722 | 0.014583 | 0.35 | 0.35 | Rebooted the PLC & reset at scada | Close | 0.0079545 | WTG Breakdown Maintenance | P-13 |  | 367
171 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | P-31 | PWEPL | MSEDCL | 2.273% | 52 | Gearbox oil ressure too lo | Gearbox oil pressure too low |  | 0.66042 | 0.66042 | 0.82778 | 0.16736 | 4.0167 | 4.0167 | Radiator motor replaced | Close | 0.091288 | WTG Breakdown Maintenance | P-03 |  | 1908
172 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-03 | P-28 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Yaw puck Pistons replacement |  | 0.51111 | 0.51111 | 0.75 | 0.23889 | 5.7333 | 5.7333 | Yaw Puck Pistons 6 nos replaced | Close | 0.1303 | WTG Unscheduled Maintenance | P-27 |  | 2526
173 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | P-28 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Yaw puck Pistons replacement |  | 0.40972 | 0.40972 | 0.74931 | 0.33958 | 8.15 | 8.15 | Yaw Puck Pistons 3 nos replaced | Close | 0.18523 | WTG Unscheduled Maintenance | P-27 |  | 4448
174 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | P-26 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | WET B card failure |  | 0.72778 | 0.72778 | 0.78611 | 0.058333 | 1.4 | 1.4 | Replaced WET B card | Close | 0.031818 | WTG Breakdown Maintenance | P-25 |  | 1349
175 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | P-38 | PWEPL | MSEDCL | 2.273% | 134 | Battery charging voltage not OK | Battery charging voltage not OK |  | 0.50764 | 0.50764 | 0.56944 | 0.061806 | 1.4833 | 1.4833 | Rebooted the PLC & reset at scada | Close | 0.033712 | WTG Breakdown Maintenance | P-17 |  | 403
176 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | P-38 | PWEPL | MSEDCL | 2.273% | 134 | Battery charging voltage not OK | Battery charging voltage not OK |  | 0.3125 | 0.3125 | 0.37083 | 0.058333 | 1.4 | 1.4 | Axis 3 Pitch Battery replaced | Close | 0.031818 | WTG Breakdown Maintenance | P-17 |  | 128
177 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | P-28 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Yaw puck Pistons replacement |  | 0.49097 | 0.49097 | 0.78264 | 0.29167 | 7 | 7 | Yaw Puck Pistons 6 nos replaced | Close | 0.15909 | WTG Unscheduled Maintenance | P-27 |  | 2265
178 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-06 | P-13 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Yaw puck Pistons replacement |  | 0.46111 | 0.46111 | 0.66528 | 0.20417 | 4.9 | 4.9 | Yaw Puck Pistons 12 nos replaced | Close | 0.11136 | WTG Unscheduled Maintenance | P-12 |  | 832
179 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-06 | P-42 | PWEPL | MSEDCL | 2.273% | 276 | Pitch thyristor 3 fault | Pitch thyristor 3 fault |  | 0.65417 | 0.65417 | 0.85972 | 0.20556 | 4.9333 | 4.9333 | Replaced Pitch Encoder & Carbon Brushes | Close | 0.11212 | WTG Breakdown Maintenance | P-48 |  | 2441
180 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | P-13 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault |  | 0.34167 | 0.34167 | 0.48056 | 0.13889 | 3.3333 | 3.3333 | Pitch Encoder replaced | Close | 0.075758 | WTG Breakdown Maintenance | P-12 |  | 147
181 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-07 | P-34 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Audit pending point closing work |  | 0.59236 | 0.59236 | 0.69931 | 0.10694 | 2.5667 | 2.5667 | Manual stop for Customer Audit pending point closing work | Close | 0.058333 | WTG Unscheduled Maintenance | P-04 |  | 692
182 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | P-12 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.44236 | 0.44236 | 0.44583 | 0.0034722 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | WTG Breakdown Maintenance | P-11 |  | 45
183 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-08 | P-48 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Audit pending point closing work |  | 0.57292 | 0.57292 | 0.61528 | 0.042361 | 1.0167 | 1.0167 | Manual stop for Customer Audit pending point closing work | Close | 0.023106 | WTG Unscheduled Maintenance | P-47 |  | 562
184 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-09 | P-34 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | IO Card 28V power supply failed |  | 0.89583 | 0.89583 | 0.90347 | 0.0076389 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | WTG Breakdown Maintenance | P-04 |  | 172
185 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | P-26 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | IO Card 28V power supply failed |  | 0.57639 | 0.57639 | 0.59028 | 0.013889 | 0.33333 | 0.33333 | Hard Rebooted Turbine from down tower assembly | Close | 0.0075758 | WTG Breakdown Maintenance | P-25 |  | 98
186 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | P-26 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | WET B card failure |  | 0.67361 | 0.67361 | 0.72708 | 0.053472 | 1.2833 | 1.2833 | Replaced WET B card | Close | 0.029167 | WTG Breakdown Maintenance | P-25 |  | 1117
187 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | P-17 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.57083 | 0.57083 | 0.57986 | 0.0090278 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | WTG Breakdown Maintenance | P-16 |  | 2
188 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | P-19 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.57083 | 0.57083 | 0.57639 | 0.0055556 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | WTG Breakdown Maintenance | P-17 |  | 94
189 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | P-20 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.57083 | 0.57083 | 0.57708 | 0.00625 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | WTG Breakdown Maintenance | P-19 |  | 106
190 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | P-38 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.57083 | 0.57083 | 0.57708 | 0.00625 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | WTG Breakdown Maintenance | P-17 |  | 106
191 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-11 | P-34 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | WET B card failure |  | 0.375 | 0.375 | 0.48819 | 0.11319 | 2.7167 | 2.7167 | Replaced WET B card & Hydraulic oil top & turbine restored | Close | 0.061742 | WTG Breakdown Maintenance | P-04 |  | 3094
192 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-13 | P-34 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | IO Card 28V power supply failed |  | 0.0069444 | 0.0069444 | 0.015278 | 0.0083333 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | WTG Breakdown Maintenance | P-04 |  | 60
193 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-13 | P-42 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | IO Card 28V power supply failed |  | 0.097917 | 0.097917 | 0.22986 | 0.13194 | 3.1667 | 3.1667 | Q13 MCB & Pitch centre box MCB tripped we reset MCB | Close | 0.07197 | WTG Breakdown Maintenance | P-48 |  | 8
194 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-13 | P-23 | PWEPL | MSEDCL | 2.273% | 274 | Pitch thyristor 1 fault | Pitch thyristor 1 fault |  | 0.20486 | 0.20486 | 0.22708 | 0.022222 | 0.53333 | 0.53333 | Rebooted the PLC & reset at scada | Close | 0.012121 | WTG Breakdown Maintenance | P-22 |  | 10
195 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-13 | P-23 | PWEPL | MSEDCL | 2.273% | 274 | Pitch thyristor 1 fault | AEPA card failure |  | 0.43611 | 0.43611 | 0.54931 | 0.11319 | 2.7167 | 2.7167 | Replaced AEPA card | Close | 0.061742 | WTG Breakdown Maintenance | P-22 |  | 126
196 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-13 | P-15 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Yaw puck Pistons replacement |  | 0.45347 | 0.45347 | 0.75347 | 0.3 | 7.2 | 7.2 | Yaw Puck Pistons 5 nos replaced | Close | 0.16364 | WTG Unscheduled Maintenance | P-14 |  | 209
197 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-13 | P-34 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | WET A card failure |  | 0.54167 | 0.54167 | 0.57708 | 0.035417 | 0.85 | 0.85 | Replaced WET A card | Close | 0.019318 | WTG Breakdown Maintenance | P-04 |  | 0
198 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-14 | P-15 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Yaw puck Pistons replacement |  | 0.42569 | 0.42569 | 0.71111 | 0.28542 | 6.85 | 6.85 | Yaw Puck Pistons 7 nos replaced | Close | 0.15568 | WTG Unscheduled Maintenance | P-14 |  | 413
199 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-15 | P-13 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault |  | 0.60764 | 0.60764 | 0.63333 | 0.025694 | 0.61667 | 0.61667 | Rebooted the PLC & reset at scada | Close | 0.014015 | WTG Breakdown Maintenance | P-12 |  | 120
200 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-15 | P-13 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | AEPA card failure |  | 0.73125 | 0.73125 | 0.925 | 0.19375 | 4.65 | 4.65 | Replaced AEPA card | Close | 0.10568 | WTG Breakdown Maintenance | P-12 |  | 2462
201 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-16 | P-13 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch Motor failure |  | 0.11389 | 0.11389 | 0.75764 | 0.64375 | 15.45 | 15.45 | Replaced Pitch motor | Close | 0.35114 | WTG Breakdown Maintenance | P-12 |  | 22312
202 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-16 | P-20 | PWEPL | MSEDCL | 2.273% | 101 | TopBox DIN21 motor protection aux contact string | DTA/MCC fuse or motor protection alarm |  | 0.18264 | 0.18264 | 0.20139 | 0.01875 | 0.45 | 0.45 | Q13 MCB tripped we reset MCB & turbine restored | Close | 0.010227 | WTG Breakdown Maintenance | P-38 |  | 1024
203 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-16 | P-34 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | WEMA card failure |  | 0.7875 | 0.7875 | 0.86806 | 0.080556 | 1.9333 | 1.9333 | Replaced WEMA card | Close | 0.043939 | WTG Breakdown Maintenance | P-04 |  | 3430
204 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-16 | P-34 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | IO Card 28V power supply failed |  | 0.89931 | 0.89931 | 0.99931 | 0.1 | 2.4 | 2.4 | work in progress | Close | 0.054545 | WTG Breakdown Maintenance | P-04 |  | 4085
205 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-04 | PWEPL | MSEDCL | 2.273% | 157 | Brake does not close | hydrolic unit valve replace & turbine restored |  | 0.29861 | 0.29861 | 0.45694 | 0.15833 | 3.8 | 3.8 | hydrolic unit valve replace & turbine restored | Close | 0.086364 | WTG Breakdown Maintenance | P-22 |  | 6064
206 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-28 | PWEPL | MSEDCL | 2.273% | 174 | Overtemperature transformer warning | Pitch thyristor 1 fault |  | 0.4 | 0.4 | 0.42778 | 0.027778 | 0.66667 | 0.66667 | Rebooted the PLC & reset at scada | Close | 0.015152 | WTG Breakdown Maintenance | P-27 |  | 1194
207 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-34 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | IO Card 28V power supply failed |  | 0 | 0 | 0.13681 | 0.13681 | 3.2833 | 3.2833 | Replaced WET B card | Close | 0.074621 | WTG Breakdown Maintenance | P-04 |  | 5432
208 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-04 | PWEPL | MSEDCL | 2.273% | 34 | Brake not released secondary brake | Secondary Hydraulic brake not released |  | 0 | 0 | 0.60486 | 0.60486 | 14.5167 | 14.5167 | Replaced Hydraulic unit pressure volve & WET C card | Close | 0.32992 | WTG Breakdown Maintenance | P-22 |  | 22835
209 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-16 | PWEPL | MSEDCL | 2.273% | 276 | Pitch thyristor 3 fault | Pitch thyristor 3 fault |  | 0.51042 | 0.51042 | 0.73403 | 0.22361 | 5.3667 | 5.3667 | Pitch Encoder replaced | Close | 0.12197 | WTG Breakdown Maintenance | P-15 |  | 8299
210 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-28 | PWEPL | MSEDCL | 2.273% | 274 | Pitch thyristor 1 fault | Pitch thyristor 1 fault |  | 0.37778 | 0.37778 | 0.42847 | 0.050694 | 1.2167 | 1.2167 | Rebooted the PLC & reset at scada | Close | 0.027652 | WTG Breakdown Maintenance | P-27 |  | 1301
211 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-28 | PWEPL | MSEDCL | 2.273% | 274 | Pitch thyristor 1 fault | Pitch thyristor 1 fault |  | 0.88611 | 0.88611 | 0.99236 | 0.10625 | 2.55 | 2.55 | Pitch Encoder clean & turbine restored | Close | 0.057955 | WTG Breakdown Maintenance | P-27 |  | 3918
212 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-56 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.83264 | 0.83264 | 0.85417 | 0.021528 | 0.51667 | 0.51667 | Rebooted the PLC & reset at scada | Close | 0.011742 | WTG Breakdown Maintenance | P-56 |  | 825
213 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-04 | PWEPL | MSEDCL | 2.273% | 34 | Brake not released secondary brake | Secondary Hydraulic brake not released |  | 0.033333 | 0.033333 | 0.24792 | 0.21458 | 5.15 | 5.15 | Replaced Hydraulic unit & turbine restored | Close | 0.11705 | WTG Breakdown Maintenance | P-22 |  | 8443
214 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-13 | PWEPL | MSEDCL | 2.273% | 14 | Generator overspeed | Generator over speed |  | 0.36875 | 0.36875 | 0.49583 | 0.12708 | 3.05 | 3.05 | Replaced Generator speed proximity sensor | Close | 0.069318 | WTG Breakdown Maintenance | P-12 |  | 4907
215 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-15 | PWEPL | MSEDCL | 2.273% | 63 | Safety chain | Safety chain |  | 0.43542 | 0.43542 | 0.49444 | 0.059028 | 1.4167 | 1.4167 | Turbine Inspection work done & turbine restored | Close | 0.032197 | WTG Breakdown Maintenance | P-14 |  | 2218
216 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-04 | PWEPL | MSEDCL | 2.273% | 34 | Brake not released secondary brake | Secondary Hydraulic brake not released |  | 0.71111 | 0.71111 | 0.99931 | 0.28819 | 6.9167 | 6.9167 | work in progress | Close | 0.1572 | WTG Breakdown Maintenance | P-22 |  | 9810
217 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-37 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.23403 | 0.23403 | 0.32708 | 0.093056 | 2.2333 | 2.2333 | Rebooted the PLC & reset at scada | Close | 0.050758 | WTG Breakdown Maintenance | P-32 |  | 5942
218 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-50 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.23403 | 0.23403 | 0.39583 | 0.16181 | 3.8833 | 3.8833 | Rebooted the PLC & reset at scada | Close | 0.088258 | WTG Breakdown Maintenance | P-51 |  | 1953
219 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-51 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.23403 | 0.23403 | 0.39583 | 0.16181 | 3.8833 | 3.8833 | Rebooted the PLC & reset at scada | Close | 0.088258 | WTG Breakdown Maintenance | P-52 |  | 8137
220 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-52 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.23403 | 0.23403 | 0.27569 | 0.041667 | 1 | 1 | Rebooted the PLC & reset at scada | Close | 0.022727 | WTG Breakdown Maintenance | P-50 |  | 0
221 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-56 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.23403 | 0.23403 | 0.29861 | 0.064583 | 1.55 | 1.55 | Rebooted the PLC & reset at scada | Close | 0.035227 | WTG Breakdown Maintenance | P-07 |  | 1502
222 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-56 | PWEPL | MSEDCL | 2.273% | 274 | Pitch thyristor 1 fault | Pitch thyristor 1 fault |  | 0.71736 | 0.71736 | 0.99931 | 0.28194 | 6.7667 | 6.7667 | work in progress | Close | 0.15379 | WTG Breakdown Maintenance | P-07 |  | 9523
223 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-56 | PWEPL | MSEDCL | 2.273% | 274 | Pitch thyristor 1 fault | Pitch thyristor 1 fault |  | 0 | 0 | 0.018056 | 0.018056 | 0.43333 | 0.43333 | Replaced K21 contactor coil & Auxilary & turbine restored | Close | 0.0098485 | WTG Breakdown Maintenance | P-55 |  | 1020
224 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-04 | PWEPL | MSEDCL | 2.273% | 34 | Brake not released secondary brake | Secondary Hydraulic brake not released |  | 0 | 0 | 0.079861 | 0.079861 | 1.9167 | 1.9167 | Replaced Hydraulic unit pressure volve & WET A card | Close | 0.043561 | WTG Breakdown Maintenance | P-22 |  | 2711
225 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-50 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.12222 | 0.12222 | 0.23681 | 0.11458 | 2.75 | 2.75 | Rebooted the PLC & reset at scada | Close | 0.0625 | WTG Breakdown Maintenance | P-51 |  | 1737
226 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-51 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.12222 | 0.12222 | 0.15556 | 0.033333 | 0.8 | 0.8 | Rebooted the PLC & reset at scada | Close | 0.018182 | WTG Breakdown Maintenance | P-52 |  | 0
227 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-37 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.12222 | 0.12222 | 0.18889 | 0.066667 | 1.6 | 1.6 | Rebooted the PLC & reset at scada | Close | 0.036364 | WTG Breakdown Maintenance | P-51 |  | 124
228 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-56 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault |  | 0.29583 | 0.29583 | 0.50694 | 0.21111 | 5.0667 | 5.0667 | Pitch Encoder clean & turbine restored | Close | 0.11515 | WTG Breakdown Maintenance | P-55 |  | 7231
229 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-50 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.29653 | 0.29653 | 0.33819 | 0.041667 | 1 | 1 | Q1 MCB tripped we reset MCB & turbine restored | Close | 0.022727 | WTG Breakdown Maintenance | P-51 |  | 1218
230 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-21 | P-37 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.38194 | 0.38194 | 0.51736 | 0.13542 | 3.25 | 3.25 | Q1 MCB tripped we reset MCB & turbine restored | Close | 0.073864 | WTG Breakdown Maintenance | P-32 |  | 3185
231 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-21 | P-06 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Foundation Inspection work |  | 0.65764 | 0.65764 | 0.68194 | 0.024306 | 0.58333 | 0.58333 | Manual stop for Foundation Inspection work | Close | 0.013258 | WTG Breakdown Maintenance | P-41 |  | 913
232 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-21 | P-45 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.67431 | 0.67431 | 0.68889 | 0.014583 | 0.35 | 0.35 | Rebooted the PLC & reset at scada | Close | 0.0079545 | WTG Breakdown Maintenance | P-46 |  | 750
233 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-21 | P-07 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault |  | 0.70278 | 0.70278 | 0.71042 | 0.0076389 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | WTG Breakdown Maintenance | P-18 |  | 184
234 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-21 | P-01 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.70903 | 0.70903 | 0.72431 | 0.015278 | 0.36667 | 0.36667 | Rebooted the PLC & reset at scada | Close | 0.0083333 | WTG Breakdown Maintenance | P-07 |  | 20
235 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | P-11 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault |  | 0.35972 | 0.35972 | 0.45556 | 0.095833 | 2.3 | 2.3 | Pitch Encoder clean & turbine restored | Close | 0.052273 | WTG Breakdown Maintenance | P-10 |  | 1968
236 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | P-37 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.82431 | 0.82431 | 0.85139 | 0.027083 | 0.65 | 0.65 | Q1 MCB tripped we reset MCB & turbine restored | Close | 0.014773 | WTG Breakdown Maintenance | P-32 |  | 1046
237 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | P-09 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.45764 | 0.45764 | 0.46042 | 0.0027778 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | WTG Breakdown Maintenance | P-08 |  | 176
238 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | P-10 | PWEPL | MSEDCL | 2.273% | 63 | Safety chain | Safety chain |  | 0.50556 | 0.50556 | 0.51181 | 0.00625 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | WTG Breakdown Maintenance | P-09 |  | 288
239 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | P-19 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.55625 | 0.55625 | 0.55903 | 0.0027778 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | WTG Breakdown Maintenance | P-20 |  | 199
240 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | P-23 | PWEPL | MSEDCL | 2.273% | 276 | Pitch thyristor 3 fault | Pitch thyristor 3 fault |  | 0.57292 | 0.57292 | 0.57569 | 0.0027778 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | WTG Breakdown Maintenance | P-22 |  | 266
241 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | P-26 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Foundation Inspection work |  | 0.58472 | 0.58472 | 0.59861 | 0.013889 | 0.33333 | 0.33333 | Manual stop for Foundation Inspection work | Close | 0.0075758 | WTG Breakdown Maintenance | P-25 |  | 791
242 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | P-34 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.55972 | 0.55972 | 0.56528 | 0.0055556 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | WTG Breakdown Maintenance | P-04 |  | 261
243 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-22 | P-38 | PWEPL | MSEDCL | 2.273% | 141 | Rotor CCU collective faults | Rotor side CCU collective faults |  | 0.53333 | 0.53333 | 0.53611 | 0.0027778 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | WTG Breakdown Maintenance | P-17 |  | 270
244 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-08 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout |  | 0.61875 | 0.61875 | 0.6625 | 0.04375 | 1.05 | 1.05 | Yaw tooth sensor clean & turbine restored | Close | 0.023864 | WTG Breakdown Maintenance | P-25 |  | 1573
245 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-09 | PWEPL | MSEDCL | 2.273% | 77 | Gearbox oil overtemperature | Gearbox oil over temperature |  | 0.65278 | 0.65278 | 0.76389 | 0.11111 | 2.6667 | 2.6667 | Replaced Radiater motor | Close | 0.060606 | WTG Breakdown Maintenance | P-10 |  | 3601
246 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-04 | PWEPL | MSEDCL | 2.273% | 352 | Communication fault wind measurement device | Wind measurment serieal communication fault |  | 0.76389 | 0.76389 | 0.79444 | 0.030556 | 0.73333 | 0.73333 | Replaced WET A card fuse & turbine restored | Close | 0.016667 | WTG Breakdown Maintenance | P-22 |  | 1330
247 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-41 | PWEPL | MSEDCL | 2.273% | 276 | Pitch thyristor 3 fault | Pitch thyristor 3 fault |  | 0.87639 | 0.87639 | 0.93819 | 0.061806 | 1.4833 | 1.4833 | Hard Rebooted Turbine from down tower assembly | Close | 0.033712 | WTG Breakdown Maintenance | P-05 |  | 2687
248 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-32 | PWEPL | MSEDCL | 2.273% | 213 | Battery voltage not OK axis 2 | Battery voltage not OK Axis 2 |  | 0.52222 | 0.52222 | 0.60556 | 0.083333 | 2 | 2 | Battery charger fuse replaced & turbine restored | Close | 0.045455 | WTG Breakdown Maintenance | P-37 |  | 3126
249 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-34 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | IO Card 28V power supply failed |  | 0.061806 | 0.061806 | 0.36458 | 0.30278 | 7.2667 | 7.2667 | WETB card & Power supply replaced | Close | 0.16515 | WTG Breakdown Maintenance | P-04 |  | 11713
250 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-50 | PWEPL | MSEDCL | 2.273% | 77 | Gearbox oil overtemperature | Gearbox oil over temperature |  | 0.50556 | 0.50556 | 0.67083 | 0.16528 | 3.9667 | 3.9667 | Replaced Radiater motor | Close | 0.090152 | WTG Breakdown Maintenance | P-51 |  | 6404
251 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-14 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout |  | 0.81736 | 0.81736 | 0.86597 | 0.048611 | 1.1667 | 1.1667 | Yaw tooth sensor clean & turbine restored | Close | 0.026515 | WTG Breakdown Maintenance | P-13 |  | 2111
252 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-04 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.72292 | 0.72292 | 0.72569 | 0.0027778 | 0.066667 | 0.066667 | Manual stop for Tower vibration test | Close | 0.0015152 | WTG Unscheduled Maintenance | P-22 |  | 262
253 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-34 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.73611 | 0.73611 | 0.7375 | 0.0013889 | 0.033333 | 0.033333 | Manual stop for Tower vibration test | Close | 0.00075758 | WTG Unscheduled Maintenance | P-04 |  | 261
254 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-23 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.74792 | 0.74792 | 0.74931 | 0.0013889 | 0.033333 | 0.033333 | Manual stop for Tower vibration test | Close | 0.00075758 | WTG Unscheduled Maintenance | P-22 |  | 264
255 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | P-04 | PWEPL | MSEDCL | 2.273% | 34 | Brake not released secondary brake | Secondary Hydraulic brake not released |  | 0.3375 | 0.3375 | 0.38542 | 0.047917 | 1.15 | 1.15 | Replaced Hydraulic unit pressure volve | Close | 0.026136 | WTG Breakdown Maintenance | P-22 |  | 1746
256 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | P-25 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Gearbox temperature warning |  | 0.58958 | 0.58958 | 0.65139 | 0.061806 | 1.4833 | 1.4833 | Replaced Thermo bypass volve | Close | 0.033712 | WTG Breakdown Maintenance | P-08 |  | 2339
257 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | P-26 | PWEPL | MSEDCL | 2.273% | 77 | Gearbox oil overtemperature | Gearbox oil over temperature |  | 0.70556 | 0.70556 | 0.85069 | 0.14514 | 3.4833 | 3.4833 | Replaced Radiater motor | Close | 0.079167 | WTG Breakdown Maintenance | P-25 |  | 4565
258 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | P-41 | PWEPL | MSEDCL | 2.273% | 276 | Pitch thyristor 3 fault | Pitch thyristor 3 fault |  | 0.62778 | 0.62778 | 0.74028 | 0.1125 | 2.7 | 2.7 | Pitch Encoder clean & turbine restored | Close | 0.061364 | WTG Breakdown Maintenance | P-05 |  | 4748
259 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | P-08 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.57917 | 0.57917 | 0.58333 | 0.0041667 | 0.1 | 0.1 | Manual stop for Tower vibration test | Close | 0.0022727 | WTG Unscheduled Maintenance | P-25 |  | 224
260 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | P-22 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.59861 | 0.59861 | 0.6 | 0.0013889 | 0.033333 | 0.033333 | Manual stop for Tower vibration test | Close | 0.00075758 | WTG Unscheduled Maintenance | P-04 |  | 269
261 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | P-43 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.6125 | 0.6125 | 0.61389 | 0.0013889 | 0.033333 | 0.033333 | Manual stop for Tower vibration test | Close | 0.00075758 | WTG Unscheduled Maintenance | P-27 |  | 207
262 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-25 | P-25 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.65139 | 0.65139 | 0.65486 | 0.0034722 | 0.083333 | 0.083333 | Manual stop for Tower vibration test | Close | 0.0018939 | WTG Unscheduled Maintenance | P-08 |  | 245
263 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-50 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | IO Card 28V power supply failed |  | 0.01875 | 0.01875 | 0.081944 | 0.063194 | 1.5167 | 1.5167 | Replaced WET B card | Close | 0.03447 | WTG Breakdown Maintenance | P-51 |  | 2635
264 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-41 | PWEPL | MSEDCL | 2.273% | 276 | Pitch thyristor 3 fault | Pitch thyristor 3 fault |  | 0.48611 | 0.48611 | 0.60833 | 0.12222 | 2.9333 | 2.9333 | Pitch Encoder replaced | Close | 0.066667 | WTG Breakdown Maintenance | P-05 |  | 4354
265 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-52 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Power curve issue |  | 0.78264 | 0.78264 | 0.81806 | 0.035417 | 0.85 | 0.85 | Uploaded CCU & WTG parameter & turbine restored | Close | 0.019318 | WTG Breakdown Maintenance | P-51 |  | 1455
266 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-27 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.70625 | 0.70625 | 0.70764 | 0.0013889 | 0.033333 | 0.033333 | Manual stop for Tower vibration test | Close | 0.00075758 | WTG Unscheduled Maintenance | P-28 |  | 214
267 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-28 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.71319 | 0.71319 | 0.71528 | 0.0020833 | 0.05 | 0.05 | Manual stop for Tower vibration test | Close | 0.0011364 | WTG Unscheduled Maintenance | P-27 |  | 168
268 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-09 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.72639 | 0.72639 | 0.72847 | 0.0020833 | 0.05 | 0.05 | Manual stop for Tower vibration test | Close | 0.0011364 | WTG Unscheduled Maintenance | P-10 |  | 214
269 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-27 | P-26 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault |  | 0.085417 | 0.085417 | 0.20694 | 0.12153 | 2.9167 | 2.9167 | Pitch Encoder clean & turbine restored | Close | 0.066288 | WTG Breakdown Maintenance | P-25 |  | 3734
270 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-27 | P-10 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.64792 | 0.64792 | 0.65 | 0.0020833 | 0.05 | 0.05 | Manual stop for Tower vibration test | Close | 0.0011364 | WTG Unscheduled Maintenance | P-09 |  | 155
271 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-27 | P-11 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.66806 | 0.66806 | 0.67014 | 0.0020833 | 0.05 | 0.05 | Manual stop for Tower vibration test | Close | 0.0011364 | WTG Unscheduled Maintenance | P-10 |  | 80
272 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-27 | P-12 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.68403 | 0.68403 | 0.68542 | 0.0013889 | 0.033333 | 0.033333 | Manual stop for Tower vibration test | Close | 0.00075758 | WTG Unscheduled Maintenance | P-11 |  | 189
273 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | P-43 | PWEPL | MSEDCL | 2.273% | 142 | Line CCU collective faults | Line CCU collective faults |  | 0.14583 | 0.14583 | 0.21875 | 0.072917 | 1.75 | 1.75 | Replace 500 Amp fuse & turbine started | Close | 0.039773 | WTG Breakdown Maintenance | P-27 |  | 2368
274 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | P-23 | PWEPL | MSEDCL | 2.273% | 276 | Pitch thyristor 3 fault | Pitch thyristor 3 fault |  | 0.34861 | 0.34861 | 0.36875 | 0.020139 | 0.48333 | 0.48333 | Rebooted the PLC & reset at scada | Close | 0.010985 | WTG Breakdown Maintenance | P-22 |  | 1035
275 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-28 | P-26 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault |  | 0.95764 | 0.95764 | 0.99931 | 0.041667 | 1 | 1 | Work in progress | open | 0.022727 | WTG Breakdown Maintenance | P-25 |  | 1791
276 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | P-26 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault |  | 0 | 0 | 0.083333 | 0.083333 | 2 | 2 | Pitch Encoder replaced | Close | 0.045455 | WTG Breakdown Maintenance | P-25 |  | 3187
277 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | P-17 | PWEPL | MSEDCL | 2.273% | 63 | Safety chain | Safety chain |  | 0.042361 | 0.042361 | 0.046528 | 0.0041667 | 0.1 | 0.1 | Rebooted the PLC & reset at scada | Close | 0.0022727 | WTG Breakdown Maintenance | P-16 |  | 444
278 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | P-19 | PWEPL | MSEDCL | 2.273% | 276 | Pitch thyristor 3 fault | Pitch thyristor 3 fault |  | 0.54722 | 0.54722 | 0.79028 | 0.24306 | 5.8333 | 5.8333 | Pitch Encoder & AEPA replaced | Close | 0.13258 | WTG Breakdown Maintenance | P-20 |  | 7104
279 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-30 | P-03 | PWEPL | MSEDCL | 2.273% | 276 | Pitch thyristor 3 fault | Pitch thyristor 3 fault |  | 0.38264 | 0.38264 | 0.99931 | 0.61667 | 14.8 | 14.8 | Work in progress | open | 0.33636 | WTG Breakdown Maintenance | P-02 |  | 22353
280 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-30 | P-11 | PWEPL | MSEDCL | 2.273% | 54 | Anemometer defec | Anemometer failure |  | 0.69861 | 0.69861 | 0.76736 | 0.06875 | 1.65 | 1.65 | connection tighght properly & turbine restored | Close | 0.0375 | WTG Breakdown Maintenance | P-10 |  | 2184
281 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-30 | P-11 | PWEPL | MSEDCL | 2.273% | 54 | Anemometer defec | Anemometer failure |  | 0.98611 | 0.98611 | 0.99931 | 0.013194 | 0.31667 | 0.31667 | Work in progress | open | 0.007197 | WTG Breakdown Maintenance | P-10 |  | 658
282 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-30 | P-16 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.65556 | 0.65556 | 0.65694 | 0.0013889 | 0.033333 | 0.033333 | Manual stop for Tower vibration test | Close | 0.00075758 | WTG Unscheduled Maintenance | P-15 |  | 48
283 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-30 | P-17 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.66944 | 0.66944 | 0.67153 | 0.0020833 | 0.05 | 0.05 | Manual stop for Tower vibration test | Close | 0.0011364 | WTG Unscheduled Maintenance | P-16 |  | 72
284 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-30 | P-19 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.64583 | 0.64583 | 0.64792 | 0.0020833 | 0.05 | 0.05 | Manual stop for Tower vibration test | Close | 0.0011364 | WTG Unscheduled Maintenance | P-17 |  | 72
285 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | P-11 | PWEPL | MSEDCL | 2.273% | 54 | Anemometer defec | Anemometer failure |  | 0 | 0 | 0.056944 | 0.056944 | 1.3667 | 1.3667 | connection tighght properly & turbine restored | Close | 0.031061 | WTG Breakdown Maintenance | P-10 |  | 1739
286 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | P-03 | PWEPL | MSEDCL | 2.273% | 276 | Pitch thyristor 3 fault | Pitch thyristor 3 fault |  | 0 | 0 | 0.60833 | 0.60833 | 14.6 | 14.6 | Replace Pitch motor bearing & turbine started | Close | 0.33182 | WTG Breakdown Maintenance | P-02 |  | 20182
287 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | P-06 | PWEPL | MSEDCL | 2.273% | 431 | Yaw tooth sensor 2 timeout | Yaw tooth sensor 2 timeout |  | 0.15972 | 0.15972 | 0.17986 | 0.020139 | 0.48333 | 0.48333 | Rebooted the PLC & reset at scada | Close | 0.010985 | WTG Breakdown Maintenance | P-41 |  | 877
288 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | P-06 | PWEPL | MSEDCL | 2.273% | 431 | Yaw tooth sensor 2 timeout | Yaw tooth sensor 2 timeout |  | 0.70208 | 0.70208 | 0.75903 | 0.056944 | 1.3667 | 1.3667 | Yaw tooth sensor clean & turbine restored | Close | 0.031061 | WTG Breakdown Maintenance | P-41 |  | 2197
289 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | P-10 | PWEPL | MSEDCL | 2.273% | 63 | Safety chain | Safety chain |  | 0.22708 | 0.22708 | 0.24375 | 0.016667 | 0.4 | 0.4 | Rebooted the PLC & reset at scada | Close | 0.0090909 | WTG Breakdown Maintenance | P-09 |  | 462
290 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | P-20 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.70417 | 0.70417 | 0.70556 | 0.0013889 | 0.033333 | 0.033333 | Manual stop for Tower vibration test | Close | 0.00075758 | WTG Unscheduled Maintenance | P-38 |  | 44
291 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | P-38 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.69236 | 0.69236 | 0.69444 | 0.0020833 | 0.05 | 0.05 | Manual stop for Tower vibration test | Close | 0.0011364 | WTG Unscheduled Maintenance | P-17 |  | 66
292 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-06 | PWEPL | MSEDCL | 2.273% | 431 | Yaw tooth sensor 2 timeout | Yaw tooth sensor 2 timeout |  | 0.48125 | 0.48125 | 0.56319 | 0.081944 | 1.9667 | 1.9667 | replce yaw tooth sensor & turbine restored | Close | 0.044697 | WTG Breakdown Maintenance | P-41 |  | 3152
293 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-20 | PWEPL | MSEDCL | 2.273% | 134 | Battery charging voltage not OK | Battery charging voltage not OK |  | 0.62708 | 0.65139 | 0.72014 | 0.093056 | 1.65 | 2.2333 | Q19 MCB tripped we reset MCB & turbine restored | Close | 0.050758 | WTG Breakdown Maintenance | P-38 |  | 2188
294 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-51 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.83542 | 0.83542 | 0.83681 | 0.0013889 | 0.033333 | 0.033333 | Manual stop for Tower vibration test | Close | 0.00075758 | WTG Unscheduled Maintenance | P-48 |  | 48
295 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-52 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.64931 | 0.64931 | 0.65208 | 0.0027778 | 0.066667 | 0.066667 | Manual stop for Tower vibration test | Close | 0.0015152 | WTG Unscheduled Maintenance | P-51 |  | 96
296 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-32 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.67361 | 0.67361 | 0.675 | 0.0013889 | 0.033333 | 0.033333 | Manual stop for Tower vibration test | Close | 0.00075758 | WTG Unscheduled Maintenance | P-37 |  | 48
297 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-37 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.68472 | 0.68472 | 0.68681 | 0.0020833 | 0.05 | 0.05 | Manual stop for Tower vibration test | Close | 0.0011364 | WTG Unscheduled Maintenance | P-32 |  | 72
298 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-17 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.65139 | 0.65139 | 0.67569 | 0.024306 | 0.58333 | 0.58333 | Rebooted the PLC & reset at scada | Close | 0.013258 | WTG Breakdown Maintenance | P-16 |  | 679
299 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-19 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.65139 | 0.65139 | 0.675 | 0.023611 | 0.56667 | 0.56667 | Rebooted the PLC & reset at scada | Close | 0.012879 | WTG Breakdown Maintenance | P-16 |  | 679
300 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-38 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.65139 | 0.65139 | 0.67431 | 0.022917 | 0.55 | 0.55 | Rebooted the PLC & reset at scada | Close | 0.0125 | WTG Breakdown Maintenance | P-16 |  | 679
301 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-34 | PWEPL | MSEDCL | 2.273% | 269 | Reboot PLC | Turbine Communication fault |  | 0.68194 | 0.68194 | 0.68889 | 0.0069444 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | WTG Breakdown Maintenance | P-04 |  | 13
302 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | P-42 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Hub door open |  | 0.50625 | 0.50625 | 0.52778 | 0.021528 | 0.51667 | 0.51667 | Hub door closing work completed | Close | 0.011742 | WTG Breakdown Maintenance | P-48 |  | 980
303 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | P-42 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.52778 | 0.52778 | 0.52986 | 0.0020833 | 0.05 | 0.05 | Manual stop for Tower vibration test | Close | 0.0011364 | WTG Unscheduled Maintenance | P-48 |  | 89
304 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | P-41 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Power curve issue |  | 0.59722 | 0.59722 | 0.62569 | 0.028472 | 0.68333 | 0.68333 | we check all circuit no deviation observe so Anemometer replaced | Close | 0.01553 | WTG Unscheduled Maintenance | P-05 |  | 1200
305 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | P-41 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.62569 | 0.62569 | 0.62847 | 0.0027778 | 0.066667 | 0.066667 | Manual stop for Tower vibration test | Close | 0.0015152 | WTG Unscheduled Maintenance | P-05 |  | 89
306 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | P-05 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.54375 | 0.54375 | 0.54653 | 0.0027778 | 0.066667 | 0.066667 | Manual stop for Tower vibration test | Close | 0.0015152 | WTG Unscheduled Maintenance | P-41 |  | 95
307 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | P-40 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.5625 | 0.5625 | 0.56528 | 0.0027778 | 0.066667 | 0.066667 | Manual stop for Tower vibration test | Close | 0.0015152 | WTG Unscheduled Maintenance | P-05 |  | 95
308 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | P-11 | PWEPL | MSEDCL | 2.273% | 276 | Pitch thyristor 3 fault | Pitch thyristor 3 fault |  | 0.91042 | 0.91042 | 0.91736 | 0.0069444 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | WTG Breakdown Maintenance | P-10 |  | 509
309 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | P-10 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | IO card 28V power supply failed |  | 0.63611 | 0.63611 | 0.65903 | 0.022917 | 0.55 | 0.55 | PDC box MCB tripped we reset MCB & turbine restored | Close | 0.0125 | WTG Breakdown Maintenance | P-09 |  | 449
310 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-04 | P-02 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.625 | 0.625 | 0.62778 | 0.0027778 | 0.066667 | 0.066667 | Manual stop for Tower vibration test | Close | 0.0015152 | WTG Unscheduled Maintenance | P-18 |  | 93
311 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-04 | P-03 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.6375 | 0.6375 | 0.64028 | 0.0027778 | 0.066667 | 0.066667 | Manual stop for Tower vibration test | Close | 0.0015152 | WTG Unscheduled Maintenance | P-31 |  | 93
312 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-04 | P-18 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.65139 | 0.65139 | 0.65347 | 0.0020833 | 0.05 | 0.05 | Manual stop for Tower vibration test | Close | 0.0011364 | WTG Unscheduled Maintenance | P-02 |  | 70
313 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-04 | P-31 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.64861 | 0.64861 | 0.65347 | 0.0048611 | 0.11667 | 0.11667 | Manual stop for Tower vibration test | Close | 0.0026515 | WTG Unscheduled Maintenance | P-03 |  | 70
314 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-04 | P-01 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | IO card 28V power supply failed |  | 0.95903 | 0.95903 | 0.99931 | 0.040278 | 0.96667 | 0.96667 | work in progress | Close | 0.02197 | WTG Breakdown Maintenance | P-07 |  | 1866
315 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-04 | P-22 | PWEPL | MSEDCL | 2.273% | 77 | Gearbox oil overtemperature | Gearbox oil over temperature |  | 0.66181 | 0.66181 | 0.7 | 0.038194 | 0.91667 | 0.91667 | Thermobypass valve replaced & gearbox inspection done. | Close | 0.020833 | WTG Breakdown Maintenance | P-04 |  | 1137
316 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-05 | P-01 | PWEPL | MSEDCL | 2.273% | 201 | PLC fault 24V Supply | IO card 28V power supply failed |  | 0 | 0 | 0.06875 | 0.06875 | 1.65 | 1.65 | Replaced WET B card | Close | 0.0375 | WTG Breakdown Maintenance | P-07 |  | 2833
317 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-05 | P-02 | PWEPL | MSEDCL | 2.273% | 77 | Gearbox oil overtemperature | Gearbox oil over temperature |  | 0.05625 | 0.05625 | 0.18611 | 0.12986 | 3.1167 | 3.1167 | Replaced Radiater motor | Close | 0.070833 | WTG Breakdown Maintenance | P-18 |  | 5277
318 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-05 | P-40 | PWEPL | MSEDCL | 2.273% | 275 | Pitch thyristor 2 fault | Pitch thyristor 2 fault |  | 0.10764 | 0.10764 | 0.59097 | 0.48333 | 11.6 | 11.6 | Pitch slipring to centre box mainson cable ground so use spare cable & WETA card replaced & turbine restored | Close | 0.26364 | WTG Breakdown Maintenance | P-05 |  | 17981
319 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-05 | P-26 | PWEPL | MSEDCL | 2.273% | 77 | Gearbox oil overtemperature | Gearbox oil over temperature |  | 0.31181 | 0.31181 | 0.36111 | 0.049306 | 1.1833 | 1.1833 | Rebooted the PLC & reset at scada | Close | 0.026894 | WTG Breakdown Maintenance | P-25 |  | 1972
320 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-05 | P-26 | PWEPL | MSEDCL | 2.273% | 77 | Gearbox oil overtemperature | Gearbox oil over temperature |  | 0.37708 | 0.37708 | 0.58611 | 0.20903 | 5.0167 | 5.0167 | Replaced Radiater motor & contactor | Close | 0.11402 | WTG Breakdown Maintenance | P-25 |  | 7062
321 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-06 | P-41 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Turbine Inspection |  | 0.72361 | 0.72361 | 0.72847 | 0.0048611 | 0.11667 | 0.11667 | Turbine Inspection done | Close | 0.0026515 | WTG Unscheduled Maintenance | P-05 |  | 265
322 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-06 | P-08 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout |  | 0.84931 | 0.84931 | 0.85764 | 0.0083333 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | WTG Breakdown Maintenance | P-25 |  | 202
323 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | P-08 | PWEPL | MSEDCL | 2.273% | 430 | Yaw tooth sensor 1 timeout | Yaw tooth sensor 1 timeout |  | 0.095139 | 0.095139 | 0.125 | 0.029861 | 0.71667 | 0.71667 | Yaw tooth sensor clean & turbine restored | Close | 0.016288 | WTG Breakdown Maintenance | P-25 |  | 1288
324 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | P-56 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.63194 | 0.63194 | 0.63403 | 0.0020833 | 0.05 | 0.05 | Manual stop for Tower vibration test | Close | 0.0011364 | WTG Unscheduled Maintenance | P-55 |  | 270
325 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | P-55 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.65208 | 0.65208 | 0.65486 | 0.0027778 | 0.066667 | 0.066667 | Manual stop for Tower vibration test | Close | 0.0015152 | WTG Unscheduled Maintenance | P-56 |  | 270
326 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | P-01 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.61181 | 0.61181 | 0.61319 | 0.0013889 | 0.033333 | 0.033333 | Manual stop for Tower vibration test | Close | 0.00075758 | WTG Unscheduled Maintenance | P-07 |  | 270
327 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | P-07 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.61875 | 0.61875 | 0.62083 | 0.0020833 | 0.05 | 0.05 | Manual stop for Tower vibration test | Close | 0.0011364 | WTG Unscheduled Maintenance | P-18 |  | 268
328 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | P-01 | PWEPL | MSEDCL | 2.273% |  | Pitch thyristor 1,2,3 fault | Pitch thyristor 1,2,3 fault |  | 0.93681 | 0.93681 | 0.99931 | 0.0625 | 1.5 | 1.5 | Work in progress | Close | 0.034091 | WTG Breakdown Maintenance | P-07 |  | 2527
329 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | P-34 | PWEPL | MSEDCL | 2.273% | 276 | Pitch thyristor 3 fault | Pitch thyristor 3 fault |  | 0.93472 | 0.93472 | 0.98819 | 0.053472 | 1.2833 | 1.2833 | Rebooted the PLC & reset at scada | Close | 0.029167 | WTG Breakdown Maintenance | P-22 |  | 2020
330 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | P-01 | PWEPL | MSEDCL | 2.273% |  | Pitch thyristor 1,2,3 fault | Pitch thyristor 1,2,3 fault |  | 0 | 0 | 0.093056 | 0.093056 | 2.2333 | 2.2333 | Replaced WET B card | Close | 0.050758 | WTG Breakdown Maintenance | P-07 |  | 3401
331 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | P-11 | PWEPL | MSEDCL | 2.273% | 54 | Anemometer defec | Anemometer failure |  | 0.38194 | 0.38194 | 0.43194 | 0.05 | 1.2 | 1.2 | Replaced Anemometer | Close | 0.027273 | WTG Breakdown Maintenance | P-10 |  | 1252
332 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | P-45 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.60972 | 0.60972 | 0.61111 | 0.0013889 | 0.033333 | 0.033333 | Manual stop for Tower vibration test | Close | 0.00075758 | WTG Unscheduled Maintenance | P-46 |  | 269
333 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | P-46 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.62083 | 0.62083 | 0.62431 | 0.0034722 | 0.083333 | 0.083333 | Manual stop for Tower vibration test | Close | 0.0018939 | WTG Unscheduled Maintenance | P-45 |  | 270
334 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | P-47 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.63056 | 0.63056 | 0.63333 | 0.0027778 | 0.066667 | 0.066667 | Manual stop for Tower vibration test | Close | 0.0015152 | WTG Unscheduled Maintenance | P-48 |  | 262
335 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | P-48 | PWEPL | MSEDCL | 2.273% | 3 | Manual Stop | Manual stop for Tower vibration test |  | 0.64236 | 0.64236 | 0.64514 | 0.0027778 | 0.066667 | 0.066667 | Manual stop for Tower vibration test | Close | 0.0015152 | WTG Unscheduled Maintenance | P-47 |  | 243
Formulas:
Month = Table5[[#This Row],[Date]]-DAY(Table5[[#This Row],[Date]])+1
Response Time = [Fault Clearance time]-[Fault Start TimeStamp]

## IGA_BD
Sr. No. | Financial Year | Calendar Year | Operating Year | Month | Date | Affected Feeder | SPV | Consumer | Plant Equivalent Weightage | Breakdown Description | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Fault Category | Loss of KWH | Estimated Energy Loss (kWh) | Scope | PTW No. | Job Card No.
1 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | Wind_F2 | PWEPL | MSEDCL | 27.27% | Group VCB-02 Yard YPM activity | 11:52 | 11:52 | 16:12 | 0 | 4.3333 | 4.3333 | Group VCB-02 Yard YPM activity complated | Close | 1.1818 | IG Scheduled Maintenance |  | 4001
2 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:12 | 16:12 | 16:32 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 27
3 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:12 | 16:12 | 16:32 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 27
4 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:12 | 16:12 | 16:32 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 27
5 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:12 | 16:12 | 16:32 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 27
6 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:12 | 16:12 | 16:32 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 27
7 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:12 | 16:12 | 16:32 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 27
8 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:12 | 16:12 | 16:32 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 27
9 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:12 | 16:12 | 16:32 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 27
10 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | P-22 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:12 | 16:12 | 16:32 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 27
11 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:12 | 16:12 | 16:32 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 27
12 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:12 | 16:12 | 16:32 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 27
13 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-29 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:12 | 16:12 | 16:32 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 27
14 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-30 | P-08 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for YPM activity | 10:22 | 10:22 | 13:42 | 0 | 3.3333 | 3.3333 | Group VCB-02,CKT-02 Yard YPM activity work | Close | 0.075758 | IG Scheduled Maintenance |  | 175
15 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-30 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:42 | 13:42 | 14:02 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 17
16 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-30 | P-25 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for YPM activity | 10:22 | 10:22 | 13:42 | 0 | 3.3333 | 3.3333 | Group VCB-02,CKT-02 Yard YPM activity work | Close | 0.075758 | IG Scheduled Maintenance |  | 175
17 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-30 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:42 | 13:42 | 14:02 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 17
18 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-30 | P-26 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for YPM activity | 10:22 | 10:22 | 13:42 | 0 | 3.3333 | 3.3333 | Group VCB-02,CKT-02 Yard YPM activity work | Close | 0.075758 | IG Scheduled Maintenance |  | 175
19 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-30 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:42 | 13:42 | 14:02 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 17
20 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-30 | P-27 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for YPM activity | 10:22 | 10:22 | 13:42 | 0 | 3.3333 | 3.3333 | Group VCB-02,CKT-02 Yard YPM activity work | Close | 0.075758 | IG Scheduled Maintenance |  | 175
21 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-30 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:42 | 13:42 | 14:02 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 17
22 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-30 | P-28 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for YPM activity | 10:22 | 10:22 | 13:42 | 0 | 3.3333 | 3.3333 | Group VCB-02,CKT-02 Yard YPM activity work | Close | 0.075758 | IG Scheduled Maintenance |  | 175
23 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-30 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:42 | 13:42 | 14:02 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Scheduled Maintenance |  | 17
24 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-04 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:10 | 11:10 | 19:53 | 0 | 8.7167 | 8.7167 | CT & PT Installation work | Close | 0.19811 | IG Unscheduled Maintenance |  | 724
25 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:53 | 19:53 | 20:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 28
26 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-22 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:10 | 11:10 | 19:53 | 0 | 8.7167 | 8.7167 | CT & PT Installation work | Close | 0.19811 | IG Unscheduled Maintenance |  | 724
27 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-22 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:53 | 19:53 | 20:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 28
28 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-23 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:10 | 11:10 | 19:53 | 0 | 8.7167 | 8.7167 | CT & PT Installation work | Close | 0.19811 | IG Unscheduled Maintenance |  | 724
29 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:53 | 19:53 | 20:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 28
30 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-34 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:10 | 11:10 | 19:53 | 0 | 8.7167 | 8.7167 | CT & PT Installation work | Close | 0.19811 | IG Unscheduled Maintenance |  | 724
31 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:53 | 19:53 | 20:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 28
32 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-43 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:10 | 11:10 | 19:53 | 0 | 8.7167 | 8.7167 | CT & PT Installation work | Close | 0.19811 | IG Unscheduled Maintenance |  | 724
33 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:53 | 19:53 | 20:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 28
34 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-32 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for Relay Removing work | 18:00 | 18:00 | 18:16 | 0 | 0.26667 | 0.26667 | Relay Removing work Complated | Close | 0.0060606 | IG Unscheduled Maintenance |  | 0
35 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:16 | 18:16 | 18:36 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 0
36 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-37 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for Relay Removing work | 16:15 | 16:15 | 16:25 | 0 | 0.16667 | 0.16667 | Relay Removing work Complated | Close | 0.0037879 | IG Unscheduled Maintenance |  | 16
37 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:25 | 16:25 | 16:44 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Unscheduled Maintenance |  | 0
38 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-42 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for Relay Removing work | 15:40 | 15:40 | 15:52 | 0 | 0.2 | 0.2 | Relay Removing work Complated | Close | 0.0045455 | IG Unscheduled Maintenance |  | 42
39 | 2025 | 2025 | Year_2 | 2025-03-01 | 2025-03-31 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:52 | 15:52 | 15:59 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | IG Unscheduled Maintenance |  | 39
40 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 19:06 | 19:06 | 20:32 | 0 | 1.4333 | 1.4333 | Test charged taken charged successfully | Close | 0.42348 | IG Breakdown Maintenance |  | 20207
41 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:32 | 20:32 | 20:49 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Breakdown Maintenance |  | 388
42 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:32 | 20:32 | 20:46 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Breakdown Maintenance |  | 388
43 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:32 | 20:32 | 20:50 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 388
44 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:32 | 20:32 | 20:47 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Breakdown Maintenance |  | 388
45 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:32 | 20:32 | 20:49 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Breakdown Maintenance |  | 388
46 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:32 | 20:32 | 20:49 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Breakdown Maintenance |  | 388
47 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:32 | 20:32 | 20:49 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Breakdown Maintenance |  | 388
48 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:32 | 20:32 | 20:45 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Breakdown Maintenance |  | 388
49 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:32 | 20:32 | 20:52 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 388
50 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:32 | 20:32 | 20:45 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Breakdown Maintenance |  | 388
51 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:32 | 20:32 | 20:52 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 388
52 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-07 | PWEPL | MSEDCL | 2.273% | VCB Tripped | 20:32 | 20:32 | 22:04 | 0 | 1.5333 | 1.5333 | VCB reet & Charge | Close | 0.034848 | IG Breakdown Maintenance |  | 450
53 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:04 | 22:04 | 22:24 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 388
54 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-56 | PWEPL | MSEDCL | 2.273% | VCB Tripped | 20:32 | 20:32 | 21:34 | 0 | 1.0333 | 1.0333 | VCB reset & Charge | Close | 0.023485 | IG Breakdown Maintenance |  | 234
55 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:34 | 21:34 | 21:54 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 388
56 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | Wind_F3 | PWEPL | MSEDCL | 20.45% | S/D for Group VCB -03 YPM Work | 13:53 | 13:53 | 16:04 | 0 | 2.1833 | 2.1833 | Group VCB-3 YPM Work completed | Close | 0.44659 | IG Scheduled Maintenance |  | 872
57 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:04 | 16:04 | 16:19 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Scheduled Maintenance |  | 17
58 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:04 | 16:04 | 16:19 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Scheduled Maintenance |  | 17
59 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:04 | 16:04 | 16:22 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Scheduled Maintenance |  | 17
60 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:04 | 16:04 | 16:20 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Scheduled Maintenance |  | 17
61 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:04 | 16:04 | 16:22 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Scheduled Maintenance |  | 17
62 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:04 | 16:04 | 16:21 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Scheduled Maintenance |  | 17
63 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:04 | 16:04 | 16:22 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Scheduled Maintenance |  | 17
64 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:04 | 16:04 | 16:20 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Scheduled Maintenance |  | 17
65 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:04 | 16:04 | 16:23 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Scheduled Maintenance |  | 17
66 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-09 | PWEPL | MSEDCL | 2.273% | VCB Tripped | 19:05 | 19:05 | 20:05 | 0 | 1 | 1 | VCB reset & Charge | Close | 0.022727 | IG Breakdown Maintenance |  | 1270
67 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-08 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:46 | 10:46 | 18:30 | 0 | 7.7333 | 7.7333 | WTG-27 & 28 Isolator shifting work | Close | 0.17576 | IG Unscheduled Maintenance |  | 1790
68 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:30 | 18:30 | 18:50 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 77
69 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-25 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:46 | 10:46 | 18:30 | 0 | 7.7333 | 7.7333 | WTG-27 & 28 Isolator shifting work | Close | 0.17576 | IG Unscheduled Maintenance |  | 1790
70 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:30 | 18:30 | 18:50 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 77
71 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-26 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:46 | 10:46 | 18:30 | 0 | 7.7333 | 7.7333 | WTG-27 & 28 Isolator shifting work | Close | 0.17576 | IG Unscheduled Maintenance |  | 1790
72 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:30 | 18:30 | 18:50 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 77
73 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-27 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:46 | 10:46 | 18:30 | 0 | 7.7333 | 7.7333 | WTG-27 & 28 Isolator shifting work | Close | 0.17576 | IG Unscheduled Maintenance |  | 1790
74 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:30 | 18:30 | 18:50 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 77
75 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-28 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:46 | 10:46 | 18:30 | 0 | 7.7333 | 7.7333 | WTG-27 & 28 Isolator shifting work | Close | 0.17576 | IG Unscheduled Maintenance |  | 1790
76 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-01 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:30 | 18:30 | 18:50 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 77
77 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | Wind_F3 | PWEPL | MSEDCL | 20.45% | Feeder tripped by E/F | 2:02 | 2:02 | 2:17 | 0 | 0.25 | 0.25 | Test charged taken charged successfully | Close | 0.051136 | IG Breakdown Maintenance |  | 904
78 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:17 | 2:17 | 2:31 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Breakdown Maintenance |  | 100
79 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:17 | 2:17 | 2:31 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Breakdown Maintenance |  | 100
80 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:17 | 2:17 | 2:33 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Breakdown Maintenance |  | 100
81 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:17 | 2:17 | 2:31 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Breakdown Maintenance |  | 100
82 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:17 | 2:17 | 2:32 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Breakdown Maintenance |  | 100
83 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:17 | 2:17 | 2:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 100
84 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:17 | 2:17 | 2:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 100
85 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:17 | 2:17 | 2:34 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Breakdown Maintenance |  | 100
86 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:17 | 2:17 | 2:32 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Breakdown Maintenance |  | 100
87 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-08 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 15:30 | 15:30 | 18:55 | 0 | 3.4167 | 3.4167 | WTG- 28 Isolator shifting work | Close | 0.077652 | IG Unscheduled Maintenance |  | 1022
88 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:55 | 18:55 | 19:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 99
89 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-25 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 15:30 | 15:30 | 18:55 | 0 | 3.4167 | 3.4167 | WTG- 28 Isolator shifting work | Close | 0.077652 | IG Unscheduled Maintenance |  | 1022
90 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:55 | 18:55 | 19:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 99
91 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-26 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 15:30 | 15:30 | 18:55 | 0 | 3.4167 | 3.4167 | WTG- 28 Isolator shifting work | Close | 0.077652 | IG Unscheduled Maintenance |  | 1022
92 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:55 | 18:55 | 19:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 99
93 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-27 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 15:30 | 15:30 | 18:55 | 0 | 3.4167 | 3.4167 | WTG- 28 Isolator shifting work | Close | 0.077652 | IG Unscheduled Maintenance |  | 1022
94 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:55 | 18:55 | 19:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 99
95 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-28 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 15:30 | 15:30 | 18:55 | 0 | 3.4167 | 3.4167 | WTG- 28 Isolator shifting work | Close | 0.077652 | IG Unscheduled Maintenance |  | 1022
96 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-02 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:55 | 18:55 | 19:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 99
97 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-14 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:01 | 11:01 | 17:00 | 0 | 5.9833 | 5.9833 | WTG- 20 Isolator shifting work | Close | 0.13598 | IG Unscheduled Maintenance |  | 437
98 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:00 | 17:00 | 17:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
99 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-15 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:01 | 11:01 | 17:00 | 0 | 5.9833 | 5.9833 | WTG- 20 Isolator shifting work | Close | 0.13598 | IG Unscheduled Maintenance |  | 437
100 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:00 | 17:00 | 17:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
101 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-16 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:01 | 11:01 | 17:00 | 0 | 5.9833 | 5.9833 | WTG- 20 Isolator shifting work | Close | 0.13598 | IG Unscheduled Maintenance |  | 437
102 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:00 | 17:00 | 17:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
103 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-17 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:01 | 11:01 | 17:00 | 0 | 5.9833 | 5.9833 | WTG- 20 Isolator shifting work | Close | 0.13598 | IG Unscheduled Maintenance |  | 437
104 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:00 | 17:00 | 17:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
105 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-19 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:01 | 11:01 | 17:00 | 0 | 5.9833 | 5.9833 | WTG- 20 Isolator shifting work | Close | 0.13598 | IG Unscheduled Maintenance |  | 437
106 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:00 | 17:00 | 17:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
107 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-20 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:01 | 11:01 | 17:00 | 0 | 5.9833 | 5.9833 | WTG- 20 Isolator shifting work | Close | 0.13598 | IG Unscheduled Maintenance |  | 437
108 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:00 | 17:00 | 17:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
109 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-38 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:01 | 11:01 | 17:00 | 0 | 5.9833 | 5.9833 | WTG- 20 Isolator shifting work | Close | 0.13598 | IG Unscheduled Maintenance |  | 437
110 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:00 | 17:00 | 17:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
111 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-34 | PWEPL | MSEDCL | 2.273% | VCB Tripped | 9:24 | 9:24 | 10:29 | 0 | 1.0833 | 1.0833 | VCB reset & Charge | Close | 0.024621 | IG Breakdown Maintenance |  | 3
112 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-03 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:29 | 10:29 | 10:33 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | IG Breakdown Maintenance |  | 0
113 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-14 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:18 | 10:18 | 19:20 | 0 | 9.0333 | 9.0333 | WTG- 19 Isolator shifting work | Close | 0.2053 | IG Unscheduled Maintenance |  | 1002
114 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:20 | 19:20 | 19:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 37
115 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-15 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:18 | 10:18 | 19:20 | 0 | 9.0333 | 9.0333 | WTG- 19 Isolator shifting work | Close | 0.2053 | IG Unscheduled Maintenance |  | 1002
116 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:20 | 19:20 | 19:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 37
117 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-16 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:18 | 10:18 | 19:20 | 0 | 9.0333 | 9.0333 | WTG- 19 Isolator shifting work | Close | 0.2053 | IG Unscheduled Maintenance |  | 1002
118 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:20 | 19:20 | 19:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 37
119 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-17 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:18 | 10:18 | 19:20 | 0 | 9.0333 | 9.0333 | WTG- 19 Isolator shifting work | Close | 0.2053 | IG Unscheduled Maintenance |  | 1002
120 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:20 | 19:20 | 19:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 37
121 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-19 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:18 | 10:18 | 19:20 | 0 | 9.0333 | 9.0333 | WTG- 19 Isolator shifting work | Close | 0.2053 | IG Unscheduled Maintenance |  | 1002
122 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:20 | 19:20 | 19:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 37
123 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-20 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:18 | 10:18 | 19:20 | 0 | 9.0333 | 9.0333 | WTG- 19 Isolator shifting work | Close | 0.2053 | IG Unscheduled Maintenance |  | 1002
124 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:20 | 19:20 | 19:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 37
125 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-38 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:18 | 10:18 | 19:20 | 0 | 9.0333 | 9.0333 | WTG- 19 Isolator shifting work | Close | 0.2053 | IG Unscheduled Maintenance |  | 1002
126 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:20 | 19:20 | 19:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 37
127 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | Wind_F4 | PWEPL | MSEDCL | 29.55% | S/D for Group VCB -4 YPM Work | 12:15 | 12:15 | 15:55 | 0 | 3.6667 | 3.6667 | Group VCB-4 YPM Work completed | Close | 1.0833 | IG Unscheduled Maintenance |  | 548
128 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:55 | 15:55 | 16:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 3.8
129 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:55 | 15:55 | 16:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 3.8
130 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:55 | 15:55 | 16:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 3.8
131 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:55 | 15:55 | 16:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 3.8
132 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:55 | 15:55 | 16:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 3.8
133 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:55 | 15:55 | 16:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 3.8
134 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:55 | 15:55 | 16:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 3.8
135 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:55 | 15:55 | 16:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 3.8
136 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:55 | 15:55 | 16:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 3.8
137 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:55 | 15:55 | 16:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 3.8
138 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:55 | 15:55 | 16:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 3.8
139 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:55 | 15:55 | 16:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 3.8
140 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:55 | 15:55 | 16:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 3.8
141 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-32 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for MSEB line cross work | 16:55 | 16:55 | 17:25 | 0 | 0.5 | 0.5 | Work Completed | Close | 0.011364 | IG Unscheduled Maintenance |  | 55
142 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-37 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for MSEB line cross work | 16:55 | 16:55 | 17:25 | 0 | 0.5 | 0.5 | Work Completed | Close | 0.011364 | IG Unscheduled Maintenance |  | 55
143 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-50 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for MSEB line cross work | 16:55 | 16:55 | 17:25 | 0 | 0.5 | 0.5 | Work Completed | Close | 0.011364 | IG Unscheduled Maintenance |  | 55
144 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-51 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for MSEB line cross work | 16:55 | 16:55 | 17:25 | 0 | 0.5 | 0.5 | Work Completed | Close | 0.011364 | IG Unscheduled Maintenance |  | 55
145 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-52 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for MSEB line cross work | 16:55 | 16:55 | 17:25 | 0 | 0.5 | 0.5 | Work Completed | Close | 0.011364 | IG Unscheduled Maintenance |  | 55
146 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-04 | P-55 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for MSEB line cross work | 16:55 | 16:55 | 17:25 | 0 | 0.5 | 0.5 | Work Completed | Close | 0.011364 | IG Unscheduled Maintenance |  | 55
147 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-01 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:40 | 8:40 | 19:35 | 0 | 10.9167 | 10.9167 | WTG- 01 Isolator shifting work | Close | 0.24811 | IG Unscheduled Maintenance |  | 1318
148 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:35 | 19:35 | 19:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 40
149 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-02 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:40 | 8:40 | 9:05 | 0 | 0.41667 | 0.41667 | WTG- 01 line jump open work | Close | 0.0094697 | IG Unscheduled Maintenance |  | 91
150 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:05 | 9:05 | 9:25 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 40
151 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-03 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:40 | 8:40 | 9:05 | 0 | 0.41667 | 0.41667 | WTG- 01 line jump open work | Close | 0.0094697 | IG Unscheduled Maintenance |  | 91
152 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:05 | 9:05 | 9:25 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 40
153 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-07 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:40 | 8:40 | 9:05 | 0 | 0.41667 | 0.41667 | WTG- 01 line jump open work | Close | 0.0094697 | IG Unscheduled Maintenance |  | 91
154 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:05 | 9:05 | 9:25 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 40
155 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-18 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:40 | 8:40 | 9:05 | 0 | 0.41667 | 0.41667 | WTG- 01 line jump open work | Close | 0.0094697 | IG Unscheduled Maintenance |  | 91
156 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:05 | 9:05 | 9:25 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 40
157 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-31 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:40 | 8:40 | 9:05 | 0 | 0.41667 | 0.41667 | WTG- 01 line jump open work | Close | 0.0094697 | IG Unscheduled Maintenance |  | 91
158 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:05 | 9:05 | 9:25 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 40
159 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-56 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:40 | 8:40 | 9:05 | 0 | 0.41667 | 0.41667 | WTG- 01 line jump open work | Close | 0.0094697 | IG Unscheduled Maintenance |  | 91
160 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:05 | 9:05 | 9:25 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 40
161 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-02 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 18:50 | 18:50 | 19:35 | 0 | 0.75 | 0.75 | WTG- 01 line jump connecting work | Close | 0.017045 | IG Unscheduled Maintenance |  | 50
162 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:35 | 19:35 | 19:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 40
163 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-03 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 18:50 | 18:50 | 19:35 | 0 | 0.75 | 0.75 | WTG- 01 line jump connecting work | Close | 0.017045 | IG Unscheduled Maintenance |  | 50
164 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:35 | 19:35 | 19:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 40
165 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-07 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 18:50 | 18:50 | 19:35 | 0 | 0.75 | 0.75 | WTG- 01 line jump connecting work | Close | 0.017045 | IG Unscheduled Maintenance |  | 50
166 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:35 | 19:35 | 19:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 40
167 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-18 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 18:50 | 18:50 | 19:35 | 0 | 0.75 | 0.75 | WTG- 01 line jump connecting work | Close | 0.017045 | IG Unscheduled Maintenance |  | 50
168 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:35 | 19:35 | 19:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 40
169 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-31 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 18:50 | 18:50 | 19:35 | 0 | 0.75 | 0.75 | WTG- 01 line jump connecting work | Close | 0.017045 | IG Unscheduled Maintenance |  | 50
170 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:35 | 19:35 | 19:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 40
171 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-56 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 18:50 | 18:50 | 19:35 | 0 | 0.75 | 0.75 | WTG- 01 line jump connecting work | Close | 0.017045 | IG Unscheduled Maintenance |  | 50
172 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-05 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:35 | 19:35 | 19:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 40
173 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-01 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 9:21 | 9:21 | 9:53 | 0 | 0.53333 | 0.53333 | WTG- 31 line jump open work | Close | 0.012121 | IG Unscheduled Maintenance |  | 47
174 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:53 | 9:53 | 10:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 29
175 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-02 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 9:21 | 9:21 | 9:53 | 0 | 0.53333 | 0.53333 | WTG- 31 line jump open work | Close | 0.012121 | IG Unscheduled Maintenance |  | 47
176 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:53 | 9:53 | 10:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 29
177 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-03 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 9:21 | 9:21 | 9:53 | 0 | 0.53333 | 0.53333 | WTG- 31 line jump open work | Close | 0.012121 | IG Unscheduled Maintenance |  | 47
178 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:53 | 9:53 | 10:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 29
179 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-07 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 9:21 | 9:21 | 9:53 | 0 | 0.53333 | 0.53333 | WTG- 31 line jump open work | Close | 0.012121 | IG Unscheduled Maintenance |  | 47
180 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:53 | 9:53 | 10:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 29
181 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-18 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 9:21 | 9:21 | 9:53 | 0 | 0.53333 | 0.53333 | WTG- 31 line jump open work | Close | 0.012121 | IG Unscheduled Maintenance |  | 47
182 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:53 | 9:53 | 10:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 29
183 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-31 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 9:21 | 9:21 | 19:21 | 0 | 10 | 10 | WTG- 31 Isolator shifting work | Close | 0.22727 | IG Unscheduled Maintenance |  | 879
184 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:21 | 19:21 | 19:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 4
185 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-56 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 9:21 | 9:21 | 9:53 | 0 | 0.53333 | 0.53333 | WTG- 31 line jump open work | Close | 0.012121 | IG Unscheduled Maintenance |  | 47
186 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:53 | 9:53 | 10:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 29
187 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 12:58 | 12:58 | 13:35 | 0 | 0.61667 | 0.61667 | Test charged taken charged successfully | Close | 0.1822 | IG Breakdown Maintenance |  | 702
188 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:35 | 13:35 | 13:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 27
189 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:35 | 13:35 | 13:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 27
190 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:35 | 13:35 | 13:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 27
191 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:35 | 13:35 | 13:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 27
192 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:35 | 13:35 | 13:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 27
193 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:35 | 13:35 | 13:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 27
194 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:35 | 13:35 | 13:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 27
195 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:35 | 13:35 | 13:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 27
196 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:35 | 13:35 | 13:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 27
197 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:35 | 13:35 | 13:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 27
198 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:35 | 13:35 | 13:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 27
199 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:35 | 13:35 | 13:55 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 27
200 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-01 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 18:37 | 18:37 | 19:21 | 0 | 0.73333 | 0.73333 | WTG- 31 line jump Connect work | Close | 0.016667 | IG Unscheduled Maintenance |  | 65
201 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:21 | 19:21 | 19:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 29
202 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-02 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 18:37 | 18:37 | 19:21 | 0 | 0.73333 | 0.73333 | WTG- 31 line jump Connect work | Close | 0.016667 | IG Unscheduled Maintenance |  | 65
203 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:21 | 19:21 | 19:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 29
204 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-03 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 18:37 | 18:37 | 19:21 | 0 | 0.73333 | 0.73333 | WTG- 31 line jump Connect work | Close | 0.016667 | IG Unscheduled Maintenance |  | 65
205 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:21 | 19:21 | 19:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 29
206 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-07 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 18:37 | 18:37 | 19:21 | 0 | 0.73333 | 0.73333 | WTG- 31 line jump Connect work | Close | 0.016667 | IG Unscheduled Maintenance |  | 65
207 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:21 | 19:21 | 19:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 29
208 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-18 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 18:37 | 18:37 | 19:21 | 0 | 0.73333 | 0.73333 | WTG- 31 line jump Connect work | Close | 0.016667 | IG Unscheduled Maintenance |  | 65
209 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:21 | 19:21 | 19:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 29
210 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-56 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 18:37 | 18:37 | 19:21 | 0 | 0.73333 | 0.73333 | WTG- 31 line jump Connect work | Close | 0.016667 | IG Unscheduled Maintenance |  | 65
211 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-06 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:21 | 19:21 | 19:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 29
212 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-05 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:36 | 8:36 | 9:29 | 0 | 0.88333 | 0.88333 | WTG- 40 Isolator shifting work | Close | 0.020076 | IG Unscheduled Maintenance |  | 112
213 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:29 | 9:29 | 9:39 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 21
214 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-06 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:36 | 8:36 | 9:29 | 0 | 0.88333 | 0.88333 | WTG- 40 Isolator shifting work | Close | 0.020076 | IG Unscheduled Maintenance |  | 112
215 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:29 | 9:29 | 9:49 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 42
216 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-40 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:36 | 8:36 | 18:54 | 0 | 10.3 | 10.3 | WTG- 40 Isolator shifting work | Close | 0.23409 | IG Unscheduled Maintenance |  | 1272
217 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:54 | 18:54 | 18:59 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | IG Unscheduled Maintenance |  | 42
218 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-41 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:36 | 8:36 | 9:29 | 0 | 0.88333 | 0.88333 | WTG- 40 Isolator shifting work | Close | 0.020076 | IG Unscheduled Maintenance |  | 112
219 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:29 | 9:29 | 9:49 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 42
220 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-05 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 17:50 | 17:50 | 18:54 | 0 | 1.0667 | 1.0667 | WTG- 41 Isolator shifting work | Close | 0.024242 | IG Unscheduled Maintenance |  | 135
221 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:54 | 18:54 | 19:14 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 42
222 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-06 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 17:50 | 17:50 | 18:54 | 0 | 1.0667 | 1.0667 | WTG- 41 Isolator shifting work | Close | 0.024242 | IG Unscheduled Maintenance |  | 135
223 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:54 | 18:54 | 19:14 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 42
224 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-41 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 17:50 | 17:50 | 18:54 | 0 | 1.0667 | 1.0667 | WTG- 41 Isolator shifting work | Close | 0.024242 | IG Unscheduled Maintenance |  | 135
225 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-07 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:54 | 18:54 | 19:14 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 42
226 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | P-42 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:06 | 8:06 | 8:57 | 0 | 0.85 | 0.85 | WTG- 47 line jump Connect work | Close | 0.019318 | IG Unscheduled Maintenance |  | 74
227 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:57 | 8:57 | 9:17 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 20
228 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | P-45 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:06 | 8:06 | 8:57 | 0 | 0.85 | 0.85 | WTG- 47 line jump Connect work | Close | 0.019318 | IG Unscheduled Maintenance |  | 74
229 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:57 | 8:57 | 9:17 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 20
230 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | P-46 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:06 | 8:06 | 8:57 | 0 | 0.85 | 0.85 | WTG- 47 line jump Connect work | Close | 0.019318 | IG Unscheduled Maintenance |  | 74
231 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:57 | 8:57 | 9:17 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 20
232 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | P-47 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:06 | 8:06 | 17:02 | 0 | 8.9333 | 8.9333 | WTG- 47 Isolator shifting work | Close | 0.20303 | IG Unscheduled Maintenance |  | 785
233 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | P-48 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:06 | 8:06 | 8:57 | 0 | 0.85 | 0.85 | WTG- 47 line jump Connect work | Close | 0.019318 | IG Unscheduled Maintenance |  | 74
234 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:57 | 8:57 | 9:17 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 20
235 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-42 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:03 | 8:03 | 8:46 | 0 | 0.71667 | 0.71667 | WTG- 48 line jump open work | Close | 0.016288 | IG Unscheduled Maintenance |  | 95
236 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:46 | 8:46 | 9:06 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 44
237 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-45 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:03 | 8:03 | 8:46 | 0 | 0.71667 | 0.71667 | WTG- 48 line jump open work | Close | 0.016288 | IG Unscheduled Maintenance |  | 95
238 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:46 | 8:46 | 9:06 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 44
239 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-46 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:03 | 8:03 | 8:46 | 0 | 0.71667 | 0.71667 | WTG- 48 line jump open work | Close | 0.016288 | IG Unscheduled Maintenance |  | 95
240 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:46 | 8:46 | 8:50 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | IG Unscheduled Maintenance |  | 9
241 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-47 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:03 | 8:03 | 8:46 | 0 | 0.71667 | 0.71667 | WTG- 48 line jump open work | Close | 0.016288 | IG Unscheduled Maintenance |  | 95
242 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:46 | 8:46 | 9:06 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 44
243 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-48 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:03 | 8:03 | 18:41 | 0 | 10.6333 | 10.6333 | WTG- 48 Isolator shifting work | Close | 0.24167 | IG Unscheduled Maintenance |  | 1400
244 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:41 | 18:41 | 18:56 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Unscheduled Maintenance |  | 40
245 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-42 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 17:45 | 17:45 | 18:41 | 0 | 0.93333 | 0.93333 | WTG- 47 line jump Connect work | Close | 0.021212 | IG Unscheduled Maintenance |  | 123
246 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:41 | 18:41 | 18:50 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | IG Unscheduled Maintenance |  | 20
247 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-45 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 17:45 | 17:45 | 18:41 | 0 | 0.93333 | 0.93333 | WTG- 47 line jump Connect work | Close | 0.021212 | IG Unscheduled Maintenance |  | 123
248 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:41 | 18:41 | 18:55 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Unscheduled Maintenance |  | 30
249 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-46 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 17:45 | 17:45 | 18:41 | 0 | 0.93333 | 0.93333 | WTG- 47 line jump Connect work | Close | 0.021212 | IG Unscheduled Maintenance |  | 123
250 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:41 | 18:41 | 18:50 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | IG Unscheduled Maintenance |  | 20
251 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-47 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 17:45 | 17:45 | 18:41 | 0 | 0.93333 | 0.93333 | WTG- 47 line jump Connect work | Close | 0.021212 | IG Unscheduled Maintenance |  | 123
252 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:41 | 18:41 | 18:52 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | IG Unscheduled Maintenance |  | 24
253 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | Wind_F1 | PWEPL | MSEDCL | 22.73% | Feeder tripped by O/C | 2:07 | 2:07 | 2:28 | 0 | 0.35 | 0.35 | Test charged taken charged successfully | Close | 0.079545 | IG Unscheduled Maintenance |  | 360
254 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:28 | 2:28 | 2:48 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 36
255 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:28 | 2:28 | 2:45 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Breakdown Maintenance |  | 36
256 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:28 | 2:28 | 2:48 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 36
257 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:28 | 2:28 | 2:46 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 36
258 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:28 | 2:28 | 2:48 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 36
259 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:28 | 2:28 | 2:41 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Breakdown Maintenance |  | 36
260 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:28 | 2:28 | 2:48 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 36
261 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:28 | 2:28 | 2:48 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 36
262 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:28 | 2:28 | 2:44 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Breakdown Maintenance |  | 36
263 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-09 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:28 | 2:28 | 2:48 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 36
264 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-32 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:58 | 7:58 | 8:39 | 0 | 0.68333 | 0.68333 | WTG- 51 & 52 line jump open work | Close | 0.01553 | IG Unscheduled Maintenance |  | 169
265 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:39 | 8:39 | 8:49 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 41
266 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-37 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:58 | 7:58 | 8:39 | 0 | 0.68333 | 0.68333 | WTG- 51 & 52 line jump open work | Close | 0.01553 | IG Unscheduled Maintenance |  | 169
267 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:39 | 8:39 | 8:49 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 41
268 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-50 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:58 | 7:58 | 8:39 | 0 | 0.68333 | 0.68333 | WTG- 51 & 52 line jump open work | Close | 0.01553 | IG Unscheduled Maintenance |  | 169
269 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:39 | 8:39 | 8:49 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 41
270 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-51 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:58 | 7:58 | 21:00 | 0 | 13.0333 | 13.0333 | WTG- 51 Isolator shifting work | Close | 0.29621 | IG Unscheduled Maintenance |  | 3226
271 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:00 | 21:00 | 21:10 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 41
272 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-52 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:58 | 7:58 | 21:00 | 0 | 13.0333 | 13.0333 | WTG- 52 Isolator shifting work | Close | 0.29621 | IG Unscheduled Maintenance |  | 3226
273 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:00 | 21:00 | 21:10 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 41
274 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-55 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:58 | 7:58 | 8:39 | 0 | 0.68333 | 0.68333 | WTG- 51 & 52 line jump open work | Close | 0.01553 | IG Unscheduled Maintenance |  | 169
275 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:39 | 8:39 | 8:49 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 41
276 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-32 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 20:28 | 20:28 | 21:00 | 0 | 0.53333 | 0.53333 | WTG- 51 & 52 line jump Connect work | Close | 0.012121 | IG Unscheduled Maintenance |  | 132
277 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:00 | 21:00 | 21:17 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Unscheduled Maintenance |  | 70
278 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-37 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 20:28 | 20:28 | 21:00 | 0 | 0.53333 | 0.53333 | WTG- 51 & 52 line jump Connect work | Close | 0.012121 | IG Unscheduled Maintenance |  | 132
279 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:00 | 21:00 | 21:10 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 41
280 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-50 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 20:28 | 20:28 | 21:00 | 0 | 0.53333 | 0.53333 | WTG- 51 & 52 line jump Connect work | Close | 0.012121 | IG Unscheduled Maintenance |  | 132
281 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:00 | 21:00 | 21:16 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Unscheduled Maintenance |  | 66
282 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-55 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 20:28 | 20:28 | 21:00 | 0 | 0.53333 | 0.53333 | WTG- 51 & 52 line jump Connect work | Close | 0.012121 | IG Unscheduled Maintenance |  | 132
283 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-10 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:00 | 21:00 | 21:09 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | IG Unscheduled Maintenance |  | 37
284 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-32 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:15 | 11:15 | 21:02 | 0 | 9.7833 | 9.7833 | WTG- 32 Isolator shifting work | Close | 0.22235 | IG Unscheduled Maintenance |  | 2168
285 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:02 | 21:02 | 21:22 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 74
286 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-37 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:15 | 11:15 | 21:02 | 0 | 9.7833 | 9.7833 | WTG- 37 Isolator shifting work | Close | 0.22235 | IG Unscheduled Maintenance |  | 2168
287 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:02 | 21:02 | 21:22 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 74
288 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-50 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:15 | 11:15 | 12:23 | 0 | 1.1333 | 1.1333 | WTG- 32 & 37 line jump open work | Close | 0.025758 | IG Unscheduled Maintenance |  | 251
289 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:23 | 12:23 | 12:43 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 74
290 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-51 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:15 | 11:15 | 12:23 | 0 | 1.1333 | 1.1333 | WTG- 32 & 37 line jump open work | Close | 0.025758 | IG Unscheduled Maintenance |  | 251
291 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:23 | 12:23 | 12:43 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 74
292 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-52 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:15 | 11:15 | 12:23 | 0 | 1.1333 | 1.1333 | WTG- 32 & 37 line jump open work | Close | 0.025758 | IG Unscheduled Maintenance |  | 251
293 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:23 | 12:23 | 12:43 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 74
294 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-55 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 11:15 | 11:15 | 12:23 | 0 | 1.1333 | 1.1333 | WTG- 32 & 37 line jump open work | Close | 0.025758 | IG Unscheduled Maintenance |  | 251
295 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:23 | 12:23 | 12:43 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 74
296 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-50 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 20:27 | 20:27 | 21:02 | 0 | 0.58333 | 0.58333 | WTG- 32 & 37 line jump Connect work | Close | 0.013258 | IG Unscheduled Maintenance |  | 129
297 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:02 | 21:02 | 21:22 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 74
298 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-51 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 20:27 | 20:27 | 21:02 | 0 | 0.58333 | 0.58333 | WTG- 32 & 37 line jump Connect work | Close | 0.013258 | IG Unscheduled Maintenance |  | 129
299 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:02 | 21:02 | 21:22 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 74
300 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-52 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 20:27 | 20:27 | 21:02 | 0 | 0.58333 | 0.58333 | WTG- 32 & 37 line jump Connect work | Close | 0.013258 | IG Unscheduled Maintenance |  | 129
301 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:02 | 21:02 | 21:22 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 74
302 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-55 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 20:27 | 20:27 | 21:02 | 0 | 0.58333 | 0.58333 | WTG- 32 & 37 line jump Connect work | Close | 0.013258 | IG Unscheduled Maintenance |  | 129
303 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-11 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:02 | 21:02 | 21:22 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 74
304 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | P-34 | PWEPL | MSEDCL | 2.273% | VCB Tripped | 3:58 | 3:58 | 4:25 | 0 | 0.45 | 0.45 | VCB reset & Charge | Close | 0.010227 | IG Breakdown Maintenance |  | 226
305 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-12 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:25 | 4:25 | 4:29 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | IG Breakdown Maintenance |  | 182
306 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | Wind_F2 | PWEPL | MSEDCL | 27.27% | Feeder tripped by O/C | 12:30 | 12:30 | 12:44 | 0 | 0.23333 | 0.23333 | Test charged taken charged successfully | Close | 0.063636 | IG Breakdown Maintenance |  | 991
307 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:44 | 12:44 | 12:50 | 0 | 0.1 | 0.1 | Rebooted the PLC & reset at scada | Close | 0.0022727 | IG Breakdown Maintenance |  | 34
308 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:44 | 12:44 | 12:47 | 0 | 0.05 | 0.05 | Rebooted the PLC & reset at scada | Close | 0.0011364 | IG Breakdown Maintenance |  | 17
309 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:44 | 12:44 | 12:48 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | IG Breakdown Maintenance |  | 22
310 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:44 | 12:44 | 12:47 | 0 | 0.05 | 0.05 | Rebooted the PLC & reset at scada | Close | 0.0011364 | IG Breakdown Maintenance |  | 17
311 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:44 | 12:44 | 12:55 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | IG Breakdown Maintenance |  | 62
312 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:44 | 12:44 | 12:57 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Breakdown Maintenance |  | 73
313 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:44 | 12:44 | 12:56 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | IG Breakdown Maintenance |  | 67
314 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:44 | 12:44 | 12:56 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | IG Breakdown Maintenance |  | 67
315 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | P-22 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:44 | 12:44 | 12:57 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Breakdown Maintenance |  | 73
316 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:44 | 12:44 | 12:57 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Breakdown Maintenance |  | 73
317 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:44 | 12:44 | 12:58 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Breakdown Maintenance |  | 78
318 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-17 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:44 | 12:44 | 12:56 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | IG Breakdown Maintenance |  | 67
319 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-21 | Wind_F1 | PWEPL | MSEDCL | 22.73% | Feeder tripped by O/C | 22:56 | 22:56 | 23:59 | 0 | 1.05 | 1.05 | work in progress | Close | 0.23864 | IG Breakdown Maintenance |  | 3475
320 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | Wind_F1 | PWEPL | MSEDCL | 22.73% | Feeder tripped by O/C | 0:00 | 0:00 | 0:20 | 0 | 0.33333 | 0.33333 | Test charged taken charged successfully | Close | 0.075758 | IG Breakdown Maintenance |  | 995
321 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 99.5
322 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 99.5
323 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 99.5
324 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 99.5
325 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 99.5
326 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 99.5
327 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 99.5
328 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 99.5
329 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 99.5
330 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:20 | 0:20 | 0:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 99.5
331 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | P-08 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:16 | 10:16 | 19:55 | 0 | 9.65 | 9.65 | CT,PT cabling & tray Installation work | Close | 0.21932 | IG Unscheduled Maintenance |  | 1694
332 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:55 | 19:55 | 20:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 60
333 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | P-25 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:16 | 10:16 | 19:55 | 0 | 9.65 | 9.65 | CT,PT cabling & tray Installation work | Close | 0.21932 | IG Unscheduled Maintenance |  | 1694
334 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:55 | 19:55 | 20:11 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Unscheduled Maintenance |  | 48
335 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | P-26 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:16 | 10:16 | 19:55 | 0 | 9.65 | 9.65 | CT,PT cabling & tray Installation work | Close | 0.21932 | IG Unscheduled Maintenance |  | 1694
336 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:55 | 19:55 | 20:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 60
337 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | P-27 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:16 | 10:16 | 19:55 | 0 | 9.65 | 9.65 | CT,PT cabling & tray Installation work | Close | 0.21932 | IG Unscheduled Maintenance |  | 1694
338 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:55 | 19:55 | 20:12 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Unscheduled Maintenance |  | 51
339 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | P-28 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 10:16 | 10:16 | 19:55 | 0 | 9.65 | 9.65 | CT,PT cabling & tray Installation work | Close | 0.21932 | IG Unscheduled Maintenance |  | 1694
340 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-23 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:55 | 19:55 | 20:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 60
341 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | P-09 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:55 | 8:55 | 19:15 | 0 | 10.3333 | 10.3333 | CT,PT cabling & tray Installation work | Close | 0.23485 | IG Unscheduled Maintenance |  | 1475
342 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:15 | 19:15 | 19:32 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Unscheduled Maintenance |  | 41
343 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | P-10 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:55 | 8:55 | 19:15 | 0 | 10.3333 | 10.3333 | CT,PT cabling & tray Installation work | Close | 0.23485 | IG Unscheduled Maintenance |  | 1475
344 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:15 | 19:15 | 19:31 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Unscheduled Maintenance |  | 39
345 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | P-11 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:55 | 8:55 | 19:15 | 0 | 10.3333 | 10.3333 | CT,PT cabling & tray Installation work | Close | 0.23485 | IG Unscheduled Maintenance |  | 1475
346 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:15 | 19:15 | 19:32 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Unscheduled Maintenance |  | 41
347 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | P-12 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:55 | 8:55 | 19:15 | 0 | 10.3333 | 10.3333 | CT,PT cabling & tray Installation work | Close | 0.23485 | IG Unscheduled Maintenance |  | 1475
348 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:15 | 19:15 | 19:31 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Unscheduled Maintenance |  | 39
349 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | P-13 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:55 | 8:55 | 19:15 | 0 | 10.3333 | 10.3333 | CT,PT cabling & tray Installation work | Close | 0.23485 | IG Unscheduled Maintenance |  | 1474
350 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-24 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:15 | 19:15 | 19:35 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 49
351 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | Wind_F1 | PWEPL | MSEDCL | 22.73% | Feeder tripped by O/C | 3:57 | 3:57 | 4:31 | 0 | 0.56667 | 0.56667 | Test charged taken charged successfully | Close | 0.12879 | IG Breakdown Maintenance |  | 1482
352 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:51 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 87
353 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:46 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Breakdown Maintenance |  | 65
354 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:50 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Breakdown Maintenance |  | 82
355 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:51 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 87
356 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:51 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 87
357 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:50 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Breakdown Maintenance |  | 82
358 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:51 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 87
359 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:51 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 87
360 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:49 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 78
361 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-25 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:31 | 4:31 | 4:51 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 87
362 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-14 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:19 | 7:19 | 18:42 | 0 | 11.3833 | 11.3833 | CT,PT cabling & tray Installation work | Close | 0.25871 | IG Unscheduled Maintenance |  | 1559
363 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:42 | 18:42 | 18:58 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Unscheduled Maintenance |  | 37
364 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-15 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:19 | 7:19 | 18:42 | 0 | 11.3833 | 11.3833 | CT,PT cabling & tray Installation work | Close | 0.25871 | IG Unscheduled Maintenance |  | 1560
365 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:42 | 18:42 | 18:52 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 23
366 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-16 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:19 | 7:19 | 18:42 | 0 | 11.3833 | 11.3833 | CT,PT cabling & tray Installation work | Close | 0.25871 | IG Unscheduled Maintenance |  | 1559
367 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:42 | 18:42 | 18:58 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Unscheduled Maintenance |  | 37
368 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-17 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:19 | 7:19 | 18:42 | 0 | 11.3833 | 11.3833 | CT,PT cabling & tray Installation work | Close | 0.25871 | IG Unscheduled Maintenance |  | 1559
369 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:42 | 18:42 | 18:57 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Unscheduled Maintenance |  | 35
370 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-19 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:19 | 7:19 | 18:42 | 0 | 11.3833 | 11.3833 | CT,PT cabling & tray Installation work | Close | 0.25871 | IG Unscheduled Maintenance |  | 1558
371 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:42 | 18:42 | 19:02 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 47
372 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-20 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:19 | 7:19 | 18:42 | 0 | 11.3833 | 11.3833 | CT,PT cabling & tray Installation work | Close | 0.25871 | IG Unscheduled Maintenance |  | 1558
373 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:42 | 18:42 | 19:02 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 47
374 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-38 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:19 | 7:19 | 18:42 | 0 | 11.3833 | 11.3833 | CT,PT cabling & tray Installation work | Close | 0.25871 | IG Unscheduled Maintenance |  | 1558
375 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-26 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:42 | 18:42 | 19:02 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 47
376 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | P-04 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:51 | 7:51 | 16:20 | 0 | 8.4833 | 8.4833 | CT,PT cabling & tray Installation work | Close | 0.1928 | IG Unscheduled Maintenance |  | 3829
377 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:20 | 16:20 | 16:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 156
378 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | P-22 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:51 | 7:51 | 16:20 | 0 | 8.4833 | 8.4833 | CT,PT cabling & tray Installation work | Close | 0.1928 | IG Unscheduled Maintenance |  | 3831
379 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | P-22 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:20 | 16:20 | 16:36 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Unscheduled Maintenance |  | 124
380 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | P-23 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:51 | 7:51 | 16:20 | 0 | 8.4833 | 8.4833 | CT,PT cabling & tray Installation work | Close | 0.1928 | IG Unscheduled Maintenance |  | 3830
381 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:20 | 16:20 | 16:37 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Unscheduled Maintenance |  | 132
382 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | P-34 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:51 | 7:51 | 16:20 | 0 | 8.4833 | 8.4833 | CT,PT cabling & tray Installation work | Close | 0.1928 | IG Unscheduled Maintenance |  | 3831
383 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:20 | 16:20 | 16:35 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Unscheduled Maintenance |  | 116
384 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | P-43 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:51 | 7:51 | 16:20 | 0 | 8.4833 | 8.4833 | CT,PT cabling & tray Installation work | Close | 0.1928 | IG Unscheduled Maintenance |  | 3831
385 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-03 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:20 | 16:20 | 16:35 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Unscheduled Maintenance |  | 116
386 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | P-19 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 10:19 | 10:19 | 10:55 | 0 | 0.6 | 0.6 | VCB reset & Charge | Close | 0.013636 | IG Breakdown Maintenance |  | 760
387 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-08 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:55 | 10:55 | 11:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 421
388 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | P-42 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:03 | 8:03 | 13:28 | 0 | 5.4167 | 5.4167 | CT,PT cabling & tray Installation work | Close | 0.12311 | IG Unscheduled Maintenance |  | 1075
389 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:28 | 13:28 | 13:42 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Unscheduled Maintenance |  | 48
390 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | P-45 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:03 | 8:03 | 13:28 | 0 | 5.4167 | 5.4167 | CT,PT cabling & tray Installation work | Close | 0.12311 | IG Unscheduled Maintenance |  | 1075
391 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:28 | 13:28 | 13:42 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Unscheduled Maintenance |  | 48
392 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | P-46 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:03 | 8:03 | 13:28 | 0 | 5.4167 | 5.4167 | CT,PT cabling & tray Installation work | Close | 0.12311 | IG Unscheduled Maintenance |  | 1075
393 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:28 | 13:28 | 13:40 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | IG Unscheduled Maintenance |  | 41
394 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | P-47 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:03 | 8:03 | 13:28 | 0 | 5.4167 | 5.4167 | CT,PT cabling & tray Installation work | Close | 0.12311 | IG Unscheduled Maintenance |  | 1075
395 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:28 | 13:28 | 13:40 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | IG Unscheduled Maintenance |  | 41
396 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | P-48 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:03 | 8:03 | 13:28 | 0 | 5.4167 | 5.4167 | CT,PT cabling & tray Installation work | Close | 0.12311 | IG Unscheduled Maintenance |  | 1075
397 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-09 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:28 | 13:28 | 13:40 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | IG Unscheduled Maintenance |  | 41
398 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-01 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:40 | 7:40 | 13:56 | 0 | 6.2667 | 6.2667 | CT,PT cabling & tray Installation work | Close | 0.14242 | IG Unscheduled Maintenance |  | 926
399 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:56 | 13:56 | 14:11 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Unscheduled Maintenance |  | 38
400 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-02 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:40 | 7:40 | 13:56 | 0 | 6.2667 | 6.2667 | CT,PT cabling & tray Installation work | Close | 0.14242 | IG Unscheduled Maintenance |  | 927
401 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:56 | 13:56 | 14:01 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | IG Unscheduled Maintenance |  | 12
402 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-03 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:40 | 7:40 | 13:56 | 0 | 6.2667 | 6.2667 | CT,PT cabling & tray Installation work | Close | 0.14242 | IG Unscheduled Maintenance |  | 924
403 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:56 | 13:56 | 14:15 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Unscheduled Maintenance |  | 49
404 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-07 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:40 | 7:40 | 13:56 | 0 | 6.2667 | 6.2667 | CT,PT cabling & tray Installation work | Close | 0.14242 | IG Unscheduled Maintenance |  | 926
405 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:56 | 13:56 | 14:06 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 25
406 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-18 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:40 | 7:40 | 13:56 | 0 | 6.2667 | 6.2667 | CT,PT cabling & tray Installation work | Close | 0.14242 | IG Unscheduled Maintenance |  | 926
407 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:56 | 13:56 | 14:07 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | IG Unscheduled Maintenance |  | 28
408 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-31 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:40 | 7:40 | 13:56 | 0 | 6.2667 | 6.2667 | CT,PT cabling & tray Installation work | Close | 0.14242 | IG Unscheduled Maintenance |  | 936
409 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:56 | 13:56 | 14:05 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | IG Unscheduled Maintenance |  | 23
410 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-56 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 7:40 | 7:40 | 13:56 | 0 | 6.2667 | 6.2667 | CT,PT cabling & tray Installation work | Close | 0.14242 | IG Unscheduled Maintenance |  | 926
411 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-10 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:56 | 13:56 | 14:07 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | IG Unscheduled Maintenance |  | 28
412 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-32 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:16 | 8:16 | 14:14 | 0 | 5.9667 | 5.9667 | CT,PT cabling & tray Installation work | Close | 0.13561 | IG Unscheduled Maintenance |  | 519
413 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:14 | 14:14 | 14:25 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | IG Unscheduled Maintenance |  | 16
414 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-37 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:16 | 8:16 | 14:14 | 0 | 5.9667 | 5.9667 | CT,PT cabling & tray Installation work | Close | 0.13561 | IG Unscheduled Maintenance |  | 518
415 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:14 | 14:14 | 14:34 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 30
416 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-50 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:16 | 8:16 | 14:14 | 0 | 5.9667 | 5.9667 | CT,PT cabling & tray Installation work | Close | 0.13561 | IG Unscheduled Maintenance |  | 518
417 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:14 | 14:14 | 14:30 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Unscheduled Maintenance |  | 24
418 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-51 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:16 | 8:16 | 14:14 | 0 | 5.9667 | 5.9667 | CT,PT cabling & tray Installation work | Close | 0.13561 | IG Unscheduled Maintenance |  | 518
419 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:14 | 14:14 | 14:27 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Unscheduled Maintenance |  | 19
420 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-52 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:16 | 8:16 | 14:14 | 0 | 5.9667 | 5.9667 | CT,PT cabling & tray Installation work | Close | 0.13561 | IG Unscheduled Maintenance |  | 518
421 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:14 | 14:14 | 14:34 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 30
422 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-55 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 8:16 | 8:16 | 14:14 | 0 | 5.9667 | 5.9667 | CT,PT cabling & tray Installation work | Close | 0.13561 | IG Unscheduled Maintenance |  | 518
423 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:14 | 14:14 | 14:24 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 15
424 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | Wind_F3 | PWEPL | MSEDCL | 20.45% | Feeder tripped by O/C | 16:19 | 16:19 | 18:00 | 0 | 1.6833 | 1.6833 | Test charged taken charged successfully | Close | 0.34432 | IG Breakdown Maintenance |  | 949
425 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:00 | 18:00 | 18:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 47
426 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:00 | 18:00 | 18:16 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Breakdown Maintenance |  | 37
427 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:00 | 18:00 | 18:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 47
428 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:00 | 18:00 | 18:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 47
429 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-42 | PWEPL | MSEDCL | 2.273% | PWEPL-46 R Phase LA failure | 18:00 | 18:00 | 18:33 | 0 | 0.55 | 0.55 | LA replaced | Close | 0.0125 | IG Breakdown Maintenance |  | 723
430 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:33 | 18:33 | 18:53 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 99
431 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-45 | PWEPL | MSEDCL | 2.273% | PWEPL-46 R Phase LA failure | 18:00 | 18:00 | 18:33 | 0 | 0.55 | 0.55 | LA replaced | Close | 0.0125 | IG Breakdown Maintenance |  | 738
432 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:33 | 18:33 | 18:50 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Breakdown Maintenance |  | 84
433 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-46 | PWEPL | MSEDCL | 2.273% | PWEPL-46 R Phase LA failure | 18:00 | 18:00 | 18:33 | 0 | 0.55 | 0.55 | LA replaced | Close | 0.0125 | IG Breakdown Maintenance |  | 723
434 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:33 | 18:33 | 18:53 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 99
435 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-47 | PWEPL | MSEDCL | 2.273% | PWEPL-46 R Phase LA failure | 18:00 | 18:00 | 18:33 | 0 | 0.55 | 0.55 | LA replaced | Close | 0.0125 | IG Breakdown Maintenance |  | 723
436 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:33 | 18:33 | 18:53 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 99
437 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-48 | PWEPL | MSEDCL | 2.273% | PWEPL-46 R Phase LA failure | 18:00 | 18:00 | 18:33 | 0 | 0.55 | 0.55 | LA replaced | Close | 0.0125 | IG Breakdown Maintenance |  | 723
438 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:33 | 18:33 | 18:53 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 99
439 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-42 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 18:53 | 18:53 | 19:48 | 0 | 0.91667 | 0.91667 | VCB reset & Charge | Close | 0.020833 | IG Breakdown Maintenance |  | 325
440 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-12 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:48 | 19:48 | 20:05 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Breakdown Maintenance |  | 144
441 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-05 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 12:29 | 12:29 | 13:32 | 0 | 1.05 | 1.05 | CT,PT cabling & tray Installation work | Close | 0.023864 | IG Unscheduled Maintenance |  | 97
442 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-06 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 12:29 | 12:29 | 13:32 | 0 | 1.05 | 1.05 | CT,PT cabling & tray Installation work | Close | 0.023864 | IG Unscheduled Maintenance |  | 97
443 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-40 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 12:29 | 12:29 | 13:32 | 0 | 1.05 | 1.05 | CT,PT cabling & tray Installation work | Close | 0.023864 | IG Unscheduled Maintenance |  | 97
444 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-41 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 12:29 | 12:29 | 13:32 | 0 | 1.05 | 1.05 | CT,PT cabling & tray Installation work | Close | 0.023864 | IG Unscheduled Maintenance |  | 97
445 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | Wind_F3 | PWEPL | MSEDCL | 20.45% | Feeder tripped by O/C | 13:32 | 13:32 | 14:01 | 0 | 0.48333 | 0.48333 | Test charged taken charged successfully | Close | 0.098864 | IG Breakdown Maintenance |  | 438
446 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Breakdown Maintenance |  | 25
447 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Breakdown Maintenance |  | 25
448 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Breakdown Maintenance |  | 25
449 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Breakdown Maintenance |  | 25
450 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Breakdown Maintenance |  | 25
451 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-05 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | CT,PT cabling & tray Installation work | Close | 0.0056818 | IG Unscheduled Maintenance |  | 23
452 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-06 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | CT,PT cabling & tray Installation work | Close | 0.0056818 | IG Unscheduled Maintenance |  | 23
453 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-40 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | CT,PT cabling & tray Installation work | Close | 0.0056818 | IG Unscheduled Maintenance |  | 23
454 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-41 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 14:01 | 14:01 | 14:16 | 0 | 0.25 | 0.25 | CT,PT cabling & tray Installation work | Close | 0.0056818 | IG Unscheduled Maintenance |  | 23
455 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | Wind_F3 | PWEPL | MSEDCL | 20.45% | Feeder tripped by O/C | 14:16 | 14:16 | 15:13 | 0 | 0.95 | 0.95 | Test charged taken charged successfully | Close | 0.19432 | IG Breakdown Maintenance |  | 952
456 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-42 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 15:13 | 15:13 | 15:31 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 60
457 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-45 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 15:13 | 15:13 | 15:31 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 60
458 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-46 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 15:13 | 15:13 | 15:21 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 33
459 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-47 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 15:13 | 15:13 | 15:33 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 66
460 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-48 | PWEPL | MSEDCL | 2.273% | Internal grid shutdown for SEM activity | 15:13 | 15:13 | 15:31 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 60
461 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-05 | PWEPL | MSEDCL | 2.273% | CP-49 B-Phase Pin insulator failure | 15:13 | 15:13 | 17:53 | 0 | 2.6667 | 2.6667 | Pin Insulator replaced | Close | 0.060606 | IG Breakdown Maintenance |  | 1443
462 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:53 | 17:53 | 18:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 46
463 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-06 | PWEPL | MSEDCL | 2.273% | CP-50 R-Phase Pin insulator failure | 15:13 | 15:13 | 17:53 | 0 | 2.6667 | 2.6667 | Pin Insulator replaced | Close | 0.060606 | IG Breakdown Maintenance |  | 1443
464 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:53 | 17:53 | 18:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 46
465 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-40 | PWEPL | MSEDCL | 2.273% | PP-43 R-Phase Pin insulator failure | 15:13 | 15:13 | 17:53 | 0 | 2.6667 | 2.6667 | Pin Insulator replaced | Close | 0.060606 | IG Breakdown Maintenance |  | 1443
466 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:53 | 17:53 | 18:13 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 46
467 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-41 | PWEPL | MSEDCL | 2.273% | PP-56 Y-Phase Pin insulator failure | 15:13 | 15:13 | 17:53 | 0 | 2.6667 | 2.6667 | Pin Insulator replaced | Close | 0.060606 | IG Breakdown Maintenance |  | 1445
468 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:53 | 17:53 | 18:12 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Breakdown Maintenance |  | 44
469 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 14:17 | 14:17 | 15:12 | 0 | 0.91667 | 0.91667 | Test charged taken charged successfully | Close | 0.27083 | IG Breakdown Maintenance |  | 3013
470 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:30 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 75
471 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:27 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Breakdown Maintenance |  | 63
472 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:30 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 75
473 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:30 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 75
474 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:30 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 75
475 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:29 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Breakdown Maintenance |  | 71
476 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:24 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | IG Breakdown Maintenance |  | 50
477 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:27 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Breakdown Maintenance |  | 63
478 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:26 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Breakdown Maintenance |  | 58
479 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:24 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | IG Breakdown Maintenance |  | 50
480 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:26 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Breakdown Maintenance |  | 58
481 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:32 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 84
482 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-14 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:12 | 15:12 | 15:31 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Breakdown Maintenance |  | 80
483 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | Wind_F3 | PWEPL | MSEDCL | 20.45% | S/D for External line tree trimming work | 8:28 | 8:28 | 15:19 | 0 | 6.85 | 6.85 | Tree trimming work done | Close | 1.4011 | IG Unscheduled Maintenance |  | 1376
484 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:34 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Unscheduled Maintenance |  | 5
485 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:34 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Unscheduled Maintenance |  | 5
486 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:33 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Unscheduled Maintenance |  | 5
487 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:34 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Unscheduled Maintenance |  | 5
488 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:33 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Unscheduled Maintenance |  | 5
489 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:33 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Unscheduled Maintenance |  | 5
490 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:29 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 3.7
491 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:28 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | IG Unscheduled Maintenance |  | 3.3
492 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:38 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Unscheduled Maintenance |  | 7
493 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | Wind_F4 | PWEPL | MSEDCL | 29.55% | S/D for External line tree trimming work | 8:28 | 8:28 | 15:19 | 0 | 6.85 | 6.85 | Tree trimming work done | Close | 2.0239 | IG Unscheduled Maintenance |  | 2249
494 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:33 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Unscheduled Maintenance |  | 5.9
495 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:29 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 4
496 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:33 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Unscheduled Maintenance |  | 5.9
497 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:33 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Unscheduled Maintenance |  | 5.9
498 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:39 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 8
499 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:28 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | IG Unscheduled Maintenance |  | 3.8
500 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:34 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Unscheduled Maintenance |  | 6
501 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:39 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 8
502 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:36 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Unscheduled Maintenance |  | 7
503 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:32 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Unscheduled Maintenance |  | 5.4
504 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:32 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Unscheduled Maintenance |  | 5.4
505 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:39 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 8
506 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-15 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:19 | 15:19 | 15:20 | 0 | 0.016667 | 0.016667 | Rebooted the PLC & reset at scada | Close | 0.00037879 | IG Unscheduled Maintenance |  | 0.4
507 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | Wind_F1 | PWEPL | MSEDCL | 22.73% | S/D for FDR 3 & 4 TP-02 R,Y,B Phase Jump & Pam connector replacement work | 9:55 | 9:55 | 15:39 | 0 | 5.7333 | 5.7333 | Jump & Pam connector replacement work done | Close | 1.303 | IG Unscheduled Maintenance |  | 102
508 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:47 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Unscheduled Maintenance |  | 0.2
509 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:44 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | IG Unscheduled Maintenance |  | 0.1
510 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:47 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Unscheduled Maintenance |  | 0.2
511 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | IG Unscheduled Maintenance |  | 0.2
512 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:49 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 0.3
513 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | IG Unscheduled Maintenance |  | 0.2
514 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:59 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 0.6
515 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:59 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 0.6
516 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:59 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 0.6
517 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:59 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 0.6
518 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | Wind_F2 | PWEPL | MSEDCL | 27.27% | S/D for FDR 3 & 4 TP-02 R,Y,B Phase Jump & Pam connector replacement work | 9:55 | 9:55 | 15:39 | 0 | 5.7333 | 5.7333 | Jump & Pam connector replacement work done | Close | 1.5636 | IG Unscheduled Maintenance |  | 133
519 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | IG Unscheduled Maintenance |  | 0.2
520 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | IG Unscheduled Maintenance |  | 0.2
521 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | IG Unscheduled Maintenance |  | 0.2
522 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | IG Unscheduled Maintenance |  | 0.2
523 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:48 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | IG Unscheduled Maintenance |  | 0.3
524 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | IG Unscheduled Maintenance |  | 0.2
525 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:46 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | IG Unscheduled Maintenance |  | 0.2
526 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:58 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Unscheduled Maintenance |  | 0.6
527 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-22 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:58 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Unscheduled Maintenance |  | 0.6
528 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:58 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Unscheduled Maintenance |  | 0.6
529 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:58 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Unscheduled Maintenance |  | 0.6
530 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:39 | 15:39 | 15:58 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Unscheduled Maintenance |  | 0.6
531 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | Wind_F3 | PWEPL | MSEDCL | 20.45% | S/D for FDR 3 & 4 TP-02 R,Y,B Phase Jump & Pam connector replacement work | 9:50 | 9:50 | 15:50 | 0 | 6 | 6 | Jump & Pam connector replacement work done | Close | 1.2273 | IG Unscheduled Maintenance |  | 144
532 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:02 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | IG Unscheduled Maintenance |  | 0.5
533 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:08 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Unscheduled Maintenance |  | 0.8
534 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:07 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Unscheduled Maintenance |  | 0.7
535 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:00 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 0.4
536 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:07 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Unscheduled Maintenance |  | 0.7
537 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:07 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Unscheduled Maintenance |  | 0.7
538 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:07 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Unscheduled Maintenance |  | 0.7
539 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 0.9
540 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:07 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Unscheduled Maintenance |  | 0.7
541 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | Wind_F4 | PWEPL | MSEDCL | 29.55% | S/D for FDR 3 & 4 TP-02 R,Y,B Phase Jump & Pam connector replacement work | 9:50 | 9:50 | 15:50 | 0 | 6 | 6 | Jump & Pam connector replacement work done | Close | 1.7727 | IG Unscheduled Maintenance |  | 151
542 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:05 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Unscheduled Maintenance |  | 0.5
543 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 15:51 | 0 | 0.016667 | 0.016667 | Rebooted the PLC & reset at scada | Close | 0.00037879 | IG Unscheduled Maintenance |  | 0
544 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:04 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Unscheduled Maintenance |  | 0.45
545 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:04 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Unscheduled Maintenance |  | 0.45
546 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:00 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 0.3
547 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:04 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Unscheduled Maintenance |  | 0.45
548 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:01 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | IG Unscheduled Maintenance |  | 0.35
549 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:04 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Unscheduled Maintenance |  | 0.45
550 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:00 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 0.3
551 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:00 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 0.3
552 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:00 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 0.3
553 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:03 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Unscheduled Maintenance |  | 0.4
554 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-16 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:00 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 0.3
555 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | P-12 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel B Phase O/C Relay replacement work | 11:50 | 11:50 | 12:09 | 0 | 0.31667 | 0.31667 | Relay replacement work done | Close | 0.007197 | IG Unscheduled Maintenance |  | 48
556 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:09 | 12:09 | 12:19 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 52
557 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | P-14 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel Y & B Phase O/C Relay replacement work | 12:32 | 12:32 | 12:50 | 0 | 0.3 | 0.3 | Relay replacement work done | Close | 0.0068182 | IG Unscheduled Maintenance |  | 8.55
558 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:50 | 12:50 | 12:54 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | IG Unscheduled Maintenance |  | 2.44
559 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | P-13 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel Y & B Phase O/C Relay & Ammeter replacement work | 14:19 | 14:19 | 14:46 | 0 | 0.45 | 0.45 | Relay replacement work done | Close | 0.010227 | IG Unscheduled Maintenance |  | 173
560 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-17 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:46 | 14:46 | 15:04 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Unscheduled Maintenance |  | 87
561 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | Wind_F1 | PWEPL | MSEDCL | 22.73% | S/D for External line tree trimming work | 10:00 | 10:00 | 15:50 | 0 | 5.8333 | 5.8333 | Tree trimming work done | Close | 1.3258 | IG Unscheduled Maintenance |  | 1816
562 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 10
563 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 10
564 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 10
565 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 10
566 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 10
567 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 10
568 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 10
569 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 10
570 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 10
571 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 10
572 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | Wind_F2 | PWEPL | MSEDCL | 27.27% | S/D for External line tree trimming work | 10:00 | 10:00 | 15:50 | 0 | 5.8333 | 5.8333 | Tree trimming work done | Close | 1.5909 | IG Unscheduled Maintenance |  | 2315
573 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 11
574 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 11
575 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 11
576 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 11
577 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 11
578 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 11
579 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 11
580 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 11
581 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-22 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 11
582 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 11
583 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 11
584 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-18 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 11
585 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | Wind_F3 | PWEPL | MSEDCL | 20.45% | Feeder tripped by E/F | 6:42 | 6:42 | 7:57 | 0 | 1.25 | 1.25 | Test charged taken charged successfully | Close | 0.25568 | IG Breakdown Maintenance |  | 900
586 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-42 | PWEPL | MSEDCL | 2.273% | PWEPL-48 B phase LA failure | 7:57 | 7:57 | 8:10 | 0 | 0.21667 | 0.21667 | LA replaced | Close | 0.0049242 | IG Breakdown Maintenance |  | 15
587 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:10 | 8:10 | 8:30 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
588 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-45 | PWEPL | MSEDCL | 2.273% | PWEPL-48 B phase LA failure | 7:57 | 7:57 | 8:10 | 0 | 0.21667 | 0.21667 | LA replaced | Close | 0.0049242 | IG Breakdown Maintenance |  | 15
589 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:10 | 8:10 | 8:30 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
590 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-46 | PWEPL | MSEDCL | 2.273% | PWEPL-48 B phase LA failure | 7:57 | 7:57 | 8:10 | 0 | 0.21667 | 0.21667 | LA replaced | Close | 0.0049242 | IG Breakdown Maintenance |  | 15
591 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:10 | 8:10 | 8:30 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
592 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-47 | PWEPL | MSEDCL | 2.273% | PWEPL-48 B phase LA failure | 7:57 | 7:57 | 8:10 | 0 | 0.21667 | 0.21667 | LA replaced | Close | 0.0049242 | IG Breakdown Maintenance |  | 15
593 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:10 | 8:10 | 8:30 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
594 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-48 | PWEPL | MSEDCL | 2.273% | PWEPL-48 B phase LA failure | 7:57 | 7:57 | 8:10 | 0 | 0.21667 | 0.21667 | LA replaced | Close | 0.0049242 | IG Breakdown Maintenance |  | 15
595 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 8:10 | 8:10 | 8:30 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
596 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 7:57 | 7:57 | 8:17 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
597 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 7:57 | 7:57 | 8:17 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
598 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 7:57 | 7:57 | 8:17 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
599 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 7:57 | 7:57 | 8:17 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
600 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 8:27 | 8:27 | 9:07 | 0 | 0.66667 | 0.66667 | Test charged taken charged successfully | Close | 0.19697 | IG Breakdown Maintenance |  | 780
601 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:07 | 9:07 | 9:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
602 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:07 | 9:07 | 9:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
603 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:07 | 9:07 | 9:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
604 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:07 | 9:07 | 9:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
605 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:07 | 9:07 | 9:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
606 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:07 | 9:07 | 9:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
607 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:07 | 9:07 | 9:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
608 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:07 | 9:07 | 9:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
609 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:07 | 9:07 | 9:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
610 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:07 | 9:07 | 9:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
611 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:07 | 9:07 | 9:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
612 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:07 | 9:07 | 9:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
613 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:07 | 9:07 | 9:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 15
614 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-04 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel Y Phase O/C Relay replacement work | 11:55 | 11:55 | 12:04 | 0 | 0.15 | 0.15 | Relay replacement work done | Close | 0.0034091 | IG Unscheduled Maintenance |  | 0
615 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:04 | 12:04 | 12:24 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 0
616 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-23 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel R & Y Phase O/C Relay replacement work | 12:17 | 12:17 | 12:31 | 0 | 0.23333 | 0.23333 | Relay replacement work done | Close | 0.005303 | IG Unscheduled Maintenance |  | 0
617 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:31 | 12:31 | 12:51 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 0
618 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-43 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel B Phase O/C Relay replacement work | 12:52 | 12:52 | 13:01 | 0 | 0.15 | 0.15 | Relay replacement work done | Close | 0.0034091 | IG Unscheduled Maintenance |  | 0
619 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:01 | 13:01 | 13:21 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 0
620 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-52 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel R & Y Phase O/C Relay replacement work | 13:34 | 13:34 | 13:49 | 0 | 0.25 | 0.25 | Relay replacement work done | Close | 0.0056818 | IG Unscheduled Maintenance |  | 0
621 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:49 | 13:49 | 14:09 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 0
622 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-02 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel B Phase O/C Relay replacement work | 15:14 | 15:14 | 15:26 | 0 | 0.2 | 0.2 | Relay replacement work done | Close | 0.0045455 | IG Unscheduled Maintenance |  | 0
623 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-19 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:26 | 15:26 | 15:46 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 0
624 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | Wind_F1 | PWEPL | MSEDCL | 22.73% | S/D for External line tree trimming work | 8:50 | 8:50 | 17:08 | 0 | 8.3 | 8.3 | Tree trimming work done | Close | 1.8864 | IG Unscheduled Maintenance |  | 557
625 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:08 | 17:08 | 17:28 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 22
626 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:08 | 17:08 | 17:28 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 22
627 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:08 | 17:08 | 17:28 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 22
628 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:08 | 17:08 | 17:28 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 22
629 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:08 | 17:08 | 17:28 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 22
630 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:08 | 17:08 | 17:28 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 22
631 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:08 | 17:08 | 17:28 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 22
632 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:08 | 17:08 | 17:28 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 22
633 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:08 | 17:08 | 17:28 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 22
634 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:08 | 17:08 | 17:28 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 22
635 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | Wind_F2 | PWEPL | MSEDCL | 27.27% | S/D for External line tree trimming work | 8:50 | 8:50 | 17:21 | 0 | 8.5167 | 8.5167 | Tree trimming work done | Close | 2.3227 | IG Unscheduled Maintenance |  | 7609
636 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:21 | 17:21 | 17:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
637 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:21 | 17:21 | 17:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
638 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:21 | 17:21 | 17:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
639 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:21 | 17:21 | 17:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
640 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:21 | 17:21 | 17:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
641 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:21 | 17:21 | 17:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
642 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:21 | 17:21 | 17:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
643 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:21 | 17:21 | 17:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
644 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-22 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:21 | 17:21 | 17:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
645 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:21 | 17:21 | 17:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
646 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:21 | 17:21 | 17:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
647 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-20 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 17:21 | 17:21 | 17:41 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 24
648 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-32 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel R & B Phase O/C Relay replacement work | 11:47 | 11:47 | 12:00 | 0 | 0.21667 | 0.21667 | Relay replacement work done | Close | 0.0049242 | IG Unscheduled Maintenance |  | 69
649 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:00 | 12:00 | 12:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 94
650 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-37 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel R Phase O/C Relay replacement work | 12:21 | 12:21 | 12:31 | 0 | 0.16667 | 0.16667 | Relay replacement work done | Close | 0.0037879 | IG Unscheduled Maintenance |  | 6
651 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:31 | 12:31 | 12:51 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 47
652 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-25 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel R & Y Phase O/C Relay replacement work | 15:26 | 15:26 | 15:50 | 0 | 0.4 | 0.4 | Relay replacement work done | Close | 0.0090909 | IG Unscheduled Maintenance |  | 152
653 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:50 | 15:50 | 16:10 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 21
654 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-27 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel R Phase O/C Relay replacement work | 13:57 | 13:57 | 14:27 | 0 | 0.5 | 0.5 | Relay replacement work done | Close | 0.011364 | IG Unscheduled Maintenance |  | 369
655 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:27 | 14:27 | 14:47 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 60
656 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 21:51 | 21:51 | 22:11 | 0 | 0.33333 | 0.33333 | Test charged taken charged successfully | Close | 0.098485 | IG Breakdown Maintenance |  | 938
657 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:11 | 22:11 | 22:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 72
658 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:11 | 22:11 | 22:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 72
659 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:11 | 22:11 | 22:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 72
660 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:11 | 22:11 | 22:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 72
661 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:11 | 22:11 | 22:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 72
662 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:11 | 22:11 | 22:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 72
663 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:11 | 22:11 | 22:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 72
664 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:11 | 22:11 | 22:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 72
665 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:11 | 22:11 | 22:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 72
666 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:11 | 22:11 | 22:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 72
667 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:11 | 22:11 | 22:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 72
668 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:11 | 22:11 | 22:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 72
669 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-22 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:11 | 22:11 | 22:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 72
670 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 1:24 | 1:24 | 1:44 | 0 | 0.33333 | 0.33333 | Test charged taken charged successfully | Close | 0.098485 | IG Breakdown Maintenance |  | 1248
671 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:44 | 1:44 | 1:52 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 96
672 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:44 | 1:44 | 1:52 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 96
673 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:44 | 1:44 | 1:52 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 96
674 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:44 | 1:44 | 1:52 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 96
675 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:44 | 1:44 | 1:52 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 96
676 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:44 | 1:44 | 1:52 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 96
677 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:44 | 1:44 | 1:52 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 96
678 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:44 | 1:44 | 1:52 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 96
679 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:44 | 1:44 | 1:52 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 96
680 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:44 | 1:44 | 1:52 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 96
681 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:44 | 1:44 | 1:52 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 96
682 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:44 | 1:44 | 1:52 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 96
683 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:44 | 1:44 | 1:52 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 96
684 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 1:52 | 1:52 | 4:55 | 0 | 3.05 | 3.05 | External line cp 186 R phase pin insulator replaced & charge | Close | 0.90114 | IG Breakdown Maintenance |  | 18067
685 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:55 | 4:55 | 5:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 150
686 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:55 | 4:55 | 5:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 150
687 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:55 | 4:55 | 5:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 150
688 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:55 | 4:55 | 5:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 150
689 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:55 | 4:55 | 5:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 150
690 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:55 | 4:55 | 5:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 150
691 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:55 | 4:55 | 5:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 150
692 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:55 | 4:55 | 5:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 150
693 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:55 | 4:55 | 5:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 150
694 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:55 | 4:55 | 5:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 150
695 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:55 | 4:55 | 5:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 150
696 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:55 | 4:55 | 5:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 150
697 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:55 | 4:55 | 5:15 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 150
698 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-05 | PWEPL | MSEDCL | 2.273% | S/D for CRP Panel R Phase O/C Relay replacement work | 11:39 | 11:39 | 11:52 | 0 | 0.21667 | 0.21667 | Relay replacement work done | Close | 0.0049242 | IG Breakdown Maintenance |  | 219
699 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-23 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 11:52 | 11:52 | 12:12 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 34
700 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 2:37 | 2:37 | 3:47 | 0 | 1.1667 | 1.1667 | PWEPL-61 SEM B Phase PT failed | Close | 0.3447 | IG Breakdown Maintenance |  | 899
701 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 3:47 | 3:47 | 4:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 20
702 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 3:47 | 3:47 | 4:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 20
703 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 3:47 | 3:47 | 4:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 20
704 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 3:47 | 3:47 | 4:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 20
705 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 3:47 | 3:47 | 4:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 20
706 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 3:47 | 3:47 | 4:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 20
707 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 3:47 | 3:47 | 4:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 20
708 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 3:47 | 3:47 | 4:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 20
709 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 3:47 | 3:47 | 4:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 20
710 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 3:47 | 3:47 | 4:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 20
711 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 3:47 | 3:47 | 4:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 20
712 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 3:47 | 3:47 | 4:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 20
713 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-25 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 3:47 | 3:47 | 4:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 20
714 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 5:49 | 5:49 | 6:17 | 0 | 0.46667 | 0.46667 | Test charged taken charged successfully | Close | 0.13788 | IG Breakdown Maintenance |  | 3324
715 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:17 | 6:17 | 6:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 183
716 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:17 | 6:17 | 6:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 183
717 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:17 | 6:17 | 6:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 183
718 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:17 | 6:17 | 6:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 183
719 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:17 | 6:17 | 6:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 183
720 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:17 | 6:17 | 6:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 183
721 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:17 | 6:17 | 6:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 183
722 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:17 | 6:17 | 6:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 183
723 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:17 | 6:17 | 6:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 183
724 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:17 | 6:17 | 6:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 183
725 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:17 | 6:17 | 6:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 183
726 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:17 | 6:17 | 6:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 183
727 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:17 | 6:17 | 6:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 183
728 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 9:47 | 9:47 | 10:15 | 0 | 0.46667 | 0.46667 | Test charged taken charged successfully | Close | 0.13788 | IG Breakdown Maintenance |  | 8936
729 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:15 | 10:15 | 10:35 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 491
730 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:15 | 10:15 | 10:35 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 491
731 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:15 | 10:15 | 10:35 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 491
732 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:15 | 10:15 | 10:35 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 491
733 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:15 | 10:15 | 10:35 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 491
734 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:15 | 10:15 | 10:35 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 491
735 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:15 | 10:15 | 10:35 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 491
736 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:15 | 10:15 | 10:35 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 491
737 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:15 | 10:15 | 10:35 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 491
738 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:15 | 10:15 | 10:35 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 491
739 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:15 | 10:15 | 10:35 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 491
740 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:15 | 10:15 | 10:35 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 491
741 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:15 | 10:15 | 10:35 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 491
742 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 18:14 | 18:14 | 18:26 | 0 | 0.2 | 0.2 | Test charged taken charged successfully | Close | 0.059091 | IG Breakdown Maintenance |  | 1953
743 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:26 | 18:26 | 18:46 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 250
744 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:26 | 18:26 | 18:46 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 250
745 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:26 | 18:26 | 18:46 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 250
746 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:26 | 18:26 | 18:46 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 250
747 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:26 | 18:26 | 18:46 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 250
748 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:26 | 18:26 | 18:46 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 250
749 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:26 | 18:26 | 18:46 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 250
750 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:26 | 18:26 | 18:46 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 250
751 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:26 | 18:26 | 18:46 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 250
752 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:26 | 18:26 | 18:46 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 250
753 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:26 | 18:26 | 18:46 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 250
754 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:26 | 18:26 | 18:46 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 250
755 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-26 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:26 | 18:26 | 18:46 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 250
756 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | Wind_F3 | PWEPL | MSEDCL | 20.45% | Feeder tripped by O/C | 17:21 | 17:21 | 21:40 | 0 | 4.3167 | 4.3167 | CKT-2 ,PP-43 B phase pin insulator replaced | Close | 0.88295 | IG Breakdown Maintenance |  | 16932
757 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:40 | 21:40 | 22:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 156
758 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:40 | 21:40 | 22:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 156
759 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:40 | 21:40 | 22:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 156
760 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:40 | 21:40 | 22:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 156
761 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:40 | 21:40 | 22:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 156
762 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:40 | 21:40 | 22:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 156
763 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:40 | 21:40 | 22:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 156
764 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:40 | 21:40 | 22:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 156
765 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-28 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 21:40 | 21:40 | 22:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 156
766 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-30 | P-46 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 17:44 | 17:44 | 18:25 | 0 | 0.68333 | 0.68333 | VCB reset & Charge | Close | 0.01553 | IG Breakdown Maintenance |  | 741
767 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-30 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:25 | 18:25 | 18:45 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 740
768 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | P-46 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 8:53 | 8:53 | 9:25 | 0 | 0.53333 | 0.53333 | VCB reset & Charge | Close | 0.012121 | IG Breakdown Maintenance |  | 805
769 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-31 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:25 | 9:25 | 9:38 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Breakdown Maintenance |  | 550
770 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | Wind_F1 | PWEPL | MSEDCL | 22.73% | Feeder tripped by O/C | 23:14 | 23:14 | 23:24 | 0 | 0.16667 | 0.16667 | Test charged taken charged successfully | Close | 0.037879 | IG Breakdown Maintenance |  | 1200
771 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:28 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | IG Breakdown Maintenance |  | 48
772 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:36 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | IG Breakdown Maintenance |  | 144
773 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:35 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | IG Breakdown Maintenance |  | 132
774 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:39 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Breakdown Maintenance |  | 180
775 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | P-13 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:35 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | IG Breakdown Maintenance |  | 132
776 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | P-08 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:30 | 0 | 0.1 | 0.1 | Rebooted the PLC & reset at scada | Close | 0.0022727 | IG Breakdown Maintenance |  | 72
777 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | P-25 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:29 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | IG Breakdown Maintenance |  | 60
778 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | P-26 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:59 | 0 | 0.58333 | 0.58333 | Rebooted the PLC & reset at scada | Close | 0.013258 | IG Breakdown Maintenance |  | 60
779 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | P-27 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:30 | 0 | 0.1 | 0.1 | Rebooted the PLC & reset at scada | Close | 0.0022727 | IG Breakdown Maintenance |  | 72
780 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | P-28 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:24 | 23:24 | 23:44 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 240
781 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | P-46 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 19:00 | 19:00 | 20:00 | 0 | 1 | 1 | VCB reset & Charge | Close | 0.022727 | IG Breakdown Maintenance |  | 966
782 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-02 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:00 | 20:00 | 20:20 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 482
783 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-03 | P-10 | PWEPL | MSEDCL | 2.273% | S/D for SEM B Phase CT replacement work | 13:39 | 13:39 | 14:30 | 0 | 0.85 | 0.85 | CT replacement work done | Close | 0.019318 | IG Unscheduled Maintenance |  | 641
784 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-03 | P-10 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 14:30 | 14:30 | 14:50 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 412
785 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-03 | P-09 | PWEPL | MSEDCL | 2.273% | S/D for SEM Y Phase PT replacement work | 14:40 | 14:40 | 15:31 | 0 | 0.85 | 0.85 | PT replacement work done | Close | 0.019318 | IG Unscheduled Maintenance |  | 381
786 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-03 | P-09 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:31 | 15:31 | 15:47 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Unscheduled Maintenance |  | 174
787 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | P-11 | PWEPL | MSEDCL | 2.273% | S/D for SEM Y Phase CT replacement work | 11:57 | 11:57 | 13:24 | 0 | 1.45 | 1.45 | CT replacement work done | Close | 0.032955 | IG Unscheduled Maintenance |  | 172
788 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-04 | P-11 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:24 | 13:24 | 13:39 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Unscheduled Maintenance |  | 35
789 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | P-01 | PWEPL | MSEDCL | 2.273% | S/D for SEM Y Phase PT replacement work | 11:20 | 11:20 | 12:11 | 0 | 0.85 | 0.85 | PT replacement work done | Close | 0.019318 | IG Unscheduled Maintenance |  | 83
790 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:11 | 12:11 | 12:18 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | IG Unscheduled Maintenance |  | 15
791 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | P-06 | PWEPL | MSEDCL | 2.273% | S/D for SEM R Phase PT replacement work | 12:33 | 12:33 | 13:09 | 0 | 0.6 | 0.6 | PT replacement work done | Close | 0.013636 | IG Unscheduled Maintenance |  | 219
792 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:09 | 13:09 | 13:19 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Unscheduled Maintenance |  | 83
793 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | Wind_F3 | PWEPL | MSEDCL | 20.45% | Feeder tripped by O/C | 16:39 | 16:39 | 16:57 | 0 | 0.3 | 0.3 | Test charged taken charged successfully | Close | 0.061364 | IG Breakdown Maintenance |  | 1647
794 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:11 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Breakdown Maintenance |  | 142
795 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:11 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Breakdown Maintenance |  | 142
796 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | P-46 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:09 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | IG Breakdown Maintenance |  | 122
797 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | P-47 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:09 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | IG Breakdown Maintenance |  | 122
798 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | P-48 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:10 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Breakdown Maintenance |  | 132
799 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:09 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | IG Breakdown Maintenance |  | 122
800 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | P-06 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:13 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Breakdown Maintenance |  | 162
801 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | P-40 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:12 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Breakdown Maintenance |  | 152
802 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-05 | P-41 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:57 | 16:57 | 17:16 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Breakdown Maintenance |  | 193
803 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 17:37 | 17:37 | 18:40 | 0 | 1.05 | 1.05 | Test charged taken charged successfully | Close | 0.31023 | IG Breakdown Maintenance |  | 23181
804 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:40 | 18:40 | 19:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 445
805 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:40 | 18:40 | 19:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 445
806 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:40 | 18:40 | 19:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 445
807 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:40 | 18:40 | 19:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 445
808 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:40 | 18:40 | 19:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 445
809 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:40 | 18:40 | 19:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 445
810 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:40 | 18:40 | 18:50 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Breakdown Maintenance |  | 445
811 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:40 | 18:40 | 19:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 445
812 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:40 | 18:40 | 19:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 445
813 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:40 | 18:40 | 19:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 445
814 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:40 | 18:40 | 19:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 445
815 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:40 | 18:40 | 19:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 445
816 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:40 | 18:40 | 19:00 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 445
817 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 19:55 | 19:55 | 20:35 | 0 | 0.66667 | 0.66667 | Test charged taken charged successfully | Close | 0.19697 | IG Breakdown Maintenance |  | 14837
818 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:35 | 20:35 | 20:48 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Breakdown Maintenance |  | 431
819 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:35 | 20:35 | 20:43 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 265
820 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:35 | 20:35 | 20:47 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | IG Breakdown Maintenance |  | 398
821 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:35 | 20:35 | 20:45 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Breakdown Maintenance |  | 331
822 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:35 | 20:35 | 20:45 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Breakdown Maintenance |  | 331
823 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:35 | 20:35 | 20:48 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Breakdown Maintenance |  | 398
824 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 20:35 | 20:35 | 20:46 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | IG Breakdown Maintenance |  | 364
825 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-32 | PWEPL | MSEDCL | 2.273% | After complete line petrolling & CKT will restored | 20:35 | 20:35 | 22:07 | 0 | 1.5333 | 1.5333 | Rebooted the PLC & reset at scada | Close | 0.034848 | IG Breakdown Maintenance |  | 1034
826 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:07 | 22:07 | 22:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 517
827 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-37 | PWEPL | MSEDCL | 2.273% | After complete line petrolling & CKT will restored | 20:35 | 20:35 | 22:07 | 0 | 1.5333 | 1.5333 | Rebooted the PLC & reset at scada | Close | 0.034848 | IG Breakdown Maintenance |  | 1034
828 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:07 | 22:07 | 22:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 517
829 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-50 | PWEPL | MSEDCL | 2.273% | After complete line petrolling & CKT will restored | 20:35 | 20:35 | 22:07 | 0 | 1.5333 | 1.5333 | Rebooted the PLC & reset at scada | Close | 0.034848 | IG Breakdown Maintenance |  | 1034
830 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:07 | 22:07 | 22:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 517
831 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-51 | PWEPL | MSEDCL | 2.273% | After complete line petrolling & CKT will restored | 20:35 | 20:35 | 22:07 | 0 | 1.5333 | 1.5333 | Rebooted the PLC & reset at scada | Close | 0.034848 | IG Breakdown Maintenance |  | 1034
832 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:07 | 22:07 | 22:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 517
833 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-52 | PWEPL | MSEDCL | 2.273% | After complete line petrolling & CKT will restored | 20:35 | 20:35 | 22:07 | 0 | 1.5333 | 1.5333 | Rebooted the PLC & reset at scada | Close | 0.034848 | IG Breakdown Maintenance |  | 1034
834 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:07 | 22:07 | 22:27 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 517
835 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-55 | PWEPL | MSEDCL | 2.273% | After complete line petrolling & CKT will restored | 20:35 | 20:35 | 22:07 | 0 | 1.5333 | 1.5333 | Rebooted the PLC & reset at scada | Close | 0.034848 | IG Breakdown Maintenance |  | 1034
836 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-32 | PWEPL | MSEDCL | 2.273% | S/D taken for 55 Y phase isolator jaw replacement work | 23:38 | 23:38 | 23:59 | 0 | 0.35 | 0.35 | work in progress | Close | 0.0079545 | IG Breakdown Maintenance |  | 659
837 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-37 | PWEPL | MSEDCL | 2.273% | S/D taken for 55 Y phase isolator jaw replacement work | 23:38 | 23:38 | 23:59 | 0 | 0.35 | 0.35 | work in progress | Close | 0.0079545 | IG Breakdown Maintenance |  | 659
838 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-50 | PWEPL | MSEDCL | 2.273% | S/D taken for 55 Y phase isolator jaw replacement work | 23:38 | 23:38 | 23:59 | 0 | 0.35 | 0.35 | work in progress | Close | 0.0079545 | IG Breakdown Maintenance |  | 659
839 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-51 | PWEPL | MSEDCL | 2.273% | S/D taken for 55 Y phase isolator jaw replacement work | 23:38 | 23:38 | 23:59 | 0 | 0.35 | 0.35 | work in progress | Close | 0.0079545 | IG Breakdown Maintenance |  | 659
840 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-52 | PWEPL | MSEDCL | 2.273% | S/D taken for 55 Y phase isolator jaw replacement work | 23:38 | 23:38 | 23:59 | 0 | 0.35 | 0.35 | work in progress | Close | 0.0079545 | IG Breakdown Maintenance |  | 659
841 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-17 | P-55 | PWEPL | MSEDCL | 2.273% | S/D taken for 55 Y phase isolator jaw replacement work | 22:07 | 22:07 | 23:59 | 0 | 1.8667 | 1.8667 | work in progress | Close | 0.042424 | IG Breakdown Maintenance |  | 2587
842 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-32 | PWEPL | MSEDCL | 2.273% | S/D taken for 55 Y phase isolator jaw replacement work | 0:00 | 0:00 | 0:18 | 0 | 0.3 | 0.3 | Jaw replacement work | Close | 0.0068182 | IG Breakdown Maintenance |  | 792
843 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:18 | 0:18 | 0:23 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | IG Breakdown Maintenance |  | 304
844 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-37 | PWEPL | MSEDCL | 2.273% | S/D taken for 55 Y phase isolator jaw replacement work | 0:00 | 0:00 | 0:18 | 0 | 0.3 | 0.3 | Jaw replacement work | Close | 0.0068182 | IG Breakdown Maintenance |  | 792
845 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:18 | 0:18 | 0:23 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | IG Breakdown Maintenance |  | 304
846 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-50 | PWEPL | MSEDCL | 2.273% | S/D taken for 55 Y phase isolator jaw replacement work | 0:00 | 0:00 | 0:18 | 0 | 0.3 | 0.3 | Jaw replacement work | Close | 0.0068182 | IG Breakdown Maintenance |  | 792
847 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:18 | 0:18 | 0:23 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | IG Breakdown Maintenance |  | 304
848 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-51 | PWEPL | MSEDCL | 2.273% | S/D taken for 55 Y phase isolator jaw replacement work | 0:00 | 0:00 | 0:18 | 0 | 0.3 | 0.3 | Jaw replacement work | Close | 0.0068182 | IG Breakdown Maintenance |  | 792
849 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:18 | 0:18 | 0:23 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | IG Breakdown Maintenance |  | 304
850 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-52 | PWEPL | MSEDCL | 2.273% | S/D taken for 55 Y phase isolator jaw replacement work | 0:00 | 0:00 | 0:18 | 0 | 0.3 | 0.3 | Jaw replacement work | Close | 0.0068182 | IG Breakdown Maintenance |  | 716
851 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:18 | 0:18 | 0:23 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | IG Breakdown Maintenance |  | 358
852 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-55 | PWEPL | MSEDCL | 2.273% | S/D taken for 55 Y phase isolator jaw replacement work | 0:00 | 0:00 | 0:18 | 0 | 0.3 | 0.3 | Jaw replacement work | Close | 0.0068182 | IG Breakdown Maintenance |  | 954
853 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:18 | 0:18 | 0:23 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | IG Breakdown Maintenance |  | 366
854 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 19:13 | 19:13 | 19:29 | 0 | 0.26667 | 0.26667 | Test charged taken charged successfully | Close | 0.078788 | IG Breakdown Maintenance |  | 7689
855 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:29 | 19:29 | 19:45 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Breakdown Maintenance |  | 591
856 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:29 | 19:29 | 19:45 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Breakdown Maintenance |  | 591
857 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:29 | 19:29 | 19:49 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 739
858 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:29 | 19:29 | 19:40 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | IG Breakdown Maintenance |  | 406
859 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:29 | 19:29 | 19:42 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Breakdown Maintenance |  | 480
860 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:29 | 19:29 | 19:49 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 739
861 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:29 | 19:29 | 19:49 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 739
862 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:29 | 19:29 | 19:39 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Breakdown Maintenance |  | 369
863 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:29 | 19:29 | 19:39 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Breakdown Maintenance |  | 369
864 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:29 | 19:29 | 19:39 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Breakdown Maintenance |  | 369
865 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:29 | 19:29 | 19:39 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Breakdown Maintenance |  | 369
866 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:29 | 19:29 | 19:38 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | IG Breakdown Maintenance |  | 332
867 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-18 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:29 | 19:29 | 19:49 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 369
868 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 3:49 | 3:49 | 4:11 | 0 | 0.36667 | 0.36667 | Test charged taken charged successfully | Close | 0.10833 | IG Breakdown Maintenance |  | 9109
869 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:11 | 4:11 | 4:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 637
870 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:11 | 4:11 | 4:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 637
871 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:11 | 4:11 | 4:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 637
872 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:11 | 4:11 | 4:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 637
873 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:11 | 4:11 | 4:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 637
874 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:11 | 4:11 | 4:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 637
875 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:11 | 4:11 | 4:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 637
876 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:11 | 4:11 | 4:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 637
877 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:11 | 4:11 | 4:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 637
878 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:11 | 4:11 | 4:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 637
879 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:11 | 4:11 | 4:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 637
880 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:11 | 4:11 | 4:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 637
881 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:11 | 4:11 | 4:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 637
882 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 4:54 | 4:54 | 5:17 | 0 | 0.38333 | 0.38333 | Test charged taken charged successfully | Close | 0.11326 | IG Breakdown Maintenance |  | 8563
883 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:17 | 5:17 | 5:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 716
884 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:17 | 5:17 | 5:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 716
885 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:17 | 5:17 | 5:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 716
886 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:17 | 5:17 | 5:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 716
887 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:17 | 5:17 | 5:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 716
888 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:17 | 5:17 | 5:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 716
889 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:17 | 5:17 | 5:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 716
890 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:17 | 5:17 | 5:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 716
891 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:17 | 5:17 | 5:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 716
892 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:17 | 5:17 | 5:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 716
893 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:17 | 5:17 | 5:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 716
894 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:17 | 5:17 | 5:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 716
895 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:17 | 5:17 | 5:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 716
896 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by E/F | 16:27 | 16:27 | 16:56 | 0 | 0.48333 | 0.48333 | Test charged taken charged successfully | Close | 0.1428 | IG Breakdown Maintenance |  | 9372
897 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:56 | 16:56 | 17:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 497
898 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:56 | 16:56 | 16:58 | 0 | 0.033333 | 0.033333 | Rebooted the PLC & reset at scada | Close | 0.00075758 | IG Breakdown Maintenance |  | 49
899 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:56 | 16:56 | 17:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 497
900 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:56 | 16:56 | 17:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 497
901 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:56 | 16:56 | 17:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 497
902 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:56 | 16:56 | 17:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 497
903 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:56 | 16:56 | 17:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 497
904 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:56 | 16:56 | 17:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 497
905 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:56 | 16:56 | 17:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 497
906 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:56 | 16:56 | 17:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 497
907 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:56 | 16:56 | 17:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 497
908 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:56 | 16:56 | 17:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 497
909 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:56 | 16:56 | 17:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 497
910 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-32 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 5:37 | 5:37 | 7:17 | 0 | 1.6667 | 1.6667 | VCB reset & Charge | Close | 0.037879 | IG Breakdown Maintenance |  | 0
911 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 7:17 | 7:17 | 7:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 0
912 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-52 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 5:37 | 5:37 | 7:17 | 0 | 1.6667 | 1.6667 | VCB reset & Charge | Close | 0.037879 | IG Breakdown Maintenance |  | 6723
913 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 7:17 | 7:17 | 7:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 1680
914 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-55 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 5:37 | 5:37 | 7:17 | 0 | 1.6667 | 1.6667 | VCB reset & Charge | Close | 0.037879 | IG Breakdown Maintenance |  | 759
915 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 7:17 | 7:17 | 7:37 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 189
916 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-23 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 3:49 | 3:49 | 4:50 | 0 | 1.0167 | 1.0167 | VCB reset & Charge | Close | 0.023106 | IG Breakdown Maintenance |  | 1721
917 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:50 | 4:50 | 4:55 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | IG Breakdown Maintenance |  | 153
918 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-12 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 4:54 | 4:54 | 5:33 | 0 | 0.65 | 0.65 | VCB reset & Charge | Close | 0.014773 | IG Breakdown Maintenance |  | 896
919 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:33 | 5:33 | 5:53 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 943
920 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-32 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 17:16 | 17:16 | 19:16 | 0 | 2 | 2 | VCB reset & Charge | Close | 0.045455 | IG Breakdown Maintenance |  | 1178
921 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:16 | 19:16 | 19:34 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 207
922 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-52 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 17:16 | 17:16 | 18:16 | 0 | 1 | 1 | VCB reset & Charge | Close | 0.022727 | IG Breakdown Maintenance |  | 101.65
923 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 18:16 | 18:16 | 18:21 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | IG Breakdown Maintenance |  | 5.35
924 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-55 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 17:16 | 17:16 | 19:16 | 0 | 2 | 2 | VCB reset & Charge | Close | 0.045455 | IG Breakdown Maintenance |  | 3400
925 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-19 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 19:16 | 19:16 | 19:27 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | IG Breakdown Maintenance |  | 343
926 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 1:39 | 1:39 | 1:47 | 0 | 0.13333 | 0.13333 | Test charged taken charged successfully | Close | 0.039394 | IG Breakdown Maintenance |  | 3504
927 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:47 | 1:47 | 2:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 674
928 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:47 | 1:47 | 2:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 674
929 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:47 | 1:47 | 2:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 674
930 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:47 | 1:47 | 2:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 674
931 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:47 | 1:47 | 2:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 674
932 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:47 | 1:47 | 2:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 674
933 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:47 | 1:47 | 2:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 674
934 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:47 | 1:47 | 2:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 674
935 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:47 | 1:47 | 2:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 674
936 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:47 | 1:47 | 2:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 674
937 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:47 | 1:47 | 2:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 674
938 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:47 | 1:47 | 2:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 674
939 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:47 | 1:47 | 2:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 674
940 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 2:29 | 2:29 | 2:56 | 0 | 0.45 | 0.45 | Test charged taken charged successfully | Close | 0.13295 | IG Breakdown Maintenance |  | 9577
941 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:56 | 2:56 | 3:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 591
942 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:56 | 2:56 | 3:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 591
943 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:56 | 2:56 | 3:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 591
944 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:56 | 2:56 | 3:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 591
945 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:56 | 2:56 | 3:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 591
946 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:56 | 2:56 | 3:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 591
947 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:56 | 2:56 | 3:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 591
948 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:56 | 2:56 | 3:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 591
949 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:56 | 2:56 | 3:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 591
950 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:56 | 2:56 | 3:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 591
951 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:56 | 2:56 | 3:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 591
952 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:56 | 2:56 | 3:16 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 591
953 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-32 | PWEPL | MSEDCL | 2.273% | Y Phase Protection PT bypass work | 2:56 | 2:56 | 4:20 | 0 | 1.4 | 1.4 | PT bypass work done | Close | 0.031818 | IG Breakdown Maintenance |  | 194
954 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:20 | 4:20 | 4:40 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 60
955 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-32 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 2:07 | 2:07 | 3:23 | 0 | 1.2667 | 1.2667 | VCB reset & Charge | Close | 0.028788 | IG Breakdown Maintenance |  | 0
956 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 3:23 | 3:23 | 3:43 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 0
957 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-52 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 2:07 | 2:07 | 3:23 | 0 | 1.2667 | 1.2667 | VCB reset & Charge | Close | 0.028788 | IG Breakdown Maintenance |  | 320
958 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 3:23 | 3:23 | 3:43 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 113
959 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-55 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 2:07 | 2:07 | 2:30 | 0 | 0.38333 | 0.38333 | VCB reset & Charge | Close | 0.0087121 | IG Breakdown Maintenance |  | 746
960 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 2:30 | 2:30 | 2:37 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | IG Breakdown Maintenance |  | 326
961 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-52 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 3:16 | 3:16 | 4:22 | 0 | 1.1 | 1.1 | VCB reset & Charge | Close | 0.025 | IG Breakdown Maintenance |  | 87
962 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 4:22 | 4:22 | 4:42 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 37
963 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 6:04 | 6:04 | 6:47 | 0 | 0.71667 | 0.71667 | Test charged taken charged successfully | Close | 0.21174 | IG Breakdown Maintenance |  | 13176
964 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:47 | 6:47 | 7:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 471
965 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:47 | 6:47 | 6:51 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | IG Breakdown Maintenance |  | 94
966 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:47 | 6:47 | 7:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 471
967 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:47 | 6:47 | 7:01 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Breakdown Maintenance |  | 330
968 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:47 | 6:47 | 7:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 471
969 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:47 | 6:47 | 7:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 471
970 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:47 | 6:47 | 7:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 471
971 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:47 | 6:47 | 7:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 471
972 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:47 | 6:47 | 7:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 471
973 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:47 | 6:47 | 7:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 471
974 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:47 | 6:47 | 7:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 471
975 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:47 | 6:47 | 7:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 471
976 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:47 | 6:47 | 7:07 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 471
977 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-32 | PWEPL | MSEDCL | 2.273% | S/D for Line Stringing work | 13:15 | 13:15 | 15:32 | 0 | 2.2833 | 2.2833 | Line Stringing work done | Close | 0.051894 | IG Unscheduled Maintenance |  | 258
978 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:32 | 15:32 | 15:52 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 43
979 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-37 | PWEPL | MSEDCL | 2.273% | S/D for Line Stringing work | 13:15 | 13:15 | 15:32 | 0 | 2.2833 | 2.2833 | Line Stringing work done | Close | 0.051894 | IG Unscheduled Maintenance |  | 211
980 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:32 | 15:32 | 15:52 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 36
981 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-50 | PWEPL | MSEDCL | 2.273% | S/D for Line Stringing work | 13:15 | 13:15 | 15:32 | 0 | 2.2833 | 2.2833 | Line Stringing work done | Close | 0.051894 | IG Unscheduled Maintenance |  | 211
982 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:32 | 15:32 | 15:52 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 36
983 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-51 | PWEPL | MSEDCL | 2.273% | S/D for Line Stringing work | 13:15 | 13:15 | 15:32 | 0 | 2.2833 | 2.2833 | Line Stringing work done | Close | 0.051894 | IG Unscheduled Maintenance |  | 262
984 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:32 | 15:32 | 15:52 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 44
985 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-52 | PWEPL | MSEDCL | 2.273% | S/D for Line Stringing work | 13:15 | 13:15 | 15:32 | 0 | 2.2833 | 2.2833 | Line Stringing work done | Close | 0.051894 | IG Unscheduled Maintenance |  | 211
986 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:32 | 15:32 | 15:52 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 36
987 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-55 | PWEPL | MSEDCL | 2.273% | S/D for Line Stringing work | 13:15 | 13:15 | 15:32 | 0 | 2.2833 | 2.2833 | Line Stringing work done | Close | 0.051894 | IG Unscheduled Maintenance |  | 3825
988 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-20 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:32 | 15:32 | 15:52 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Unscheduled Maintenance |  | 653
989 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 7:48 | 7:48 | 11:30 | 0 | 3.7 | 3.7 | Test charged taken charged successfully | Close | 1.0932 | IG Breakdown Maintenance |  | 33792
990 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 11:30 | 11:30 | 11:41 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | IG Breakdown Maintenance |  | 241
991 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 11:30 | 11:30 | 11:38 | 0 | 0.13333 | 0.13333 | Rebooted the PLC & reset at scada | Close | 0.0030303 | IG Breakdown Maintenance |  | 175
992 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 11:30 | 11:30 | 11:43 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Breakdown Maintenance |  | 285
993 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 11:30 | 11:30 | 11:44 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Breakdown Maintenance |  | 307
994 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 11:30 | 11:30 | 11:44 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Breakdown Maintenance |  | 307
995 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 11:30 | 11:30 | 11:45 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Breakdown Maintenance |  | 329
996 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 11:30 | 11:30 | 11:37 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | IG Breakdown Maintenance |  | 153
997 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-32 | PWEPL | MSEDCL | 2.273% | After complete line petrolling & CKT will restored | 11:30 | 11:30 | 12:11 | 0 | 0.68333 | 0.68333 | Rebooted the PLC & reset at scada | Close | 0.01553 | IG Breakdown Maintenance |  | 1062
998 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:11 | 12:11 | 12:31 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 531
999 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-37 | PWEPL | MSEDCL | 2.273% | After complete line petrolling & CKT will restored | 11:30 | 11:30 | 12:11 | 0 | 0.68333 | 0.68333 | Rebooted the PLC & reset at scada | Close | 0.01553 | IG Breakdown Maintenance |  | 1248
1000 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:11 | 12:11 | 12:24 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Breakdown Maintenance |  | 345
1001 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-50 | PWEPL | MSEDCL | 2.273% | After complete line petrolling & CKT will restored | 11:30 | 11:30 | 12:11 | 0 | 0.68333 | 0.68333 | Rebooted the PLC & reset at scada | Close | 0.01553 | IG Breakdown Maintenance |  | 1102
1002 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:11 | 12:11 | 12:28 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Breakdown Maintenance |  | 451
1003 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-51 | PWEPL | MSEDCL | 2.273% | After complete line petrolling & CKT will restored | 11:30 | 11:30 | 12:11 | 0 | 0.68333 | 0.68333 | Rebooted the PLC & reset at scada | Close | 0.01553 | IG Breakdown Maintenance |  | 1102
1004 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:11 | 12:11 | 12:28 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Breakdown Maintenance |  | 451
1005 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-52 | PWEPL | MSEDCL | 2.273% | After complete line petrolling & CKT will restored | 11:30 | 11:30 | 12:11 | 0 | 0.68333 | 0.68333 | Rebooted the PLC & reset at scada | Close | 0.01553 | IG Breakdown Maintenance |  | 1089
1006 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:11 | 12:11 | 12:30 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Breakdown Maintenance |  | 504
1007 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-55 | PWEPL | MSEDCL | 2.273% | After complete line petrolling & CKT will restored | 11:30 | 11:30 | 12:11 | 0 | 0.68333 | 0.68333 | Rebooted the PLC & reset at scada | Close | 0.01553 | IG Breakdown Maintenance |  | 1301
1008 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:11 | 12:11 | 12:22 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | IG Breakdown Maintenance |  | 292
1009 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-42 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 8:40 | 8:40 | 10:00 | 0 | 1.3333 | 1.3333 | VCB reset & Charge | Close | 0.030303 | IG Breakdown Maintenance |  | 2211
1010 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-23 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:00 | 10:00 | 10:14 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Breakdown Maintenance |  | 468
1011 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 10:00 | 10:00 | 10:37 | 0 | 0.61667 | 0.61667 | Test charged taken charged successfully | Close | 0.1822 | IG Breakdown Maintenance |  | 14822
1012 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:37 | 10:37 | 10:56 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Breakdown Maintenance |  | 585
1013 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:37 | 10:37 | 10:48 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | IG Breakdown Maintenance |  | 338
1014 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:37 | 10:37 | 10:57 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 616
1015 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:37 | 10:37 | 10:48 | 0 | 0.18333 | 0.18333 | Rebooted the PLC & reset at scada | Close | 0.0041667 | IG Breakdown Maintenance |  | 338
1016 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:37 | 10:37 | 10:56 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Breakdown Maintenance |  | 585
1017 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:37 | 10:37 | 10:53 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Breakdown Maintenance |  | 493
1018 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:37 | 10:37 | 10:57 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 616
1019 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:37 | 10:37 | 10:57 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 616
1020 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:37 | 10:37 | 10:57 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 616
1021 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:37 | 10:37 | 10:57 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 616
1022 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:37 | 10:37 | 10:57 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 616
1023 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:37 | 10:37 | 10:57 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 616
1024 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-07 | PWEPL | MSEDCL | 2.273% | Y Phase Protection PT bypass work | 10:37 | 10:37 | 11:07 | 0 | 0.5 | 0.5 | PT bypass work done | Close | 0.011364 | IG Breakdown Maintenance |  | 215
1025 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 11:07 | 11:07 | 11:25 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 321
1026 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-55 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 10:57 | 10:57 | 11:19 | 0 | 0.36667 | 0.36667 | VCB reset & Charge | Close | 0.0083333 | IG Breakdown Maintenance |  | 333
1027 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-24 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 11:19 | 11:19 | 11:28 | 0 | 0.15 | 0.15 | Rebooted the PLC & reset at scada | Close | 0.0034091 | IG Breakdown Maintenance |  | 230
1028 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | Wind_F4 | PWEPL | MSEDCL | 29.55% | Feeder tripped by O/C | 11:55 | 11:55 | 12:04 | 0 | 0.15 | 0.15 | Test charged taken charged successfully | Close | 0.044318 | IG Breakdown Maintenance |  | 3923
1029 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-01 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:04 | 12:04 | 12:08 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | IG Breakdown Maintenance |  | 134
1030 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-02 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:04 | 12:04 | 12:17 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Breakdown Maintenance |  | 435
1031 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-03 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:04 | 12:04 | 12:21 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Breakdown Maintenance |  | 570
1032 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-07 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:04 | 12:04 | 12:21 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Breakdown Maintenance |  | 570
1033 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-18 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:04 | 12:04 | 12:17 | 0 | 0.21667 | 0.21667 | Rebooted the PLC & reset at scada | Close | 0.0049242 | IG Breakdown Maintenance |  | 435
1034 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-31 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:04 | 12:04 | 12:22 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 603
1035 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-56 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:04 | 12:04 | 12:19 | 0 | 0.25 | 0.25 | Rebooted the PLC & reset at scada | Close | 0.0056818 | IG Breakdown Maintenance |  | 503
1036 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-32 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:04 | 12:04 | 12:20 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Breakdown Maintenance |  | 536
1037 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-37 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:04 | 12:04 | 12:24 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 670
1038 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-50 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:04 | 12:04 | 12:22 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 603
1039 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-51 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:04 | 12:04 | 12:22 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 570
1040 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-52 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:04 | 12:04 | 12:21 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Breakdown Maintenance |  | 603
1041 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-26 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:04 | 12:04 | 12:22 | 0 | 0.3 | 0.3 | Rebooted the PLC & reset at scada | Close | 0.0068182 | IG Breakdown Maintenance |  | 737
1042 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | P-14 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 0:20 | 0:20 | 0:56 | 0 | 0.6 | 0.6 | VCB reset & Charge | Close | 0.013636 | IG Breakdown Maintenance |  | 1147
1043 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:56 | 0:56 | 1:06 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Breakdown Maintenance |  | 318
1044 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | P-12 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 5:25 | 5:25 | 5:55 | 0 | 0.5 | 0.5 | VCB reset & Charge | Close | 0.011364 | IG Breakdown Maintenance |  | 981
1045 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | P-12 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:55 | 5:55 | 5:59 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | IG Breakdown Maintenance |  | 130
1046 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | P-45 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 5:25 | 5:25 | 6:54 | 0 | 1.4833 | 1.4833 | VCB reset & Charge | Close | 0.033712 | IG Breakdown Maintenance |  | 2000
1047 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | P-45 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 6:54 | 6:54 | 6:58 | 0 | 0.066667 | 0.066667 | Rebooted the PLC & reset at scada | Close | 0.0015152 | IG Breakdown Maintenance |  | 89
1048 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | P-05 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 12:52 | 12:52 | 13:55 | 0 | 1.05 | 1.05 | VCB reset & Charge | Close | 0.023864 | IG Breakdown Maintenance |  | 1552
1049 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 13:55 | 13:55 | 14:02 | 0 | 0.11667 | 0.11667 | Rebooted the PLC & reset at scada | Close | 0.0026515 | IG Breakdown Maintenance |  | 172
1050 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-29 | P-05 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 23:54 | 23:54 | 23:59 | 0 | 0.083333 | 0.083333 | WORK IN PROGRESS | OPEN | 0.0018939 | IG Breakdown Maintenance |  | 260
1051 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-30 | P-05 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 0:00 | 0:00 | 1:15 | 0 | 1.25 | 1.25 | VCB reset & Charge | Close | 0.028409 | IG Breakdown Maintenance |  | 1768
1052 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-30 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:15 | 1:15 | 1:17 | 0 | 0.033333 | 0.033333 | Rebooted the PLC & reset at scada | Close | 0.00075758 | IG Breakdown Maintenance |  | 54
1053 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-30 | P-05 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 21:38 | 21:38 | 22:32 | 0 | 0.9 | 0.9 | VCB reset & Charge | Close | 0.020455 | IG Breakdown Maintenance |  | 1634
1054 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-30 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 22:32 | 22:32 | 22:42 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Breakdown Maintenance |  | 302
1055 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | P-05 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 3:13 | 3:13 | 5:04 | 0 | 1.85 | 1.85 | VCB reset & Charge | Close | 0.042045 | IG Breakdown Maintenance |  | 2627
1056 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 5:04 | 5:04 | 5:06 | 0 | 0.033333 | 0.033333 | Rebooted the PLC & reset at scada | Close | 0.00075758 | IG Breakdown Maintenance |  | 47
1057 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | P-05 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 6:59 | 6:59 | 9:12 | 0 | 2.2167 | 2.2167 | VCB reset & Charge | Close | 0.050379 | IG Breakdown Maintenance |  | 3420
1058 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-01 | P-05 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 9:12 | 9:12 | 9:15 | 0 | 0.05 | 0.05 | Rebooted the PLC & reset at scada | Close | 0.0011364 | IG Breakdown Maintenance |  | 77
1059 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | Wind_F2 | PWEPL | MSEDCL | 27.27% | Feeder tripped by E/F | 14:37 | 14:37 | 15:18 | 0 | 0.68333 | 0.68333 | Test charged taken charged successfully | Close | 0.18636 | IG Breakdown Maintenance |  | 8993
1060 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-14 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:18 | 15:18 | 15:32 | 0 | 0.23333 | 0.23333 | Rebooted the PLC & reset at scada | Close | 0.005303 | IG Breakdown Maintenance |  | 255
1061 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-15 | PWEPL | MSEDCL | 2.273% | VCB Tripped | 15:18 | 15:18 | 16:15 | 0 | 0.95 | 0.95 | VCB reset & Charge | Close | 0.021591 | IG Breakdown Maintenance |  | 9824
1062 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:15 | 16:15 | 16:25 | 0 | 0.16667 | 0.16667 | Rebooted the PLC & reset at scada | Close | 0.0037879 | IG Breakdown Maintenance |  | 310
1063 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-16 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:18 | 15:18 | 15:35 | 0 | 0.28333 | 0.28333 | Rebooted the PLC & reset at scada | Close | 0.0064394 | IG Breakdown Maintenance |  | 310
1064 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-17 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:18 | 15:18 | 15:38 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 409
1065 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-19 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:18 | 15:18 | 15:38 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 409
1066 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-20 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:18 | 15:18 | 15:38 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 409
1067 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-38 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 15:18 | 15:18 | 15:38 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 409
1068 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-04 | PWEPL | MSEDCL | 2.273% | PWEPL-04 R phase LA failure | 15:18 | 15:18 | 16:02 | 0 | 0.73333 | 0.73333 | LA replaced | Close | 0.016667 | IG Breakdown Maintenance |  | 1057
1069 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:02 | 16:02 | 16:21 | 0 | 0.31667 | 0.31667 | Rebooted the PLC & reset at scada | Close | 0.007197 | IG Breakdown Maintenance |  | 310
1070 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-22 | PWEPL | MSEDCL | 2.273% | PWEPL-04 R phase LA failure | 15:18 | 15:18 | 16:02 | 0 | 0.73333 | 0.73333 | LA replaced | Close | 0.016667 | IG Breakdown Maintenance |  | 1057
1071 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-22 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:02 | 16:02 | 16:22 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 310
1072 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-23 | PWEPL | MSEDCL | 2.273% | PWEPL-04 R phase LA failure | 15:18 | 15:18 | 16:02 | 0 | 0.73333 | 0.73333 | LA replaced | Close | 0.016667 | IG Breakdown Maintenance |  | 1057
1073 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-23 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:02 | 16:02 | 16:22 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 310
1074 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-34 | PWEPL | MSEDCL | 2.273% | PWEPL-04 R phase LA failure | 15:18 | 15:18 | 16:02 | 0 | 0.73333 | 0.73333 | LA replaced | Close | 0.016667 | IG Breakdown Maintenance |  | 1057
1075 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-34 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:02 | 16:02 | 16:22 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 310
1076 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-43 | PWEPL | MSEDCL | 2.273% | PWEPL-04 R phase LA failure | 15:18 | 15:18 | 16:02 | 0 | 0.73333 | 0.73333 | LA replaced | Close | 0.016667 | IG Breakdown Maintenance |  | 1057
1077 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-02 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 16:02 | 16:02 | 16:22 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 310
1078 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | P-42 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 9:47 | 9:47 | 10:31 | 0 | 0.73333 | 0.73333 | VCB reset & Charge | Close | 0.016667 | IG Breakdown Maintenance |  | 1375
1079 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 10:31 | 10:31 | 10:51 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 625
1080 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | P-15 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 12:05 | 12:05 | 12:25 | 0 | 0.33333 | 0.33333 | VCB reset & Charge | Close | 0.0075758 | IG Breakdown Maintenance |  | 620
1081 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-03 | P-15 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 12:25 | 12:25 | 12:31 | 0 | 0.1 | 0.1 | Rebooted the PLC & reset at scada | Close | 0.0022727 | IG Breakdown Maintenance |  | 186
1082 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | P-04 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 23:16 | 23:16 | 23:59 | 0 | 0.71667 | 0.71667 | Work in progress | Close | 0.016288 | IG Breakdown Maintenance |  | 1265
1083 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | P-43 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 22:26 | 22:26 | 23:22 | 0 | 0.93333 | 0.93333 | VCB reset & Charge | Close | 0.021212 | IG Breakdown Maintenance |  | 1254
1084 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | P-43 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 23:22 | 23:22 | 23:42 | 0 | 0.33333 | 0.33333 | Rebooted the PLC & reset at scada | Close | 0.0075758 | IG Breakdown Maintenance |  | 696
1085 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | P-42 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 23:16 | 23:16 | 23:59 | 0 | 0.71667 | 0.71667 | Work in progress | Close | 0.016288 | IG Breakdown Maintenance |  | 921
1086 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-07 | P-55 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 22:55 | 22:55 | 23:59 | 0 | 1.0667 | 1.0667 | Work in progress | Close | 0.024242 | IG Breakdown Maintenance |  | 2084
1087 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | P-04 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 0:00 | 0:00 | 0:10 | 0 | 0.16667 | 0.16667 | VCB reset & Charge | Close | 0.0037879 | IG Breakdown Maintenance |  | 11
1088 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | P-04 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 0:10 | 0:10 | 0:15 | 0 | 0.083333 | 0.083333 | Rebooted the PLC & reset at scada | Close | 0.0018939 | IG Breakdown Maintenance |  | 11
1089 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | P-55 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 0:00 | 0:00 | 1:00 | 0 | 1 | 1 | VCB reset & Charge | Close | 0.022727 | IG Breakdown Maintenance |  | 1648
1090 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | P-55 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:00 | 1:00 | 1:12 | 0 | 0.2 | 0.2 | Rebooted the PLC & reset at scada | Close | 0.0045455 | IG Breakdown Maintenance |  | 412
1091 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | P-42 | PWEPL | MSEDCL | 2.273% | Undervoltage fault | 0:00 | 0:00 | 1:18 | 0 | 1.3 | 1.3 | VCB reset & Charge | Close | 0.029545 | IG Breakdown Maintenance |  | 2045
1092 | 2026 | 2025 | Year_3 | 2025-07-01 | 2025-07-08 | P-42 | PWEPL | MSEDCL | 2.273% | System re-initialization after grid outage | 1:18 | 1:18 | 1:34 | 0 | 0.26667 | 0.26667 | Rebooted the PLC & reset at scada | Close | 0.0060606 | IG Breakdown Maintenance |  | 527
Formulas:
Month = Table6[[#This Row],[Date]]-DAY(Table6[[#This Row],[Date]])+1

## Grid_BD
Sr. No. | Financial Year | Calendar Year | Operating Year | Month | Date | Affected Feeder | SPV | Concumaer | Plant Equivalent Weightage | Breakdown Description | Breakdown Type | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Fault Category | Paired WTG for Enegy based MA | Loss of KWH | Estimated Energy Loss (kWh) | Curtailment Order imit. | EGA_Including_CurtailmentOrder | PTW No. | Job Card No.
1 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | Wind_F1 | PWEPL | MSEDCL | 22.73% | S/D for SS V.C.B VDR & IR testing work |  | 9:54 | 0.4125 | 0.70625 | 0 | 7.05 | 7.05 | Testing work completed | Close | 1.6023 | EG Scheduled Maintenance | Site Average |  | 6060 |  | 100%
2 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | Wind_F2 | PWEPL | MSEDCL | 27.27% | S/D for SS V.C.B VDR & IR testing work |  | 10:58 | 0.45694 | 0.70694 | 0 | 6 | 6 | Testing work completed | Close | 1.6364 | EG Scheduled Maintenance | Site Average |  | 6204 |  | 100%
3 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | Wind_F3 | PWEPL | MSEDCL | 20.45% | S/D for SS V.C.B VDR & IR testing work |  | 17:02 | 0.70972 | 0.84375 | 0 | 3.2167 | 3.2167 | Testing work completed | Close | 0.65795 | EG Scheduled Maintenance | Site Average |  | 2547 |  | 100%
4 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-08 | Wind_F4 | PWEPL | MSEDCL | 29.55% | S/D for SS V.C.B VDR & IR testing work |  | 17:06 | 0.7125 | 0.84375 | 0 | 3.15 | 3.15 | Testing work completed | Close | 0.93068 | EG Scheduled Maintenance | Site Average |  | 3601 |  | 100%
5 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | Wind_F1 | PWEPL | MSEDCL | 22.73% | S/D for Nerale S/S bus bar jump replacement work |  | 8:55 | 0.37153 | 0.78125 | 0 | 9.8333 | 9.8333 | Jump replacement work completed | Close | 2.2348 | EG Scheduled Maintenance | Site Average |  | 23600 |  | 100%
6 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-15 | Wind_F2 | PWEPL | MSEDCL | 27.27% | S/D for Nerale S/S bus bar jump replacement work |  | 8:55 | 0.37153 | 0.78125 | 0 | 9.8333 | 9.8333 | Jump replacement work completed | Close | 2.6818 | EG Scheduled Maintenance | Site Average |  | 28440 |  | 100%
7 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | Wind_F3 | PWEPL | MSEDCL | 20.45% | S/D for Nerale S/S bus bar jump replacement work |  | 10:21 | 0.43125 | 0.78819 | 0 | 8.5667 | 8.5667 | Jump replacement work completed | Close | 1.7523 | EG Scheduled Maintenance | Site Average |  | 8850 |  | 100%
8 | 2026 | 2025 | Year_3 | 2025-04-01 | 2025-04-22 | Wind_F4 | PWEPL | MSEDCL | 29.55% | S/D for Nerale S/S bus bar jump replacement work |  | 10:22 | 0.43194 | 0.77778 | 0 | 8.3 | 8.3 | Jump replacement work completed | Close | 2.4523 | EG Scheduled Maintenance | Site Average |  | 12270 |  | 100%
9 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | Wind_F3 | PWEPL | MSEDCL | 20.45% | S/D for Nerale S/S 33kv Side Maintenance & Externel line Maintenance work |  | 10:00 | 0.41667 | 0.69444 | 0 | 6.6667 | 6.6667 | Side Maintenance & Externel line Maintenance work done | Close | 1.3636 | EG Scheduled Maintenance | Site Average |  | 4737 |  | 100%
10 | 2026 | 2025 | Year_3 | 2025-05-01 | 2025-05-13 | Wind_F4 | PWEPL | MSEDCL | 29.55% | S/D for Nerale S/S 33kv Side Maintenance & Externel line Maintenance work |  | 10:00 | 0.41667 | 0.69444 | 0 | 6.6667 | 6.6667 | Side Maintenance & Externel line Maintenance work done | Close | 1.9697 | EG Scheduled Maintenance | Site Average |  | 6724 |  | 100%
11 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | Wind_F1 | PWEPL | MSEDCL | 22.73% | S/D for Nerale S/S 33kv side Maintenance & testing work |  | 10:58 | 0.45694 | 0.57014 | 0 | 2.7167 | 2.7167 | Side Maintenance & Testing work completed | Close | 0.61742 | EG Scheduled Maintenance | Site Average |  | 18741 |  | 100%
12 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | Wind_F2 | PWEPL | MSEDCL | 27.27% | S/D for Nerale S/S 33kv side Maintenance & testing work |  | 11:15 | 0.46875 | 0.57083 | 0 | 2.45 | 2.45 | Side Maintenance & Testing work completed | Close | 0.66818 | EG Scheduled Maintenance | Site Average |  | 20430 |  | 100%
13 | 2026 | 2025 | Year_3 | 2025-06-01 | 2025-06-10 | Wind_F3 | PWEPL | MSEDCL | 20.45% | S/D for Nerale S/S 33kv side Maintenance & testing work |  | 13:25 | 0.55903 | 0.59583 | 0 | 0.88333 | 0.88333 | Side Maintenance & Testing work completed | Close | 0.18068 | EG Scheduled Maintenance | Site Average |  | 5386 |  | 100%
Formulas:
Month = Table9[[#This Row],[Date]]-DAY(Table9[[#This Row],[Date]])+1

## PM
Sr. No. | Location No. | Location Type | FY | CY | Cycle No. | Frequency | PM Title | Day 1 Planned Maintenance Date | Day 2 Planned Maintenance Date | Day 1 Actual Maintenance Date | Day 2 Actual Maintenance Date | Delay Day 1 | Delay Day 2 | Remark
1 | PWEPL-27 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-02 |  | 2023-10-05 |  | 3 |  | 11th Semi Annual Maintenance activity Completed
2 | PWEPL-17 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-03 |  | 2023-10-06 |  | 3 |  | 11th Semi Annual Maintenance activity Completed
3 | PWEPL-38 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-04 |  | 2023-10-07 |  | 3 |  | 11th Semi Annual Maintenance activity Completed
4 | PWEPL-09 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-05 |  | 2023-10-11 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
5 | PWEPL-10 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-06 |  | 2023-10-12 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
6 | PWEPL-11 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-07 |  | 2023-10-13 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
7 | PWEPL-12 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-09 |  | 2023-10-14 |  | 5 |  | 11th Semi Annual Maintenance activity Completed
8 | PWEPL-13 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-10 |  | 2023-10-16 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
9 | PWEPL-14 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-11 |  | 2023-10-17 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
10 | PWEPL-15 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-12 |  | 2023-10-18 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
11 | PWEPL-16 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-13 |  | 2023-10-19 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
12 | PWEPL-19 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-14 |  | 2023-10-20 |  | 6 |  | 11th Semi Annual Maintenance activity Completed
13 | PWEPL-20 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-16 |  | 2023-10-21 |  | 5 |  | 11th Semi Annual Maintenance activity Completed
14 | PWEPL-28 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-17 |  | 2023-10-25 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
15 | PWEPL-26 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-18 |  | 2023-10-26 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
16 | PWEPL-25 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-19 |  | 2023-10-27 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
17 | PWEPL-08 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-20 |  | 2023-10-28 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
18 | PWEPL-43 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-21 |  | 2023-10-30 |  | 9 |  | 11th Semi Annual Maintenance activity Completed
19 | PWEPL-22 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-23 |  | 2023-10-31 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
20 | PWEPL-23 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-24 |  | 2023-11-01 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
21 | PWEPL-04 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-25 |  | 2023-11-02 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
22 | PWEPL-34 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-26 |  | 2023-11-03 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
23 | PWEPL-32 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-27 |  | 2023-11-04 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
24 | PWEPL-37 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-28 |  | 2023-11-06 |  | 9 |  | 11th Semi Annual Maintenance activity Completed
25 | PWEPL-50 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-30 |  | 2023-11-07 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
26 | PWEPL-51 |  | 2024 | 2023 | 11 |  | SAM | 2023-10-31 |  | 2023-11-08 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
27 | PWEPL-52 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-01 |  | 2023-11-09 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
28 | PWEPL-31 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-02 |  | 2023-11-10 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
29 | PWEPL-03 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-03 |  | 2023-11-11 |  | 8 |  | 11th Semi Annual Maintenance activity Completed
30 | PWEPL-02 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-04 |  | 2023-11-16 |  | 12 |  | 11th Semi Annual Maintenance activity Completed
31 | PWEPL-18 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-06 |  | 2023-11-17 |  | 11 |  | 11th Semi Annual Maintenance activity Completed
32 | PWEPL-01 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-07 |  | 2023-11-18 |  | 11 |  | 11th Semi Annual Maintenance activity Completed
33 | PWEPL-07 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-08 |  | 2023-11-20 |  | 12 |  | 11th Semi Annual Maintenance activity Completed
34 | PWEPL-56 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-09 |  | 2023-11-21 |  | 12 |  | 11th Semi Annual Maintenance activity Completed
35 | PWEPL-55 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-10 |  | 2023-11-22 |  | 12 |  | 11th Semi Annual Maintenance activity Completed
36 | PWEPL-45 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-11 |  | 2023-11-23 |  | 12 |  | 11th Semi Annual Maintenance activity Completed
37 | PWEPL-46 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-20 |  | 2023-11-24 |  | 4 |  | 11th Semi Annual Maintenance activity Completed
38 | PWEPL-47 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-21 |  | 2023-11-25 |  | 4 |  | 11th Semi Annual Maintenance activity Completed
39 | PWEPL-48 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-22 |  | 2023-11-27 |  | 5 |  | 11th Semi Annual Maintenance activity Completed
40 | PWEPL-42 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-23 |  | 2023-11-28 |  | 5 |  | 11th Semi Annual Maintenance activity Completed
41 | PWEPL-06 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-24 |  | 2023-11-29 |  | 5 |  | 11th Semi Annual Maintenance activity Completed
42 | PWEPL-41 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-25 |  | 2023-11-30 |  | 5 |  | 11th Semi Annual Maintenance activity Completed
43 | PWEPL-05 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-27 |  | 2023-12-01 |  | 4 |  | 11th Semi Annual Maintenance activity Completed
44 | PWEPL-40 |  | 2024 | 2023 | 11 |  | SAM | 2023-11-28 |  | 2023-12-02 |  | 4 |  | 11th Semi Annual Maintenance activity Completed
1 | PWEPL-09 |  | 2024 | 2024 | 11 |  | AM | 2024-02-12 | 2024-02-13 | 2024-02-13 | 2024-02-19 | 1 | 6 | 11th Annual Maintenance activity Completed
2 | PWEPL-10 |  | 2024 | 2024 | 11 |  | AM | 2024-02-14 | 2024-02-15 | 2024-02-14 | 2024-02-20 | 0 | 5 | 11th Annual Maintenance activity Completed
3 | PWEPL-11 |  | 2024 | 2024 | 11 |  | AM | 2024-02-16 | 2024-02-17 | 2024-02-15 | 2024-02-22 | -1 | 5 | 11th Annual Maintenance activity Completed
4 | PWEPL-12 |  | 2024 | 2024 | 11 |  | AM | 2024-02-19 | 2024-02-20 | 2024-02-16 | 2024-02-23 | -3 | 3 | 11th Annual Maintenance activity Completed
5 | PWEPL-13 |  | 2024 | 2024 | 11 |  | AM | 2024-02-21 | 2024-02-22 | 2024-02-26 | 2024-02-29 | 5 | 7 | 11th Annual Maintenance activity Completed
6 | PWEPL-14 |  | 2024 | 2024 | 11 |  | AM | 2024-02-23 | 2024-02-24 | 2024-02-27 | 2024-03-01 | 4 | 6 | 11th Annual Maintenance activity Completed
7 | PWEPL-15 |  | 2024 | 2024 | 11 |  | AM | 2024-02-26 | 2024-02-27 | 2024-02-28 | 2024-03-08 | 2 | 10 | 11th Annual Maintenance activity Completed
8 | PWEPL-16 |  | 2024 | 2024 | 11 |  | AM | 2024-02-28 | 2024-02-29 | 2024-03-05 | 2024-03-05 | 6 | 5 | 11th Annual Maintenance activity Completed
9 | PWEPL-17 |  | 2024 | 2024 | 11 |  | AM | 2024-03-01 | 2024-03-02 | 2024-03-07 | 2024-03-07 | 6 | 5 | 11th Annual Maintenance activity Completed
10 | PWEPL-19 |  | 2024 | 2024 | 11 |  | AM | 2024-03-04 | 2024-03-05 | 2024-03-12 | 2024-03-12 | 8 | 7 | 11th Annual Maintenance activity Completed
11 | PWEPL-20 |  | 2024 | 2024 | 11 |  | AM | 2024-03-06 | 2024-03-07 | 2024-03-13 | 2024-03-15 | 7 | 8 | 11th Annual Maintenance activity Completed
12 | PWEPL-38 |  | 2024 | 2024 | 11 |  | AM | 2024-03-08 | 2024-03-09 | 2024-03-14 | 2024-03-14 | 6 | 5 | 11th Annual Maintenance activity Completed
13 | PWEPL-28 |  | 2024 | 2024 | 11 |  | AM | 2024-03-11 | 2024-03-12 | 2024-03-06 | 2024-03-06 | -5 | -6 | 11th Annual Maintenance activity Completed
14 | PWEPL-27 |  | 2024 | 2024 | 11 |  | AM | 2024-03-13 | 2024-03-14 | 2024-03-18 | 2024-03-21 | 5 | 7 | 11th Annual Maintenance activity Completed
15 | PWEPL-26 |  | 2024 | 2024 | 11 |  | AM | 2024-03-15 | 2024-03-16 | 2024-03-19 | 2024-03-23 | 4 | 7 | 11th Annual Maintenance activity Completed
16 | PWEPL-25 |  | 2024 | 2024 | 11 |  | AM | 2024-03-18 | 2024-03-19 | 2024-03-20 | 2024-03-26 | 2 | 7 | 11th Annual Maintenance activity Completed
17 | PWEPL-08 |  | 2024 | 2024 | 11 |  | AM | 2024-03-20 | 2024-03-21 | 2024-03-28 | 2024-03-29 | 8 | 8 | 11th Annual Maintenance activity Completed
18 | PWEPL-43 |  | 2024 | 2024 | 11 |  | AM | 2024-03-22 | 2024-03-23 | 2024-03-31 | 2024-04-01 | 9 | 9 | 11th Annual Maintenance activity Completed
19 | PWEPL-22 |  | 2024 | 2024 | 11 |  | AM | 2024-03-26 | 2024-03-27 | 2024-04-02 | 2024-04-03 | 7 | 7 | 11th Annual Maintenance activity Completed
20 | PWEPL-23 |  | 2024 | 2024 | 11 |  | AM | 2024-03-28 | 2024-03-29 | 2024-04-05 | 2024-04-06 | 8 | 8 | 11th Annual Maintenance activity Completed
21 | PWEPL-04 |  | 2024 | 2024 | 11 |  | AM | 2024-03-30 | 2024-04-01 | 2024-04-08 | 2024-04-09 | 9 | 8 | 11th Annual Maintenance activity Completed
22 | PWEPL-34 |  | 2024 | 2024 | 11 |  | AM | 2024-04-02 | 2024-04-03 | 2024-04-10 | 2024-04-11 | 8 | 8 | 11th Annual Maintenance activity Completed
23 | PWEPL-32 |  | 2024 | 2024 | 11 |  | AM | 2024-04-04 | 2024-04-05 | 2024-05-16 | 2024-05-17 | 42 | 42 | 11th Annual Maintenance activity Completed
24 | PWEPL-37 |  | 2024 | 2024 | 11 |  | AM | 2024-04-06 | 2024-04-08 | 2024-05-18 | 2024-05-18 | 42 | 40 | 11th Annual Maintenance activity Completed
25 | PWEPL-50 |  | 2024 | 2024 | 11 |  | AM | 2024-04-10 | 2024-04-11 | 2024-04-15 | 2024-04-15 | 5 | 4 | 11th Annual Maintenance activity Completed
26 | PWEPL-51 |  | 2024 | 2024 | 11 |  | AM | 2024-04-12 | 2024-04-13 | 2024-04-18 | 2024-04-18 | 6 | 5 | 11th Annual Maintenance activity Completed
27 | PWEPL-52 |  | 2024 | 2024 | 11 |  | AM | 2024-04-15 | 2024-04-16 | 2024-04-16 | 2024-04-16 | 1 | 0 | 11th Annual Maintenance activity Completed
28 | PWEPL-31 |  | 2024 | 2024 | 11 |  | AM | 2024-04-17 | 2024-04-18 | 2024-04-24 | 2024-04-24 | 7 | 6 | 11th Annual Maintenance activity Completed
29 | PWEPL-03 |  | 2024 | 2024 | 11 |  | AM | 2024-04-19 | 2024-04-20 | 2024-04-23 | 2024-04-23 | 4 | 3 | 11th Annual Maintenance activity Completed
30 | PWEPL-02 |  | 2024 | 2024 | 11 |  | AM | 2024-04-22 | 2024-04-23 | 2024-04-20 | 2024-04-20 | -2 | -3 | 11th Annual Maintenance activity Completed
31 | PWEPL-18 |  | 2024 | 2024 | 11 |  | AM | 2024-04-24 | 2024-04-25 | 2024-04-25 | 2024-04-25 | 1 | 0 | 11th Annual Maintenance activity Completed
32 | PWEPL-01 |  | 2024 | 2024 | 11 |  | AM | 2024-04-26 | 2024-04-27 | 2024-04-19 | 2024-04-19 | -7 | -8 | 11th Annual Maintenance activity Completed
33 | PWEPL-07 |  | 2024 | 2024 | 11 |  | AM | 2024-04-29 | 2024-04-30 | 2024-04-27 | 2024-04-27 | -2 | -3 | 11th Annual Maintenance activity Completed
34 | PWEPL-56 |  | 2024 | 2024 | 11 |  | AM | 2024-05-02 | 2024-05-03 | 2024-05-01 | 2024-05-01 | -1 | -2 | 11th Annual Maintenance activity Completed
35 | PWEPL-55 |  | 2024 | 2024 | 11 |  | AM | 2024-05-04 | 2024-05-06 | 2024-04-26 | 2024-04-26 | -8 | -10 | 11th Annual Maintenance activity Completed
36 | PWEPL-45 |  | 2024 | 2024 | 11 |  | AM | 2024-05-07 | 2024-05-08 | 2024-05-02 | 2024-05-03 | -5 | -5 | 11th Annual Maintenance activity Completed
37 | PWEPL-46 |  | 2024 | 2024 | 11 |  | AM | 2024-05-09 | 2024-05-10 | 2024-05-04 | 2024-05-04 | -5 | -6 | 11th Annual Maintenance activity Completed
38 | PWEPL-47 |  | 2024 | 2024 | 11 |  | AM | 2024-05-11 | 2024-05-13 | 2024-05-15 | 2024-05-15 | 4 | 2 | 11th Annual Maintenance activity Completed
39 | PWEPL-48 |  | 2024 | 2024 | 11 |  | AM | 2024-05-14 | 2024-05-15 | 2024-05-05 | 2024-05-05 | -9 | -10 | 11th Annual Maintenance activity Completed
40 | PWEPL-42 |  | 2024 | 2024 | 11 |  | AM | 2024-05-16 | 2024-05-17 | 2024-05-06 | 2024-05-06 | -10 | -11 | 11th Annual Maintenance activity Completed
41 | PWEPL-06 |  | 2024 | 2024 | 11 |  | AM | 2024-05-18 | 2024-05-20 | 2024-05-07 | 2024-05-07 | -11 | -13 | 11th Annual Maintenance activity Completed
42 | PWEPL-41 |  | 2024 | 2024 | 11 |  | AM | 2024-05-21 | 2024-05-22 | 2024-05-08 | 2024-05-08 | -13 | -14 | 11th Annual Maintenance activity Completed
43 | PWEPL-05 |  | 2024 | 2024 | 11 |  | AM | 2024-05-23 | 2024-05-24 | 2024-05-09 | 2024-05-09 | -14 | -15 | 11th Annual Maintenance activity Completed
44 | PWEPL-40 |  | 2024 | 2024 | 11 |  | AM | 2024-05-25 | 2024-05-27 | 2024-05-14 | 2024-05-14 | -11 | -13 | 11th Annual Maintenance activity Completed
1 | PWEPL-09 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-03 |  | 2024-10-03 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
2 | PWEPL-10 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-04 |  | 2024-10-04 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
3 | PWEPL-11 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-07 |  | 2024-10-07 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
4 | PWEPL-12 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-08 |  | 2024-10-08 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
5 | PWEPL-13 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-09 |  | 2024-10-09 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
6 | PWEPL-14 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-10 |  | 2024-10-10 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
7 | PWEPL-15 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-11 |  | 2024-10-14 |  | 3 |  | 12th Semi Annual Maintenance activity Completed
8 | PWEPL-16 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-14 |  | 2024-10-15 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
9 | PWEPL-17 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-15 |  | 2024-10-16 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
10 | PWEPL-38 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-16 |  | 2024-10-17 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
11 | PWEPL-20 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-17 |  | 2024-10-18 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
12 | PWEPL-19 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-18 |  | 2024-10-21 |  | 3 |  | 12th Semi Annual Maintenance activity Completed
13 | PWEPL-27 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-21 |  | 2024-10-22 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
14 | PWEPL-28 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-22 |  | 2024-10-23 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
15 | PWEPL-26 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-23 |  | 2024-10-24 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
16 | PWEPL-25 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-24 |  | 2024-10-25 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
17 | PWEPL-08 |  | 2024 | 2024 | 12 |  | SAM | 2024-10-25 |  | 2024-10-26 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
18 | PWEPL-43 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-03 |  | 2024-10-27 |  | -7 |  | 12th Semi Annual Maintenance activity Completed
19 | PWEPL-22 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-04 |  | 2024-10-28 |  | -7 |  | 12th Semi Annual Maintenance activity Completed
20 | PWEPL-23 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-05 |  | 2024-10-29 |  | -7 |  | 12th Semi Annual Maintenance activity Completed
21 | PWEPL-04 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-10 |  | 2024-10-30 |  | -11 |  | 12th Semi Annual Maintenance activity Completed
22 | PWEPL-34 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-06 |  | 2024-11-07 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
23 | PWEPL-32 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-11 |  | 2024-11-08 |  | -3 |  | 12th Semi Annual Maintenance activity Completed
24 | PWEPL-37 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-12 |  | 2024-11-09 |  | -3 |  | 12th Semi Annual Maintenance activity Completed
25 | PWEPL-50 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-13 |  | 2024-11-11 |  | -2 |  | 12th Semi Annual Maintenance activity Completed
26 | PWEPL-51 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-14 |  | 2024-11-12 |  | -2 |  | 12th Semi Annual Maintenance activity Completed
27 | PWEPL-52 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-17 |  | 2024-11-14 |  | -3 |  | 12th Semi Annual Maintenance activity Completed
28 | PWEPL-31 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-18 |  | 2024-11-15 |  | -3 |  | 12th Semi Annual Maintenance activity Completed
29 | PWEPL-03 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-19 |  | 2024-11-18 |  | -1 |  | 12th Semi Annual Maintenance activity Completed
30 | PWEPL-02 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-20 |  | 2024-11-19 |  | -1 |  | 12th Semi Annual Maintenance activity Completed
31 | PWEPL-18 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-21 |  | 2024-11-21 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
32 | PWEPL-01 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-24 |  | 2024-11-22 |  | -2 |  | 12th Semi Annual Maintenance activity Completed
33 | PWEPL-07 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-25 |  | 2024-11-25 |  | 0 |  | 12th Semi Annual Maintenance activity Completed
34 | PWEPL-56 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-26 |  | 2024-11-27 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
35 | PWEPL-55 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-27 |  | 2024-11-28 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
36 | PWEPL-45 |  | 2024 | 2024 | 12 |  | SAM | 2024-11-28 |  | 2024-11-30 |  | 2 |  | 12th Semi Annual Maintenance activity Completed
37 | PWEPL-46 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-01 |  | 2024-12-02 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
38 | PWEPL-47 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-02 |  | 2024-12-04 |  | 2 |  | 12th Semi Annual Maintenance activity Completed
39 | PWEPL-48 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-03 |  | 2024-12-05 |  | 2 |  | 12th Semi Annual Maintenance activity Completed
40 | PWEPL-42 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-04 |  | 2024-12-06 |  | 2 |  | 12th Semi Annual Maintenance activity Completed
41 | PWEPL-06 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-05 |  | 2024-12-07 |  | 2 |  | 12th Semi Annual Maintenance activity Completed
42 | PWEPL-41 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-08 |  | 2024-12-09 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
43 | PWEPL-05 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-09 |  | 2024-12-10 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
44 | PWEPL-40 |  | 2024 | 2024 | 12 |  | SAM | 2024-12-10 |  | 2024-12-11 |  | 1 |  | 12th Semi Annual Maintenance activity Completed
1 | PWEPL-09 |  | 2025 | 2025 | 12 |  | AM | 2025-02-03 | 2025-02-04 | 2025-02-04 | 2025-02-11 | 1 | 7 | 12th Annual Maintenance activity Completed
2 | PWEPL-10 |  | 2025 | 2025 | 12 |  | AM | 2025-02-05 | 2025-02-06 | 2025-02-05 | 2025-02-12 | 0 | 6 | 12th Annual Maintenance activity Completed
3 | PWEPL-11 |  | 2025 | 2025 | 12 |  | AM | 2025-02-07 | 2025-02-08 | 2025-02-06 | 2025-02-13 | -1 | 5 | 12th Annual Maintenance activity Completed
4 | PWEPL-12 |  | 2025 | 2025 | 12 |  | AM | 2025-02-10 | 2025-02-11 | 2025-02-07 | 2025-02-14 | -3 | 3 | 12th Annual Maintenance activity Completed
5 | PWEPL-13 |  | 2025 | 2025 | 12 |  | AM | 2025-02-12 | 2025-02-13 | 2025-02-08 | 2025-02-17 | -4 | 4 | 12th Annual Maintenance activity Completed
6 | PWEPL-14 |  | 2025 | 2025 | 12 |  | AM | 2025-02-14 | 2025-02-15 | 2025-02-10 | 2025-02-18 | -4 | 3 | 12th Annual Maintenance activity Completed
7 | PWEPL-15 |  | 2025 | 2025 | 12 |  | AM | 2025-02-17 | 2025-02-18 | 2025-02-19 | 2025-02-20 | 2 | 2 | 12th Annual Maintenance activity Completed
8 | PWEPL-16 |  | 2025 | 2025 | 12 |  | AM | 2025-02-19 | 2025-02-20 | 2025-02-24 | 2025-02-25 | 5 | 5 | 12th Annual Maintenance activity Completed
9 | PWEPL-17 |  | 2025 | 2025 | 12 |  | AM | 2025-02-21 | 2025-02-22 | 2025-02-26 | 2025-02-27 | 5 | 5 | 12th Annual Maintenance activity Completed
10 | PWEPL-19 |  | 2025 | 2025 | 12 |  | AM | 2025-02-24 | 2025-02-25 | 2025-03-03 | 2025-03-03 | 7 | 6 | 12th Annual Maintenance activity Completed
11 | PWEPL-20 |  | 2025 | 2025 | 12 |  | AM | 2025-02-26 | 2025-02-27 | 2025-03-01 | 2025-03-02 | 3 | 3 | 12th Annual Maintenance activity Completed
12 | PWEPL-38 |  | 2025 | 2025 | 12 |  | AM | 2025-02-28 | 2025-03-01 | 2025-02-28 | 2025-03-02 | 0 | 1 | 12th Annual Maintenance activity Completed
13 | PWEPL-28 |  | 2025 | 2025 | 12 |  | AM | 2025-03-03 | 2025-03-04 | 2025-02-21 | 2025-02-22 | -10 | -10 | 12th Annual Maintenance activity Completed
14 | PWEPL-27 |  | 2025 | 2025 | 12 |  | AM | 2025-03-05 | 2025-03-06 | 2025-03-04 | 2025-03-05 | -1 | -1 | 12th Annual Maintenance activity Completed
15 | PWEPL-26 |  | 2025 | 2025 | 12 |  | AM | 2025-03-07 | 2025-03-08 | 2025-03-06 | 2025-03-07 | -1 | -1 | 12th Annual Maintenance activity Completed
16 | PWEPL-25 |  | 2025 | 2025 | 12 |  | AM | 2025-03-10 | 2025-03-11 | 2025-03-08 | 2025-03-08 | -2 | -3 | 12th Annual Maintenance activity Completed
17 | PWEPL-08 |  | 2025 | 2025 | 12 |  | AM | 2025-03-12 | 2025-03-13 | 2025-03-10 | 2025-03-12 | -2 | -1 | 12th Annual Maintenance activity Completed
18 | PWEPL-43 |  | 2025 | 2025 | 12 |  | AM | 2025-03-14 | 2025-03-15 | 2025-03-17 | 2025-03-18 | 3 | 3 | 12th Annual Maintenance activity Completed
19 | PWEPL-22 |  | 2025 | 2025 | 12 |  | AM | 2025-03-17 | 2025-03-18 | 2025-03-13 | 2025-03-15 | -4 | -3 | 12th Annual Maintenance activity Completed
20 | PWEPL-23 |  | 2025 | 2025 | 12 |  | AM | 2025-03-19 | 2025-03-20 | 2025-03-19 | 2025-03-20 | 0 | 0 | 12th Annual Maintenance activity Completed
21 | PWEPL-04 |  | 2025 | 2025 | 12 |  | AM | 2025-03-21 | 2025-03-22 | 2025-03-21 | 2025-03-22 | 0 | 0 | 12th Annual Maintenance activity Completed
22 | PWEPL-34 |  | 2025 | 2025 | 12 |  | AM | 2025-03-24 | 2025-03-25 | 2025-03-24 | 2025-03-24 | 0 | -1 | 12th Annual Maintenance activity Completed
23 | PWEPL-32 |  | 2025 | 2025 | 12 |  | AM | 2025-03-26 | 2025-03-27 | 2025-03-25 | 2025-03-25 | -1 | -2 | 12th Annual Maintenance activity Completed
24 | PWEPL-37 |  | 2025 | 2025 | 12 |  | AM | 2025-03-28 | 2025-03-29 | 2025-03-26 | 2025-03-26 | -2 | -3 | 12th Annual Maintenance activity Completed
25 | PWEPL-50 |  | 2025 | 2025 | 12 |  | AM | 2025-03-31 | 2025-04-01 | 2025-03-27 | 2025-03-28 | -4 | -4 | 12th Annual Maintenance activity Completed
26 | PWEPL-51 |  | 2025 | 2025 | 12 |  | AM | 2025-04-02 | 2025-04-03 | 2025-03-29 | 2025-03-29 | -4 | -5 | 12th Annual Maintenance activity Completed
27 | PWEPL-52 |  | 2025 | 2025 | 12 |  | AM | 2025-04-04 | 2025-04-05 | 2025-03-31 | 2025-03-31 | -4 | -5 | 12th Annual Maintenance activity Completed
28 | PWEPL-31 |  | 2025 | 2025 | 12 |  | AM | 2025-04-07 | 2025-04-08 | 2025-04-03 | 2025-04-05 | -4 | -3 | 12th Annual Maintenance activity Completed
29 | PWEPL-03 |  | 2025 | 2025 | 12 |  | AM | 2025-04-09 | 2025-04-10 | 2025-04-07 | 2025-04-07 | -2 | -3 | 12th Annual Maintenance activity Completed
30 | PWEPL-02 |  | 2025 | 2025 | 12 |  | AM | 2025-04-11 | 2025-04-12 | 2025-04-08 | 2025-04-12 | -3 | 0 | 12th Annual Maintenance activity Completed
31 | PWEPL-18 |  | 2025 | 2025 | 12 |  | AM | 2025-04-14 | 2025-04-15 | 2025-04-09 | 2025-04-09 | -5 | -6 | 12th Annual Maintenance activity Completed
32 | PWEPL-01 |  | 2025 | 2025 | 12 |  | AM | 2025-04-16 | 2025-04-17 | 2025-04-10 | 2025-04-10 | -6 | -7 | 12th Annual Maintenance activity Completed
33 | PWEPL-07 |  | 2025 | 2025 | 12 |  | AM | 2025-04-18 | 2025-04-19 | 2025-04-11 | 2025-04-30 | -7 | 11 | 12th Annual Maintenance activity Completed
34 | PWEPL-56 |  | 2025 | 2025 | 12 |  | AM | 2025-04-21 | 2025-04-22 | 2025-04-15 | 2025-04-16 | -6 | -6 | 12th Annual Maintenance activity Completed
35 | PWEPL-55 |  | 2025 | 2025 | 12 |  | AM | 2025-04-23 | 2025-04-24 | 2025-04-17 | 2025-04-30 | -6 | 6 | 12th Annual Maintenance activity Completed
36 | PWEPL-45 |  | 2025 | 2025 | 12 |  | AM | 2025-04-25 | 2025-04-26 | 2025-04-18 | 2025-04-30 | -7 | 4 | 12th Annual Maintenance activity Completed
37 | PWEPL-46 |  | 2025 | 2025 | 12 |  | AM | 2025-04-28 | 2025-04-29 | 2025-04-19 | 2025-04-30 | -9 | 1 | 12th Annual Maintenance activity Completed
38 | PWEPL-47 |  | 2025 | 2025 | 12 |  | AM | 2025-04-30 | 2025-05-02 | 2025-04-23 | 2025-05-01 | -7 | -1 | 12th Annual Maintenance activity Completed
39 | PWEPL-48 |  | 2025 | 2025 | 12 |  | AM | 2025-05-03 | 2025-05-05 | 2025-04-24 | 2025-05-01 | -9 | -4 | 12th Annual Maintenance activity Completed
40 | PWEPL-42 |  | 2025 | 2025 | 12 |  | AM | 2025-05-06 | 2025-05-07 | 2025-04-25 | 2025-05-01 | -11 | -6 | 12th Annual Maintenance activity Completed
41 | PWEPL-06 |  | 2025 | 2025 | 12 |  | AM | 2025-05-08 | 2025-05-09 | 2025-04-26 | 2025-05-02 | -12 | -8 | 12th Annual Maintenance activity Completed
42 | PWEPL-41 |  | 2025 | 2025 | 12 |  | AM | 2025-05-12 | 2025-05-13 | 2025-04-27 | 2025-05-02 | -15 | -16 | 12th Annual Maintenance activity Completed
43 | PWEPL-05 |  | 2025 | 2025 | 12 |  | AM | 2025-05-14 | 2025-05-15 | 2025-04-28 | 2025-05-02 | -16 | -17 | 12th Annual Maintenance activity Completed
44 | PWEPL-40 |  | 2025 | 2025 | 12 |  | AM | 2025-05-16 | 2025-05-17 | 2025-04-29 | 2025-05-02 | -17 | -18 | 12th Annual Maintenance activity Completed

## Basic Data (hidden)
[18 empty] | 1 | Programstart PLC
| Generator | Consumer | Capacity | % Plant Equiva. Weightage | Feeder Number | USS YARD | METERING YARD | OG | Total Capacity | 70.4 | [7 empty] | 2 | No Errors
P-01 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-01 |  | OG1 |  |  | Open | PM |  | WTG | IG | EG |  | 3 | Manual Stop
P-02 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-02 |  | OG1 |  |  | Close | BM |  | WTG Unscheduled Maintenance | IG Unscheduled Maintenance | EG Unscheduled Maintenance |  | 6 | System OK
P-03 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-03 |  | OG1 |  |  |  |  | BM | WTG Breakdown Maintenance | IG Breakdown Maintenance | EG Breakdown Maintenance |  | 7 | Storm shutdown
P-04 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-04 |  | OG1 |  |  |  |  | PM | WTG Scheduled Maintenance | IG Scheduled Maintenance | EG Scheduled Maintenance |  | 8 | Overvoltage
P-05 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-05 |  | OG1 | [5 empty] | WTG Environmental | IG Force Major | EG Force Major |  | 9 | Undervoltage
P-06 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-06 |  | OG1 | [5 empty] | WTG Force Majeure |  |  |  | 10 | Underfrequency
P-07 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-07 |  | OG1 | [9 empty] | 11 | Overfrequency
P-08 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-08 |  | OG1 | [5 empty] | Major Breakdown |  |  |  | 12 | Phase angle error
P-09 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-09 |  | OG1 | [5 empty] | Breakdown |  |  |  | 13 | Asymmetric generator current
P-10 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-10 |  | OG1 | [5 empty] | Manual Stop |  |  |  | 14 | Generator overspeed
P-11 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-11 |  | OG1 | [5 empty] | ROW |  |  |  | 15 | Rotor overspeed
P-12 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-12 |  | OG1 | [9 empty] | 16 | RotorSpeedMonitor
P-13 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-13 |  | OG1 | [9 empty] | 19 | Maximum motor power
P-14 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-14 |  | OG1 | [9 empty] | 20 | Cable twisting right
P-15 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-15 |  | OG1 | [9 empty] | 21 | Cable twisting left
P-16 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-16 |  | OG1 | [9 empty] | 22 | Yaw drive stop position
P-17 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-17 |  | OG1 | [9 empty] | 23 | PowerExceedPeakValue
P-18 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-18 |  | OG1 | [9 empty] | 24 | Primary braking time too high
P-19 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-19 |  | OG1 | [9 empty] | 25 | No red. of speed when braking with primarybrake
P-20 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-20 |  | OG1 | [9 empty] | 27 | Secondary braking time too high
P-22 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-22 |  | OG1 | [9 empty] | 28 | No speed reduction with secondary braking
P-23 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-23 |  | OG1 | [9 empty] | 31 | Timeout yaw counter
P-25 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-25 |  | OG1 | [9 empty] | 34 | Brake not released secondary brake
P-26 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-26 |  | OG1 | [9 empty] | 35 | Emergency stop tower base
P-27 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-27 |  | OG1 | [9 empty] | 36 | Speed with braked turbine
P-28 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F1 | P-28 |  | OG1 | [9 empty] | 38 | Secondary brake test
P-31 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-31 |  | OG1 | [9 empty] | 41 | Vibrations sensor Defect
P-32 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-32 |  | OG1 | [9 empty] | 42 | Wrong yaw direction of rotation
P-34 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-34 |  | OG1 | [9 empty] | 45 | Hydraulic pump time too high
P-37 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-37 |  | OG1 | [9 empty] | 46 | Hydraulic pump time too low
P-38 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-38 |  | OG1 | [9 empty] | 47 | Service switch hydraulic top cabinet
P-40 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-40 |  | OG1 | [9 empty] | 48 | Hydraulic oil level too low
P-41 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-41 |  | OG1 | [9 empty] | 51 | Gearbox oil level too low
P-42 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-42 |  | OG1 | [9 empty] | 52 | Gearbox oil ressure too lo
P-43 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F2 | P-43 |  | OG1 | [9 empty] | 53 | Wind vane defect
P-45 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-45 |  | OG1 | [9 empty] | 54 | Anemometer defec
P-46 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-46 |  | OG1 | [9 empty] | 55 | Rotor impulse sensor defect
P-47 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-47 |  | OG1 | [9 empty] | 56 | Generator impulse sensor defect
P-48 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F3 | P-48 |  | OG1 | [9 empty] | 57 | Ratio generator-/rotor speed
P-50 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-50 |  | OG1 | [9 empty] | 58 | Demand to stop by an external device
P-51 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-51 |  | OG1 | [9 empty] | 59 | Vibration switch
P-52 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-52 |  | OG1 | [9 empty] | 60 | Yaw limit switch activated
P-55 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-55 |  | OG1 | [9 empty] | 63 | Safety chain
P-56 | PWEPL | MSEDCL | 1.6 | 2.273% | Wind_F4 | P-56 |  | OG1 | [9 empty] | 65 | Main switch released
Wind_F1 | PWEPL | MSEDCL | 16 | 22.73% |  |  |  | OG1 | [9 empty] | 71 | Dirty gearing oil filter
Wind_F2 | PWEPL | MSEDCL | 19.2 | 27.27% |  |  |  | OG1 | [9 empty] | 72 | Gear oil temperature switching contact
Wind_F3 | PWEPL | MSEDCL | 14.4 | 20.45% |  |  |  | OG1 | [9 empty] | 75 | Generator bearing A overtemperature
Wind_F4 | PWEPL | MSEDCL | 20.8 | 29.55% |  |  |  | OG1 | [9 empty] | 76 | Generator bearing B overtemperature
[18 empty] | 77 | Gearbox oil overtemperature
[18 empty] | 78 | Outside temperature too low
[18 empty] | 81 | Shaft bearing overtemperature
[18 empty] | 82 | Yaw motor overtemperature
[18 empty] | 84 | Gearbox oil temperature too low
[18 empty] | 86 | Braking pad of secondary brake worn out
[18 empty] | 87 | Restart time delay
[18 empty] | 88 | Multiple overtemperature switch off
[18 empty] | 89 | Gearbox oil filter dirty (warning)
[18 empty] | 91 | Gearbox running hot in low stage
[18 empty] | 97 | Generator cooling air overtemperature
[18 empty] | 98 | Gearbox bearing overtemperature
[18 empty] | 99 | Generator overtemperature 1
[18 empty] | 100 | Generator overtemperature 2
[18 empty] | 101 | TopBox DIN21 motor protection aux contact string
[18 empty] | 102 | DTA DIN03 control breaker status
[18 empty] | 105 | Rotor CCU fault voltage
[18 empty] | 106 | Rotor CCU fault current
[18 empty] | 107 | Rotor CCU fault temperature
[18 empty] | 108 | Rotor locking
[18 empty] | 110 | Speed in the tower resonance range
[18 empty] | 112 | Feedback signal from CCU
[18 empty] | 113 | Line CCU fault voltage
[18 empty] | 114 | Line CCU fault current
[18 empty] | 115 | Line CCU fault temperature
[18 empty] | 116 | Line fault voltage
[18 empty] | 117 | Line fault frequency
[18 empty] | 118 | Emergency stop nacelle / hub
[18 empty] | 120 | Communication fault Pitch controller
[18 empty] | 121 | axis 1 fault pitch controller
[18 empty] | 122 | Collective fault pitch controller
[18 empty] | 124 | Pitch Overrun 0deg
[18 empty] | 125 | Pitch Overrun 90deg
[18 empty] | 127 | Generator power switch
[18 empty] | 129 | Generator speed not plausible
[18 empty] | 130 | Braking time rotor blade 1 too high
[18 empty] | 131 | Braking time rotor blade 2 too high
[18 empty] | 132 | Braking time rotor blade 3 too high
[18 empty] | 133 | Battery charging rotor blade drive
[18 empty] | 134 | Battery charging voltage not OK
[18 empty] | 135 | Battery test
[18 empty] | 136 | Limit switch 0deg-rotorblade angle unclear
[18 empty] | 137 | Limit switch 90deg-rotorblade defective
[18 empty] | 138 | Temperature warning pitch motor
[18 empty] | 139 | Overtemperature pitch motor
[18 empty] | 140 | Motor protection pitch motor
[18 empty] | 141 | Rotor CCU collective faults
[18 empty] | 142 | Line CCU collective faults
[18 empty] | 143 | Pulse sensor rotor monitor defect
[18 empty] | 144 | Blade angle asymmetry
[18 empty] | 145 | Pitch control deviation axis 1
[18 empty] | 146 | Turbine stopped due to calm
[18 empty] | 147 | Load shutdown
[18 empty] | 148 | Generator fan service switch
[18 empty] | 149 | axis 2 fault pitch controller
[18 empty] | 150 | axis 3 fault pitch controlle
[18 empty] | 152 | Obstruction light fault / failure
[18 empty] | 153 | Generator brushes worn
[18 empty] | 155 | Maintenance
[18 empty] | 156 | Repair
[18 empty] | 157 | Brake does not close
[18 empty] | 161 | Overvoltage protection triggered
[18 empty] | 163 | Torque deviation
[18 empty] | 164 | Maintenance switch pitch
[18 empty] | 165 | Service switch pitch
[18 empty] | 166 | Normal operation
[18 empty] | 167 | Voltage limiting activated
[18 empty] | 168 | yaw emergency stop
[18 empty] | 169 | Waiting for gearbox oil pressure
[18 empty] | 170 | Increasing speed with falling blade angle
[18 empty] | 171 | Service key brake release
[18 empty] | 173 | Low-noise operation
[18 empty] | 174 | Overtemperature transformer warning
[18 empty] | 175 | Overtemperature transformer disturbance
[18 empty] | 176 | Drive train vibration
[18 empty] | 177 | Tower vibration
[18 empty] | 178 | Fault battery charge switching shut down
[18 empty] | 179 | Successful battery test is needed
[18 empty] | 180 | Wind deviation
[18 empty] | 181 | Spinning position
[18 empty] | 182 | Start-up
[18 empty] | 183 | Load operation
[18 empty] | 184 | Shut down
[18 empty] | 185 | Manual operation pitch
[18 empty] | 186 | Manual operation speed
[18 empty] | 187 | Manual operation torque
[18 empty] | 188 | Manual operation line separation
[18 empty] | 189 | Manual operation yaw
[18 empty] | 190 | Container / nacelle temp.fault (not for CWE turbines)
[18 empty] | 191 | Manual operation generator fan
[18 empty] | 193 | aviation light system common alarm
[18 empty] | 194 | By-pass filter soiling
[18 empty] | 195 | Gearbox pressure loss by-pass filter
[18 empty] | 201 | PLC fault 24V Supply
[18 empty] | 203 | Fault temperature measurement
[18 empty] | 205 | Overtemperature cabinet
[18 empty] | 207 | Ground fault LVMD
[18 empty] | 208 | No communication Cu
[18 empty] | 212 | Battery voltage not OK axis 1
[18 empty] | 213 | Battery voltage not OK axis 2
[18 empty] | 214 | Battery voltage not OK axis 3
[18 empty] | 215 | Direction dependent shut-down
[18 empty] | 218 | Too Frequent cut-ins
[18 empty] | 220 | External stop caused by curtailment
[18 empty] | 221 | External power limitation
[18 empty] | 222 | Yaw runaway
[18 empty] | 223 | Blade angle not plausible axis 1
[18 empty] | 224 | Feedback error circuit breaker
[18 empty] | 235 | Power circuit breaker CCU released
[18 empty] | 237 | Generator overtemperature 3
[18 empty] | 250 | Temp. sensor error (shut down)
[18 empty] | 251 | Temp. sensor error (warning)
[18 empty] | 252 | Temp. not plausible
[18 empty] | 261 | Manual Hydraulic / Brake
[18 empty] | 269 | Reboot PLC
[18 empty] | 271 | Malfunction particle counter
[18 empty] | 272 | Shadow related shut down
[18 empty] | 273 | Too long manual / Service operation
[18 empty] | 274 | Pitch thyristor 1 fault
[18 empty] | 275 | Pitch thyristor 2 fault
[18 empty] | 276 | Pitch thyristor 3 fault
[18 empty] | 277 | Power limitation due to high temperature
[18 empty] | 278 | Shut-down low voltage
[18 empty] | 279 | Low voltage ride through
[18 empty] | 280 | Prepressure error, active brake
[18 empty] | 281 | Prepressure warning, active brake
[18 empty] | 282 | Test prepressure active brake
[18 empty] | 286 | Crow bar triggered CCU
[18 empty] | 287 | Power limitation CCU
[18 empty] | 288 | Response signal interrupt battery driven pitching
[18 empty] | 289 | Test measuring system
[18 empty] | 290 | Idling in speed control
[18 empty] | 291 | Undertemperature Cabinet
[18 empty] | 294 | Warning adv controls sensors
[18 empty] | 295 | Heat up state
[18 empty] | 297 | Turbine heat up error
[18 empty] | 302 | Brake pad worn, warning
[18 empty] | 306 | Manual operation yaw hydraulic
[18 empty] | 308 | Idling command at WTG
[18 empty] | 310 | Fault reset
[18 empty] | 313 | Cabinet overtemperature warning
[18 empty] | 314 | Power limitation freq. dependent
[18 empty] | 317 | Undertemperature slipring
[18 empty] | 319 | Service Switch Rotorlock
[18 empty] | 324 | Activation rotor lock
[18 empty] | 333 | Block restart due to grid frequency
[18 empty] | 334 | Circuit breaker maintenance necessary
[18 empty] | 335 | Generator overspeed 2
[18 empty] | 336 | Rotor overspeed 2
[18 empty] | 337 | Line CCU temperature warning
[18 empty] | 338 | Rotor CCU temperature warning
[18 empty] | 340 | Pitch control deviation Axis 2
[18 empty] | 341 | Pitch control deviation Axis 3
[18 empty] | 342 | Blade Angle not plausible Axis 2
[18 empty] | 343 | Blade Angle not plausible Axis 3
[18 empty] | 344 | Pitch malfunction 2 or 3 blades
[18 empty] | 345 | Battery drive after grid fault
[18 empty] | 346 | Rotor speeds not plausible
[18 empty] | 348 | Service stop
[18 empty] | 349 | Service stop with fault
[18 empty] | 352 | Communication fault wind measurement device
[18 empty] | 353 | Malfunction wind measurement device
[18 empty] | 355 | Power limitation fault adv.Controls sensor
[18 empty] | 357 | Grid voltage drop CU
[18 empty] | 359 | Internal Pitch Mode
[18 empty] | 360 | Internal Pitch Mode Implausible
[18 empty] | 361 | Power limitation adv Power limitation adv control hub offsets
[18 empty] | 362 | Calibrating ALC gains
[18 empty] | 363 | Mapping ALC hub offsets
[18 empty] | 365 | Service switch pitch unplausible
[18 empty] | 366 | Aero balance worsening
[18 empty] | 368 | MSF bending out of threshold
[18 empty] | 371 | Pitch limitation low power avoidance
[18 empty] | 377 | Communication to the frequency converter is not active
[18 empty] | 381 | Communication fault pitch controller Axis 1
[18 empty] | 382 | Communication fault pitch controller Axis 2
[18 empty] | 383 | Communication fault pitch controller Axis 3
[18 empty] | 394 | Yaw Map pending
[18 empty] | 395 | Yaw Mapping
[18 empty] | 396 | Yaw Mapping Error
[17 empty] | New Added | 424 | System re-initialization after grid outage
[18 empty] | 430 | Yaw tooth sensor 1 timeout
[18 empty] | 431 | Yaw tooth sensor 2 timeout
[18 empty] | 907 | Yaw Brake Voltage 230Volt not OK
[18 empty] | 367 | CCU fault at abnormal grid condition
[18 empty] | VCB_OC | Internal Line VCB tripped in over current
[18 empty] | Y_Sens_Err | Yaw sensor error
[18 empty] | CE100001 | Manual Stop
[18 empty] | CE100002 | Major BD - Blade
[18 empty] | CE100003 | Major BD - Transformer
[18 empty] | CE100004 | Major BD - Generator
[18 empty] | CE100005 | Major BD - Gearbox
[18 empty] | CE100006 | Major BD - Main Bearing
[18 empty] | CE100007 | Transmission Line Related work
[18 empty] | CE100008 | General Work Stoppage
[18 empty] | CE100009 | Major BD - Power Cable
[18 empty] | CE100011 | Major BD - DFIG
[18 empty] | CE100012 | Major BD - Foundation
[18 empty] | CE100013 | Theft
[18 empty] | CE100010 | Manual Stop - Preventive Maintenance Activity
[18 empty] | CE100014 | Manual Stop - Audit
[18 empty] | CE100015 | Manual Stop - Safety Related
[18 empty] | CE100016 | Manual Stop - Blade Cleaning
[18 empty] | CE100017 | UPS breakdown
[18 empty] | 123 | Generator carbon brush warn

## WTG Reactive Power
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49
Date | Financial Year | Calendar Year | Month Year | P-01 | P-02 | P-03 | P-04 | P-05 | P-06 | P-07 | P-08 | P-09 | P-10 | P-11 | P-12 | P-13 | P-14 | P-15 | P-16 | P-17 | P-18 | P-19 | P-20 | P-22 | P-23 | P-25 | P-26 | P-27 | P-28 | P-31 | P-32 | P-34 | P-37 | P-38 | P-40 | P-41 | P-42 | P-43 | P-45 | P-46 | P-47 | P-48 | P-50 | P-51 | P-52 | P-55 | P-56 | Total Reactive Power (kVArH)
2025-03-29 | 2025 | 2025 | 2025-03-01 | [44 empty] | 0
2025-03-30 | 2025 | 2025 | 2025-03-01 | [44 empty] | 0
2025-03-31 | 2025 | 2025 | 2025-04-01 | [44 empty] | 0
2025-04-01 | 2026 | 2025 | 2025-04-01 | 721.7855 | 706.556 | 649.4168 | 1211.4642 | 927.1955 | 923.1035 | 457.2925 | 847.4782 | 717.8808 | 1008.006 | 1258.9807 | 1222.2958 | 1134.9852 | 1084.4103 | 898.1967 | 845.6648 | 759.9462 | 547.7623 | 994.5882 | 832.4698 | 1290.2067 | 1277.826 | 1090.8723 | 1058.623 | 592.3165 | 982.1397 | 599.5368 | 424.3102 | 1014.0687 | 450.91 | 926.223 | 672.3055 | 890.8138 | 769.964 | 1258.6622 | 1286.8588 | 906.5793 | 699.6832 | 802.4002 | 384.6693 | 475.28 | 544.0825 | 639.4147 | 531.5318 | 37.3188
2025-04-02 | 2026 | 2025 | 2025-04-01 | 1279.0202 | 1000.0012 | 826.3672 | 974.136 | 2179.488 | 1830.5527 | 1022.2077 | 940.6755 | 648.2487 | 1004.6227 | 1201.2533 | 1484.9563 | 1740.974 | 1764.889 | 1291.6612 | 1538.5458 | 1692.3157 | 1164.2563 | 2025.9788 | 1739.0328 | 949.6493 | 981.2805 | 1364.3895 | 1696.8098 | 1684.1342 | 1635.549 | 861.6737 | 1131.5123 | 711.7767 | 1502.0345 | 1956.7857 | 1168.4542 | 2110.2432 | 1617.4118 | 1506.7738 | 2441.3997 | 1560.4152 | 1820.044 | 1734.4628 | 1280.416 | 1536.9065 | 1486.0708 | 1869.9907 | 1636.3545 | 63.5937
2025-04-03 | 2026 | 2025 | 2025-04-01 | 554.4818 | 496.6758 | 503.4407 | 503.5803 | 461.6213 | 345.3613 | 403.0327 | 207.971 | 150.5168 | 181.7885 | 187.0547 | 200.022 | 200.4837 | 104.6352 | 108.9352 | 136.3832 | 171.5277 | 501.6038 | 188.559 | 155.3565 | 442.681 | 479.5362 | 261.4628 | 302.9595 | 332.9407 | 295.0062 | 258.4425 | 254.4163 | 508.0893 | 337.8037 | 211.6938 | 294.4058 | 416.0837 | 507.034 | 280.368 | 575.4567 | 529.6665 | 474.1397 | 516.1133 | 208.4443 | 343.6465 | 340.8348 | 540.7648 | 489.9962 | 14.965
2025-04-04 | 2026 | 2025 | 2025-04-01 | 489.2198 | 529.7375 | 586.2853 | 564.4553 | 625.9117 | 482.957 | 493.733 | 420.319 | 304.201 | 337.3478 | 339.1455 | 342.3332 | 405.7633 | 248.7777 | 127.5992 | 165.7818 | 220.4193 | 603.6432 | 226.8388 | 168.4955 | 568.778 | 634.6315 | 525.7253 | 483.5422 | 568.7925 | 523.5513 | 651.1248 | 412.3463 | 520.4463 | 601.5575 | 226.2915 | 285.0857 | 566.729 | 526.5558 | 529.306 | 875.848 | 732.8268 | 601.3043 | 561.9275 | 282.435 | 496.273 | 574.691 | 638.1777 | 607.9772 | 20.6789
2025-04-05 | 2026 | 2025 | 2025-04-01 | 81.5366 | 88.2896 | 97.7142 | 94.0759 | 104.3186 | 80.4928 | 82.2888 | 70.0532 | 50.7002 | 56.2246 | 56.5243 | 57.0555 | 67.6272 | 41.4629 | 21.2665 | 27.6303 | 36.7366 | 100.6072 | 37.8065 | 28.0826 | 94.7963 | 105.7719 | 87.6209 | 80.5904 | 94.7987 | 87.2586 | 108.5208 | 68.7244 | 86.7411 | 100.2596 | 37.7152 | 47.5143 | 94.4548 | 87.7593 | 88.2177 | 145.9747 | 122.1378 | 100.2174 | 93.6546 | 47.0725 | 82.7122 | 95.7818 | 106.3629 | 101.3295 | 3.4465
2025-04-06 | 2026 | 2025 | 2025-04-01 | 13.5894 | 14.7149 | 16.2857 | 15.6793 | 17.3864 | 13.4155 | 13.7148 | 11.6755 | 8.45 | 9.3708 | 9.4207 | 9.5093 | 11.2712 | 6.9105 | 3.5444 | 4.6051 | 6.1228 | 16.7679 | 6.3011 | 4.6804 | 15.7994 | 17.6287 | 14.6035 | 13.4317 | 15.7998 | 14.5431 | 18.0868 | 11.4541 | 14.4568 | 16.7099 | 6.2859 | 7.919 | 15.7425 | 14.6266 | 14.7029 | 24.3291 | 20.3563 | 16.7029 | 15.6091 | 7.8454 | 13.7854 | 15.9636 | 17.7272 | 16.8883 | 0.57441
2025-04-07 | 2026 | 2025 | 2025-04-01 | 766.1405 | 953.848 | 977.1735 | 218.835 | 402.0165 | 71.0122 | 604.976 | 210.8173 | 141.7167 | 174.9242 | 186.0918 | 246.5557 | 260.5342 | 296.4995 | 275.0082 | 312.4618 | 322.5043 | 792.7053 | 383.831 | 333.2443 | 639.3802 | 759.6718 | 376.4815 | 391.3165 | 447.5158 | 418.6393 | 1054.543 | 442.2398 | 651.2677 | 600.4277 | 346.387 | 90.3937 | 89.7267 | 177.1713 | 437.7782 | 159.2613 | 154.8428 | 141.25 | 134.819 | 511.1667 | 768.8697 | 804.645 | 819.6978 | 661.0078 | 19.0094
2025-04-08 | 2026 | 2025 | 2025-04-01 | 322.8392 | 282.5615 | 252.7505 | 166.8033 | 257.2093 | 246.5115 | 265.0405 | 123.1237 | 67.9717 | 70.8108 | 76.4518 | 98.8395 | 112.1115 | 103.0065 | 76.2238 | 78.0282 | 96.8097 | 267.808 | 148.2382 | 104.9922 | 228.0207 | 243.1193 | 164.6447 | 150.2137 | 183.5645 | 187.9168 | 132.58 | 77.8038 | 116.6928 | 184.8913 | 99.639 | 161.6448 | 336.349 | 255.3023 | 147.0575 | 329.405 | 242.273 | 196.0913 | 234.4248 | 79.8872 | 143.5565 | 193.2657 | 393.9905 | 279.1617 | 7.9796
2025-04-09 | 2026 | 2025 | 2025-04-01 | 849.8133 | 757.3283 | 541.2778 | 580.889 | 604.3397 | 594.166 | 774.0387 | 311.0168 | 198.2693 | 243.0448 | 297.5775 | 330.3118 | 350.6927 | 375.0405 | 349.0463 | 423.0813 | 449.911 | 432.8312 | 448.4453 | 405.452 | 557.9507 | 439.6465 | 333.3012 | 417.1175 | 413.441 | 417.847 | 443.9377 | 322.2847 | 606.307 | 417.1 | 453.239 | 418.2953 | 210.5095 | 615.0903 | 383.0875 | 636.4005 | 360.6735 | 419.14 | 374.594 | 411.0922 | 438.6935 | 458.0137 | 801.5085 | 850.621 | 20.5165
2025-04-10 | 2026 | 2025 | 2025-04-01 | 2114.2597 | 2469.9707 | 1278.5827 | 1552.1752 | 1427.267 | 1568.134 | 2346.9182 | 728.8465 | 402.8562 | 420.008 | 566.8998 | 723.704 | 929.5363 | 888.341 | 867.8032 | 904.208 | 996.6408 | 1871.2138 | 1019.6708 | 845.1308 | 1368.2078 | 1056.7385 | 755.3748 | 867.1655 | 879.7385 | 821.7757 | 851.9553 | 271.6058 | 1519.342 | 392.4403 | 960.6945 | 859.5238 | 1392.5213 | 1716.1448 | 730.8452 | 1851.0557 | 1830.6425 | 1329.832 | 1792.784 | 527.9238 | 565.9292 | 627.124 | 2215.041 | 2454.979 | 51.5616
2025-04-11 | 2026 | 2025 | 2025-04-01 | 1608.4338 | 1381.5393 | 1246.4048 | 1233.9242 | 1655.1192 | 1243.6768 | 874.8345 | 713.3523 | 510.9652 | 649.7318 | 750.9972 | 898.927 | 895.5882 | 908.6788 | 877.1323 | 1011.4342 | 1175.6393 | 1520.1668 | 1085.9738 | 949.4033 | 1250.7088 | 1258.6677 | 974.6503 | 1072.6845 | 1146.301 | 1054.384 | 989.6468 | 93.6302 | 1050.2753 | 156.0095 | 1266.753 | 816.2688 | 1571.87 | 1707.7953 | 920.553 | 1421.6427 | 1500.4217 | 1326.6895 | 1558.4938 | 599.0033 | 619.6803 | 712.9038 | 1282.2733 | 1461.9598 | 47.0052
2025-04-12 | 2026 | 2025 | 2025-04-01 | 1891.5332 | 1542.1888 | 1482.765 | 1458.7167 | 1396.8868 | 1039.9977 | 1479.2027 | 735.7097 | 529.0943 | 683.7618 | 809.7427 | 949.3212 | 969.2393 | 1048.0093 | 985.904 | 1226.3092 | 1386.881 | 1621.3808 | 1232.396 | 1066.126 | 1366.1548 | 1616.0542 | 990.9915 | 1091.9385 | 1276.1627 | 1244.5188 | 1147.5052 | 634.194 | 1342.5977 | 807.2152 | 1470.8357 | 797.0488 | 1292.2252 | 1654.4412 | 1175.968 | 2121.3305 | 2039.9872 | 1705.4485 | 1645.064 | 635.0845 | 482.0728 | 971.9917 | 1909.6392 | 1559.7473 | 54.5134
2025-04-13 | 2026 | 2025 | 2025-04-01 | 2080.7448 | 1721.4688 | 1831.614 | 1113.559 | 1107.5483 | 921.0442 | 1962.5255 | 387.7745 | 271.2782 | 304.4303 | 367.9083 | 434.9452 | 410.4843 | 444.565 | 398.7813 | 464.851 | 591.967 | 1817.9848 | 578.6202 | 591.2592 | 1585.4322 | 1704.2888 | 768.7523 | 792.3302 | 952.3043 | 767.52 | 1393.5975 | 763.9332 | 1085.2165 | 1107.2802 | 684.7227 | 408.2552 | 1046.9242 | 1612.7378 | 773.671 | 1569.5888 | 1224.4425 | 1229.485 | 1290.5342 | 641.3092 | 1128.9767 | 1597.8045 | 2266.8295 | 1681.5147 | 45.8808
2025-04-14 | 2026 | 2025 | 2025-04-01 | 1760.998 | 2114.2968 | 2290.731 | 1070.9975 | 1129.1787 | 1090.5463 | 1294.9527 | 658.2933 | 467.1207 | 488.0563 | 525.349 | 581.9282 | 573.2733 | 490.7425 | 416.1177 | 506.4842 | 592.0163 | 1513.3087 | 511.0275 | 412.007 | 1051.1225 | 1189.4933 | 743.9377 | 713.4633 | 856.7233 | 759.0162 | 2129.8542 | 1034.7615 | 1207.254 | 1279.665 | 584.9233 | 675.7923 | 1113.8685 | 1264.3828 | 755.8178 | 1596.1132 | 1459.4208 | 1136.8318 | 1247.9865 | 1124.5065 | 1487.9262 | 1738.2153 | 1553.4983 | 1229.1473 | 46.4211
2025-04-15 | 2026 | 2025 | 2025-04-01 | 1164.4358 | 1117.97 | 1274.8743 | 414.202 | 687.504 | 602.9888 | 883.9807 | 179.564 | 94.9353 | 75.0628 | 74.1143 | 102.2182 | 119.6953 | 143.6773 | 124.1687 | 168.47 | 236.981 | 761.9668 | 125.4875 | 98.1012 | 694.7813 | 868.648 | 264.8942 | 273.4003 | 364.5635 | 321.4822 | 1023.286 | 551.3152 | 377.9115 | 599.6252 | 197.0737 | 264.8218 | 696.5588 | 781.5178 | 281.5758 | 664.6138 | 526.2702 | 555.97 | 537.1208 | 1017.6382 | 891.6502 | 1041.3667 | 957.715 | 627.8675 | 22.8321
2025-04-16 | 2026 | 2025 | 2025-04-01 | 435.7065 | 290.2683 | 253.6542 | 379.8172 | 432.5345 | 295.5975 | 382.8972 | 167.4968 | 118.3662 | 196.0182 | 225.8325 | 266.0245 | 288.2907 | 269.2752 | 245.527 | 269.7627 | 341.9405 | 402.4802 | 284.9163 | 270.4168 | 346.2877 | 317.9907 | 231.19 | 279.3553 | 310.8142 | 313.2643 | 158.141 | 132.7457 | 353.7523 | 162.1092 | 343.414 | 193.4893 | 383.5737 | 448.8047 | 253.7585 | 249.5773 | 323.2482 | 327.5302 | 387.5435 | 191.9708 | 190.2013 | 242.3032 | 377.0317 | 194.2082 | 12.5291
2025-04-17 | 2026 | 2025 | 2025-04-01 | 1972.8162 | 1498.9122 | 1482.4532 | 1133.7433 | 1727.8893 | 1778.6953 | 1717.9773 | 616.2722 | 448.183 | 546.5468 | 563.8882 | 592.9608 | 618.525 | 638.4598 | 537.7372 | 644.345 | 710.5653 | 1677.4428 | 703.9098 | 612.0318 | 1350.4222 | 1502.7798 | 967.427 | 941.8353 | 1152.2888 | 1002.564 | 1215.1803 | 723.436 | 1118.2323 | 1122.337 | 694.6005 | 726.9845 | 1867.0477 | 2293.482 | 880.6715 | 1905.7312 | 2019.7993 | 1997.4907 | 2016.6897 | 733.5103 | 1206.4843 | 1573.9703 | 1848.9403 | 1985.833 | 53.0711
2025-04-18 | 2026 | 2025 | 2025-04-01 | 2078.1465 | 1629.2487 | 1619.6813 | 1382.1412 | 1666.8478 | 1081.0132 | 1837.0563 | 689.8722 | 454.3758 | 599.512 | 674.0715 | 695.7633 | 715.1133 | 714.5557 | 598.4747 | 806.5745 | 860.2965 | 1980.8495 | 866.2475 | 737.7935 | 1541.7563 | 1540.6817 | 1056.4167 | 1043.2535 | 1140.638 | 946.4703 | 1077.4003 | 640.8297 | 1217.0738 | 927.792 | 927.3877 | 550.5767 | 1488.7143 | 1596.0592 | 923.5377 | 962.3747 | 1296.3575 | 1275.275 | 1420.7282 | 847.6945 | 1057.7462 | 1358.1933 | 1976.6917 | 1852.6223 | 50.3539
2025-04-19 | 2026 | 2025 | 2025-04-01 | 2722.8897 | 2608.8077 | 2678.8308 | 1666.5987 | 2052.902 | 1482.2565 | 2153.1465 | 767.5222 | 565.3922 | 692.2865 | 709.7587 | 741.204 | 738.5128 | 779.8368 | 733.6333 | 903.6823 | 994.0512 | 2510.202 | 986.9905 | 870.2955 | 1840.5067 | 2120.023 | 1175.3282 | 1207.3363 | 1289.7187 | 1116.9925 | 2355.6053 | 811.8427 | 1597.0257 | 1152.7723 | 1136.702 | 872.016 | 1918.8392 | 1793.993 | 1082.1028 | 1776.825 | 1055.4002 | 1629.2565 | 1782.7552 | 819.7858 | 1271.6648 | 1712.0558 | 2335.7152 | 2070.3727 | 63.2834
2025-04-20 | 2026 | 2025 | 2025-04-01 | 2862.7638 | 2556.8227 | 2478.6698 | 1370.2927 | 1435.9765 | 1130.4698 | 2483.1532 | 675.6132 | 425.6995 | 494.8247 | 521.8198 | 597.1288 | 553.6932 | 585.2047 | 551.2635 | 620.1447 | 721.071 | 2527.9688 | 747.8802 | 705.8115 | 1992.7833 | 2342.4738 | 1116.6205 | 1117.8915 | 1336.0983 | 1082.8585 | 2025.8425 | 1038.3293 | 1274.1183 | 1506.588 | 837.2748 | 671.938 | 1369.0402 | 1570.0682 | 1084.7992 | 1960.0612 | 1560.1232 | 1458.2888 | 1464.8512 | 1294.6817 | 1400.3492 | 2231.6618 | 2756.8547 | 2109.3882 | 60.6493
2025-04-21 | 2026 | 2025 | 2025-04-01 | 1430.9505 | 1604.0968 | 1691.2038 | 824.112 | 761.8 | 651.977 | 1297.8167 | 405.2408 | 211.8423 | 256.3237 | 281.8137 | 355.1842 | 336.2593 | 360.6883 | 329.808 | 358.3427 | 389.2835 | 1526.446 | 472.1967 | 411.1158 | 1304.596 | 1534.3645 | 637.1972 | 630.8513 | 806.6393 | 662.0367 | 1580.6055 | 1091.2405 | 759.7673 | 1379.9302 | 459.4442 | 409.844 | 725.677 | 991.624 | 810.581 | 1332.1655 | 974.9922 | 901.5143 | 880.1583 | 1193.5423 | 1133.4868 | 1710.4473 | 1529.873 | 1264.9947 | 38.6621
2025-04-22 | 2026 | 2025 | 2025-04-01 | 707.6333 | 636.7458 | 517.6427 | 692.7192 | 414.757 | 420.0403 | 668.9273 | 487.3283 | 377.208 | 354.2953 | 604.3208 | 661.029 | 643.0283 | 572.9013 | 536.8937 | 589.6428 | 668.0233 | 712.3203 | 700.034 | 636.1015 | 839.473 | 819.653 | 622.5835 | 694.6297 | 768.4103 | 713.6578 | 424.6633 | 178.982 | 631.254 | 245.3877 | 730.3728 | 292.2763 | 405.6548 | 381.8617 | 648.7917 | 656.4942 | 506.8318 | 371.7525 | 423.7307 | 253.6452 | 229.415 | 335.7673 | 753.8975 | 649.1158 | 24.1799
2025-04-23 | 2026 | 2025 | 2025-04-01 | 1505.4293 | 1195.8597 | 1135.243 | 395.0345 | 1115.4778 | 840.7738 | 1357.136 | 200.3623 | 383.4843 | 522.4017 | 608.5028 | 685.6587 | 702.2625 | 675.0713 | 646.8023 | 704.6632 | 799.69 | 1409.1922 | 717.6608 | 653.4078 | 579.5885 | 601.2973 | 316.1223 | 305.6963 | 372.5237 | 260.9138 | 823.8888 | 541.9567 | 276.6703 | 753.4847 | 768.4938 | 525.1638 | 1042.3613 | 1263.4588 | 282.9478 | 1234.4692 | 1224.0398 | 266.6348 | 1146.3632 | 736.6848 | 763.243 | 963.03 | 1592.4295 | 1394.7382 | 34.2903
2025-04-24 | 2026 | 2025 | 2025-04-01 | 1505.4293 | 1195.8597 | 1135.243 | 395.0345 | 1115.4778 | 840.7738 | 1357.136 | 200.3623 | 383.4843 | 522.4017 | 608.5028 | 685.6587 | 702.2625 | 675.0713 | 646.8023 | 704.6632 | 799.69 | 1409.1922 | 717.6608 | 653.4078 | 579.5885 | 601.2973 | 316.1223 | 305.6963 | 372.5237 | 260.9138 | 823.8888 | 541.9567 | 276.6703 | 753.4847 | 768.4938 | 525.1638 | 1042.3613 | 1263.4588 | 282.9478 | 1234.4692 | 1224.0398 | 266.6348 | 1146.3632 | 736.6848 | 763.243 | 963.03 | 1592.4295 | 1394.7382 | 34.2903
2025-04-25 | 2026 | 2025 | 2025-04-01 | 1342.3078 | 957.6253 | 820.5778 | 1061.9793 | 1071.0782 | 720.2827 | 1200.8175 | 466.7165 | 239.3713 | 267.4797 | 308.4397 | 342.2948 | 409.8095 | 467.0943 | 448.573 | 546.1183 | 671.1193 | 1271.1873 | 683.2643 | 609.121 | 1207.4765 | 1221.4202 | 722.6425 | 729.218 | 866.5518 | 805.2377 | 687.4973 | 253.8692 | 827.3202 | 520.7445 | 758.538 | 249.7898 | 933.0615 | 1103.5077 | 822.0845 | 1146.6617 | 1060.1327 | 965.4663 | 1297.36 | 361.3475 | 426.3833 | 647.8698 | 1471.076 | 1502.4093 | 34.4929
2025-04-26 | 2026 | 2025 | 2025-04-01 | 1141.5353 | 923.9072 | 802.7843 | 853.1982 | 927.1827 | 336.6265 | 636.4075 | 490.2338 | 402.2518 | 451.1557 | 500.6875 | 550.7045 | 602.25 | 163.0742 | 173.9693 | 190.9832 | 174.1897 | 1011.5827 | 221.1958 | 173.9317 | 836.6625 | 779.0373 | 623.2628 | 675.5605 | 761.0622 | 658.621 | 835.5803 | 402.3182 | 757.1542 | 663.9462 | 144.1933 | 596.5015 | 919.2272 | 1184.9717 | 682.5078 | 1001.618 | 1041.0212 | 947.5315 | 1077.3883 | 349.7342 | 509.1333 | 670.2403 | 1147.9367 | 1068.3587 | 29.0614
2025-04-27 | 2026 | 2025 | 2025-04-01 | 772.6577 | 576.3972 | 575.5663 | 516.271 | 816.8423 | 548.4598 | 596.8792 | 295.245 | 213.2803 | 297.6057 | 345.7778 | 404.554 | 434.3018 | 400.1512 | 387.047 | 403.7878 | 465.8558 | 682.3127 | 435.9282 | 405.1203 | 586.5062 | 549.0692 | 454.36 | 500.6338 | 558.9923 | 501.6048 | 484.2567 | 311.5283 | 523.9998 | 423.981 | 483.6585 | 333.014 | 449.4668 | 881.241 | 482.9005 | 688.5557 | 712.636 | 713.8075 | 796.788 | 396.3142 | 433.373 | 532.5863 | 766.49 | 774.0765 | 22.9139
2025-04-28 | 2026 | 2025 | 2025-04-01 | 772.6577 | 576.3972 | 575.5663 | 516.271 | 816.8423 | 548.4598 | 596.8792 | 295.245 | 213.2803 | 297.6057 | 345.7778 | 404.554 | 434.3018 | 400.1512 | 387.047 | 403.7878 | 465.8558 | 682.3127 | 435.9282 | 405.1203 | 586.5062 | 549.0692 | 454.36 | 500.6338 | 558.9923 | 501.6048 | 484.2567 | 311.5283 | 523.9998 | 423.981 | 483.6585 | 333.014 | 449.4668 | 881.241 | 482.9005 | 688.5557 | 712.636 | 713.8075 | 796.788 | 396.3142 | 433.373 | 532.5863 | 766.49 | 774.0765 | 22.9139
2025-04-29 | 2026 | 2025 | 2025-04-01 | 1560.4042 | 1329.7775 | 1080.5257 | 1083.6692 | 1356.5602 | 1046.659 | 1238.1288 | 553.5475 | 408.4417 | 539.6457 | 596.5655 | 679.3695 | 682.371 | 687.4558 | 658.9067 | 782.9637 | 892.0457 | 1634.1247 | 864.4613 | 711.0245 | 1052.359 | 1190.8057 | 816.2277 | 933.3618 | 1061.0877 | 912.841 | 695.8552 | 359.3957 | 976.1777 | 559.5995 | 859.5272 | 249.2282 | 1290.2077 | 1610.1578 | 748.8715 | 1336.8385 | 1281.2798 | 1266.9823 | 1459.8042 | 403.8873 | 492.5062 | 662.7975 | 1416.8055 | 1400.1438 | 41.4234
2025-04-30 | 2026 | 2025 | 2025-05-01 | 2636.7143 | 2208.6975 | 2127.2432 | 1695.6358 | 2056.9987 | 1534.8863 | 2086.4805 | 654.374 | 504.9968 | 620.1455 | 656.6592 | 619.4683 | 711.4377 | 782.906 | 752.469 | 886.5908 | 970.8263 | 2382.1197 | 922.5835 | 726.2488 | 1725.4717 | 1957.094 | 1152.0232 | 1223.632 | 1362.8792 | 1159.3218 | 1753.5925 | 854.0923 | 1596.4583 | 1144.0068 | 1025.1497 | 750.277 | 1967.0767 | 2065.9718 | 1080.9808 | 1675.2665 | 1551.2895 | 1637.1128 | 1833.6532 | 696.9585 | 1401.3903 | 1799.5333 | 2491.8758 | 2067.6248 | 61.5102
2025-05-01 | 2026 | 2025 | 2025-05-01 | 2769.0955 | 2678.2778 | 2886.2608 | 1881.964 | 1955.3052 | 1484.6278 | 2409.6515 | 632.6983 | 376.2025 | 436.0105 | 451.3138 | 512.7787 | 512.037 | 567.8458 | 544.7223 | 644.2347 | 902.3568 | 2515.4775 | 764.0413 | 711.7403 | 2312.384 | 2569.8947 | 1114.3947 | 1070.2673 | 1283.0125 | 975.684 | 2491.1845 | 1074.3277 | 1669.3173 | 1524.1458 | 927.1267 | 626.6207 | 1792.999 | 2147.1847 | 1070.2182 | 2270.9492 | 1760.621 | 1692.9672 | 1754.4548 | 1639.0407 | 1928.2032 | 2523.9095 | 2965.3643 | 2171.5975 | 66.9925
2025-05-02 | 2026 | 2025 | 2025-05-01 | 3635.8133 | 3561.94 | 3863.5488 | 1761.8272 | 2677.8895 | 2947.3107 | 3172.9808 | 1070.1908 | 725.7755 | 781.9655 | 816.1525 | 921.5865 | 940.5352 | 1097.3277 | 1101.1423 | 1567.5758 | 1664.445 | 3186.4858 | 1351.0998 | 1033.9712 | 2183.2717 | 2856.9695 | 1516.3417 | 1518.6858 | 1795.4558 | 1684.6347 | 3743.7538 | 2080.3363 | 1966.847 | 2738.7663 | 1405.954 | 1457.9387 | 2963.6228 | 3441.1665 | 1510.5095 | 3774.8488 | 3507.2212 | 3175.5748 | 3105.6547 | 2699.206 | 2875.7877 | 3491.4565 | 3452.3818 | 2937.4417 | 99.7634
2025-05-03 | 2026 | 2025 | 2025-05-01 | 3192.2992 | 3465.025 | 3522.5752 | 2322.4707 | 2763.052 | 2686.442 | 2439.9805 | 1117.7605 | 1003.53 | 1043.5332 | 1050.9515 | 1027.5568 | 1037.3063 | 1048.2038 | 1006.4512 | 1139.3343 | 1317.8508 | 3244.2895 | 1396.4378 | 1301.477 | 2247.997 | 2763.2198 | 1567.8518 | 1552.7533 | 1743.8287 | 1562.3963 | 3438.0475 | 2267.6192 | 2776.5668 | 2828.1383 | 1604.7577 | 2091.0747 | 2866.3547 | 2964.5378 | 1452.508 | 3796.257 | 3571.4975 | 2946.9928 | 2942.43 | 1820.0212 | 2563.9478 | 2812.1283 | 2999.8795 | 2493.5985 | 96.8009
2025-05-04 | 2026 | 2025 | 2025-05-01 | 2912.6513 | 2691.9805 | 2363.4183 | 3021.562 | 3578.7297 | 3305.4008 | 2505.4768 | 1039.3208 | 976.2073 | 1108.776 | 1203.0945 | 1349.6293 | 1171.0998 | 1295.2288 | 1154.9283 | 1385.119 | 1469.4135 | 3309.0897 | 1459.947 | 1247.7488 | 2579.8973 | 3084.5385 | 1727.9383 | 1789.0272 | 1947.58 | 1664.8685 | 2652.5443 | 2141.9397 | 3184.0918 | 2928.3898 | 1695.9543 | 2173.721 | 3614.1863 | 3520.468 | 1751.3677 | 4173.4835 | 4010.3185 | 3478.1203 | 3456.3465 | 866.074 | 1609.9667 | 2150.098 | 3089.2285 | 3015.6313 | 100.8546
2025-05-05 | 2026 | 2025 | 2025-05-01 | 3489.8155 | 3695.5155 | 3732.9093 | 2669.0658 | 2470.979 | 2153.7322 | 2417.1913 | 756.6178 | 829.578 | 1008.9793 | 1113.2725 | 1224.799 | 1158.9653 | 1126.7583 | 1010.4368 | 1164.7913 | 1447.1667 | 3277.4523 | 1311.0528 | 1126.8212 | 2603.3745 | 3088.4918 | 1600.3347 | 1673.9815 | 1904.0848 | 1618.6278 | 3548.7738 | 1915.0052 | 2862.9035 | 2504.1575 | 1595.5933 | 1450.7693 | 2422.1705 | 2745.9005 | 1708.8077 | 3144.1272 | 2879.0488 | 2490.1527 | 2472.1532 | 1308.8187 | 2160.5127 | 2748.0033 | 3109.7725 | 2488.9073 | 93.2304
2025-05-06 | 2026 | 2025 | 2025-05-01 | 2575.6895 | 2385.083 | 1967.9995 | 2063.7697 | 2218.2333 | 2078.7282 | 1635.108 | 947.3103 | 1007.0768 | 1242.5617 | 1264.0975 | 1305.9703 | 1227.0705 | 1231.9077 | 1145.8388 | 1307.2853 | 1424.0315 | 2317.5282 | 1253.5958 | 1071.9403 | 1879.0558 | 2062.685 | 1360.1533 | 1451.4268 | 1546.625 | 1390.8668 | 2091.082 | 1468.7155 | 2144.943 | 1934.397 | 1475.229 | 1484.4492 | 2178.5495 | 2327.803 | 1505.8515 | 2777.5787 | 2727.5193 | 2418.8175 | 2413.1078 | 801.968 | 1613.1078 | 1839.0877 | 2501.23 | 2053.9558 | 77.119
2025-05-07 | 2026 | 2025 | 2025-05-01 | 3167.0492 | 2323.4595 | 2539.6637 | 2376.6853 | 3364.5237 | 2855.5405 | 2300.885 | 1565.302 | 1333.5392 | 1919.5543 | 2154.2375 | 2389.3745 | 2182.835 | 1978.9248 | 1749.1697 | 2029.0158 | 1957.288 | 2537.0852 | 1963.639 | 1620.0067 | 2184.2623 | 2305.2673 | 1918.3187 | 2091.9832 | 2348.2115 | 2055.7453 | 2286.2375 | 1985.6512 | 2387.709 | 2453.6388 | 2019.6455 | 2140.363 | 3354.5283 | 3302.5357 | 1732.3578 | 3803.0048 | 3891.3752 | 3284.6317 | 3403.6492 | 1747.0783 | 2520.8648 | 2608.574 | 3390.2357 | 2985.8745 | 106.5095
2025-05-08 | 2026 | 2025 | 2025-05-01 | 4065.4567 | 3435.2857 | 2766.1313 | 3294.3103 | 3728.4225 | 3987.7822 | 3706.0017 | 2228.0403 | 1399.5235 | 1508.1715 | 1651.0942 | 2483.253 | 2551.7488 | 2441.0623 | 1881.8767 | 2447.3368 | 2342.2658 | 2906.3697 | 2215.9842 | 1977.976 | 3058.4283 | 2638.9248 | 2365.4577 | 1451.2468 | 2444.7693 | 2044.4482 | 2278.2347 | 2349.806 | 3179.3162 | 2805.5953 | 2081.0682 | 2820.0562 | 3705.4852 | 3115.2645 | 2056.214 | 4720.8912 | 4424.1213 | 2863.245 | 3996.1732 | 2593.5677 | 3003.584 | 3319.5478 | 4639.7533 | 4285.2592 | 125.2586
2025-05-09 | 2026 | 2025 | 2025-05-01 | 1668.5602 | 1826.4508 | 1226.601 | 1495.9443 | 946.5897 | 1410.7058 | 1571.9698 | 899.883 | 516.23 | 352.2473 | 364.7297 | 742.3433 | 631.4465 | 504.3193 | 540.3407 | 707.6218 | 682.2715 | 1326.4772 | 1015.6377 | 677.1443 | 1418.6137 | 1252.0545 | 389.6217 | 273.0332 | 527.6663 | 759.0737 | 897.7943 | 618.5952 | 1453.6958 | 754.958 | 680.9003 | 918.2488 | 1158.6008 | 761.2333 | 995.8328 | 1546.3997 | 1387.2357 | 705.1733 | 1228.8013 | 621.3433 | 725.4945 | 925.0483 | 1703.0403 | 1534.64 | 42.3446
2025-05-10 | 2026 | 2025 | 2025-05-01 | 1130.5383 | 1420.1587 | 1047.7382 | 1086.2245 | 781.4452 | 983.023 | 1106.5243 | 604.3245 | 396.0218 | 283.8162 | 356.3197 | 437.6957 | 406.9997 | 100.7705 | 440.8383 | 504.0375 | 572.4737 | 1087.6328 | 738.6767 | 580.4585 | 1001.9552 | 252.2467 | 531.9317 | 591.4955 | 328.6938 | 456.975 | 837.0063 | 290.7772 | 1082.4945 | 363.4528 | 558.9007 | 631.9753 | 698.9022 | 791.8805 | 647.4303 | 1148.8772 | 1028.3548 | 588.4667 | 942.9488 | 286.1242 | 375.599 | 443.8322 | 1129.5837 | 1074.884 | 30.1505
2025-05-11 | 2026 | 2025 | 2025-05-01 | 840.2778 | 871.6407 | 495.537 | 631.9733 | 520.7533 | 708.217 | 786.2723 | 353.9152 | 192.2605 | 198.1087 | 230.5065 | 399.4992 | 363.3923 | 380.6563 | 336.4285 | 385.0598 | 384.0487 | 563.7102 | 484.8787 | 370.5232 | 582.279 | 343.4295 | 368.2335 | 364.3385 | 401.11 | 340.1182 | 405.5693 | 385.4957 | 641.1575 | 512.016 | 388.1737 | 472.4452 | 606.4318 | 529.1022 | 357.9082 | 932.9873 | 837.5072 | 507.0555 | 723.8015 | 43.3092 | 491.8343 | 153.1353 | 919.5817 | 825.122 | 21.6298
2025-05-12 | 2026 | 2025 | 2025-05-01 | 948.9998 | 291.0832 | 788.2033 | 521.49 | 325.6413 | 551.639 | 708.6413 | 255.1653 | 496.6462 | 546.469 | 542.5987 | 535.526 | 518.1523 | 579.6903 | 593.1335 | 644.3423 | 703.0897 | 708.9067 | 672.2545 | 664.7398 | 505.9027 | 458.916 | 290.592 | 329.8688 | 371.685 | 353.589 | 713.2185 | 187.8877 | 525.927 | 345.8442 | 740.2117 | 250.4352 | 96.7875 | 464.0558 | 349.6563 | 658.2008 | 543.2735 | 390.722 | 565.4913 | 237.96 | 375.0413 | 174.0245 | 897.7218 | 917.9912 | 22.3414
2025-05-13 | 2026 | 2025 | 2025-05-01 | 344.5638 | 251.1817 | 290.7602 | 611.3807 | 398.9268 | 268.2918 | 221.5855 | 365.8182 | 267.8437 | 318.04 | 449.5347 | 377.8713 | 355.7462 | 315.3737 | 316.9277 | 389.683 | 481.234 | 300.499 | 318.6363 | 338.7037 | 598.9163 | 581.0035 | 492.3575 | 537.7458 | 549.6062 | 483.2733 | 251.5017 | 177.0187 | 579.5997 | 212.8768 | 496.2668 | 165.6563 | 0 | 353.1422 | 111.4742 | 386.7338 | 335.6382 | 358.219 | 377.4817 | 214.9612 | 262.4137 | 223.1878 | 348.5743 | 303.8673 | 15.3841
2025-05-14 | 2026 | 2025 | 2025-05-01 | 754.6305 | 703.5328 | 605.72 | 100.9903 | 114.0243 | 328.9923 | 471.0223 | 293.4108 | 220.1272 | 250.6257 | 241.6107 | 286.5827 | 302.9762 | 300.9918 | 287.123 | 338.5937 | 364.5148 | 716.712 | 408.5385 | 366.9863 | 602.4975 | 637.9402 | 438.2387 | 426.7613 | 499.9062 | 451.6873 | 611.5937 | 318.3042 | 604.3137 | 756.074 | 327.886 | 185.7147 | 227.3288 | 570.0137 | 222.9377 | 631.7672 | 493.9598 | 476.4715 | 516.911 | 243.7993 | 409.055 | 592.9318 | 826.6618 | 761.4187 | 19.2919
2025-05-15 | 2026 | 2025 | 2025-05-01 | 706.1887 | 607.4902 | 576.3323 | 228.4907 | 349.6332 | 472.8933 | 522.612 | 244.2305 | 135.849 | 153.6445 | 181.2108 | 216.674 | 213.3352 | 217.5595 | 186.186 | 242.8332 | 304.8668 | 711.2155 | 322.3245 | 303.1043 | 704.8867 | 744.5152 | 406.0542 | 428.7303 | 465.6235 | 374.1987 | 508.3142 | 262.9677 | 747.267 | 504.5282 | 371.005 | 244.971 | 501.7158 | 795.7513 | 473.4977 | 709.2042 | 630.7482 | 622.2672 | 721.5852 | 218.2207 | 367.4767 | 529.9872 | 792.5142 | 774.1097 | 19.7968
2025-05-16 | 2026 | 2025 | 2025-05-01 | 38.4313 | 26.5782 | 19.4512 | 22.7245 | 38.1415 | 18.7582 | 23.1643 | 0.8105 | 0 | 0 | 0 | 2.6968 | 1.3352 | 1.1443 | 1.8928 | 9.1228 | 17.2753 | 25.3435 | 19.5617 | 22.6925 | 24.2977 | 24.7593 | 4.218 | 8.2223 | 10.1902 | 9.3467 | 5.8357 | 0.89833 | 21.2055 | 3.542 | 18.3343 | 3.325 | 25.9808 | 54.5052 | 14.3535 | 18.482 | 19.192 | 24.2043 | 39.5348 | 12.7888 | 12.1555 | 9.5103 | 25.8252 | 27.9768 | 0.70781
2025-05-17 | 2026 | 2025 | 2025-05-01 | 344.5638 | 251.1817 | 290.7602 | 611.3807 | 398.9268 | 268.2918 | 221.5855 | 365.8182 | 267.8437 | 318.04 | 449.5347 | 377.8713 | 355.7462 | 315.3737 | 316.9277 | 389.683 | 481.234 | 300.499 | 318.6363 | 338.7037 | 598.9163 | 581.0035 | 492.3575 | 537.7458 | 549.6062 | 483.2733 | 251.5017 | 177.0187 | 579.5997 | 212.8768 | 496.2668 | 165.6563 | 0 | 353.1422 | 111.4742 | 386.7338 | 335.6382 | 358.219 | 377.4817 | 214.9612 | 262.4137 | 223.1878 | 348.5743 | 303.8673 | 15.3841
2025-05-18 | 2026 | 2025 | 2025-05-01 | 57.4273 | 41.8636 | 48.46 | 101.8968 | 66.4878 | 44.7153 | 36.9309 | 60.9697 | 44.6406 | 53.0067 | 74.9224 | 62.9786 | 59.291 | 52.5623 | 52.8213 | 64.9472 | 80.2057 | 50.0832 | 53.1061 | 56.4506 | 99.8194 | 96.8339 | 82.0596 | 89.6243 | 91.601 | 80.5456 | 41.9169 | 29.5031 | 96.5999 | 35.4795 | 82.7111 | 27.6094 | 0 | 58.857 | 18.579 | 64.4556 | 55.9397 | 59.7032 | 62.9136 | 35.8269 | 43.7356 | 37.198 | 58.0957 | 50.6446 | 2.564
2025-05-19 | 2026 | 2025 | 2025-05-01 | 70.2792 | 62.2593 | 62.9267 | 56.805 | 38.0287 | 37.0869 | 52.2397 | 18.2814 | 14.5151 | 13.4757 | 8.3177 | 11.9002 | 10.9807 | 7.9328 | 10.5803 | 12.1025 | 15.7468 | 61.3857 | 17.9212 | 13.0607 | 57.0704 | 57.2963 | 30.7453 | 26.5727 | 19.6335 | 25.6727 | 76.7752 | 35.5897 | 45.2383 | 43.8947 | 17.4318 | 21.3094 | 29.4918 | 56.6236 | 39.7455 | 60.0693 | 53.9682 | 48.0629 | 54.8224 | 11.9227 | 44.4108 | 44.2796 | 67.6776 | 54.9113 | 1.619
2025-05-20 | 2026 | 2025 | 2025-05-01 | 10.3543 | 8.557 | 1.1525 | 10.8707 | 2.7775 | 6.484 | 2.6727 | 5.132 | 9.3113 | 7.25 | 12.9285 | 10.4893 | 9.7488 | 8.4478 | 3.8362 | 1.4568 | 1.8588 | 0.314 | 4.4727 | 0 | 20.1777 | 18.4245 | 16.8713 | 18.402 | 15.165 | 16.5087 | 0.29633 | 4.6192 | 3.4642 | 18.387 | 0 | 3.5728 | 4.3073 | 4.5702 | 19.429 | 19.6693 | 2.5833 | 0 | 4.1188 | 3.0355 | 4.3 | 19.7535 | 15.302 | 2.7643 | 0.35384
2025-05-21 | 2026 | 2025 | 2025-05-01 | [44 empty] | 0
2025-05-22 | 2026 | 2025 | 2025-05-01 | 568.1742 | 641.5852 | 539.2913 | 251.5083 | 93.5138 | 346.261 | 485.017 | 521.7978 | 583.8722 | 397.2052 | 510.0913 | 579.9178 | 463.481 | 483.8787 | 268.8848 | 453.7277 | 388.06 | 436.7503 | 399.4282 | 237.336 | 402.3813 | 472.7203 | 466.161 | 454.6742 | 524.5423 | 531.3343 | 453.2938 | 61.6898 | 239.35 | 202.7173 | 152.092 | 261.8975 | 222.1125 | 420.3543 | 277.2652 | 753.5845 | 376.5542 | 518.223 | 593.2063 | 92.5488 | 128.6288 | 192.0787 | 901.4638 | 593.9197 | 17.9426
2025-05-23 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-24 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-25 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-26 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-27 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-28 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-29 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-30 | 2026 | 2025 | 2025-05-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-05-31 | 2026 | 2025 | 2025-06-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-06-01 | 2026 | 2025 | 2025-06-01 | 784.08 | 1028.976 | 652.872 | 29.136 | 0 | 329.04 | 848.4 | 398.952 | 691.776 | 191.208 | 604.056 | 843.6 | 530.208 | 812.352 | 250.992 | 846.744 | 471.36 | 391.68 | 444.768 | 208.416 | 508.536 | 878.64 | 467.04 | 326.376 | 712.584 | 466.08 | 647.4 | 0 | 210.048 | 258.624 | 43.032 | 55.296 | 189.144 | 523.272 | 74.928 | 1051.896 | 422.928 | 780.528 | 926.952 | 0 | 0 | 171.792 | 2005.512 | 1072.68 | 22.1519
2025-06-02 | 2026 | 2025 | 2025-06-01 | 1183.049 | 1271.1273 | 761.3673 | 883.4788 | 992.8548 | 1179.9508 | 1107.8433 | 555.8388 | 357.8962 | 331.7582 | 352.5453 | 633.5462 | 648.5772 | 718.3917 | 539.264 | 629.558 | 431.1553 | 792.565 | 723.71 | 451.307 | 776.6743 | 724.4562 | 620.7183 | 544.3365 | 608.035 | 490.2773 | 350.782 | 587.2278 | 905.8972 | 798.0212 | 398.9797 | 777.3623 | 956.159 | 678.8772 | 540.2485 | 1402.0772 | 983.7573 | 741.7743 | 1199.3075 | 694.9947 | 800.0698 | 950.6318 | 1337.6397 | 1251.5353 | 33.6656
2025-06-03 | 2026 | 2025 | 2025-06-01 | 3036.79 | 2787.6085 | 2206.3088 | 2234.11 | 2660.4152 | 2844.3665 | 2592.8893 | 1578.1537 | 924.2208 | 1176.408 | 2059.5643 | 2797.876 | 2523.2265 | 2038.8833 | 1798.0878 | 1804.3425 | 1502.597 | 1900.9288 | 1791.0952 | 1151.6105 | 2126.666 | 1706.8418 | 1627.1855 | 1761.3403 | 1972.9295 | 1262.6765 | 1790.1242 | 1747.6392 | 2154.3148 | 2300.338 | 1324.287 | 1972.8075 | 2357.1703 | 2611.1197 | 1492.1467 | 3319.5803 | 3419.6717 | 2207.277 | 3098.3795 | 1813.5995 | 2284.1557 | 2743.8393 | 3434.9162 | 3104.778 | 95.0433
2025-06-04 | 2026 | 2025 | 2025-06-01 | 3124.585 | 2930.4908 | 2925.4907 | 2339.7387 | 2657.7822 | 2863.3913 | 2564.2972 | 1901.2288 | 1678.3185 | 1456.0295 | 1587.185 | 1712.9485 | 1490.3197 | 1509.1542 | 1384.5257 | 1632.4833 | 1801.8912 | 2236.5505 | 1979.0332 | 1410.2003 | 2435.0858 | 2194.4672 | 2407.2573 | 1841.6298 | 1994.901 | 898.2133 | 2672.5243 | 1746.4107 | 2330.1292 | 2079.4133 | 1811.131 | 1987.0713 | 2619.2377 | 2256.196 | 1939.275 | 3802.0742 | 3331.6132 | 2463.8073 | 2307.7432 | 1871.2565 | 2261.2652 | 2267.3287 | 3442.9577 | 2492.7375 | 96.6394
2025-06-05 | 2026 | 2025 | 2025-06-01 | 2031.0357 | 2167.9003 | 2191.7555 | 1690.9687 | 2146.525 | 2073.3272 | 1432.8647 | 918.076 | 1078.4707 | 1287.7355 | 1210.3648 | 1222.4653 | 1038.3502 | 1132.811 | 941.3117 | 1060.7415 | 1035.757 | 2085.0217 | 907.8993 | 751.339 | 1548.2012 | 1620.8472 | 1527.726 | 1439.3545 | 1386.4013 | 773.5038 | 2689.8837 | 1047.336 | 1657.2388 | 1440.57 | 1017.7008 | 1341.715 | 2267.0227 | 2274.5542 | 1076.6833 | 2270.9687 | 2240.657 | 2039.2307 | 2201.6273 | 835.8283 | 1432.0103 | 1587.9913 | 1864.0955 | 1705.373 | 67.6912
2025-06-06 | 2026 | 2025 | 2025-06-01 | 1982.9333 | 1957.4335 | 1623.254 | 1194.5977 | 1122.0002 | 1044.1207 | 1127.3992 | 480.4492 | 330.9067 | 346.9813 | 352.5877 | 347.633 | 214.3 | 376.383 | 344.0793 | 406.9587 | 509.3145 | 1997.252 | 533.3808 | 471.5885 | 1245.3435 | 1391.8548 | 734.5007 | 744.6988 | 844.7862 | 737.6463 | 1489.5537 | 737.4567 | 1251.9993 | 1164.2105 | 619.393 | 680.0763 | 1131.8052 | 1086.916 | 960.1952 | 1565.3762 | 1373.5472 | 1277.2013 | 1419.1235 | 302.55 | 1035.0332 | 1354.2917 | 1741.3113 | 1619.206 | 43.2716
2025-06-07 | 2026 | 2025 | 2025-06-01 | 2079.4483 | 1974.6708 | 1547.3072 | 1640.9432 | 1485.2195 | 1462.4532 | 1217.1478 | 659.632 | 570.569 | 619.2765 | 612.2145 | 592.2402 | 536.2447 | 612.4492 | 566.7508 | 638.7342 | 738.9653 | 2178.6327 | 718.224 | 575.3577 | 1557.0407 | 1661.3697 | 1116.7753 | 1067.1502 | 1146.1477 | 1016.476 | 1596.6358 | 712.6062 | 1448.9178 | 1187.3393 | 829.6437 | 975.63 | 1539.8782 | 2043.8737 | 1196.039 | 1913.3132 | 1766.74 | 1716.0737 | 1765.5408 | 288.392 | 919.0335 | 1228.412 | 1934.6552 | 1788.0708 | 53.4422
2025-06-08 | 2026 | 2025 | 2025-06-01 | 3006.8752 | 3043.5467 | 2686.2795 | 2796.2018 | 2974.229 | 2898.6975 | 2072.699 | 1206.8467 | 1221.1432 | 1367.0017 | 1355.2938 | 1333.3395 | 1167.3105 | 1283.8678 | 1158.4188 | 1329.4583 | 1357.5438 | 3412.8695 | 1352.7622 | 1152.9492 | 2576.2147 | 2821.6212 | 1980.4157 | 2004.096 | 2025.8587 | 1729.4663 | 2806.66 | 1308.6815 | 2668.1475 | 1927.12 | 1581.936 | 2000.1262 | 3107.5847 | 3592.8522 | 1902.8192 | 3176.1012 | 3059.2395 | 2959.7157 | 3153.4512 | 826.7727 | 1579.1333 | 1989.915 | 2760.3985 | 2656.7203 | 94.3724
2025-06-09 | 2026 | 2025 | 2025-06-01 | 3091.1317 | 3316.7352 | 3090.34 | 3054.5342 | 3846.4002 | 3871.6212 | 2247.4247 | 1627.4772 | 1781.272 | 1957.45 | 1925.744 | 1875.1132 | 1692.607 | 1809.0698 | 1676.4513 | 1762.8602 | 1750.7525 | 3670.0607 | 1842.5352 | 1754.5445 | 2998.0393 | 3105.9925 | 2502.9918 | 2559.0925 | 2741.1128 | 2502.3135 | 3255.5683 | 1688.2057 | 2904.9043 | 2421.295 | 2134.8607 | 2536.141 | 4087.3652 | 4460.362 | 2541.8953 | 4121.8112 | 4030.2318 | 3832.6203 | 4197.3928 | 885.6402 | 1982.1977 | 2311.4148 | 3185.327 | 3239.923 | 117.8708
2025-06-10 | 2026 | 2025 | 2025-06-01 | 2482.4427 | 2485.534 | 2291.8115 | 1922.611 | 1825.4868 | 1796.0508 | 1613.3112 | 909.0767 | 707.5853 | 711.1578 | 641.9425 | 568.6457 | 547.4782 | 637.2282 | 600.7473 | 641.318 | 614.9328 | 2458.4622 | 787.2145 | 678.8597 | 2069.0888 | 2122.5815 | 1306.318 | 1236.2758 | 1239.8082 | 1131.2663 | 1838.8235 | 1447.6295 | 2032.4635 | 1935.6473 | 817.6318 | 1115.805 | 1879.8508 | 2490.6555 | 1600.6272 | 2401.0672 | 2068.1697 | 2035.9123 | 2267.9217 | 684.0372 | 1925.4353 | 2214.9025 | 2430.1225 | 2248.3428 | 67.4623
2025-06-11 | 2026 | 2025 | 2025-06-01 | 1790.7097 | 2166.0123 | 2299.6973 | 1543.8738 | 1963.1892 | 1889.0648 | 1268.663 | 973.0462 | 1118.2548 | 1132.2887 | 1126.4022 | 1089.8483 | 1094.278 | 1135.0103 | 1046.0923 | 1140.6743 | 1033.0767 | 1918.0007 | 1108.5932 | 1062.3942 | 1443.9965 | 1619.8077 | 1311.8057 | 1412.9708 | 1456.3167 | 1398.4928 | 2567.8255 | 1093.7773 | 1516.2782 | 1339.617 | 1284.4355 | 1410.7018 | 2080.1928 | 2135.7103 | 1386.0825 | 1904.7392 | 1898.8708 | 1801.1908 | 1966.407 | 743.5148 | 1562.1753 | 1577.8973 | 1519.4418 | 1414.8338 | 65.7463
2025-06-12 | 2026 | 2025 | 2025-06-01 | 4597.7643 | 5485.3198 | 5601.8052 | 2940.9632 | 3084.8662 | 3149.6283 | 3112.287 | 2135.7507 | 1934.8242 | 1938.6197 | 1721.4252 | 1587.9643 | 1565.9048 | 1628.0687 | 1501.1652 | 1478.8243 | 1662.0485 | 4492.1827 | 1744.66 | 1538.6325 | 3086.279 | 3640.4603 | 2461.1788 | 2425.4995 | 2579.0147 | 2471.1448 | 5611.332 | 2213.9443 | 3274.2257 | 2897.989 | 1835.8108 | 2198.8635 | 3222.4398 | 4201.9018 | 2739.6938 | 4187.0807 | 3985.7583 | 3572.6008 | 3742.484 | 1735.6668 | 3650.9502 | 3973.708 | 3897.5102 | 3729.9207 | 130.2382
2025-06-13 | 2026 | 2025 | 2025-06-01 | 117.3958 | 134.5655 | 145.6875 | 90.8433 | 49.5908 | 48.2702 | 118.1942 | 51.1667 | 34.9652 | 27.092 | 49.8778 | 42.8413 | 43.0513 | 50.125 | 8.1537 | 32.868 | 19.5187 | 104.1187 | 45.9993 | 50.016 | 137.5542 | 65.1868 | 74.6592 | 55.9852 | 67.2415 | 77.2897 | 108.7362 | 54.7957 | 39.4102 | 126.486 | 56.2208 | 25.6662 | 26.7853 | 66.8845 | 81.6437 | 178.2285 | 89.8347 | 61.0385 | 73.9405 | 63.9233 | 81.371 | 128.2468 | 176.5303 | 108.7725 | 3.2908
2025-06-14 | 2026 | 2025 | 2025-06-01 | 480.6407 | 543.3658 | 592.594 | 303.4273 | 363.7528 | 488.2828 | 440.9833 | 279.1312 | 188.3083 | 159.8918 | 183.1278 | 191.997 | 195.4957 | 202.837 | 108.4435 | 244.883 | 303.1 | 428.2348 | 311.9932 | 269.5042 | 300.7102 | 234.8332 | 254.4447 | 236.0728 | 264.898 | 249.7492 | 568.3972 | 104.706 | 300.0677 | 148.1712 | 293.7672 | 431.6312 | 354.2023 | 505.7638 | 185.6067 | 552.728 | 415.6073 | 403.8352 | 456.9413 | 109.1713 | 151.3907 | 156.5852 | 509.4363 | 302.9198 | 13.7716
2025-06-15 | 2026 | 2025 | 2025-06-01 | 2571.2255 | 2423.61 | 1978.651 | 2332.5835 | 1689.861 | 2384.648 | 2367.1623 | 1851.3523 | 1453.7215 | 1206.6182 | 1494.1132 | 1661.1195 | 1070.6785 | 1734.1458 | 1508.1643 | 1664.467 | 1695.6017 | 1762.4012 | 2117.2615 | 1469.6792 | 2427.082 | 1930.6517 | 2078.444 | 1586.3592 | 1773.1275 | 1885.7037 | 1504.9308 | 1404.0317 | 2408.1113 | 1675.2228 | 1596.736 | 1746.2653 | 1753.4775 | 1813.52 | 1837.9617 | 3223.173 | 2578.4008 | 1937.8925 | 1879.0423 | 1549.8238 | 1766.7843 | 1641.6267 | 3152.8357 | 2102.1248 | 83.6904
2025-06-16 | 2026 | 2025 | 2025-06-01 | 6659.6317 | 6339.9977 | 6052.7018 | 6227.5328 | 6470.0028 | 6420.4955 | 6387.5558 | 5677.1195 | 4901.5462 | 5271.78 | 5786.6803 | 6323.11 | 2235.546 | 6116.4797 | 5696.2678 | 5912.3577 | 5909.13 | 6170.6837 | 6075.4402 | 5441.1675 | 6231.5552 | 5983.739 | 5910.0125 | 6122.6007 | 6135.4045 | 5940.9313 | 5417.3648 | 5844.1523 | 4775.7425 | 6270.2242 | 5704.9482 | 5703.3198 | 6420.301 | 6406.5085 | 5621.892 | 6699.6247 | 6702.5933 | 6419.8313 | 6610.8013 | 5774.6382 | 6312.0425 | 6483.8117 | 6721.9732 | 6593.5778 | 262.8828
2025-06-17 | 2026 | 2025 | 2025-06-01 | 2659.9567 | 2570.5528 | 2270.7157 | 1943.7172 | 2581.3167 | 2707.478 | 2586.1309 | 2394.4643 | 2117.8051 | 2029.5752 | 2346.5363 | 2596.3372 | 2706.8993 | 2598.9602 | 2395.3357 | 2455.5685 | 2433.2508 | 2431.3114 | 2595.6711 | 2341.2981 | 2586.1642 | 2466.1424 | 2460.0276 | 2545.3275 | 2552.0327 | 2340.9932 | 1786.5931 | 2341.109 | 2134.9895 | 0 | 2293.28 | 2387.5026 | 2585.3099 | 2563.6381 | 2337.891 | 2768.7757 | 2745.4618 | 2547.5996 | 2706.6439 | 2191.4019 | 2407.5308 | 2594.521 | 2728.425 | 2676.6429 | 105.5109
2025-06-18 | 2026 | 2025 | 2025-06-01 | 7132.3977 | 6897.3145 | 6434.4167 | 2737.105 | 7056.3845 | 7215.3027 | 6990.3268 | 6580.5215 | 5779.56 | 5825.7545 | 6441.9618 | 7065.504 | 7177.613 | 6931.2123 | 6680.488 | 5105.9628 | 6846.019 | 6649.2453 | 7003.3932 | 6537.8757 | 7121.9328 | 6836.1215 | 6738.9133 | 6952.8987 | 7002.9943 | 5645.9973 | 5581.4355 | 6514.9698 | 7165.9872 | 6877.9053 | 6668.245 | 6622.1663 | 7099.2793 | 7109.963 | 6494.2587 | 7347.6973 | 7318.5587 | 7100.077 | 7284.5132 | 6318.2318 | 6719.8673 | 6705.4862 | 7135.7988 | 6854.7615 | 292.3064
2025-06-19 | 2026 | 2025 | 2025-06-01 | 6142.4948 | 6083.95 | 6426.016 | 3504.8373 | 6990.3897 | 6961.2785 | 5936.9465 | 6424.972 | 5701.9778 | 5586.5512 | 6413.8745 | 6304.8538 | 6021.804 | 6680.9722 | 5511.5962 | 6475.3565 | 6709.077 | 6847.7948 | 6654.2817 | 6129.0857 | 6889.3107 | 6144.177 | 6493.4608 | 6661.3552 | 6780.0882 | 6645.4422 | 5748.1827 | 4235.8487 | 6787.928 | 6570.1852 | 6641.005 | 6335.2667 | 6956.6493 | 7011.6138 | 6255.2295 | 7155.9365 | 7186.7478 | 6942.9288 | 7161.6477 | 4364.0368 | 4718.1727 | 4435.5867 | 4999.6448 | 3995.632 | 270.6242
2025-06-20 | 2026 | 2025 | 2025-06-01 | 6142.4948 | 6083.95 | 6426.016 | 3504.8373 | 6990.3897 | 6961.2785 | 5936.9465 | 6424.972 | 5701.9778 | 5586.5512 | 6413.8745 | 6304.8538 | 6021.804 | 6680.9722 | 5511.5962 | 6475.3565 | 6709.077 | 6847.7948 | 6654.2817 | 6129.0857 | 6889.3107 | 6144.177 | 6493.4608 | 6661.3552 | 6780.0882 | 6645.4422 | 5748.1827 | 4235.8487 | 6787.928 | 6570.1852 | 6641.005 | 6335.2667 | 6956.6493 | 7011.6138 | 6255.2295 | 7155.9365 | 7186.7478 | 6942.9288 | 7161.6477 | 4364.0368 | 4718.1727 | 4435.5867 | 4999.6448 | 3995.632 | 270.6242
2025-06-21 | 2026 | 2025 | 2025-06-01 | 6659.6317 | 6339.9977 | 6052.7018 | 6227.5328 | 6470.0028 | 6420.4955 | 6387.5558 | 5677.1195 | 4901.5462 | 5271.78 | 5786.6803 | 6323.11 | 2235.546 | 6116.4797 | 5696.2678 | 5912.3577 | 5909.13 | 6170.6837 | 6075.4402 | 5441.1675 | 6231.5552 | 5983.739 | 5910.0125 | 6122.6007 | 6135.4045 | 5940.9313 | 5417.3648 | 5844.1523 | 4775.7425 | 6270.2242 | 5704.9482 | 5703.3198 | 6420.301 | 6406.5085 | 5621.892 | 6699.6247 | 6702.5933 | 6419.8313 | 6610.8013 | 5774.6382 | 6312.0425 | 6483.8117 | 6721.9732 | 6593.5778 | 262.8828
2025-06-22 | 2026 | 2025 | 2025-06-01 | 6583.8867 | 5830.8217 | 5246.4412 | 6318.4368 | 6203.3967 | 6117.995 | 6338.5657 | 5697.4095 | 4384.9763 | 5078.9802 | 5240.7543 | 6671.3317 | 6727.0455 | 5643.1863 | 5612.778 | 5657.7347 | 6207.9147 | 5658.5565 | 5415.6377 | 4711.8905 | 6230.4935 | 5053.2173 | 5589.871 | 5832.5967 | 6256.0938 | 6208.156 | 4659.5603 | 5303.0652 | 5882.228 | 5746.4927 | 5537.3318 | 4734.2418 | 6074.0483 | 6483.6773 | 5108.9233 | 6782.5423 | 6756.031 | 6352.7163 | 6674.614 | 5918.9605 | 6528.425 | 5121.636 | 6884.8322 | 6729.9697 | 257.7975
2025-06-23 | 2026 | 2025 | 2025-06-01 | 5866.7162 | 5703.2975 | 5999.035 | 6290.0395 | 6713.1672 | 6682.7022 | 5815.699 | 5944.8578 | 4839.5425 | 5600.5532 | 6303.2343 | 6586.9022 | 6695.7135 | 6354.9647 | 6140.4793 | 6380.9525 | 6362.068 | 5728.6393 | 6587.038 | 6323.8802 | 6594.3612 | 6434.1807 | 6429.1022 | 6496.405 | 6539.1023 | 6449.8675 | 5037.1647 | 4636.2877 | 5851.5528 | 7206.7533 | 6483.7225 | 6267.5247 | 6129.2783 | 6580.1085 | 6284.4952 | 6793.8663 | 6807.8905 | 6733.0395 | 6792.4353 | 5238.308 | 5436.1823 | 4191.5123 | 5694.8507 | 5911.8285 | 269.9393
2025-06-24 | 2026 | 2025 | 2025-06-01 | 7180.0408 | 6783.0503 | 7102.9887 | 7326.6253 | 7408.4395 | 7231.4667 | 6892.5213 | 7089.5112 | 6184.1808 | 6685.418 | 6964.5053 | 7391.2922 | 7488.192 | 6669.7915 | 6718.3312 | 7217.4167 | 6843.2632 | 7208.5607 | 7078.3775 | 6754.8073 | 7284.4663 | 6980.9165 | 7168.4635 | 7061.3492 | 7445.6687 | 7389.7212 | 6637.5287 | 6344.4167 | 5368.4883 | 6695.3845 | 7106.4507 | 6439.262 | 7154.0122 | 7415.3253 | 6919.3678 | 7547.514 | 7422.7367 | 7498.5645 | 7521.1363 | 5457.9363 | 6946.3967 | 5228.7268 | 7076.065 | 7170.773 | 305.4995
2025-06-25 | 2026 | 2025 | 2025-06-01 | 6975.6902 | 6827.226 | 6315.4612 | 6471.6672 | 6827.0422 | 6889.1717 | 6924.7907 | 6145.4645 | 5133.3702 | 5276.4023 | 6261.434 | 6759.4715 | 6871.9138 | 6335.8122 | 5956.6152 | 6227.75 | 6440.5952 | 6558.8832 | 6280.135 | 5831.216 | 6710.6287 | 6264.9307 | 5659.8413 | 5445.4488 | 6476.064 | 6434.4208 | 5704.6338 | 6258.8877 | 6875.729 | 6698.6757 | 6282.8745 | 6125.8472 | 5502.8623 | 6851.2433 | 5842.9413 | 7019.1613 | 7009.6993 | 6740.0715 | 6999.0613 | 6422.9723 | 6893.3865 | 5277.7252 | 7113.4705 | 7060.1492 | 280.9808
2025-06-26 | 2026 | 2025 | 2025-06-01 | 7038.3843 | 6866.5472 | 6123.4253 | 6819.2295 | 6959.886 | 6953.5618 | 6885.9378 | 5890.6495 | 5044.1522 | 5076.7728 | 5864.1828 | 6532.8677 | 6819.8772 | 6475.3577 | 5844.498 | 6007.1205 | 6124.2258 | 6384.199 | 6478.1437 | 5819.5095 | 6733.951 | 6206.3382 | 6072.991 | 6475.308 | 6402.4437 | 6139.569 | 5003.2673 | 6003.9678 | 6884.6648 | 6576.4713 | 5838.7492 | 6264.3183 | 5956.3338 | 6762.1843 | 5819.7332 | 7229.1747 | 7186.1637 | 6712.3667 | 7107.293 | 5723.0363 | 6536.455 | 5352.474 | 7074.4192 | 7001.2428 | 279.0714
2025-06-27 | 2026 | 2025 | 2025-06-01 | 7139.6518 | 6754.3647 | 5168.5133 | 6895.373 | 6603.8267 | 6949.2903 | 6815.8992 | 5779.5235 | 5219.405 | 4717.4038 | 5320.74 | 6283.0565 | 6643.2353 | 6532.4995 | 5597.7542 | 5758.8253 | 5407.6953 | 5590.7442 | 6275.9057 | 5172.1635 | 6705.6853 | 6254.2293 | 5936.2053 | 5536.0787 | 6242.1628 | 5825.0175 | 3707.1595 | 5731.908 | 6803.0435 | 6561.3085 | 4766.1503 | 5810.33 | 6502.64 | 6003.4558 | 5538.9958 | 7414.3102 | 7336.073 | 6038.7615 | 7011.756 | 5353.7875 | 6204.9472 | 6907.598 | 7483.7257 | 7277.1417 | 269.5783
2025-06-28 | 2026 | 2025 | 2025-06-01 | 6965.8997 | 6559.1327 | 4978.6547 | 6654.9897 | 6651.324 | 6942.4448 | 6670.6955 | 5818.2255 | 4891.3442 | 4832.0628 | 5700.3218 | 6660.7653 | 6990.3428 | 6563.2487 | 5803.1265 | 6018.9615 | 6117.8065 | 5398.7462 | 6384.7782 | 5524.3508 | 6601.7777 | 5623.3275 | 5754.5067 | 6143.3247 | 6297.4178 | 6076.5667 | 3573.8218 | 5518.0513 | 6822.9393 | 6391.2368 | 5598.367 | 5914.6037 | 6485.0422 | 6124.2258 | 4833.4202 | 7377.056 | 7222.4363 | 5974.6952 | 7017.6493 | 5504.269 | 6249.5938 | 6813.1672 | 7406.9622 | 7221.946 | 270.6736
2025-06-29 | 2026 | 2025 | 2025-06-01 | 7001.582 | 6380.7983 | 5742.7688 | 6624.136 | 6106.125 | 6301.1057 | 6498.4805 | 6054.9705 | 4857.7782 | 5316.099 | 6275.7118 | 6609.5568 | 6914.5768 | 5590.3328 | 5482.9402 | 5948.324 | 6184.8683 | 5988.0522 | 4111.049 | 5021.1752 | 6536.2915 | 5819.3175 | 5980.651 | 5607.4377 | 6430.0545 | 6329.6753 | 4942.7695 | 5605.759 | 6665.4145 | 6322.058 | 5900.3253 | 5059.4873 | 6301.3352 | 6605.4955 | 5464.242 | 6700.213 | 7101.7162 | 6463.3403 | 6976.7578 | 6249.7318 | 6791.4522 | 6736.6462 | 7273.2083 | 7022.23 | 269.896
2025-06-30 | 2026 | 2025 | 2025-07-01 | 7099.5178 | 6753.7388 | 2314.513 | 6938.8902 | 5964.2755 | 6725.362 | 6994.846 | 6481.3267 | 5425.6867 | 5729.376 | 5938.6165 | 7031.5762 | 7092.7215 | 6280.1037 | 6149.9772 | 6476.3793 | 6586.0837 | 6687.3988 | 6345.7398 | 5913.9657 | 6855.766 | 6408.3463 | 6510.7497 | 6683.2285 | 6821.2707 | 6757.0955 | 6001.2535 | 6285.3612 | 6968.947 | 6759.818 | 6408.5752 | 5876.2963 | 6756.4683 | 6906.3437 | 6178.1078 | 7192.4428 | 7182.0925 | 6897.8857 | 7097.1353 | 6502.6897 | 6877.313 | 6999.4612 | 7242.8308 | 7154.1435 | 286.2537
2025-07-01 | 2026 | 2025 | 2025-07-01 | 7188.7035 | 6561.6218 | 2561.7002 | 6730.8018 | 5526.4327 | 5732.6348 | 6761.7055 | 6128.874 | 4659.2657 | 5472.4578 | 6092.218 | 7055.4888 | 6935.7013 | 5987.0288 | 5625.5335 | 6225.7198 | 6480.6593 | 6553.8447 | 5697.3562 | 4996.4638 | 6535.6228 | 5857.5762 | 6092.4463 | 6385.854 | 6757.098 | 6457.2645 | 6165.1033 | 5696.0662 | 6736.6103 | 6432.6703 | 6185.6002 | 4588.2133 | 6602.5897 | 6830.7928 | 5607.3765 | 7207.1432 | 7241.85 | 6877.2463 | 7012.0553 | 6647.227 | 6996.6048 | 6774.611 | 7381.9608 | 7125.2582 | 275.1691
2025-07-02 | 2026 | 2025 | 2025-07-01 | 7393.2048 | 6998.6567 | 6927.6943 | 6369.6172 | 7274.4152 | 6008.1833 | 7095.4893 | 6551.5055 | 5494.1493 | 6409.1258 | 7124.3682 | 7288.4647 | 7030.7238 | 6382.4355 | 5762.4128 | 6386.2897 | 6431.2847 | 6988.753 | 6070.9658 | 5311.388 | 6358.7428 | 6024.2455 | 6710.6598 | 6955.8053 | 7225.0867 | 6897.0785 | 6484.3608 | 6242.7707 | 6414.1277 | 6802.3788 | 6247.2658 | 5703.2208 | 7209.9072 | 7142.1582 | 6021.3652 | 7408.9047 | 7426.0768 | 7263.0158 | 7337.6735 | 7077.4897 | 7243.9302 | 7112.2022 | 7495.1095 | 7317.6108 | 295.4203
2025-07-03 | 2026 | 2025 | 2025-07-01 | 7150.4173 | 6886.1197 | 6365.1362 | 6851.323 | 7163.1982 | 7111.721 | 7108.1227 | 6413.5557 | 5377.856 | 5404.5778 | 6287.9847 | 6980.7532 | 7083.5218 | 6565.3982 | 6122.5477 | 6531.6313 | 6584.1782 | 6686.1828 | 6646.8452 | 6073.3007 | 6661.7707 | 6210.229 | 6449.8998 | 6708.7022 | 6833.6717 | 6703.5123 | 5688.8513 | 6149.7615 | 6811.4598 | 6682.6337 | 6305.0265 | 6328.6475 | 6856.128 | 6350.3742 | 6098.2658 | 7367.7198 | 7367.1177 | 6944.853 | 7254.1385 | 6522.2557 | 6852.8462 | 7045.9518 | 7382.3505 | 7339.8935 | 292.3104
2025-07-04 | 2026 | 2025 | 2025-07-01 | 6959.8708 | 6605.0893 | 5458.5695 | 6449.1437 | 6785.1932 | 6424.289 | 6823.4165 | 5815.3867 | 4799.5117 | 4903.5048 | 5909.0408 | 6495.7648 | 6747.285 | 6229.4758 | 5747.1048 | 6097.7957 | 6218.4847 | 6320.9217 | 6041.6665 | 5577.6003 | 6157.4167 | 5857.3967 | 5849.9162 | 6236.789 | 6339.0575 | 6161.5175 | 5353.3282 | 5931.3517 | 6446.3017 | 6483.7182 | 6046.5383 | 5668.2155 | 6642.5407 | 6753.2038 | 5611.6933 | 7054.1333 | 6984.9618 | 6649.8182 | 6991.6445 | 6130.7153 | 6609.6165 | 6761.8958 | 7109.6092 | 7025.062 | 275.2656
2025-07-05 | 2026 | 2025 | 2025-07-01 | 6921.0333 | 5988.7728 | 6888.8623 | 7110.8183 | 7130.9552 | 6902.5388 | 7258.8868 | 6591.334 | 5582.3333 | 5658.2303 | 6615.194 | 7214.6595 | 7223.5545 | 6778.1468 | 6579.9583 | 6680.8278 | 7003.1105 | 7050.6667 | 6729.1325 | 6341.716 | 7013.4568 | 6587.9983 | 6705.4865 | 4758.6948 | 7000.2588 | 6890.4713 | 6324.6687 | 6778.1135 | 7169.2473 | 7109.8555 | 6819.296 | 3082.3303 | 7177.4035 | 7241.1753 | 6585.3677 | 7392.131 | 7386.1513 | 7210.2587 | 7336.5098 | 6886.2083 | 7268.7548 | 7311.1633 | 7463.8588 | 7390.2508 | 297.1398
2025-07-06 | 2026 | 2025 | 2025-07-01 | 7394.6078 | 7285.1657 | 6846.955 | 7326.9142 | 7231.0767 | 7325.0525 | 7368.7188 | 6685.0625 | 6185.3358 | 6141.0673 | 6896.6753 | 7305.4585 | 7370.5415 | 7054.158 | 6713.6243 | 7057.51 | 7186.0103 | 7063.5763 | 7228.8262 | 6952.2157 | 7290.2898 | 7084.5513 | 7022.2987 | 7127.3873 | 7212.2875 | 7153.2953 | 6088.5107 | 7097.9412 | 7327.9962 | 7348.0598 | 7226.8952 | 6928.9092 | 7097.7573 | 7324.1022 | 6838.4045 | 7421.9405 | 7414.6943 | 7294.2408 | 7396.7655 | 6987.3187 | 7358.1185 | 7406.3778 | 7449.4325 | 7421.98 | 312.9381
2025-07-07 | 2026 | 2025 | 2025-07-01 | 6146.7683 | 6204.5548 | 5736.943 | 6121.7638 | 6348.4512 | 6110.6298 | 6339.8738 | 5767.5262 | 5089.2147 | 5220.4387 | 6101.5492 | 6455.0108 | 6552.4948 | 6066.7177 | 5740.5442 | 5961.0243 | 6176.0777 | 6015.419 | 5986.215 | 5551.1388 | 6316.8107 | 5866.7027 | 6009.5943 | 6199.04 | 6266.695 | 6203.7775 | 5132.8023 | 5718.7253 | 6099.1613 | 6076.7187 | 6034.2432 | 5604.053 | 6277.7397 | 6073.4377 | 5379.1102 | 6544.3033 | 6522.9775 | 6282.9547 | 6486.138 | 5896.6183 | 6261.422 | 6431.5565 | 6319.9963 | 6491.8128 | 266.1887
2025-07-08 | 2026 | 2025 | 2025-07-01 | 6592.6573 | 6382.0645 | 6274.261 | 6511.6908 | 6689.7397 | 5949.1437 | 6667.0837 | 6041.73 | 4637.1172 | 5385.1233 | 5430.8978 | 6890.3142 | 6809.431 | 5917.9648 | 5683.6605 | 6261.4727 | 6469.1723 | 6418.9998 | 5695.9463 | 5227.0138 | 6399.3633 | 5764.7977 | 5894.7368 | 6162.8385 | 6532.0632 | 6496.9 | 5737.4325 | 5778.8225 | 6599.6383 | 6242.6375 | 6323.6282 | 5096.8047 | 6588.4127 | 6519.761 | 5484.5125 | 6886.8538 | 6975.962 | 6726.5412 | 6854.7358 | 6542.1862 | 6842.8492 | 6747.0802 | 7028.3843 | 6950.3917 | 275.1128
2025-07-09 | 2026 | 2025 | 2025-07-01 | 5944.8698 | 4997.7542 | 4515.8775 | 5669.3458 | 5653.3107 | 5245.874 | 5496.8067 | 5071.3435 | 3792.2 | 4251.7428 | 5271.9052 | 5841.2607 | 5973.3083 | 4888.7062 | 4549.993 | 4913.1585 | 5230.914 | 4786.0907 | 4508.726 | 3959.6755 | 5525.7463 | 4538.0933 | 4738.8378 | 5151.2508 | 5277.0325 | 5128.5967 | 3941.2465 | 4450.8328 | 5825.2857 | 5132.7608 | 5002.601 | 3944.3965 | 5425.854 | 5690.3102 | 4412.3033 | 6239.7023 | 6204.5508 | 5491.6792 | 6003.5373 | 4973.9175 | 5666.3175 | 5648.2173 | 6372.1867 | 6105.3132 | 227.4534
2025-07-10 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-11 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-12 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-13 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-14 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-15 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-16 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-17 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-18 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-19 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-20 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-21 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-22 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-23 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-24 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-25 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-26 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-27 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-28 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-29 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-30 | 2026 | 2025 | 2025-07-01 | [44 empty] | 0
2025-07-31 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-01 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-02 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-03 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-04 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-05 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-06 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-07 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-08 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-09 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-10 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-11 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-12 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-13 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-14 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-15 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-16 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-17 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-18 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-19 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-20 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-21 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-22 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-23 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-24 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-25 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-26 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-27 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-28 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-29 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-30 | 2026 | 2025 | 2025-08-01 | [44 empty] | 0
2025-08-31 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-01 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-02 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-03 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-04 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-05 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-06 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-07 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-08 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-09 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-10 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-11 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-12 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-13 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-14 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-15 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-16 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-17 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-18 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-19 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-20 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-21 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-22 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-23 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-24 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-25 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-26 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-27 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-28 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-29 | 2026 | 2025 | 2025-09-01 | [44 empty] | 0
2025-09-30 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-01 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-02 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-03 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-04 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-05 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-06 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-07 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-08 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-09 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-10 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-11 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-12 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-13 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-14 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-15 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-16 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-17 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-18 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-19 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-20 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-21 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-22 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-23 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-24 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-25 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-26 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-27 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-28 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-29 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-30 | 2026 | 2025 | 2025-10-01 | [44 empty] | 0
2025-10-31 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-01 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-02 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-03 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-04 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-05 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-06 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-07 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-08 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-09 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-10 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-11 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-12 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-13 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-14 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-15 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-16 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-17 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-18 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-19 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-20 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-21 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-22 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-23 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-24 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-25 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-26 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-27 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-28 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-29 | 2026 | 2025 | 2025-11-01 | [44 empty] | 0
2025-11-30 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-01 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-02 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-03 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-04 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-05 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-06 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-07 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-08 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-09 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-10 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-11 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-12 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-13 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-14 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-15 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-16 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-17 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-18 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-19 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-20 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-21 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-22 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-23 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-24 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-25 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-26 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-27 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-28 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-29 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-30 | 2026 | 2025 | 2025-12-01 | [44 empty] | 0
2025-12-31 | 2026 | 2025 | 2026-01-01 | [44 empty] | 0
2026-01-01 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-02 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-03 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-04 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-05 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-06 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-07 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-08 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-09 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-10 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-11 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-12 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-13 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-14 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-15 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-16 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-17 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-18 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-19 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-20 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-21 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-22 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-23 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-24 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-25 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-26 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-27 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-28 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-29 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-30 | 2026 | 2026 | 2026-01-01 | [44 empty] | 0
2026-01-31 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-01 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-02 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-03 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-04 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-05 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-06 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-07 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-08 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-09 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-10 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-11 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-12 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-13 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-14 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-15 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-16 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-17 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-18 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-19 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-20 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-21 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-22 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-23 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-24 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-25 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-26 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-27 | 2026 | 2026 | 2026-02-01 | [44 empty] | 0
2026-02-28 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-01 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-02 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-03 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-04 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-05 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-06 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-07 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-08 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-09 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-10 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-11 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-12 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-13 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-14 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-15 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-16 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-17 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-18 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-19 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-20 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-21 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-22 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-23 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-24 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-25 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-26 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-27 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-28 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-29 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-30 | 2026 | 2026 | 2026-03-01 | [44 empty] | 0
2026-03-31 | 2026 | 2026 | #VALUE! | [44 empty] | 0
Formulas:
Month Year = Daily_KPI[[#This Row],[Date]]-DAY(Daily_KPI[[#This Row],[Date]])+1

## Modelling New (hidden)
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | Total Capacity | 70.4
1 | April | 4 | 2022-04-01 | 2022 | FY23 | 30 |  |  | 5.22 |  |  | 6797.3115 | 70.4 |  |  | 0 |  |  | 226.577 | 0 | 0 | 13.41% |  |  | 0 | 70.4 |  | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
2 | May | 5 | 2022-05-01 | 2022 | FY23 | 31 |  |  | 5.7233 |  |  | 10772.5855 | 70.4 |  |  | 0 |  |  | 347.5028 | 0 | 0 | 20.57% |  |  | 0 | 70.4 |  | 5.9682 | 6.1861 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
3 | June | 6 | 2022-06-01 | 2022 | FY23 | 30 |  |  | 6.81 |  |  | 15494.0713 | 70.4 |  |  | 0 |  |  | 516.469 | 0 | 0 | 30.57% |  |  | 0 | 70.4 |  | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
4 | July | 7 | 2022-07-01 | 2022 | FY23 | 31 |  |  | 9.8233 |  |  | 27867.6204 | 70.4 |  |  | 0 |  |  | 898.9555 | 0 | 0 | 53.21% |  |  | 0 | 70.4 |  | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
5 | August | 8 | 2022-08-01 | 2022 | FY23 | 31 |  |  | 9.1 |  |  | 32561.9712 | 70.4 |  |  | 0 |  |  | 1050.3862 | 0 | 0 | 62.17% |  |  | 0 | 70.4 |  | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
6 | September | 9 | 2022-09-01 | 2022 | FY23 | 30 |  |  | 5.56 |  |  | 11125.3402 | 70.4 |  |  | 0 |  |  | 370.8447 | 0 | 0 | 21.95% |  |  | 0 | 70.4 |  | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
7 | October | 10 | 2022-10-01 | 2022 | FY23 | 31 |  |  | 4.1733 |  |  | 4626.5134 | 70.4 |  |  | 0 |  |  | 149.2424 | 0 | 0 | 8.833% |  |  | 0 | 70.4 |  | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
8 | November | 11 | 2022-11-01 | 2022 | FY23 | 30 |  |  | 4.4633 |  |  | 7150.0662 | 70.4 |  |  | 0 |  |  | 238.3355 | 0 | 0 | 14.11% |  |  | 0 | 70.4 |  | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
9 | December | 12 | 2022-12-01 | 2022 | FY23 | 31 |  |  | 4.79 |  |  | 7204.3361 | 70.4 |  |  | 0 |  |  | 232.3979 | 0 | 0 | 13.75% |  |  | 0 | 70.4 |  | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
10 | January | 1 | 2023-01-01 | 2023 | FY23 | 31 |  |  | 3.75 |  |  | 3283.3321 | 70.4 |  |  | 0 |  |  | 105.9139 | 0 | 0 | 6.269% |  |  | 0 | 70.4 |  | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
11 | February | 2 | 2023-02-01 | 2023 | FY23 | 28 |  |  | 3.925 |  |  | 3324.0346 | 70.4 |  |  | 0 |  |  | 118.7155 | 0 | 0 | 7.026% |  |  | 0 | 70.4 |  | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
12 | March | 4 | 2023-03-01 | 2023 | FY23 | 31 |  |  | 4.565 |  |  | 5467.6977 | 70.4 |  |  | 0 |  |  | 176.3773 | 0 | 0 | 10.44% |  |  | 0 | 70.4 |  | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
13 | April | 5 | 2023-04-01 | 2023 | FY24 | 30 |  |  | 5.22 |  |  | 6300 | 70.4 |  |  | 0 |  |  | 210 | 0 | 0 | 12.43% |  |  | 0 | 70.4 |  | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
14 | May | 6 | 2023-05-01 | 2023 | FY24 | 31 |  |  | 5.7233 |  |  | 10320 | 70.4 |  |  | 0 |  |  | 332.9032 | 0 | 0 | 19.7% |  |  | 0 | 70.4 |  | 5.9682 | 6.1861 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
15 | June | 7 | 2023-06-01 | 2023 | FY24 | 30 |  |  | 6.81 |  |  | 14360 | 70.4 |  |  | 0 |  |  | 478.6667 | 0 | 0 | 28.33% |  |  | 0 | 70.4 |  | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
16 | July | 8 | 2023-07-01 | 2023 | FY24 | 31 |  |  | 9.8233 |  |  | 26690 | 70.4 |  |  | 0 |  |  | 860.9677 | 0 | 0 | 50.96% |  |  | 0 | 70.4 |  | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
17 | August | 9 | 2023-08-01 | 2023 | FY24 | 31 |  |  | 9.1 |  |  | 31190 | 70.4 |  |  | 0 |  |  | 1006.129 | 0 | 0 | 59.55% |  |  | 0 | 70.4 |  | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
18 | September | 10 | 2023-09-01 | 2023 | FY24 | 30 |  |  | 5.56 |  |  | 10320 | 70.4 |  |  | 0 |  |  | 344 | 0 | 0 | 20.36% |  |  | 0 | 70.4 |  | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
19 | October | 11 | 2023-10-01 | 2023 | FY24 | 31 |  |  | 4.1733 |  |  | 4720 | 70.4 |  |  | 0 |  |  | 152.2581 | 0 | 0 | 9.011% |  |  | 0 | 70.4 |  | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
20 | November | 12 | 2023-11-01 | 2023 | FY24 | 30 |  |  | 4.4633 |  |  | 7060 | 70.4 |  |  | 0 |  |  | 235.3333 | 0 | 0 | 13.93% |  |  | 0 | 70.4 |  | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
21 | December | 1 | 2023-12-01 | 2023 | FY24 | 31 |  |  | 4.79 |  |  | 7340 | 70.4 |  |  | 0 |  |  | 236.7742 | 0 | 0 | 14.01% |  |  | 0 | 70.4 |  | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
22 | January | 2 | 2024-01-01 | 2024 | FY24 | 31 |  |  | 3.75 |  |  | 3350 | 70.4 |  |  | 0 |  |  | 108.0645 | 0 | 0 | 6.396% |  |  | 0 | 70.4 |  | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
23 | February | 4 | 2024-02-01 | 2024 | FY24 | 29 |  |  | 3.925 |  |  | 3170 | 70.4 |  |  | 0 |  |  | 109.3103 | 0 | 0 | 6.47% |  |  | 0 | 70.4 |  | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
24 | March | 5 | 2024-03-01 | 2024 | FY24 | 31 |  |  | 4.565 |  |  | 5570 | 70.4 |  |  | 0 |  |  | 179.6774 | 0 | 0 | 10.63% |  |  | 0 | 70.4 |  | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
25 | April | 6 | 2024-04-01 | 2024 | FY25 | 30 |  |  | 5.22 |  |  | 6843.4 | 70.4 |  |  | 0 |  |  | 228.1133 | 0 | 532.0645 | 13.5% |  |  | 0 | 70.4 |  | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
26 | May | 7 | 2024-05-01 | 2024 | FY25 | 31 |  |  | 5.7233 |  |  | 10848.5 | 70.4 |  |  | 0 |  |  | 349.9516 | 0 | 532.0645 | 20.71% |  |  | 0 | 70.4 |  | 5.9682 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
27 | June | 8 | 2024-06-01 | 2024 | FY25 | 30 |  |  | 6.81 |  |  | 15593.1 | 70.4 |  |  | 0 |  |  | 519.77 | 0 | 0 | 30.76% |  |  | 0 | 70.4 |  | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
28 | July | 9 | 2024-07-01 | 2024 | FY25 | 31 |  |  | 9.8233 |  |  | 28051.7 | 70.4 |  |  | 0 |  |  | 904.8935 | 0 | 0 | 53.56% |  |  | 0 | 70.4 |  | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
29 | August | 10 | 2024-08-01 | 2024 | FY25 | 31 |  |  | 9.1 |  |  | 32781.6 | 70.4 |  |  | 0 |  |  | 1057.471 | 0 | 0 | 62.59% |  |  | 0 | 70.4 |  | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
30 | September | 11 | 2024-09-01 | 2024 | FY25 | 30 |  |  | 5.56 |  |  | 11201.7 | 70.4 |  |  | 0 |  |  | 373.39 | 0 | 0 | 22.1% |  |  | 0 | 70.4 |  | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
31 | October | 12 | 2024-10-01 | 2024 | FY25 | 31 |  |  | 4.1733 |  |  | 4658.2 | 70.4 |  |  | 0 |  |  | 150.2645 | 0 | 0 | 8.893% |  |  | 0 | 70.4 |  | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
32 | November | 1 | 2024-11-01 | 2024 | FY25 | 30 |  |  | 4.4633 |  |  | 7203.1 | 70.4 |  |  | 0 |  |  | 240.1033 | 0 | 0 | 14.21% |  |  | 0 | 70.4 |  | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
33 | December | 2 | 2024-12-01 | 2024 | FY25 | 31 |  |  | 4.79 |  |  | 7252 | 70.4 |  |  | 0 |  |  | 233.9355 | 0 | 0 | 13.85% |  |  | 0 | 70.4 |  | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
34 | January | 4 | 2025-01-01 | 2025 | FY25 | 31 |  |  | 3.75 |  |  | 3308.3 | 70.4 |  |  | 0 |  |  | 106.7194 | 0 | 0 | 6.316% |  |  | 0 | 70.4 |  | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
35 | February | 5 | 2025-02-01 | 2025 | FY25 | 28 |  |  | 3.925 |  |  | 3320.2 | 70.4 |  |  | 0 |  |  | 118.5786 | 0 | 0 | 7.018% |  |  | 0 | 70.4 |  | 7.0533 | 7.31 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
36 | March | 6 | 2025-03-01 | 2025 | FY25 | 31 |  |  | 4.565 |  |  | 5498 | 70.4 |  |  | 3 |  |  | 177.3548 | 532.0645 | 532.0645 | 10.5% | 10.5% | 10.5% | 6.8129 | 70.4 |  | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
37 | April | 7 | 2025-04-01 | 2025 | FY26 | 30 |  |  | 5.22 |  |  | 6843.3984 | 70.4 |  |  | 30 |  |  | 228.1133 | 6843.3984 | 6843.3984 | 13.5% | 13.5% | 13.5% | 70.4 | 70.4 |  | 6.4041 | 6.4041 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
38 | May | 8 | 2025-05-01 | 2025 | FY26 | 31 |  |  | 5.7233 |  |  | 10848.466 | 70.4 |  |  | 31 |  |  | 349.9505 | 10848.466 | 17691.8644 | 20.71% | 20.71% | 17.17% | 70.4 | 70.4 |  | 5.9682 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
39 | June | 9 | 2025-06-01 | 2025 | FY26 | 30 |  |  | 6.81 |  |  | 15593.0879 | 70.4 |  |  | 30 |  |  | 519.7696 | 15593.0879 | 33284.9523 | 30.76% | 30.76% | 21.65% | 70.4 | 70.4 |  | 5.6311 | 6.0011 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
40 | July | 10 | 2025-07-01 | 2025 | FY26 | 31 |  |  | 9.8233 |  |  | 28051.7141 | 70.4 |  |  | 9 |  |  | 904.894 | 8144.046 | 41428.9983 | 53.56% | 53.56% | 24.52% | 20.4387 | 70.4 |  | 7.1311 | 6.2836 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
41 | August | 11 | 2025-08-01 | 2025 | FY26 | 31 |  |  | 9.1 |  |  | 32781.5854 | 70.4 |  |  | 0 |  |  | 1057.4705 | 0 | 41428.9983 | 62.59% |  | 24.52% | 0 | 70.4 |  | 9.453 | 6.9175 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
42 | September | 12 | 2025-09-01 | 2025 | FY26 | 30 |  |  | 5.56 |  |  | 11201.6537 | 70.4 |  |  | 0 |  |  | 373.3885 | 0 | 41428.9983 | 22.1% |  | 24.52% | 0 | 70.4 |  | 10.3038 | 7.4819 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
43 | October | 1 | 2025-10-01 | 2025 | FY26 | 31 |  |  | 4.1733 |  |  | 4658.2035 | 70.4 |  |  | 0 |  |  | 150.2646 | 0 | 41428.9983 | 8.894% |  | 24.52% | 0 | 70.4 |  | 8.5195 | 7.6301 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
44 | November | 2 | 2025-11-01 | 2025 | FY26 | 30 |  |  | 4.4633 |  |  | 7203.0753 | 70.4 |  |  | 0 |  |  | 240.1025 | 0 | 41428.9983 | 14.21% |  | 24.52% | 0 | 70.4 |  | 7.2367 | 7.5809 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
45 | December | 4 | 2025-12-01 | 2025 | FY26 | 31 |  |  | 4.79 |  |  | 7252.0328 | 70.4 |  |  | 0 |  |  | 233.9365 | 0 | 41428.9983 | 13.85% |  | 24.52% | 0 | 70.4 |  | 6.0016 | 7.4054 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
46 | January | 5 | 2026-01-01 | 2026 | FY26 | 31 |  |  | 3.75 |  |  | 3308.3229 | 70.4 |  |  | 0 |  |  | 106.7201 | 0 | 41428.9983 | 6.316% |  | 24.52% | 0 | 70.4 |  | 6.7074 | 7.3356 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
47 | February | 6 | 2026-02-01 | 2026 | FY26 | 28 |  |  | 3.925 |  |  | 3320.2002 | 70.4 |  |  | 0 |  |  | 118.5786 | 0 | 41428.9983 | 7.018% |  | 24.52% | 0 | 70.4 |  | 7.0533 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
48 | March | 7 | 2026-03-01 | 2026 | FY26 | 31 |  |  | 4.565 |  |  | 5498.0142 | 70.4 |  |  | 0 |  |  | 177.3553 | 0 | 41428.9983 | 10.5% |  | 24.52% | 0 | 70.4 |  | 7.4111 | 7.3184 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))