## Dashboard
Performance Summary of JPPL 50 MW Agra as on date and YTD
Month | 2025-07-01
Date | 2025-07-23
Operation Year | FY26
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 224.1121 | 110.7543 | -50.58%
| E_Grid MTD(MWh) | 5154.5775 | 4981.0177 | -3.367%
| E_Grid YTD (MWh) | 33310.432 | 31524.4362 | -5.362%
2 | CUF Daily(%) | 13.99% | 6.914% | -50.58%
| CUF MTD(%) | 13.99% | 13.52% | -3.367%
| CUF YTD(%) | 18.24% | 17.26% | -5.362%
3 | PR_Daily (%) | 77.09% | 79.01% | 2.49%
| PR_MTD (%) | 77.09% | 77.65% | 0.7272%
| PR_YTD (%) | 76.12% | 76.14% | 0.03418%
4 | POA Daily (KWh/m2) | 4.3548 | 2.1 | -51.78%
| POA MTD(KWh/m2) | 100.1613 | 96.09 | -4.065%
| POA YTD(KWh/m2) | 655.5613 | 620.2002 | -5.394%
5 | PA Daily | 99.5% | 99.87% | 0.3687%
| PA MTD | 99.5% | 99.74% | 0.2411%
| PA YTD | 99.5% | 98.91% | -0.5912%
6 | GA Daily | 99.5% | 100% | 0.5025%
| GA MTD | 99.5% | 100% | 0.5025%
| GA YTD | 99.5% | 100% | 0.5025%

## Annual_KPI
Till Date | 2025-07-23 | 2025-07-01
JPPL 50 MW Performance Summary-YTD
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2026 | 114 | 655.5613 | 620.2002 | 33310.432 | 31524.4362 | 76.12% | 76.14% | 18.24% | 17.26% | 99.5% | 100% | 99.5% | 98.91% | 0 | 0
JPPL 50 MW Performance Summary-Monthwise
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-04-01 | 30 | 206.6 | 181.3903 | 10495.2627 | 9324.465 | 76.1% | 77.01% | 21.84% | 19.4% | 99.5% | 100% | 99.5% | 99.69% | 0 | 0
2025-05-01 | 31 | 191.7 | 182.72 | 9688.8168 | 8998.9708 | 75.71% | 73.78% | 19.51% | 18.12% | 99.5% | 100% | 99.5% | 97.38% | 0 | 0
2025-06-01 | 30 | 157.1 | 160 | 7971.775 | 8219.9827 | 76.01% | 76.96% | 16.59% | 17.1% | 99.5% | 100% | 99.5% | 99.09% | 0 | 0
2025-07-01 | 23 | 100.1613 | 96.09 | 5154.5775 | 4981.0177 | 77.09% | 77.65% | 13.99% | 13.52% | 99.5% | 100% | 99.5% | 99.74% | 0 | 0
2025-08-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2025-09-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2025-10-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2025-11-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2025-12-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2026-01-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2026-02-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2026-03-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0

## Monthly_KPI
Till Date | 2025-07-23
JPPL 50 MW Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-07-01 | 23 | 100.1613 | 96.09 | 5154.5775 | 4981.0177 | 77.09% | 77.65% | 13.99% | 13.52% | 99.5% | 100% | 99.5% | 99.74% | 0 | 0
Start Date | 2025-07-17
End Date | 2025-07-23
JPPL50 MW Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-07-01 | 7 | 30.4839 | 28.27 | 1568.7845 | 1475.4415 | 77.09% | 78.18% | 13.99% | 13.16% | 99.5% | 100% | 99.5% | 99.88% | 0 | 0
Formulas:
Days = [Days, row below]-6

## Grass_Ct
Sr. No. | Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Cycle Number | Resources | Blk1 | Blk2 | Blk3 | Blk4 | Blk5 | Blk6 | Blk7 | Blk8 | Total No.Table GC done | Mrthod of Cutting | Remarks for the day
1 | 2023-10-01 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
2 | 2023-10-02 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
3 | 2023-10-03 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
4 | 2023-10-04 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
5 | 2023-10-05 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
6 | 2023-10-06 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
7 | 2023-10-07 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
8 | 2023-10-08 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
9 | 2023-10-09 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
10 | 2023-10-10 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
11 | 2023-10-11 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
12 | 2023-10-12 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
13 | 2023-10-13 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
14 | 2023-10-14 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
15 | 2023-10-15 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
16 | 2023-10-16 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
17 | 2023-10-17 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
18 | 2023-10-18 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
19 | 2023-10-19 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
20 | 2023-10-20 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
21 | 2023-10-21 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
22 | 2023-10-22 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
23 | 2023-10-23 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
24 | 2023-10-24 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
25 | 2023-10-25 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
26 | 2023-10-26 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
27 | 2023-10-27 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
28 | 2023-10-28 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
29 | 2023-10-29 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
30 | 2023-10-30 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
31 | 2023-10-31 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
32 | 2023-11-01 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
33 | 2023-11-02 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
34 | 2023-11-03 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
35 | 2023-11-04 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
36 | 2023-11-05 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
37 | 2023-11-06 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
38 | 2023-11-07 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
39 | 2023-11-08 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
40 | 2023-11-09 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
41 | 2023-11-10 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
42 | 2023-11-11 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
43 | 2023-11-12 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
44 | 2023-11-13 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
45 | 2023-11-14 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
46 | 2023-11-15 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
47 | 2023-11-16 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
48 | 2023-11-17 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
49 | 2023-11-18 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
50 | 2023-11-19 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
51 | 2023-11-20 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
52 | 2023-11-21 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
53 | 2023-11-22 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
54 | 2023-11-23 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
55 | 2023-11-24 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
56 | 2023-11-25 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
57 | 2023-11-26 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
58 | 2023-11-27 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
59 | 2023-11-28 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
60 | 2023-11-29 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
61 | 2023-11-30 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
62 | 2023-12-01 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
63 | 2023-12-02 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
64 | 2023-12-03 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
65 | 2023-12-04 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
66 | 2023-12-05 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
67 | 2023-12-06 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
68 | 2023-12-07 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
69 | 2023-12-08 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
70 | 2023-12-09 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
71 | 2023-12-10 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
72 | 2023-12-11 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
73 | 2023-12-12 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
74 | 2023-12-13 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
75 | 2023-12-14 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
76 | 2023-12-15 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
77 | 2023-12-16 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
78 | 2023-12-17 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
79 | 2023-12-18 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
80 | 2023-12-19 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
81 | 2023-12-20 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
82 | 2023-12-21 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
83 | 2023-12-22 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
84 | 2023-12-23 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
85 | 2023-12-24 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
86 | 2023-12-25 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
87 | 2023-12-26 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
88 | 2023-12-27 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
89 | 2023-12-28 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
90 | 2023-12-29 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
91 | 2023-12-30 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
92 | 2023-12-31 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
93 | 2024-01-01 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
94 | 2024-01-02 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
95 | 2024-01-03 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
96 | 2024-01-04 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
97 | 2024-01-05 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
98 | 2024-01-06 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
99 | 2024-01-07 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
100 | 2024-01-08 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
101 | 2024-01-09 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
102 | 2024-01-10 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
103 | 2024-01-11 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
104 | 2024-01-12 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
105 | 2024-01-13 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
106 | 2024-01-14 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
107 | 2024-01-15 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
108 | 2024-01-16 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
109 | 2024-01-17 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
110 | 2024-01-18 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
111 | 2024-01-19 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
112 | 2024-01-20 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
113 | 2024-01-21 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
114 | 2024-01-22 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
115 | 2024-01-23 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
116 | 2024-01-24 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
117 | 2024-01-25 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
118 | 2024-01-26 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
119 | 2024-01-27 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
120 | 2024-01-28 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
120 | 2024-01-29 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
122 | 2024-01-30 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
123 | 2024-01-31 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
124 | 2024-02-01 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
125 | 2024-02-02 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
126 | 2024-02-03 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-04 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-05 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-06 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-07 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-08 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-09 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-10 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-11 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-12 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-13 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-14 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-15 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
139 | 2024-02-16 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
140 | 2024-02-17 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
141 | 2024-02-18 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
142 | 2024-02-19 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
143 | 2024-02-20 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
144 | 2024-02-21 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
145 | 2024-02-22 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
146 | 2024-02-23 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
147 | 2024-02-24 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
148 | 2024-02-25 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
149 | 2024-02-26 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
150 | 2024-02-27 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
151 | 2024-02-28 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
152 | 2024-02-29 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
153 | 2024-03-01 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
154 | 2024-03-02 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
155 | 2024-03-03 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
156 | 2024-03-04 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
157 | 2024-03-05 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
158 | 2024-03-06 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
159 | 2024-03-07 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
160 | 2024-03-08 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
161 | 2024-03-09 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
162 | 2024-03-10 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
163 | 2024-03-11 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
164 | 2024-03-12 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
165 | 2024-03-13 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
166 | 2024-03-14 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
167 | 2024-03-15 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
168 | 2024-03-16 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
169 | 2024-03-17 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
170 | 2024-03-18 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
171 | 2024-03-19 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
172 | 2024-03-20 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
173 | 2024-03-21 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
174 | 2024-03-22 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
175 | 2024-03-23 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
176 | 2024-03-24 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
177 | 2024-03-25 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
177 | 2024-03-26 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
179 | 2024-03-27 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
180 | 2024-03-28 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
181 | 2024-03-29 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
182 | 2024-03-30 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
183 | 2024-03-31 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
184 | 2024-04-01 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
185 | 2024-04-02 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
186 | 2024-04-03 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
187 | 2024-04-04 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
188 | 2024-04-05 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
189 | 2024-04-06 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
190 | 2024-04-07 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
191 | 2024-04-08 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
192 | 2024-04-09 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
193 | 2024-04-10 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
194 | 2024-04-11 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
195 | 2024-04-12 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
196 | 2024-04-13 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
197 | 2024-04-14 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
198 | 2024-04-15 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
199 | 2024-04-16 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
200 | 2024-04-17 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
201 | 2024-04-18 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
202 | 2024-04-19 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
203 | 2024-04-20 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
204 | 2024-04-21 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
205 | 2024-04-22 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
206 | 2024-04-23 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
207 | 2024-04-24 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
208 | 2024-04-25 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
209 | 2024-04-26 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
210 | 2024-04-27 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
211 | 2024-04-28 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
212 | 2024-04-29 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
213 | 2024-04-30 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
214 | 2024-05-01 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
215 | 2024-05-02 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
216 | 2024-05-03 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
217 | 2024-05-04 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
218 | 2024-05-05 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
219 | 2024-05-06 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
220 | 2024-05-07 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
221 | 2024-05-08 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
222 | 2024-05-09 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
223 | 2024-05-10 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
224 | 2024-05-11 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
225 | 2024-05-12 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
226 | 2024-05-13 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
227 | 2024-05-14 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
228 | 2024-05-15 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
229 | 2024-05-16 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
230 | 2024-05-17 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 130
231 | 2024-05-18 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
232 | 2024-05-19 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
233 | 2024-05-20 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
234 | 2024-05-21 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
235 | 2024-05-22 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
236 | 2024-05-23 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
237 | 2024-05-24 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
238 | 2024-05-25 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
239 | 2024-05-26 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
240 | 2024-05-27 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
241 | 2024-05-28 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
242 | 2024-05-29 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
243 | 2024-05-30 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
244 | 2024-05-31 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
245 | 2024-06-01 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
246 | 2024-06-02 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
247 | 2024-06-03 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
248 | 2024-06-04 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
249 | 2024-06-05 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
250 | 2024-06-06 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
251 | 2024-06-07 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
252 | 2024-06-08 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
253 | 2024-06-09 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
254 | 2024-06-10 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
255 | 2024-06-11 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
256 | 2024-06-12 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
257 | 2024-06-13 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
258 | 2024-06-14 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
259 | 2024-06-15 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
260 | 2024-06-16 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
261 | 2024-06-17 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
262 | 2024-06-18 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
263 | 2024-06-19 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
264 | 2024-06-20 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
265 | 2024-06-21 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
266 | 2024-06-22 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
267 | 2024-06-23 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
268 | 2024-06-24 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
269 | 2024-06-25 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
270 | 2024-06-26 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
271 | 2024-06-27 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
272 | 2024-06-28 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
273 | 2024-06-29 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
274 | 2024-06-30 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
275 | 2024-07-01 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
276 | 2024-07-02 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
277 | 2024-07-03 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
278 | 2024-07-04 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
279 | 2024-07-05 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
280 | 2024-07-06 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0 |  | It was raining so grass could not be harvested
281 | 2024-07-07 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0 |  | It was raining so grass could not be harvested
282 | 2024-07-08 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0 |  | It was raining so grass could not be harvested
283 | 2024-07-09 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
284 | 2024-07-10 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
285 | 2024-07-11 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
286 | 2024-07-12 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
287 | 2024-07-13 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
288 | 2024-07-14 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
289 | 2024-07-15 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
290 | 2024-07-16 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
291 | 2024-07-17 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
292 | 2024-07-18 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
293 | 2024-07-19 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
294 | 2024-07-20 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
295 | 2024-07-21 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
296 | 2024-07-22 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
297 | 2024-07-23 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
298 | 2024-07-24 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
299 | 2024-07-25 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
300 | 2024-07-26 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
301 | 2024-07-27 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
302 | 2024-07-28 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
303 | 2024-07-29 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
304 | 2024-07-30 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
305 | 2024-07-31 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
306 | 2024-08-01 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
307 | 2024-08-02 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
308 | 2024-08-03 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
309 | 2024-08-04 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
310 | 2024-08-05 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
311 | 2024-08-06 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
312 | 2024-08-07 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
313 | 2024-08-08 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
314 | 2024-08-09 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
315 | 2024-08-10 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
316 | 2024-08-11 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
317 | 2024-08-12 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
318 | 2024-08-13 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
319 | 2024-08-14 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
320 | 2024-08-15 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
321 | 2024-08-16 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
322 | 2024-08-17 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
323 | 2024-08-18 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
324 | 2024-08-19 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
325 | 2024-08-20 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
326 | 2024-08-21 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
327 | 2024-08-22 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
328 | 2024-08-23 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
329 | 2024-08-24 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
330 | 2024-08-25 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
331 | 2024-08-26 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
332 | 2024-08-27 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
333 | 2024-08-28 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
334 | 2024-08-29 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
335 | 2024-08-30 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
336 | 2024-08-31 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
337 | 2024-09-01 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
338 | 2024-09-02 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
339 | 2024-09-03 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
340 | 2024-09-04 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
341 | 2024-09-05 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
342 | 2024-09-06 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
343 | 2024-09-07 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
344 | 2024-09-08 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
345 | 2024-09-09 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
346 | 2024-09-10 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
347 | 2024-09-11 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
348 | 2024-09-12 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
349 | 2024-09-13 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
350 | 2024-09-14 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
351 | 2024-09-15 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
352 | 2024-09-16 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
353 | 2024-09-17 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
354 | 2024-09-18 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
355 | 2024-09-19 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
356 | 2024-09-20 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
357 | 2024-09-21 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
358 | 2024-09-22 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
359 | 2024-09-23 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
360 | 2024-09-24 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
361 | 2024-09-25 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
362 | 2024-09-26 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
363 | 2024-09-27 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
364 | 2024-09-28 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
365 | 2024-09-29 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
366 | 2024-09-30 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
367 | 2024-10-01 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
368 | 2024-10-02 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
369 | 2024-10-03 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
370 | 2024-10-04 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
371 | 2024-10-05 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
372 | 2024-10-06 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
373 | 2024-10-07 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
374 | 2024-10-08 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
375 | 2024-10-09 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
376 | 2024-10-10 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
377 | 2024-10-11 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
378 | 2024-10-12 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
379 | 2024-10-13 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
380 | 2024-10-14 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
381 | 2024-10-15 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
382 | 2024-10-16 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
383 | 2024-10-17 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
384 | 2024-10-18 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
385 | 2024-10-19 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
386 | 2024-10-20 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
387 | 2024-10-21 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
388 | 2024-10-22 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
389 | 2024-10-23 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
390 | 2024-10-24 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
391 | 2024-10-25 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
392 | 2024-10-26 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
393 | 2024-10-27 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
394 | 2024-10-28 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
395 | 2024-10-29 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
396 | 2024-10-30 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
397 | 2024-10-31 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
398 | 2024-11-01 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
399 | 2024-11-02 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
400 | 2024-11-03 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
401 | 2024-11-04 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
402 | 2024-11-05 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
403 | 2024-11-06 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
404 | 2024-11-07 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
405 | 2024-11-08 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
406 | 2024-11-09 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
407 | 2024-11-10 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
408 | 2024-11-11 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
409 | 2024-11-12 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
410 | 2024-11-13 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
411 | 2024-11-14 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
412 | 2024-11-15 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
413 | 2024-11-16 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
414 | 2024-11-17 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
415 | 2024-11-18 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
416 | 2024-11-19 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
417 | 2024-11-20 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
418 | 2024-11-21 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
419 | 2024-11-22 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
420 | 2024-11-23 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
421 | 2024-11-24 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
422 | 2024-11-25 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
423 | 2024-11-26 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
424 | 2024-11-27 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
425 | 2024-11-28 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
426 | 2024-11-29 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
427 | 2024-11-30 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
428 | 2024-12-01 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
429 | 2024-12-02 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
430 | 2024-12-03 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
431 | 2024-12-04 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
432 | 2024-12-05 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
433 | 2024-12-06 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
434 | 2024-12-07 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
435 | 2024-12-08 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
436 | 2024-12-09 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
437 | 2024-12-10 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
438 | 2024-12-11 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
439 | 2024-12-12 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
440 | 2024-12-13 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
441 | 2024-12-14 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
442 | 2024-12-15 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
443 | 2024-12-16 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
444 | 2024-12-17 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
445 | 2024-12-18 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
446 | 2024-12-19 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
447 | 2024-12-20 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
448 | 2024-12-21 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
449 | 2024-12-22 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
450 | 2024-12-23 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
451 | 2024-12-24 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
452 | 2024-12-25 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
453 | 2024-12-26 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
454 | 2024-12-27 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
455 | 2024-12-28 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
456 | 2024-12-29 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
457 | 2024-12-30 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
458 | 2024-12-31 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
459 | 2025-01-01 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
460 | 2025-01-02 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
461 | 2025-01-03 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
462 | 2025-01-04 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
463 | 2025-01-05 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
464 | 2025-01-06 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
465 | 2025-01-07 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
466 | 2025-01-08 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
467 | 2025-01-09 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
468 | 2025-01-10 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
469 | 2025-01-11 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
470 | 2025-01-12 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
471 | 2025-01-13 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
472 | 2025-01-14 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
473 | 2025-01-15 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
474 | 2025-01-16 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
475 | 2025-01-17 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
476 | 2025-01-18 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
477 | 2025-01-19 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
478 | 2025-01-20 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
479 | 2025-01-21 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
480 | 2025-01-22 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
481 | 2025-01-23 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting happened near MCR area.
482 | 2025-01-24 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting happened near MCR area.
483 | 2025-01-25 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
484 | 2025-01-26 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
485 | 2025-01-27 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
486 | 2025-01-28 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
487 | 2025-01-29 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
488 | 2025-01-30 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
489 | 2025-01-31 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
490 | 2025-02-01 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
491 | 2025-02-02 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
492 | 2025-02-03 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
493 | 2025-02-04 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
494 | 2025-02-05 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
495 | 2025-02-06 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
496 | 2025-02-07 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
497 | 2025-02-08 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
498 | 2025-02-09 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
499 | 2025-02-10 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
500 | 2025-02-11 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
501 | 2025-02-12 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
502 | 2025-02-13 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
503 | 2025-02-14 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
504 | 2025-02-15 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
505 | 2025-02-16 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
506 | 2025-02-17 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
507 | 2025-02-18 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
508 | 2025-02-19 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
509 | 2025-02-20 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
510 | 2025-02-21 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
511 | 2025-02-22 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
512 | 2025-02-23 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
513 | 2025-02-24 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
514 | 2025-02-25 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
515 | 2025-02-26 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
516 | 2025-02-27 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
517 | 2025-02-28 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
518 | 2025-03-01 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
519 | 2025-03-02 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
520 | 2025-03-03 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
521 | 2025-03-04 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
522 | 2025-03-05 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
523 | 2025-03-06 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
524 | 2025-03-07 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
525 | 2025-03-08 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
527 | 2025-03-09 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
528 | 2025-03-10 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
529 | 2025-03-11 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
530 | 2025-03-12 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
531 | 2025-03-13 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
532 | 2025-03-14 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
533 | 2025-03-15 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
534 | 2025-03-16 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
535 | 2025-03-17 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
536 | 2025-03-18 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
537 | 2025-03-19 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
538 | 2025-03-20 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
539 | 2025-03-21 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
540 | 2025-03-22 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
541 | 2025-03-23 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
542 | 2025-03-24 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
543 | 2025-03-25 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
544 | 2025-03-26 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
545 | 2025-03-27 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
546 | 2025-03-28 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
547 | 2025-03-29 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
548 | 2025-03-30 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
549 | 2025-03-31 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
550 | 2025-04-01 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | [10 empty] | 0
551 | 2025-04-02 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk5: 90 | 90 | Tractor Based Rotavetor
552 | 2025-04-03 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk5: 118 | 118 | Tractor Based Rotavetor
553 | 2025-04-04 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk5: 112 | 112 | Tractor Based Rotavetor
554 | 2025-04-05 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | [8 empty] | 0 | Tractor Based Rotavetor
555 | 2025-04-06 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk6: 120 | 120 | Tractor Based Rotavetor
556 | 2025-04-07 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk6: 50 | 50 | Tractor Based Rotavetor
557 | 2025-04-08 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk6: 20 | 20 | Tractor Based Rotavetor
558 | 2025-04-09 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | [8 empty] | 0 | Tractor Based Rotavetor
559 | 2025-04-10 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk6: 24 | 24 | Tractor Based Rotavetor
560 | 2025-04-11 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Honda Machine | Blk5: 50; Blk6: 49 | 99 | Honda Machine
561 | 2025-04-12 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Honda Machine | Blk5: 45; Blk6: 50 | 95 | Honda Machine
562 | 2025-04-13 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Honda Machine | [8 empty] | 0 | Honda Machine
563 | 2025-04-14 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Honda Machine | Blk5: 65 | 65 | Honda Machine
564 | 2025-04-15 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk6: 82 | 82 | Tractor Based Rotavetor
565 | 2025-04-16 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk1: 60 | 60 | Tractor Based Rotavetor
566 | 2025-04-17 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk1: 130 | 130 | Tractor Based Rotavetor
567 | 2025-04-18 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk1: 40; Blk2: 80; Blk3: 80 | 200 | Tractor Based Rotavetor
568 | 2025-04-19 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk1: 95; Blk2: 95; Blk3: 130 | 320 | Tractor Based Rotavetor
569 | 2025-04-21 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk1: 30; Blk2: 35; Blk3: 25 | 90 | Tractor Based Rotavetor
570 | 2025-04-22 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk2: 40; Blk3: 40 | 80 | Tractor Based Rotavetor
571 | 2025-04-23 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk2: 40 | 40 | Tractor Based Rotavetor
572 | 2025-04-24 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk4: 140 | 140 | Tractor Based Rotavetor
573 | 2025-04-25 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk7: 80 | 80 | Tractor Based Rotavetor
574 | 2025-04-26 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk7: 120 | 120 | Tractor Based Rotavetor
575 | 2025-04-27 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk7: 80 | 80 | Tractor Based Rotavetor
576 | 2025-04-28 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk7: 70 | 70 | Tractor Based Rotavetor
577 | 2025-04-29 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Honda Machine | Blk1: 40; Blk2: 40 | 80 | Honda Machine
578 | 2025-04-30 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 80 | 80
579 | 2025-05-01 | 2026 | 2025 |  |  | May-25 | 31 |  |  | Blk8: 40 | 40
580 | 2025-05-02 | 2026 | 2025 |  |  | May-25 | 31 | [10 empty] | 0
581 | 2025-05-03 | 2026 | 2025 |  |  | May-25 | 31 |  |  | Blk8: 100 | 100 | Tractor Based Rotavetor & Honda Machine
582 | 2025-05-04 | 2026 | 2025 |  |  | May-25 | 31 |  | Honda Machine | Blk8: 90 | 90 | Honda Machine
583 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
584 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
585 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
586 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
587 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
588 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
589 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
590 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
591 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
592 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
593 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
594 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
595 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
596 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
597 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
598 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
599 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
600 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
601 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
602 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
603 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
604 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
605 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
606 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
607 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
608 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
609 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
610 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
611 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
612 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
613 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
614 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
615 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
616 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
617 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
618 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
619 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
620 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
621 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
622 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
623 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
624 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
625 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
626 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
627 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
628 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
629 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
630 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
631 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
632 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
633 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
634 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
635 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
636 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
637 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
638 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
639 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
640 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
641 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
642 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
Formulas:
Days = DAY(EOMONTH(GC[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## Mod_CL
Sr. No. | Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Cycle Number | Resources | Blk1 | Blk2 | Blk3 | Blk4 | Blk5 | Blk6 | Blk7 | Blk8 | Total NO. Module cleaned | Morning Start Time | Morning End Time | Evening Start Time | Evening End time | Brush/MOP Replcemnet | Water Test Report | Remarks for the day
1 | 2023-10-01 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
2 | 2023-10-02 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
3 | 2023-10-03 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
4 | 2023-10-04 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
5 | 2023-10-05 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
6 | 2023-10-06 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
7 | 2023-10-07 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
8 | 2023-10-08 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
9 | 2023-10-09 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
10 | 2023-10-10 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
11 | 2023-10-11 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
12 | 2023-10-12 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
13 | 2023-10-13 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
14 | 2023-10-14 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
15 | 2023-10-15 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
16 | 2023-10-16 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
17 | 2023-10-17 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
18 | 2023-10-18 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
19 | 2023-10-19 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
20 | 2023-10-20 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
21 | 2023-10-21 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
22 | 2023-10-22 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
23 | 2023-10-23 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
24 | 2023-10-24 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
25 | 2023-10-25 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
26 | 2023-10-26 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
27 | 2023-10-27 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
28 | 2023-10-28 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
29 | 2023-10-29 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
30 | 2023-10-30 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
31 | 2023-10-31 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
32 | 2023-11-01 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
33 | 2023-11-02 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
34 | 2023-11-03 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
35 | 2023-11-04 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
36 | 2023-11-05 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
37 | 2023-11-06 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
38 | 2023-11-07 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
39 | 2023-11-08 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
40 | 2023-11-09 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
41 | 2023-11-10 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
42 | 2023-11-11 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
43 | 2023-11-12 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
44 | 2023-11-13 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
45 | 2023-11-14 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
46 | 2023-11-15 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
47 | 2023-11-16 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
48 | 2023-11-17 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
49 | 2023-11-18 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
50 | 2023-11-19 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
51 | 2023-11-20 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
52 | 2023-11-21 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
53 | 2023-11-22 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
54 | 2023-11-23 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
55 | 2023-11-24 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
56 | 2023-11-25 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
57 | 2023-11-26 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
58 | 2023-11-27 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
59 | 2023-11-28 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
60 | 2023-11-29 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
61 | 2023-11-30 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
62 | 2023-12-01 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
63 | 2023-12-02 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
64 | 2023-12-03 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
65 | 2023-12-04 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
66 | 2023-12-05 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
67 | 2023-12-06 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
68 | 2023-12-07 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
69 | 2023-12-08 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
70 | 2023-12-09 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
71 | 2023-12-10 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
72 | 2023-12-11 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
73 | 2023-12-12 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
74 | 2023-12-13 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
75 | 2023-12-14 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
76 | 2023-12-15 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
77 | 2023-12-16 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
78 | 2023-12-17 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
79 | 2023-12-18 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
80 | 2023-12-19 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
81 | 2023-12-20 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
82 | 2023-12-21 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
83 | 2023-12-22 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
84 | 2023-12-23 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
85 | 2023-12-24 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
86 | 2023-12-25 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
87 | 2023-12-26 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
88 | 2023-12-27 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
89 | 2023-12-28 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
90 | 2023-12-29 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
91 | 2023-12-30 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
92 | 2023-12-31 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
93 | 2024-01-01 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
94 | 2024-01-02 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
95 | 2024-01-03 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
96 | 2024-01-04 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
97 | 2024-01-05 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
98 | 2024-01-06 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
99 | 2024-01-07 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
100 | 2024-01-08 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
101 | 2024-01-09 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
102 | 2024-01-10 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
103 | 2024-01-11 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
104 | 2024-01-12 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
105 | 2024-01-13 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
106 | 2024-01-14 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
107 | 2024-01-15 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
108 | 2024-01-16 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
109 | 2024-01-17 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
110 | 2024-01-18 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
111 | 2024-01-19 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
112 | 2024-01-20 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
113 | 2024-01-21 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
114 | 2024-01-22 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
115 | 2024-01-23 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
116 | 2024-01-24 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
117 | 2024-01-25 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
118 | 2024-01-26 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
119 | 2024-01-27 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
120 | 2024-01-28 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
120 | 2024-01-29 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
122 | 2024-01-30 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
123 | 2024-01-31 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
124 | 2024-02-01 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000
125 | 2024-02-02 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000
126 | 2024-02-03 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000
127 | 2024-02-04 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000
127 | 2024-02-05 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-06 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-07 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-08 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-09 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-10 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-11 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP |  | Cleaning Stop due to Fanbalt Broken
127 | 2024-02-12 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-13 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-14 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning not done due to marriage in vendor's family
127 | 2024-02-15 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning not done due to marriage in vendor's family
139 | 2024-02-16 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP |  | Cleaning stop due to Tractor pulli Broken
140 | 2024-02-17 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning Stop due to Tractor under breakdown
141 | 2024-02-18 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning Stop due to Tractor under breakdown
142 | 2024-02-19 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
143 | 2024-02-20 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 5:00 | 11:00 | MOP
144 | 2024-02-21 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
145 | 2024-02-22 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
146 | 2024-02-23 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
147 | 2024-02-24 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
148 | 2024-02-25 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
149 | 2024-02-26 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
150 | 2024-02-27 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
151 | 2024-02-28 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
152 | 2024-02-29 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
153 | 2024-03-01 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
154 | 2024-03-02 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
155 | 2024-03-03 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
156 | 2024-03-04 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
157 | 2024-03-05 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
158 | 2024-03-06 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
159 | 2024-03-07 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
160 | 2024-03-08 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Module cleaning stopped by vendor due to festival yesterday.
161 | 2024-03-09 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP |  | Venders absent
162 | 2024-03-10 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP |  | Venders absent
163 | 2024-03-11 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP |  | Venders absent
164 | 2024-03-12 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP |  | Venders absent
165 | 2024-03-13 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP |  | Venders absent
166 | 2024-03-14 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
167 | 2024-03-15 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
168 | 2024-03-16 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
169 | 2024-03-17 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
170 | 2024-03-18 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
171 | 2024-03-19 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
172 | 2024-03-20 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
173 | 2024-03-21 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
174 | 2024-03-22 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
175 | 2024-03-23 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
176 | 2024-03-24 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning Stop due to Festival
177 | 2024-03-25 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning Stop due to Festival
177 | 2024-03-26 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
179 | 2024-03-27 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP |  | Cleaning happed only evening due to tractor breadown on 26 March night.
180 | 2024-03-28 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
181 | 2024-03-29 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
182 | 2024-03-30 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
183 | 2024-03-31 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
184 | 2024-04-01 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
185 | 2024-04-02 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
186 | 2024-04-03 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
187 | 2024-04-04 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
188 | 2024-04-05 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
189 | 2024-04-06 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
190 | 2024-04-07 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
191 | 2024-04-08 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
192 | 2024-04-09 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
193 | 2024-04-10 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
194 | 2024-04-11 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
195 | 2024-04-12 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
196 | 2024-04-13 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
197 | 2024-04-14 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
198 | 2024-04-15 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
199 | 2024-04-16 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
200 | 2024-04-17 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
201 | 2024-04-18 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
202 | 2024-04-19 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
203 | 2024-04-20 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
204 | 2024-04-21 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
205 | 2024-04-22 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
206 | 2024-04-23 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
207 | 2024-04-24 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
208 | 2024-04-25 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
209 | 2024-04-26 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
210 | 2024-04-27 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
211 | 2024-04-28 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
212 | 2024-04-29 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
213 | 2024-04-30 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
214 | 2024-05-01 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
215 | 2024-05-02 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 |  |  | MOP |  | One tractor breakdown
216 | 2024-05-03 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
217 | 2024-05-04 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
218 | 2024-05-05 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 |  |  | MOP |  | One tractor breakdown
219 | 2024-05-06 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
220 | 2024-05-07 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
221 | 2024-05-08 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
222 | 2024-05-09 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 |  |  | MOP |  | One tractor breakdown
223 | 2024-05-10 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 14950 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
224 | 2024-05-11 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
225 | 2024-05-12 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
226 | 2024-05-13 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
227 | 2024-05-14 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
228 | 2024-05-15 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
229 | 2024-05-16 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
230 | 2024-05-17 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
231 | 2024-05-18 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
232 | 2024-05-19 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
233 | 2024-05-20 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
234 | 2024-05-21 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
235 | 2024-05-22 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
236 | 2024-05-23 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 |  |  | MOP |  | One tractor breakdown
237 | 2024-05-24 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
238 | 2024-05-25 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
239 | 2024-05-26 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
240 | 2024-05-27 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
241 | 2024-05-28 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 |  |  | MOP |  | One tractor breakdown
242 | 2024-05-29 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 |  |  | MOP |  | One tractor breakdown
243 | 2024-05-30 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
244 | 2024-05-31 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
245 | 2024-06-01 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
246 | 2024-06-02 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
247 | 2024-06-03 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
248 | 2024-06-04 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
249 | 2024-06-05 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 |  |  | MOP |  | One tractor breakdown
250 | 2024-06-06 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
251 | 2024-06-07 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
252 | 2024-06-08 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
253 | 2024-06-09 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
254 | 2024-06-10 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
255 | 2024-06-11 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
256 | 2024-06-12 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP |  | One tractor breakdown
257 | 2024-06-13 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
258 | 2024-06-14 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
259 | 2024-06-15 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
260 | 2024-06-16 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
261 | 2024-06-17 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
262 | 2024-06-18 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
263 | 2024-06-19 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
264 | 2024-06-20 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
265 | 2024-06-21 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
266 | 2024-06-22 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
267 | 2024-06-23 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
268 | 2024-06-24 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
269 | 2024-06-25 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
270 | 2024-06-26 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning was stopped at the site yesterday because module cleaning was done by rain.
271 | 2024-06-27 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
272 | 2024-06-28 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
273 | 2024-06-29 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning was stopped at the site yesterday because module cleaning was done by rain.
274 | 2024-06-30 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
275 | 2024-07-01 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
276 | 2024-07-02 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
277 | 2024-07-03 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
278 | 2024-07-04 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning was stopped at the site yesterday due to heavy rain
279 | 2024-07-05 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 13.40mm Rain fall at Site
280 | 2024-07-06 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 53.40mm Rain fall at Site
281 | 2024-07-07 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 180.20mm Rain fall at Site
282 | 2024-07-08 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
283 | 2024-07-09 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
284 | 2024-07-10 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
285 | 2024-07-11 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 111.20mm Rain fall at Site
286 | 2024-07-12 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
287 | 2024-07-13 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 36.0mm rainfall at site
288 | 2024-07-14 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
289 | 2024-07-15 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
290 | 2024-07-16 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 10250 |  |  | 16:30 | 23:00 | MOP
291 | 2024-07-17 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
292 | 2024-07-18 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
293 | 2024-07-19 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 15.2mm rainfall at site
294 | 2024-07-20 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
295 | 2024-07-21 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
296 | 2024-07-22 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
297 | 2024-07-23 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 3.20mm rainfall at site
298 | 2024-07-24 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | light Rain at Site
299 | 2024-07-25 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
300 | 2024-07-26 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 2.2mm rainfall at site
301 | 2024-07-27 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 22.2mm rainfall at site
302 | 2024-07-28 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
303 | 2024-07-29 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
304 | 2024-07-30 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
305 | 2024-07-31 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 7.80mm rainfall at site
306 | 2024-08-01 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | light Rain at Site
307 | 2024-08-02 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
308 | 2024-08-03 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
309 | 2024-08-04 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 12.2 mm rainfall at Site
310 | 2024-08-05 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 9.20mm rainfall at site
311 | 2024-08-06 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
312 | 2024-08-07 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 6.60mm rainfall at site
313 | 2024-08-08 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 27.60mm rainfall at site
314 | 2024-08-09 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 6.8mm rainfall at site
315 | 2024-08-10 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 4.5mm rainfall at site
316 | 2024-08-11 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 12.6mm rainfall at site
317 | 2024-08-12 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 38.2mm rainfall at site
318 | 2024-08-13 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 6.8mm rainfall at site
319 | 2024-08-14 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 13.6mm rainfall at site
320 | 2024-08-15 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 8.2mm rainfall at site
321 | 2024-08-16 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000
322 | 2024-08-17 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 0.8 mm rainfall at site
323 | 2024-08-18 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 0.9 mm rainfall at site
324 | 2024-08-19 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 15.8mm rainfall at site
325 | 2024-08-20 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 0.6mm rainfall at site
326 | 2024-08-21 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
327 | 2024-08-22 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000
328 | 2024-08-23 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 14.6mm rainfall at site
329 | 2024-08-24 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000
330 | 2024-08-25 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 7mm rainfall at site
331 | 2024-08-26 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 0.2mm rainfall at site
332 | 2024-08-27 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 4.2mm rainfall at site
333 | 2024-08-28 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 8.0mm rainfall at site
334 | 2024-08-29 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 0.2mm rainfall at site
335 | 2024-08-30 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 8.4mm rainfall at site
336 | 2024-08-31 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000
337 | 2024-09-01 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
338 | 2024-09-02 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
339 | 2024-09-03 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | 23.20mm rainfall at site
340 | 2024-09-04 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | 42.40mm rainfall at site
341 | 2024-09-05 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | 2.6mm rainfall at site
342 | 2024-09-06 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | 144.4mm rainfall at site
343 | 2024-09-07 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
344 | 2024-09-08 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
345 | 2024-09-09 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
346 | 2024-09-10 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
347 | 2024-09-11 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
348 | 2024-09-12 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
349 | 2024-09-13 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
350 | 2024-09-14 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
351 | 2024-09-15 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
352 | 2024-09-16 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
353 | 2024-09-17 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
354 | 2024-09-18 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
355 | 2024-09-19 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
356 | 2024-09-20 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
357 | 2024-09-21 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
358 | 2024-09-22 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
359 | 2024-09-23 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
360 | 2024-09-24 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
361 | 2024-09-25 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
362 | 2024-09-26 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
363 | 2024-09-27 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
364 | 2024-09-28 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
365 | 2024-09-29 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
366 | 2024-09-30 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
367 | 2024-10-01 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
368 | 2024-10-02 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
369 | 2024-10-03 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
370 | 2024-10-04 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
371 | 2024-10-05 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
372 | 2024-10-06 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
373 | 2024-10-07 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
374 | 2024-10-08 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
375 | 2024-10-09 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
376 | 2024-10-10 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
377 | 2024-10-11 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
378 | 2024-10-12 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
379 | 2024-10-13 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
380 | 2024-10-14 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
381 | 2024-10-15 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
382 | 2024-10-16 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
383 | 2024-10-17 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
384 | 2024-10-18 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
385 | 2024-10-19 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
386 | 2024-10-20 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
387 | 2024-10-21 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
388 | 2024-10-22 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
389 | 2024-10-23 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
390 | 2024-10-24 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
391 | 2024-10-25 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
392 | 2024-10-26 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
393 | 2024-10-27 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
394 | 2024-10-28 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
395 | 2024-10-29 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
396 | 2024-10-30 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
397 | 2024-10-31 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
398 | 2024-11-01 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
399 | 2024-11-02 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
400 | 2024-11-03 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
401 | 2024-11-04 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
402 | 2024-11-05 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
403 | 2024-11-06 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
404 | 2024-11-07 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
405 | 2024-11-08 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
406 | 2024-11-09 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
407 | 2024-11-10 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
408 | 2024-11-11 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP |  | Tractor breakdown
409 | 2024-11-12 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
410 | 2024-11-13 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
411 | 2024-11-14 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
412 | 2024-11-15 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
413 | 2024-11-16 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP |  | one tractor breakdown
414 | 2024-11-17 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP |  | one tractor breakdown
415 | 2024-11-18 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP |  | one tractor breakdown
416 | 2024-11-19 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP |  | one tractor breakdown
417 | 2024-11-20 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
418 | 2024-11-21 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
419 | 2024-11-22 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
420 | 2024-11-23 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
421 | 2024-11-24 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
422 | 2024-11-25 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
423 | 2024-11-26 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
424 | 2024-11-27 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
425 | 2024-11-28 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
426 | 2024-11-29 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
427 | 2024-11-30 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
428 | 2024-12-01 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
429 | 2024-12-02 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
430 | 2024-12-03 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
431 | 2024-12-04 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
432 | 2024-12-05 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
433 | 2024-12-06 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
434 | 2024-12-07 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
435 | 2024-12-08 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
436 | 2024-12-09 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
437 | 2024-12-10 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
438 | 2024-12-11 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
439 | 2024-12-12 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
440 | 2024-12-13 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
441 | 2024-12-14 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
442 | 2024-12-15 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
443 | 2024-12-16 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
444 | 2024-12-17 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
445 | 2024-12-18 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
446 | 2024-12-19 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
447 | 2024-12-20 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
448 | 2024-12-21 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
449 | 2024-12-22 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
450 | 2024-12-23 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
451 | 2024-12-24 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
452 | 2024-12-25 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
453 | 2024-12-26 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
454 | 2024-12-27 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
455 | 2024-12-28 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
456 | 2024-12-29 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
457 | 2024-12-30 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
458 | 2024-12-31 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 17250 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
459 | 2025-01-01 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Yesterday module cleaning stopped because the vendor did not come due to the New Year.
460 | 2025-01-02 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
461 | 2025-01-03 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 14250 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
462 | 2025-01-04 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
463 | 2025-01-05 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
464 | 2025-01-06 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
465 | 2025-01-07 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
466 | 2025-01-08 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
467 | 2025-01-09 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
468 | 2025-01-10 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
469 | 2025-01-11 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
470 | 2025-01-12 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
471 | 2025-01-13 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
472 | 2025-01-14 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
473 | 2025-01-15 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
474 | 2025-01-16 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
475 | 2025-01-17 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
476 | 2025-01-18 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
477 | 2025-01-19 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
478 | 2025-01-20 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
479 | 2025-01-21 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
480 | 2025-01-22 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
481 | 2025-01-23 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning stopped that day due to bad weather.
482 | 2025-01-24 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
483 | 2025-01-25 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
484 | 2025-01-26 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
485 | 2025-01-27 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
486 | 2025-01-28 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
487 | 2025-01-29 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
488 | 2025-01-30 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
489 | 2025-01-31 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
490 | 2025-02-01 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
491 | 2025-02-02 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
492 | 2025-02-03 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
493 | 2025-02-04 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
494 | 2025-02-05 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
495 | 2025-02-06 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
496 | 2025-02-07 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
497 | 2025-02-08 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
498 | 2025-02-09 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning stopped that day due to vendor home family function.
499 | 2025-02-10 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
500 | 2025-02-11 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning stopped that day due to vendor home family function.
501 | 2025-02-12 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000
502 | 2025-02-13 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
503 | 2025-02-14 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
504 | 2025-02-15 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
505 | 2025-02-16 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
506 | 2025-02-17 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
507 | 2025-02-18 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
508 | 2025-02-19 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
509 | 2025-02-20 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
510 | 2025-02-21 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
511 | 2025-02-22 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
512 | 2025-02-23 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
513 | 2025-02-24 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
514 | 2025-02-25 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
515 | 2025-02-26 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
516 | 2025-02-27 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
517 | 2025-02-28 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000
518 | 2025-03-01 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
519 | 2025-03-02 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
520 | 2025-03-03 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
521 | 2025-03-04 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
522 | 2025-03-05 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
523 | 2025-03-06 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
524 | 2025-03-07 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Function at vendor's home
525 | 2025-03-08 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
526 | 2025-03-09 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
527 | 2025-03-10 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
528 | 2025-03-11 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
529 | 2025-03-12 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
530 | 2025-03-13 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
531 | 2025-03-14 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
532 | 2025-03-15 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
533 | 2025-03-16 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
534 | 2025-03-17 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
535 | 2025-03-18 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
536 | 2025-03-19 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
537 | 2025-03-20 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
538 | 2025-03-21 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
539 | 2025-03-22 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
540 | 2025-03-23 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
541 | 2025-03-24 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
542 | 2025-03-25 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
543 | 2025-03-26 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
544 | 2025-03-27 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
545 | 2025-03-28 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
546 | 2025-03-29 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
547 | 2025-03-30 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
548 | 2025-03-31 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
549 | 2025-04-01 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
550 | 2025-04-02 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
551 | 2025-04-03 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
552 | 2025-04-04 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
553 | 2025-04-05 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
554 | 2025-04-06 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
555 | 2025-04-07 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
556 | 2025-04-08 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
557 | 2025-04-09 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | Blk8: 6000 | 6000
558 | 2025-04-10 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | Blk4: 4200; Blk6: 6600; Blk7: 6000; Blk8: 6000 | 22800 | 9:00 | 12:00 | 14:00 | 18:00
559 | 2025-04-11 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7200 | 7450 | 7800 | 7250 |  | 7200 |  | 6000 | 42900 | 9:00 | 12:00 | 14:00 | 18:00
560 | 2025-04-12 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 6500 | 7550 | 7100 | 7300 | 6900 |  |  | 6000 | 41350 | 9:00 | 12:00 | 14:00 | 18:00
561 | 2025-04-13 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7100 | 7200 | 6000 |  | 7500 | 7700 | 7800 | 6000 | 49300 | 9:00 | 12:00 | 14:00 | 18:00
562 | 2025-04-14 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7600 | 7800 |  |  | 9000 | 6500 | 7250 | 5500 | 43650 | 9:00 | 12:00 | 14:00 | 18:00
563 | 2025-04-15 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7600 | 7450 | 5600 | 7250 | 6300 | 5000 | 0 | 4100 | 43300 | 9:00 | 12:00 | 14:00 | 18:00
564 | 2025-04-16 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7600 | 6750 | 7800 | 6500 | 7600 |  |  | 7600 | 49200 | 9:00 | 12:00 | 14:00 | 18:00
565 | 2025-04-17 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning |  | 7600 | 7600 | 6300 | 6300 |  |  | 7000 | 34800 | 9:00 | 12:00 | 14:00 | 18:00
566 | 2025-04-18 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7800 | 7600 | 7500 | 6500 | 7100 |  |  | 6000 | 42500 | 9:00 | 12:00 | 14:00 | 18:00
567 | 2025-04-19 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 8580 | 8640 | 10080 |  | 8880 | 9240 | 8700 | 6000 | 45100 | 9:00 | 12:00 | 14:00 | 18:00
568 | 2025-04-20 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7600 |  | 9360 |  | 9180 | 9360 | 9360 | 6000 | 38650 | 9:00 | 12:00 | 14:00 | 18:00
569 | 2025-04-21 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 5760 | 9360 | 10080 |  | 9360 | 9120 | 9000 | 6000 | 46300 | 9:00 | 12:00 | 14:00 | 18:00
570 | 2025-04-22 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7600 | 6000 | 7600 | 7250 | 7200 | 7600 |  | 6000 | 49250 | 9:00 | 12:00 | 14:00 | 18:00
571 | 2025-04-23 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 6200 | 6000 | 6000 | 8640 | 7500 | 7920 | 7000 | 0 | 49260 | 9:00 | 12:00 | 14:00 | 18:00
572 | 2025-04-24 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7200 | 6000 | 5500 | 9900 | 7200 | 8640 |  | 0 | 44440 | 9:00 | 12:00 | 14:00 | 18:00
573 | 2025-04-25 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7200 | 6000 | 6800 | 7500 | 7400 | 6200 | 6800 | 0 | 47900 | 9:00 | 12:00 | 14:00 | 18:00
574 | 2025-04-26 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 6200 | 6800 | 5750 | 6200 | 6900 | 6200 | 5100 | 0 | 43150 | 9:00 | 12:00 | 14:00 | 18:00
575 | 2025-04-27 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7200 | 7200 | 6000 | 7400 | 7200 | 6600 | 7200 | 0 | 48800 | 9:00 | 12:00 | 14:00 | 18:00
576 | 2025-04-28 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | Blk2: 0; Blk3: 0 | 0 | 9:00 | 12:00 | 14:00 | 18:00
577 | 2025-04-29 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | Blk2: 3600; Blk3: 4800; Blk8: 6000 | 14400
578 | 2025-04-30 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | Blk2: 3250; Blk6: 7200; Blk8: 110 | 10560 | 9:00 | 12:00 | 14:00 | 18:00
579 | 2025-05-01 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | 7200 |  |  | 3600 | 7200 | 2500 | 6600 |  | 27100 | 9:00 | 12:00 | 14:00 | 18:00
580 | 2025-05-02 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 7500; Blk4: 5450; Blk5: 6250; Blk6: 6600 | 25800 | [6 empty] | RO
581 | 2025-05-03 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 7050; Blk4: 6600; Blk5: 7150; Blk7: 5500 | 26300
582 | 2025-05-04 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (1 to 11),Robot2 (73 to 79),Robot 3(80 to 86) & Robot 4 (87 to 92)
583 | 2025-05-05 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (12 to 18),Robot2 (70 to 73),Robot 3(93 to 98) & Robot 4 (99 to104)
584 | 2025-05-06 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (19 to 33),Robot2 (81 to 86),Robot 3(105 to 112) & Robot 4 (113 to126)
585 | 2025-05-07 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (22 to 33),Robot2 (34 to 40),Robot 3(80 to 92) & Robot 4 (127 to144)
586 | 2025-05-08 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (40 to 55),Robot2 (73 to 77),Robot 3(93 to 98) & Robot 4 (137 to 166)
587 | 2025-05-09 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (132 to 152),Robot2 (56 to 64),Robot 3(68 to 72) & Robot 4 (99 to 104)
588 | 2025-05-10 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (57 to 63),Robot2 (64 to 67),Robot 3(95 to 111) & Robot 4 (172 to 185)
589 | 2025-05-11 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (50 to 56),Robot2 (68to 74),Robot 3(123 to 131) & Robot 4 (110 to 116)
590 | 2025-05-12 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (26 to 49),Robot2 (2 to 17),Robot 3(103 to 110) & Robot 4 (64 to 69)
591 | 2025-05-13 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (44 to 59),Robot2 (17 to 34),Robot 3(67 to 70) & Robot 4 (97 to 102)
592 | 2025-05-14 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (40 to 55),Robot2 (76 to 79),Robot 3(87 to 91) & Robot 4 (104 to 113)
593 | 2025-05-15 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (62 to 65),Robot2 (81 to 84),Robot 3(87 to 90) & Robot 4 (98 to 102)
594 | 2025-05-16 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (01 to 08),Robot2 (158 to165),Robot 3(148 to 157) & Robot 4 (104 to 110)
595 | 2025-05-17 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 5500; Blk4: 3250; Blk6: 4000; Blk8: 2250 | 15000 | 9:00 | 12:00 | 14:00 | 18:00
596 | 2025-05-18 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 7750; Blk4: 7250; Blk6: 7450; Blk8: 3750 | 26200 | 9:00 | 12:00 | 14:00 | 18:00
597 | 2025-05-19 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 7450; Blk4: 7550; Blk6: 7250; Blk8: 5250 | 27500 | 9:00 | 12:00 | 14:00 | 18:00
598 | 2025-05-20 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk2: 7650; Blk4: 1400; Blk5: 5400; Blk8: 5100 | 19550 | 9:00 | 12:00 | 14:00 | 18:00
599 | 2025-05-21 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning |  | 7400 | 7700 |  | 5400 | 1700 | 7750 |  | 29950 | 9:00 | 12:00 | 14:00 | 18:00
600 | 2025-05-22 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk2: 4600; Blk3: 5950; Blk5: 7000; Blk7: 5100 | 22650 | 9:00 | 12:00 | 14:00 | 18:00
601 | 2025-05-23 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk5: 3900; Blk7: 3250; Blk8: 3500 | 10650 | 9:00 | 12:00 | 14:00 | 18:00
602 | 2025-05-24 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk4: 3000; Blk5: 3650; Blk8: 3400 | 10050 | 9:00 | 12:00 | 14:00 | 18:00
603 | 2025-05-25 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 7600; Blk4: 7600; Blk8: 7550 | 22750 | 9:00 | 12:00 | 14:00 | 18:00
604 | 2025-05-26 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0
605 | 2025-05-27 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0
606 | 2025-05-28 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk2: 7000; Blk3: 3500; Blk5: 5250; Blk7: 4000 | 19750 | 9:00 | 12:00 | 14:00 | 18:00
607 | 2025-05-29 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0
608 | 2025-05-30 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk2: 4400; Blk6: 6900 | 11300 | 9:00 | 12:00 | 14:00 | 18:00
609 | 2025-05-31 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk2: 7000; Blk3: 7250; Blk6: 7000; Blk7: 8250 | 29500 | 9:00 | 12:00 | 14:00 | 18:00
610 | 2025-06-01 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk2: 8250; Blk3: 7250; Blk6: 5400; Blk7: 6600 | 27500 | 9:00 | 12:00 | 14:00 | 18:00
611 | 2025-06-02 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 6000 |  | 6400 | 2400 |  | 6050 | 1100 | 4500 | 26450 | 9:00 | 12:00 | 14:00 | 18:00
612 | 2025-06-03 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk1: 6600; Blk4: 7800; Blk5: 7250; Blk8: 5500 | 27150 | 9:00 | 12:00 | 14:00 | 18:00
613 | 2025-06-04 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk1: 7500; Blk4: 7500; Blk5: 7800; Blk8: 6600 | 29400 | 9:00 | 12:00 | 14:00 | 18:00
614 | 2025-06-05 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 4500 | 7250 | 7200 | 1850 |  | 7800 | 7750 |  | 36350 | 9:00 | 12:00 | 14:00 | 18:00
615 | 2025-06-06 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | [8 empty] | 0
616 | 2025-06-07 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk2: 7800; Blk3: 7200; Blk6: 6500; Blk7: 7200 | 28700 | 9:00 | 12:00 | 14:00 | 18:00
617 | 2025-06-08 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 1300 | 2650 |  |  |  | 6100 | 1100 | 4900 | 16050 | 9:00 | 12:00 | 14:00 | 18:00
618 | 2025-06-09 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 7300 |  | 4800 | 3250 | 8600 |  |  | 5000 | 28950 | 9:00 | 12:00 | 14:00 | 18:00
619 | 2025-06-10 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk1: 5800; Blk4: 7300; Blk5: 8000; Blk8: 6750 | 27850 | 9:00 | 12:00 | 14:00 | 18:00
620 | 2025-06-11 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 5700 | 2000 | 4050 | 7200 | 3900 |  |  |  | 22850 | 9:00 | 12:00 | 14:00 | 18:00
621 | 2025-06-12 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning |  | 7200 | 7700 | 1800 |  | 5450 | 7000 |  | 29150 | 9:00 | 12:00 | 14:00 | 18:00
622 | 2025-06-13 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk2: 7500; Blk3: 7600; Blk6: 7700; Blk7: 7250 | 30050 | 9:00 | 12:00 | 14:00 | 18:00
623 | 2025-06-14 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 4000 | 3000 |  | 7500 |  | 7700 | 2300 | 6300 | 30800 | 9:00 | 12:00 | 14:00 | 18:00
624 | 2025-06-15 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk1: 8000; Blk4: 9700; Blk5: 7750; Blk8: 6000 | 31450 | 9:00 | 12:00 | 14:00 | 18:00
625 | 2025-06-16 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 8000 |  |  | 3150 | 6050 | 4500 |  | 6500 | 28200 | 9:00 | 12:00 | 14:00 | 18:00
626 | 2025-06-17 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk2: 7500; Blk5: 6800; Blk6: 7550; Blk7: 7100 | 28950 | 9:00 | 12:00 | 14:00 | 18:00
627 | 2025-06-18 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk2: 7500; Blk3: 7400; Blk6: 7600; Blk7: 7150 | 29650 | 9:00 | 12:00 | 14:00 | 18:00
628 | 2025-06-19 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 2500 | 4500 |  |  | 6600 | 1100 | 6500 |  | 21200 | 9:00 | 12:00 | 14:00 | 18:00
Formulas:
Days = DAY(EOMONTH(MC[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## Raw_Data
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 | 237 | 238 | 239 | 240 | 241 | 242 | 243 | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273 | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302
Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Plant DC Capcity (MW) | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | BLK1_INV1 | BLK1_INV2 | BLK1_INV3 | BLK1_INV4 | BLK1_INV5 | BLK1_INV6 | BLK1_INV7 | BLK1_INV8 | BLK1_INV9 | BLK1_INV10 | BLK1_INV11 | BLK1_INV12 | BLK1_INV13 | BLK1_INV14 | BLK1_INV15 | BLK1_INV16 | BLK1_INV17 | BLK1_INV18 | BLK1_INV19 | BLK1_INV20 | BLK1_INV21 | BLK1_INV22 | BLK1_INV23 | BLK1_INV24 | BLK1_INV25 | BLK1_INV26 | BLK1_INV27 | BLK1_INV28 | BLK1_INV29 | BLK1_INV30 | BLK1_INV31 | BLK1_INV32 | BLK2_INV1 | BLK2_INV2 | BLK2_INV3 | BLK2_INV4 | BLK2_INV5 | BLK2_INV6 | BLK2_INV7 | BLK2_INV8 | BLK2_INV9 | BLK2_INV10 | BLK2_INV11 | BLK2_INV12 | BLK2_INV13 | BLK2_INV14 | BLK2_INV15 | BLK2_INV16 | BLK2_INV17 | BLK2_INV18 | BLK2_INV19 | BLK2_INV20 | BLK2_INV21 | BLK2_INV22 | BLK2_INV23 | BLK2_INV24 | BLK2_INV25 | BLK2_INV26 | BLK2_INV27 | BLK2_INV28 | BLK2_INV29 | BLK2_INV30 | BLK2_INV31 | BLK2_INV32 | BLK3_INV1 | BLK3_INV2 | BLK3_INV3 | BLK3_INV4 | BLK3_INV5 | BLK3_INV6 | BLK3_INV7 | BLK3_INV8 | BLK3_INV9 | BLK3_INV10 | BLK3_INV11 | BLK3_INV12 | BLK3_INV13 | BLK3_INV14 | BLK3_INV15 | BLK3_INV16 | BLK3_INV17 | BLK3_INV18 | BLK3_INV19 | BLK3_INV20 | BLK3_INV21 | BLK3_INV22 | BLK3_INV23 | BLK3_INV24 | BLK3_INV25 | BLK3_INV26 | BLK3_INV27 | BLK3_INV28 | BLK3_INV29 | BLK3_INV30 | BLK3_INV31 | BLK4_INV1 | BLK4_INV2 | BLK4_INV3 | BLK4_INV4 | BLK4_INV5 | BLK4_INV6 | BLK4_INV7 | BLK4_INV8 | BLK4_INV9 | BLK4_INV10 | BLK4_INV11 | BLK4_INV12 | BLK4_INV13 | BLK4_INV14 | BLK4_INV15 | BLK4_INV16 | BLK4_INV17 | BLK4_INV18 | BLK4_INV19 | BLK4_INV20 | BLK4_INV21 | BLK4_INV22 | BLK4_INV23 | BLK4_INV24 | BLK4_INV25 | BLK4_INV26 | BLK4_INV27 | BLK4_INV28 | BLK4_INV29 | BLK4_INV30 | BLK4_INV31 | BLK5_INV1 | BLK5_INV2 | BLK5_INV3 | BLK5_INV4 | BLK5_INV5 | BLK5_INV6 | BLK5_INV7 | BLK5_INV8 | BLK5_INV9 | BLK5_INV10 | BLK5_INV11 | BLK5_INV12 | BLK5_INV13 | BLK5_INV14 | BLK5_INV15 | BLK5_INV16 | BLK5_INV17 | BLK5_INV18 | BLK5_INV19 | BLK5_INV20 | BLK5_INV21 | BLK5_INV22 | BLK5_INV23 | BLK5_INV24 | BLK5_INV25 | BLK5_INV26 | BLK5_INV27 | BLK5_INV28 | BLK5_INV29 | BLK5_INV30 | BLK5_INV31 | BLK5_INV32 | BLK6_INV1 | BLK6_INV2 | BLK6_INV3 | BLK6_INV4 | BLK6_INV5 | BLK6_INV6 | BLK6_INV7 | BLK6_INV8 | BLK6_INV9 | BLK6_INV10 | BLK6_INV11 | BLK6_INV12 | BLK6_INV13 | BLK6_INV14 | BLK6_INV15 | BLK6_INV16 | BLK6_INV17 | BLK6_INV18 | BLK6_INV19 | BLK6_INV20 | BLK6_INV21 | BLK6_INV22 | BLK6_INV23 | BLK6_INV24 | BLK6_INV25 | BLK6_INV26 | BLK6_INV27 | BLK6_INV28 | BLK6_INV29 | BLK6_INV30 | BLK6_INV31 | BLK6_INV32 | BLK7_INV1 | BLK7_INV2 | BLK7_INV3 | BLK7_INV4 | BLK7_INV5 | BLK7_INV6 | BLK7_INV7 | BLK7_INV8 | BLK7_INV9 | BLK7_INV10 | BLK7_INV11 | BLK7_INV12 | BLK7_INV13 | BLK7_INV14 | BLK7_INV15 | BLK7_INV16 | BLK7_INV17 | BLK7_INV18 | BLK7_INV19 | BLK7_INV20 | BLK7_INV21 | BLK7_INV22 | BLK7_INV23 | BLK7_INV24 | BLK7_INV25 | BLK7_INV26 | BLK7_INV27 | BLK7_INV28 | BLK7_INV29 | BLK7_INV30 | BLK7_INV31 | BLK7_INV32 | BLK8_INV1 | BLK8_INV2 | BLK8_INV3 | BLK8_INV4 | BLK8_INV5 | BLK8_INV6 | BLK8_INV7 | BLK8_INV8 | BLK8_INV9 | BLK8_INV10 | BLK8_INV11 | BLK8_INV12 | BLK8_INV13 | BLK8_INV14 | BLK8_INV15 | BLK8_INV16 | BLK8_INV17 | BLK8_INV18 | BLK8_INV19 | BLK8_INV20 | BLK8_INV21 | BLK8_INV22 | BLK8_INV23 | BLK8_INV24 | BLK8_INV25 | BLK8_INV26 | BLK8_INV27 | BLK8_INV28 | AT (°C) 14 Hours | MT (°C) Gen. Hours | WS_Avg (m/s) (24 Hours) | WS_Max (m/s) | Rain (mm) | GHI | POA | GHI_Lost | POA_Lost | 33kV_IC1_ExPort | 33kV_IC1_Import | 33kV_IC2_ExPort | 33kV_IC2_Import | 33kV_IC3_ExPort | 33kV_IC3_Import | 33kV_IC4_ExPort | 33kV_IC4_Import |  | I31kV_PQM_Im | 33kV_IC1_ExPort(KWh) | 33kV_IC1_Import(KWh) | 33kV_IC2_ExPort(KWh) | 33kV_IC2_Import(KWh) | 33kV_IC3_ExPort(KWh) | 33kV_IC3_Import(KWh) | 33kV_IC4_ExPort(kWh) | 33kV_IC4_Import(KWh) | 132kV_PQM_Ex(KWh) | 132kV_PQM_Im(KWh) | 33kV_Net_Ex (kWh) | 132kV_Net_Ex (kWh) | Operating Hours | GHI (KWh/m2)2 | POA(KWh/m2)2 | Amm_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | Inv_Exp(KWh) | WPR_Eac | WPR_Edc | WPR
2025-03-29 | 2025 | 2025 |  |  | Mar-25 | 31 | 66750 | 7:00 | 19:00 | [266 empty] | 54996.705 | 306246841.6003 | 81683.2331 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-03-30 | 2025 | 2025 |  |  | Mar-25 | 31 | 66750 | 7:00 | 19:00 | [266 empty] | 55011.744 | 306590465.4889 | 81745.1624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.039 | 343623.8886 | 61.9293 | -15.039 | 343561.9593 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-03-31 | 2025 | 2025 |  |  | Mar-25 | 31 | 66750 | 7:00 | 19:00 | 1590.1 | 1625.2 | 1522.4 | 1520.1 | 1598.4 | 1485.5 | 1544.3 | 1555.5 | 1580.5 | 1513.2 | 1550.6 | 1573 | 1569.8 | 1408.7 | 1504.6 | 1484.1 | 1452.9 | 1468 | 1589.1 | 1590.5 | 1596.5 | 1494.7 | 1541.1 | 1529.8 | 1509.6 | 1605.5 | 1593.4 | 1625.1 | 1594.9 | 1646.2 | 1616.2 | 1543.3 | 1387.5 | 1817.1 | 1398.5 | 1593.3 | 1512.2 | 1457.7 | 1508.8 | 1471.4 | 1478.6 | 1456.7 | 1512.4 | 1529.3 | 1535.4 | 1547.8 | 1567.5 | 1472.3 | 1542.2 | 1494.4 | 1431.4 | 1453.4 | 1610.5 | 1732.5 | 1563.5 | 1613.1 | 1633.3 | 1544.4 | 1634.4 | 1601.2 | 1478.6 | 1625 | 1455 | 1300.5 | 1644.7 | 1649.7 | 1648.2 | 1654.1 | 1502.1 | 1508.6 | 1506.5 | 1492.4 | 1471.1 | 1522.5 | 1602.1 | 1694.3 | 1724.1 | 1445.1 | 1482.4 | 1604.5 | 1541.1 | 1529.1 | 1512.1 | 1523.2 | 1542.2 | 1492.5 | 1529.5 | 1451.4 | 1470.1 | 1472.5 | 1548.5 | 1574.5 | 1540.3 | 1462.6 | 1631.5 | 1470.1 | 1492 | 1511.1 | 1515.1 | 1505.1 | 1538.2 | 1498.1 | 1522.1 | 1474.1 | 1679.1 | 1565.1 | 1740.2 | 1676.5 | 1471.4 | 1613.2 | 1559.1 | 1572.4 | 1620.1 | 1710.4 | 1510.4 | 1484.3 | 1660.1 | 1624.2 | 1628.1 | 1543.3 | 1506.1 | 1645.2 | 1616.2 | 1546.4 | 1456.7 | 1621.1 | 0 | 1403.4 | 1717.1 | 1629 | 1560.1 | 1589.2 | 1582.2 | 1356.6 | 1602 | 1575.4 | 1561.2 | 1548.5 | 1623.5 | 1304.5 | 1635.6 | 1562.3 | 1544.4 | 1524 | 1317 | 1563.3 | 1427.7 | 1449.8 | 1605.7 | 1550.5 | 1650.6 | 1502.2 | 1561.5 | 1507.5 | 1489.4 | 1448.5 | 1461.4 | 1440.4 | 1320 | 1285 | 1540 | 1371 | 1305 | 1408 | 1512 | 1406 | 1360 | 1421 | 1462 | 1375 | 1422 | 1430 | 1597 | 1512 | 1626 | 1413 | 1433 | 1280 | 1732 | 1526 | 1495 | 1584 | 1525 | 1568 | 1524 | 1576 | 1508 | 1524 | 1510 | 1437 | 1419 | 1450 | 1436 | 1429 | 1549 | 1397 | 1292 | 1565 |  |  | 1262 | 1064 | 1532 |  | 1659 | 1454 | 1514 | 1472 | 1495 | 1511 | 1521 | 1531 | 1533 | 1537 | 1550 | 1546 | 1521 | 1729 | 1306 | 1295 | 1033 | 908 | 1084 | 1279 | 1486 | 1676 | 1472 | 1533 | 1555 | 1551 | 1593 | 1618 | 1178 | 1422 | 1293 | 1409 | 1141 |  | 1843 | 1480 | 564 | 1371 | 1421 |  |  | 1266 | 1268 | 1417 | 1250 | 1154 | 30.32 | 40.28 | 1.71 | 6.3 |  | 0 | 7.31 |  |  | 80931088.744 | 281250.305 | 54078351.551 | 61052.203 | 81718077.5 | 185254.507 | 59077703.113 | 55026.783 | 306934089.3774 | 81807.0917 | 80931088.744 | 281250.305 | 54078351.551 | 61052.203 | 81718077.5 | 185254.507 | 59077703.113 | 15.039 | 343623.8886 | 61.9293 | 275277648.854 | 343561.9593 | 12 | 0 | 7.31 | 30.32 | 40.28 | 1.71 | 6.3 | 364093.2
2025-04-01 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1577 | 1616 | 1507 | 1509 | 1568 | 1462 | 1505 | 1498 | 1469 | 1476 | 1539 | 1533 | 1529 | 1371 | 1508 | 1488 | 1398 | 1410 | 1535 | 1600 | 1519 | 1458 | 1565 | 1487 | 1592 | 1580 | 1565 | 1592 | 1557 | 1609 | 1590 | 1504 | 1400 | 1797 | 1399 | 1602 | 1507 | 1442 | 1467 | 1420 | 1465 | 1435 | 1473 | 1487 | 1492 | 1503 | 1621 | 1432 | 1510 | 1470 | 1398 | 1420 | 1560 | 1698 | 1488 | 1598 | 1560 | 1490 | 1590 | 1590 | 1348 | 1610 | 1390 | 1290 | 1350 | 1611 | 1616 | 1423 | 1484 | 1489 | 1263 | 1353 | 1448 | 1511 | 1467 | 1657 | 1680 | 1402 | 1439 | 1565 | 1498 | 1485 | 1468 | 1478 | 1498 | 1457 | 1487 | 1411 | 1410 | 1434 | 1510 | 1510 | 1502 | 1390 | 1610 | 1425 | 1446 | 1469 | 1470 | 1363 | 1496 | 1451 | 1474 | 1427 | 1641 | 1321 | 1692 | 1630 | 1427 | 1631 | 1516 | 1594 | 1637 | 1672 | 1453 | 1495 | 1626 | 1546 | 1594 | 1476 | 1503 | 1591 | 1536 | 1414 | 1496 | 1590 | 0 | 1377 | 1680 | 1678 | 1531 | 1554 | 1533 | 1190 | 1591 | 1481 | 1564 | 1514 | 1580 | 1367 | 1406 | 1483 | 1488 | 1506 | 1285 | 1676 | 1474 | 1340 | 1556 | 1563 | 1603 | 1461 | 1611 | 1509 | 1427 | 1410 | 1410 | 1403 | 1291 | 1257 | 1498 | 1334 | 1271 | 1370 | 1490 | 1390 | 1337 | 1580 | 1430 | 1336 | 1386 | 1391 | 1556 | 1471 | 1591 | 1470 | 1453 | 1311 | 1720 | 1521 | 1502 | 1547 | 1481 | 1526 | 1548 | 1544 | 1544 | 1548 | 1469 | 1396 | 1372 | 1404 | 1390 | 1381 | 1505 | 1354 | 1255 | 1525 |  |  | 1299 | 1048 | 1492 |  | 1618 | 1390 | 1468 | 1417 | 1461 | 1462 | 1476 | 1488 | 1488 | 1496 | 1506 | 1501 | 1478 | 1691 | 1338 | 1257 | 1080 | 930 | 998 | 1181 | 1368 | 1550 | 1350 | 1406 | 1490 | 1520 | 1480 | 1491 | 1111 | 1313 | 1188 | 1298 | 1052 |  | 1760 | 1470 | 590 | 1380 | 1298 |  |  | 1385 | 1184 | 1410 | 1230 | 1150 | 25.08 | 40.95 | 1.76 | 5.3 |  | 0 | 7.18 |  |  | 81024220.217 | 281265.893 | 54170029.175 | 61064.408 | 81809917.614 | 185282.999 | 59149543.494 | 55041.822 | 307277713.266 | 81869.021 | 93131.473 | 15.588 | 91677.624 | 12.205 | 91840.114 | 28.492 | 71840.381 | 15.039 | 343623.8886 | 61.9293 | 348418.268 | 343561.9593 | 12 | 0 | 7.18 | 25.08 | 40.95 | 1.76 | 5.3 | 354559
2025-04-02 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1496 | 1535 | 1432 | 1434 | 1510 | 1388 | 1470 | 1398 | 1390 | 1404 | 1498 | 1454 | 1451 | 1304 | 1370 | 1415 | 1352 | 1360 | 1511 | 1547 | 1439 | 1384 | 1583 | 1480 | 1562 | 1558 | 1551 | 1580 | 1546 | 1599 | 1526 | 1490 | 1330 | 1703 | 1370 | 1522 | 1467 | 1380 | 1409 | 1449 | 1402 | 1381 | 1414 | 1427 | 1418 | 1439 | 1538 | 1358 | 1480 | 1410 | 1370 | 1378 | 1507 | 1561 | 1480 | 1490 | 1510 | 1404 | 1568 | 1520 | 1413 | 1563 | 1340 | 1300 | 1410 | 1573 | 1581 | 1410 | 1436 | 1444 | 1278 | 1319 | 1390 | 1464 | 1498 | 1571 | 1594 | 1333 | 1364 | 1499 | 1418 | 1406 | 1390 | 1402 | 1423 | 1389 | 1438 | 1361 | 1420 | 1394 | 1490 | 1490 | 1456 | 1300 | 1582 | 1351 | 1371 | 1399 | 1393 | 1340 | 1417 | 1374 | 1397 | 1355 | 1583 | 1290 | 1623 | 1547 | 1351 | 1581 | 1472 | 1511 | 1562 | 1586 | 1381 | 1416 | 1544 | 1519 | 1543 | 1432 | 1468 | 1549 | 1507 | 1387 | 1456 | 1577 | 0 | 1341 | 1646 | 1631 | 1498 | 1510 | 1488 | 1178 | 1507 | 1490 | 1482 | 1387 | 1495 | 1292 | 1398 | 1411 | 1413 | 1426 | 1278 | 1586 | 1396 | 1274 | 1492 | 1487 | 1529 | 1414 | 1531 | 1422 | 1391 | 1369 | 1387 | 1333 | 1290 | 1292 | 1445 | 1282 | 1360 | 1378 | 1478 | 1398 | 1335 | 1501 | 1398 | 1378 | 1390 | 1321 | 1477 | 1397 | 1508 | 1392 | 1373 | 1242 | 1630 | 1441 | 1419 | 1464 | 1505 | 1445 | 1467 | 1510 | 1460 | 1467 | 1393 | 1410 | 1296 | 1320 | 1313 | 1305 | 1425 | 1282 | 1188 | 1446 |  |  | 1265 | 990 | 1410 |  | 1534 | 1310 | 1390 | 1339 | 1387 | 1387 | 1401 | 1412 | 1411 | 1422 | 1470 | 1490 | 1460 | 1710 | 1272 | 1186 | `1031 | 910 | 992 | 1173 | 1363 | 1546 | 1344 | 1400 | 1510 | 1498 | 1472 | 1489 | 1123 | 1303 | 1177 | 1289 | 1043 |  | 1175 | 1450 | 690 | 1310 | 1290 |  |  | 1368 | 1012 | 1390 | 1190 | 1158 | 26.5 | 39.7 | 1.9 | 5.9 |  | 0 | 6.87 |  |  | 81114928.986 | 281280.784 | 54257592.783 | 61077.806 | 81897649.596 | 185319.828 | 59218660.672 | 55054.694 | 307612421.636 | 81927.037 | 90708.769 | 14.891 | 87563.608 | 13.398 | 87731.982 | 36.829 | 69117.178 | 12.872 | 334708.37 | 58.016 | 335043.547 | 334650.354 | 12 | 0 | 6.87 | 26.5 | 39.7 | 1.9 | 5.9 | 341179
2025-04-03 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1342 | 1375 | 1283 | 1281 | 1292 | 1245 | 1134 | 1189 | 1199 | 1258 | 1313 | 1304 | 1299 | 1163 | 1230 | 1265 | 1211 | 1229 | 1379 | 1401 | 1308 | 1283 | 1422 | 1304 | 1409 | 1404 | 1397 | 1423 | 1405 | 1447 | 1387 | 1391 | 1197 | 1534 | 1194 | 1444 | 1226 | 1243 | 1283 | 1315 | 1263 | 1248 | 1296 | 1302 | 1295 | 1321 | 1398 | 1221 | 1203 | 1218 | 1166 | 1155 | 1331 | 1406 | 1187 | 1362 | 1231 | 1264 | 1411 | 1355 | 1272 | 1406 | 1300 | 1280 | 1156 | 1405 | 1439 | 1253 | 1289 | 1294 | 1078 | 1191 | 1257 | 1315 | 1285 | 1450 | 1467 | 1202 | 1249 | 1382 | 1301 | 1305 | 1298 | 1309 | 1303 | 1268 | 1315 | 1247 | 1154 | 1274 | 1324 | 690 | 1331 | 1125 | 1393 | 1248 | 1258 | 1284 | 1251 | 1184 | 1318 | 1285 | 1306 | 1273 | 1448 | 1152 | 1497 | 1365 | 1244 | 1448 | 1363 | 1358 | 1409 | 1422 | 1262 | 1272 | 1388 | 1373 | 1420 | 1286 | 1321 | 1395 | 1356 | 1254 | 1327 | 1431 | 521 | 775 | 1490 | 1460 | 1322 | 1326 | 1306 | 975 | 1346 | 1178 | 1325 | 1240 | 1338 | 1175 | 1196 | 1296 | 1265 | 1274 | 1108 | 1449 | 1293 | 1181 | 1372 | 1384 | 1412 | 1291 | 1375 | 1291 | 1265 | 1251 | 1261 | 1202 | 1151 | 1157 | 1293 | 1145 | 1076 | 1165 | 1144 | 966 | 1197 | 1343 | 1215 | 1137 | 1184 | 1185 | 1323 | 1248 | 1345 | 1242 | 1228 | 1109 | 1456 | 1286 | 1267 | 1313 | 1249 | 1290 | 1310 | 1308 | 1303 | 1308 | 1246 | 1184 | 1164 | 1194 | 1178 | 1173 | 1284 | 1153 | 1070 | 1302 |  |  | 1146 | 895 | 1273 |  | 1389 | 1124 | 1250 | 1203 | 1252 | 1249 | 1259 | 1269 | 1269 | 1278 | 1279 | 1277 | 1271 | 1444 | 1143 | 1062 | 919 | 762 | 894 | 1057 | 1225 | 1391 | 1207 | 1256 | 1400 | 1385 | 1338 | 1346 | 1041 | 1174 | 1058 | 1162 | 939 |  | 1265 | 1180 | 700 | 1087 | 1186 |  |  | 1012 | 815 | 1049 | 1180 | 1110 | 25.78 | 32 | 2.63 | 5.3 |  | 0 |  |  |  | 81196825.693 | 281293.339 | 54337502.169 | 61098.808 | 81976932.974 | 185359.42 | 59281082.425 | 55074.059 | 307915539.166 | 81986.655 | 81896.707 | 12.555 | 79909.386 | 21.002 | 79283.378 | 39.592 | 62421.753 | 19.365 | 303117.53 | 59.618 | 161772.536 | 303057.912 | 12 | 0 | 0 | 25.78 | 32 | 2.63 | 5.3 | 305040
2025-04-04 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1401 | 1428 | 1331 | 1332 | 1354 | 1301 | 1170 | 1235 | 1243 | 1311 | 1368 | 1770 | 1355 | 1216 | 1282 | 1320 | 1250 | 1273 | 1420 | 1445 | 1349 | 1296 | 1476 | 1345 | 1450 | 1445 | 1435 | 1472 | 1440 | 1489 | 1460 | 1389 | 1241 | 1624 | 1226 | 1393 | 1267 | 1272 | 1302 | 1378 | 1289 | 1273 | 1311 | 1318 | 1424 | 1349 | 1441 | 1256 | 1264 | 1286 | 1232 | 1195 | 1373 | 1478 | 1241 | 1438 | 1263 | 1306 | 1442 | 1384 | 1290 | 1449 | 1350 | 1380 | 1192 | 1446 | 1474 | 1311 | 1322 | 1329 | 1123 | 1222 | 1314 | 1351 | 1357 | 1517 | 1532 | 1277 | 1314 |  | 1348 | 1353 | 1336 | 1345 | 1327 | 1321 | 1348 | 1276 | 1214 | 1303 | 1376 | 1303 | 1367 | 1152 | 1410 | 1304 | 1314 | 1359 | 1290 | 1264 | 1379 | 1331 | 1348 | 1303 | 1504 | 1209 | 1528 | 1443 | 1307 | 1488 | 1413 | 1465 | 1518 | 1533 | 1337 | 1379 | 1505 | 1405 | 1472 | 1329 | 1363 | 1439 | 1405 | 1291 | 1366 | 1478 | 1237 | 1243 | 1525 | 1503 | 1363 | 1400 | 1374 | 1017 | 1402 | 1212 | 1365 | 1236 | 1406 | 1207 | 1253 | 1337 | 1318 | 1335 | 1140 | 1489 | 1301 | 1217 | 1408 | 1424 | 1449 | 1322 | 1432 | 1363 | 1294 | 1280 | 1278 | 1287 | 1183 | 1196 | 1340 | 1202 | 1134 | 1218 | 1205 | 1017 | 1227 | 1419 | 1273 | 1190 | 1237 | 1242 | 1393 | 1319 | 1405 | 1273 | 1255 | 1132 | 1493 | 1317 | 1299 | 1373 | 1298 | 1352 | 1340 | 1359 | 1337 | 1346 | 1311 | 1239 | 1231 | 1271 | 1226 | 1226 | 1327 | 1199 | 1117 | 1353 |  |  | 1032 | 923 | 1323 |  | 1458 | 1164 | 1316 | 1270 | 1310 | 1312 | 1326 | 1335 | 1336 | 1342 | 1350 | 1370 | 1359 | 1543 | 1231 | 1148 | 1020 | 798 | 979 | 1148 | 1337 | 1483 | 1310 | 1374 | 1510 | 1470 | 1447 | 1446 | 1095 | 1240 | 1114 | 1230 | 1000 |  | 1175 | 1250 | 677 | 990 | 1243 |  |  | 1143 | 910 | 1120 | 1272 | 1090 | 35.1 | 50.1 | 1.5 | 4.3 |  | 0 | 6.1 |  |  | 81281718.732 | 281316.668 | 54421147.914 | 61118.521 | 82060118.024 | 185405.861 | 59347306.787 | 55089.676 | 308233092.831 | 82048.512 | 84893.039 | 23.329 | 83645.745 | 19.713 | 83185.05 | 46.441 | 66224.362 | 15.617 | 317553.665 | 61.857 | 168495.742 | 317491.808 | 12 | 0 | 6.1 | 35.1 | 50.1 | 1.5 | 4.3 | 318035
2025-04-05 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1504.6 | 1533.2 | 1434.3 | 1430 | 1445 | 1391.2 | 1356.7 | 1317.3 | 1381.6 | 1387.3 | 1455.5 | 1454.2 | 1440.4 | 1292.1 | 1355.1 | 1394 | 1331.7 | 1348.9 | 1501.1 | 1530.4 | 1546.5 | 1371.2 | 1560.1 | 1454.4 | 1534.3 | 1532.5 | 1531.3 | 1556.2 | 1527.9 | 1570.5 | 1505.5 | 1470.6 | 1313.6 | 1720.1 | 1297.8 | 1377.2 | 1345.7 | 1374.3 | 1377.6 | 1415.6 | 1362.5 | 1347.5 | 1385 | 1394.4 | 1407.1 | 1428.5 | 1531 | 1333.2 | 1335.4 | 1362.9 | 1293.4 | 1251.3 | 1435.5 | 1343.4 | 1343.5 | 1484.5 | 1393 | 1358.5 | 1493.6 | 1333.7 | 1336.2 | 1499.5 | 1330 | 1395 | 1228.2 | 1532.6 | 1556.8 | 1350.6 | 1398.8 | 1407.9 | 1155.1 | 1292.6 | 1352.3 | 1432.4 | 1406.4 | 1606.7 | 1626.1 | 1350.6 | 1390.2 | 1511.4 | 1330 | 1433.2 | 1416.4 | 1424.6 | 1408.1 | 1373.2 | 1428.1 | 1353.6 | 1261.8 | 1373.2 | 1445.8 | 1376.7 | 1448.3 | 1178.7 | 1335.9 | 1379.4 | 1391.1 | 1416.3 | 1364.5 | 1307.3 | 1407.6 | 1412.5 | 1353.5 | 1383.5 | 1585.5 | 1249.3 | 1625.4 | 1526.1 | 1387.9 | 1584.4 | 1465.9 | 1561.4 | 1594.4 | 1626 | 1388.8 | 1473.8 | 1592.9 | 1492.1 | 1537.2 | 1431.1 | 1447.2 | 1531.9 | 1473.6 | 1370.8 | 1451.2 | 1552.8 | 1306.1 | 1312.9 | 1614.4 | 1593.2 | 1447.4 | 1484.4 | 1451.1 | 1099.1 | 1502.4 | 1283.3 | 1499.9 | 1288.7 | 1498.1 | 1287.1 | 1328.6 | 1418.7 | 1403.1 | 1421.5 | 1217 | 1590.5 | 1425.6 | 1295.5 | 1495.1 | 1511.4 | 1542.1 | 1403.5 | 1418.5 | 1401 | 1470.4 | 1351.9 | 1352.2 | 1358.2 | 1260.1 | 1267.4 | 1420.8 | 1278.4 | 1204.2 | 1290.1 | 1275.9 | 1071.1 | 1297 | 1495.6 | 1347.2 | 1256.5 | 1304.3 | 1310.9 | 1471.5 | 1394.5 | 1532.6 | 1363.3 | 1339.4 | 1214.8 | 1587.4 | 1414.3 | 1383.9 | 1456.3 | 1382.3 | 1489.4 | 1433.9 | 1459 | 1438.5 | 1348.5 | 1388.4 | 1313.8 | 1306.3 | 1356.6 | 1317.1 | 1306.6 | 1420.1 | 1307.2 | 1211.5 | 1468.8 |  |  | 1255 | 961.6 | 1405.3 |  | 1536.5 | 1228.2 | 1427.6 | 1380.2 | 1379.5 | 1421.6 | 1440.7 | 1446.3 | 1448.2 | 1447.2 | 1467.8 | 1470.2 | 1421.8 | 1651.1 | 1307.4 | 1216.5 | 1054.2 | 886.9 | 976.1 | 1125.9 | 1296.6 | 1452.6 | 1280.3 | 1343.2 | 1345.4 | 1350.3 | 1382 | 1407 | 1368.9 | 1237.2 | 1020.7 | 1222.8 | 1112 |  | 1357.6 | 1431.1 | 664.3 | 1326.3 | 1213.4 |  |  | 1352.3 | 1156.6 | 1200 | 1239.6 | 1315.3 | 37.8 | 58.63 | 1.48 | 7.5 |  | 0 | 5.9 |  |  | 81371402.865 | 281330.577 | 54509149.521 | 61128.592 | 82148517.468 | 185452.895 | 59414773.455 | 55101.734 | 308566273.151 | 82104.15 | 89684.133 | 13.909 | 88001.607 | 10.071 | 88399.444 | 47.034 | 67466.668 | 12.058 | 333180.32 | 55.638 | 177661.76 | 333124.682 | 12 | 0 | 5.9 | 37.8 | 58.63 | 1.48 | 7.5 | 336772.2
2025-04-06 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1483.7 | 1507.4 | 1390.6 | 1398.6 | 1408.1 | 1355.9 | 1384.8 | 1284.1 | 1385.7 | 1350.6 | 1418.7 | 1416.1 | 1404.9 | 1259.1 | 1321.8 | 1359.1 | 1288 | 1315.5 | 1451.8 | 1491 | 1390.3 | 1335.5 | 1520.9 | 1442 | 1495.9 | 1491.9 | 1482.8 | 1512.8 | 1484.6 | 1525.3 | 1420.3 | 1423.9 | 1281.8 | 1680.4 | 1266 | 1439.6 | 1311.6 | 1314.3 | 1342.3 | 1379.1 | 1330.4 | 1315.1 | 1351.1 | 1360.9 | 1367.2 | 1392.8 | 1401.6 | 1297.1 | 1335.7 | 1369.1 | 1287.3 | 1247.5 | 1430.7 | 1539 | 1396 | 1484 | 1406.3 | 1355.5 | 1490.3 | 1428 | 1401 | 1494.7 | 1330 | 1240 | 1290 | 1492.7 | 1521 | 1380.5 | 1361.5 | 1371.4 | 1186 | 1254.6 | 1292 | 1384.8 | 1390.5 | 1568.8 | 1584.7 | 1318.2 | 1354.2 | 1466.8 | 1392.7 | 1396.5 | 1379.4 | 1386.8 | 1371.7 | 1320 | 1391.2 | 1320.6 | 1190 | 1336.6 | 1400 | 1327.1 | 1411.7 | 1132 | 1311.5 | 1343.4 | 1354.1 | 1356.8 | 1329.4 | 1291.2 | 1422.7 | 1375.3 | 1392.6 | 1344.3 | 1547.1 | 1184.1 | 1579.4 | 1489.2 | 1350.9 | 1536 | 1419.3 | 1522.7 | 1545.1 | 1587.3 | 1335.4 | 1343.4 | 1555.8 | 1448.9 | 1404.1 | 1378.2 | 1408.2 | 1480.4 | 1421 | 1334 | 1402 | 1474 | 1280.9 | 1285.1 | 1631.8 | 1558.2 | 1414.7 | 1491.6 | 1419.5 | 1075 | 1459.2 | 1255.6 | 1412.5 | 1258.4 | 1461.4 | 1256.3 | 1298.5 | 1388.3 | 1368.9 | 1388.3 | 1187 | 1553.6 | 1393.8 | 1263.7 | 1460.7 | 1476.7 | 1505.2 | 1371.8 | 1481.4 | 1357.2 | 1339.9 | 1323.9 | 1325.2 | 1330.4 | 1231 | 1240.3 | 1425 | 1281 | 1226.7 | 1352 | 1257.6 | 1044.9 | 1265.9 | 1460.2 | 1317 | 1229.5 | 1274.1 | 1297.8 | 1433.1 | 1365.5 | 1544.3 | 1365.1 | 1357.1 | 1225.7 | 1500 | 1416.6 | 1394.3 | 1448.1 | 1403 | 1471.9 | 1439.5 | 1455 | 1444.6 | 1444.5 | 1393.3 | 1327.1 | 1359.2 | 1359.1 | 1314.7 | 1345.6 | 1408.7 | 1267.8 | 1163.3 | 1428 |  |  | 1244.9 | 955.3 | 1397 |  | 1559.7 | 1228 | 1408.2 | 1357.1 | 1340.5 | 1405.4 | 1413.7 | 1419.4 | 1422.7 | 1443.7 | 1435 | 1430.4 | 1382.3 | 1613.2 | 1272.7 | 1185.7 | 1040 | 855 | 988.1 | 1154 | 1354.8 | 1534.6 | 1334.7 | 1407 | 1405 | 1402 | 1416.5 | 1470.3 | 1098.5 | 1277.1 | 1167.1 | 1276.3 | 1026.3 |  | 1176.1 | 1407.9 | 758.9 | 1223.4 | 1213.7 |  |  | 1391.4 | 1280.4 | 1195 | 1190.5 | 1310 | 39.3 | 47.4 | 1.2 | 5.33 |  | 0 | 6.92 |  |  | 81459682.41 | 281344.869 | 54594618.216 | 61137.77 | 82235619.976 | 185501.963 | 59483445.32 | 55113.894 | 308895385.727 | 82159.511 | 88279.545 | 14.292 | 85468.695 | 9.178 | 87102.508 | 49.068 | 68671.865 | 12.16 | 329112.576 | 55.361 | 173724.77 | 329057.215 | 12 | 0 | 6.92 | 39.3 | 47.4 | 1.2 | 5.33 | 331522.2
2025-04-07 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1422 | 1445 | 1333 | 1339 | 1390 | 1300 | 1328 | 1280 | 1328 | 1340 | 1358 | 1356 | 1344 | 1204 | 1262 | 1299 | 1290 | 1256 | 1400 | 1422 | 1328 | 1276 | 1452 | 1420 | 1427 | 1421 | 1414 | 1440 | 1411 | 1444 | 1478 | 1390 | 1226 | 1612 | 1280 | 1410 | 1296 | 1259 | 1286 | 1322 | 1276 | 1262 | 1294 | 1303 | 1310 | 1334 | 1429 | 1297 | 1310 | 1314 | 1260 | 1230 | 1398 | 1476 | 1388 | 1426 | 1424 | 1301 | 1427 | 1394 | 1301 | 1435 | 1340 | 1310 | 1440 | 1430 | 1456 | 1299 | 1302 | 1315 | 1328 | 1210 | 1250 | 1332 | 1350 | 1502 | 1519 | 1320 | 1300 | 1406 | 1334 | 1338 | 1322 | 1330 | 1315 | 1297 | 1333 | 1317 | 1296 | 1281 | 1342 | 1376 | 1353 | 1191 | 1410 | 1289 | 1300 | 1299 | 1276 | 1260 | 1364 | 1319 | 1336 | 1293 | 1487 | 1200 | 1514 | 1425 | 1295 | 1473 | 1390 | 1460 | 1472 | 1519 | 1269 | 1374 | 1488 | 1420 | 1406 | 1331 | 1353 | 1420 | 1390 | 1282 | 1354 | 1478 | 1260 | 1280 | 1513 | 1491 | 1396 | 1392 | 1398 | 1100 | 1404 | 1299 | 1391 | 1260 | 1394 | 1280 | 1290 | 1388 | 1307 | 1399 | 1189 | 1484 | 1331 | 1211 | 1400 | 1415 | 1439 | 1316 | 1421 | 1312 | 1286 | 1271 | 1310 | 1274 | 1287 | 1303 | 1433 | 1269 | 1280 | 1372 | 1311 | 1099 | 1242 | 1430 | 1307 | 1299 | 1298 | 1296 | 1427 | 1341 | 1528 | 1337 | 1314 | 1230 | 1543 | 1364 | 1355 | 1403 | 1395 | 1430 | 1409 | 1475 | 1393 | 1402 | 1369 | 1306 | 1304 | 1304 | 1258 | 1291 | 1353 | 1211 | 1116 | 1354 |  |  | 1220 | 939 | 1360 |  | 1488 | 1230 | 1350 | 1301 | 1275 | 1339 | 1357 | 1357 | 1365 | 1378 | 1384 | 1372 | 1320 | 1552 | 1224 | 1135 | 1020 | 910 | 972 | 1145 | 1336 | 1510 | 1314 | 1386 | 1410 | 1378 | 1387 | 1459 | 1200 | 1256 | 1155 | 1268 | 1150 |  | 1700 | 1410 | 600 | 1210 | 1245 |  |  | 1178 | 1300 | 1300 | 1130 | 1098 | 41.9 | 51.1 | 1.1 | 3.13 |  | 0 | 6.5257 |  |  | 81544202.804 | 281359.701 | 54676516.993 | 61149.622 | 82320465.624 | 185544.891 | 59549914.342 | 55125.834 | 309212772.728 | 82213.909 | 84520.394 | 14.832 | 81898.777 | 11.852 | 84845.648 | 42.928 | 66469.022 | 11.94 | 317387.001 | 54.398 | 166392.487 | 317332.603 | 12 | 0 | 6.5257 | 41.9 | 51.1 | 1.1 | 3.13 | 324271
2025-04-08 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1318.6 | 1341.3 | 1243.2 | 1247 | 1320.2 | 1214.4 | 1280.2 | 1243.7 | 1300.1 | 1272.5 | 1269.5 | 1258.1 | 1280 | 1177.2 | 1212.7 | 1230 | 1240 | 1245 | 1380 | 1324 | 1335.1 | 1240.1 | 1340.2 | 1430 | 1324.4 | 1313.7 | 1380 | 1388 | 1382.3 | 1395.6 | 1390.6 | 1325.8 | 1190 | 1600.1 | 1248.6 | 1391.3 | 1275.2 | 1230.4 | 1280.2 | 1237.1 | 1290 | 1250 | 1240 | 1219.6 | 1228.8 | 1245.6 | 1341.3 | 1287.8 | 1301.9 | 1300.9 | 1278.2 | 1272.1 | 1390.9 | 1396.9 | 1345.9 | 1420.1 | 1420.7 | 1290.3 | 1448.3 | 1377.7 | 1249.4 | 1420 | 1308 | 1215.9 | 1333.8 | 1331.1 | 1352.3 | 1270.2 | 1280.4 | 1312.7 | 1239.3 | 1219.4 | 1243.7 | 1246.1 | 1333.5 | 1408.1 | 1423.7 | 1235.4 | 1292.2 | 1401.8 | 1250.3 | 1254.3 | 1238.3 | 1245.2 | 1239.6 | 1277.3 | 1243.8 | 1280.5 | 1290.2 | 1280.5 | 1336.9 | 1350.1 | 1265.5 | 1232.5 | 1360.4 | 1280.9 | 1290.7 | 1288.9 | 1240.4 | 1255.4 | 1253.8 | 1232 | 1248.8 | 1280.1 | 1395.2 | 1230.9 | 1413.9 | 1420.8 | 1289.4 | 1430.5 | 1370.5 | 1369 | 1396.3 | 1427.1 | 1250.6 | 1301.5 | 1405.5 | 1401.3 | 1399.4 | 1254.3 | 1268.5 | 1390.1 | 1368.2 | 1290.5 | 1268.5 | 1463.7 | 1247.1 | 1252.4 | 1419 | 1399.3 | 1372.1 | 1390.7 | 1376 | 1090 | 1398.1 | 1290.3 | 1366 | 1300.5 | 1310.7 | 1227.4 | 1265.5 | 1352 | 1324.9 | 1388.5 | 1190 | 1395.2 | 1299.5 | 1190.8 | 1390.3 | 1428.4 | 1399 | 1331 | 1426.6 | 1264 | 1299.3 | 1289.5 | 1295.9 | 1292.9 | 1276 | 1244.6 | 1477.1 | 1266.3 | 1328.3 | 1397 | 1423.5 | 1230.5 | 1277.5 | 1380.6 | 1249.5 | 1300.4 | 1299.9 | 1290.3 | 1410.4 | 1364.3 | 1454 | 1278.8 | 1281.5 | 1250.5 | 1475.3 | 1305.3 | 1366.5 | 1400.8 | 1388.2 | 1420 | 1388 | 1405.5 | 1339.6 | 1329.6 | 1310.6 | 1343.2 | 1288.1 | 1322.6 | 1250 | 1280 | 1270.9 | 1235.8 | 1052.1 | 1272.5 |  |  | 1204.6 | 930.1 | 1270.3 |  | 1452.5 | 1212.5 | 1261.4 | 1287.9 | 1272.6 | 1280.9 | 1287.5 | 1295.7 | 1297 | 1317.5 | 1290.5 | 1282.4 | 1324.1 | 1454.9 | 1144.9 | 1120.5 | 916.4 | 760.2 | 970.5 | 1177.5 | 1352.4 | 1415.5 | 1300 | 1296 | 1295.8 | 1280.2 | 1380.8 | 1471.4 | 1190.3 | 1250.5 | 1187 | 1250.8 | 1092.1 |  | 1708.5 | 1400.2 | 550.8 | 1210.9 | 1212.7 |  |  | 1162.8 | 1288.5 | 1315.2 | 1140.2 | 1115.2 | 43.9 | 51.1 | 1.1 | 3.13 |  | 0 | 6.0578 |  |  | 81623456.674 | 281374.677 | 54753444.461 | 61162.416 | 82400731.86 | 185586.944 | 59612531.256 | 55139.475 | 309511535.47 | 82271.483 | 79253.87 | 14.976 | 76927.468 | 12.794 | 80266.236 | 42.053 | 62616.914 | 13.641 | 298762.742 | 57.574 | 156153.568 | 298705.168 | 12 | 0 | 6.0578 | 43.9 | 51.1 | 1.1 | 3.13 | 315636
2025-04-09 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1233 | 1254 | 1180 | 1165 | 1222 | 1133 | 1158 | 1172 | 1199 | 1188 | 1189 | 1184 | 1173 | 1040 | 1098 | 1130 | 1120 | 1130 | 1219 | 1232 | 1150 | 1130 | 1248 | 1250 | 1231 | 1222 | 1290 | 1250 | 1255 | 1250 | 1300 | 1242 | 1073 | 351 | 1114 | 1208 | 1150 | 1102 | 1124 | 1155 | 1160 | 1160 | 1132 | 1141 | 1146 | 1164 | 1252 | 1136 | 1188 | 1178 | 1150 | 1171 | 1336 | 1329 | 1250 | 1278 | 1280 | 1171 | 1281 | 1270 | 1149 | 1291 | 1220 | 1080 | 1246 | 1244 | 1264 | 1190 | 1148 | 1143 | 1158 | 1132 | 1140 | 1166 | 1277 | 1316 | 1330 | 1154 | 1138 | 1250 | 1168 | 1172 | 1156 | 1164 | 1148 | 1155 | 1162 | 1143 | 1129 | 1140 | 1180 | 1310 | 1182 | 1160 | 1398 | 1125 | 1135 | 1162 | 1160 | 1150 | 1195 | 1153 | 1170 | 1131 | 1304 | 1140 | 1325 | 1302 | 1180 | 1290 | 1222 | 1281 | 1325 | 1334 | 1140 | 1205 | 1310 | 1319 | 1262 | 1178 | 1187 | 1298 | 1240 | 1123 | 1186 | 1498 | 1167 | 1140 | 1321 | 1303 | 1240 | 1218 | 1230 | 1000 | 1225 | 1245 | 1199 | 1200 | 1215 | 1150 | 1199 | 1240 | 1138 | 1230 | 1100 | 1298 | 1134 | 1057 | 1260 | 1239 | 1253 | 1147 | 1290 | 1141 | 1120 | 1108 | 1198 | 1140 | 1098 | 1162 | 1293 | 1146 | 1230 | 1280 | 1270 | 1160 | 1129 | 1297 | 1179 | 1200 | 1162 | 1166 | 1280 | 1207 | 1359 | 1195 | 1200 | 1176 | 1386 | 1218 | 1226 | 1259 | 1290 | 1300 | 1256 | 1327 | 1252 | 1243 | 1232 | 1240 | 1153 | 1156 | 1130 | 1139 | 1220 | 1150 | 1009 | 1233 |  |  | 1198 | 898 | 1280 |  | 1250 | 1278 | 1182 | 1172 | 1149 | 1209 | 1214 | 1233 | 1230 | 1244 | 1213 | 1201 | 1230 | 1365 | 1072 | 1110 | 860 | 810 | 910 | 1011 | 1213 | 1372 | 1198 | 1244 | 1298 | 1278 | 1287 | 1300 | 1099 | 1219 | 1099 | 1124 | 1010 |  | 1498 | 1398 | 450 | 1198 | 1123 |  |  | 1098 | 1298 | 1199 | 1110 | 1110 | 39.9 | 50.1 | 1.1 | 3.4 |  | 0 | 5.6268 |  |  | 81698640.225 | 281383.068 | 54825971.097 | 61171.181 | 82476110.299 | 185620.066 | 59671741.712 | 55149.599 | 309793554.329 | 82309.564 | 75183.551 | 8.391 | 72526.636 | 8.765 | 75378.439 | 33.122 | 59210.456 | 10.124 | 282018.859 | 38.081 | 147693.031 | 281980.778 | 12 | 0 | 5.6268 | 39.9 | 50.1 | 1.1 | 3.4 | 289705
2025-04-10 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 971 | 984 | 912 | 911 | 965 | 892 | 901 | 932 | 990 | 940 | 926 | 922 | 910 | 818 | 854 | 882 | 940 | 940 | 952 | 963 | 896 | 920 | 981 | 960 | 963 | 954 | 999 | 950 | 935 | 954 | 990 | 1000 | 835 | 1105 | 888 | 940 | 898 | 857 | 874 | 890 | 899 | 899 | 888 | 883 | 893 | 908 | 978 | 884 | 898 | 976 | 925 | 864 | 990 | 980 | 950 | 997 | 988 | 860 | 999 | 990 | 943 | 1010 | 910 | 898 | 968 | 964 | 980 | 950 | 884 | 885 | 898 | 881 | 862 | 902 | 1010 | 1020 | 1030 | 893 | 899 | 968 | 904 | 906 |  | 900 | 889 | 899 | 907 | 895 | 883 | 898 | 917 | 992 | 918 | 892 | 978 | 868 | 876 | 897 | 896 | 949 | 926 | 895 | 908 | 950 | 1008 | 909 | 1021 | 1005 | 914 | 1000 | 947 | 989 | 1032 | 1031 | 883 | 933 | 1012 | 961 | 972 | 938 | 960 | 978 | 943 | 894 | 919 | 1010 | 826 | 833 | 1022 | 1010 | 920 | 949 | 927 | 805 | 958 | 913 | 916 | 809 | 949 | 929 | 946 | 915 | 850 | 960 | 931 | 928 | 840 | 784 | 904 | 921 | 928 | 847 | 1010 | 845 | 831 | 822 | 910 | 922 | 862 | 916 | 1009 | 893 | 933 | 968 | 1002 | 945 | 883 | 1007 | 932 | 961 | 919 | 913 | 1015 | 954 | 1053 | 924 | 928 | 931 | 1068 | 942 | 945 | 970 | 952 | 1009 | 971 | 1031 | 969 | 965 | 957 | 920 | 899 | 994 | 851 | 886 | 946 | 853 | 796 | 964 |  |  | 840 | 646 | 940 |  | 1012 | 929 | 912 | 897 | 890 | 932 | 945 | 947 | 948 | 958 | 970 | 950 | 954 | 1101 | 834 | 767 | 620 | 610 | 653 | 760 | 895 | 1014 | 943 | 929 | 978 | 998 | 967 | 949 | 913 | 932 | 846 | 934 | 773 |  | 1175 | 950 | 426 | 862 | 815 |  |  | 898 | 978 | 1010 | 898 | 810 | 34.9 | 49 | 3 | 5 |  | 0 | 4.36 |  |  | 81756527.707 | 281390.022 | 54882722.441 | 61177.887 | 82534835.19 | 185649.094 | 59717471.191 | 55158.877 | 310012420.729 | 82339.924 | 57887.482 | 6.954 | 56751.344 | 6.706 | 58724.891 | 29.028 | 45729.479 | 9.278 | 218866.4 | 30.36 | 114625.166 | 218836.04 | 12 | 0 | 4.36 | 34.9 | 49 | 3 | 5 | 223694
2025-04-11 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1107 | 1131 | 1048 | 1046 | 1110 | 1025 | 1029 | 1010 | 1041 | 1024 | 1059 | 1057 | 1043 | 938 | 1012 | 1049 | 963 | 996 | 1092 | 1126 | 1059 | 1022 | 1171 | 1093 | 1113 | 1110 | 1097 | 1120 | 1091 | 1121 | 1200 | 1098 | 961 | 1283 | 908 | 1079 | 986 | 987 | 1033 | 1057 | 989 | 989 | 1029 | 1044 | 1025 | 1049 | 1122 | 1040 | 1035 | 1060 | 1004 | 1050 | 1201 | 1188 | 1087 | 1154 | 1143 | 1040 | 1149 | 1106 | 1034 | 1163 | 1210 | 1098 | 1128 | 1120 | 1150 | 1099 | 1027 | 1031 | 1069 | 1059 | 1046 | 1049 | 1170 | 1170 | 1184 | 1017 | 1007 | 1122 | 1040 | 1040 | 1038 | 1039 | 1026 | 1036 | 1084 | 1074 | 1044 | 1041 | 1067 | 1078 | 1082 | 1024 | 1200 | 1002 | 1032 | 1063 | 1038 | 1041 | 1079 | 1035 | 1066 | 1036 | 1198 | 1044 | 1186 | 1175 | 1068 | 1187 | 1146 | 1140 | 1201 | 1189 | 1048 | 1074 | 1172 | 1114 | 1175 | 1064 | 1094 | 1133 | 1114 | 1030 | 1081 | 1478 | 950 | 968 | 1165 | 1154 | 1059 | 1083 | 1051 | 898 | 1104 | 1098 | 1051 | 978 | 1059 | 1004 | 988 | 1046 | 1024 | 1094 | 999 | 1168 | 1006 | 942 | 1093 | 1113 | 1126 | 1026 | 1119 | 1024 | 1001 | 988 | 1050 | 1178 | 966 | 1025 | 1130 | 1001 | 1039 | 1088 | 1125 | 1055 | 983 | 1137 | 1040 | 999 | 1025 | 1019 | 1140 | 1068 | 1201 | 1044 | 1043 | 931 | 1199 | 1059 | 1068 | 1096 | 1076 | 1159 | 1100 | 1172 | 1089 | 1104 | 1069 | 1034 | 1021 | 1016 | 977 | 1005 | 1064 | 962 | 900 | 1086 |  |  | 944 | 738 | 1059 |  | 1165 | 1132 | 1051 | 1020 | 1045 | 1058 | 1065 | 1072 | 1069 | 1083 | 1086 | 1080 | 1149 | 1235 | 975 | 894 | 790 | 640 | 781 | 913 | 999 | 1200 | 1018 | 1100 | 1098 | 1097 | 1186 | 1141 | 975 | 994 | 900 | 997 | 960 |  | 1250 | 1068 | 398 | 985 | 918 |  |  | 1000 | 1000 | 1088 | 945 | 913 | 36.6 | 55.86 | 2.52 | 13.1 |  | 0 | 4.88 |  |  | 81824612.484 | 281411.612 | 54949789.39 | 61214.424 | 82601901.2 | 185683.778 | 59770602.626 | 55201.359 | 310267495.625 | 82401.977 | 68084.777 | 21.59 | 67066.949 | 36.537 | 67066.01 | 34.684 | 53131.435 | 42.482 | 255074.896 | 62.053 | 135093.599 | 255012.843 | 12 | 0 | 4.88 | 36.6 | 55.86 | 2.52 | 13.1 | 257651
2025-04-12 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1392 | 1415 | 1315 | 1313 | 1396 | 1287 | 1302 | 1199 | 1310 | 1288 | 1332 | 1330 | 1311 | 1180 | 1282 | 1324 | 1249 | 1276 | 1409 | 1442 | 1345 | 1293 | 1481 | 1303 | 1448 | 1440 | 1433 | 1457 | 1386 | 1425 | 1350 | 1378 | 1215 | 1600 | 1148 | 1364 | 1263 | 1294 | 1315 | 1346 | 1296 | 1283 | 1310 | 1327 | 1323 | 1325 | 1442 | 1332 | 1230 | 1260 | 1210 | 1198 | 1388 | 1330 | 1202 | 1275 | 1255 | 1133 | 1286 | 1232 | 1178 | 1283 | 1226 | 1110 | 1455 | 1446 | 1484 | 1318 | 1327 | 1334 | 1358 | 1333 | 1268 | 1357 | 1396 | 1480 | 1496 | 1286 | 1271 | 1422 | 1315 | 1316 | 1314 | 1316 | 1325 | 1284 | 1365 | 1352 | 1326 | 1320 | 1378 | 1240 | 1377 | 1313 | 1330 | 1310 | 1319 | 1357 | 1349 | 1265 | 1394 | 1348 | 1370 | 1321 | 1518 | 1220 | 1501 | 1505 | 1370 | 1506 | 1425 | 1441 | 1505 | 1517 | 1327 | 1360 | 1494 | 1404 | 1455 | 1341 | 1375 | 1432 | 1394 | 1297 | 1365 | 1498 | 1229 | 1261 | 1478 | 1470 | 1398 | 1378 | 1335 | 1131 | 1432 | 1299 | 1365 | 1270 | 1341 | 1331 | 1271 | 1318 | 1310 | 1440 | 1254 | 1486 | 1282 | 1202 | 1390 | 1411 | 1432 | 1306 | 1424 | 1344 | 1272 | 1254 | 1190 | 1245 | 1213 | 1288 | 1419 | 1257 | 1285 | 1373 | 1340 | 1267 | 1242 | 1429 | 1307 | 1203 | 1285 | 1277 | 1426 | 1341 | 1520 | 1330 | 1339 | 1206 | 1531 | 1361 | 1374 | 1404 | 1367 | 1452 | 1399 | 1481 | 1401 | 1403 | 1344 | 1318 | 1287 | 1283 | 1200 | 1262 | 1333 | 1206 | 1129 | 1357 |  |  | 1197 | 926 | 1327 |  | 1466 | 1210 | 1324 | 1289 | 1303 | 1331 | 1339 | 1346 | 1342 | 1362 | 1365 | 1361 | 1361 | 1553 | 1225 | 1138 | 910 | 810 | 977 | 1143 | 1327 | 1510 | 1282 | 1386 | 1298 | 1310 | 1445 | 1432 | 1178 | 1248 | 1136 | 1251 | 1178 |  | 1478 | 1263 | 578 | 1163 | 1153 |  |  | 1078 | 1178 | 1299 | 1270 | 1078 | 29.88 | 43.21 | 1.3 | 6.1 |  | 0 | 6.15 |  |  | 81907526.273 | 281425.064 | 55034099.627 | 61224.371 | 82686891.459 | 185720.486 | 59836769.598 | 55214.015 | 310585448.108 | 82457.052 | 82913.789 | 13.452 | 84310.237 | 9.947 | 84990.259 | 36.708 | 66166.972 | 12.656 | 317952.483 | 55.075 | 167200.627 | 317897.408 | 12 | 0 | 6.15 | 29.88 | 43.21 | 1.3 | 6.1 | 321089
2025-04-13 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1443 | 1470 | 1366 | 1365 | 1450 | 1339 | 1367 | 1257 | 1372 | 1348 | 1426 | 1416 | 1391 | 1259 | 1335 | 1374 | 1312 | 1329 | 1487 | 1496 | 1394 | 1339 | 1532 | 1445 | 1504 | 1493 | 1486 | 1516 | 1473 | 1510 | 1310 | 1334 | 1276 | 1687 | 1200 | 1433 | 1316 | 1339 | 1358 | 1394 | 1342 | 1331 | 1354 | 1369 | 1383 | 1405 | 1508 | 1384 | 1308 | 1340 | 1266 | 1331 | 1518 | 1502 | 1388 | 1478 | 1445 | 1305 | 1491 | 1433 | 1332 | 1477 | 1278 | 1080 | 1515 | 1506 | 1525 | 1340 | 1380 | 1387 | 1396 | 1345 | 1277 | 1408 | 1417 | 1548 | 1570 | 1370 | 1363 | 1486 | 1403 | 1402 | 1397 | 1399 | 1385 | 1326 | 1407 | 1391 | 1365 | 1358 | 1418 | 1278 | 1427 | 1363 | 1310 | 1365 | 1361 | 1386 | 1393 | 1278 | 1445 | 1391 | 1413 | 1364 | 1564 | 1198 | 1568 | 1563 | 1425 | 1551 | 1444 | 1512 | 1558 | 1582 | 1357 | 1423 | 1550 | 1449 | 1479 | 1390 | 1419 | 1491 | 1416 | 1340 | 1412 | 1464 | 1290 | 1319 | 1546 | 1539 | 1463 | 1446 | 1402 | 1195 | 1532 | 1480 | 1477 | 1454 | 1407 | 1399 | 1332 | 1390 | 1379 | 1550 | 1321 | 1573 | 1393 | 1262 | 1453 | 1478 | 1495 | 1364 | 1485 | 1357 | 1326 | 1312 | 1178 | 1326 | 1265 | 1341 | 1518 | 1317 | 1378 | 1452 | 1354 | 1231 | 1307 | 1512 | 1386 | 1284 | 1372 | 1364 | 1508 | 1431 | 1578 | 1382 | 1399 | 1254 | 1604 | 1418 | 1437 | 1471 | 1442 | 1505 | 1453 | 1544 | 1454 | 1458 | 1432 | 1389 | 1327 | 1322 | 1165 | 1301 | 1384 | 1241 | 1164 | 1401 |  |  | 1203 | 955 | 1364 |  | 1503 | 1210 | 1370 | 1348 | 1335 | 1390 | 1401 | 1411 | 1406 | 1426 | 1408 | 1417 | 1365 | 1601 | 1273 | 1182 | 898 | 878 | 1007 | 1184 | 1373 | 1578 | 1365 | 1452 | 1278 | 1363 | 1482 | 1486 | 1117 | 1295 | 1179 | 1299 | 1198 |  | 1520 | 1365 | 644 | 1183 | 1195 |  |  | 1163 | 1191 | 1298 | 1263 | 1191 | 31.82 | 40.8 | 3.02 | 7.1 |  | 0 | 6.14 |  |  | 81995608.799 | 281439.981 | 55121205.499 | 61234.011 | 82776560.366 | 185766.511 | 59905210.194 | 55227.06 | 310918312.508 | 82518.014 | 88082.526 | 14.917 | 87105.872 | 9.64 | 89668.907 | 46.025 | 68440.596 | 13.045 | 332864.4 | 60.962 | 175163.841 | 332803.438 | 12 | 0 | 6.14 | 31.82 | 40.8 | 3.02 | 7.1 | 335292
2025-04-14 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1457 | 1485 | 1383 | 1384 | 1471 | 1363 | 1382 | 1266 | 1395 | 1362 | 1427 | 1413 | 1392 | 1266 | 1323 | 1363 | 1295 | 1314 | 1471 | 1480 | 1380 | 1326 | 1521 | 1432 | 1489 | 1477 | 1472 | 1503 | 1460 | 1495 | 1363 | 1322 | 1300 | 1681 | 1208 | 1455 | 1304 | 1321 | 1347 | 1379 | 1324 | 1311 | 1336 | 1351 | 1355 | 1388 | 1491 | 1378 | 1306 | 1336 | 1263 | 1328 | 1503 | 1483 | 1374 | 1465 | 1450 | 1285 | 1471 | 1413 | 1314 | 1477 | 1263 | 1098 | 1499 | 1488 | 1509 | 1330 | 1365 | 1371 | 1381 | 1331 | 1270 | 1392 | 1398 | 1557 | 1588 | 1371 | 1355 | 1468 | 1406 | 1401 | 1383 | 1383 | 1369 | 1307 | 1391 | 1377 | 1350 | 1345 | 1399 | 1298 | 1412 | 1349 | 1298 | 1348 | 1344 | 1373 | 1376 | 1266 | 1424 | 1373 | 1396 | 1348 | 1541 | 1182 | 1572 | 1545 | 1406 | 1534 | 1402 | 1496 | 1547 | 1563 | 1342 | 1406 | 1533 | 1433 | 1456 | 1377 | 1403 | 1478 | 1398 | 1324 | 1394 | 1478 | 1276 | 1297 | 1521 | 1514 | 1438 | 1450 | 1423 | 1207 | 1544 | 1486 | 1480 | 1439 | 1398 | 1402 | 1353 | 1398 | 1391 | 1546 | 1328 | 1565 | 1356 | 1251 | 1446 | 1470 | 1480 | 1353 | 1495 | 1345 | 1319 | 1307 | 1190 | 1325 | 1281 | 1356 | 1534 | 1330 | 1307 | 1453 | 1357 | 1191 | 1312 | 1512 | 1376 | 1269 | 1361 | 1349 | 1379 | 1417 | 1548 | 1357 | 1378 | 1233 | 1578 | 1394 | 1415 | 1446 | 1424 | 1480 | 1428 | 1531 | 1433 | 1433 | 1412 | 1273 | 1324 | 1306 | 1166 | 1330 | 1395 | 1255 | 1168 | 1419 |  |  | 1188 | 943 | 1357 |  | 1484 | 1173 | 1353 | 1339 | 1334 | 1382 | 1399 | 1406 | 1403 | 1420 | 1404 | 1399 | 1358 | 1587 | 1257 | 1164 | 963 | 810 | 993 | 1174 | 1379 | 1562 | 1386 | 1448 | 1298 | 1378 | 1490 | 1469 | 1109 | 1291 | 1169 | 1300 | 1178 |  | 1498 | 1382 | 633 | 1197 | 1176 |  |  | 1110 | 1263 | 1278 | 1210 | 1163 | 32.37 | 45.01 | 1.79 | 6.1 |  | 0 | 6.51 |  |  | 82083194.141 | 281455.645 | 55207413.543 | 61246.338 | 82865707.869 | 185809.522 | 59973320.461 | 55239.414 | 311248951.343 | 82573.423 | 87585.342 | 15.664 | 86208.044 | 12.327 | 89147.503 | 43.011 | 68110.267 | 12.354 | 330638.835 | 55.409 | 173765.395 | 330583.426 | 12 | 0 | 6.51 | 32.37 | 45.01 | 1.79 | 6.1 | 333086
2025-04-15 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1424 | 1452 | 1351 | 1355 | 1432 | 1328 | 1333 | 1228 | 1351 | 1319 | 1378 | 1365 | 1343 | 1222 | 1274 | 1315 | 1276 | 1273 | 1433 | 1422 | 1325 | 1272 | 1460 | 1364 | 1435 | 1419 | 1415 | 1447 | 1410 | 1444 | 1378 | 1307 | 1269 | 1631 | 1194 | 1425 | 1295 | 1301 | 1312 | 1349 | 1308 | 1290 | 1301 | 1315 | 1322 | 1345 | 1444 | 1333 | 1288 | 1318 | 1246 | 1311 | 1484 | 1465 | 1357 | 1449 | 1431 | 1267 | 1471 | 1414 | 1312 | 1467 | 1278 | 1461 | 1451 | 1457 | 1289 | 1318 | 1326 | 1335 | 1290 | 1229 | 1346 | 1377 | 1525 | 1545 | 1323 | 1424 | 1360 | 1356 | 1337 | 1337 | 1325 | 1272 | 1345 | 1333 | 1304 | 1301 | 1351 | 1412 | 1365 | 1303 | 1410 | 1363 | 1278 | 1302 | 1311 | 1332 | 1337 | 1234 | 1379 | 1333 | 1356 | 1334 | 1495 | 1151 | 1520 | 1496 | 1360 | 1484 | 1364 | 1465 | 1512 | 1514 | 1304 | 1359 | 1485 | 1340 | 1413 | 1345 | 1376 | 1437 | 1362 | 1281 | 1348 | 1463 | 1259 | 1279 | 1502 | 1497 | 1429 | 1435 | 1394 | 1190 | 1519 | 1470 | 1471 | 1445 | 1351 | 1358 | 1330 | 1361 | 1349 | 1499 | 1286 | 1510 | 1315 | 1214 | 1401 | 1428 | 1435 | 1316 | 1458 | 1314 | 1292 | 1278 | 1163 | 1280 | 1242 | 1316 | 1496 | 1299 | 1421 | 1434 | 1317 | 1289 | 1269 | 1462 | 1328 | 1218 | 1314 | 1299 | 1292 | 1364 | 1499 | 1313 | 1332 | 1194 | 1524 | 1348 | 1368 | 1394 | 1394 | 1432 | 1380 | 1487 | 1386 | 1386 | 1356 | 1250 | 1306 | 1259 | 1150 | 1292 | 1349 | 1224 | 1144 | 1376 |  |  | 1157 | 926 | 1317 |  | 1436 | 1214 | 1307 | 1292 | 1294 | 1336 | 1353 | 1359 | 1356 | 1371 | 1380 | 1384 | 1333 | 1568 | 1217 | 1125 | 925 | 863 | 881 | 1178 | 1363 | 1510 | 1310 | 1410 | 1263 | 1298 | 1445 | 1478 | 1111 | 1270 | 1163 | 1278 | 1110 |  | 1478 | 1351 | 614 | 1180 | 1168 |  |  | 1135 | 1256 | 1270 | 1225 | 1135 | 32.7 | 43.6 | 1.6 | 6.5 |  | 0 | 6.23 |  |  | 82168621 | 281469 | 55291405 | 61256 | 82952664 | 185854 | 60036190 | 55251 | 311567840.3 | 82626.6 | 85426.859 | 13.355 | 83991.457 | 9.662 | 86956.131 | 44.478 | 62869.539 | 11.586 | 318888.957 | 53.177 | 169395.299 | 318835.78 | 12 | 0 | 6.23 | 32.7 | 43.6 | 1.6 | 6.5 | 326506
2025-04-16 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1403 | 1428 | 1328 | 1330 | 1407 | 1310 | 1313 | 1209 | 1330 | 1298 | 1360 | 1346 | 1322 | 1202 | 1275 | 1314 | 1266 | 1274 | 1431 | 1434 | 1331 | 1280 | 1465 | 1380 | 1432 | 1413 | 1413 | 1430 | 1380 | 1409 | 1363 | 1253 | 1250 | 1608 | 1211 | 1402 | 1307 | 1288 | 1309 | 1342 | 1294 | 1279 | 1290 | 1304 | 1308 | 1355 | 1444 | 1315 | 1283 | 1313 | 1247 | 1312 | 1495 | 1480 | 1355 | 1437 | 1411 | 1252 | 1480 | 1415 | 1301 | 1450 | 1263 | 1425 | 1462 | 1453 | 1476 | 1268 | 1323 | 1333 | 1342 | 1277 | 1196 | 1331 | 1355 | 1512 | 1525 | 1301 | 1288 | 1396 | 1338 | 1335 | 1314 | 1316 | 1309 | 1255 | 1341 | 1330 | 1314 | 1307 | 1369 | 1290 | 1351 | 1298 | 1263 | 1282 | 1290 | 1302 | 1315 | 1202 | 1360 | 1314 | 1337 | 1315 | 1478 | 1124 | 1497 | 1472 | 1340 | 1496 | 1353 | 1444 | 1474 | 1490 | 1272 | 1339 | 1464 | 1338 | 1411 | 1341 | 1380 | 1427 | 1352 | 1303 | 1371 | 1425 | 1255 | 1295 | 1510 | 1509 | 1428 | 1425 | 1371 | 1168 | 1491 | 1442 | 1440 | 1415 | 1309 | 1332 | 1308 | 1362 | 1323 | 1471 | 1262 | 1481 | 1331 | 1238 | 1429 | 1470 | 1466 | 1335 | 1443 | 1327 | 1304 | 1296 | 1098 | 1259 | 1225 | 1298 | 1478 | 1284 | 1400 | 1431 | 1299 | 1269 | 1252 | 1439 | 1306 | 1199 | 1291 | 1277 | 1270 | 1338 | 1476 | 1294 | 1311 | 1176 | 1500 | 1328 | 1348 | 1376 | 1411 | 1411 | 1361 | 1466 | 1362 | 1364 | 1334 | 1188 | 1287 | 1244 | 1111 | 1272 | 1327 | 1203 | 1124 | 1350 |  |  | 1180 | 919 | 1296 |  | 1494 | 1220 | 1287 | 1275 | 1261 | 1317 | 1332 | 1337 | 1334 | 1350 | 1360 | 1363 | 1300 | 1546 | 1199 | 1105 | 910 | 825 | 943 | 1117 | 1316 | 1531 | 1339 | 1399 | 1278 | 1300 | 1418 | 1366 | 1094 | 1241 | 1113 | 1237 | 996 |  | 1175 | 1345 | 604 | 1261 | 1214 |  |  | 1098 | 1234 | 1301 | 1270 | 1117 | 34.09 | 46.02 | 1.33 | 6.1 |  | 0 | 6.27 |  |  | 82253458.237 | 281482.329 | 55374252.019 | 61264.956 | 83038923.775 | 185897.441 | 60101967.276 | 55263.176 | 311887179.23 | 82681.229 | 84837.237 | 13.329 | 82847.019 | 8.956 | 86259.775 | 43.441 | 65777.276 | 12.176 | 319338.93 | 54.629 | 167661.971 | 319284.301 | 12 | 0 | 6.27 | 34.09 | 46.02 | 1.33 | 6.1 | 323020
2025-04-17 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1355 | 1375 | 1281 | 1281 | 1360 | 1265 | 1275 | 1248 | 1295 | 1286 | 1306 | 1318 | 1296 | 1152 | 1240 | 1272 | 1217 | 1235 | 1379 | 1389 | 1297 | 1252 | 1423 | 1341 | 1381 | 1389 | 1379 | 1411 | 1370 | 1395 | 1310 | 1253 | 1203 | 1546 | 1189 | 1350 | 1285 | 1244 | 1275 | 1300 | 1246 | 1233 | 1257 | 1277 | 1267 | 1310 | 1389 | 1288 | 1219 | 1300 | 1208 | 1369 | 1450 | 1400 | 1314 | 1309 | 1400 | 1334 | 1400 | 1400 | 1324 | 1400 | 1461 | 1406 | 1398 | 1422 | 1400 | 1269 | 1295 | 1305 | 1211 | 1200 | 1300 | 1270 | 1460 | 1468 | 1500 | 1266 | 1360 | 1301 | 1308 | 1299 | 1303 | 1260 | 1180 | 1318 | 1303 | 1284 | 1248 | 1248 | 1331 | 1226 | 1334 | 1272 | 1298 | 1261 | 1264 | 1225 | 1266 | 1119 | 1307 | 1266 | 1294 | 1290 | 1452 | 1045 | 1499 | 1413 | 1289 | 1461 | 1306 | 1387 | 1391 | 1431 | 1192 | 1288 | 1409 | 1300 | 1359 | 1292 | 1326 | 1373 | 1280 | 1258 | 1331 | 1426 | 1213 | 1245 | 1451 | 1450 | 1376 | 1375 | 1318 | 1122 | 1436 | 1383 | 1387 | 1364 | 1293 | 1321 | 1262 | 1338 | 1288 | 1442 | 1240 | 1457 | 1306 | 1201 | 1394 | 1427 | 1427 | 1307 | 1451 | 1309 | 1286 | 1269 | 1026 | 1232 | 1178 | 1243 | 1423 | 1228 | 1337 | 1374 | 1239 | 1216 | 1201 | 1378 | 1254 | 1153 | 1240 | 1216 | 1284 | 1424 | 1245 | 1264 | 1132 | 1439 | 1500 | 1297 | 1323 | 1361 | 1400 | 1408 | 1316 | 1400 | 1284 | 1300 | 1284 | 1149 | 1236 | 1205 | 1079 | 1225 | 1274 | 1152 | 1069 | 1297 |  |  | 1132 | 882 | 1246 |  | 1363 | 1173 | 1241 | 1232 | 1183 | 1267 | 1281 | 1283 | 1281 | 1299 | 1308 | 1311 | 1215 | 1483 | 1152 | 1062 | 926 | 855 | 906 | 1082 | 1296 | 1480 | 1312 | 1364 | 1226 | 1280 | 1327 | 1331 | 1066 | 1228 | 1082 | 1218 | 984 |  | 1175 | 1318 | 585 | 1285 | 1178 |  |  | 1185 | 1251 | 1299 | 1251 | 1074 | 35.7 | 46 | 0.6 | 6.78 |  | 0 | 6.11 |  |  | 82335200 | 281497 | 55454144 | 61275 | 83122389 | 185944 | 60165461 | 55276 | 312195388.5 | 82741.8 | 81741.763 | 14.671 | 79891.981 | 10.044 | 83465.225 | 46.559 | 63493.724 | 12.824 | 308209.27 | 60.571 | 161609.029 | 308148.699 | 12 | 0 | 6.11 | 35.7 | 46 | 0.6 | 6.78 | 314197
2025-04-18 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1328 | 1353 | 1259 | 1355 | 1356 | 1247 | 1235 | 1251 | 1266 | 1254 | 1260 | 1276 | 1256 | 1105 | 1190 | 1224 | 1175 | 1184 | 1319 | 1330 | 1349 | 1204 | 1370 | 1379 | 1325 | 1333 | 1325 | 1359 | 1317 | 1347 | 1326 | 1225 | 1176 | 1505 | 1154 | 1324 | 1240 | 1202 | 1236 | 1262 | 1202 | 1201 | 1223 | 1243 | 1220 | 1261 | 1340 | 1242 | 1241 | 1271 | 1195 | 1257 | 1430 | 1417 | 1335 | 1384 | 1390 | 1273 | 1405 | 1363 | 1247 | 1402 | 1363 | 1463 | 1364 | 1357 | 1378 | 1195 | 1237 | 1244 | 1255 | 1204 | 1124 | 1259 | 1294 | 1436 | 1445 | 1242 | 1230 | 1347 | 1261 | 1271 | 1270 | 1263 | 1212 | 1179 | 1264 | 1251 | 1229 | 1222 | 1295 | 1210 | 1284 | 1223 | 1226 | 1224 | 1235 | 1235 | 1254 | 1148 | 1297 | 1260 | 1284 | 1266 | 1430 | 1062 | 1477 | 1393 | 1271 | 1402 | 1284 | 1331 | 1365 | 1403 | 1203 | 1248 | 1380 | 1280 | 1337 | 1237 | 1274 | 1368 | 1297 | 1261 | 1279 | 1468 | 1167 | 1198 | 1397 | 1399 | 1329 | 1343 | 1297 | 1113 | 1421 | 1357 | 1373 | 1327 | 1284 | 1281 | 1240 | 1284 | 1266 | 1405 | 1206 | 1368 | 1256 | 1156 | 1343 | 1374 | 1375 | 1258 | 1400 | 1260 | 1239 | 1224 | 1068 | 1204 | 1198 | 1199 | 1369 | 1187 | 1292 | 1323 | 1263 | 1210 | 1155 | 1326 | 1207 | 1107 | 1190 | 1179 | 1170 | 1234 | 1371 | 1199 | 1216 | 1090 | 1385 | 1228 | 1247 | 1276 | 1315 | 1312 | 1258 | 1360 | 1267 | 1269 | 1235 | 1102 | 1180 | 1146 | 1021 | 1168 | 1218 | 1107 | 1033 | 1241 |  |  | 1233 | 875 | 1184 |  | 1297 | 1118 | 1186 | 1176 | 1170 | 1212 | 1227 | 1234 | 1229 | 1244 | 1253 | 1258 | 1217 | 1424 | 1103 | 1014 | 963 | 896 | 998 | 1056 | 1240 | 1417 | 1249 | 1302 | 1263 | 1298 | 1319 | 1270 | 1012 | 1176 | 1032 | 1178 | 948 |  | 1175 | 1263 | 551 | 1173 | 1127 |  |  | 1098 | 1235 | 1264 | 1200 | 1063 | 35.61 | 47.4 | 1.3 | 5.1 |  | 0 | 5.95 |  |  | 82415821.321 | 281510.713 | 55532508.045 | 61284.336 | 83203137.502 | 185982.206 | 60226428.183 | 55288.399 | 312495765.901 | 82799.368 | 80621.321 | 13.713 | 78364.045 | 9.336 | 80748.502 | 38.206 | 60967.183 | 12.399 | 300377.401 | 57.568 | 158962.317 | 300319.833 | 12 | 0 | 5.95 | 35.61 | 47.4 | 1.3 | 5.1 | 305558
2025-04-19 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1318 | 1344 | 1246 | 1236 | 1328 | 1232 | 1209 | 1219 | 1244 | 1234 | 1237 | 1246 | 1226 | 1079 | 1188 | 1224 | 1175 | 1190 | 1128 | 1322 | 1250 | 1197 | 1375 | 1280 | 1303 | 1307 | 1298 | 1331 | 1283 | 1315 | 1363 | 1193 | 1162 | 1476 | 1131 | 1313 | 1212 | 1173 | 1205 | 1230 | 1170 | 1168 | 1190 | 1210 | 1185 | 1259 | 1325 | 1212 | 1189 | 1217 | 1160 | 1220 | 1392 | 1379 | 1316 | 1314 | 1363 | 1221 | 1367 | 1328 | 1188 | 1349 | 1400 | 1461 | 13143 | 1337 | 1356 | 1163 | 1227 | 1234 | 1245 | 1202 | 1082 | 1218 | 1256 | 1398 | 1407 | 1208 | 1192 | 1331 | 1228 | 1237 | 1209 | 1211 | 1178 | 1182 | 1264 | 1252 | 1225 | 1220 | 1271 | 1256 | 1277 | 1247 | 1268 | 1201 | 1200 | 1225 | 1222 | 1135 | 1271 | 1228 | 1252 | 1231 | 1398 | 1054 | 1446 | 1373 | 1254 | 1371 | 1278 | 1330 | 1382 | 1379 | 1201 | 1252 | 1367 | 1312 | 1319 | 1225 | 1246 | 1338 | 1280 | 1232 | 1293 | 1498 | 1167 | 1197 | 1400 | 1388 | 1325 | 1331 | 1284 | 1103 | 1399 | 1324 | 1338 | 1267 | 1283 | 1272 | 1230 | 1270 | 1255 | 1397 | 1197 | 1353 | 1229 | 1133 | 1310 | 1344 | 1341 | 1230 | 1368 | 1226 | 1206 | 1193 | 1100 | 1169 | 1106 | 1172 | 1338 | 1160 | 1257 | 1292 | 1166 | 1143 | 1126 | 1294 | 1179 | 1080 | 1162 | 1161 | 1142 | 1203 | 1413 | 1227 | 1221 | 1101 | 1369 | 1242 | 1204 | 1237 | 1282 | 1357 | 1287 | 1377 | 1283 | 1301 | 1202 | 1076 | 1156 | 1126 | 1011 | 1142 | 1195 | 1083 | 1014 | 1214 |  |  | 1098 | 858 | 1162 |  | 1297 | 1091 | 1186 | 1184 | 1162 | 1230 | 1227 | 1246 | 1233 | 1263 | 1221 | 1232 | 1207 | 1389 | 1080 | 1063 | 998 | 898 | 889 | 1040 | 1238 | 1390 | 1228 | 1277 | 1268 | 1310 | 1309 | 1251 | 1001 | 1156 | 1014 | 1157 | 929 |  | 1175 | 1241 | 604 | 1156 | 1108 |  |  | 1110 | 1278 | 1263 | 1210 | 1063 | 35.4 | 46.4 | 1.2 | 5.3 |  | 0 | 5.87 |  |  | 82494845 | 281530 | 55609764 | 61302 | 83282860 | 186033 | 60286490 | 55303 | 312791511.1 | 82871.8 | 79023.679 | 19.287 | 77255.955 | 17.664 | 79722.498 | 50.794 | 60061.817 | 14.601 | 295745.199 | 72.432 | 156242.683 | 295672.767 | 12 | 0 | 5.87 | 35.4 | 46.4 | 1.2 | 5.3 | 312642
2025-04-20 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1466 | 1477 | 1357 | 1354 | 1446 | 1337 | 1345 | 1357 | 1374 | 1381 | 1364 | 1378 | 1363 | 1213 | 1306 | 1342 | 1280 | 1309 | 1474 | 1466 | 1374 | 1303 | 1488 | 1404 | 1468 | 1447 | 1441 | 1457 | 1390 | 1423 | 1402 | 1294 | 1261 | 1602 | 1230 | 1426 | 1317 | 1277 | 1310 | 1336 | 1271 | 1273 | 1294 | 1316 | 1286 | 1374 | 1440 | 1315 | 1319 | 1352 | 1273 | 1339 | 1519 | 1506 | 1435 | 1467 | 1503 | 1334 | 1488 | 1443 | 1288 | 1460 | 1463 | 1498 | 1459 | 1454 | 1069 | 1194 | 1318 | 1334 | 1355 | 1250 | 1385 | 1356 | 1556 | 1537 | 1553 | 1338 | 1329 | 1412 | 1354 | 1373 | 1365 | 1370 | 1280 | 1213 | 1385 | 1371 | 1333 | 1295 | 1365 | 1298 | 1398 | 1388 | 1302 | 1299 | 1320 | 1282 | 1322 | 1168 | 1371 | 1329 | 1358 | 1336 | 1508 | 1071 | 1568 | 1480 | 1363 | 1486 | 1329 | 1435 | 1450 | 1515 | 1253 | 1357 | 1486 | 1483 | 1391 | 1334 | 1351 | 1436 | 1334 | 1335 | 1354 | 1563 | 1275 | 1299 | 1515 | 1512 | 1443 | 1445 | 1390 | 1194 | 1522 | 1436 | 1455 | 1374 | 1405 | 1391 | 1335 | 1389 | 1376 | 1523 | 1317 | 1486 | 1376 | 1270 | 1450 | 1475 | 1485 | 1358 | 1485 | 1336 | 1314 | 1313 | 1278 | 1296 | 1213 | 1279 | 1451 | 1260 | 1366 | 1402 | 1266 | 1256 | 1255 | 1437 | 1319 | 1221 | 1300 | 1295 | 1277 | 1358 | 1545 | 1348 | 1355 | 1218 | 1503 | 1370 | 1307 | 1370 | 1396 | 1477 | 1412 | 1500 | 1417 | 1429 | 1362 | 1222 | 1266 | 1224 | 1139 | 1307 | 1354 | 1233 | 1117 | 1368 |  |  | 1197 | 932 | 1280 |  | 1388 | 1189 | 1327 | 1304 | 1267 | 1350 | 1361 | 1350 | 1362 | 1383 | 1263 | 1210 | 1244 | 1534 | 1171 | 1077 | 1010 | 963 | 965 | 1134 | 1355 | 1509 | 1330 | 1383 | 1310 | 1398 | 1362 | 1349 | 1086 | 1256 | 1101 | 1256 | 1007 |  | 1175 | 1348 | 660 | 1249 | 1199 |  |  | 1202 | 1212 | 1280 | 1298 | 1096 | 35.9 | 47.6 | 1.6 | 5.1 |  | 0 | 6.7 |  |  | 82581398.495 | 281543.717 | 55693455.236 | 61311.454 | 83370328.118 | 186091.183 | 60351293.025 | 55314.633 | 313113666.068 | 82927.647 | 86553.495 | 13.717 | 83691.236 | 9.454 | 87468.118 | 58.183 | 64803.025 | 11.633 | 322154.968 | 55.847 | 170221.56 | 322099.121 | 12 | 0 | 6.7 | 35.9 | 47.6 | 1.6 | 5.1 | 327345
2025-04-21 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1450 | 1498 | 1344 | 1338 | 1447 | 1326 | 1369 | 1367 | 1393 | 1398 | 1360 | 1376 | 1359 | 1219 | 1302 | 1337 | 1266 | 1297 | 1464 | 1458 | 1361 | 1295 | 1475 | 1400 | 1460 | 1438 | 1431 | 1461 | 1431 | 1460 | 1450 | 1450 | 1400 | 1650 | 1400 | 1441 | 1302 | 1263 | 1292 | 1320 | 1300 | 1405 | 1276 | 1297 | 1287 | 1376 | 1445 | 1400 | 1409 | 1410 | 1300 | 1289 | 1466 | 1452 | 1450 | 1391 | 1452 | 1271 | 1413 | 1374 | 1224 | 1388 | 1490 | 1510 | 1454 | 1448 | 1467 | 1205 | 1327 | 1351 | 1361 | 1259 | 1390 | 1362 | 1557 | 1535 | 1549 | 1329 | 1318 | 1404 | 1344 | 1363 | 1349 | 1355 | 1282 | 1214 | 1395 | 1391 | 1344 | 1301 | 1368 | 1397 | 1385 | 1384 | 1310 | 1291 | 1302 | 1278 | 1304 | 1150 | 1355 | 1312 | 1342 | 1320 | 1490 | 1098 | 1555 | 1470 | 1346 | 1475 | 1324 | 1426 | 1448 | 1500 | 1250 | 1342 | 1468 | 1463 | 1384 | 1317 | 1334 | 1422 | 1329 | 1318 | 1337 | 1426 | 1257 | 1280 | 1495 | 1489 | 1422 | 1428 | 1384 | 1200 | 1529 | 1436 | 1468 | 1386 | 1378 | 1373 | 1332 | 1379 | 1350 | 1502 | 1295 | 1516 | 1355 | 1252 | 1449 | 1456 | 1477 | 1362 | 1465 | 1360 | 1337 | 1320 | 1325 | 1282 | 1246 | 1314 | 1503 | 1303 | 1443 | 1445 | 1317 | 1270 | 1263 | 1447 | 1322 | 1218 | 1302 | 1292 | 1281 | 1356 | 1528 | 1333 | 1341 | 1203 | 1486 | 1355 | 1292 | 1358 | 1428 | 1462 | 1396 | 1502 | 1401 | 1412 | 1354 | 1218 | 1250 | 1213 | 1132 | 1300 | 1339 | 1203 | 1121 | 1357 |  |  | 1181 | 921 | 1272 |  | 1394 | 1242 | 1311 | 1290 | 1259 | 1334 | 1343 | 1339 | 1343 | 1368 | 1369 | 1356 | 1235 | 1542 | 1156 | 1061 | 1062 | 998 | 952 | 1116 | 1337 | 1489 | 1317 | 1369 | 1362 | 1400 | 1398 | 1380 | 1090 | 1300 | 1150 | 1303 | 1100 |  | 1250 | 1360 | 668 | 1298 | 1283 |  |  | 1210 | 1412 | 1300 | 1310 | 1117 | 37.4 | 47.37 | 2.08 | 5.4 |  | 0 | 6.75 |  |  | 82666836.801 | 281560.312 | 55776650.679 | 61327.538 | 83457790.293 | 186135.647 | 60416203.414 | 55328.08 | 313434297.117 | 82986.708 | 85438.306 | 16.595 | 83195.443 | 16.084 | 87462.175 | 44.464 | 64910.389 | 13.447 | 320631.049 | 59.061 | 168601.07 | 320571.988 | 12 | 0 | 6.75 | 37.4 | 47.37 | 2.08 | 5.4 | 328589
2025-04-22 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1563 | 1564 | 1437 | 1432 | 1551 | 1422 | 1464 | 1462 | 1483 | 1494 | 1492 | 1488 | 1466 | 1316 | 1397 | 1423 | 1308 | 1339 | 1506 | 1502 | 1405 | 1357 | 1539 | 1455 | 1507 | 1484 | 1478 | 1509 | 1504 | 1528 | 1498 | 1398 | 1324 | 1681 | 1347 | 1551 | 1387 | 1352 | 1403 | 1433 | 1340 | 1347 | 1387 | 1409 | 1412 | 1470 | 1577 | 1427 | 1382 | 1421 | 1335 | 1409 | 1603 | 1586 | 1479 | 1525 | 1575 | 1376 | 1529 | 1484 | 1325 | 1428 | 1510 | 1580 | 1580 | 1571 | 1590 | 1261 | 1413 | 1422 | 1464 | 1326 | 1479 | 1434 | 1638 | 1611 | 1635 | 1406 | 1398 | 1467 | 1427 | 1448 | 1424 | 1414 | 1423 | 1339 | 1488 | 1475 | 1448 | 1379 | 1478 | 1400 | 1483 | 1475 | 1378 | 1353 | 1386 | 1339 | 1379 | 1419 | 1431 | 1398 | 1429 | 1406 | 1565 | 1424 | 1638 | 1566 | 1436 | 1561 | 1384 | 1506 | 1522 | 1594 | 1310 | 1423 | 1552 | 1593 | 1446 | 1443 | 1476 | 1520 | 1408 | 1447 | 1438 | 1463 | 1354 | 1390 | 1614 | 1622 | 1549 | 1561 | 1510 | 1296 | 1652 | 1548 | 1486 | 1492 | 1470 | 1462 | 1448 | 1479 | 1399 | 1605 | 1391 | 1625 | 1600 | 1341 | 1543 | 1556 | 1576 | 1451 | 1557 | 1447 | 1426 | 1407 | 1363 | 1304 | 1343 | 1408 | 1618 | 1401 | 1554 | 1559 | 1412 | 1346 | 1347 | 1538 | 1405 | 1297 | 1386 | 1373 | 1357 | 1444 | 1628 | 1429 | 1428 | 1281 | 1585 | 1442 | 1378 | 1442 | 1547 | 1556 | 1479 | 1606 | 1493 | 1505 | 1441 | 1296 | 1332 | 1286 | 1198 | 1385 | 1428 | 1262 | 1181 | 1452 |  |  | 1266 | 982 | 1354 |  | 1561 | 1363 | 1396 | 1370 | 1323 | 1418 | 1431 | 1410 | 1432 | 1451 | 1461 | 1450 | 1572 | 1627 | 1232 | 1133 | 1100 | 1010 | 1019 | 1189 | 1427 | 1582 | 1399 | 1452 | 1410 | 1462 | 1421 | 1414 | 1141 | 1319 | 1156 | 1318 | 1052 |  | 1175 | 1414 | 700 | 1313 | 1257 |  |  | 1278 | 1400 | 1335 | 1320 | 1149 | 37.9 | 46.08 | 1.93 | 5.1 |  | 0 | 7.08 |  |  | 82757675.466 | 281573.49 | 55865708.265 | 61336.975 | 83551224.232 | 186178.147 | 60485503.243 | 55339.845 | 313776481.848 | 83040.583 | 90838.665 | 13.178 | 89057.586 | 9.437 | 93433.939 | 42.5 | 69299.829 | 11.765 | 342184.731 | 53.875 | 179873.636 | 342130.856 | 12 | 0 | 7.08 | 37.9 | 46.08 | 1.93 | 5.1 | 347261
2025-04-23 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1634 | 1639 | 1516 | 1505 | 1633 | 1507 | 1518 | 1519 | 1486 | 1560 | 1548 | 1539 | 1517 | 1362 | 1440 | 1467 | 1357 | 1368 | 1535 | 1529 | 1433 | 1385 | 1574 | 1482 | 1534 | 1512 | 1507 | 1504 | 1529 | 1557 | 1560 | 1425 | 1383 | 1730 | 1424 | 1614 | 1481 | 1434 | 1460 | 1494 | 1424 | 1423 | 1443 | 1463 | 1458 | 1524 | 1623 | 1483 | 1435 | 1476 | 1387 | 1461 | 1664 | 1646 | 1574 | 1612 | 1652 | 1426 | 1601 | 1540 | 1431 | 808 | 1570 | 1560 | 1623 | 1616 | 1634 | 1278 | 1448 | 1440 | 1524 | 1354 | 1526 | 1468 | 1662 | 1637 | 1668 | 1434 | 1434 | 1498 | 1474 | 1484 | 1476 | 1482 | 1462 | 1518 | 1548 | 1536 | 1506 | 1420 | 1518 | 852 | 1526 | 1522 | 1392 | 1380 | 1445 | 1374 | 1467 | 1475 | 1474 | 1478 | 1511 | 1491 | 1614 | 1520 | 1670 | 1602 | 1478 | 1644 | 1440 | 1540 | 1554 | 1631 | 1336 | 1451 | 1586 | 1656 | 1488 | 1495 | 1533 | 1558 | 1441 | 1517 | 1528 | 1489 | 1402 | 1439 | 1671 | 1678 | 1600 | 1605 | 1543 | 1329 | 1682 | 1585 | 1621 | 1524 | 1501 | 1501 | 1483 | 1526 | 1424 | 1651 | 1393 | 1673 | 1561 | 1408 | 1614 | 1641 | 1640 | 1516 | 1615 | 1508 | 1487 | 1467 | 1430 | 1400 | 1395 | 1455 | 1671 | 1438 | 1592 | 1600 | 1445 | 1376 | 1415 | 1571 | 1486 | 1358 | 1457 | 1440 | 1388 | 1511 | 1673 | 1459 | 1467 | 1314 | 1627 | 1461 | 1416 | 1477 | 1643 | 1682 | 1526 | 1668 | 1536 | 1547 | 1509 | 1340 | 1424 | 1389 | 1234 | 1445 | 1481 | 1301 | 1210 | 1489 |  |  | 1303 | 1009 | 1400 |  | 1606 | 1405 | 1308 | 1339 | 1506 | 1502 | 1405 | 1358 | 1540 | 1416 | 1432 | 1461 | 1461 | 1450 | 1627 | 1233 | 1134 | 1111 | 1011 | 1189 | 1337 | 1478 | 1378 | 1410 | 1428 | 1463 | 1232 | 1310 | 1067 | 1232 | 1081 | 1234 | 998 |  | 1175 | 1445 | 699 | 1343 | 1284 |  |  | 1210 | 1310 | 1380 | 1298 | 1175 | 38 | 46.1 | 2 | 5.3 |  | 0 | 7.22 |  |  | 82851348.837 | 281586.673 | 55957678.329 | 61345.996 | 83647713.106 | 186202.292 | 60554920.387 | 55352.806 | 314127642.011 | 83095.409 | 93673.371 | 13.183 | 91970.064 | 9.021 | 96488.874 | 24.145 | 69417.144 | 12.961 | 351160.163 | 54.826 | 185621.231 | 351105.337 | 12 | 0 | 7.22 | 38 | 46.1 | 2 | 5.3 | 355743
2025-04-24 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1619 | 1624 | 1501 | 1492 | 1608 | 1487 | 1482 | 1482 | 1453 | 1527 | 1514 | 1502 | 1484 | 1328 | 1433 | 1477 | 1432 | 1435 | 1605 | 1575 | 1490 | 1438 | 1641 | 1538 | 1575 | 1545 | 1533 | 1506 | 1552 | 1579 | 1580 | 1445 | 1374 | 1712 | 1418 | 1616 | 1470 | 1408 | 1427 | 1459 | 1399 | 1394 | 1415 | 1429 | 1448 | 1515 | 1604 | 1455 | 1224 | 1256 | 1187 | 1252 | 1426 | 1414 | 1346 | 1381 | 1402 | 1220 | 1411 | 1370 | 1226 | 1112 | 1595 | 1563 | 1594 | 1587 | 1603 | 1251 | 1418 | 1419 | 1491 | 1311 | 1512 | 1436 | 1648 | 1622 | 1653 | 1414 | 1421 | 1452 | 1470 | 1476 | 1471 | 1487 | 1452 | 1509 | 1518 | 1505 | 1476 | 1377 | 1474 | 755 | 1508 | 1515 | 1395 | 1325 | 1422 | 1321 | 1461 | 1486 | 1463 | 1475 | 1505 | 1482 | 1589 | 1493 | 1638 | 1611 | 1498 | 1578 | 1394 | 1501 | 1509 | 1623 | 1306 | 1430 | 1580 | 1613 | 1440 | 1456 | 1497 | 1515 | 1390 | 1478 | 1492 | 1492 | 1377 | 1406 | 1631 | 1639 | 1567 | 1571 | 1525 | 1322 | 1680 | 1568 | 1612 | 1515 | 1513 | 1500 | 1465 | 1501 | 1436 | 1658 | 1386 | 1671 | 1483 | 1376 | 1587 | 1654 | 1608 | 1491 | 1631 | 1486 | 1447 | 1472 | 1389 | 1404 | 1366 | 1424 | 1636 | 1408 | 1557 | 1567 | 1413 | 1343 | 1388 | 1534 | 1452 | 1334 | 1432 | 1418 | 1354 | 1480 | 1671 | 1462 | 1482 | 1324 | 1671 | 1488 | 1449 | 1491 | 1606 | 1650 | 1527 | 1644 | 1543 | 1551 | 1489 | 1342 | 1413 | 1379 | 1229 | 1423 | 1472 | 1274 | 1184 | 1479 |  |  | 1279 | 992 | 1369 |  | 1573 | 1371 | 1448 | 1342 | 1334 | 1416 | 1459 | 1401 | 1453 | 1452 | 1468 | 1453 | 1574 | 1625 | 1430 | 1139 | 1139 | 1114 | 1008 | 1175 | 1405 | 1564 | 1377 | 1435 | 1434 | 1467 | 1538 | 1392 | 1127 | 1302 | 1141 | 1304 | 1441 |  | 1175 | 1449 | 621 | 1315 | 1263 |  |  | 1278 | 1353 | 1260 | 1152 | 1182 | 36.5 | 45.1 | 2.47 | 8.3 |  | 0 | 7.18 |  |  | 82942719.164 | 281600.438 | 56048174.186 | 61355.935 | 83743255.547 | 186244.522 | 60624877.611 | 55365.967 | 314474585.976 | 83153.541 | 91370.327 | 13.765 | 90495.857 | 9.939 | 95542.441 | 42.23 | 69957.224 | 13.161 | 346943.965 | 58.132 | 181842.48 | 346885.833 | 12 | 0 | 7.18 | 36.5 | 45.1 | 2.47 | 8.3 | 351420
2025-04-25 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1522 | 1531 | 1418 | 1410 | 1520 | 1408 | 1398 | 1398 | 1371 | 1443 | 1433 | 1420 | 1399 | 1254 | 1354 | 1398 | 1178 | 1179 | 1330 | 1312 | 1226 | 1191 | 1354 | 1282 | 1325 | 1308 | 1302 | 1282 | 1293 | 1319 | 1584 | 1208 | 1287 | 1621 | 1343 | 1420 | 1391 | 1331 | 1352 | 1379 | 1343 | 1333 | 1361 | 1371 | 1395 | 1438 | 1534 | 1398 | 1347 | 1397 | 1321 | 1390 | 1578 | 1563 | 1475 | 1519 | 1535 | 1333 | 1553 | 1508 | 1340 | 1115 | 1592 | 1573 | 1508 | 1500 | 1517 | 1183 | 1348 | 1342 | 1413 | 1260 | 1443 | 1364 | 1573 | 1549 | 1579 | 1356 | 1361 | 1391 | 1402 | 1404 | 1401 | 1415 | 1400 | 1433 | 1451 | 1438 | 1409 | 1292 | 1312 | 1000 | 1533 | 1443 | 1396 | 1355 | 1365 | 1408 | 1377 | 1401 | 1437 | 1390 | 1417 | 1394 | 1540 | 1404 | 1541 | 1520 | 1417 | 1504 | 1508 | 1453 | 1469 | 1559 | 1408 | 1383 | 1517 | 1539 | 1512 | 1392 | 1422 | 1428 | 1513 | 1401 | 1405 | 1489 | 1319 | 1347 | 1563 | 1570 | 1508 | 1517 | 1472 | 1262 | 1597 | 1490 | 1531 | 1437 | 1439 | 1420 | 1408 | 1415 | 1358 | 1561 | 1306 | 1574 | 1435 | 1296 | 1494 | 1510 | 1512 | 1403 | 1535 | 1400 | 1382 | 1374 | 1392 | 1335 | 1280 | 1339 | 1533 | 1324 | 1459 | 1468 | 1408 | 1267 | 1307 | 1446 | 1370 | 1258 | 1353 | 1339 | 1280 | 1393 | 1610 | 1402 | 1410 | 1266 | 1595 | 1424 | 1380 | 1420 | 1506 | 1568 | 1466 | 1570 | 1476 | 1482 | 1408 | 1310 | 1335 | 1303 | 1203 | 1343 | 1429 | 1257 | 1170 | 1410 |  |  | 1231 | 934 | 1290 |  | 1488 | 1296 | 1379 | 1327 | 1382 | 1378 | 1390 | 1395 | 1398 | 1394 | 1389 | 1440 | 1493 | 1550 | 1364 | 1163 | 1132 | 1107 | 929 | 1084 | 1297 | 1441 | 1270 | 1319 | 1421 | 1455 | 1416 | 1285 | 1035 | 1199 | 1049 | 1202 | 956 |  | 1175 | 1433 | 581 | 1237 | 1188 |  |  | 1271 | 1347 | 1188 | 1152 | 1039 | 37.08 | 47.02 | 1.4 | 6.5 |  | 0 | 7.1 |  |  | 83028954.272 | 281612.677 | 56135133.047 | 61364.572 | 83833891.496 | 186312.499 | 60691066.882 | 55377.348 | 314804205.234 | 83205.261 | 86235.108 | 12.239 | 86958.861 | 8.637 | 90635.949 | 67.977 | 66189.271 | 11.381 | 329619.258 | 51.72 | 173173.093 | 329567.538 | 12 | 0 | 7.1 | 37.08 | 47.02 | 1.4 | 6.5 | 335649
2025-04-26 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1168 | 1144 | 1091 | 1079 | 1169 | 1088 | 1086 | 1088 | 1071 | 1133 | 1116 | 1104 | 1086 | 1060 | 1039 | 1071 | 1038 | 1036 | 1174 | 1155 | 1079 | 1053 | 1195 | 1133 | 1166 | 1155 | 1151 | 1162 | 1158 | 1180 | 1076 | 1089 | 1081 | 1243 | 1037 | 1091 | 1087 | 1044 | 1057 | 1077 | 1044 | 1029 | 1049 | 1056 | 1070 | 1092 | 1173 | 1071 | 1071 | 1099 | 1047 | 1088 | 1240 | 1226 | 1168 | 1203 | 1228 | 1095 | 1227 | 1191 | 1080 | 1206 | 1083 | 1204 | 1175 | 1170 | 1184 | 974 | 1055 | 1030 | 1084 | 1042 | 1102 | 1062 | 1211 | 1198 | 1214 | 1048 | 1056 | 1104 | 1074 | 1077 | 1077 | 1085 | 1068 | 1083 | 1103 | 1090 | 1088 | 1082 | 1116 | 1131 | 1103 | 1097 | 1134 | 1052 | 1053 | 1069 | 1046 | 1064 | 1092 | 1058 | 1078 | 1068 | 1196 | 1100 | 1189 | 1170 | 1077 | 1197 | 1187 | 1136 | 1160 | 1200 | 1068 | 1074 | 1169 | 1216 | 1209 | 1082 | 1101 | 1127 | 1183 | 1090 | 1105 | 1196 | 1017 | 1037 | 1199 | 1199 | 1153 | 1156 | 1131 | 966 | 1223 | 1142 | 1170 | 1101 | 1102 | 1093 | 1077 | 1088 | 1033 | 1193 | 1002 | 1198 | 1073 | 998 | 1161 | 1174 | 1177 | 1084 | 1174 | 1084 | 1067 | 1055 | 1054 | 1022 | 1083 | 1039 | 1195 | 1027 | 1125 | 1141 | 1110 | 985 | 1016 | 1122 | 1060 | 977 | 1053 | 1034 | 1001 | 1078 | 1241 | 1079 | 1088 | 1089 | 1233 | 1102 | 1067 | 1106 | 1163 | 1208 | 1133 | 1216 | 1139 | 1140 | 1097 | 1101 | 1019 | 1011 | 1113 | 1025 | 1082 | 1130 | 1060 | 1083 |  |  | 1050 | 768 | 1013 |  | 1137 | 1011 | 1054 | 1020 | 1053 | 1065 | 1056 | 1073 | 1084 | 1105 | 1086 | 1114 | 1166 | 1219 | 1035 | 1113 | 1050 | 1060 | 914 | 1008 | 1029 | 1153 | 1026 | 1055 | 1021 | 1089 | 1130 | 1038 | 835 | 957 | 842 | 959 | 758 |  | 1175 | 1163 | 588 | 1200 | 1050 |  |  | 1011 | 1100 | 1080 | 1157 | 981 | 36.9 | 43.37 | 1.8 | 9.9 |  | 0 | 5.34 |  |  | 83099811.757 | 281622.638 | 56203507.306 | 61372.195 | 83904016.468 | 186328.13 | 60742671.538 | 55387.237 | 315064821.334 | 83247.126 | 70857.485 | 9.961 | 68374.259 | 7.623 | 70124.972 | 15.631 | 51604.656 | 9.889 | 260616.1 | 41.865 | 139214.16 | 260574.235 | 12 | 0 | 5.34 | 36.9 | 43.37 | 1.8 | 9.9 | 266123
2025-04-27 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1233 | 1194 | 1147 | 1136 | 1228 | 1137 | 1142 | 1133 | 1126 | 1192 | 1170 | 1150 | 1136 | 1125 | 1192 | 1170 | 1082 | 1094 | 1226 | 1150 | 1146 | 1262 | 1187 | 1232 | 1225 | 1232 | 1214 | 1262 | 1234 | 1206 | 1235 | 1213 | 975 | 1048 | 930 | 1069 | 1069 | 1027 | 1054 | 1074 | 1022 | 1011 | 1045 | 1050 | 1053 | 1078 | 1172 | 1071 | 1068 | 1068 | 1093 | 1041 | 1080 | 1236 | 1225 | 1162 | 1180 | 1228 | 1094 | 1213 | 1178 | 1070 | 1192 | 1213 | 1205 | 1199 | 1219 | 1088 | 1096 | 1055 | 1127 | 1129 | 1143 | 1100 | 1273 | 1254 | 1276 | 1102 | 1099 | 1158 | 1128 | 1134 | 1119 | 1086 | 1112 | 1134 | 1151 | 1139 | 1136 | 1130 | 1159 | 1241 | 1145 | 1160 | 1206 | 1086 | 1091 | 1121 | 1111 | 1111 | 1141 | 1122 | 1137 | 1113 | 1273 | 1133 | 1276 | 1220 | 1127 | 1221 | 1205 | 1170 | 1227 | 1248 | 1131 | 1111 | 1209 | 1225 | 1224 | 1106 | 1124 | 1149 | 1196 | 1115 | 1133 | 1187 | 1056 | 1073 | 1249 | 1246 | 1196 | 1201 | 1169 | 1005 | 1257 | 1192 | 1218 | 1160 | 1162 | 1151 | 1115 | 1153 | 1086 | 1258 | 1052 | 1262 | 1125 | 1043 | 1204 | 1224 | 1226 | 1123 | 1214 | 1121 | 1104 | 1092 | 1057 | 1081 | 1026 | 1078 | 1237 | 1065 | 1170 | 1182 | 1160 | 1021 | 1060 | 1165 | 1125 | 1026 | 1113 | 1086 | 1032 | 1125 | 1177 | 1277 | 1113 | 1008 | 1275 | 1139 | 1100 | 1140 | 1208 | 1252 | 1167 | 1255 | 1175 | 1170 | 1138 | 1028 | 1031 | 1011 | 1103 | 1133 | 1095 | 982 | 956 | 1106 |  |  | 997 | 765 | 1027 |  | 1171 | 1018 | 1076 | 1042 | 1078 | 1091 | 1086 | 1100 | 1112 | 1126 | 1136 | 1134 | 1183 | 1206 | 1255 | 1069 | 903 | 1052 | 760 | 912 | 1050 | 1151 | 1050 | 1061 | 1133 | 1092 | 1140 | 1083 | 950 | 1103 | 930 | 1010 | 965 |  | 1172 | 1170 | 931 | 1204 | 1032 |  |  | 1056 | 1032 | 1078 | 1153 | 1103 | 38 | 45.8 | 1.9 | 6.1 |  | 0 | 5.5 |  |  | 83171848.185 | 281686.886 | 56274614.128 | 61382.252 | 83976924.049 | 186398.997 | 60795693.149 | 55399.988 | 315333493.718 | 83305.997 | 72036.428 | 64.248 | 71106.822 | 10.057 | 72907.581 | 70.867 | 53021.611 | 12.751 | 268672.384 | 58.871 | 143068.945 | 268613.513 | 12 | 0 | 5.5 | 38 | 45.8 | 1.9 | 6.1 | 274076
2025-04-28 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1375.6 | 1331.9 |  | 1267.5 | 1366.8 | 1266.4 | 1274 | 1261.9 | 1255.4 | 1325.2 | 1314 | 1280.1 | 1260.3 | 1179.1 | 1207.8 | 1246.7 | 1208.7 | 1222.7 | 1364 | 1373.6 | 1286.6 | 1292.1 | 1403.3 | 1340.3 | 1382.2 | 1364.7 | 1361.8 | 1400.7 | 1344.6 | 1378.4 | 1239.3 | 1259.8 | 1154.4 | 1456.1 | 1099.5 | 1263.6 | 1258.1 | 1200.2 | 1264.1 | 1277.8 | 1210.7 | 1222.4 | 1262.5 | 1254.9 | 1249.1 | 1273.8 | 1386.9 | 1270.6 | 1258.1 | 1287.1 | 1222.1 | 1269.6 | 1401.5 | 1440.5 | 1367.4 | 1385.9 | 1442.9 | 1295.4 | 1421.2 | 1377.5 | 1261.4 | 1398 | 1265.7 | 1132.1 | 1370.1 | 1363.1 | 1386.9 | 1216.6 | 1251 | 1201.1 | 1267.4 | 1266.5 | 1284.2 | 1267.1 | 1471.6 | 1450.4 | 1459.5 | 1253.7 | 1242.1 | 1337.1 | 1270.1 | 1279.5 | 1265.2 | 1225.3 | 1252.5 | 1270.1 | 1289.3 | 1275.4 | 1272.8 | 1268 | 1323.4 | 1375 | 1296 | 1291.7 | 1328.4 | 1217.8 | 1235.5 | 1266.1 | 1255.9 | 1258.6 | 1291.2 | 1267.7 | 1287.9 | 1260.9 | 1405.5 | 1282.3 | 1385.6 | 1409.7 | 1286.1 | 1403.7 | 1373.7 | 1374.1 | 1421.3 | 1443.1 | 1284.1 | 1293.4 | 1405.1 | 1406.2 | 1401.9 | 1248.1 | 1281.5 | 1326.1 | 1364.2 | 1264.9 | 1282.2 | 1386.5 | 1179.3 | 1202.7 | 1400 | 1399.8 | 1343.1 | 1350.2 | 1306.9 | 1138 | 1440 | 1371.1 | 1387.3 | 1311.5 | 1306.5 | 1288.3 | 1247.4 | 1292.3 | 1223.2 | 1411.5 | 1183.6 | 1417.6 | 1264.1 | 1171.9 | 1353.6 | 1372.9 | 1378.7 | 1267 | 1369.3 | 1307 | 1246.5 | 1230.7 | 1235.5 | 1213.2 | 1147.1 | 1203.1 | 1378.6 | 1189.4 | 1309.9 | 1317.6 | 1279 | 1135.2 | 1187.9 | 1295.1 | 1251.3 | 1141.7 | 1242.5 | 1210.6 | 1149.4 | 1252.3 | 1430.2 | 1248.4 | 1255.6 | 1129.8 | 1427.7 | 1274.2 | 1230.7 | 1271.1 | 1351.6 | 1397.8 | 1309.4 | 1405.5 | 1317 | 1319.4 | 1268.8 | 1145.4 | 1160.7 | 1133.9 | 817 | 1180.2 | 1273.8 | 1122.8 | 1086.4 | 1302.2 |  |  | 1085.6 | 848.4 | 1175.3 |  | 1327.6 | 1157.3 | 1219.3 | 1188.2 | 1224.8 | 1233.6 | 1232.3 | 1244.3 | 1258.9 | 1291.9 | 1291.5 | 1297.9 | 1374.4 | 1438.4 | 1214.6 | 1021.2 | 930.5 | 574.8 | 862.5 | 1005.9 | 1163 | 1308.6 | 1171.9 | 1214.6 | 1224.5 | 1276 | 1307.2 | 1192.9 | 969.7 | 1106.5 | 977.5 | 1112.9 | 1065 |  | 1670.5 | 1313 | 512.6 | 1245 | 1200 |  |  | 1202.9 | 1173.9 | 738.9 | 1112 | 1012 | 38.9724 | 45.8338 | 2.2649 | 5.9 |  | 0 | 6.2 |  |  | 83254910.28 | 281723.886 | 56355236.306 | 61393.252 | 84058696.005 | 186454.997 | 60856040.738 | 55412 | 315638896.479 | 83366.997 | 83062.095 | 37 | 80622.178 | 11 | 81771.956 | 56 | 60347.589 | 12.012 | 305402.761 | 61 | 163636.273 | 305341.761 | 12 | 0 | 6.2 | 38.9724 | 45.8338 | 2.2649 | 5.9 | 306127.9
2025-04-29 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1407 | 1364 | 1308 | 1299 | 1396 | 1295 | 1302 | 1289 | 1283 | 1353 | 1343 | 1311 | 1290 | 1208 | 1234 | 1278 | 1238 | 1306 | 1394 | 1408 | 1318 | 1321 | 1439 | 1369 | 1414 | 1398 | 1394 | 1432 | 1371 | 1411 | 1264 | 1289 | 1177 | 1560 | 1117 | 1288 | 1290 | 1258 | 1293 | 1308 | 1254 | 1251 | 1291 | 1282 | 1301 | 1320 | 1437 | 1300 | 1289 | 1318 | 1255 | 1302 | 1445 | 1490 | 1397 | 1418 | 1475 | 1325 | 1458 | 1409 | 1294 | 1428 | 1299 | 1154 | 1404 | 1396 | 1421 | 1325 | 1281 | 1283 | 1299 | 1298 | 1311 | 1302 | 1504 | 1483 | 1495 | 1299 | 1279 | 1390 | 1331 | 1327 | 1298 | 1307 | 1302 | 1313 | 1322 | 1307 | 1302 | 1299 | 1354 | 1363 | 1329 | 1325 | 1399 | 1239 | 1270 | 1298 | 1290 | 1293 | 1324 | 1301 | 1326 | 1300 | 1447 | 1320 | 1601 | 1444 | 1320 | 1448 | 1410 | 1411 | 1485 | 1479 | 1314 | 1328 | 1440 | 1441 | 1437 | 1284 | 1319 | 1356 | 1401 | 1298 | 1316 | 1425 | 1210 | 1223 | 1428 | 1429 | 1373 | 1379 | 1327 | 1163 | 1471 | 1399 | 1477 | 1337 | 1338 | 1314 | 1267 | 1316 | 1149 | 1447 | 1214 | 1454 | 1290 | 1200 | 1386 | 1406 | 1414 | 1301 | 1486 | 1304 | 1280 | 1262 | 1280 | 1251 | 1173 | 1228 | 1410 | 1215 | 1339 | 1344 | 1293 | 1163 | 1208 | 1319 | 1277 | 1161 | 1262 | 1230 | 1168 | 1277 | 1465 | 1276 | 1286 | 1153 | 1462 | 1304 | 1259 | 1291 | 1383 | 1431 | 1339 | 1439 | 1347 | 1351 | 1292 | 1164 | 1191 | 1154 | 940 | 1209 | 1309 | 1169 | 1113 | 1336 |  |  | 1254 | 872 | 1182 |  | 1330 | 1255 | 1249 | 1214 | 1255 | 1264 | 1266 | 1278 | 1296 | 1326 | 1321 | 1331 | 1405 | 1472 | 1246 | 1040 | 951 | 688 | 894 | 1057 | 1334 | 1368 | 1323 | 1335 | 1230 | 1450 | 1381 | 1264 | 1022 | 1224 | 1031 | 1194 | 1031 |  | 1665 | 1195 | 520 | 1110 | 1142 |  |  | 1097 | 1225 | 798 | 1178 | 1099 | 40 | 46 | 2.1 | 5.1 |  | 0 | 6.38 |  |  | 83340164.309 | 281785 | 56438227.545 | 61405 | 84142145.623 | 186495 | 60919090.96 | 55425 | 315953204.4097 | 83421 | 85254.029 | 61.114 | 82991.239 | 11.748 | 83449.618 | 40.003 | 63050.222 | 13 | 314307.9307 | 54.003 | 168172.406 | 314253.9277 | 12 | 0 | 6.38 | 40 | 46 | 2.1 | 5.1 | 316090
2025-04-30 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1370.1 | 1329.7 | 1272 | 1262.9 | 1358.6 | 1260.8 | 1269.7 | 1256.5 | 1248.5 | 1318.5 | 1307.4 | 1276 | 1257.2 | 1174.6 | 1202 | 1245.6 | 1206.7 | 1273.1 | 1358.5 | 1372.7 | 1285.1 | 1286.5 | 1401 | 1437.3 | 1377.9 | 1359.5 | 1356.9 | 1396 | 1373.5 | 1376.2 | 1236.2 | 1321.7 | 1147.6 | 1524.4 | 1195.9 | 1253.7 | 1258.2 | 1233 | 1259.4 | 1275.4 | 1240.3 | 1227 | 1258.2 | 1248.8 | 1277.8 | 1306.8 | 1409.5 | 1266.1 | 1255.5 | 1283.7 | 1223.3 | 1276.8 | 1430.6 | 1472.1 | 1362.2 | 1168.5 | 1438.9 | 1289.9 | 1420.2 | 1430.4 | 1263.4 | 1393.4 | 1262.7 | 1126.5 | 1367.2 | 1359.2 | 1383.6 | 1270.4 | 1247.3 | 1249.6 | 1265.3 | 1263.7 | 1275.4 | 1266.9 | 1462.6 | 1441.3 | 1454.4 | 1267.1 | 1246.1 | 1350.9 | 1300.6 | 1295.4 | 1261.9 | 1271.6 | 1276.6 | 1302.5 | 1233.8 | 1278 | 1268.7 | 1263 | 1317.4 | 1342.6 | 1294 | 1289.4 | 1377.2 | 1205.9 | 1235.9 | 1264.7 | 1254 | 1257.2 | 1287.4 | 1264.1 | 1289.1 | 1262.8 | 1406.4 | 1281.9 | 1557.6 | 1405.2 | 1282.3 | 1407.4 | 1371.8 | 1371.3 | 1441.7 | 1438.3 | 1279.3 | 1290.8 | 1401.1 | 1403.5 | 1398 | 1249.3 | 1282.8 | 1322.6 | 1365 | 1262.9 | 1280.2 | 1385.9 | 1183.5 | 1195.2 | 1391.4 | 1394.1 | 1341.2 | 1346.8 | 1293.7 | 1133.4 | 1434.5 | 1363.4 | 1382 | 1301.8 | 1305.5 | 1283 | 1236.9 | 1285.4 | 1121.4 | 1411.4 | 1184.3 | 1372.9 | 1262.1 | 1170.8 | 1351.4 | 1372.4 | 1378.7 | 1269.9 | 1449.2 | 1270.6 | 1250.9 | 1230.9 | 1239.5 | 1221.7 | 1144 | 1197.3 | 1374.1 | 1186.7 | 1306.7 | 1310.3 | 1243.5 | 997.1 | 1200.4 | 1334.4 | 1252.2 | 1129.5 | 1237.7 | 1194.8 | 1173.4 | 1243.2 | 1427.4 | 1245.6 | 1256.1 | 1126.4 | 1445.2 | 1274.1 | 1244 | 1261.1 | 1350.8 | 1396.6 | 1307.9 | 1404.2 | 1313.1 | 1317 | 1256.5 | 1131.1 | 1157.1 | 1122.2 | 1101.1 | 1175.6 | 1272.5 | 1233.1 | 1082.5 | 1298.2 |  |  | 1087.1 | 847.8 | 1208.7 |  | 1321.5 | 1149.9 | 1215 | 1181.6 | 1220.6 | 1231.8 | 1232.5 | 1244.2 | 1261.8 | 1292.3 | 1285 | 1295 | 1365.3 | 1431.5 | 1213.7 | 1014.9 | 926 | 717.9 | 850.9 | 1006.8 | 1277.5 | 1392.3 | 1296.6 | 1308.2 | 1315.5 | 1365.5 | 1390.3 | 1312.7 | 976.6 | 1203 | 980.5 | 1152.8 | 1005.7 |  | 1645 | 1282.1 | 521.5 | 1192.2 | 1128 |  |  | 1190.8 | 1166.4 | 794.5 | 1121.6 | 1055.5 | 35.51 | 43.47 | 2.54 | 6.7 |  | 0 | 6.29 |  |  | 83423432.755 | 281823.456 | 56518786.828 | 61413.795 | 84223652.282 | 186538.509 | 60981207.812 | 55435.396 | 316260211.859 | 83464.615 | 83268.446 | 38.456 | 80559.283 | 8.795 | 81506.659 | 43.509 | 62116.852 | 10.396 | 307007.4493 | 43.615 | 163780.478 | 306963.8343 | 12 | 0 | 6.29 | 35.51 | 43.47 | 2.54 | 6.7 | 308834.9
2025-05-01 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 7:00 | 19:00 | 1312.3 | 1273.4 | 1219.5 | 1212.5 | 1304.8 | 1208.9 | 1214.3 | 1201.7 | 1215.7 | 1263 | 1251.2 | 1221.8 | 1201.9 | 1124.6 | 1183.3 | 1231.8 | 1181.6 | 1238.4 | 1305.5 | 1314.2 | 1241.1 | 1251.2 | 1375.2 | 1381.6 | 1319.7 | 1301.1 | 1300.8 | 1340.8 | 1326.2 | 1317.6 | 1312.2 | 1288.2 | 1119.2 | 1462.8 | 1145.2 | 1201 | 1203.7 | 1178.1 | 1205.3 | 1219.7 | 1184.7 | 1172.4 | 1204.6 | 1195.6 | 1223.5 | 1255.4 | 1349.6 | 1211.8 | 1213.2 | 1233.5 | 1176.1 | 1231.4 | 1380.8 | 1413.8 | 1307.8 | 1324.4 | 1375.3 | 1233.9 | 1386.7 | 1379.8 | 1206.9 | 1333.7 | 1201.6 | 1071.2 | 1364.9 | 1304.8 | 1323 | 1225.9 | 1193.3 | 1194.8 | 1210.8 | 1208.6 | 1220.3 | 1211.2 | 1398.2 | 1378 | 1389.4 | 1210 | 1190 | 1289.5 | 1243.2 | 1238.4 | 1206.8 | 1215.9 | 1221.6 | 1250.9 | 1184.8 | 1226.2 | 1211.6 | 1210.1 | 1262 | 1292.3 | 1236.7 | 1233 | 1313.5 | 1171.5 | 1180.2 | 1209.1 | 1198.3 | 1202.5 | 1231.2 | 1208.8 | 1233.6 | 1208.2 | 1344.6 | 1220.9 | 1490.8 | 1343 | 1226.5 | 1345.8 | 1312.3 | 1320.5 | 1388.2 | 1380.2 | 1222.8 | 1239.8 | 1345 | 1341.3 | 1334.2 | 1215.9 | 1249.2 | 1334.7 | 1316.7 | 1207.8 | 1224.5 | 1312.5 | 1159.3 | 1161.3 | 1330.4 | 1333.3 | 1275 | 1319.5 | 1268.4 | 1085.1 | 1375.1 | 1306.1 | 1326.1 | 1247 | 1251.9 | 1243.2 | 1185.4 | 1258.8 | 1077.4 | 1345.4 | 1136.4 | 1342.8 | 1223.8 | 1124.1 | 1292.6 | 1316 | 1319.7 | 1213.6 | 1386.9 | 1215.3 | 1195.7 | 1178.3 | 1181.3 | 1189.6 | 1119.4 | 1145.7 | 1317.8 | 1136.5 | 1249.2 | 1255 | 1282.6 | 1100.7 | 1173.7 | 1311.6 | 1221 | 1081.8 | 1193.7 | 1144.2 | 1233.4 | 1208.4 | 1367.2 | 1194.3 | 1249.5 | 1111.5 | 1415.5 | 1251.3 | 1230.2 | 1212 | 1294.6 | 1339.3 | 1251.8 | 1344.3 | 1264.4 | 1260.6 | 1201.5 | 1118.6 | 1151.3 | 1114.2 | 1063.2 | 1149.3 | 1227.5 | 1209.9 | 1036.9 | 1265.6 |  |  | 1042 | 813.4 | 1158.6 |  | 1268.2 | 1120.2 | 1167.2 | 1138.7 | 1175.2 | 1179 | 1181.3 | 1190.6 | 1209.3 | 1237.2 | 1228.2 | 1245.6 | 1306.2 | 1369.4 | 1163.3 | 971 | 886.5 | 707.1 | 899.1 | 1017.6 | 1254.2 | 1357.1 | 1263 | 1273.4 | 1277.6 | 1323.1 | 1356.2 | 1273.2 | 958.4 | 1180 | 960.6 | 1128.9 | 984.4 |  | 1578.1 | 1229.2 | 501.1 | 1143.4 | 1100.8 |  |  | 1139.3 | 1117.4 | 797.8 | 1080 | 1000.1 | 34.64 | 42.7 | 3.78 | 7.5 |  | 0 | 6.3 |  |  | 83503615.233 | 281835.466 | 56596133.071 | 61424 | 84302475.451 | 186580 | 61041530.906 | 55471.573 | 316556555.744 | 83487.6 | 80182.478 | 12.01 | 77346.243 | 10.205 | 78823.169 | 41.491 | 60323.094 | 36.177 | 296343.885 | 22.985 | 157506.506 | 296320.9 | 12 | 0 | 6.3 | 34.64 | 42.7 | 3.78 | 7.5 | 298175.2
2025-05-02 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 7:00 | 19:00 | 931.2 | 903.1 | 871.3 | 863.9 | 932.6 | 866.2 | 858.4 | 859.9 | 858.4 | 904.8 | 880.7 | 873 | 859.6 | 810.1 | 830.1 | 864.1 | 823.6 | 859 | 932.3 | 928.7 | 866.7 | 873.6 | 957.6 | 979.4 | 931.5 | 922.8 | 917.2 | 950.4 | 958 | 942.1 | 938.6 | 941.3 | 796.7 | 1105.3 | 832.4 | 859.7 | 857.5 | 837.6 | 845.6 | 850.7 | 840.1 | 822.2 | 843.6 | 836.8 | 854.1 | 887.4 | 934.1 | 846.8 | 856.7 | 877.3 | 833.9 | 854.3 | 952.1 | 975.8 | 926.8 | 942.8 | 971.1 | 859.2 | 969.6 | 985.1 | 858.5 | 970.4 | 853.5 | 879.4 | 932.7 | 917.8 | 933.3 | 899.7 | 845.2 | 842.2 | 854.9 | 853.4 | 863.3 | 855.4 | 970.7 | 556.1 | 988.2 | 836.9 | 827.3 | 915.9 | 857.9 | 855.8 | 849.7 | 857.1 | 850.1 | 861.4 | 873 | 861.5 | 854.8 | 850.3 | 887.9 | 924 | 874.2 | 871.9 | 930.6 | 836.2 | 825.7 | 868 | 839.1 | 848.4 | 871.1 | 843.6 | 869.9 | 853.6 | 955 | 863.4 | 1054.7 | 942.8 | 860.7 | 953.2 | 933.3 | 918.2 | 971.2 | 962.9 | 853 | 861 | 940.8 | 960.6 | 953.4 | 853.4 | 875.7 | 948 | 937.3 | 854.4 | 868 | 931.4 | 828.7 | 823.2 | 940.7 | 941.5 | 892.2 | 907.4 | 894.6 | 764.3 | 963.3 | 916.8 | 923.9 | 877.8 | 880.2 | 875.1 | 837.6 | 915.7 | 764.7 | 958 | 800.6 | 932.5 | 855 | 793.3 | 915.7 | 933.3 | 936.2 | 859.4 | 986.2 | 858.2 | 840.7 | 829.9 | 830.3 | 828.6 | 850.2 | 819.2 | 947 | 812.5 | 913.3 | 918.4 | 926.2 | 792.1 | 809.4 | 922.6 | 843.6 | 805.8 | 852.8 | 818.9 | 915.2 | 855.7 | 962 | 842 | 852.2 | 810.2 | 973.1 | 871.4 | 905.9 | 910.2 | 955.4 | 943.6 | 885.1 | 950.1 | 887.4 | 892.2 | 854.9 | 842.1 | 813.4 | 822.2 | 814.9 | 811.9 | 854.6 | 835.9 | 723 | 873.3 |  |  | 756.4 | 592.7 | 855 |  | 918.5 | 798.1 | 849.3 | 822.4 | 843.1 | 840.1 | 844.5 | 850.2 | 850.6 | 869.3 | 853.6 | 870.7 | 923.3 | 977.9 | 826.8 | 720.5 | 650.1 | 578.8 | 652.7 | 739.2 | 853.6 | 929.2 | 899.4 | 903.6 | 900.1 | 896.6 | 922 | 903.3 | 697.9 | 833 | 697 | 813.6 | 709.8 |  | 1101 | 870.2 | 347.6 | 802.5 | 775.1 |  |  | 822.7 | 853.1 | 565.1 | 767.8 | 725.4 | 26.59 | 33.02 | 3.03 | 7.7 |  | 0 | 4.16 |  |  | 83560630.704 | 281851.284 | 56650810.423 | 61437 | 84358523.571 | 186623 | 61084340.104 | 55483 | 316766786.327 | 83569.12 | 57015.471 | 15.818 | 54677.352 | 13 | 56048.12 | 43 | 42809.198 | 11.427 | 210230.583 | 81.52 | 111664.005 | 210149.063 | 12 | 0 | 4.16 | 26.59 | 33.02 | 3.03 | 7.7 | 211112
2025-05-03 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 7:00 | 19:00 | 1289.3 | 1249.1 | 1206.8 | 1201.5 | 1293.8 | 1199.4 | 1192.9 | 1196.8 | 1192 | 1253.4 | 1220.5 | 1214.9 | 1198.1 | 1129.2 | 1169 | 1198.8 | 1146.1 | 1194.5 | 1293.9 | 1289.1 | 1205.7 | 1209.7 | 1328.7 | 1356.4 | 1300.9 | 1283.5 | 1278.5 | 1325.8 | 1332.1 | 1319 | 1329.5 | 1320.7 | 1118.1 | 1541.2 | 1143.8 | 1212.9 | 1189.9 | 1167.9 | 1184.2 | 1197.9 | 1178 | 1158.2 | 1182 | 1175 | 1189.5 | 1202.2 | 1295.5 | 1184.4 | 1194.1 | 1191.6 | 1153.2 | 1196.7 | 1345.9 | 1351 | 1289.6 | 1309.6 | 1347.4 | 1206.4 | 1344.4 | 1361.1 | 1196.4 | 1350.5 | 1198.2 | 1193.1 | 1296.1 | 1276.2 | 1299.1 | 1230 | 1186.8 | 1177.7 | 1189.8 | 1189 | 1214.3 | 1194.2 | 1355.2 | 1345.4 | 1348.4 | 1170.3 | 1157.7 | 1269.3 | 1196.5 | 1195.7 | 1186.8 | 1196.7 | 1189.1 | 1197.4 | 1211.9 | 1196.7 | 1170.1 | 1183.2 | 1237.3 | 1286 | 1218.2 | 1214.1 | 1293.8 | 1142.4 | 1156.7 | 1199.4 | 1177.7 | 1188 | 1219.6 | 1182.4 | 1210.1 | 1189.9 | 1349.5 | 1199 | 1439 | 1322.9 | 1201.3 | 1320.5 | 1292.2 | 1279.3 | 1348.1 | 1341.1 | 1191.3 | 1200.8 | 1313.5 | 1329.2 | 1321.1 | 1186.1 | 1213.3 | 1313.3 | 1294.3 | 1189 | 1205.2 | 1332.5 | 1120.1 | 1138.5 | 1322 | 1319.3 | 1220 | 1266 | 1225.6 | 1069.4 | 1342.2 | 1283.7 | 1294.9 | 1228.1 | 1218.7 | 1208.8 | 1270.4 | 1266.2 | 1144.8 | 1324.4 | 1101.6 | 1337.3 | 1187 | 1101.5 | 1272.2 | 1297 | 1299.8 | 1192.7 | 1365.3 | 1229.3 | 1173.1 | 1159 | 1149.1 | 1155.4 | 1184 | 1146.8 | 1313.8 | 1142.7 | 1292.4 | 1273.5 | 1309.5 | 1114.1 | 1128.1 | 1290.4 | 1171 | 1125.9 | 1230 | 1147.2 | 1280.9 | 1199.6 | 1335.9 | 1173.5 | 1176.2 | 1112.6 | 1349.6 | 1177.8 | 1261.8 | 1278.6 | 1307.8 | 1303.5 | 1230.9 | 1325.6 | 1233.6 | 1214 | 1194.6 | 1174.7 | 1130 | 1123.8 | 1070.4 | 1127.1 | 1186.5 | 1159.8 | 1003.5 | 1207.9 |  |  | 1043.7 | 816.6 | 1173 |  | 1277.9 | 1096.1 | 1180.7 | 1151.8 | 1175.6 | 1182.4 | 1183.7 | 1192.1 | 1201.5 | 1216.8 | 1142.5 | 1211 | 1290.5 | 1361.9 | 1140.9 | 1007.7 | 905.2 | 800.1 | 873 | 1035.9 | 1200.2 | 1334.2 | 1251.6 | 1252.2 | 1204.6 | 1301.6 | 1330.7 | 1188 | 1012] | 1169.2 | 1018.8 | 1113 | 991 |  | 1356 | 1167.5 | 508 | 1089.3 | 1059.2 |  |  | 1206.8 | 1243.5 | 784.2 | 1015.6 | 931 | 27 | 31 | 3.1 | 5.9 |  | 0 | 5.85 |  |  | 83639719.132 | 281866.63 | 56726946.982 | 61457.096 | 84436429.55 | 186658.586 | 61144398.403 | 55497.082 | 317059642.463 | 83628.29 | 79088.428 | 15.346 | 76136.559 | 20.096 | 77905.979 | 35.586 | 60058.299 | 14.082 | 292856.136 | 59.17 | 155189.545 | 292796.966 | 12 | 0 | 5.85 | 27 | 31 | 3.1 | 5.9 | 293330
2025-05-04 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:29 | 6:20 | 1414 | 1371 | 1323 | 1318 | 1423 | 1316 | 1307 | 1328 | 1372 | 1383 | 1338 | 1345 | 1325 | 1244 | 1318 | 1312 | 1255 | 1310 | 1417 | 1417 | 1322 | 1326 | 1451 | 1484 | 1428 | 1409 | 1403 | 1453 | 1462 | 1442 | 1410 | 1444 | 1222 | 1617 | 1251 | 1328 | 1306 | 1292 | 1305 | 1321 | 1297 | 1282 | 1301 | 1294 | 1313 | 1332 | 1430 | 1303 | 1353 | 1331 | 1274 | 1328 | 1513 | 1498 | 1412 | 1436 | 1479 | 1321 | 1473 | 1494 | 1324 | 1483 | 1307 | 1304 | 1414 | 1395 | 1418 | 1310 | 1292 | 1286 | 1302 | 1299 | 1339 | 1308 | 1475 | 1398 | 1468 | 1276 | 1273 | 1376 | 1310 | 1313 | 1309 | 1320 | 1312 | 1326 | 1342 | 1325 | 1244 | 1290 | 1345 | 1378 | 1293 | 1341 | 1412 | 1269 | 1278 | 1328 | 1300 | 1317 | 1355 | 1312 | 1341 | 1316 | 1488 | 1328 | 1564 | 1444 | 1322 | 1455 | 1432 | 1387 | 1452 | 1463 | 1303 | 1298 | 1432 | 1453 | 1469 | 1306 | 1328 | 1423 | 1418 | 1300 | 1337 | 1433 | 1221 | 1245 | 1443 | 1443 | 1284 | 1389 | 1341 | 1168 | 1471 | 1404 | 1417 | 1382 | 1333 | 1322 | 1326 | 1378 | 1198 | 1450 | 1213 | 1464 | 1299 | 1207 | 1390 | 1414 | 1426 | 1306 | 1493 | 1308 | 1286 | 1267 | 1414 | 1234 | 1300 | 1253 | 1445 | 1247 | 1422 | 1408 | 1433 | 1217 | 1235 | 1409 | 1484 | 1233 | 1310 | 1251 | 1396 | 1312 | 1476 | 1291 | 1301 | 1222 | 1483 | 1322 | 1387 | 1407 | 1477 | 1446 | 1352 | 1459 | 1397 | 1364 | 1311 | 1294 | 1237 | 1237 | 1244 | 1317 | 1267 | 1278 | 1100 | 1276 |  |  | 1100 | 998 | 1396 |  | 1259 | 1313 | 1279 | 1312 | 1309 | 1316 | 1318 | 1328 | 1339 | 1252 | 1328 | 1411 | 1485 | 1378 | 1106 | 999 | 876 | 798 | 929 | 1114 | 1323 | 1434 | 1342 | 1342 | 1219 | 1310 | 1403 | 1393 | 1109 | 1285 | 1113 | 1207 | 1074 |  | 1410 | 1333 | 598 | 1246 | 1195 |  |  | 1339 | 1383 | 860 | 1126 | 1010 | 33.65 | 43.22 | 1.9 | 7.5 |  | 0 | 6.49 |  |  | 83726824.722 | 281882.851 | 56809802.29 | 61467.68 | 84521862.024 | 186707.953 | 61210236.424 | 55510.862 | 317380486.88 | 83692.452 | 87105.59 | 16.221 | 82855.308 | 10.584 | 85432.474 | 49.367 | 65838.021 | 13.78 | 320844.417 | 64.162 | 169934.093 | 320780.255 | 12 | 0 | 6.49 | 33.65 | 43.22 | 1.9 | 7.5 | 322757
2025-05-05 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:32 | 18:17 | 927.5 | 900.4 | 867.5 | 865.8 | 933.3 | 861.3 | 868.1 | 864.7 | 893.3 | 901.5 | 877.5 | 875.4 | 862.5 | 811.6 | 856.7 | 854.1 | 822.7 | 856.2 | 925 | 925.5 | 861.6 | 857.7 | 944.4 | 962.7 | 929.6 | 912.4 | 907.1 | 942.3 | 942.5 | 935.4 | 929.5 | 934.9 | 805.9 | 1065.4 | 841.4 | 938.1 | 861.6 | 853.1 | 864.9 | 874.9 | 859.6 | 846.8 | 863.1 | 855.8 | 871.8 | 878.3 | 946.8 | 865.7 | 899.4 | 884.6 | 842 | 871.8 | 994.1 | 984.5 | 931.7 | 942.5 | 984 | 868.7 | 968.1 | 978.7 | 873.6 | 976.5 | 870 | 847 | 931.4 | 918.7 | 934.7 | 905 | 855.6 | 779 | 861.2 | 860 | 877.9 | 861.5 | 965.7 | 1001.5 | 960 | 834.2 | 832.7 | 922.6 | 867.9 | 865.1 | 861.8 | 864.7 | 864.7 | 871.3 | 880.1 | 868.5 | 874.1 | 855.7 | 888.1 | 934.6 | 870.2 | 879 | 932.5 | 821.7 | 835.9 | 866.3 | 857.2 | 853.5 | 885.5 | 860.4 | 880 | 862.8 | 979.2 | 867.2 | 1019 | 954.6 | 872 | 962.1 | 938.8 | 892.7 | 955.7 | 962.7 | 858.7 | 863.7 | 946.7 | 956.3 | 960.4 | 859.3 | 875.6 | 938.8 | 934.6 | 856.3 | 872 | 940.1 | 834.3 | 835.1 | 941.9 | 945.2 | 901.7 | 908.1 | 905.2 | 768.3 | 962.4 | 926.3 | 931.2 | 879.7 | 876 | 858.2 | 832.5 | 903.3 | 769.1 | 947.7 | 783.9 | 924.6 | 846.4 | 785.7 | 906.4 | 923.7 | 930.3 | 853.5 | 945.6 | 861.8 | 850.5 | 831.1 | 827.7 | 810.9 | 850.9 | 817.6 | 959.3 | 830.1 | 951.6 | 922.6 | 953.3 | 791.8 | 806 | 919.7 | 839.3 | 804.3 | 826.6 | 816.5 | 909.2 | 853.8 | 977.1 | 845.9 | 949.1 | 796.3 | 974 | 864.5 | 905.7 | 917.4 | 975.6 | 952.9 | 890.1 | 972.6 | 884 | 892 | 858.8 | 792.6 | 797.5 | 780.6 | 773.3 | 807.5 | 852.7 | 818.4 | 710.3 | 859.8 |  |  | 782.6 | 541.4 | 827 |  | 917.1 | 765.1 | 854.3 | 827.3 | 854.2 | 860.3 | 862.9 | 866 | 868.7 | 876.1 | 809.1 | 865 | 926 | 940.2 | 807 | 718.3 | 644.6 | 568.5 | 623.4 | 749.5 | 893 | 957.9 | 881.2 | 888.7 | 810.5 | 931.4 | 913.5 | 913.6 | 727.1 | 857.6 | 736 | 814.6 | 719.9 |  | 1139.9 | 868.9 | 397.2 | 813.4 | 780.9 |  |  | 870.2 | 900.7 | 568 | 748.4 | 741.8 | 27.91 | 34.01 | 2.69 | 9.1 |  | 0 | 4.14 |  |  | 83784058.891 | 281898.851 | 56864716.575 | 61479.68 | 84577882.491 | 186757.953 | 61253729.251 | 55528.862 | 317591883.672 | 83756.214 | 57234.169 | 16 | 54914.285 | 12 | 56020.467 | 50 | 43492.827 | 18 | 211396.792 | 63.762 | 112120.454 | 211333.03 | 12 | 0 | 4.14 | 27.91 | 34.01 | 2.69 | 9.1 | 212087.7
2025-05-06 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:09 | 18:24 | 1403.8 | 1413.5 | 1314.9 | 1308.9 | 1410.1 | 1303.3 | 1310.6 | 1311.6 | 1353.5 | 1366.1 | 1332.4 | 1325.1 | 1304.5 | 1228.6 | 1307.5 | 1301.2 | 1245.2 | 1296.6 | 1404.3 | 1402.9 | 1308.5 | 1313.6 | 1436.6 | 1472.5 | 1414.1 | 1396.7 | 1389 | 1443.5 | 1454.8 | 1436.5 | 1441.5 | 1444.8 | 1194.9 | 1567 | 1227 | 1395.6 | 1263.4 | 1244 | 1259.7 | 1274.3 | 1252.8 | 1234.1 | 1255.7 | 1249.6 | 1265.9 | 1281.6 | 1375.4 | 1255.4 | 1315.2 | 1293.1 | 1271.4 | 1271.1 | 1450.2 | 1438.1 | 1367.7 | 1386.7 | 1441.3 | 1281.4 | 1425.5 | 1444.7 | 1272.1 | 1440.2 | 1267.6 | 1257.9 | 1413.7 | 1402.1 | 1417.7 | 1425.8 | 1296.2 | 1301.1 | 1302.6 | 1300.7 | 1325.2 | 1301.2 | 1466.2 | 1471.5 | 1466.8 | 1273 | 1266.2 | 1372.6 | 1308.7 | 1310.1 | 1303.2 | 1314.7 | 1304.8 | 1314.8 | 1326.9 | 1306.7 | 1303.7 | 1293.1 | 1353.9 | 1361.2 | 1338.1 | 1328.8 | 1440.5 | 1302.3 | 1300.4 | 1311.9 | 1293.1 | 1300 | 1336.8 | 1298.7 | 1325.5 | 1300.7 | 1471.5 | 1312.1 | 1549.1 | 1447 | 1316.4 | 1449 | 1413.9 | 1390.2 | 1451.9 | 1462.6 | 1304.1 | 1279.5 | 1434.5 | 1450.8 | 1447.2 | 1297.4 | 1322.4 | 1418.2 | 1413.1 | 1301.5 | 1315.9 | 1430.4 | 1293.6 | 1304.5 | 1439 | 1438.6 | 1378.9 | 1382.6 | 1371.2 | 1162.9 | 1467.7 | 1403.3 | 1416.6 | 1389.7 | 1382.2 | 1308.4 | 1273.9 | 1380.2 | 1251.2 | 1440.9 | 1203 | 1455.7 | 1289.4 | 1201.9 | 1385.2 | 1409.6 | 1418.3 | 1302.6 | 1487.8 | 1302.6 | 1283.3 | 1264.8 | 1265.8 | 1278.5 | 1297.5 | 1245.9 | 1447.9 | 1248.1 | 1430.6 | 1407 | 1446.5 | 1221.8 | 1240.3 | 1407.2 | 1286.3 | 1236 | 1275.7 | 1250.8 | 1410.3 | 1312.7 | 1474 | 1289.1 | 1300 | 1240 | 1482.5 | 1347.2 | 1158.1 | 1417.2 | 1455.7 | 1425 | 1373.1 | 1458.3 | 1355.8 | 1364.2 | 1315.5 | 1208 | 1247.6 | 1245.6 | 1187.9 | 1242.6 | 1240.2 | 1201.3 | 1096.7 | 1308.8 |  |  | 1003.4 | 873 | 1292.1 |  | 1388.3 | 1193.3 | 1262.9 | 1265.2 | 1289.4 | 1296.9 | 1297.1 | 1304.3 | 1307.7 | 1322.8 | 1256.6 | 1324.7 | 1469.7 | 1490.2 | 1224.9 | 1125.6 | 1010.6 | 863 | 956 | 1142.8 | 1360.1 | 1464.9 | 1381.8 | 1375 | 1345.5 | 1379.2 | 1398.4 | 1436 | 1153.8 | 1297.7 | 1165.3 | 1243.2 | 1020.2 |  | 1693.2 | 1313.9 | 541.4 | 1226.2 | 1187.7 |  |  | 1308.4 | 1371.1 | 878 | 1167.9 | 980.5 | 30.59 | 43.32 | 1.89 | 5.1 |  | 0 | 6.31 |  |  | 83869638.121 | 281921.136 | 56947478.718 | 61523.885 | 84663181.628 | 186809.826 | 61320152.131 | 55583.377 | 317911517.35 | 83859.522 | 85579.23 | 22.285 | 82762.143 | 44.205 | 85299.137 | 51.873 | 66422.88 | 54.515 | 319633.678 | 103.308 | 168274.883 | 319530.37 | 12.25 | 0 | 6.31 | 30.59 | 43.32 | 1.89 | 5.1 | 321279.5
2025-05-07 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:56 | 18:30 | 885.8 | 892.1 | 827.8 | 823.8 | 893.8 | 825.8 | 830.3 | 830.1 | 853.1 | 859.5 | 841.9 | 838.3 | 826 | 774.2 | 826.5 | 820 | 789.5 | 823.8 | 887.6 | 889.3 | 831.4 | 828.9 | 903.4 | 926.9 | 898.9 | 887 | 878.9 | 910.3 | 917 | 906.8 | 915.2 | 911.1 | 783.6 | 1023.8 | 803.4 | 911.6 | 824.3 | 811.5 | 823.4 | 831.1 | 821.8 | 815.1 | 821.1 | 818.2 | 828.3 | 837.8 | 894.5 | 821 | 855.9 | 841 | 827.1 | 829.8 | 945 | 939.6 | 893.5 | 904.3 | 8938.5 | 834.2 | 928.3 | 938 | 829.6 | 935.9 | 823.9 | 802 | 899.7 | 893.5 | 902.7 | 907.1 | 822.4 | 826.2 | 828.1 | 825.1 | 846.8 | 831.8 | 936.3 | 906.7 | 935.2 | 814.4 | 810.6 | 873.7 | 832.3 | 833.7 | 828.4 | 836.8 | 828.3 | 834.5 | 840.6 | 829.4 | 826 | 819.5 | 859 | 886.2 | 848.2 | 846 | 927.8 | 808.3 | 813 | 841 | 830.9 | 834.7 | 855.8 | 830.4 | 847 | 832.2 | 944.2 | 834.5 | 976.5 | 926.8 | 841.1 | 923.6 | 898.6 | 892.3 | 922.1 | 936.1 | 833.4 | 769.8 | 921.9 | 920.6 | 922.6 | 825.2 | 842.6 | 905.4 | 897.4 | 828.5 | 838.9 | 908.3 | 790.9 | 794.6 | 921.3 | 921 | 887.2 | 881.1 | 850.2 | 739.3 | 934.2 | 900.2 | 906.4 | 892.9 | 877.6 | 833.8 | 809.8 | 870.8 | 806.8 | 916.2 | 761.5 | 927 | 822 | 764.7 | 880.6 | 894.9 | 905.1 | 829.3 | 944.3 | 831.7 | 819.2 | 807.9 | 811.5 | 798.2 | 827 | 794.8 | 921 | 800.1 | 917.5 | 895.3 | 927.4 | 778.1 | 796.7 | 905.9 | 825.9 | 799.9 | 822.3 | 801.1 | 842.2 | 842.2 | 938.5 | 822.5 | 828.4 | 814 | 947.5 | 838.5 | 888.2 | 899 | 935.7 | 907 | 898.4 | 933.3 | 863.8 | 866.7 | 838 | 781 | 801.2 | 790.5 | 672.9 | 820.1 | 791.5 | 818.9 | 704.5 | 841.5 |  |  | 655.5 | 564.5 | 823.2 |  | 888.2 | 772.5 | 810.3 | 802.6 | 825.6 | 821.9 | 825.6 | 824.1 | 836.2 | 841 | 823.7 | 847.3 | 938.8 | 954.2 | 776.4 | 741.3 | 600.2 | 500 | 607.2 | 725.5 | 870.8 | 931.8 | 866.6 | 869.3 | 881.5 | 869.5 | 891 | 900 | 722 | 827.9 | 735.5 | 788.2 | 670.9 |  | 1075.5 | 835.5 | 376.2 | 779.5 | 750 |  |  | 832.7 | 873.8 | 562.1 | 744.1 | 610.1 | 26.11 | 40.91 | 2.1 | 4.9 |  | 0 | 5.46 |  |  | 83924495.221 | 281921.743 | 56999990.355 | 61559.483 | 84717738.397 | 186820.499 | 61362560.511 | 55627.81 | 318115576.327 | 83861.638 | 54857.1 | 0.607 | 52511.637 | 35.598 | 54556.769 | 10.673 | 42408.38 | 44.433 | 204058.977 | 2.116 | 107332.532 | 204056.861 | 12.5667 | 0 | 5.46 | 26.11 | 40.91 | 2.1 | 4.9 | 213164.2
2025-05-08 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:13 | 18:40 | 1281 | 1291 | 1205 | 1195 | 1300 | 1200 | 1210 | 1210 | 1254 | 1264 | 1226 | 1219 | 1202 | 1133 | 1205 | 1201 | 1148 | 1195 | 1302 | 1294 | 1207 | 1215 | 1329 | 1366 | 1307 | 1291 | 1288 | 1340 | 1349 | 1334 | 1310 | 1342 | 1147 | 934 | 1180 | 1340 | 1213 | 1190 | 1202 | 1208 | 1202 |  | 1205 | 1201 | 1215 | 1217 | 1310 | 1201 | 1240 | 1217 | 1200 | 1200 | 1370 | 1360 | 1299 | 1306 | 1367 | 1212 | 1351 | 1375 | 1212 | 1361 | 1276 | 1098 | 1382 | 1374 | 1383 | 1230 | 1280 | 1283 | 1291 | 1248 | 1335 | 1275 | 1433 | 1402 | 1436 | 1258 | 1259 | 1340 | 1304 | 1302 | 1288 | 1303 | 1296 | 1294 | 1300 | 1275 | 1266 | 1265 | 1301 | 1210 | 1312 | 1321 | 1398 | 1266 | 1263 | 1312 | 1285 | 1298 | 1330 | 1288 | 1315 | 1297 | 1447 | 1303 | 1513 | 1432 | 1308 | 1413 | 1404 | 1380 | 1422 | 1306 | 1188 | 1404 | 1420 | 1424 | 1286 | 1304 | 1377 | 1389 | 1296 | 1317 | 1298 | 1410 | 1062 | 1099 | 1270 | 1273 | 1135 | 1225 | 1175 | 1039 | 1316 | 1270 | 1271 | 1254 | 1237 | 1173 | 1123 | 1227 | 1120 | 1289 | 1078 | 1255 | 1155 | 1074 | 1225 | 1254 | 1255 | 1155 | 1322 | 1160 | 1145 | 1123 | 1110 | 1131 | 1096 | 1198 | 1152 | 1341 | 1155 | 1318 | 1301 | 1228 | 1025 | 1150 | 1062 | 1150 | 1062 | 1192 | 1301 | 1217 | 1360 | 1189 | 1199 | 1173 | 1369 | 1215 | 1284 | 1310 | 1343 | 1316 | 1299 | 1347 | 1251 | 1258 | 1215 | 1224 | 1269 | 1261 | 1248 | 1276 | 1234 | 1277 | 1098 | 1304 |  |  | 1140 | 879 | 1284 |  | 1373 | 1206 | 1282 | 1249 | 1280 | 1286 | 1284 | 1292 | 1297 | 1299 | 1308 | 1440 | 1463 | 1193 | 1143 | 1198 | 1010 | 810 | 944 | 1128 | 1348 | 1440 | 1374 | 1368 | 1310 | 1346 | 1385 | 1423 | 1151 | 1294 | 1159 | 1230 | 1048 |  | 1175 | 1310 | 587 | 810 | 1164 |  |  | 1278 | 1337 | 864 | 1161 | 990 | 31.23 | 40.22 | 2.05 | 7.9 |  | 0 | 6.54 |  |  | 84038086.452 | 281938.345 | 57081493.737 | 61571.092 | 84794945.871 | 186840 | 61428667.418 | 55643.599 | 318419804.813 | 83928.17 | 113591.231 | 16.602 | 81503.382 | 11.609 | 77207.474 | 19.501 | 66106.907 | 15.789 | 304228.486 | 66.532 | 195066.402 | 304161.954 | 12.45 | 0 | 6.54 | 31.23 | 40.22 | 2.05 | 7.9 | 302578
2025-05-09 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:15 | 18:24 | 1446 | 1459 | 1359 | 1353 | 1466 | 1363 | 1364 | 1366 | 1414 | 1430 | 1380 | 1376 | 1358 | 1282 | 1358 | 1354 | 1278 | 1310 | 1396 | 1408 | 1309 | 1316 | 1478 | 1478 | 1415 | 1410 | 1393 | 1452 | 1457 | 1439 | 1498 | 1468 | 1272 | 1637 | 1315 | 1482 | 1336 | 1315 | 1340 | 1354 | 1329 | 1314 | 1336 | 1332 | 1347 | 1355 | 1431 | 1343 | 1399 | 1373 | 1349 | 1343 | 1532 | 1520 | 1460 | 1473 | 1541 | 1363 | 1512 | 1533 | 1346 | 1523 | 1378 | 1363 | 1447 | 1432 | 1455 | 1219 | 1326 | 1328 | 1346 | 1349 | 1361 | 1308 | 1495 | 1455 | 1500 | 1308 | 1302 | 1367 | 1355 | 1352 | 1339 | 1347 | 1350 | 1351 | 1365 | 1344 | 1352 | 1340 | 1388 | 1310 | 1373 | 1365 | 1410 | 1290 | 1296 | 1344 | 1318 | 1331 | 1362 | 1320 | 1347 | 1329 | 1498 | 1233 | 1557 | 1478 | 1350 | 1446 | 1446 | 1405 | 1461 | 1492 | 1343 | 1203 | 1457 | 1478 | 1475 | 1319 | 1350 | 1395 | 1447 | 1336 | 1349 | 1463 | 1239 | 1271 | 1464 | 1469 | 1307 | 1419 | 1370 | 1201 | 1503 | 1450 | 1449 | 1431 | 1406 | 1334 | 1307 | 1400 | 1278 | 1463 | 1224 | 1427 | 1316 | 1225 | 1401 | 1426 | 1433 | 1321 | 1515 | 1322 | 1305 | 1288 | 1278 | 1255 | 1353 | 1301 | 1510 | 1305 | 1491 | 1467 | 1393 | 1163 | 1303 | 1206 | 1344 | 1314 | 1346 | 1317 | 1480 | 1387 | 1528 | 1339 | 1342 | 1321 | 1542 | 1368 | 1445 | 1472 | 1516 | 1482 | 1465 | 1520 | 1401 | 1409 | 1370 | 1377 | 1298 | 1286 | 1268 | 1307 | 1268 | 1312 | 1134 | 1364 |  |  | 1121 | 914 | 1338 |  | 1436 | 1271 | 1312 | 1286 | 1309 | 1315 | 1320 | 1322 | 1358 | 1363 | 1346 | 1349 | 1493 | 1519 | 1243 | 1199 | 1095 | 870 | 921 | 1096 | 1308 | 1397 | 1328 | 1320 | 1390 | 1410 | 1341 | 1375 | 1106 | 1251 | 1115 | 1188 | 1014 |  | 1175 | 1378 | 518 | 1228 | 1193 |  |  | 1310 | 1318 | 1382 | 898 | 1184 | 32.39 | 43.99 | 1.81 | 7.1 |  | 0 | 6.68 |  |  | 84093096.913 | 281952.252 | 57165631.997 | 61582.723 | 84882994.442 | 186889.538 | 61495600.917 | 55657.622 | 318747693.799 | 83981.736 | 55010.461 | 13.907 | 84138.26 | 11.631 | 88048.571 | 49.538 | 66933.499 | 14.023 | 327888.986 | 53.566 | 139123.183 | 327835.42 | 12.15 | 0 | 6.68 | 32.39 | 43.99 | 1.81 | 7.1 | 328786
2025-05-10 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:05 | 18:10 | 1244 | 1254.3 | 1165.3 | 1160.2 | 1256.7 | 1160.3 | 1168 | 1168.3 | 1205.5 | 1214.9 | 1188.9 | 1182.5 | 1164.5 | 1096.4 | 1132.6 | 1156.7 | 1106.2 | 1147.7 | 1238.9 | 1238.4 | 1159.3 | 1159.3 | 1271.1 | 1298.5 | 1254.6 | 1234.5 | 1126.4 | 1274 | 1282.3 | 1265.1 | 1165.3 | 1268.6 | 1087.3 | 1415.9 | 1124.9 | 1263 | 1151.4 | 1137.4 | 1155.6 | 1167.69 | 1147.9 | 1136.2 | 1105.1 | 1147 | 1160.3 | 1166.2 | 1257.8 | 1152.9 | 1203.5 | 1181.8 | 1161.3 | 1159.6 | 1322.3 | 1312.3 | 1251.7 | 1267.5 | 1320.6 | 1175.8 | 1298.7 | 1306.9 | 1167.8 | 1306.9 | 1162.3 | 1135.6 | 1256.3 | 1247.3 | 1260.1 | 1098.3 | 1142.6 | 1151.7 | 1161.1 | 1157.4 | 1177.9 | 1141.5 | 1300.3 | 1270.6 | 1302.9 | 1125.8 | 1123.6 | 1200 | 1165.9 | 1163.9 | 1152.3 | 1162.6 | 1161.6 | 1172.7 | 1155.6 | 1158.3 | 1148 | 1192.9 | 824.9 | 1182.1 | 1177.4125 | 1251 | 1321 | 1115.3 | 1124.7 | 1169.6 | 1150.2 | 1158.2 | 1186.3 | 1153.6 | 1174.7 | 1157.7 | 1314.9 | 1158.2 | 1376.2 | 1288.7 | 1171.4 | 1269.2 | 1257.1 | 1225.4 | 1278.2 | 1296.8 | 1165.9 | 1104.5 | 1269.3 | 1288.6 | 1285.6 | 1154.6 | 1177 | 1228.7 | 1259.4 | 1161.8 | 1171.6 | 1270.3 | 1069.6 | 1097 | 1268.2 | 1218.6 | 1123.9 | 1216.7 | 1168 | 1026.6 | 1289.9 | 1238.2 | 1244.4 | 1113.4 | 1209.9 | 1147.6 | 1117 | 1209.3 | 1103.1 | 1263.5 | 1055.1 | 1233.9 | 1136.2 | 1058.9 | 1223.96 | 1247 | 1251.2 | 1148 | 1319.4 | 1174 | 1147.8 | 1133.2 | 1118.9 | 1080.6 | 1138.5 | 1091.3 | 1268.4 | 1097.6 | 1252.7 | 1226.8 | 1168.3 | 968.2 | 1095.5 | 1000.2 | 1135.5 | 1109.6 | 1132.3 | 1110.7 | 1247.3 | 1165.4 | 1237.6 | 1124.6 | 1135.9 | 1113.6 | 1303 | 1152.4 | 1219.3 | 1248.1 | 1270.3 | 1241.8 | 1231.6 | 1275 | 1168.1. | 1189.5 | 1160.8 | 1166 | 1143.9 | 1122.8 | 1110.4 | 1167.4 | 1107.1 | 1165.4 | 981.4 | 1187.6 |  |  | 1005.6 | 799.5 | 1161.9 |  | 1251.2 | 1109.4 | 1165.2 | 1124.7 | 1159.6 | 1162.3 | 1180.1 | 1170 | 1181.4 | 1184.2 | 1166.9 | 1176.4 | 1298.7 | 1317 | 1079.4 | 1041.1 | 998 | 962 | 821 | 975.7 | 1168.2 | 1246.7 | 1180.3 | 1177.9 | 1306 | 1256.3 | 1200.1 | 1220.7 | 974.6 | 1112 | 988.4 | 1059.3 | 901 |  | 1175.1 | 1290 | 520 | 1198 | 1075.2 |  |  | 1280 | 1150.9 | 1204 | 766 | 1020.1 | 29.02 | 40.1 | 1.6 | 5.4 |  | 0 | 5.78 |  |  | 84170081.762 | 281964.316 | 57238934.706 | 61593.285 | 84958087.189 | 186920.646 | 61554663.804 | 55671.488 | 319031987.79 | 84029.622 | 76984.849 | 12.064 | 73302.709 | 10.562 | 75092.747 | 31.108 | 59062.887 | 13.866 | 284293.991 | 47.886 | 150264.932 | 284246.105 | 12.0833 | 0 | 5.78 | 29.02 | 40.1 | 1.6 | 5.4 | 283650.6625
2025-05-11 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:48 | 18:15 | 1468 | 1482 | 1375 | 1367 | 1475 | 1366 | 1372 | 1375 | 1420 | 1431 | 1398 | 1394 | 1373 | 1294 | 1376 | 1370 | 1312 | 1367 | 1475 | 1477 | 1380 | 1382 | 1513 | 1545 | 1489 | 1468 | 1461 | 1514 | 1525 | 1510 | 1440 | 1517 | 1272 | 1668 | 1313 | 1482 | 1363 | 1341 | 1356 | 1370 | 1352 | 1336 | 1292 | 1344 | 1362 | 1374 | 1481 | 1352 | 1416 | 1392 | 1368 | 1366 | 1555 | 1543 | 1468 | 1490 | 1550 | 1383 | 1539 | 1557 | 1373 | 1546 | 1310 | 1310 | 1482 | 1472 | 1491 | 1328 | 1360 | 1355 | 1366 | 1361 | 1384 | 1370 | 1545 | 1495 | 1538 | 1319 | 1313 | 1439 | 1365 | 1366 | 1356 | 1395 | 1363 | 1369 | 1384 | 1364 | 1364 | 1351 | 1417 | 1310 | 1391 | 1384 | 1478 | 1308 | 1319 | 1376 | 1355 | 1364 | 1399 | 1363 | 1384 | 1363 | 1560 | 1374 | 1638 | 1525 | 1386 | 1560 | 1491 | 1471 | 1537 | 1538 | 1371 | 1387 | 1514 | 1547 | 1534 | 1376 | 1396 | 1482 | 1497 | 1377 | 1385 | 1460 | 1264 | 1310 | 1503 | 1452 | 1333 | 1442 | 1375 | 1217 | 1533 | 1465 | 1478 | 1458 | 1439 | 1371 | 1319 | 1420 | 1313 | 1502 | 1266 | 1520 | 1351 | 1258 | 1474 | 1482 | 1496 | 1370 | 1576 | 1375 | 1357 | 1341 | 1310 | 1276 | 1358 | 1304 | 1512 | 1254 | 1487 | 1464 | 1504 | 1329 | 1298 | 1311 | 1350 | 1313 | 1340 | 1308 | 1478 | 1383 | 1476 | 1341 | 1357 | 1325 | 1512 | 1357 | 1471 | 1473 | 1515 | 1482 | 1469 | 1518 | 1410 | 1418 | 1374 | 1374 | 1356 | 1344 | 1227 | 1379 | 1307 | 1378 | 1156 | 1405 |  |  | 1177 | 926 | 1377 |  | 1488 | 1314 | 1378 | 1342 | 1373 | 1372 | 1392 | 1381 | 1393 | 1414 | 1382 | 1388 | 1546 | 1576 | 1281 | 1236 | 1278 | 1263 | 1105 | 1196 | 1429 | 1541 | 1465 | 1453 | 1410 | 1478 | 1475 | 1517 | 1220 | 1360 | 1234 | 1305 | 1107 |  | 1350 | 1398 | 587 | 1280 | 1281 |  |  | 1230 | 1319 | 1369 | 1436 | 1226 | 31.8 | 43.4 | 1.5 | 4.8 |  | 0 | 6.7 |  |  | 84260905.719 | 281980.514 | 57325630.313 | 61632.383 | 85046238.548 | 186946.059 | 61625296.528 | 55720.302 | 319368171.542 | 84092.853 | 90823.957 | 16.198 | 86695.607 | 39.098 | 88151.359 | 25.413 | 70632.724 | 48.814 | 336183.752 | 63.231 | 177464.268 | 336120.521 | 12.45 | 0 | 6.7 | 31.8 | 43.4 | 1.5 | 4.8 | 338732
2025-05-12 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:13 | 18:32 | 1500 | 1512 | 1401 | 1395 | 1502 | 1392 | 1401 | 1403 | 1446 | 1460 | 1427 | 1422 | 1401 | 1319 | 1392 | 1394 | 1336 | 1393 | 1508 | 1511 | 1401 | 1409 | 1539 | 1579 | 1522 | 1502 | 1496 | 1550 | 1565 | 1542 | 1425 | 1552 | 1305 | 1702 | 1347 | 1517 | 1391 | 1371 | 1388 | 1401 | 1380 | 1354 | 1323 | 1377 | 1391 | 1404 | 1511 | 1381 | 1444 | 1421 | 1394 | 1393 | 1585 | 1576 | 1500 | 1516 | 1579 | 1412 | 1568 | 1590 | 1401 | 1577 | 1391 | 1370 | 1518 | 1508 | 1526 | 1350 | 1385 | 1388 | 1397 | 1393 | 1415 | 1396 | 1590 | 1545 | 1583 | 1350 | 1342 | 1452 | 1397 | 1397 | 1387 | 1397 | 1386 | 1399 | 1413 | 1394 | 1393 | 1379 | 1447 | 1356 | 1423 | 1416 | 1543 | 1342 | 1351 | 1408 | 1388 | 1396 | 1436 | 1395 | 1424 | 1396 | 1599 | 1413 | 1674 | 1560 | 1417 | 1556 | 1528 | 1499 | 1541 | 1576 | 1404 | 1301 | 1548 | 1585 | 1574 | 1413 | 1430 | 1512 | 1534 | 1409 | 1419 | 1548 | 1346 | 1367 | 1563 | 1495 | 1364 | 1474 | 1408 | 1244 | 1570 | 1501 | 1512 | 1481 | 1474 | 1406 | 1350 | 1455 | 1345 | 1539 | 1367 | 1555 | 1387 | 1291 | 1511 | 1520 | 1533 | 1405 | 1615 | 1410 | 1389 | 1375 | 1328 | 1307 | 1393 | 1341 | 1552 | 1283 | 1525 | 1498 | 1539 | 1297 | 1323 | 1518 | 1375 | 1339 | 1352 | 1334 | 1504 | 1410 | 1517 | 1377 | 1389 | 1355 | 1524 | 1405 | 1486 | 1504 | 1551 | 1517 | 1507 | 1497 | 1447 | 1455 | 1400 | 1404 | 1392 | 1386 | 1362 | 1413 | 1340 | 1411 | 1185 | 1437 |  |  | 1205 | 980 | 1409 |  | 1520 | 1343 | 1414 | 1378 | 1406 | 1405 | 1423 | 1414 | 1424 | 1444 | 1415 | 1422 | 1582 | 1611 | 1305 | 1266 | 1095 | 919 | 1130 | 1185 | 1420 | 1519 | 1458 | 1460 | 1450 | 1478 | 1463 | 1511 | 1212 | 1357 | 1226 | 1290 | 1097 |  | 1520 | 1368 | 534 | 1280 | 1400 |  |  | 1470 | 1312 | 1335 | 1415 | 1422 | 35.13 | 43.88 | 1.88 | 7.3 |  | 0 | 6.85 |  |  | 84353521.617 | 281995.734 | 57414124.155 | 61641.407 | 85137234.455 | 186972.569 | 61697142.631 | 55734.393 | 319711873.326 | 84154.281 | 92615.898 | 15.22 | 88493.842 | 9.024 | 90995.907 | 26.51 | 71846.103 | 14.091 | 343701.784 | 61.428 | 181085.496 | 343640.356 | 12.3167 | 0 | 6.85 | 35.13 | 43.88 | 1.88 | 7.3 | 345699
2025-05-13 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:03 | 18:30 | 1250 | 1272 | 1181 | 1176 | 1270 | 1173 | 1178 | 1182 | 1221 | 1232 | 1168 | 1182 | 1156 | 1076 | 1132 | 1175 | 1088 | 1071 | 1161 | 1161 | 1075 | 1084 | 1188.9 | 1218 | 1171 | 1156 | 1153 | 1198 | 1209 | 1192 | 1198 | 1202 | 1126.7 | 1430 | 1131 | 1267 | 1166 | 1151 | 1168 | 1180 | 1163 | 1105 | 1135 | 1158 | 1168 | 1178 | 1267 | 1159 | 1213 | 1195 | 1171 | 1168 | 1331 | 1320 | 1260 | 1281 | 1330 | 1192 | 1317 | 1333 | 1180 | 1297 | 1158 | 1110 | 1273 | 1262 | 1277 | 1128.8 | 1159 | 1160 | 1169 | 1166 | 1186 | 1159 | 1322 | 1298 | 1325 | 1139 | 1131 | 1210 | 1171 | 1178 | 1161 | 1169 | 1165 | 1170 | 1183 | 1167 | 1167 | 1158 | 1212 | 1212 | 1175 | 1154 | 1303 | 1117 | 1127 | 1167 | 1148 | 1157 | 1188 | 1156 | 1175 | 1153 | 1310 | 1167 | 1371 | 1289 | 1172 | 1267 | 1258 | 1233 | 1273 | 1304 | 1163 | 1106 | 1276 | 1301 | 1291 | 1165 | 1185 | 1263 | 1267 | 1166 | 1174 | 1398 | 1130 | 1134 | 1302 | 1238 | 1159 | 1246 | 1164 | 1025 | 1298 | 1244 | 1254 | 1238 | 1214 | 1155 | 1117 | 1212 | 1124 | 1270 | 1080 | 1241 | 1147 | 1069 | 1249 | 1264 | 1265 | 1158 | 1327 | 1159 | 1144 | 1135 | 1198 | 1088 | 1170 | 1131 | 1308 | 1112 | 1291 | 1263 | 1301 | 1089 | 1110 | 1276 | 1157 | 1125 | 1131 | 1123 | 1273 | 1186 | 1272 | 1157 | 1166 | 1141 | 1282 | 1182 | 1250 | 1264 | 1308 | 1278 | 1268 | 1260 | 1214 | 1221 | 1173 | 1169 | 1144 | 1137 | 1119 | 1162 | 1131 | 1160 | 975 | 1183 |  |  | 1004 | 842 | 1155 |  | 1252 | 1114 | 1163 | 1126 | 1158 | 1159 | 1171 | 1164 | 1175 | 1187 | 1165 | 1173 | 1301 | 1332 | 1075 | 1037 | 908 | 750 | 894 | 1003 | 1205 | 1282 | 1234 | 1223 | 1208 | 1228 | 1243 | 1278 | 1032 | 1145 | 1037 | 1091 | 925 |  | 1375 | 1170 | 425.9 | 1070.4 | 1076 |  |  | 1098 | 1142 | 1103 | 1103 | 1032 | 34.36 | 42.16 | 1.65 | 11.7 |  | 0 | 5.73 |  |  | 84429612.061 | 282011.535 | 57488191.804 | 61677.352 | 85214024.795 | 187000.005 | 61757442.493 | 55778.947 | 319998971.929 | 84220.239 | 76090.444 | 15.801 | 74067.649 | 35.945 | 76790.34 | 27.436 | 60299.862 | 44.554 | 287098.603 | 65.958 | 150106.347 | 287032.645 | 12.45 | 0 | 5.73 | 34.36 | 42.16 | 1.65 | 11.7 | 286967.7
2025-05-14 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:30 | 18:25 | 1516 | 1529 | 1418 | 1410 | 1463 | 1406 | 1420 | 1424 | 1466 | 1477 | 1451 | 1444 | 1424 | 1339 | 1358 | 1408 | 1351 | 1408 | 1522 | 1529 | 1362 | 1423 | 1558 | 1598 | 1542 | 1522 | 1516 | 1471 | 1588 | 1563 | 1542 | 1577 | 1311 | 1719 | 1351 | 1521 | 1404 | 1384 | 1406 | 1421 | 1396 | 1331 | 1341 | 1395 | 1406 | 1418 | 1526 | 1399 | 1466 | 1441 | 1410 | 1408 | 1602 | 1591 | 1511 | 1535 | 1602 | 1433 | 1585 | 1605 | 1419 | 1591 | 1425 | 1309 | 1537 | 1527 | 1547 | 1313 | 1408 | 1403 | 1419 | 1414 | 1426 | 1407 | 1628 | 1572 | 1604 | 1365 | 1348 | 1453 | 1415 | 1410 | 1398 | 1406 | 1407 | 1412 | 1427 | 1408 | 1415 | 1400 | 1468 | 1422 | 1437 | 1429 | 1415 | [63 empty] | 1404 | 1352 | 1565 | 1351 | 1544 | 1510 | 1556 | 1300 | 1332 | 1532 | 1390 | 1354 | 1381 | 1347 | 1525 | 1426 | 1528 | 1386 | 1400 | 1362 | 1542 | 1416 | 1502 | 1515 | 1567 | 1533 | 1519 | 1508 | 1456 | 1468 | 1416 | 1416 | [32 empty] | 844 | 1003 | 1205 | 1282 | 1234 | 1223 | 1363 | 1310 | 1243 | 1278 | 1032 | 1145 | 1037 | 1091 | 925 | [13 empty] | 38.2 | 45.38 | 2.6 | 7.1 |  | 0 | 6.95 |  |  | 84523132.602 | 282028.228 | 57577637.485 | 61704.247 | 85306571.244 | 187045.615 | 61830305.101 | 55807.783 | 320347094.315 | 84286.91 | 93520.541 | 16.693 | 89445.681 | 26.895 | 92546.449 | 45.61 | 72862.608 | 28.836 | 348122.386 | 66.671 | 182922.634 | 348055.715 | 12.9167 | 0 | 6.95 | 38.2 | 45.38 | 2.6 | 7.1 | 201945
2025-05-15 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:40 | 18:34 | 1470 | 1483 | 1376 | 1367 | 1442.4 | 1368 | 1382 | 1385 | 1428 | 1438 | 1407 | 1400 | 1382 | 1301 | 1318 | 1366 | 1378 | 1364 | 1476 | 1480 | 1321 | 1381 | 1511 | 1551 | 1495 | 1510 | 1471 | 1525 | 1543 | 1518 | 1563 | 1530 | 1268 | 1669 | 1311 | 1494 | 1364 | 1343 | 1364 | 1379 | 1354 | 1289 | 1301 | 1352 | 1377 | 1374 | 1489 | 1364 | 1424 | 1398 | 1378 | 1374 | 1555 | 1543 | 1471 | 1488 | 1559 | 1389 | 1536 | 1556 | 1376 | 1545 | 1463 | 1298 | 1488 | 1478 | 1498 | 1273 | 1359 | 1367 | 1375 | 1372 | 1389 | 1363 | 1558 | 1523 | 1552 | 1346 | 1318 | 1401 | 1379 | 1380 | 1356 | 1362 | 1375 | 1369 | 1393 | 1374 | 1373 | 1359 | 1421 | 1298 | 1400 | 1390 | 1410 | 1343 | 1354 | 1357 | 1329 | 1291 | 1421 | 1375 | 1393 | 1344 | 1547 | 1184 | 1379 | 1489 | 1391 | 1536 | 1419 | 1523 | 1545 | 1587 | 1331 | 1343 | 1556 | 1449 | 1404 | 1378 | 1408 | 1480 | 1421 | 1334 | 1402 | 1474 | 1259 | 1285 | 1510 | 1498 | 1426 | 1428 | 1384 | 1263 | 1529 | 1436 | 1478 | 1400 | 1398 | 1383 | 1342 | 1389 | 1350 | 1510 | 1300 | 1516 | 1400 | 1268 | 1449 | 1456 | 1477 | 1362 | 1465 | 1360 | 1337 | 1320 | 1325 | 1282 | 1361 | 1311 | 1522 | 1312 | 1496 | 1464 | 1508 | 1260 | 1289 | 1485 | 1349 | 1312 | 1339 | 1306 | 1478 | 1379 | 1480 | 1343 | 1357 | 1320 | 1495 | 1372 | 1455 | 1470 | 1523 | 1489 | 1471 | 1462 | 1411 | 1422 | 1377 | 1371 | 1268 | 1213 | 1210 | 1310 | 1339 | 1210 | 1121 | 1357 |  |  | 1181 | 921 | 1272 |  | 1394 | 1242 | 1311 | 1290 | 1259 | 1334 | 1343 | 1339 | 1343 | 1368 | 1369 | 1356 | 1398 | 1542 | 1156 | 1061 | 1069 | 998 | 952 | 1116 | 1337 | 1489 | 1317 | 1369 | 1362 | 1400 | 1398 | 1380 | 1090 | 1300 | 1150 | 1303 | 1100 |  | 1250 | 1360 | 610 | 1298 | 1283 |  |  | 1210 | 1412 | 1300 | 1310 | 1117 | 38.52 | 46.82 | 2.05 | 5.8 |  | 0 | 6.81 |  |  | 84614020.421 | 282042.855 | 57664448.69 | 61713.367 | 85396598.142 | 187073.753 | 61901422.817 | 55823.055 | 320685759.859 | 84346.922 | 90887.819 | 14.627 | 86811.205 | 9.12 | 90026.898 | 28.138 | 71117.716 | 15.272 | 338665.544 | 60.012 | 177675.277 | 338605.532 | 12.9 | 0 | 6.81 | 38.52 | 46.82 | 2.05 | 5.8 | 334705.4
2025-05-16 | 2026 |  |  |  | May-25 | 31 | 66750 | 5:15 | 18:24 | 1262 | 1272 | 1181 | 1176 | 1250 | 1173 | 1179 | 1181 | 1221 | 1233 | 1208 | 1202 | 1186 | 1116 | 1167 | 1175 | 1167 | 1153 | 1249 | 1253 | 1209 | 1283 | 1318 | 1303 | 1312 | 1253 | 1253 | 1339 | 1313 | 1298 | 1292 | 1332 | 1130 | 1430 | 1203 | 1293 | 1167 | 1151 | 1168 | 1181 | 1163 | 1170 | 1158 | 1208 | 1168 | 1178 | 1267 | 1159 | 1213 | 1196 | 1171 | 1168 | 1331 | 1321 | 1260 | 1281 | 1330 | 1192 | 1303 | 1317 | 1334 | 1292 | 1227 | 1109 | 1273 | 1262 | 1277 | 1088 | 1193 | 1197 | 1192 | 1166 | 1186 | 1159 | 1322 | 1293 | 1325 | 1139 | 1181 | 1299 | 1201 | 1172 | 1161 | 1169 | 1165 | 1170 | 1183 | 1167 | 1167 | 1158 | 1212 | 1270 | 1190 | 1184 | 1200 | 1125 | 1135 | 1162 | 1160 | 1150 | 1195 | 1153 | 1170 | 1193 | 1304 | 1140 | 1325 | 1302 | 1180 | 1290 | 1282 | 1281 | 1325 | 1334 | 1140 | 1205 | 1310 | 1319 | 1262 | 1178 | 1187 | 1298 | 1240 | 1123 | 1186 | 1498 | 1167 | 1140 | 1321 | 1303 | 1240 | 1258 | 1230 | 1102 | 1225 | 1245 | 1240 | 1234 | 1215 | 1150 | 1199 | 1240 | 1138 | 1230 | 1100 | 1298 | 1134 | 1057 | 1260 | 1239 | 1253 | 1147 | 1290 | 1141 | 1180 | 1160 | 1198 | 1140 | 1171 | 1131 | 1308 | 1180 | 1291 | 1320 | 1301 | 1089 | 1160 | 1276 | 1157 | 1125 | 1132 | 1123 | 1273 | 1186 | 1272 | 1157 | 1166 | 1141 | 1282 | 1182 | 1250 | 1264 | 1308 | 1278 | 1268 | 1260 | 1214 | 1221 | 1173 | 1169 | 1153 | 1156 | 1130 | 1139 | 1220 | 1150 | 1009 | 1233 |  |  | 1198 | 898 | 1280 |  | 1250 | 1278 | 1182 | 1172 | 1149 | 1209 | 1214 | 1233 | 1230 | 1244 | 1213 | 1201 | 1230 | 1365 | 1072 | 1110 | 860 | 810 | 910 | 1011 | 1213 | 1372 | 1198 | 1244 | 1298 | 1278 | 1287 | 1300 | 1099 | 1219 | 1099 | 1100 | 970 |  | 1230 | 1200 | 450 | 1210 | 1123 |  |  | 1098 | 1298 | 1050 | 1100 | 930 | 37.78 | 42.3 | 2.3 | 11.3 |  | 0 | 5.56 |  |  | 84689361.033 | 282058.64 | 57735686.702 | 61735.503 | 85470963.71 | 187105.571 | 61960225.142 | 55851.671 | 320965372.624 | 84407.417 | 75340.612 | 15.785 | 71238.012 | 22.136 | 74365.568 | 31.818 | 58802.325 | 28.616 | 279612.765 | 60.495 | 146540.703 | 279552.27 | 13.15 | 0 | 5.56 | 37.78 | 42.3 | 2.3 | 11.3 | 292468
2025-05-17 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:27 | 18:25 | 1094 | 1105 | 1030 | 1026 | 1080 | 1024 | 1018 | 1021 | 1053 | 1060 | 1038 | 1036 | 1019 | 958 | 998 | 1009 | 993 | 1000 | 1076 | 1083 | 998 | 1016 | 1113 | 1142 | 1098 | 1082 | 1082 | 1123 | 1126 | 1115 | 1123 | 1121 | 998 | 1271 | 993 | 1123 | 994 | 1013 | 994 | 1004 | 1023 | 993 | 1001 | 1023 | 999 | 1016 | 1088 | 992 | 1039 | 1098 | 1008 | 1066 | 1150 | 1140 | 1093 | 1116 | 1144 | 1020 | 1122 | 1153 | 1005 | 1126 | 1030 | 998 | 1085 | 1076 | 1090 | 998 | 1098 | 1088 | 1098 | 1023 | 1008 | 998 | 1154 | 1190 | 1145 | 1034 | 1023 | 1098 | 1006 | 1013 | 1003 | 1006 | 1003 | 1014 | 1011 | 999 | 1023 | 1013 | 1089 | 1100 | 1019 | 1078 | 1100 | 1002 | 1032 | 1063 | 1038 | 1041 | 1079 | 1035 | 1066 | 1036 | 1198 | 1044 | 1186 | 1175 | 1068 | 1187 | 1146 | 1140 | 1201 | 1189 | 1048 | 1074 | 1172 | 1114 | 1175 | 1064 | 1094 | 1133 | 1114 | 1030 | 1081 | 1478 | 950 | 968 | 1165 | 1154 | 1059 | 1083 | 1051 | 898 | 1104 | 1098 | 1051 | 1083 | 1059 | 1004 | 988 | 1046 | 1024 | 1094 | 999 | 1168 | 1006 | 942 | 1093 | 1113 | 1126 | 1026 | 1119 | 1024 | 1001 | 988 | 1050 | 1178 | 994 | 958 | 1108 | 959 | 1103 | 1073 | 1112 | 928 | 950 | 1086 | 985 | 959 | 980 | 959 | 1081 | 1009 | 1085 | 985 | 990 | 967 | 1093 | 1003 | 1061 | 1074 | 1125 | 1096 | 1078 | 1070 | 1030 | 1040 | 1008 | 1003 | 1021 | 1016 | 977 | 1005 | 1064 | 961 | 900 | 1086 |  |  | 944 | 738 | 1059 |  | 1165 | 1132 | 1051 | 1020 | 1045 | 1058 | 1065 | 1072 | 1069 | 1083 | 1086 | 1080 | 1149 | 1235 | 975 | 894 | 790 | 640 | 783 | 913 | 999 | 1200 | 1018 | 1100 | 1098 | 1097 | 1186 | 1141 | 975 | 994 | 900 | 997 | 960 |  | 1250 | 1068 | 498 | 985 | 918 |  |  | 1000 | 1000 | 970 | 920 | 860 | 34.4 | 42 | 2.7 | 19.29 |  | 0 | 4.84 |  |  | 84756017.786 | 282077.977 | 57798684.403 | 61771.515 | 85536883.57 | 187144.417 | 62011259.85 | 55889.816 | 321211838.837 | 84479.581 | 66656.753 | 19.337 | 62997.701 | 36.012 | 65919.86 | 38.846 | 51034.708 | 38.145 | 246466.213 | 72.164 | 129599.105 | 246394.049 | 12.9667 | 0 | 4.84 | 34.4 | 42 | 2.7 | 19.29 | 254893
2025-05-18 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:14 | 18:23 | 1439 | 1449 | 1344 | 1339 | 1402 | 1340 | 1343 | 1346 | 1387 | 1395 | 1368 | 1363 | 1343 | 1262 | 1310 | 1328 | 1298 | 1327 | 1440 | 1441 | 1310 | 1341 | 1470 | 1507 | 1455 | 1435 | 1430 | 1485 | 1500 | 1480 | 1498 | 1490 | 1247 | 1630 | 1293 | 1455 | 1304 | 1307 | 1324 | 1336 | 1317 | 1298 | 1298 | 1330 | 1276 | 1388 | 1441 | 1317 | 1378 | 1355 | 1398 | 1330 | 1513 | 1502 | 1435 | 1462 | 1516 | 1351 | 1496 | 1458 | 1337 | 1507 | 1337 | 1298 | 1445 | 1435 | 1455 | 1227 | 1316 | 1321 | 1331 | 1326 | 1346 | 1295 | 1518 | 1483 | 1509 | 1300 | 1298 | 1403 | 1336 | 1337 | 1323 | 1329 | 1330 | 1334 | 1347 | 1328 | 1328 | 1314 | 1382 | 1398 | 1358 | 1348 | 1463 | 1328 | 1344 | 1373 | 1376 | 1310 | 1424 | 1373 | 1396 | 1348 | 1541 | 1310 | 1572 | 1545 | 1406 | 1534 | 1402 | 1496 | 1547 | 1563 | 1342 | 1406 | 1533 | 1433 | 1456 | 1377 | 1403 | 1478 | 1417 | 1324 | 1394 | 1482 | 1276 | 1297 | 1521 | 1514 | 1438 | 1450 | 1423 | 1207 | 1544 | 1486 | 1480 | 1439 | 1398 | 1402 | 1353 | 1398 | 1391 | 1546 | 1328 | 1565 | 1356 | 1251 | 1446 | 1470 | 1480 | 1353 | 1496 | 1345 | 1318 | 1307 | 1310 | 1325 | 1328 | 1278 | 1482 | 1282 | 1465 | 1412 | 1477 | 1244 | 1263 | 1455 | 1317 | 1285 | 1309 | 1278 | 1443 | 1360 | 1444 | 1315 | 1315 | 1287 | 1457 | 1338 | 1414 | 1442 | 1482 | 1442 | 1439 | 1426 | 1375 | 1389 | 1351 | 1350 | 1324 | 1306 | 1266 | 1330 | 1395 | 1232 | 1168 | 1419 |  |  | 1210 | 943 | 1357 |  | 1484 | 1378 | 1353 | 1339 | 1334 | 1382 | 1399 | 1406 | 1403 | 1420 | 1404 | 1399 | 1478 | 1587 | 1257 | 1164 | 963 | 810 | 998 | 1174 | 1379 | 1562 | 1386 | 1448 | 1363 | 1378 | 1490 | 1468 | 1264 | 1291 | 1169 | 1300 | 1198 |  | 1478 | 1383 | 633 | 1263 | 1278 |  |  | 1160 | 1263 | 1234 | 1198 | 1110 | 32.3 | 41.68 | 1.14 | 4.7 |  | 0 | 6.4 |  |  | 84844195.864 | 282091.684 | 57882888.841 | 61778.917 | 85624746.958 | 187158.05 | 62078515.979 | 55902.753 | 321539137.169 | 84534.381 | 88178.078 | 13.707 | 84204.438 | 7.402 | 87863.388 | 13.633 | 67256.129 | 12.937 | 327298.332 | 54.8 | 172361.407 | 327243.532 | 13.15 | 0 | 6.4 | 32.3 | 41.68 | 1.14 | 4.7 | 332920
2025-05-19 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:14 | 18:27 | 1413 | 1425 | 1321 | 1315 | 1373 | 1317 | 1317 | 1320 | 1360 | 1372 | 1346 | 1341 | 1321 | 1242 | 1308 | 1317 | 1261 | 1311 | 1417 | 1418 | 1310 | 1326 | 1454 | 1490 | 1428 | 1410 | 1406 | 1459 | 1471 | 1452 | 1425 | 1464 | 1221 | 1597 | 1269 | 1447 | 1304 | 1280 | 1296 | 1309 | 1290 | 1259 | 1276 | 1246 | 1284 | 1311 | 1411 | 1290 | 1348 | 1326 | 1305 | 1302 | 1483 | 1472 | 1402 | 1432 | 1483 | 1328 | 1475 | 1437 | 1309 | 1476 | 1359 | 1258 | 1415 | 1403 | 1427 | 1285 | 1301 | 1292 | 1308 | 1306 | 1333 | 1288 | 1488 | 1456 | 1479 | 1271 | 1249 | 1391 | 1308 | 1307 | 1295 | 1302 | 1303 | 1306 | 1332 | 1301 | 1305 | 1288 | 1356 | 1400 | 1340 | 1331 | 1398 | 1273 | 1264 | 1326 | 1302 | 1316 | 1351 | 1309 | 1336 | 1276 | 1499 | 1329 | 1557 | 1465 | 1328 | 1469 | 1433 | 1406 | 1474 | 1474 | 1317 | 1322 | 1450 | 1481 | 1478 | 1316 | 1335 | 1417 | 1372 | 1321 | 1369 | 1432 | 1264 | 1264 | 1463 | 1458 | 1408 | 1418 | 1412 | 1195 | 1484 | 1380 | 1434 | 1420 | 1397 | 1324 | 1338 | 1371 | 1327 | 1437 | 1284 | 1399 | 1304 | 1211 | 1358 | 1424 | 1431 | 1311 | 1505 | 1318 | 1298 | 1286 | 1254 | 1232 | 1310 | 1270 | 1458 | 1264 | 1437 | 1411 | 1449 | 1220 | 1243 | 1428 | 1303 | 1259 | 1288 | 1253 | 1418 | 1328 | 1416 | 1292 | 1306 | 1273 | 1439 | 1325 | 1398 | 1412 | 1475 | 1414 | 1415 | 1398 | 1365 | 1365 | 1319 | 1312 | 1293 | 1224 | 1218 | 1313 | 1245 | 1311 | 1102 | 1336 |  |  | 1168 | 912 | 1309 |  | 1424 | 1258 | 1315 | 1280 | 1308 | 1310 | 1324 | 1278 | 1323 | 1283 | 1317 | 1325 | 1475 | 1504 | 1216 | 1177 | 910 | 798 | 936 | 1111 | 1314 | 1404 | 1343 | 1332 | 1378 | 1398 | 1358 | 1392 | 1136 | 1266 | 1136 | 1278 | 1210 |  | 1401 | 1402 | 610 | 1298 | 1237 |  |  | 1198 | 1278 | 1210 | 1178 | 1121 | 36.2 | 40 | 1.1 | 4.2 |  | 0 | 6.27 |  |  | 84931095.141 | 282106.839 | 57965993.75 | 61788.116 | 85711093.859 | 187189.533 | 62145633.467 | 55919.967 | 321862485.793 | 84589.752 | 86899.277 | 15.155 | 83104.909 | 9.199 | 86346.901 | 31.483 | 67117.488 | 17.214 | 323348.624 | 55.371 | 169979.832 | 323293.253 | 13.2167 | 0 | 6.27 | 36.2 | 40 | 1.1 | 4.2 | 324288
2025-05-20 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:14 | 18:26 | 1397 | 1409 | 1306 | 1301 | 1370 | 1301 | 1302 | 1305 | 1345 | 1356 | 1330 | 1325 | 1305 | 1228 | 1304 | 1298 | 1268 | 1303 | 1414 | 1416 | 1316 | 1317 | 1438 | 1482 | 1430 | 1411 | 1405 | 1460 | 1472 | 1452 | 1415 | 1461 | 1207 | 1583 | 1243 | 1455 | 1298 | 1267 | 1278 | 1293 | 1272 | 1270 | 1282 | 1268 | 1308 | 1308 | 1404 | 1275 | 1338 | 1314 | 1293 | 1309 | 1467 | 1463 | 1392 | 1415 | 1467 | 1313 | 1455 | 1433 | 1295 | 1465 | 1398 | 1260 | 1413 | 1391 | 1423 | 1263 | 1282 | 1278 | 1295 | 1292 | 1318 | 1285 | 1494 | 1457 | 1481 | 1263 | 1232 | 1351 | 1300 | 1298 | 1281 | 1288 | 1290 | 1292 | 1317 | 1310 | 1291 | 1281 | 1342 | 1363 | 1325 | 1318 | 1398 | 1262 | 1260 | 1316 | 1298 | 1306 | 1344 | 1301 | 1333 | 1311 | 1497 | 1321 | 1564 | 1450 | 1314 | 1436 | 1423 | 1385 | 1426 | 1456 | 1302 | 1310 | 1434 | 1468 | 1471 | 1303 | 1321 | 1401 | 1360 | 1308 | 1327 | 1470 | 1255 | 1263 | 1450 | 1446 | 1395 | 1404 | 1400 | 1197 | 1476 | 1365 | 1424 | 1405 | 1389 | 1316 | 1327 | 1359 | 1320 | 1427 | 1276 | 1353 | 1295 | 1203 | 1353 | 1411 | 1421 | 1302 | 1493 | 1315 | 1292 | 1275 | 1298 | 1227 | 1296 | 1254 | 1441 | 1246 | 1423 | 1393 | 1431 | 1202 | 1259 | 1447 | 1302 | 1245 | 1288 | 1233 | 1416 | 1312 | 1411 | 1280 | 1302 | 1266 | 1429 | 1311 | 1393 | 1395 | 1467 | 1405 | 1398 | 1383 | 1353 | 1353 | 1301 | 1294 | 1283 | 1236 | 1201 | 1307 | 1230 | 1313 | 1089 | 1329 |  |  | 1134 | 904 | 1292 |  | 1410 | 1249 | 1302 | 1272 | 1295 | 1297 | 1310 | 1300 | 1308 | 1329 | 1302 | 1311 | 1459 | 1476 | 1201 | 1167 | 910 | 810 | 957 | 1136 | 1378 | 1439 | 1377 | 1363 | 1398 | 1363 | 1386 | 1427 | 1202 | 1296 | 1161 | 1263 | 1223 |  | 1855 | 1361 | 598 | 1278 | 1223 |  |  | 1210 | 1356 | 1226 | 1164 | 1132 | 36.2 | 38.23 | 1.3 | 6.3 |  | 0 | 6.27 |  |  | 85017444.06 | 282131.806 | 58048179.351 | 61814.197 | 85796789.223 | 187222.612 | 62212722.54 | 55950.155 | 322183673.474 | 84680.598 | 86348.919 | 24.967 | 82185.601 | 26.081 | 85695.364 | 33.079 | 67089.073 | 30.188 | 321187.681 | 90.846 | 168483.472 | 321096.835 | 13.2 | 0 | 6.27 | 36.2 | 38.23 | 1.3 | 6.3 | 323147
2025-05-21 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:16 | 18:27 | 1279 | 1291 | 1197 | 1194 | 1252 | 1192 | 1220.3 | 1193 | 1232 | 1242 | 1217 | 1211 | 1196 | 1124 | 1193 | 1189 | 1174 | 1193 | 1293 | 1295 | 1205 | 1205 | 1319 | 1360 | 1310 | 1291 | 1288 | 1340 | 1355 | 1339 | 1325 | 1352 | 1128 | 1458 | 1176 | 1346 | 1208 | 1188 | 1203 | 1202 | 1201 | 1185 | 1212 | 1185 | 1214 | 1210 | 1310 | 1189 | 1223 | 1205 | 1196 | 1197 | 1372 | 1343 | 1275 | 1308 | 1341 | 1201 | 1340 | 1308 | 1209 | 1363 | 1325 | 1208 | 1290 | 1269 | 1300 | 1167 | 1171 | 1165 | 1183 | 1180 | 1216 | 1186 | 1374 | 1343 | 1364 | 1171 | 1169.4 | 1254 | 1208 | 1208 | 1196 | 1201 | 1205 | 1202 | 1203 | 1196 | 1179 | 1170 | 1226 | 1298 | 1226 | 1217 | 1310 | 1155 | 1163 | 1199 | 1184 | 1192 | 1225 | 1186 | 1215 | 1195 | 1361 | 1205 | 1428 | 1323 | 1198 | 1305 | 1296 | 1270 | 1315 | 1330 | 1188 | 1263 | 1311 | 1335 | 1337 | 1188 | 1207 | 1294.1 | 1309.1 | 1195 | 1210 | 1326 | 1192 | 1165 | 1323 | 1319 | 1273 | 1281 | 1277 | 1093 | 1344 | 1249 | 1300 | 1286 | 1266 | 1195 | 1210 | 1246 | 1206 | 1300 | 1209 | 1263 | 1179 | 1095 | 1258 | 1287 | 1295 | 1184 | 1355 | 1198 | 1181 | 1163 | 1165 | 1145 | 1181 | 1144 | 1311 | 1165 | 1298 | 1276 | 1308 | 1163 | 1170 | 1328 | 1192 | 1144 | 1184 | 1150 | 1309 | 1204 | 1330 | 1169 | 1186 | 1162 | 1304 | 1199 | 1268 | 1287 | 1284 | 1278 | 1275 | 1281 | 1236 | 1233 | 1203 | 1245 | 1188 | 1165 | 1119 | 1220 | 1152 | 1211 | 1000 | 1238 |  |  | 1046 | 824 | 1179 |  | 1291 | 1144 | 1205 | 1175 | 1211 | 1181 | 1219 | 1186 | 1208 | 1214 | 1203 | 1198 | 1378 | 1364 | 1098 | 1066 | 868 | 726 | 889.7 | 1047 | 1260 | 1328 | 1270 | 1263 | 1264 | 1298 | 1323 | 1298 | 1126 | 1180 | 1054 | 1163 | 1126 |  | 1698 | 1298 | 550 | 1210 | 1169 |  |  | 1110 | 1266 | 1240 | 1110 | 1051 | 35.5 | 28 | 1.1 | 4.3 |  | 0 | 5.79 |  |  | 85097003.114 | 282158.202 | 58123585.217 | 61835.796 | 85875128.954 | 187246.759 | 62274322.813 | 55975.842 | 322478484.407 | 84768.572 | 79559.054 | 26.396 | 75405.866 | 21.599 | 78339.731 | 24.147 | 61600.273 | 25.687 | 294810.933 | 87.974 | 154916.925 | 294722.959 | 13.1833 | 0 | 5.79 | 35.5 | 28 | 1.1 | 4.3 | 297837.6
2025-05-22 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:16 | 18:29 | 1401 | 1396 | 1300 | 1275 | 1384 | 1319 | 1294 | 1316 | 1362 | 1372 | 1334 | 1338 | 1321 | 1243 | 1311 | 1321 | 1260 | 1314 | 1423 | 1411 | 1292 | 1332 | 1461 | 1475 | 1443 | 1392 | 1420 | 1476 | 1479 | 1458 | 1443.5 | 1486 | 1208 | 1610 | 1297 | 1478 | 1239 | 1300 | 1319 | 1275 | 1316 | 1284 | 1300 | 1268 | 1300 | 1327 | 1433 | 1304 | 1366 | 1344 | 1276 | 1333 | 1514 | 1492 | 1409 | 1434 | 1480 | 1325 | 1479 | 1438 | 1325 | 1495 | 1412 | 1305 | 1421 | 1395 | 1433 | 1311 | 1311 | 1298 | 1318 | 1316 | 1338 | 1309 | 1500 | 1465 | 1493 | 1279 | 1293 | 1398 | 1319 | 1314 | 1304 | 1308 | 1313 | 1301 | 1328 | 1319 | 1315 | 1308 | 1359 | 1375 | 1348 | 1341 | 1423.6 | 1271 | 1264 | 1312 | 1292 | 1303 | 1342 | 1300 | 1330 | 1305 | 1432 | 1322 | 1559 | 1446 | 1312 | 1456 | 1423 | 1394 | 1472 | 1485 | 1302 | 1271 | 1432 | 1463 | 1462 | 1316 | 1329 | 1429 | 1427 | 1312 | 1328 | 1438 | 1241 | 1275 | 1462 | 1450 | 1405 | 1421 | 1368 | 1228 | 1513 | 1402 | 1450 | 1443 | 1425 | 1334 | 1342 | 1396 | 1346 | 1462 | 1302 | 1390 | 1313 | 1139 | 1395 | 1419 | 1422 | 1296 | 1492 | 1312 | 1290 | 1275 | 1325 | 1277 | 1311 | 1271 | 1455 | 1263 | 1443 | 1409 | 1454 | 1280 | 1295 | 1468 | 1320 | 1316 | 1332 | 1318 | 1450 | 1357 | 1474 | 1296 | 1308 | 1284 | 1446 | 1328 | 1399 | 1420 | 1431 | 1425 | 1417 | 1400 | 1368 | 1316 | 1319 | 1391 | 1294 | 1265 | 1217 | 1321 | 1256 | 1314 | 1105 | 1344 |  |  | 1190 | 849 | 1255 |  | 1418 | 1251 | 1321 | 1290 | 1317 | 1325 | 1333 | 1333 | 1336 | 1364 | 1322 | 1316 | 1473 | 1500 | 1212 | 1166 | 962 | 835 | 964 | 1053 | 1368 | 1461 | 1387 | 1369 | 1378 | 1450.2 | 1455 | 1441 | 1226 | 1271 | 1163 | 1322 | 1192 |  | 1721 | 1371.1 | 519 | 1275 | 1227 |  |  | 1127.6 | 1362.5 | 1348.6 | 1207.7 | 1097 | 33.8 | 43.42 | 3.64 | 8.3 |  | 6.88 | 6.41 |  |  | 85184158.709 | 282186.32 | 58207030.719 | 61858.545 | 85961987.153 | 187281.33 | 62341902.179 | 56009.599 | 322803070.42 | 84859.421 | 87155.595 | 28.118 | 83445.502 | 22.749 | 86858.199 | 34.571 | 67579.366 | 33.757 | 324586.013 | 90.849 | 170550.23 | 324495.164 | 13.2167 | 6.88 | 6.41 | 33.8 | 43.42 | 3.64 | 8.3 | 327534.8
2025-05-23 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:13 | 18:29 | 1402.2 | 1418.1 | 1319.9 | 1316.7 | 1391.6 | 1310.8 | 1294.8 | 1301 | 1352.3 | 1367.5 | 1324.6 | 1320.9 | 1308.7 | 1241.4 | 1309.5 | 1312.2 | 1261.1 | 1300.1 | 1411.7 | 1413.8 | 1318.2 | 1322.8 | 1456.9 | 1495 | 1430.4 | 1412.6 | 1410.5 | 1470.4 | 1476.87 | 1462.2 | 1449.6 | 1473.7 | 1240 | 1599.3 | 1283.4 | 1471.4 | 1314.7 | 1283.6 | 1303.6 | 1344.4 | 1302 | 1263.6 | 1309.8 | 1287.4 | 1311.7 | 1318.6 | 1428.6 | 1300.1 | 1368.5 | 1346.8 | 1274.9 | 1329.8 | 1522.8 | 1482.3 | 1394.7 | 1421.1 | 1459.9 | 1315.6 | 1468.5 | 1432.7 | 1332.1 | 1496.5 | 1328.3 | 1274.6 | 1441 | 1421.4 | 1450.4 | 1301.6 | 1316.1 | 1303.2 | 1259.7 | 1318.8 | 1323.5 | 1293.7 | 1482.8 | 1446.9 | 1477.9 | 1292.9 | 1278 | 1375.7 | 1311.9 | 1311 | 1299.1 | 1309.7 | 1304 | 1301.5 | 1317.9 | 1280.7 | 1320.3 | 1312.2 | 1377.4 | 1385.8 | 1336.5 | 1327.4 | 1485.5 | 1279.2 | 1269.5 | 1297.9 | 1276.1 | 1289.6 | 1330.2 | 1284.5 | 1318.1 | 1289.2 | 1422.4 | 1314.2 | 1542 | 1433.1 | 1302.8 | 1430.7 | 1417.7 | 1391.4 | 1456 | 1445.7 | 1288.8 | 1282.6 | 1420.2 | 1459.6 | 1458.3 | 1325 | 1331.8 | 1432.8 | 1443.1 | 1306.5 | 1321.4 | 1432.5 | 1265.4 | 1264.9 | 1458.2 | 1459.5 | 1432.3 | 1439.7 | 1432.5 | 1227.2 | 1508.6 | 1393.1 | 1435 | 1429.4 | 1410.1 | 1324.4 | 1382 | 1398.4 | 1330.5 | 1455.6 | 1286.4 | 1394.4 | 1318.7 | 1222.8 | 1409.9 | 1430 | 1414.9 | 1285.6 | 1479 | 1298.2 | 1272.9 | 1267.4 | 1268.5 | 1271.4 | 1298.8 | 1259.7 | 1445.3 | 1250.3 | 1429.4 | 1406.5 | 1438.3 | 1279.1 | 1285 | 1458.3 | 1306.8 | 1321 | 1322.1 | 1306.8 | 1439.8 | 1346.9 | 1465.8 | 1285.5 | 1294 | 1272.6 | 1432.3 | 1317.5 | 1385.8 | 1407.1 | 1417.5 | 1415.1 | 1405.7 | 1408.7 | 1354.9 | 1307.7 | 1317.1 | 1379.6 | 1286 | 1260.3 | 1217.7 | 1313.6 | 1254.9 | 1304.9 | 1094.5 | 1333 |  |  | 1174.4 | 902.9 | 1282.1 |  | 1393.3 | 1228 | 1322.9 | 1304.9 | 1310.1 | 1342.1 | 1332.4 | 1348.8 | 1340.7 | 1378.5 | 1320.8 | 1333.3 | 1488.7 | 1517.4 | 1198.7 | 1151.6 | 999.8 | 851.6 | 967 | 1100 | 1356.5 | 1440.2 | 1374.7 | 1369.8 | 1390.2 | 1450.1 | 1437.8 | 1465.6 | 1239 | 1273.7 | 1166.8 | 1257 | 1176.8 |  | 1751 | 1381.2 | 520.8 | 1293.9 | 1238.7 |  |  | 1301.9 | 1331.6 | 1351.4 | 1212.7 | 1095 | 34.93 | 46.23 | 3.32 | 7.1 |  | 6.9 | 6.38 |  |  | 85271343.807 | 282224.438 | 58289730.442 | 61891.294 | 86048437.603 | 187325.901 | 62409065.75 | 56053.356 | 323126301.235 | 84960.27 | 87185.098 | 38.118 | 82699.723 | 32.749 | 86450.45 | 44.571 | 67163.571 | 43.757 | 323230.815 | 100.849 | 169813.954 | 323129.966 | 13.2667 | 6.9 | 6.38 | 34.93 | 46.23 | 3.32 | 7.1 | 326090.97
2025-05-24 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:15 | 18:29 | 1259.4 | 1269.5 | 1180 | 1169.7 | 1227.7 | 1172.6 | 1146.2 | 1148.8 | 1187 | 1197.9 | 1177.5 | 1170.4 | 1151.3 | 1089 | 1155 | 1153.4 | 1128.5 | 1148.6 | 1250.8 | 1247.9 | 1158.2 | 1163.4 | 1278.3 | 1311.4 | 1280 | 1274.3 | 1261.4 | 1293.7 | 1311.1 | 1290.1 | 1295.5 | 1300.7 | 1104.5 | 1430.4 | 1141.9 | 1315.1 | 1145.2 | 1142.7 | 1160.8 | 1188.3 | 1158.3 | 1137.5 | 1163.7 | 1143.1 | 1164.4 | 1170.3 | 1267.4 | 1155.7 | 1213.9 | 1191.7 | 1129.4 | 1177.7 | 1347.1 | 1315.2 | 1254.5 | 1287.6 | 1307.7 | 1172.6 | 1304.5 | 1273.9 | 1183.5 | 1332.5 | 1174.2 | 1141.5 | 1281.8 | 1261.4 | 1290.2 | 1159.5 | 1162.5 | 1152.8 | 1168.6 | 1172.6 | 1183 | 1144.9 | 1333.9 | 1303.8 | 1325.4 | 1149.9 | 1135.3 | 1235.4 | 1163 | 1164.9 | 1158.2 | 1172.4 | 1155.3 | 1159 | 1168.8 | 1115.4 | 1171.9 | 1161.1 | 1217.6 | 1241.5 | 1144.1 | 1180.5 | 1330.5 | 1136.6 | 1127.8 | 1149.3 | 1136.3 | 1141.6 | 1176.5 | 1143.4 | 1172.6 | 1146.6 | 1266.5 | 1161.4 | 1383.1 | 1260.9 | 1148.1 | 1268.7 | 1252.1 | 1251.4 | 1318.6 | 1301.6 | 1135.7 | 1129.9 | 1276.1 | 1312.9 | 1296.1 | 1189 | 1203.7 | 1279.2 | 1217.4 | 1167.3 | 1165.1 | 1271.5 | 1194.5 | 1180.3 | 1339.4 | 1330 | 1283.2 | 1291.3 | 1281.7 | 1100.5 | 1357.5 | 1251.6 | 1293.2 | 1286.8 | 1274.4 | 1198.1 | 1269.9 | 1263.3 | 1196.5 | 1311.1 | 1159.2 | 1228.8 | 1188.7 | 1107.3 | 1238.1 | 1306.3 | 1307.4 | 1183.5 | 1334.7 | 1169.2 | 1144.5 | 1150.3 | 1157.2 | 1155.5 | 1158.3 | 1124.4 | 1295.4 | 1116.6 | 1272.5 | 1255.4 | 1273 | 1176.4 | 1135.8 | 1290.8 | 1164.7 | 1160.5 | 1171.9 | 1167.4 | 1274.4 | 1190.1 | 1268.6 | 1154.3 | 1167.1 | 1142.4 | 1279.2 | 1178.1 | 1241.5 | 1255.6 | 1127.9 | 762.5 | 1257.9 | 1264.9 | 1222.6 | 1176.1 | 1171.5 | 1232.9 | 1138.1 | 1078.4 | 1114.9 | 1158.4 | 1101.5 | 1150 | 962 | 1174.4 |  |  | 1039.3 | 812.6 | 1152.1 |  | 1236 | 1099.9 | 1171.6 | 1155.3 | 1156 | 1186 | 1171.3 | 1186.1 | 1175.8 | 1206.8 | 1164.5 | 1193.2 | 1318.8 | 1344.8 | 1061.7 | 1020.2 | 895.5 | 770 | 869.4 | 1005.8 | 1196.3 | 1281.7 | 1227.8 | 1224.6 | 1212.5 | 1311.5 | 1276.7 | 1272.8 | 1120.3 | 1151.8 | 1061.8 | 1127.5 | 1093.2 |  | 1550.5 | 1227.4 | 472 | 1141 | 1098.2 |  |  | 1161.4 | 1197.3 | 1187.1 | 1078.7 | 992.2 | 35.89 | 44.51 | 4.63 | 7.7 |  | 6.17 | 5.67 |  |  | 85348803.993 | 282272.556 | 58363669.317 | 61938.043 | 86125519.623 | 187381.472 | 62469113.062 | 56111.113 | 323414575.721 | 85081.119 | 77460.186 | 48.118 | 73938.875 | 46.749 | 77082.02 | 55.571 | 60047.312 | 57.757 | 288274.486 | 120.849 | 151304.194 | 288153.637 | 13.2333 | 6.17 | 5.67 | 35.89 | 44.51 | 4.63 | 7.7 | 290997.7
2025-05-25 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:45 | 18:31 | 1448 | 1462.1 | 1353.7 | 1350 | 1443.4 | 1344.4 | 1343.4 | 1345.2 | 1391.6 | 1399.1 | 1368.1 | 1359.4 | 1341.6 | 1264.3 | 1339 | 1336.9 | 1337.2 | 1329.1 | 1438.8 | 1442.6 | 1345 | 1344 | 1475.9 | 1516.9 | 1462.5 | 1450.6 | 1439.4 | 1491.2 | 1503.2 | 1485.5 | 1501.1 | 1496.2 | 1260.7 | 1637.4 | 1313 | 1501.1 | 1345.8 | 1310.8 | 1332.6 | 1356.7 | 1329.9 | 1314.7 | 1338.9 | 1312.8 | 1336.9 | 1346.9 | 1451.4 | 1325.3 | 1383.7 | 1360.6 | 1301.2 | 1254.1 | 1537.8 | 1510.4 | 1438.7 | 1522.1 | 1516.3 | 1349.5 | 1498.8 | 1458.4 | 1350 | 1520.1 | 1336.8 | 1302.3 | 1458.7 | 1446.5 | 1465.8 | 1359.8 | 1338.5 | 1329.6 | 1339.2 | 1337.5 | 1357.8 | 1342.6 | 1526.9 | 1492.4 | 1527.8 | 1342.9 | 1325.1 | 1461.2 | 1348.5 | 1351.3 | 1337.1 | 1354.9 | 1336.7 | 1339.1 | 1355.4 | 1342.9 | 1334.4 | 1324.7 | 1387.2 | 1474.3 | 1369.3 | 1359.9 | 1507.6 | 1323 | 1334.2 | 1326 | 1302 | 1316 | 1351 | 1309 | 1336 | 1326 | 1499 | 1329 | 1557 | 1465 | 1328 | 1469 | 1433 | 1406 | 1474 | 1474 | 1317 | 1322 | 1450 | 1481 | 1428 | 1316 | 1335 | 1477 | 1372 | 1321 | 1338 | 1525 | 1324 | 1331.9 | 1463 | 1458 | 1408 | 1418 | 1412 | 1195 | 1484 | 1400 | 1434 | 1350 | 1397 | 1324 | 1418 | 1421 | 1327 | 1437 | 1334 | 1409 | 1304 | 1211 | 1408 | 1424 | 1431 | 1311 | 1505 | 1318 | 1328 | 1332.9 | 1329.1 | 1332 | 1326.7 | 1289.9 | 1470.7 | 1298.2 | 1458.3 | 1489.1 | 1467.5 | 1379.1 | 1308.2 | 1485.5 | 1336.2 | 1333.6 | 1354.5 | 1350.9 | 1471.7 | 1374.9 | 1443 | 1315.8 | 1325.6 | 1304 | 1461.8 | 1344.6 | 1416.6 | 1448.1 | 1445 | 1444.1 | 1438.7 | 1451.4 | 1383.4 | 1335.4 | 1351.9 | 1405.4 | 1293 | 1324 | 1258 | 1313 | 1345 | 1271 | 1102 | 1336 |  |  | 1188 | 932 | 1319 |  | 1424 | 1278 | 1315 | 1280 | 1308 | 1310 | 1324 | 1333 | 1323 | 1335.3 | 1317 | 1325 | 1475 | 1504 | 1216 | 1177 | 1026 | 897.1 | 1016 | 1131 | 1354 | 1474 | 1423 | 1432.1 | 1353.5 | 1465.9 | 1478 | 1462 | 1296 | 1366 | 1256 | 1350 | 1273 |  | 1875 | 1421.8 | 537 | 1320 | 1287 |  |  | 1278 | 1401 | 1370 | 1266 | 1181 | 36.28 | 44.75 | 2.4 | 6.5 |  | 6.76 | 6.25 |  |  | 85437787.569 | 282335.674 | 58448978.722 | 61998.792 | 86213949.856 | 187445.043 | 62538374.165 | 56181.87 | 323746300.695 | 85241.968 | 88983.576 | 63.118 | 85309.405 | 60.749 | 88430.233 | 63.571 | 69261.103 | 70.757 | 331724.974 | 160.849 | 174169.114 | 331564.125 | 12.7667 | 6.76 | 6.25 | 36.28 | 44.75 | 2.4 | 6.5 | 333824.3
2025-05-26 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:14 | 18:31 | 1120.8 | 1087.1 | 1051.2 | 1046.4 | 1081.8 | 1042.9 | 1041.2 | 1043.8 | 1081.4 | 1088 | 1061.3 | 1056 | 1041.4 | 979.4 | 1037.6 | 1037.9 | 990.2 | 1030.2 | 1119.5 | 1121 | 1040.7 | 1043.8 | 1144.9 | 1176.4 | 1134.3 | 1125.7 | 1116.1 | 1155 | 1172.6 | 1151.8 | 1152.5 | 1162.8 | 968.8 | 1271.8 | 1009.5 | 1155.4 | 1041.7 | 1014.3 | 1030.4 | 1049.9 | 1025.7 | 1010.7 | 1033.9 | 1013.7 | 1032.2 | 1041.2 | 1122.8 | 1028.5 | 1066.6 | 1049.6 | 1014.1 | 1035.1 | 1186.5 | 1166.9 | 1112.7 | 1176.4 | 1176.3 | 1049.6 | 1163.8 | 1135 | 1044.8 | 1181.2 | 1035.9 | 1018 | 1121 | 1111 | 1126.6 | 1085.3 | 1028.8 | 1021.6 | 1030.8 | 1028.1 | 1051.2 | 1034.6 | 1170.7 | 1150.9 | 1173.5 | 1029.7 | 1017.4 | 1125 | 1036.6 | 1039.3 | 1028.3 | 1041.2 | 1026.8 | 1032.3 | 1044.9 | 1034.4 | 1027.8 | 1017 | 1066.2 | 1091.2 | 1055.4 | 1045.7 | 1156.2 | 1018 | 1013.7 | 1040.9 | 1025.4 | 1031.3 | 1058.1 | 1025.9 | 1044.6 | 1023.4 | 1170.1 | 1039.5 | 1226.2 | 1149.7 | 1041.9 | 1154.5 | 1120.3 | 1107.8 | 1170 | 1160.1 | 1033.7 | 1019.7 | 1145.9 | 1161.3 | 1154 | 1038.3 | 1054.7 | 1121.6 | 1090.7 | 1039.2 | 1045.4 | 1183 | 1009 | 1011.6 | 1166.8 | 1152.3 | 1110.8 | 1116.4 | 1113 | 952.5 | 1170.1 | 1088.4 | 1124.6 | 1118.5 | 1100.8 | 1039.3 | 1098.8 | 1101.5 | 1032.7 | 1133.36 | 1008.1 | 1097.9 | 1027.7 | 958.6 | 1066.5 | 1126.6 | 1130.3 | 1036 | 1184.9 | 1038.5 | 1022.8 | 1015.3 | 1025.5 | 1019.4 | 1018.1 | 988.5 | 1142.9 | 1011.9 | 1112.8 | 1121.2 | 1122.5 | 1034.7 | 1004.2 | 1151.6 | 1030.7 | 1031.1 | 1043.9 | 1028.6 | 1145.5 | 1064.7 | 1123.1 | 1004.6 | 1012.1 | 997.2 | 1121.2 | 1031.5 | 1080.6 | 1128.2 | 1110.3 | 1106.6 | 1101 | 1118.1 | 1059.8 | 1042.6 | 1037.6 | 1087.8 | 1014.2 | 1005.1 | 1012.1 | 1030 | 1026.4 | 1031.8 | 866.9 | 1054.4 |  |  | 935.5 | 729.4 | 1030.4 |  | 1113.5 | 999.4 | 1034.4 | 869.6 | 1027.7 | 1033.3 | 1039.6 | 1038.3 | 1041.5 | 1060.6 | 1035.1 | 1044.8 | 1164 | 1187.1 | 960.6 | 924.7 | 800.2 | 677 | 769.6 | 883.5 | 1025.9 | 1104.2 | 1050.4 | 1041.3 | 1019.4 | 1055.5 | 1098.2 | 1086.8 | 927.1 | 998.7 | 931.8 | 962.9 | 897 |  | 1450.1 | 1098.4 | 411.5 | 1007.7 | 975.9 |  |  | 1030.1 | 1075.5 | 1063.4 | 993.6 | 920.1 | 32.47 | 39.01 | 3.18 | 8.3 |  | 5.25 | 4.81 |  |  | 85506921.012 | 282398.792 | 58515310.988 | 62059.541 | 86282183.959 | 187508.614 | 62591209.703 | 56252.627 | 324002684.181 | 85402.817 | 69133.443 | 63.118 | 66332.266 | 60.749 | 68234.103 | 63.571 | 52835.538 | 70.757 | 256383.486 | 160.849 | 135341.842 | 256222.637 | 13.2833 | 5.25 | 4.81 | 32.47 | 39.01 | 3.18 | 8.3 | 258237.06
2025-05-27 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:10 | 18:31 | 1358.8 | 1320.4 | 1274 | 1270.6 | 1315.6 | 1266.5 | 1263 | 1270 | 1311.4 | 1321.7 | 1286.2 | 1280.9 | 1266.5 | 1190.4 | 1264 | 1261.4 | 1179.8 | 1154.3 | 1250.9 | 1253.7 | 1168.7 | 1171.8 | 1255.9 | 1316.7 | 1260.4 | 1276.1 | 1267.6 | 1311.2 | 1302 | 1318.8 | 1300.9 | 1310 | 1167.4 | 1529.4 | 1211.3 | 1398.5 | 1251.7 | 1217.1 | 1235.5 | 1261 | 1243 | 1216.3 | 1237.3 | 1211.8 | 1229.6 | 1234.6 | 1341.7 | 1228.3 | 1264.7 | 1265.5 | 1209.6 | 1228.5 | 1415.9 | 1389.8 | 1341.4 | 1427.3 | 1421.7 | 1267.1 | 1407.2 | 1372.4 | 1258.5 | 1422.6 | 1235.6 | 1201.5 | 1340.5 | 1331.7 | 1339.8 | 1314.6 | 1233.2 | 1227.9 | 1224 | 1217.1 | 1261.1 | 1236.4 | 1406.2 | 1384.1 | 1404 | 1233 | 1219.4 | 1330.1 | 1240.4 | 1244.7 | 1225.5 | 1247 | 1226.2 | 1225.1 | 1236.8 | 1228.1 | 1215.1 | 1207.1 | 1265.5 | 1332.5 | 1251.3 | 1248.6 | 1378.3 | 1228.3 | 1225.7 | 1254.7 | 1246.5 | 1246.5 | 1281.7 | 1250.8 | 1276.4 | 1249.4 | 1419.8 | 1257.8 | 1485.2 | 1385.5 | 1255.4 | 1363.7 | 1341.7 | 1323.3 | 1391.4 | 1393.4 | 1247.2 | 1212.6 | 1375.3 | 1375.5 | 1373.8 | 1242.1 | 1265.7 | 1357.5 | 1361.5 | 1254.7 | 1259.6 | 1408.6 | 1145.4 | 1139.9 | 1406 | 1390.7 | 1355.6 | 1359.1 | 1352.8 | 1159.1 | 1437.4 | 1329.7 | 1389.7 | 1377.5 | 1374.5 | 1293.2 | 1339.2 | 1340.7 | 1297.4 | 1405.1 | 1257.1 | 1322.1 | 1264.2 | 1178.9 | 1367.3 | 1380 | 1394.4 | 1273.5 | 1443 | 1272.9 | 1245.9 | 1237.1 | 1239.3 | 1169.5 | 1264.5 | 1255.1 | 1414.3 | 1222.4 | 1398.7 | 1355.7 | 1400.2 | 1260.1 | 1245.5 | 1422.2 | 1277.9 | 1270.7 | 1290 | 1265.7 | 1406.8 | 1311.2 | 1370.2 | 1247.3 | 1245.6 | 1234.4 | 1395.3 | 1277.6 | 1332.5 | 1359.1 | 1392.7 | 1380.3 | 1365.8 | 1352.6 | 1308.5 | 1267.8 | 1244.5 | 1332 | 1216.1 | 1205.1 | 1237.4 | 1240.5 | 1242.1 | 1250.7 | 1049.4 | 1277.7 |  |  | 1121 | 870.3 | 1238.7 |  | 1353 | 1218.1 | 1232.5 | 1223.5 | 1230 | 1232.2 | 1261 | 1247.1 | 1264.2 | 1274.7 | 1254.8 | 1262.6 | 1404.3 | 1429 | 1146 | 1116.8 | 960.4 | 811.1 | 955.1 | 1101.1 | 1293.1 | 1380.9 | 1324.4 | 1321.1 | 1313.5 | 1366 | 1376.1 | 1364.1 | 1190.1 | 1268.1 | 1212.1 | 1223.1 | 1141.1 |  | 1717.8 | 1301.4 | 501.4 | 1212 | 1178.3 |  |  | 1199.1 | 1313.1 | 1275.1 | 1194.1 | 1091.7 | 34.17 | 39.27 | 1.95 | 5.7 |  | 6.45 | 5.98 |  |  | 85588649.621 | 282458.91 | 58594183.415 | 62116.29 | 86365956.86 | 187568.185 | 62655291.274 | 56322.384 | 324310907.99 | 85561.666 | 81728.609 | 60.118 | 78872.427 | 56.749 | 83772.901 | 59.571 | 64081.571 | 69.757 | 308223.809 | 158.849 | 160484.169 | 308064.96 | 13.35 | 6.45 | 5.98 | 34.17 | 39.27 | 1.95 | 5.7 | 311840.2
2025-05-28 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:06 | 18:31 | 1052.8 | 1019.8 | 983.2 | 980.7 | 1016.2 | 978.1 | 981.6 | 981.9 | 1014 | 1017.8 | 1000.4 | 993.2 | 978.5 | 921.5 | 974.5 | 971.2 | 932 | 968.1 | 1046.9 | 1049.2 | 980.2 | 989.5 | 1073.5 | 1104.4 | 1066.9 | 1060.1 | 1052.3 | 1090 | 1103.5 | 1087.6 | 1006.1 | 1097.5 | 851.4 | 1055.6 | 954.8 | 1081.6 | 984.7 | 960.5 | 955.8 | 989.5 | 971.7 | 963.5 | 977.8 | 960.2 | 977.1 | 985.4 | 1060.4 | 979.2 | 1009.9 | 991.7 | 938.5 | 981.3 | 1122.7 | 1103.8 | 1050.5 | 1107.6 | 1109.3 | 986.7 | 1093.8 | 1061.7 | 989.5 | 1113.8 | 977.2 | 951.1 | 1054.4 | 1046.8 | 1061.5 | 1036.8 | 935.1 | 962.1 | 970.2 | 967.6 | 987 | 969 | 1104.8 | 1085.7 | 1105.1 | 971.2 | 955.9 | 1046.1 | 972.8 | 977.2 | 965.3 | 979.6 | 962.9 | 967.3 | 978.9 | 969 | 962.6 | 953.3 | 1001.8 | 1049.9 | 990.9 | 982.8 | 1089.7 | 958.1 | 961.9 | 978.7 | 974.7 | 971.2 | 998.2 | 974.8 | 995.7 | 978.7 | 1116.4 | 986.4 | 1163.4 | 1085.6 | 982.6 | 1083.7 | 1055.8 | 1044.8 | 1096.7 | 1094.9 | 975.8 | 928.8 | 1082.5 | 1091.8 | 1087.4 | 975.4 | 992.6 | 1044.5 | 1013.6 | 977.7 | 984.7 | 1111.6 | 551.7 | 586.4 | 703.7 | 692.8 | 615.2 | 666.6 | 655.8 | 559.8 | 684.9 | 639.8 | 662 | 656.2 | 646.2 | 614.2 | 647.2 | 643.8 | 622.3 | 674 | 603.3 | 639.8 | 617.5 | 580.7 | 678 | 682.9 | 687.2 | 630.5 | 715.8 | 631.8 | 622 | 618.3 | 624.5 | 620.4 | 451.5 | 436.9 | 503 | 436.9 | 508.9 | 482.7 | 516.2 | 444.5 | 445.7 | 506.2 | 457.3 | 452.7 | 462.9 | 455.9 | 501.6 | 471.9 | 472 | 447.8 | 450 | 443.5 | 502.8 | 457.3 | 478.5 | 487.4 | 506.7 | 492.9 | 486 | 483.6 | 468.6 | 454.7 | 437.6 | 477.2 | 935.2 | 915.3 | 881.2 | 956 | 952.9 | 956.1 | 802.2 | 974.6 |  |  | 852 | 643.4 | 946 |  | 1030.7 | 904.1 | 959 | 934.8 | 953.8 | 959.8 | 973.1 | 968.2 | 973.4 | 991.6 | 968.6 | 980 | 1092.7 | 1116.1 | 897 | 868.4 | 750.7 | 631.8 | 692.5 | 813.5 | 985.8 | 1047.1 | 993.9 | 976.5 | 985.5 | 1041.5 | 1044.4 | 1026.3 | 836.2 | 927.7 | 835.8 | 885.5 | 783.4 |  | 1180.5 | 942.8 | 391.3 | 873 | 845.7 |  |  | 962.9 | 978 | 875.9 | 841.5 | 741.5 | 36.79 | 48.09 | 1.97 | 4.9 |  | 6.79 | 6.28 |  |  | 85653541.874 | 282521.028 | 58656363.174 | 62174.039 | 86401496.786 | 187607.756 | 62704410.555 | 56393.141 | 324522533.773 | 85721.515 | 64892.253 | 62.118 | 62179.759 | 57.749 | 35539.926 | 39.571 | 49119.281 | 70.757 | 211625.783 | 159.849 | 126952.145 | 211465.934 | 13.4167 | 6.79 | 6.28 | 36.79 | 48.09 | 1.97 | 4.9 | 212537.6
2025-05-29 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:09 | 18:19 | 1087.9 | 1075.2 | 1015.7 | 1014.6 | 1048.6 | 1009.8 | 1010.7 | 1012.3 | 1045.3 | 1051.3 | 1029.8 | 1022.9 | 1007.6 | 944.7 | 1003.8 | 1000.8 | 1001.3 | 1000.2 | 1077.8 | 1082.1 | 1010.7 | 1007.8 | 1104.6 | 1134.4 | 1100.4 | 1089.8 | 1081 | 1124.3 | 1138.1 | 1135.2 | 1129.1 | 1131.8 | 940 | 1245.8 | 992.9 | 1126.6 | 1017.7 | 998.8 | 1002.5 | 1031.3 | 1012.4 | 1007.9 | 1021.4 | 1004.5 | 1010.5 | 1018 | 1095.4 | 1003.5 | 1045.1 | 1027.6 | 968.6 | 1012.4 | 1158.7 | 1139.9 | 1081.8 | 1126 | 1143.2 | 1017.4 | 1128.8 | 1094.4 | 1026.3 | 1152.5 | 1010.6 | 974.9 | 1097.1 | 1090.1 | 1105.1 | 1080.8 | 1004.7 | 1003.3 | 1010 | 1007.8 | 1027.5 | 1010 | 1166.5 | 1143.3 | 1163.1 | 1023.7 | 999.6 | 1090.9 | 1022.8 | 1022.7 | 1007.8 | 1019.9 | 1005.4 | 1010.7 | 1021.4 | 1012.3 | 1006.4 | 997.4 | 1047.7 | 1088.5 | 1031.4 | 1022.2 | 1137.6 | 998.2 | 1006.5 | 1019.1 | 1018.2 | 1012.5 | 1037.2 | 1016.2 | 1034 | 1017.7 | 1164.3 | 1018.4 | 1199.2 | 1131.3 | 1020.5 | 1126.5 | 1094.6 | 1091.1 | 1147 | 1140.3 | 1015.4 | 962.5 | 1128.3 | 1134.7 | 1130.2 | 1015.4 | 1029 | 1090.5 | 1055.1 | 1014.7 | 1021.2 | 1153.7 | 925.1 | 945.2 | 1059.4 | 1044.4 | 927.8 | 1009.3 | 999.1 | 854.7 | 1048.3 | 977.3 | 1014.2 | 1002.3 | 983.5 | 931.7 | 984.8 | 980.7 | 940.5 | 1017.8 | 901 | 959.1 | 926.4 | 862.6 | 1004.8 | 1011.4 | 1016.5 | 935.7 | 1069.4 | 942 | 931.7 | 922.9 | 935.5 | 931.4 | 110.4 | 108.1 | 123.3 | 106.7 | 123.7 | 121.8 | 123.5 | 115.7 | 107.8 | 121.9 | 105.8 | 113.9 | 111.2 | 114.9 | 122.6 | 115.8 | 120.9 | 108.2 | 105.8 | 107.4 | 124.9 | 106.4 | 117.8 | 123.8 | 110.4 | 119.5 | 116.7 | 118.1 | 113.6 | 112.1 | 113 | 116.9 | 994 | 967 | 921.8 | 1012.2 | 1004.6 | 1011.8 | 847.6 | 1030.6 |  |  | 916.6 | 686.4 | 1001 |  | 976 | 1009.8 | 1009.8 | 980.6 | 1007.3 | 1009.3 | 1027.7 | 1021.5 | 1025.4 | 1042.3 | 1017.6 | 1029.3 | 1148.3 | 1171.9 | 936.8 | 912.2 | 786.1 | 663.4 | 670.5 | 791.7 | 953.2 | 1022.7 | 961.3 | 943.1 | 964.5 | 991.5 | 1019.2 | 955.6 | 855.4 | 907 | 807.7 | 865.3 | 768.4 |  | 1300.2 | 1014.2 | 385.1 | 938.4 | 910.4 |  |  | 1033 | 1052.4 | 885 | 910.9 | 788 | 35.73 | 41.95 | 2.07 | 9.69 |  | 5.38 | 4.87 |  |  | 85720663.674 | 282584.146 | 58721000.481 | 62233.788 | 86435802.361 | 187649.327 | 62755226.617 | 56462.898 | 324739366.519 | 85883.364 | 67121.8 | 63.118 | 64637.307 | 59.749 | 34305.575 | 41.571 | 50816.062 | 69.757 | 216832.746 | 161.849 | 131636.24 | 216670.897 | 13.1667 | 5.38 | 4.87 | 35.73 | 41.95 | 2.07 | 9.69 | 218430.9
2025-05-30 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:12 | 18:13 | 1194.2 | 1189.9 | 1157.9 | 1113.5 | 1171.6 | 1111 | 1108.3 | 1111.7 | 1149 | 1159.6 | 1130.2 | 1124.7 | 1109.3 | 1041.8 | 1106.8 | 1101.8 | 1085.4 | 1100.2 | 1168.3 | 1190.8 | 1111.3 | 1110.7 | 1213.8 | 1246 | 1208.8 | 1199.1 | 1199.1 | 1230.5 | 1231.9 | 1253 | 1259.5 | 1238.1 | 1030.5 | 1360.7 | 1085.3 | 1231.9 | 1123.4 | 1095.4 | 1112.1 | 1129.8 | 1108.5 | 1096.9 | 1114.9 | 1094.4 | 1113 | 1111.4 | 1209.7 | 1140.6 | 1140.6 | 1121.2 | 1089.7 | 1104.7 | 1269.7 | 1249.8 | 1188.7 | 1255.2 | 1252.4 | 1118.3 | 1240.6 | 1208.6 | 1126.1 | 1268.8 | 1104.5 | 1075.2 | 1196.8 | 1189.7 | 1205.4 | 1176.6 | 1096.5 | 1094.1 | 1101.6 | 1098.1 | 1120 | 1101.1 | 1267.2 | 1241.2 | 1265.7 | 1114.2 | 1092.6 | 1182.6 | 1113.4 | 1114.5 | 1096.1 | 1111.4 | 1110.2 | 1104.8 | 1113.2 | 1102.5 | 1096.6 | 1085.7 | 1142.7 | 1185.5 | 1124.1 | 1115.5 | 1241.1 | 1087 | 1092.1 | 1112.3 | 1103.7 | 1104.4 | 1136.2 | 1107.4 | 1131 | 1110.5 | 1271.3 | 1118 | 1314.2 | 1232 | 1117.5 | 1229.7 | 1202.8 | 1188.5 | 1250.8 | 1243.9 | 1107.1 | 1081.6 | 1227.8 | 1246.4 | 1239.2 | 1116 | 1128.6 | 1243.5 | 1289.5 | 1113.2 | 1121.2 | 1266.7 | 1081.1 | 1078.4 | 1258.8 | 1243.6 | 1175.8 | 1203.8 | 1192.5 | 1022.5 | 1254.9 | 1164.1 | 1210.3 | 1173.3 | 1177.5 | 1116.6 | 1176.7 | 1172.2 | 1116.9 | 1213.6 | 1079.9 | 1167.9 | 1105.6 | 1030.3 | 1195.4 | 1208.8 | 1216.7 | 1118.5 | 1283.5 | 1127.6 | 1110.7 | 1097.2 | 1101.5 | 1087.9 | 1071.2 | 1079.6 | 1211.1 | 1064.5 | 1215.8 | 1201.2 | 1195.8 | 1121.5 | 1071.7 | 1203.4 | 1064.5 | 1111.5 | 1108.2 | 1121.5 | 1207.9 | 1169.1 | 1216.5 | 1063.8 | 1069.1 | 1075.5 | 1213.5 | 1078.8 | 1179.5 | 1201.2 | 1197.5 | 1121.7 | 1154.5 | 1220.5 | 1111.8 | 1119.7 | 1108.5 | 1159.4 | 1095.8 | 1079 | 1080.5 | 1111.9 | 1105.5 | 1114 | 931.4 | 1134 |  |  | 1008.2 | 792.1 | 1104.8 |  | 1203.1 | 1069.2 | 1112.5 | 1081.1 | 1107 | 1108.6 | 1127 | 1121.4 | 1124.1 | 1143.6 | 1117 | 1128.8 | 1256.4 | 1279.8 | 1025 | 996.6 | 860 | 724.1 | 845.3 | 981.7 | 1149 | 1243.1 | 1173.1 | 1247 | 1151.4 | 1174.9 | 1234.5 | 1251.5 | 1091.4 | 1134.6 | 1082.7 | 1087.8 | 1027.8 |  | 1475.5 | 1190.6 | 437.5 | 1078.3 | 1050.8 |  |  | 1081 | 1121.7 | 1101.3 | 1043.6 | 997 | 36.45 | 45.55 | 2.33 | 7.9 |  | 5.85 | 5.34 |  |  | 85794428.611 | 282650.264 | 58791589.399 | 62295.537 | 86508783.115 | 187691.898 | 62812737.713 | 56533.655 | 325014163.677 | 86045.213 | 73764.937 | 66.118 | 70588.918 | 61.749 | 72980.754 | 42.571 | 57511.096 | 70.757 | 274797.158 | 161.849 | 144225.988 | 274635.309 | 13.0167 | 5.85 | 5.34 | 36.45 | 45.55 | 2.33 | 7.9 | 277904.9
2025-05-31 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:13 | 18:24 | 1073.4 | 1003 | 1002 | 1000.6 | 1001 | 995.6 | 997.5 | 998.1 | 1031.4 | 1039.6 | 1014.1 | 1009.4 | 995.1 | 937 | 994.4 | 991.1 | 997 | 989.2 | 1068 | 1071.4 | 1008 | 1023.09 | 1098.8 | 1141 | 1099 | 1081.4 | 1071 | 1109.5 | 1129.5 | 1107.8 | 1121.8 | 1117.4 | 944.8 | 1234.4 | 988.6 | 1107.8 | 1006.4 | 980.7 | 995.9 | 1014.1 | 990.1 | 985.8 | 989.8 | 975.5 | 1010.2 | 989.2 | 1096.6 | 993.7 | 1039.9 | 1032.6 | 908.9 | 1010.6 | 1161.2 | 1144.4 | 1070.1 | 1128.3 | 1127.2 | 1003.1 | 1113 | 1009.4 | 1008.3 | 1135.5 | 1005.4 | 961.7 | 1084.1 | 1076.4 | 1092.9 | 1063.1 | 991.9 | 992.7 | 998.8 | 994.3 | 1017.1 | 995.9 | 1157.9 | 1134 | 1156.1 | 1015 | 994.1 | 1062.9 | 1010.3 | 1012.9 | 992.1 | 1008.1 | 1009.6 | 1014.7 | 1010.2 | 998.9 | 992.2 | 981.9 | 1033.4 | 1065.2 | 1018.3 | 1012 | 1123.7 | 985.8 | 992 | 1009.9 | 1001.8 | 1003.3 | 1032.2 | 1005 | 1028.2 | 1007.6 | 1158.2 | 1012.1 | 1119.5 | 1118.1 | 1013.2 | 1103.3 | 1087.1 | 1072.7 | 1114.9 | 1125.3 | 1004.2 | 997.5 | 1112.8 | 1123.3 | 1120.6 | 1006 | 1020.2 | 1113.2 | 1124.1 | 1006.2 | 1014.4 | 1144.9 | 998.9 | 987.1 | 1139.9 | 1120.6 | 1076 | 1084.2 | 1074.2 | 921.2 | 1059.4 | 1050.6 | 1090.4 | 1100.5 | 1060.5 | 1007.2 | 1059.6 | 1060.7 | 1007.3 | 1095.8 | 973.4 | 1035.3 | 1000.5 | 932.8 | 1081.3 | 1093.6 | 1102.5 | 1013 | 1164.3 | 1022.3 | 1006.1 | 994 | 1005.5 | 998 | 989.5 | 980.9 | 1121.2 | 972.6 | 1119.5 | 1125.5 | 1120.1 | 1035.5 | 981.5 | 1118.4 | 991.5 | 1031.5 | 1036.9 | 1034.8 | 1124.5 | 1031.8 | 1021.5 | 992.6 | 989.5 | 981.5 | 1129.6 | 987.5 | 1084.2 | 1116.2 | 1123.1 | 1029.5 | 1081.6 | 1013.8 | 1029.5 | 988.8 | 1026.4 | 1079.5 | 984.9 | 981.2 | 991.5 | 1002.4 | 998.6 | 1001.8 | 840.9 | 1021.7 |  |  | 906.5 | 710.5 | 991.9 |  | 1084.2 | 980.7 | 1011.3 | 980.2 | 1002.9 | 1007.3 | 1023.3 | 1018.9 | 1022.7 | 1033.6 | 1014 | 1024 | 1143 | 1163.8 | 924 | 899 | 774.3 | 656.1 | 769.2 | 879.3 | 1034.5 | 1109.7 | 1066.6 | 1122 | 1031.5 | 1061.4 | 1104.2 | 1112.6 | 950 | 1020.9 | 941.5 | 991 | 926 |  | 1330 | 1067.7 | 414.1 | 995.4 | 938.8 |  |  | 1024.6 | 1040.2 | 1053.7 | 946.8 | 901 | 33.5 | 42 | 3.1 | 8.3 |  | 5.3 | 4.85 |  |  | 85860885.701 | 282715.293 | 58855621.315 | 62358.83 | 86575069.974 | 187741 | 62864610.12 | 56612.761 | 325261923.023 | 86205.025 | 66457.09 | 65.029 | 64031.916 | 63.293 | 66286.859 | 49.102 | 51872.407 | 79.106 | 247759.346 | 159.812 | 130360.684 | 247599.534 | 13.1833 | 5.3 | 4.85 | 33.5 | 42 | 3.1 | 8.3 | 251303.79
2025-06-01 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:14 | 18:33 | 985.3 | 995.1 | 908.1 | 920.9 | 994.5 | 918.2 | 921.1 | 912.5 | 954.2 | 959.4 | 938.8 | 934.2 | 917.9 | 862.9 | 917.1 | 921.5 | 873.6 | 910 | 987.9 | 990.7 | 920.6 | 920.2 | 1007.6 | 1036 | 1006.9 | 997.3 | 988.7 | 1021.7 | 1040.6 | 1023.5 | 1031.7 | 1030.8 | 865.2 | 1139.4 | 902.2 | 1031.9 | 925.6 | 901 | 918.2 | 931.6 | 913.1 | 907.3 | 920.6 | 832.1 | 918 | 921.7 | 995.5 | 911.5 | 946.7 | 930.7 | 916.6 | 918.9 | 1050 | 1034.8 | 988.2 | 1040.1 | 1042.5 | 927.5 | 1028.5 | 1041.4 | 925.1 | 1046.4 | 918.8 | 892.2 | 987.9 | 980.6 | 996.5 | 971.1 | 905.9 | 901.1 | 909.8 | 905.8 | 927.6 | 911.9 | 1051 | 1030.4 | 1045.5 | 916.1 | 906 | 985.3 | 920 | 922.1 | 909.2 | 921.2 | 911.5 | 913.5 | 920 | 912.1 | 905.3 | 916.9 | 942.7 | 990.8 | 929.8 | 922.3 | 1023 | 900.1 | 903.5 | 915.8 | 909.4 | 908.5 | 933.4 | 908.6 | 927.8 | 910.6 | 1047.7 | 912.8 | 1090.1 | 1017.1 | 917.7 | 1014.6 | 981.8 | 983.2 | 1029 | 1024.6 | 911.3 | 915.5 | 1015 | 1017.6 | 1014.6 | 912.3 | 927 | 1019.1 | 1025.5 | 910.9 | 916.4 | 1021.5 | 901.4 | 909.9 | 1029.3 | 1018.7 | 907.2 | 989.5 | 985.7 | 843.6 | 1036 | 1041.4 | 1031.8 | 1038.5 | 973 | 926.5 | 1042 | 1036.6 | 921.2 | 1003.7 | 887.9 | 948.2 | 914 | 850.2 | 981.8 | 994.7 | 998.7 | 912.3 | 1040.7 | 915.7 | 921.6 | 911.6 | 909.6 | 917.5 | 887.5 | 891.2 | 1027.5 | 892.3 | 1031.3 | 1029.5 | 1025.6 | 919.5 | 889.5 | 1021.5 | 885.5 | 920.1 | 911.5 | 915.7 | 1030.6 | 915.4 | 1021.5 | 891.1 | 886.4 | 890.7 | 1024.4 | 888.1 | 957.6 | 1019.5 | 1028.3 | 916.4 | 966.3 | 1024.4 | 920.4 | 923.5 | 921.4 | 964.5 | 901.5 | 911.2 | 907.5 | 916.6 | 907.8 | 676.5 | 769.2 | 929 |  |  | 820.9 | 621.7 | 907.7 |  | 993.4 | 878 | 918 | 892.5 | 913.6 | 914.6 | 925.3 | 920.9 | 925.2 | 936.2 | 920.7 | 930.2 | 1037.4 | 1056.8 | 849.7 | 827.8 | 710.6 | 601.2 | 717.4 | 808.4 | 943.4 | 1017.8 | 983.7 | 962.4 | 935.5 | 989.7 | 1010.7 | 1116.3 | 860.9 | 929.5 | 869.2 | 926.7 | 868.5 |  | 1238.4 | 965.1 | 424.5 | 897.9 | 873.4 |  |  | 906.6 | 950.9 | 911.7 | 856.9 | 815.3 | 31.9 | 40.8 | 3.4 | 6.2 |  | 4.91 | 4.4 |  |  | 85922250.649 | 282756.322 | 58914133.54 | 62411.123 | 86636539.254 | 187780.102 | 62911708.9 | 56689.867 | 325491068.834 | 86361.837 | 61364.948 | 41.029 | 58512.225 | 52.293 | 61469.28 | 39.102 | 47098.78 | 77.106 | 229145.811 | 156.812 | 119783.851 | 228988.999 | 13.3167 | 4.91 | 4.4 | 31.9 | 40.8 | 3.4 | 6.2 | 229035.1
2025-06-02 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:15 | 17:56 | 1020.1 | 1026 | 984.9 | 1026 | 1098.5 | 1016.8 | 1014.6 | 932.7 | 1051.5 | 1057.3 | 1034.1 | 1030 | 1013.7 | 952.5 | 1012.5 | 1006.2 | 963.1 | 1004.7 | 1091.6 | 1092.3 | 1016.1 | 1016.4 | 1110.6 | 1144.6 | 1111.2 | 1100.8 | 1093.6 | 1130.8 | 1153.3 | 1130 | 1155.5 | 1145.5 | 1005.2 | 1154.5 | 1050.2 | 1182.9 | 1054 | 1024.5 | 1043 | 1056.2 | 1038.1 | 1030.5 | 1047.4 | 1041.2 | 1042.3 | 1049 | 1130.8 | 1035.8 | 1078.3 | 1058.6 | 1041.5 | 1044.4 | 1194.9 | 1177.3 | 1123.6 | 1199 | 1185 | 1054.3 | 1169.4 | 1185.9 | 1050.7 | 1193.2 | 1037.1 | 1021.1 | 1166.8 | 1161.2 | 1170 | 1141.6 | 1069.2 | 1067.6 | 1071.8 | 1066.7 | 1084 | 1066.3 | 1207.5 | 1187 | 1210.7 | 1066.2 | 1056.8 | 1141.7 | 1025.9 | 1076.3 | 1061.3 | 1077.6 | 1060.3 | 1062.6 | 1071.2 | 1060.6 | 1062.8 | 1052 | 1108 | 1168.09 | 1083.1 | 1075.4 | 1203 | 1055.7 | 1054.3 | 1078.3 | 1062.2 | 1070 | 1097.8 | 1065.4 | 1087.1 | 1064 | 1215.6 | 1077.7 | 1265 | 1188 | 1080.5 | 1183.4 | 1160.7 | 1140.5 | 1196.1 | 1196.7 | 1073.3 | 1027.4 | 1181.2 | 1199.9 | 1198.7 | 1077.6 | 1089.3 | 1148.2 | 1144.3 | 1073.1 | 1083.3 | 1217.5 | 903.2 | 917.7 | 1145.5 | 1132 | 1008.7 | 1097.7 | 1094.5 | 938.1 | 1155 | 1075.2 | 1114.9 | 1021.3 | 1093 | 1034.9 | 1081.6 | 1078.5 | 1028.1 | 1119.9 | 996.1 | 1061.3 | 1019.5 | 946.8 | 1092.3 | 1106.8 | 1114.3 | 1019.2 | 1167.1 | 1024.6 | 1006 | 1005 | 1010.5 | 1006.4 | 960.3 | 944.4 | 1090.2 | 951.1 | 1100.1 | 1109.1 | 1101.6 | 965.6 | 954.6 | 1111.8 | 960.6 | 969.3 | 965.6 | 967.1 | 1090.1 | 992.1 | 1109.1 | 948.8 | 957.2 | 953.3 | 1101.4 | 955.1 | 1070.7 | 1101.1 | 1111.9 | 971.2 | 1067.1 | 1107.8 | 1000.1 | 1001.1 | 1011.2 | 1069.1 | 1054.4 | 1050.3 | 1055.2 | 1068.9 | 1064.1 | 1059.9 | 900 | 1083.8 |  |  | 960.1 | 723.8 | 1060 |  | 1144.2 | 1019.3 | 1075.3 | 1071.1 | 1068.9 | 1070.8 | 1083.1 | 1079.7 | 1083.8 | 1095.4 | 1076.4 | 1086.7 | 1250.5 | 1221.7 | 980 | 955.8 | 823.3 | 694.4 | 841.2 | 961.5 | 1119.3 | 1191.7 | 1122 | 1121.1 | 1105.5 | 1134.5 | 1171.7 | 1182.8 | 1008.4 | 1100.7 | 996 | 1052.3 | 985.5 |  | 1400.5 | 1097.4 | 484.3 | 1021.1 | 991.1 |  |  | 1079.8 | 1091.7 | 1090.1 | 1018.9 | 912.1 | 32.2 | 41.3 | 3.2 | 4.8 |  | 5.82 | 5.25 |  |  | 85990477.919 | 282794.351 | 58982150.982 | 62461.416 | 86703331.58 | 187817.204 | 62966455.413 | 56765.973 | 325748697.178 | 86518.649 | 68227.27 | 38.029 | 68017.442 | 50.293 | 66792.326 | 37.102 | 54746.513 | 76.106 | 257628.344 | 156.812 | 136156.39 | 257471.532 | 12.6833 | 5.82 | 5.25 | 32.2 | 41.3 | 3.2 | 4.8 | 259288.99
2025-06-03 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:19 | 18:33 | 891.8 | 902.2 | 825.3 | 977.8 | 1052.6 | 976.4 | 976.5 | 924.2 | 1010.1 | 1016.3 | 992.7 | 988.2 | 971.4 | 912.8 | 971.3 | 966.6 | 922.9 | 961.3 | 1039.7 | 1043.5 | 972.5 | 973.6 | 1066.8 | 1095.1 | 1060.1 | 1051.7 | 1044.5 | 1082.6 | 1094.4 | 1081.4 | 1101.5 | 1105.5 | 726.3 | 831.2 | 853.5 | 959 | 857.9 | 837.3 | 853.8 | 866.4 | 846.6 | 840 | 857.6 | 860.5 | 855.5 | 860.8 | 928.3 | 834.5 | 885.5 | 870.1 | 857.7 | 867.8 | 980.4 | 966.6 | 922.2 | 975.7 | 972.3 | 866 | 956.7 | 967.3 | 859.7 | 971.7 | 852.2 | 835 | 1061.7 | 1056.6 | 1064.3 | 1040.5 | 980.5 | 980.3 | 991.2 | 986.2 | 1007.6 | 978.7 | 1105.3 | 1084.2 | 1115.9 | 986.6 | 980 | 1042.7 | 955.1 | 999.2 | 987.7 | 1002.3 | 990.2 | 993.4 | 999.2 | 991.7 | 984.96 | 975.3 | 1012 | 1045.5 | 1004.8 | 1001.3 | 1099.2 | 995.5 | 980.2 | 996.8 | 982.6 | 989.5 | 1013.3 | 987.1 | 1003.1 | 983.8 | 1110.4 | 994.9 | 1148.6 | 1087.8 | 996 | 1074.9 | 1065.3 | 982.9 | 1088.9 | 1098.9 | 993.4 | 934.5 | 1077.8 | 1094.1 | 1093.9 | 993.4 | 1000.1 | 1045.6 | 1030.3 | 990.8 | 1001.1 | 1112 | 812.2 | 817.2 | 918.6 | 905.9 | 839.4 | 875.6 | 870.9 | 749 | 917.6 | 857.1 | 887.7 | 810.5 | 863.1 | 820 | 862 | 762.7 | 816.9 | 889.6 | 784.4 | 872.9 | 810.1 | 673 | 871.6 | 881.4 | 887.9 | 814.6 | 930.1 | 818.4 | 836 | 814.6 | 820.5 | 821.4 | 935.5 | 929.5 | 1035.5 | 933.4 | 1031.5 | 1039.4 | 1021.5 | 975.8 | 940.5 | 1045.5 | 920.2 | 970.5 | 974.5 | 971.4 | 1034.4 | 969.1 | 1044.5 | 931.9 | 939.4 | 945.1 | 1047.5 | 933.5 | 999.5 | 1041.5 | 1037.1 | 1020.4 | 987.1 | 1045 | 965.5 | 983.7 | 971.5 | 999 | 953.3 | 940.2 | 820 | 965.4 | 962.9 | 841.5 | 816 | 979.2 |  |  | 856.3 | 662.3 | 960.4 |  | 1038.7 | 932.7 | 989.5 | 928.4 | 985.9 | 987.4 | 999 | 996.7 | 999.8 | 998.7 | 994.9 | 1000 | 1103.8 | 1122.4 | 882.4 | 866.4 | 744.8 | 625.1 | 724.2 | 849.5 | 1014.7 | 1082.8 | 1027.1 | 1005.2 | 1021.5 | 1045.5 | 1076.1 | 1021.1 | 869.4 | 977.9 | 867.1 | 931.6 | 838.4 |  | 1270.2 | 976.5 | 401.1 | 918.1 | 883 |  |  | 1002.9 | 994.3 | 980.6 | 881.8 | 831.2 | 32.1 | 40.8 | 2.8 | 7.1 |  | 5.12 | 4.62 |  |  | 86050319.559 | 282835.659 | 59044847.468 | 62500.709 | 86761490.088 | 187849.235 | 63016997.599 | 56840.709 | 325979691.535 | 86675.461 | 59841.64 | 41.308 | 62696.486 | 39.293 | 58158.508 | 32.031 | 50542.186 | 74.736 | 230994.357 | 156.812 | 122457.525 | 230837.545 | 13.2333 | 5.12 | 4.62 | 32.1 | 40.8 | 2.8 | 7.1 | 231929.06
2025-06-04 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:10 | 18:33 | 1193.4 | 1204.8 | 1072 | 1113.2 | 1198.9 | 1113.2 | 1115.2 | 1066.5 | 1157.3 | 1160.4 | 1138.8 | 1135.5 | 1116 | 1053.6 | 1116 | 1112.8 | 1067.3 | 1095.5 | 1198.3 | 1197.9 | 1113.6 | 1074.4 | 1226.6 | 1260.3 | 1210.6 | 1203.9 | 1194.6 | 1234.3 | 1256.6 | 1229.4 | 1245.5 | 1239.5 | 1031.4 | 1290.7 | 1061.2 | 1208.4 | 1084.5 | 1066.1 | 1076 | 1096.3 | 1064.4 | 1063.1 | 1079.5 | 1071.1 | 1077.5 | 1085.6 | 1172.5 | 1071.1 | 1114 | 1115.1 | 1082.2 | 1069.9 | 1240.8 | 1220.7 | 1166.7 | 1230.2 | 1233.4 | 1100 | 1219.7 | 1236.5 | 1087.7 | 1231.4 | 1069.1 | 993.2 | 1191.5 | 1183.1 | 1198.7 | 1168.5 | 1094.1 | 1086.1 | 1096 | 1092.4 | 1114.9 | 1098.5 | 1252.1 | 1230.4 | 1250.9 | 1099.5 | 1087.2 | 1197.9 | 1071.1 | 1107.7 | 1096.4 | 1110.6 | 1096 | 1098.2 | 1107.1 | 1098.3 | 1087.1 | 1075.5 | 1136.7 | 1214.5 | 1121.4 | 1109.2 | 1231.9 | 1078.5 | 1078.4 | 1108.4 | 1087.9 | 1096.2 | 1126.5 | 1091.4 | 1110.3 | 1079.5 | 1247.2 | 1107.8 | 1311.7 | 1224.1 | 1110.1 | 1230.8 | 1197.5 | 1178.4 | 1244.1 | 1238.1 | 1100.7 | 1100.5 | 1221 | 1246.9 | 1238 | 1106.3 | 1120.9 | 1244.2 | 1241.5 | 1104.9 | 1112.5 | 1261.6 | 1082.2 | 1088.8 | 1233.7 | 1215.1 | 1133.1 | 1177.1 | 1171.6 | 1003.8 | 1235.5 | 1147 | 1188.4 | 1109.1 | 1162.2 | 1099.4 | 1157.3 | 1153.7 | 1090.9 | 1193.1 | 1063.8 | 1211.5 | 1084.1 | 1008.7 | 1172.9 | 1184.6 | 1195.5 | 1094.9 | 1254.8 | 1099.7 | 1079.5 | 1069.7 | 1078.5 | 1037.5 | 1064.5 | 1069.5 | 1201.2 | 1071.5 | 1188.1 | 1181.5 | 1193.1 | 1109.2 | 1074.5 | 1189.3 | 1077.5 | 1111.8 | 1107.5 | 1109.4 | 1181.6 | 1109.5 | 1185.2 | 1079.5 | 1074.6 | 1081.6 | 1189.9 | 1069.5 | 1149.5 | 1188.2 | 1196.2 | 1104.5 | 1145.8 | 1191.2 | 1104.6 | 1109.4 | 1111.9 | 1141.4 | 1075.5 | 1083.2 | 1078.1 | 1090.3 | 1088.5 | 1094.4 | 920.9 | 1115 |  |  | 981.8 | 781.1 | 1094.5 |  | 1180.4 | 1071.2 | 1101.9 | 977.2 | 1089 | 1097.7 | 1105.4 | 1104.2 | 1107 | 1125.2 | 1104.8 | 1109.8 | 1240.7 | 1263.4 | 1020.7 | 989.4 | 850.9 | 717.9 | 852.1 | 981.2 | 1132.9 | 1216.6 | 1165.6 | 1169.2 | 1142.5 | 1174.5 | 1208.1 | 1201 | 1055.6 | 1123.2 | 1032.1 | 1071.2 | 1001.2 |  | 1455.5 | 1168 | 447.2 | 1079.2 | 1032.1 |  |  | 1123.2 | 1140.1 | 1140.1 | 1044.3 | 984.2 | 36.4 | 48 | 3.1 | 6.3 |  | 5.74 | 5.18 |  |  | 86122985.268 | 282856.967 | 59115455.755 | 62524.002 | 86834246.849 | 187871.266 | 63073854.344 | 56919.445 | 326252327.595 | 86832.273 | 72665.709 | 21.308 | 70608.287 | 23.293 | 72756.761 | 22.031 | 56856.745 | 78.736 | 272636.06 | 156.812 | 143229.395 | 272479.248 | 13.3833 | 5.74 | 5.18 | 36.4 | 48 | 3.1 | 6.3 | 273632.5
2025-06-05 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:06 | 18:36 | 1276 | 1349 | 1245 | 1245 | 1343 | 1247 | 1253 | 1228 | 1294 | 1299 | 1278 | 1272 | 1250 | 1176 | 1252 | 1244 | 1191 | 1236 | 1352 | 1351 | 1254 | 1205 | 1320 | 1416 | 1367 | 1355 | 1346 | 1391 | 1413 | 1382 | 1254 | 1289 | 1213 | 1449 | 1212 | 1422 | 1247 | 1240 | 1257 | 1278 | 1254 | 1244 | 1261 | 1138 | 1259 | 1271 | 1368 | 1197 | 1303 | 1281 | 1261 | 1213 | 1446 | 1427 | 1358 | 1432 | 1438 | 1280 | 1420 | 1440 | 1213 | 1367 | 1254 | 958 | 1421 | 1395 | 1433 | 1311 | 1311 | 1298 | 1318 | 1316 | 1338 | 1309 | 1500 | 1465 | 1493 | 1278 | 1253 | 1397 | 1319 | 1314 | 1304 | 1380 | 1313 | 1301 | 1328 | 1319 | 1315 | 1308 | 1359 | 1347 | 1348 | 1341 | 1325 | 1157 | 1286 | 1317 | 1298 | 1305 | 1340 | 1303 | 1325 | 1293 | 1474 | 1321 | 1538 | 1445 | 1318 | 1441 | 1422 | 1298 | 1457 | 1465 | 1310 | 1190 | 1438 | 1478 | 1469 | 1316 | 1328 | 1400 | 1376 | 1312 | 1324 | 1253 | 1105 | 1124 | 1401 | 1383 | 1285 | 1340 | 1334 | 1142 | 1402 | 1289 | 1337 | 1221 | 1307 | 1248 | 1319 | 1301 | 1241 | 1357 | 1207 | 1332 | 1238 | 1153 | 1337 | 1352 | 1362 | 1249 | 1430 | 1255 | 1232 | 1221 | 1254 | 1223 | 1310 | 1270 | 1458 | 1264 | 1437 | 1411 | 1449 | 1350 | 1243 | 1428 | 1303 | 1302 | 1325 | 1358 | 1418 | 1328 | 1416 | 1292 | 1306 | 1273 | 1439 | 1325 | 1398 | 1412 | 1475 | 1365 | 1415 | 1425 | 1365 | 1365 | 1319 | 1412 | 1266 | 1277 | 1248 | 1280 | 1270 | 1283 | 1066 | 1300 |  |  | 1131 | 898 | 1264 |  | 1353 | 1298 | 1320 | 1283 | 1310 | 1307 | 1326 | 1325 | 1326 | 1334 | 1318 | 1319 | 1468 | 1495 | 1190 | 1161 | 903 | 825 | 965 | 1132 | 1360 | 1457 | 1404 | 1362 | 1294 | 1377 | 1447 | 1392 | 1230 | 1297 | 1198 | 1298 | 1210 |  | 1698 | 1357 | 488 | 1298 | 1359 |  |  | 1341 | 1184 | 1310 | 1198 | 1122 | 36.8 | 52.03 | 3.2 | 8.3 |  | 6.7 | 6.3 |  |  | 86205731.344 | 282896.231 | 59198310.589 | 62568.023 | 86917129.675 | 187898.132 | 63141168.652 | 56991.445 | 326567840.292 | 86987.148 | 82746.076 | 39.264 | 82854.834 | 44.021 | 82882.826 | 26.866 | 67314.308 | 72 | 315512.697 | 154.875 | 165517.625 | 315357.822 | 13.5 | 6.7 | 6.3 | 36.8 | 52.03 | 3.2 | 8.3 | 317965
2025-06-06 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:09 | 18:36 | 1375 | 1406 | 1249 | 1299 | 1395 | 1296 | 1296 | 1191 | 1344 | 1351 | 1318 | 1312 | 1292 | 1216 | 1292 | 1287 | 1228 | 1277 | 1388 | 1388 | 1291 | 1242 | 1365 | 1458 | 1404 | 1391 | 1383 | 1433 | 1452 | 1428 | 1270 | 1332 | 1232 | 1578 | 1231 | 1446 | 1294 | 1263 | 1282 | 1301 | 1278 | 1269 | 1286 | 1154 | 1281 | 1293 | 1390 | 1220 | 1279 | 1262 | 1290 | 1236 | 1472 | 1450 | 1384 | 1465 | 1463 | 1300 | 1441 | 1457 | 1297 | 1461 | 1268 | 968 | 1398 | 1387 | 1389 | 1278 | 1287 | 1250 | 1265 | 1289 | 1290 | 1290 | 1423 | 1387 | 1403 | 1250 | 1207 | 1308 | 1209 | 1278 | 1289 | 1209 | 1267 | 1290 | 1265 | 1293 | 1245 | 1246 | 1301 | 1296 | 1291 | 1295 | 1308 | 1152 | 1250 | 1295 | 1280 | 1285 | 1320 | 1283 | 1309 | 1281 | 1471 | 1301 | 1538 | 1438 | 1300 | 1421 | 1407 | 1376 | 1440 | 1450 | 1285 | 1164 | 1433 | 1462 | 1456 | 1299 | 1312 | 1400 | 1359 | 1295 | 1305 | 1298 | 1149 | 1168 | 1456 | 1437 | 1336 | 1395 | 1389 | 1189 | 1465 | 1355 | 1406 | 1287 | 1376 | 1311 | 1374 | 1354 | 1304 | 1419 | 1269 | 1438 | 1291 | 1198 | 1392 | 1407 | 1416 | 1299 | 1489 | 1305 | 1282 | 1269 | 1300 | 1275 | 1298 | 1239 | 1443 | 1257 | 1429 | 1401 | 1412 | 1348 | 1221 | 1413 | 1278 | 1290 | 1302 | 1340 | 1398 | 1302 | 1421 | 1278 | 1301 | 1257 | 1401 | 1313 | 1378 | 1401 | 1460 | 1368 | 1402 | 1411 | 1378 | 1360 | 1311 | 1419 | 1285 | 1256 | 1241 | 1267 | 1269 | 1278 | 1082 | 1298 |  |  | 1151 | 912 | 1284 |  | 1395 | 1303 | 1301 | 1272 | 1289 | 1295 | 1303 | 1300 | 1303 | 1321 | 1301 | 1303 | 1456 | 1485 | 1192 | 1164 | 978 | 780 | 978 | 1152 | 1339 | 1444 | 1379 | 1389 | 1310 | 1391 | 1434 | 1398 | 1247 | 1310 | 1228 | 1289 | 1191 |  | 1678 | 1398 | 481 | 1287 | 1212 |  |  | 1173 | 1210 | 1270 | 1178 | 1108 | 30.8 | 50.3 | 31.1 | 8.5 |  | 6.6 | 6.32 |  |  | 86290534.396 | 282928.059 | 59280165.923 | 62601.116 | 87002384.052 | 187939.878 | 63207771.983 | 57066.456 | 326886109.748 | 87143.419 | 84803.052 | 31.828 | 81855.334 | 33.093 | 85254.377 | 41.746 | 66603.331 | 75.011 | 318269.456 | 156.271 | 166593.465 | 318113.185 | 13.45 | 6.6 | 6.32 | 30.8 | 50.3 | 31.1 | 8.5 | 319248
2025-06-07 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:07 | 18:36 | 1464 | 1500 | 1332 | 1388 | 1487 | 1381 | 1381 | 1275 | 1428 | 1435 | 1405 | 1396 | 1377 | 1296 | 1374 | 1370 | 1308 | 1361 | 1475 | 1480 | 1379 | 1323 | 1459 | 1556 | 1501 | 1484 | 1477 | 1532 | 1546 | 1526 | 1310 | 1424 | 1363 | 1678 | 1307 | 1533 | 1372 | 1343 | 1363 | 1388 | 1363 | 1348 | 1371 | 1243 | 1374 | 1382 | 1489 | 1306 | 1359 | 1343 | 1373 | 1316 | 1571 | 1548 | 1470 | 1562 | 1557 | 1383 | 1532 | 1549 | 1380 | 1552 | 1363 | 1100 | 1455 | 1435 | 1442 | 1369 | 1327 | 1324 | 1331 | 1325 | 1338 | 1328 | 1500 | 1475 | 1490 | 1328 | 1289 | 1397 | 1319 | 1378 | 1352 | 1308 | 1345 | 1342 | 1328 | 1344 | 1332 | 1329 | 1385 | 1463 | 1348 | 1341 | 1410 | 1240 | 1353 | 1381 | 1365 | 1371 | 1407 | 1369 | 1392 | 1360 | 1561 | 1382 | 1609 | 1531 | 1388 | 1502 | 1502 | 1445 | 1506 | 1544 | 1378 | 1250 | 1524 | 1549 | 1539 | 1384 | 1402 | 1502 | 1458 | 1381 | 1390 | 1385 | 1221 | 1240 | 1549 | 1527 | 1417 | 1479 | 1477 | 1267 | 1548 | 1444 | 1497 | 1369 | 1449 | 1374 | 1458 | 1423 | 1385 | 1501 | 1341 | 1467 | 1360 | 1266 | 1476 | 1489 | 1501 | 1376 | 1572 | 1383 | 1363 | 1350 | 1390 | 1357 | 1378 | 1322 | 1578 | 1363 | 1588 | 1563 | 1510 | 1498 | 1363 | 1563 | 1478 | 1410 | 1408 | 1478 | 1510 | 1398 | 1508 | 1398 | 1408 | 1363 | 1563 | 1410 | 1478 | 1498 | 1563 | 1463 | 1502 | 1503 | 1498 | 1478 | 1498 | 1510 | 1360 | 1350 | 1334 | 1368 | 1365 | 1371 | 1159 | 1399 |  |  | 1229 | 998 | 1365 |  | 1487 | 1385 | 1381 | 1342 | 1374 | 1387 | 1390 | 1388 | 1391 | 1406 | 1393 | 1400 | 1560 | 1591 | 1272 | 1245 | 998 | 1010 | 1068 | 1342 | 1420 | 1506 | 1445 | 1455 | 1391 | 1480 | 1520 | 1503 | 1300 | 1394 | 1319 | 1392 | 1298 |  | 1785 | 1487 | 520 | 1332 | 1297 |  |  | 1198 | 1305 | 1364 | 1261 | 1219 | 31.9 | 52.8 | 3.9 | 6.4 |  | 6.98 | 6.78 |  |  | 86380975.695 | 282973 | 59366988.104 | 62645 | 87093065.921 | 187994.148 | 63278498.708 | 57141 | 327224555.014 | 87299.1 | 90441.299 | 44.941 | 86822.181 | 43.884 | 90681.869 | 54.27 | 70726.725 | 74.544 | 338445.266 | 155.681 | 177174.655 | 338289.585 | 13.4833 | 6.98 | 6.78 | 31.9 | 52.8 | 3.9 | 6.4 | 340883
2025-06-08 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:08 | 18:36 | 1418.2 | 1451 | 1308.4 | 1342.1 | 1441.1 | 1338.1 | 1338.8 | 1342 | 1384.4 | 1392 | 1308.9 | 1357 | 1335.3 | 1257.1 | 1336.3 | 1330 | 1298.4 | 1323.7 | 1439.1 | 1439.6 | 1341 | 1311.1 | 1412.6 | 1508.9 | 1460 | 1442.4 | 1435.8 | 1486.6 | 1505.9 | 1481.3 | 1405.2 | 1441.5 | 1271.2 | 1634.2 | 1301.3 | 1493.2 | 1337.8 | 1305.9 | 1333.9 | 1349.1 | 1323.8 | 1312.2 | 1337.6 | 1325.8 | 1345.6 | 1348.7 | 1456 | 1329.6 | 1379.8 | 1356.8 | 1344 | 1344.6 | 1539.3 | 1516.9 | 1429.2 | 1513.5 | 1511.3 | 1345 | 1491.96 | 1509.9 | 1342.5 | 1513.8 | 1283.6 | 1293.7 | 1442.2 | 1433.2 | 1453.7 | 1412.2 | 1322.3 | 1331.2 | 1338.9 | 1333 | 1363.5 | 1319.8 | 1522.5 | 1490.1 | 1517 | 1337.1 | 1321.1 | 1424.8 | 1341.1 | 1346.6 | 1329.6 | 1348.2 | 1343.2 | 1346.2 | 1349.8 | 1257 | 1327.3 | 1311.6 | 1374.5 | 1412.4 | 1367.6 | 1368.6 | 1493.5 | 1261.2 | 1314.2 | 1341.4 | 1324.6 | 1330.4 | 1364.8 | 1328.4 | 1352.7 | 1321.5 | 1519.2 | 1342.7 | 1577.8 | 1480.4 | 1346.1 | 1465.4 | 1450.2 | 1403.8 | 1472.4 | 1499.6 | 1338.1 | 1269.9 | 1484.9 | 1506.4 | 1497.7 | 1343.9 | 1358.4 | 1491.5 | 1498.5 | 1338.7 | 1347.4 | 1501.5 | 1194.7 | 1215.4 | 1511.7 | 1489.6 | 1401 | 1441.2 | 1436.8 | 1232.9 | 1516 | 1411.4 | 1458.2 | 1343.1 | 1416.6 | 1344.2 | 1421.1 | 1401 | 1351.1 | 1463.4 | 1311.5 | 1431.3 | 1327.7 | 1234.4 | 1435.8 | 1448.3 | 1462.5 | 1341.8 | 1531.5 | 1345.4 | 1325.2 | 1312.9 | 1324.5 | 1335.4 | 1311.1 | 1315.4 | 1484.4 | 1312.5 | 1487.1 | 1467.5 | 1481.5 | 1501.1 | 1311.5 | 1477 | 1321.5 | 1345.5 | 1349.4 | 1389.4 | 1443.4 | 1341.5 | 1488.4 | 1321.5 | 1319.4 | 1315.9 | 1481.4 | 1324.5 | 1424.8 | 1488.4 | 1496.4 | 1405.5 | 1441.1 | 1496.4 | 1349.5 | 1339.2 | 1342.5 | 1398.4 | 1322.1 | 1318.9 | 1216.23 | 1311.4 | 1323.7 | 1225.4 | 1129.5 | 1356.4 |  |  | 1193.3 | 929.4 | 1328.5 |  | 1467.5 | 1296.5 | 1341.2 | 1314.4 | 1334.6 | 1338.4 | 1349.1 | 1346.6 | 1348.6 | 1365.3 | 1359 | 1363.6 | 1516.2 | 1551 | 1230.1 | 1173.4 | 1006 | 866.2 | 1009.1 | 1171.4 | 1382.1 | 1485.1 | 1413.1 | 1411.1 | 1401.1 | 1434.5 | 1478.1 | 1511.1 | 1298.4 | 1411.1 | 1321.4 | 1375.4 | 1255.4 |  | 1799.4 | 1401 | 495.1 | 1296.4 | 1265.4 |  |  | 1208.4 | 1294.4 | 1323.7 | 1241.1 | 1215.5 | 38.8 | 45.5 | 1.23 | 6.3 |  | 6.9 | 6.38 |  |  | 86469599.092 | 283017.941 | 59451373.583 | 62688.884 | 87181638.97 | 188048.418 | 63347683.734 | 57215.544 | 327555142.666 | 87454.781 | 88623.397 | 44.941 | 84385.479 | 43.884 | 88573.049 | 54.27 | 69185.026 | 74.544 | 330587.652 | 155.681 | 172920.051 | 330431.971 | 13.4667 | 6.9 | 6.38 | 38.8 | 45.5 | 1.23 | 6.3 | 332985.59
2025-06-09 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:08 | 18:36 | 1460.9 | 1473.2 | 1324.6 | 1379.1 | 1477.2 | 1376.3 | 1356.5 | 1364.9 | 1410.8 | 1421.6 | 1383.3 | 1376.6 | 1356 | 1231 | 1354.3 | 1349.2 | 1346.2 | 1344.2 | 1460.8 | 1463.5 | 1360.3 | 1363 | 1462.4 | 1531.8 | 1484 | 1464.9 | 1458.4 | 1511 | 1531.5 | 1504.2 | 1511.1 | 1501.5 | 1283.6 | 1650.7 | 1285.4 | 1511.6 | 1354.6 | 1322.4 | 1342.2 | 1363.8 | 1355.6 | 1325.7 | 1351.1 | 1339 | 1359.8 | 1362.2 | 1472.9 | 1344.5 | 1409.8 | 1388.3 | 1367.5 | 1365.4 | 1531.2 | 1538 | 1458.8 | 1521.1 | 1532.8 | 1363.6 | 1516.6 | 1530.8 | 1361.9 | 1534.9 | 1367.4 | 1307.9 | 1478.2 | 1469 | 1489.3 | 1438 | 1337.4 | 1352.2 | 1360.1 | 1354.5 | 1361 | 1331.6 | 1542.8 | 1512 | 1539.1 | 1352.4 | 1339.1 | 1442.1 | 1357.7 | 1363.8 | 1346.5 | 1363.7 | 1361.2 | 1365.6 | 1367.2 | 1302 | 1345.6 | 1331.6 | 1398.9 | 1431.1 | 1359 | 1374.4 | 1528.4 | 1277.5 | 1331.4 | 1360.6 | 1341.2 | 1350.4 | 1356 | 1347.7 | 1355 | 1340.9 | 1547.1 | 1365.9 | 1501 | 1511.9 | 1366.8 | 1483.3 | 1476.2 | 1431.1 | 1482.6 | 1519.3 | 1356.4 | 1276.5 | 1500.3 | 1531.4 | 1524.5 | 1367.9 | 1382.1 | 1489.3 | 1494.9 | 1361.1 | 1370.5 | 1550.3 | 1317.6 | 1337 | 1529.5 | 1510.7 | 1402.7 | 1461.3 | 1456.9 | 1223 | 1454 | 1425.7 | 1483.6 | 1386.3 | 1421 | 1351 | 1442.4 | 1422.6 | 1373.4 | 1504.2 | 1352.5 | 1472.3 | 1363.7 | 1257.2 | 1460.9 | 1471.4 | 1487.5 | 1362.8 | 1527 | 1367.3 | 1345.6 | 1331.1 | 1344.7 | 1337.9 | 1333.5 | 1332.2 | 1525.5 | 1331.5 | 1531.5 | 1511.1 | 1516.1 | 1384.2 | 1328.1 | 1539.1 | 1334.5 | 1379.4 | 1391.5 | 1386.7 | 1521.8 | 1393.4 | 1501 | 1340.5 | 1323.4 | 1333.6 | 1502 | 1328.4 | 1429.4 | 1497 | 1525.8 | 1389.4 | 1437.8 | 1499 | 1389.4 | 1396.1 | 1384.7 | 1434.8 | 1346.8 | 1342 | 1313.1 | 1337 | 1346.7 | 1356.7 | 1147.1 | 1377.9 |  |  | 1218.1 | 941.5 | 1340.1 |  | 1487.1 | 1325.3 | 1366.7 | 1322.6 | 1357.3 | 1358.4 | 1370.7 | 1368.2 | 1368.5 | 1379.4 | 1379.3 | 1387 | 1543.7 | 1569.4 | 1201.1 | 1198 | 1022.5 | 843.3 | 1036.5 | 1201.1 | 1405.7 | 1508.5 | 1437.7 | 1437.4 | 1425.5 | 1455.5 | 1502.8 | 1501 | 1312.4 | 1392.2 | 1278.3 | 1345.4 | 1255 |  | 1785.5 | 1434.2 | 501 | 1323 | 1284.6 |  |  | 1250 | 1332.2 | 1355 | 1265.2 | 1189 | 40.38 | 45.99 | 2.41 | 7.7 |  | 7.2 | 6.66 |  |  | 86559923.409 | 283057.882 | 59536817.374 | 62724.768 | 87271938.549 | 188098.688 | 63418184.82 | 57284.088 | 327891536.652 | 87601.462 | 90324.317 | 39.941 | 85443.791 | 35.884 | 90299.579 | 50.27 | 70501.086 | 68.544 | 336393.986 | 146.681 | 175692.283 | 336247.305 | 13.4667 | 7.2 | 6.66 | 40.38 | 45.99 | 2.41 | 7.7 | 338140.4
2025-06-10 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:09 | 18:38 | 1556.6 | 1591.8 | 1474.2 | 1469.9 | 1582.7 | 1472.9 | 1465.7 | 1471.4 | 1519.2 | 1528.1 | 1423.1 | 1444.1 | 1466.4 | 1332.1 | 1464.9 | 1458.6 | 1455.1 | 1448.9 | 1554.9 | 1560.1 | 1462.6 | 1467.5 | 1574.1 | 1587.9 | 1578.2 | 1558.9 | 1551.1 | 1607.3 | 1626.1 | 1600.1 | 1601.1 | 1596.4 | 1366.4 | 1763.6 | 1427 | 1625.6 | 1446.7 | 1409.6 | 1435.5 | 1455.3 | 1425.7 | 1464.5 | 1459.5 | 1425 | 1454.1 | 1456.6 | 1572.7 | 1430.5 | 1498.4 | 1476.6 | 1454.9 | 1451.9 | 1663.6 | 1636.7 | 1566 | 1634.4 | 1585 | 1431.1 | 1633.3 | 1628.1 | 1449.9 | 1633.1 | 1453.4 | 1301.1 | 1576.2 | 1565.2 | 1563.2 | 1525.3 | 1418.5 | 1442 | 1449.8 | 1443.6 | 1455.2 | 1456.1 | 1630.2 | 1602 | 1633.2 | 1428.2 | 1424.7 | 1555 | 1445.6 | 1451.2 | 1433.8 | 1452 | 1448.8 | 1453.5 | 1456.9 | 1446 | 1435.1 | 1420.7 | 1477.9 | 1554.1 | 1443 | 1432.2 | 1631.3 | 1419.5 | 1415.4 | 1450.5 | 1423.3 | 1441.1 | 1401.1 | 1438.2 | 1464.1 | 1433.4 | 1596.1 | 1458.7 | 1621.2 | 1615.2 | 1465 | 1591.1 | 1580.7 | 1531.1 | 1599.1 | 1623.6 | 1454.5 | 1481.6 | 1586.3 | 1633.4 | 1617.8 | 1452.5 | 1459.2 | 1587.1 | 1591.1 | 1468.4 | 1467.9 | 1650.8 | 1417.7 | 1446.8 | 1653.5 | 1634.2 | 1577 | 1584.5 | 1551.1 | 1311.1 | 1558.1 | 1544.9 | 1557.1 | 1541.2 | 1511.1 | 1440.1 | 1563.3 | 1531.1 | 1439 | 1555.1 | 1453.1 | 1575.5 | 1438 | 1338.9 | 1558.1 | 1569.6 | 1583.9 | 1453.2 | 1616.2 | 1434.6 | 1454.2 | 1424.8 | 1425.5 | 1430.5 | 1401.1 | 1398.2 | 1621.1 | 1411.1 | 1619.1 | 1601 | 1597.4 | 1462.1 | 1415.1 | 1596.1 | 1407.6 | 1459.8 | 1462.4 | 1455.8 | 1611.2 | 1447 | 1591.2 | 1409.1 | 1415.5 | 1405.1 | 1596.5 | 1412.6 | 1534.2 | 1604 | 1594.4 | 1459.1 | 1527.1 | 1651.1 | 1455.1 | 1449.5 | 1457.4 | 1529.8 | 1436.1 | 1427.2 | 1393.2 | 1399 | 1437.2 | 1447.7 | 1176.3 | 1411.1 |  |  | 1302.6 | 1011.1 | 1434.1 |  | 1581.6 | 1411.1 | 1454.4 | 1434.1 | 1448.3 | 1451.9 | 1461.7 | 1429.1 | 1459.2 | 1450.7 | 1409.2 | 1444.5 | 1634.4 | 1623.2 | 1254.1 | 1254.1 | 1087.5 | 861.1 | 1101.1 | 1272.2 | 1526.2 | 1627 | 1557.7 | 1530.1 | 1496.1 | 1564.5 | 1623.5 | 1601.1 | 1371.8 | 1465.1 | 1378.1 | 1434.1 | 1331.1 |  | 1879.2 | 1515.1 | 541.1 | 1434.1 | 1367.8 |  |  | 1312.7 | 1403 | 1153.4 | 1376.5 | 1277.7 | 41.33 | 46.5 | 3.21 | 8.7 |  | 7.54 | 7.03 |  |  | 86656408.961 | 283097.823 | 59628020.794 | 62760.652 | 87368567.069 | 188148.958 | 63492214.783 | 57352.632 | 328249588.859 | 87748.143 | 96485.552 | 39.941 | 91203.42 | 35.884 | 96628.52 | 50.27 | 74029.963 | 68.544 | 358052.207 | 146.681 | 187613.147 | 357905.526 | 13.4833 | 7.54 | 7.03 | 41.33 | 46.5 | 3.21 | 8.7 | 359956.5
2025-06-11 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:10 | 18:37 | 1454.2 | 1488.4 | 1322.3 | 1374 | 1478.6 | 1359.1 | 1370.5 | 1361.1 | 1420.2 | 1428.9 | 1371.1 | 1351.1 | 1372 | 1288.1 | 1373 | 1367.7 | 1366.2 | 1363.5 | 1484.4 | 1487.3 | 1379.6 | 1380.6 | 1450.1 | 1531.1 | 1467.1 | 1485 | 1478.7 | 1531.7 | 1542.5 | 1536.2 | 1545.6 | 1524.2 | 1279.7 | 1678.6 | 1334.9 | 1516.1 | 1350.7 | 1326.1 | 1340.7 | 1357.8 | 1332.6 | 1317.9 | 1342 | 1330.1 | 1353.6 | 1358.6 | 1467.7 | 1337.8 | 1402.3 | 1380.2 | 1359.7 | 1357.6 | 1555.6 | 1528.1 | 1459.5 | 1519.1 | 1548 | 1361.1 | 1535 | 1521.1 | 1354.9 | 1527.8 | 1358 | 1223.1 | 1476.9 | 1468.8 | 1487.9 | 1445.8 | 1342.4 | 1345.5 | 1354.2 | 1348.7 | 1377 | 1330.1 | 1521.1 | 1520.6 | 1523.1 | 1352.7 | 1332 | 1434.1 | 1353.3 | 1358.4 | 1340.1 | 1355.7 | 1352.6 | 1357.4 | 1361.7 | 1338 | 1339.4 | 1327.7 | 1401.4 | 1431.2 | 1361.2 | 1368.8 | 1533.47 | 1330.6 | 1319.7 | 1359.3 | 1340.4 | 1368.7 | 1361.9 | 1351.9 | 1372 | 1326.8 | 1485.4 | 1375.3 | 1496.1 | 1511.1 | 1351.2 | 1497.2 | 1451.1 | 1442.2 | 1486.1 | 1543.5 | 1345.2 | 1386.5 | 1517.2 | 1551.6 | 1501 | 1355.2 | 1356.2 | 1501 | 1496.3 | 1361.2 | 1356.7 | 1541.1 | 1321 | 1352.7 | 1547.6 | 1527 | 1473 | 1477.6 | 1475.5 | 1265.7 | 1456 | 1443.9 | 1466.7 | 1458.9 | 1444.4 | 1378.8 | 1460.2 | 1438.5 | 1357.5 | 1459.1 | 1348.7 | 1469.6 | 1360.7 | 1237.2 | 1479.7 | 1453.3 | 1475.2 | 1351.2 | 1547.2 | 1353.1 | 1349.6 | 1351.2 | 1355.5 | 1339.6 | 1310.2 | 1320.5 | 1482.2 | 1311.5 | 1465.5 | 1481.1 | 1467.6 | 1367.2 | 1321.5 | 1471.5 | 1312.5 | 1387.1 | 1369.2 | 1371.2 | 1469.5 | 1366.9 | 1471.5 | 1311.5 | 1315.5 | 1309.5 | 1471.2 | 1311.5 | 1461.2 | 1485.2 | 1486.8 | 1369.1 | 1471.5 | 1481.5 | 1371.2 | 1401.2 | 1378.2 | 1471.9 | 1340.6 | 1331.5 | 1313.2 | 1332.8 | 1342.2 | 1351 | 1101.1 | 1323.2 |  |  | 1215.9 | 950.1 | 1341.8 |  | 1483.2 | 1341.2 | 1359.9 | 1335.6 | 1352.5 | 1356 | 1365.7 | 1362.9 | 1363.2 | 1378.8 | 1336.6 | 1387 | 1538.5 | 1541.2 | 1181.1 | 1131.1 | 971.2 | 823.2 | 1050.2 | 1212.1 | 1425.6 | 1533 | 1455.5 | 1429.1 | 1435.5 | 1461.5 | 1488.2 | 1487.6 | 1275.2 | 1377.5 | 1287 | 1343.1 | 1241.2 |  | 1955.1 | 1434.2 | 521.1 | 1323 | 1277.6 |  |  | 1276 | 1365.1 | 1401.2 | 1272.2 | 1234.2 | 40.35 | 47.76 | 2.22 | 5.5 |  | 7.17 | 6.59 |  |  | 86747016.976 | 283137.764 | 59713989.758 | 62796.536 | 87459071.419 | 188199.228 | 63561866.987 | 57421.176 | 328586168.023 | 87894.824 | 90608.015 | 39.941 | 85968.964 | 35.884 | 90504.35 | 50.27 | 69652.204 | 68.544 | 336579.164 | 146.681 | 176501.154 | 336432.483 | 13.45 | 7.17 | 6.59 | 40.35 | 47.76 | 2.22 | 5.5 | 338030.77
2025-06-12 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:09 | 18:35 | 1321.1 | 1352.8 | 1233.2 | 1249.8 | 1344.5 | 1252.1 | 1250.1 | 1251.1 | 1291.9 | 1298.8 | 1232 | 1231 | 1246.7 | 1134 | 1246.6 | 1242.9 | 1240.3 | 1236.6 | 1352 | 1349.9 | 1251.3 | 1212 | 1351 | 1392 | 1348 | 1352.9 | 1345.8 | 1400 | 1412 | 1392.7 | 1389.1 | 1396.4 | 1195.6 | 1515.5 | 1251.2 | 1356.8 | 1258.6 | 1222.3 | 1220.1 | 1239.3 | 1236.5 | 1214.3 | 1222.4 | 1211.5 | 1230.9 | 1235.4 | 1336 | 1220 | 1275.3 | 1257.3 | 1236.2 | 1235.6 | 1418 | 1389.1 | 1334.3 | 1408.3 | 1411.8 | 1256.2 | 1395.1 | 1391 | 1259.87 | 1376 | 1236.3 | 1106 | 1340 | 1329.9 | 1349.6 | 1314.3 | 1223.3 | 1222 | 1230.8 | 1225.2 | 1251 | 1229.2 | 1388 | 1400.3 | 1424 | 1255.5 | 1240.3 | 1324.4 | 1244 | 1235 | 1248.8 | 1243 | 1226.3 | 1230.3 | 1259.5 | 1250 | 1220.4 | 1211.1 | 1276.4 | 1355.2 | 1234 | 1229 | 1392.1 | 1247.5 | 1230.5 | 1233 | 1246.6 | 1245.5 | 1234 | 1246.3 | 1244 | 1212.3 | 1370.5 | 1256.6 | 1387 | 1380.1 | 1255.4 | 1381.1 | 1348.9 | 1323.2 | 1369.3 | 1398.2 | 1247.1 | 1251.7 | 1378.2 | 1400 | 1395.8 | 1240.1 | 1262.8 | 1378.5 | 1381.3 | 1246.6 | 1257 | 1409 | 1223 | 1229.1 | 1408.8 | 1387 | 1336.7 | 1341.9 | 1338.7 | 1149.4 | 1334 | 1316.6 | 1332 | 1332 | 1301 | 1248.7 | 1319.9 | 1323 | 1243 | 1351 | 1216.5 | 1333 | 1236.3 | 1157.8 | 1350.9 | 1367.9 | 1349 | 1254.7 | 1421.8 | 1253 | 1236.6 | 1230.1 | 1235.5 | 1239.9 | 1230.5 | 1235.5 | 1356.5 | 1231.5 | 1355.5 | 1364.5 | 1359.1 | 1275.5 | 1245.5 | 1374.5 | 1239.4 | 1279.4 | 1271.5 | 1269.5 | 1366.5 | 1281.4 | 1375.5 | 1231.5 | 1249 | 1234.4 | 1369.4 | 1236.5 | 1313.2 | 1361.5 | 1369.4 | 1279.4 | 1321.2 | 1371.5 | 1269.6 | 1268.7 | 1288.5 | 1326 | 1239.9 | 1227 | 1212 | 1244.4 | 1238.6 | 1250 | 1033 | 1223 |  |  | 1095.5 | 869.4 | 1232.2 |  | 1342.8 | 1211 | 1249.2 | 1212 | 1246.5 | 1229.1 | 1227.8 | 1238.3 | 1255.4 | 1252.7 | 1222.7 | 1252.3 | 1389.4 | 1417.1 | 1055 | 1095.7 | 901 | 755 | 945 | 1089 | 1289.8 | 1387.8 | 1315.7 | 1323 | 1301.2 | 1321.2 | 1382 | 1371 | 1212 | 1261 | 1201 | 1212 | 1121 |  | 1755 | 1342 | 476 | 1212 | 1232 |  |  | 1176 | 1256 | 1275.5 | 1165 | 1100 | 39.97 | 49.84 | 2.3 | 5.5 |  | 6.58 | 6.05 |  |  | 86829808.384 | 283177.705 | 59792684.301 | 62832.42 | 87541481.108 | 188249.498 | 63625249.37 | 57489.72 | 328893320.931 | 88041.505 | 82791.408 | 39.941 | 78694.543 | 35.884 | 82409.689 | 50.27 | 63382.383 | 68.544 | 307152.908 | 146.681 | 161410.126 | 307006.227 | 13.4333 | 6.58 | 6.05 | 39.97 | 49.84 | 2.3 | 5.5 | 309854.97
2025-06-13 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:11 | 16:34 | 1178.3 | 1208.4 | 1099.7 | 1113.8 | 1200.4 | 1117.2 | 1115.4 | 1116.3 | 1151.9 | 1154.4 | 1137.1 | 1127.3 | 1110.6 | 1046.1 | 1112.6 | 1109.9 | 1107.8 | 1105.5 | 1207.2 | 1206.5 | 1119.6 | 1122.3 | 1231.1 | 1271.5 | 1227.5 | 1212.8 | 1209.1 | 1258.1 | 1269.2 | 1249.8 | 1255.5 | 1261.1 | 1069.5 | 1369.2 | 1119.5 | 1221.1 | 1126.9 | 1099.6 | 1123 | 1139.8 | 1116.4 | 1104.3 | 1128.5 | 1117.2 | 1130.9 | 1130.4 | 1222.3 | 1119.2 | 1145.5 | 1139.3 | 1110.4 | 1115 | 1287.4 | 1266.4 | 1190.5 | 1260.5 | 1260.3 | 1122.1 | 1245.9 | 1262.9 | 1133.2 | 1275.3 | 1106.3 | 1011 | 1233.2 | 1209.5 | 1222.9 | 1185.9 | 1092.6 | 1124.4 | 1131.6 | 1126.1 | 1148.1 | 1091.1 | 1267.2 | 1249.2 | 1262.6 | 1114 | 1114.1 | 1186.1 | 1126.7 | 1128.7 | 1119.2 | 1135.1 | 1127.5 | 1125.2 | 1134 | 1124.1 | 1119.8 | 1112.5 | 1148.5 | 1180.5 | 1144.4 | 1142.4 | 1278.8 | 1119.3 | 1109 | 1130.9 | 1120.7 | 1121.7 | 1121 | 1122 | 1138.9 | 1100.3 | 1227.3 | 1129.9 | 1242 | 1220.3 | 1132.3 | 1242.9 | 1212.5 | 1181.1 | 1223 | 1246.3 | 1123.4 | 1132.8 | 1231.4 | 1239.7 | 1236.7 | 1121.8 | 1135.2 | 1226.6 | 1230 | 1126.6 | 1133.5 | 1223.9 | 1089.3 | 1096.6 | 1262 | 1241 | 1192.9 | 1196.1 | 1194.2 | 1027.6 | 1188 | 1179.6 | 1201 | 1205.8 | 1170.7 | 1109.1 | 1178.7 | 1178 | 1118.1 | 1210.9 | 1106 | 1186.9 | 1103.1 | 1034.4 | 1210.1 | 1222.3 | 1221 | 1122 | 1272.6 | 1123.8 | 1109.8 | 1101 | 1115.5 | 1120.5 | 1114 | 1111.1 | 1255.9 | 1090.8 | 1239 | 1255.5 | 1244 | 1165.8 | 1108.2 | 1263.5 | 1118 | 1121.5 | 1137.6 | 1121.1 | 1232.1 | 1148.4 | 1223 | 1117.1 | 1116 | 1103.4 | 1241 | 1111 | 1180.6 | 1236.2 | 1243.4 | 1131 | 1201 | 1251 | 1154 | 1159 | 1123 | 1174.7 | 1101 | 1105.1 | 1078 | 1115 | 1119 | 1111 | 910 | 1090 |  |  | 996.4 | 782 | 1109.1 |  | 1214 | 1091.1 | 1137.4 | 1091.1 | 1121 | 1119.2 | 1123 | 1123 | 1118.3 | 1127.2 | 1125 | 1115 | 1265.4 | 1271 | 954 | 986 | 821 | 667 | 861.1 | 981.1 | 1170.2 | 1251.5 | 1182.1 | 1212 | 1189.1 | 1255.5 | 1232.7 | 1233.1 | 1056 | 1156.1 | 1050 | 1099.1 | 1017.5 |  | 1459.5 | 1176.2 | 421 | 1111.2 | 1056.2 |  |  | 1065 | 1123 | 1149.8 | 1055.5 | 1001.5 | 39.42 | 48.96 | 3.4 | 12.9 |  | 5.96 | 5.45 |  |  | 86904181.726 | 283217.646 | 59863454.302 | 62868.304 | 87615930.416 | 188299.768 | 63682724.362 | 57558.264 | 329170266.65 | 88188.186 | 74373.342 | 39.941 | 70770.001 | 35.884 | 74449.308 | 50.27 | 57474.992 | 68.544 | 276945.719 | 146.681 | 145067.518 | 276799.038 | 11.3833 | 5.96 | 5.45 | 39.42 | 48.96 | 3.4 | 12.9 | 279024.1
2025-06-14 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:08 | 18:43 | 1326 | 1354 | 1203 | 1253 | 1338 | 1246 | 1237 | 1240 | 1280 | 1291 | 1260 | 1256 | 1236 | 1161 | 1237 | 1233 | 1225 | 1224 | 1328 | 1331 | 1240 | 1244 | 1361 | 1399 | 1349 | 1336 | 1328 | 1377 | 1399 | 1374 | 1381 | 1385 | 1173 | 1513 | 1224 | 1342 | 1233 | 1202 | 1221 | 1238 | 1217 | 1208 | 1224 | 1209 | 1224 | 1228 | 1323 | 1211 | 1280 | 1258 | 1235 | 1232 | 1400 | 1377 | 1324 | 1411 | 1393 | 1241 | 1377 | 1397 | 1235 | 1395 | 1220 | 1087 | 1327 | 1317 | 1336 | 1300 | 1215 | 1209 | 1218 | 1211 | 1239 | 1219 | 1393 | 1368 | 1390 | 1224 | 1211 | 1313 | 1228 | 1232 | 1216 | 1234 | 1217 | 1220 | 1228 | 1216 | 1203 | 1194 | 1263 | 1331 | 1242 | 1232 | 1370 | 1210 | 1204 | 1229 | 1215 | 1218 | 1252 | 1213 | 1238 | 1208 | 1378 | 1231 | 1411 | 1366 | 1234 | 1371 | 1331 | 1324 | 1385 | 1394 | 1226 | 1253 | 1378 | 1397 | 1378 | 1246 | 1262 | 1352 | 1349 | 1232 | 1238 | 1351 | 1200 | 1214 | 1386 | 1367 | 1316 | 1321 | 1318 | 1131 | 1321 | 1298 | 1341 | 1335 | 1289 | 1239 | 1307 | 1311 | 1240 | 1347 | 1203 | 1319 | 1219 | 1132 | 1321 | 1331 | 1340 | 1231 | 1409 | 1236 | 1212 | 1203 | 1199 | 1211 | 1223 | 1199 | 1370 | 1181 | 1365 | 1356 | 1385 | 1260 | 1215 | 1383 | 1223 | 1252 | 1278 | 1251 | 1386 | 1289 | 1331 | 1208 | 1221 | 1198 | 1411 | 1236 | 1316 | 1388 | 1348 | 1311 | 1324 | 1375 | 1275 | 1276 | 1250 | 1323 | 1217 | 1217 | 1189 | 1227 | 1216 | 1101 | 1028 | 1248 |  |  | 1095 | 881 | 1215 |  | 1333 | 1201 | 1231 | 1206 | 1224 | 1227 | 1241 | 1233 | 1239 | 1261 | 1234 | 1247 | 1383 | 1411 | 1067 | 1071 | 886.8 | 756.6 | 941 | 1099 | 1294 | 1375 | 1319 | 1292 | 1261 | 1331 | 1373 | 1351 | 1169 | 1256 | 1199 | 1223 | 1123 |  | 1655 | 1301 | 471 | 1199 | 1178 |  |  | 1151 | 1222 | 1255 | 1155 | 1087 | 37.79 | 49.04 | 1.63 | 4.9 |  | 6.54 | 6.01 |  |  | 86986303.472 | 283257.587 | 59941488.966 | 62904.188 | 87698030.148 | 188350.038 | 63745789.345 | 57626.808 | 329475498.732 | 88334.867 | 82121.746 | 39.941 | 78034.664 | 35.884 | 82099.732 | 50.27 | 63064.983 | 68.544 | 305232.082 | 146.681 | 160080.585 | 305085.401 | 13.5833 | 6.54 | 6.01 | 37.79 | 49.04 | 1.63 | 4.9 | 307007.4
2025-06-15 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:15 | 18:29 | 970.9 | 991.1 | 901 | 910.7 | 988.2 | 916.3 | 918.3 | 920.4 | 951.3 | 953.9 | 935.2 | 930.1 | 912.7 | 871 | 911.4 | 909 | 904.4 | 913 | 979 | 981 | 897.4 | 905.8 | 998.4 | 1015.8 | 974.2 | 981 | 971 | 1021 | 1014.3 | 1022 | 1022 | 1024 | 850.1 | 1101 | 901 | 1001 | 906 | 891 | 901 | 898.1 | 893.2 | 899.5 | 901 | 901 | 906 | 888.9 | 991 | 901 | 941 | 939.2 | 901 | 904.2 | 1011 | 1017 | 971 | 1011 | 1014.1 | 904 | 1001.1 | 1012 | 905 | 1009.1 | 904.1 | 801 | 1001.6 | 993.8 | 1007.2 | 982.1 | 918.3 | 912.4 | 921.3 | 915.3 | 938.9 | 919.3 | 1049.2 | 1030.4 | 1047.4 | 923.1 | 912.6 | 1001.1 | 926.1 | 928.8 | 917.9 | 931.8 | 917.3 | 921.5 | 928.5 | 919.1 | 910.6 | 902.7 | 953.6 | 1010 | 939.3 | 932.1 | 1035.6 | 912.7 | 907.4 | 945.2 | 926.1 | 937.2 | 941 | 929.3 | 941.1 | 911.1 | 1031.1 | 918.9 | 1021 | 1045.8 | 921 | 1031.1 | 1009 | 1002.1 | 1060.8 | 1055.9 | 943.6 | 950.8 | 1039.8 | 1073.2 | 1065.2 | 949.2 | 959.7 | 1025.1 | 1012 | 948.7 | 955.4 | 1191.1 | 891 | 893.4 | 1013.4 | 1006.4 | 969.5 | 973.2 | 974.3 | 838.5 | 971 | 961 | 994.4 | 986.6 | 955.1 | 901.3 | 965.9 | 971 | 891.6 | 980.4 | 891 | 981 | 891 | 823.1 | 962.3 | 970.3 | 973.3 | 896.1 | 1027.5 | 895.9 | 898 | 891 | 893 | 889 | 881.4 | 884 | 991.1 | 901 | 1001 | 996 | 994.2 | 941 | 901 | 999.8 | 911.1 | 932 | 925.8 | 921 | 1009.1 | 931 | 992 | 911 | 885.1 | 901 | 1027.3 | 898.2 | 969.3 | 1015.5 | 1022 | 961.7 | 955.1 | 991.6 | 929.7 | 924.7 | 949.7 | 964.9 | 922.5 | 930.3 | 982.5 | 927.6 | 921.5 | 929.9 | 789.6 | 948.7 |  |  | 822 | 650.3 | 927.8 |  | 1024.4 | 900.8 | 934.3 | 914.5 | 926.8 | 931.4 | 938.1 | 934.6 | 937.3 | 955.5 | 932.3 | 942.5 | 1043.8 | 1064.8 | 801 | 798 | 656 | 555 | 699.8 | 824.3 | 985.1 | 1065.1 | 1025.7 | 1010.7 | 985 | 1021 | 1056.1 | 1011.9 | 893 | 945.3 | 872 | 902.7 | 834.3 |  | 1242 | 1001 | 349 | 901 | 901 |  |  | 851 | 901 | 934 | 868 | 820 | 34.83 | 42.57 | 3.24 | 10.7 |  | 4.87 | 4.49 |  |  | 87046079.3 | 283297.528 | 60001329.281 | 62940.072 | 87758029.79 | 188400.308 | 63794673.512 | 57695.352 | 329703925.03 | 88481.548 | 59775.828 | 39.941 | 59840.315 | 35.884 | 59999.642 | 50.27 | 48884.167 | 68.544 | 228426.298 | 146.681 | 119540.318 | 228279.617 | 13.2333 | 4.87 | 4.49 | 34.83 | 42.57 | 3.24 | 10.7 | 229066.5
2025-06-16 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 6:13 | 17:53 | 1297 | 1322.9 | 1213.2 | 1214.1 | 1317.5 | 1224.1 | 1227.1 | 1227.8 | 1265.3 | 1269.7 | 1250.4 | 1241.9 | 1223.3 | 1153.3 | 1224.6 | 1222.8 | 1217.7 | 1211.2 | 1315.9 | 1316 | 1222.6 | 1227 | 1347.3 | 1377.2 | 1331.4 | 1314.4 | 1308.5 | 1359.7 | 1373.1 | 1354.3 | 1355.5 | 1349.5 | 1142 | 1484.1 | 1209.5 | 1335.3 | 1193.7 | 1184.3 | 1222.5 | 1215.9 | 1225.4 | 1201 | 1206.9 | 1192.7 | 1206.7 | 1210.7 | 1302.4 | 1211.5 | 1243.4 | 1236 | 1209.1 | 1204.2 | 1373.6 | 1353.7 | 1292.9 | 1365.4 | 1368.1 | 1219.8 | 1351.7 | 1369.6 | 1215.7 | 1370.6 | 1206.8 | 1100 | 1326.2 | 1316.7 | 1330.7 | 1298.2 | 1218.1 | 1213.3 | 1221 | 1214.8 | 1245 | 1222.3 | 1390.4 | 1365.5 | 1392 | 1225 | 1211.1 | 1323.3 | 1230.4 | 1234.7 | 1218.8 | 1235.8 | 1218.3 | 1220.5 | 1229.1 | 1218.1 | 1205 | 1197.9 | 1261.1 | 1325 | 1242.9 | 1236.5 | 1368.4 | 1212.9 | 1207.2 | 1239.7 | 1222.1 | 1226.9 | 1255.4 | 1224.5 | 1240.4 | 1213.4 | 1387.4 | 1238.2 | 1398.1 | 1365 | 1236.2 | 1375.2 | 1330 | 1310.6 | 1385.2 | 1376.2 | 1233.3 | 1240.5 | 1356.8 | 1375.3 | 1368.8 | 1232.6 | 1248.5 | 1344 | 1349.1 | 1231.7 | 1241.7 | 1394.9 | 1177.2 | 1170.2 | 1311 | 1321.6 | 1271.7 | 1279.6 | 1277.7 | 1080 | 1250 | 1261.4 | 1261 | 1259.9 | 1221 | 1156.3 | 1263.8 | 1257.5 | 1178 | 1276 | 1162.1 | 1279 | 1180.6 | 1078 | 1271 | 1269 | 1268 | 1172 | 1318 | 1172 | 1176.5 | 1168.7 | 1163.8 | 1172 | 1212.7 | 1190.1 | 1355.9 | 1175.4 | 1345.5 | 1337.9 | 1363.5 | 1248.2 | 1198.2 | 1361.5 | 1229.4 | 1226.6 | 1248.8 | 1224.5 | 1354.7 | 1261.5 | 1350.3 | 1201.3 | 1215.6 | 1191.2 | 1385.3 | 1228.4 | 1296.4 | 1366.4 | 1328.1 | 1276 | 1309.3 | 1360.2 | 1270.8 | 1270.8 | 1277.9 | 1301.2 | 1219.9 | 1209.1 | 1201 | 1221.7 | 1221.7 | 1225.5 | 1034.6 | 1249.4 |  |  | 1117.4 | 845.6 | 1230.3 |  | 1336.1 | 1183.1 | 1230.6 | 1196.3 | 1227.6 | 1227.5 | 1238 | 1236 | 1240.1 | 1252.2 | 1234.1 | 1242 | 1381.9 | 1409.7 | 1089 | 1070 | 901 | 754 | 932 | 1083.5 | 1283.4 | 1381.7 | 1318.4 | 1313.4 | 1295.5 | 1321.5 | 1374 | 1342 | 1143 | 1237 | 1151 | 1183.9 | 1123 |  | 1580.5 | 1278.2 | 461 | 1192.1 | 1141 |  |  | 1142 | 1204 | 1234 | 1156 | 1101 | 32.82 | 40.29 | 3.89 | 8.5 |  | 6.29 | 5.78 |  |  | 87126863.647 | 283334.469 | 60079561.358 | 62971.956 | 87838349.007 | 188447.578 | 63858367.094 | 57759.896 | 330006760.635 | 88625.229 | 80784.347 | 36.941 | 78232.077 | 31.884 | 80319.217 | 47.27 | 63693.582 | 64.544 | 302835.605 | 143.681 | 158947.599 | 302691.924 | 11.6667 | 6.29 | 5.78 | 32.82 | 40.29 | 3.89 | 8.5 | 303505.1
2025-06-17 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:12 | 16:05 | 911.4 | 933.7 | 865.2 | 867.9 | 924.3 | 859.1 | 857.6 | 860.3 | 888.8 | 894 | 872.4 | 867.2 | 855.7 | 807 | 852.9 | 842.3 | 846.7 | 843.5 | 910 | 915 | 855 | 854.2 | 943.3 | 963.9 | 929 | 915 | 910.5 | 949.3 | 952 | 942.5 | 951.5 | 948.8 | 805.4 | 1044.4 | 840.8 | 946.5 | 844.2 | 826.9 | 843 | 857.4 | 835.4 | 828.2 | 843.9 | 836.1 | 846.5 | 849.6 | 915.5 | 837.8 | 877.2 | 863.9 | 850.7 | 847.8 | 970 | 953 | 915 | 971.3 | 965.3 | 856.7 | 947.6 | 955.4 | 853 | 961 | 851.9 | 812.8 | 920.6 | 913.8 | 924 | 899.7 | 841.6 | 839.6 | 844.9 | 839.3 | 861 | 833.7 | 959.1 | 939.5 | 959.5 | 843.8 | 834 | 921 | 846.8 | 850.3 | 839.9 | 850.6 | 837.9 | 842.7 | 848.7 | 842.4 | 832.2 | 828.8 | 869.9 | 913.5 | 858.6 | 853.6 | 950.2 | 835.1 | 833.2 | 854.5 | 848.2 | 850.1 | 869.9 | 846.5 | 857.3 | 834.5 | 964.1 | 850.3 | 980.4 | 949 | 857.6 | 946.8 | 915.5 | 898.9 | 952 | 954.3 | 852 | 860.2 | 941.6 | 945.1 | 943.4 | 847.2 | 865.1 | 934 | 944 | 851.9 | 856.4 | 948.5 | 841.6 | 836.2 | 963.3 | 947.8 | 909.8 | 910.7 | 910.7 | 785.7 | 902 | 900.6 | 930.6 | 916.5 | 900.1 | 834 | 899 | 894.1 | 856.5 | 931.4 | 844 | 901 | 842.3 | 782.4 | 912.5 | 920.4 | 926.9 | 849.3 | 966.5 | 852.5 | 840.4 | 833.8 | 835.8 | 838.5 | 833.4 | 819 | 931.7 | 833 | 934.1 | 922.2 | 952.4 | 861.5 | 824.8 | 938.4 | 843.2 | 861 | 856.9 | 859 | 933 | 865.6 | 945.4 | 831.4 | 837.1 | 821.8 | 953.3 | 845.1 | 890.7 | 937.4 | 921.8 | 903.8 | 906.8 | 941.1 | 878.3 | 879.3 | 876.6 | 889.6 | 839 | 831 | 840.6 | 844.4 | 842 | 847.2 | 713.5 | 864.9 |  |  | 786.1 | 601 | 842.5 |  | 935.2 | 831.7 | 845.5 | 839 | 846.6 | 847.9 | 859 | 853.7 | 860.3 | 862.1 | 853.1 | 861.5 | 963.1 | 983.6 | 755 | 751 | 631 | 531 | 651 | 747.5 | 891.6 | 956.8 | 894 | 898.8 | 901.1 | 925.5 | 953.1 | 934 | 801 | 863 | 803 | 831 | 768 |  | 1151 | 901 | 335 | 831 | 801 |  |  | 799 | 855 | 868 | 801 | 755 | 33.67 | 42.05 | 2.77 | 8.9 | 0.8 | 4.44 | 3.98 |  |  | 87183482.456 | 283371.41 | 60133871.225 | 63003.84 | 87894643.099 | 188494.848 | 63902423.975 | 57824.44 | 330217933.48 | 88768.91 | 56618.809 | 36.941 | 54309.867 | 31.884 | 56294.092 | 47.27 | 44056.881 | 64.544 | 211172.845 | 143.681 | 110859.851 | 211029.164 | 10.8833 | 4.44 | 3.98 | 33.67 | 42.05 | 2.77 | 8.9 | 212042.5
2025-06-18 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:06 | 18:34 | 1115 | 1136.1 | 1053.4 | 1050.5 | 1142.4 | 1052.8 | 1065.8 | 1065.5 | 1095.4 | 1102.4 | 1085.5 | 1079.8 | 1057.3 | 995.3 | 1061.1 | 1013.1 | 1056.5 | 1057.5 | 1150.6 | 1152.4 | 1067 | 1066.2 | 1147.5 | 1201.8 | 1165.2 | 1149.4 | 1140.5 | 1186.3 | 1200.5 | 1215.5 | 1221.5 | 1205.4 | 944 | 1111.4 | 986.1 | 1115.9 | 986.1 | 988.3 | 1001.1 | 995.5 | 980.5 | 993.1 | 981 | 994.4 | 1004.2 | 991 | 1081.1 | 996.5 | 1034.1 | 1037.5 | 999.6 | 995.5 | 1124.2 | 1122.4 | 1081.2 | 1124.5 | 1139.8 | 1003.2 | 1123.5 | 1129.1 | 1002.9 | 1110.7 | 1001.1 | 941 | 1131.9 | 1123.2 | 1135 | 1105.4 | 1044.1 | 1044.1 | 1050.4 | 1044.9 | 1075.1 | 1032.2 | 1194 | 1177.3 | 1197.4 | 1057.6 | 1055.5 | 1148.5 | 1021 | 1041 | 1053 | 1070.6 | 1057.8 | 1057.5 | 1060.2 | 1051.3 | 1037.2 | 1029.4 | 1070 | 1125.7 | 1070.2 | 1067.6 | 1161.9 | 1049.9 | 1044.1 | 1065.7 | 1051.9 | 1057.6 | 1083.1 | 1055.1 | 1071.5 | 1046.6 | 1186.7 | 1056.2 | 1217.2 | 1169.3 | 1061.2 | 1177.7 | 1135.1 | 1111 | 1164.5 | 1172.8 | 1061.4 | 1063.4 | 1151.4 | 1174.1 | 1171.85 | 1053.7 | 1062.2 | 1146 | 1149.8 | 1052.3 | 1061.3 | 1187 | 1048 | 1051 | 1198.7 | 1183.3 | 1142.2 | 1144.7 | 1151.6 | 962.6 | 1101.8 | 1136.9 | 1169.2 | 1156.1 | 1129.4 | 1020.4 | 1135.3 | 1120.1 | 1064.7 | 1161.7 | 1028.6 | 1133.7 | 1058.2 | 980.4 | 1139.7 | 1149.7 | 1146.2 | 1053.3 | 1193.7 | 1056.3 | 1043.5 | 1039.7 | 1044.7 | 1043.4 | 1041 | 1051.5 | 1197.9 | 1039.2 | 1188 | 1180.4 | 1150 | 1096 | 1051.4 | 1175.1 | 1040 | 1071.2 | 1097.2 | 1069.4 | 1190.9 | 1101.6 | 1178 | 1071.1 | 1075 | 1058.9 | 1190.1 | 1048 | 1145.7 | 1176 | 1176.2 | 1101 | 1123 | 1179 | 1121.4 | 1126.3 | 1114 | 1142 | 1039.9 | 1022.4 | 1011 | 1038.2 | 1041.6 | 1023 | 882 | 1062.7 |  |  | 930.1 | 744 | 1038.7 |  | 1123.5 | 1022 | 1052 | 971.6 | 1048.9 | 1056.4 | 1059.1 | 1058.6 | 1059.4 | 1022 | 1053.4 | 1062.4 | 1175.8 | 1194.2 | 901 | 901 | 771 | 644 | 801 | 912.4 | 1094.8 | 1164.9 | 1114.7 | 1108.8 | 1099.5 | 1129.2 | 1159.2 | 1156 | 1011 | 1055 | 981 | 1044 | 945 |  | 1378 | 1101 | 412 | 1051 | 981 |  |  | 965 | 1039 | 1071 | 981 | 931 | 31.72 | 42.78 | 1.64 | 5.1 |  | 5.32 | 4.96 |  |  | 87251038.44 | 283395.351 | 60201269.853 | 63035.724 | 87965830.574 | 188542.118 | 63956006.601 | 57882.984 | 330477604.223 | 88904.591 | 67555.984 | 23.941 | 67398.628 | 31.884 | 71187.475 | 47.27 | 53582.626 | 58.544 | 259670.743 | 135.681 | 134898.787 | 259535.062 | 13.4667 | 5.32 | 4.96 | 31.72 | 42.78 | 1.64 | 5.1 | 261299.05
2025-06-19 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:24 | 17:50 | 989 | 984 | 912.2 | 911.6 | 978.4 | 907.6 | 911.3 | 911.3 | 940.2 | 946.8 | 919.3 | 923.1 | 908.3 | 854.3 | 910 | 885 | 906.2 | 902.5 | 978 | 980.7 | 912.9 | 912 | 963.2 | 1028 | 994.4 | 981.5 | 975.3 | 1015.7 | 1024.6 | 1024.5 | 1019.1 | 1028 | 878.6 | 1113.1 | 912.7 | 1033.5 | 910.7 | 885.6 | 895.5 | 914.5 | 901.5 | 893.3 | 903.3 | 913.5 | 905 | 909.4 | 977.6 | 901.2 | 931.4 | 945 | 903.8 | 901.1 | 1030.2 | 1017.7 | 968.8 | 1023.4 | 1027.4 | 914.5 | 1016.9 | 1030.1 | 911.7 | 1034.9 | 900.2 | 872 | 978.7 | 972.8 | 979.8 | 957.4 | 902.2 | 898.5 | 902.7 | 896.5 | 921.6 | 906.8 | 1044.4 | 1020 | 1042.3 | 914.1 | 900.8 | 990.6 | 910.2 | 913.9 | 900.8 | 913.3 | 897.1 | 902 | 906.4 | 899.8 | 887.9 | 902 | 927.8 | 968.8 | 918.3 | 914.2 | 1006.2 | 899.4 | 900.1 | 916.8 | 912.1 | 909.9 | 928.9 | 908.8 | 919.4 | 896.8 | 1028.2 | 908.7 | 1065.3 | 1011.2 | 911.9 | 1011.3 | 972.7 | 961 | 1020.2 | 1018.7 | 911.1 | 914.9 | 1006.2 | 1001.2 | 1005 | 897.7 | 915.4 | 1001 | 1011 | 903.1 | 911.1 | 1022.2 | 900.9 | 905.2 | 1039.3 | 1027.7 | 989 | 989.9 | 989.7 | 853.9 | 1009.8 | 979.9 | 1017.8 | 1002.8 | 988.6 | 891.5 | 978.8 | 976.8 | 934.9 | 1018.7 | 898.5 | 971 | 921.1 | 855.4 | 991.9 | 1000.7 | 1003.9 | 915.9 | 1039.1 | 917.6 | 906.3 | 902.4 | 912.2 | 905.4 | 913.4 | 896.6 | 1022.6 | 885.2 | 1020.7 | 1016.1 | 1030.3 | 936.7 | 898.6 | 1020.3 | 921.5 | 912.9 | 934.2 | 912.4 | 1016.1 | 939.9 | 1044.5 | 913.5 | 919.7 | 902.6 | 1045 | 927.8 | 978.4 | 1026.7 | 1014.4 | 950 | 994 | 1035.1 | 962.8 | 965.5 | 950.3 | 971.9 | 882.4 | 889.1 | 891.1 | 885.2 | 887.7 | 886.1 | 754.5 | 908.3 |  |  | 827 | 643.2 | 901 |  | 982.3 | 889.2 | 893.6 | 819.8 | 892.4 | 894.6 | 905.2 | 901.2 | 907.3 | 915.9 | 904 | 912 | 1018.1 | 1039.1 | 802.2 | 808.4 | 690.7 | 562.5 | 699.2 | 802.2 | 933.9 | 1003.4 | 961.6 | 978.1 | 941.2 | 978.7 | 1025.2 | 1012 | 890 | 925.5 | 890.1 | 888.7 | 853.5 |  | 1212.5 | 961.5 | 350.4 | 901.1 | 882 |  |  | 844.5 | 902.6 | 932.5 | 881.2 | 814.5 | 30.22 | 39.34 | 3.06 | 9.5 | 0.03 | 4.53 | 4.17 |  |  | 87311402.499 | 283419.292 | 60259321.38 | 63067.608 | 88027176.227 | 188589.388 | 64002405.579 | 57941.528 | 330703683.51 | 89040.272 | 60364.059 | 23.941 | 58051.527 | 31.884 | 61345.653 | 47.27 | 46398.978 | 58.544 | 226079.287 | 135.681 | 118359.761 | 225943.606 | 12.4333 | 4.53 | 4.17 | 30.22 | 39.34 | 3.06 | 9.5 | 227578.3
2025-06-20 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:27 | 18:42 | 570 | 581 | 539.1 | 536.5 | 562.3 | 536.6 | 536.8 | 537.3 | 341 | 558.7 | 547.4 | 543.9 | 534.4 | 502 | 535.3 | 511.63 | 532.4 | 529.9 | 582.7 | 580.7 | 536.2 | 537.9 | 566.9 | 608.4 | 586.6 | 581.9 | 578.5 | 602.1 | 613.1 | 580.7 | 588.5 | 434 | 518.8 | 432 | 538.4 | 610.3 | 540.6 | 525.3 | 533.3 | 541 | 533 | 522.6 | 536.6 | 531.3 | 536.1 | 536.8 | 444 | 528.8 | 552.6 | 391 | 534.5 | 535.1 | 611.2 | 602.7 | 573.8 | 608.1 | 607.1 | 539.3 | 600.4 | 612.4 | 538.6 | 615.2 | 533.7 | 521.2 | 574.6 | 571.2 | 589 | 586 | 526.2 | 525.2 | 528.5 | 523.7 | 541.1 | 532.1 | 608.9 | 599.7 | 607.9 | 533.3 | 527.3 | 584.6 | 534.1 | 474.1 | 528 | 534.4 | 524.6 | 527.9 | 522.3 | 527.4 | 518.3 | 508.7 | 543.6 | 569.1 | 530.4 | 531.3 | 607 | 0 | 0 | 536 | 532.8 | 522.5 | 546.8 | 520.1 | 539.1 | 525 | 610.2 | 0 | 0 | 601 | 536.3 | 602.9 | 581.4 | 589 | 601.4 | 596.8 | 530 | 537.3 | 570 | 599 | 601.7 | 530.8 | 541.2 | 532 | 519 | 535.2 | 540.3 | 599.3 | 544 | 529.1 | 568.4 | 444 | 579.6 | 578.4 | 578.8 | 501.2 | 592.9 | 575.9 | 595.5 | 584.1 | 577.5 | 549 | 589 | 577.5 | 538.1 | 588.3 | 520.7 | 560.3 | 539.1 | 499.9 | 581.5 | 582.4 | 582.3 | 464.1 | 613.3 | 541.8 | 531.2 | 527.3 | 539.5 | 533.5 | 538.9 | 530.8 | 606.7 | 522.9 | 470.6 | 524 | 609.5 | 556.9 | 452.9 | 451 | 356 | 529.4 | 553.6 | 527.2 | 434.6 | 385 | 598.1 | 524.1 | 538.6 | 529.1 | 615.4 | 545.9 | 424 | 444.7 | 596.3 | 585.5 | 585.1 | 608.2 | 558.3 | 555.5 | 448.5 | 330.9 | 522.4 | 515.4 | 523 | 513 | 522.2 | 391 | 442.4 | 538.4 |  |  | 469 | 371 | 534 |  | 579 | 510 | 521 | 519.1 | 527.3 | 533.4 | 535.2 | 512 | 534.8 | 542 | 529.6 | 401 | 599 | 612.6 | 493.1 | 478 | 407.5 | 345.3 | 397.6 | 470 | 537.3 | 597.3 | 569.9 | 565.4 | 544.5 | 577.5 | 594.2 | 587.5 | 523 | 534.9 | 524 | 534 | 473.4 |  | 711 | 565 | 201 | 507.2 | 489.6 |  |  | 488 | 503 | 534 | 491.8 | 475 | 28.91 | 32.29 | 0.946 | 5.7 | 0.4 | 2.53 | 2.4 |  |  | 87345961.541 | 283443.233 | 60291502.496 | 63099.492 | 88060847.752 | 188636.658 | 64029792.6 | 58000.072 | 330831376.797 | 89175.953 | 34559.042 | 23.941 | 32181.116 | 31.884 | 33671.525 | 47.27 | 27387.021 | 58.544 | 127693.287 | 135.681 | 66684.333 | 127557.606 | 13.25 | 2.53 | 2.4 | 28.91 | 32.29 | 0.946 | 5.7 | 128207.03
2025-06-21 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:10 | 18:40 | 1162.5 | 1155 | 1069 | 1064.6 | 1179.5 | 1069 | 1059 | 1072.2 | 1084 | 1130.5 | 1061 | 1081 | 1082.4 | 985 | 1082.3 | 1035.6 | 1074.7 | 1071.4 | 1167.2 | 1167.3 | 1067.2 | 1061 | 1144.4 | 1220.4 | 1151 | 1167.9 | 1159.8 | 1202.1 | 1218.7 | 1166 | 1161 | 1101 | 1024.1 | 1296.7 | 1065.5 | 1202 | 1059.6 | 1047.4 | 1072.4 | 1086.4 | 1059.8 | 1048.3 | 1073.8 | 1059.8 | 1078.9 | 1045 | 1119.2 | 1065.2 | 1120.3 | 1124.3 | 1051 | 1087.2 | 1240.7 | 1220.9 | 1144.9 | 1180 | 1218.8 | 1080.4 | 1193.4 | 1206.6 | 1074.2 | 1211.6 | 1061 | 1002 | 1161 | 1162.8 | 1156 | 1163.1 | 1058 | 1071 | 1068 | 1071.4 | 1084.5 | 1061 | 1219.8 | 1201 | 1224.6 | 1081.8 | 1083.7 | 1056 | 1067 | 1060.8 | 1084.6 | 1076 | 1079 | 1071 | 1074 | 1071 | 1063 | 1059.8 | 1101 | 1157.7 | 1064 | 1075.9 | 1212.9 | 1035.2 | 1033 | 1044.4 | 1031 | 1029.7 | 1048.9 | 1036 | 1033.6 | 1038 | 1171 | 928 | 1059 | 1154 | 1028.4 | 1169.6 | 1134 | 1139 | 1163.6 | 1160.4 | 1042.2 | 1042.1 | 1156 | 1159 | 1169 | 1037 | 1034.8 | 1081.2 | 1082 | 1037 | 1030.8 | 1181 | 1061 | 1055 | 1167 | 1161.1 | 1148.4 | 1123 | 1146.8 | 990.8 | 1139 | 1134.6 | 1154 | 1145.7 | 1124 | 1036 | 1139.3 | 1131.1 | 1077 | 1161.7 | 1044.9 | 1121 | 1063.1 | 985.6 | 1129.6 | 1152.6 | 1155.9 | 1050.2 | 1185.3 | 1042.9 | 1034 | 1034.1 | 1035.5 | 1047.4 | 1050 | 1064.2 | 1171 | 1040 | 1166.5 | 1191.8 | 1189.1 | 1109 | 1054.9 | 1184.7 | 1051.1 | 1103.6 | 1090 | 1104.3 | 1026 | 1068 | 1190 | 1051 | 1057 | 1061 | 1201 | 1055 | 1109 | 1188.9 | 1197.9 | 1071 | 1128 | 1184 | 1081 | 1103.2 | 1081 | 1110 | 1051 | 1053.4 | 1042 | 1063.5 | 1059 | 1051 | 867 | 1044 |  |  | 951 | 736.3 | 1058.9 |  | 1188.4 | 1057.2 | 1031 | 1044 | 1076.2 | 1067.3 | 1061 | 1054 | 1071 | 1043 | 1041 | 1035 | 1213.5 | 1201 | 901 | 901 | 789 | 671 | 808.7 | 956.4 | 1101 | 1211.2 | 1158.4 | 1154.9 | 1101 | 1169.5 | 1203.9 | 1193.6 | 1001 | 1081 | 1002 | 1033.4 | 968.5 |  | 1390 | 1112 | 401 | 1035 | 1001 |  |  | 990 | 1010 | 1080 | 992 | 933.5 | 31.15 | 42.22 | 1.35 | 6.1 |  | 5.62 | 5.19 |  |  | 87417389.103 | 283465.174 | 60358361.347 | 63129.376 | 88130710.583 | 188681.928 | 64085431.87 | 58056.616 | 331095030.155 | 89309.634 | 71427.562 | 21.941 | 66858.851 | 29.884 | 69862.831 | 45.27 | 55639.27 | 56.544 | 263653.358 | 133.681 | 138234.588 | 263519.677 | 13.5 | 5.62 | 5.19 | 31.15 | 42.22 | 1.35 | 6.1 | 264314.4
2025-06-22 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 4:59 | 18:12 | 1230.5 | 1228.1 | 1129.1 | 1134.2 | 1221 | 1141 | 1138 | 1145 | 1190 | 1190 | 1127 | 1147 | 1115.3 | 1046 | 1143 | 1100 | 1134 | 1152.5 | 1246 | 1231 | 1133 | 1135 | 1226.9 | 1280 | 1231 | 1239 | 1233.7 | 1285 | 1298 | 1239 | 1255.5 | 1198 | 1090 | 1379.4 | 1150.8 | 1280 | 1154.2 | 1135.8 | 1151.1 | 1147 | 1131 | 1135.6 | 1134 | 1121 | 1148 | 1129 | 1201 | 1141 | 1166.2 | 1103.4 | 1152 | 1150.5 | 1301 | 1290 | 1235.5 | 1278 | 1271 | 1132 | 1270 | 1290 | 1138 | 1290 | 1147.1 | 1050 | 1229 | 1231 | 1246.1 | 1215.3 | 1132 | 1136.1 | 1139 | 1134 | 1121 | 1145.1 | 1270 | 1282 | 1284.3 | 1145.4 | 1142.7 | 1251.7 | 1131 | 1129.1 | 1135.4 | 1149.6 | 1151 | 1146.1 | 1143.8 | 1143.7 | 1123.9 | 1115.2 | 1169.7 | 1199 | 1131 | 1127.3 | 1273.9 | 1139 | 1132.1 | 1127 | 1146.1 | 1143.2 | 1135 | 1143.4 | 1134 | 1121.7 | 1282.2 | 1135.5 | 1222 | 1267.1 | 1146.6 | 1269 | 1221.9 | 1150 | 1268.6 | 1277.2 | 1148.8 | 1141.3 | 1234 | 1248.3 | 1257.4 | 1122.2 | 1145.5 | 1186.4 | 1161.4 | 1133.2 | 1143 | 1275.1 | 1142.8 | 1139.9 | 1241 | 1265.2 | 1229.5 | 1201 | 1241.2 | 1051 | 1219 | 1231 | 1231 | 1224 | 1180 | 1101 | 1233.6 | 1213.6 | 1132 | 1234 | 1136 | 1148.7 | 1121 | 1041 | 1236.3 | 1232.2 | 1233 | 1147.3 | 1287.8 | 1134.1 | 1134.9 | 1128.8 | 1135.1 | 1142.5 | 1129.7 | 1132.8 | 1261 | 1112 | 1253.7 | 1262.5 | 1251 | 1186.3 | 1113.8 | 1253 | 1102 | 1152.8 | 1151.6 | 1155.4 | 1266 | 1152.1 | 1268 | 1101 | 1119.7 | 1127.2 | 1280 | 1137.6 | 1198.4 | 1249.2 | 1270.7 | 1180 | 1223.5 | 1271.5 | 1160 | 1170 | 1176.1 | 1142 | 1090 | 1111 | 1123 | 1101 | 1096.2 | 1117.3 | 935.4 | 1124.3 |  |  | 1021 | 801 | 1141 |  | 1212.3 | 1121 | 1109.6 | 1121.7 | 1112 | 1106.1 | 1122.6 | 1121.4 | 1129.1 | 1119.5 | 1128.5 | 1109.4 | 1269.7 | 1298.3 | 970 | 960 | 833 | 688 | 871.5 | 1001.1 | 1149.8 | 1249.8 | 1198.4 | 1209.7 | 1155.5 | 1212 | 1243.4 | 1249.55 | 1101.1 | 1155.4 | 1103.3 | 1131 | 1058 |  | 1500.1 | 1223 | 421 | 1109 | 1071 |  |  | 1040 | 1101 | 1143 | 1071 | 1031 | 33.23 | 41.42 | 1.87 | 4.9 |  | 5.81 | 5.3 |  |  | 87494165.934 | 283487.115 | 60430998.241 | 63159.26 | 88205890.186 | 188727.198 | 64142279.414 | 58113.16 | 331376520.795 | 89443.315 | 76776.831 | 21.941 | 72636.894 | 29.884 | 75179.603 | 45.27 | 56847.544 | 56.544 | 281490.64 | 133.681 | 149361.9 | 281356.959 | 13.2167 | 5.81 | 5.3 | 33.23 | 41.42 | 1.87 | 4.9 | 282611.15
2025-06-23 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:12 | 18:30 | 1067 | 1053.4 | 978 | 973.1 | 1049.2 | 973.9 | 972.6 | 973.1 | 931.6 | 1013.1 | 981 | 986.2 | 981.1 | 891 | 968.2 | 967.8 | 965.5 | 998.2 | 1045.4 | 1043.8 | 969.2 | 972 | 1046.1 | 1099.5 | 1057.6 | 1048.3 | 1059.1 | 1088.1 | 1097.8 | 1091.2 | 1109 | 1010 | 935.2 | 1232 | 970.4 | 1071 | 976.7 | 991 | 981.2 | 977.9 | 962.4 | 989.9 | 999.1 | 994.6 | 975.4 | 979.4 | 951 | 959.1 | 1010 | 911 | 969.6 | 973 | 1090 | 1091.4 | 1034.1 | 1100 | 1099.5 | 969.9 | 1087.4 | 1104.4 | 976.1 | 1080 | 973.4 | 890 | 1052.3 | 1057.4 | 1044 | 1038.1 | 976 | 974.1 | 975.4 | 967.1 | 961 | 961 | 1080 | 1098.5 | 1078 | 982.9 | 973 | 1071.9 | 980.6 | 965.9 | 974 | 989 | 970.6 | 973.1 | 974.9 | 968.8 | 956.1 | 945.7 | 999.9 | 1017 | 955 | 958 | 1071 | 958.1 | 745 | 985.2 | 956 | 960 | 970 | 958 | 951 | 946.6 | 1080 | 951 | 1080 | 1079.4 | 951 | 1059 | 1045.2 | 1052.8 | 1070 | 1061 | 951 | 964 | 967 | 1090 | 1059 | 975.5 | 956 | 1039.6 | 1016.1 | 951 | 967 | 1089 | 940.1 | 964.1 | 1080 | 1046 | 1029 | 1019.3 | 1044.5 | 860 | 1020 | 1030.7 | 869.7 | 1029 | 990 | 934 | 1039.6 | 1020.4 | 962.4 | 1042 | 946.6 | 1044 | 965 | 876 | 1063.4 | 1060.6 | 1048 | 971.2 | 1081 | 962.4 | 974 | 962.2 | 965.1 | 953 | 959.3 | 949.1 | 1079.5 | 920.9 | 989.4 | 988.2 | 1049 | 994 | 940 | 992.6 | 940 | 965.2 | 991.6 | 968.6 | 1060 | 980 | 1076.2 | 954.1 | 941 | 944.3 | 1061.6 | 951 | 1020 | 1041 | 1071 | 990 | 1024.5 | 1072.7 | 971 | 990.9 | 920 | 1010 | 950.1 | 935.8 | 941 | 941.7 | 956.6 | 931 | 780 | 931 |  |  | 860 | 615.9 | 953.6 |  | 1065.3 | 943.5 | 901.3 | 941.3 | 959.6 | 967.8 | 977 | 976.1 | 941 | 974.1 | 977.6 | 941 | 1080 | 1100 | 830 | 819 | 698 | 591 | 741 | 867.2 | 1032.5 | 1101.1 | 1051.5 | 1064.8 | 1032.7 | 1072.6 | 1110.7 | 1092.6 | 941.6 | 981 | 929.9 | 941.6 | 876.6 |  | 1301 | 1020 | 372 | 934 | 902 |  |  | 943 | 950 | 964 | 898 | 861.2 | 30.76 | 41.42 | 1.21 | 6.5 |  | 4.95 | 4.58 |  |  | 87558522.716 | 283500.056 | 60492999.11 | 63189.144 | 88268514.617 | 188772.468 | 64192397.921 | 58169.704 | 331615308.592 | 89576.996 | 64356.782 | 12.941 | 62000.869 | 29.884 | 62624.431 | 45.27 | 50118.507 | 56.544 | 238787.797 | 133.681 | 126314.826 | 238654.116 | 13.3 | 4.95 | 4.58 | 30.76 | 41.42 | 1.21 | 6.5 | 239843.7
2025-06-24 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:11 | 18:31 | 1415.2 | 1450.2 | 1345.8 | 1327 | 1436.1 | 1338.3 | 1337.7 | 1344.2 | 1391 | 1399.9 | 1361 | 1358 | 1287 | 1265.8 | 1341.4 | 1340.6 | 1329.7 | 1326.7 | 1440.1 | 1439.8 | 1342.7 | 1348.9 | 1421.6 | 1516.6 | 1463.2 | 1450.4 | 1409.1 | 1493.2 | 1509.5 | 1455 | 1455.5 | 1451.1 | 1258 | 1698.7 | 1311.1 | 1478.2 | 1283.4 | 1292.2 | 1317 | 1329.6 | 1307.1 | 1302.5 | 1326.1 | 1316.9 | 1335.1 | 1340.9 | 1408.9 | 1314.3 | 1373.3 | 1355 | 1331.9 | 1330.5 | 1519.3 | 1499.2 | 1421.4 | 1504 | 1501.7 | 1337.2 | 1483.1 | 1503.5 | 1333.2 | 1504.5 | 1329.7 | 1289.3 | 1453.1 | 1440.1 | 1452.1 | 1406.3 | 1328.1 | 1325.7 | 1327 | 1317.3 | 1351.3 | 1322.1 | 1491.7 | 1460.2 | 1499.9 | 1329 | 1318.5 | 1446.5 | 1342.5 | 1346.7 | 1327.7 | 1340.7 | 1329.6 | 1334.8 | 1331.7 | 1329.9 | 1301.8 | 1293.8 | 1352.5 | 1401.2 | 1348.2 | 1300.7 | 1483.4 | 1310.7 | 1288 | 1347.9 | 1315.6 | 1334.9 | 1362.4 | 1323.6 | 1332.7 | 1310.1 | 1501.5 | 1297.5 | 1536.6 | 746.5 | 1345.2 | 1495.1 | 1447.14 | 1435.1 | 1490.1 | 1501 | 1348.1 | 1343.4 | 1446.5 | 1486.2 | 1488 | 1334.5 | 1352.7 | 1427.6 | 1395.65 | 1337.9 | 1309.2 | 1478.9 | 1311.4 | 1292.4 | 1485.5 | 1472.2 | 1410.1 | 1390.7 | 1415.7 | 1201.1 | 1442.6 | 1376.8 | 1423 | 1435.6 | 1382.7 | 1319 | 1410.2 | 1402.2 | 1315.2 | 1441.2 | 1283.5 | 1416.5 | 1291.9 | 1209 | 1414 | 1409.8 | 1440.6 | 1313.5 | 1479 | 1312.4 | 1289 | 1291.1 | 1282.6 | 1303.4 | 1327.1 | 1303.1 | 1478.9 | 1282.1 | 1446 | 1447.2 | 1454 | 1365.4 | 1292.7 | 1457.3 | 1288 | 1326.7 | 1367.3 | 1337.5 | 1444 | 1370.5 | 1480.3 | 1309 | 1311.6 | 1287.6 | 1455.7 | 1335.2 | 1389.1 | 1453.1 | 1441 | 1420 | 1431 | 1474.8 | 1371.5 | 1350 | 1333.8 | 1410 | 1318.3 | 1309.1 | 1278 | 1302.1 | 1311.9 | 1281.1 | 1103.2 | 1290 |  |  | 1176 | 921 | 1312 |  | 1431.4 | 1297.1 | 1303.8 | 1303.6 | 1325.6 | 1327.7 | 1335.9 | 1336.1 | 1333.8 | 1289.1 | 1325.2 | 1335 | 1490.3 | 1497.6 | 1144 | 1101 | 944 | 801 | 1024.2 | 1165.3 | 1384 | 1497.3 | 1428.5 | 1423.7 | 1395.5 | 1435.5 | 1489.8 | 1476.3 | 1245 | 1339.1 | 1242.5 | 1323.2 | 1229.1 |  | 1801 | 1401.2 | 524.5 | 1301 | 1243.5 |  |  | 1301 | 1277.2 | 1301 | 1243.3 | 1178.5 | 33.08 | 45.26 | 1.88 | 5.5 |  | 6.96 | 6.44 |  |  | 87646933.478 | 283502.997 | 60576457.037 | 63219.028 | 88355329.828 | 188817.738 | 64260621.588 | 58226.248 | 331941994.034 | 89710.677 | 88410.762 | 2.941 | 83457.927 | 29.884 | 86815.211 | 45.27 | 68223.667 | 56.544 | 326685.442 | 133.681 | 171835.864 | 326551.761 | 13.3333 | 6.96 | 6.44 | 33.08 | 45.26 | 1.88 | 5.5 | 329656.49
2025-06-25 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:11 | 18:50 | 1398.7 | 1401.2 | 1326.1 | 1324.9 | 1421.9 | 1318.4 | 1322.7 | 1301.2 | 1365.9 | 1368.9 | 1312.1 | 1309.6 | 1264.1 | 1190.2 | 1316.9 | 1315.5 | 1310 | 1304.2 | 1409.8 | 1416.2 | 1321.2 | 1321.7 | 1398.6 | 1488.3 | 1436.1 | 1418.6 | 1371.1 | 1464.9 | 1472 | 1421.2 | 1425.5 | 1417.5 | 1255.2 | 1623.1 | 1297.7 | 1463.2 | 1309.5 | 1281.4 | 1303 | 1324.7 | 1293.7 | 1282 | 1306.5 | 1295.7 | 1316.6 | 1318 | 1411.5 | 1300.5 | 1356.2 | 1313.5 | 1313.2 | 1311 | 1469.7 | 1477.9 | 1387.7 | 1467.2 | 1464.1 | 1299.7 | 1469.5 | 1464.6 | 1320.3 | 1461.8 | 1313.7 | 1258.7 | 1429.3 | 1417.1 | 1434.3 | 1391.9 | 1312.5 | 1307.3 | 1312.5 | 1299.7 | 1319.1 | 1312.7 | 1488 | 1457.3 | 1490 | 1314.5 | 1300.7 | 1435 | 1321 | 1301 | 1305.8 | 1322.1 | 1303.6 | 1310 | 1308.2 | 1305.5 | 1277.8 | 1267.4 | 1336.9 | 1376.5 | 1330.1 | 1291.1 | 1467.3 | 1299.4 | 1303.3 | 1326.6 | 1310.4 | 1317.8 | 1321.1 | 1302.9 | 1315.1 | 1301.2 | 1485.2 | 1290.1 | 1490.3 | 1414.2 | 1309.1 | 1468.2 | 1421.4 | 1420.5 | 1456.1 | 1466.2 | 1324.2 | 1267.2 | 1418.6 | 1457.8 | 1466.8 | 1316.6 | 1319.1 | 1405.6 | 1368.1 | 1316.6 | 1290.2 | 1467.1 | 1290.2 | 1293.3 | 1413.8 | 1448.1 | 1402.1 | 1389.4 | 1395.1 | 1203.3 | 1401.1 | 1374.2 | 1390.1 | 1413.2 | 1354.3 | 1272.2 | 1381.8 | 1371.8 | 1303.3 | 1401.1 | 1264.5 | 1392.8 | 1280.8 | 1197.7 | 1402.8 | 1414.8 | 1401.1 | 1298.2 | 1486.5 | 1299.1 | 1275.2 | 1272.8 | 1272.8 | 1298.9 | 1275.7 | 1251.6 | 1414.9 | 1254.6 | 1408 | 1399 | 1442.2 | 1317.3 | 1251.2 | 1431.5 | 1264.5 | 1313.5 | 1317.6 | 1313.01 | 1414.4 | 1331.4 | 1418.2 | 1261.8 | 1273.8 | 1269.5 | 1411.6 | 1284.7 | 1359.2 | 1403.4 | 1442.5 | 1362.2 | 1376.7 | 1418.8 | 1333.7 | 1330.4 | 1324 | 1355.6 | 1279.3 | 1251.7 | 1264.5 | 1264 | 1294.3 | 1267.9 | 1071.2 | 1290 |  |  | 1174.4 | 902 | 1302.4 |  | 1417.7 | 1272.1 | 1287.8 | 1271.1 | 1303.2 | 1309.1 | 1321 | 1322.8 | 1290.1 | 1271.5 | 1317.5 | 1290 | 1482.4 | 1516.8 | 1154 | 1123 | 967 | 789 | 1000 | 1142.2 | 1366.4 | 1463 | 1386 | 1386.5 | 1374.5 | 1394.5 | 1460.8 | 1431.4 | 1224 | 1321.2 | 1221 | 1268 | 1204.5 |  | 1789 | 1367.7 | 503 | 1276.6 | 1230.6 |  |  | 1261.4 | 1255 | 1313 | 1232.5 | 1190.6 | 33.46 | 42.64 | 3.12 | 7.5 |  | 6.57 | 6.18 |  |  | 87734214.23 | 283515.938 | 60659715.158 | 63240.912 | 88440708.476 | 188855.008 | 64327958.783 | 58275.792 | 332265085.404 | 89831.358 | 87280.752 | 12.941 | 83258.121 | 21.884 | 85378.648 | 37.27 | 67337.195 | 49.544 | 323091.37 | 120.681 | 170504.048 | 322970.689 | 13.65 | 6.57 | 6.18 | 33.46 | 42.64 | 3.12 | 7.5 | 324493.01
2025-06-26 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:14 | 18:40 | 1414 | 1423.1 | 1339.2 | 1335.9 | 1427.5 | 1328.1 | 1320.3 | 1325.6 | 1369.2 | 1373.8 | 1336.6 | 1327.7 | 1289.7 | 1212 | 1308.2 | 1306.2 | 1297.9 | 1291.9 | 1397.6 | 1402 | 1310 | 1312.6 | 1387.4 | 1471.9 | 1417.9 | 1401.3 | 1369.6 | 1444.2 | 1453.8 | 1444.2 | 1423.4 | 1434.8 | 1247.4 | 1674.5 | 1290.8 | 1452.6 | 1300.1 | 1271.6 | 1291.6 | 1314.8 | 1285.3 | 1273.3 | 1293.8 | 1283.1 | 1308.1 | 1315.1 | 1414.9 | 1292.6 | 1366.7 | 1321.3 | 1320.4 | 1317.4 | 1471.8 | 1478.3 | 1378.7 | 1471.2 | 1459.4 | 1316.7 | 1458.5 | 1474 | 1310.1 | 1479.9 | 1307.5 | 1268.2 | 1425.3 | 1411.3 | 1429.7 | 1396 | 1310.8 | 1303.7 | 1313.6 | 1303.1 | 1302.3 | 1301.1 | 1456.7 | 1433.4 | 1470.4 | 1301.1 | 1290.6 | 1413.5 | 1309.8 | 1315.4 | 1301.2 | 1314.9 | 1297.4 | 1307.1 | 1309.2 | 1309.7 | 1280.4 | 1273 | 1342.5 | 1381.6 | 1326.3 | 1313.5 | 1459.6 | 1290.4 | 1287.7 | 1320.7 | 1295.5 | 1307.9 | 1311.2 | 1289.7 | 1302.8 | 1286.7 | 1454.3 | 1221.5 | 1493 | 1435.5 | 1313.9 | 1455.2 | 1403.3 | 1416.3 | 1461.3 | 1467.5 | 1318.1 | 1271.1 | 1435.3 | 1431.2 | 1444.4 | 1310.2 | 1326.4 | 1401 | 1353.4 | 1304.7 | 1309.1 | 1467.8 | 1289.6 | 1288.4 | 1431.1 | 1448.3 | 1391.5 | 1391.7 | 1396.4 | 1202.4 | 1389.1 | 1373.2 | 1398.2 | 1401.2 | 1351.2 | 1300.2 | 1387.4 | 1381.1 | 1308.4 | 1425.6 | 1271.8 | 1396.6 | 1280.7 | 1194.7 | 1384.5 | 1403.8 | 1410.5 | 1285.1 | 1475.6 | 1289.9 | 1268.6 | 1278.1 | 1266.9 | 1290.1 | 1289.6 | 1271.1 | 1431.1 | 1265.7 | 1421.1 | 1434.2 | 1439.1 | 1321.1 | 1265.5 | 1451.1 | 1280 | 1355 | 1343 | 1331.4 | 1421.6 | 1341.1 | 1421 | 1271.1 | 1271.8 | 1291 | 1431.1 | 1301 | 1384.5 | 1421.5 | 1410.5 | 1371.1 | 1398.1 | 1434.7 | 1344 | 1344.1 | 1339.4 | 1371.1 | 1291.8 | 1285.4 | 1286.1 | 1289.5 | 1290 | 1278 | 1070 | 1301.1 |  |  | 1181 | 915.7 | 1302.7 |  | 1442.7 | 1285.9 | 1291.4 | 1281.6 | 1301 | 1295.8 | 1331.1 | 1323.1 | 1301.1 | 1290 | 1312 | 1324.9 | 1483.3 | 1516.9 | 1151 | 1133.6 | 974.5 | 799 | 999.3 | 1176 | 1371.6 | 1476.7 | 1411 | 1409.5 | 1371.1 | 1421.7 | 1497.2 | 1479.8 | 1241.2 | 1347.7 | 1233.8 | 1289.8 | 1190.9 |  | 1801 | 1376.6 | 513.2 | 1275.8 | 1232.5 |  |  | 1261 | 1278.6 | 1321.1 | 1225.8 | 1206.1 | 34.28 | 42.05 | 4.04 | 8.1 |  | 6.68 | 6.3 |  |  | 87821123.068 | 283528.879 | 60742286.209 | 63259.796 | 88526223.941 | 188889.278 | 64396685.26 | 58321.336 | 332588605.236 | 89948.039 | 86908.838 | 12.941 | 82571.051 | 18.884 | 85515.465 | 34.27 | 68726.477 | 45.544 | 323519.832 | 116.681 | 169448.064 | 323403.151 | 13.4333 | 6.68 | 6.3 | 34.28 | 42.05 | 4.04 | 8.1 | 325151.3
2025-06-27 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:48 | 18:41 | 1288.4 | 1291.1 | 1190 | 1201 | 1300 | 1197.5 | 1181.6 | 1198.1 | 1202.1 | 1210 | 1190.1 | 1198.7 | 1144.7 | 1060 | 1186.6 | 1191.1 | 1181 | 1179.5 | 1251.6 | 1254.1 | 1167.6 | 1171.8 | 1257.9 | 1301.1 | 1267.8 | 1265.6 | 1221.5 | 1322.8 | 1317.6 | 1269.9 | 1265.5 | 1277.1 | 1102.4 | 1456.6 | 1142.8 | 1275.5 | 1151.6 | 1130 | 1148.9 | 1172.7 | 1140.6 | 1133.1 | 1150.5 | 1140.3 | 1166.3 | 1170.6 | 1212 | 1156.3 | 1220 | 1167.8 | 1171.1 | 1173 | 1301.1 | 1313.7 | 1212 | 1301.2 | 1312.2 | 1179 | 1298.8 | 1305.6 | 1167.4 | 1311.4 | 1159.6 | 1101.5 | 1259 | 1265.8 | 1271.8 | 1251.4 | 1152.5 | 1154.6 | 1161.9 | 1171.7 | 1165.7 | 1163 | 1304.7 | 1287.1 | 1299.8 | 1170.8 | 1167.9 | 1262.8 | 1163.5 | 1157.6 | 1169.8 | 1173.2 | 1169.3 | 1158.8 | 1158.8 | 1154 | 1154.8 | 1142.9 | 1196.4 | 1226 | 1167 | 1165.6 | 1316.6 | 1171 | 764.7 | 1172.6 | 1170.3 | 1167.8 | 1162.5 | 1173.1 | 1181.2 | 1127.7 | 1305.2 | 1178.8 | 1314.8 | 1257.8 | 1171.8 | 1316.5 | 1272.9 | 1258.8 | 1305.8 | 1320.8 | 1152.2 | 1123 | 1254.1 | 1275.6 | 1282 | 1175.6 | 1187.8 | 1236.2 | 1227.5 | 1154.4 | 1163.9 | 1278 | 1154 | 1141 | 1267.1 | 1269 | 1218.2 | 1230.9 | 1233.8 | 1061.6 | 1230.2 | 1212 | 1225.7 | 1220 | 1179.7 | 1127.78 | 1232.5 | 1221.1 | 1128.5 | 1230.6 | 1131.1 | 1231.1 | 1131.1 | 1034.6 | 1231.5 | 1220.6 | 1226.2 | 1123.1 | 1282.9 | 1124.8 | 1131.1 | 1125.1 | 1145.5 | 1140.5 | 1140.9 | 1119.4 | 1263 | 1131.4 | 1252.9 | 1254.8 | 1281.4 | 1176.1 | 1129.6 | 1247.4 | 1133.3 | 1172.4 | 1174.1 | 1156.2 | 1263.2 | 1182.6 | 1254.1 | 1122.5 | 1133.4 | 1121.1 | 1251.5 | 1140.2 | 1212 | 1254.1 | 1264.5 | 1215.8 | 1226.7 | 1267.4 | 1182.8 | 1183.4 | 1197.9 | 1210 | 1132.1 | 1135.8 | 1121.1 | 1138.3 | 1131.1 | 1113.1 | 956.1 | 1124.1 |  |  | 0.1 | 806.7 | 1148.9 |  | 1278.1 | 1158.9 | 1171.1 | 1128.3 | 1171.1 | 1160.3 | 1167.7 | 1174.8 | 1154.8 | 1131.8 | 1151.2 | 1156.4 | 1322.2 | 1350.6 | 1024.1 | 1020 | 871.2 | 701.2 | 886.7 | 1041.3 | 1248.5 | 1326.3 | 1262 | 1267.9 | 1255.5 | 1285 | 1320.3 | 1299 | 1091.1 | 1187.2 | 1101 | 1141.5 | 1051.7 |  | 1621.5 | 1221.1 | 435.8 | 1132.1 | 1091.6 |  |  | 1121.1 | 1142.6 | 1181.7 | 1121 | 1055.1 | 31.5 | 41.46 | 2.01 | 6.7 |  | 6.01 | 5.64 |  |  | 87898891.252 | 283537.82 | 60816362.773 | 63272.68 | 88601459.192 | 188919.548 | 64456309.176 | 58361.88 | 332875063.14 | 90053.72 | 77768.184 | 8.941 | 74076.564 | 12.884 | 75235.251 | 30.27 | 59623.916 | 40.544 | 286457.904 | 105.681 | 151822.923 | 286352.223 | 12.8833 | 6.01 | 5.64 | 31.5 | 41.46 | 2.01 | 6.7 | 287351.88
2025-06-28 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:26 | 18:29 | 1049.2 | 1069.3 | 961.1 | 963.7 | 1068 | 984 | 990.6 | 990.6 | 1019.1 | 1024.2 | 968.8 | 997.9 | 939.4 | 878.1 | 983.3 | 974.1 | 977.7 | 976.2 | 1052.4 | 1055.7 | 951.1 | 959.8 | 1026.3 | 1093.9 | 1034.6 | 1048.5 | 1013.2 | 1069.1 | 1078.9 | 1063.2 | 1071.1 | 1051.2 | 902.1 | 1201.2 | 971.2 | 1050 | 971.2 | 966 | 871 | 974.5 | 976 | 972.6 | 971.2 | 965.6 | 961.2 | 956.8 | 1030 | 967.8 | 996.8 | 972.9 | 971.2 | 974.8 | 1093.2 | 1098.7 | 1023 | 1100.1 | 1103.6 | 872.2 | 1076.7 | 1091.2 | 991.7 | 1055 | 985.6 | 902 | 1060.5 | 1041.2 | 1056.2 | 1042.6 | 973.6 | 963.7 | 967 | 981.1 | 969.4 | 955.7 | 1072.7 | 1081.1 | 1090.7 | 969.8 | 973.3 | 1061 | 957.8 | 971.2 | 979.2 | 966.9 | 980.2 | 966.2 | 956.2 | 978.3 | 970.4 | 957.2 | 997 | 1018.6 | 961.2 | 854 | 1100.8 | 974.7 | 0 | 972.1 | 958 | 954.2 | 964.6 | 951.6 | 959.4 | 950.3 | 1071 | 967 | 1083.7 | 1051.3 | 939.9 | 1105 | 1032 | 1019.2 | 1057.9 | 1071.5 | 966.9 | 956.1 | 1061.2 | 1054 | 1069.9 | 954.2 | 967.2 | 999 | 1005 | 956 | 941 | 1059 | 956 | 946 | 1090 | 1080.4 | 957.1 | 1047.2 | 1062 | 905 | 1066.5 | 1019.5 | 1065.3 | 1060.3 | 1026.7 | 876.1 | 1049.5 | 1026.7 | 980 | 1074.1 | 952.1 | 1052.3 | 964 | 903.2 | 1045.5 | 1057.4 | 1056.8 | 957.8 | 1074.2 | 948.7 | 945.7 | 950 | 967.6 | 987.5 | 967.9 | 940.5 | 1082.9 | 928 | 1050.5 | 1044.5 | 1080.9 | 983.9 | 942.8 | 1045.1 | 934.3 | 960 | 989.2 | 969.4 | 1052.6 | 893.2 | 1068.2 | 959.2 | 975 | 964.8 | 1071.4 | 956 | 1012 | 1056.2 | 1050.2 | 1010 | 1021.1 | 1081.6 | 978 | 990 | 962.9 | 932.5 | 945.4 | 967.1 | 959.2 | 971.5 | 955.9 | 945 | 795.5 | 949.5 |  |  | 0 | 681.2 | 958.8 |  | 1034 | 971.1 | 956 | 959.1 | 857.8 | 981.2 | 966.3 | 974.1 | 946.8 | 956.8 | 948.3 | 949 | 1062.5 | 1143 | 851 | 841 | 721 | 590 | 741.7 | 849.6 | 1006.4 | 1077.4 | 1014.5 | 1015.6 | 1021.5 | 1034.5 | 1068.2 | 1078.1 | 931.1 | 1012.2 | 909 | 948.6 | 878.9 |  | 1345 | 1021 | 362.5 | 934 | 912 |  |  | 901 | 956 | 978 | 907.7 | 871 | 30.91 | 41.13 | 1.51 | 9.7 |  | 5.07 | 4.65 |  |  | 87963945.817 | 283546.761 | 60876406.429 | 63285.564 | 88665002.114 | 188949.818 | 64504361.702 | 58402.424 | 333111507.545 | 90159.401 | 65054.565 | 8.941 | 60043.656 | 12.884 | 63542.922 | 30.27 | 48052.526 | 40.544 | 236444.405 | 105.681 | 125076.396 | 236338.724 | 13.05 | 5.07 | 4.65 | 30.91 | 41.13 | 1.51 | 9.7 | 238197.7
2025-06-29 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:18 | 18:29 | 913 | 932 | 862 | 859 | 928 | 857 | 861 | 864 | 892 | 896 | 856 | 839.8 | 839 | 807 | 859 | 851.2 | 852 | 851 | 925 | 928 | 849 | 862 | 908 | 969 | 901 | 929 | 902 | 958 | 966 | 944.2 | 952 | 917.2 | 801 | 1072.2 | 849 | 958 | 856 | 829 | 844 | 860 | 836 | 834.1 | 846 | 819.2 | 853 | 856 | 901 | 846 | 882 | 861.2 | 850 | 854 | 973 | 961 | 914.7 | 954.5 | 961.2 | 846.7 | 960 | 933.4 | 856 | 972 | 865 | 788 | 923 | 919 | 928 | 894 | 845 | 848 | 852 | 838 | 839 | 847 | 965 | 953 | 967 | 849 | 845 | 930 | 854 | 860 | 846 | 852 | 838 | 848 | 840 | 843 | 839.8 | 834.2 | 879.2 | 901 | 858 | 831.2 | 948 | 844 | 0 | 847 | 852 | 839 | 833 | 855 | 836 | 852 | 965 | 841 | 983 | 952.6 | 843 | 957 | 921 | 921 | 934.3 | 927.7 | 860 | 836.8 | 945.2 | 931 | 951 | 853 | 834.7 | 899 | 883 | 854 | 828.8 | 958 | 832.3 | 839.7 | 932.5 | 955.7 | 902.7 | 916.6 | 922.6 | 766 | 899 | 900.3 | 892.8 | 903 | 871 | 861 | 919.1 | 905 | 846 | 942.1 | 831.1 | 925.5 | 848.1 | 788 | 921 | 944.2 | 934.1 | 865 | 951.2 | 845 | 852.3 | 840.8 | 856 | 871.2 | 848 | 828 | 944 | 818 | 935 | 922 | 952 | 869 | 826 | 896 | 835.4 | 851.2 | 864 | 865.9 | 939 | 820 | 929.7 | 834 | 846 | 824 | 926 | 845 | 912.7 | 931 | 927 | 872 | 892.7 | 952 | 871.2 | 865.7 | 864.2 | 902 | 821 | 834.2 | 842.7 | 835 | 834 | 829 | 689 | 823 |  |  | 0 | 601 | 856 |  | 926.5 | 849 | 845.7 | 839.7 | 840.9 | 843.7 | 836 | 848.7 | 839.7 | 846.5 | 852 | 832.2 | 961.1 | 1001 | 752.2 | 739 | 629 | 534 | 645 | 750 | 865 | 958 | 901 | 900 | 898 | 934 | 955 | 937.4 | 801 | 866 | 809 | 842.3 | 782.2 |  | 1171.2 | 909.6 | 322 | 835 | 803 |  |  | 788 | 851 | 845 | 809 | 759.7 | 30.09 | 37.22 | 2.43 | 9.3 |  | 4.19 | 3.89 |  |  | 88020668.84 | 283555.702 | 60929965.521 | 63298.448 | 88720828.316 | 188980.088 | 64547622.07 | 58442.968 | 333320660.333 | 90265.082 | 56723.023 | 8.941 | 53559.092 | 12.884 | 55826.202 | 30.27 | 43260.368 | 40.544 | 209152.788 | 105.681 | 110260.29 | 209047.107 | 13.1833 | 4.19 | 3.89 | 30.09 | 37.22 | 2.43 | 9.3 | 210024.2
2025-06-30 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:20 | 18:23 | 739 | 732 | 677 | 673 | 728 | 674 | 677 | 679 | 701 | 704 | 691 | 686 | 681 | 634 | 674 | 673 | 670 | 666 | 730 | 727 | 674 | 676 | 729 | 763 | 733 | 726 | 735 | 755 | 758 | 761 | 759 | 753 | 649 | 864 | 662 | 744 | 673 | 664 | 652 | 672 | 673 | 656 | 687 | 676 | 684 | 673 | 682 | 675.8 | 661 | 659 | 664 | 678 | 751 | 764 | 723 | 763 | 765 | 680 | 756 | 766 | 670 | 768 | 673 | 624 | 727 | 724 | 728 | 734 | 662 | 664 | 674 | 671 | 683 | 679 | 767.8 | 751 | 762 | 669 | 674.7 | 731 | 668 | 673 | 663 | 669 | 674 | 655 | 681 | 655 | 656 | 666 | 681.2 | 723 | 667 | 634 | 756 | 662 | 47.5 | 676 | 683 | 672 | 657.8 | 684.7 | 657.9 | 667 | 755 | 648 | 763.3 | 739 | 671 | 756 | 727 | 743 | 756 | 758 | 672 | 673 | 752 | 732 | 755 | 673 | 654.6 | 708 | 727 | 668 | 669 | 754 | 674 | 684 | 721 | 771 | 739 | 745 | 739 | 612 | 722 | 721 | 711 | 729 | 703 | 682 | 718.6 | 715 | 683 | 709 | 682 | 711.2 | 665.1 | 619.3 | 739 | 734 | 738.9 | 678.2 | 761.2 | 679.3 | 668.7 | 684 | 670 | 685 | 661 | 669.7 | 737 | 649 | 754 | 727 | 731 | 676 | 674 | 701 | 651 | 681 | 698 | 679 | 739 | 668 | 739 | 652.6 | 654 | 654.8 | 724 | 651 | 724 | 731 | 724 | 672.9 | 711 | 736 | 692 | 694 | 645 | 701 | 656.8 | 645 | 656 | 652 | 655 | 658.4 | 544 | 660 |  |  | 0 | 463.6 | 656 |  | 728 | 682 | 653.2 | 654 | 685 | 667 | 668 | 658.1 | 670 | 656.5 | 665 | 661 | 759 | 774 | 587 | 573 | 494 | 414 | 504 | 595 | 704 | 761 | 732 | 721 | 713 | 739 | 759 | 755 | 639 | 676 | 643 | 666 | 612 |  | 934 | 709 | 252 | 661 | 634 |  |  | 639 | 678 | 684 | 636 | 601 | 29.64 | 35.33 | 1.69 | 4.3 |  | 3.23 | 3.03 |  |  | 88065461.3 | 283564.643 | 60972342.552 | 63311.332 | 88764796.416 | 189003.358 | 64582109.651 | 58471.512 | 333486061.493 | 90360.763 | 44792.46 | 8.941 | 42377.031 | 12.884 | 43968.1 | 23.27 | 34487.581 | 28.544 | 165401.16 | 95.681 | 87147.666 | 165305.479 | 13.05 | 3.23 | 3.03 | 29.64 | 35.33 | 1.69 | 4.3 | 166212.4
2025-07-01 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:34 | 18:43 | 588.4 | 599 | 554.2 | 551.4 | 597.2 | 550.8 | 553.6 | 555.2 | 501 | 543 | 566.1 | 562.4 | 528.2 | 520.4 | 552.8 | 553 | 547.5 | 545.4 | 599 | 598 | 553.6 | 557 | 587.3 | 632.2 | 605.4 | 601.2 | 597.6 | 622.9 | 629.4 | 602.5 | 615.2 | 612 | 517.6 | 690 | 544.4 | 590 | 536 | 521.1 | 532 | 536.8 | 526 | 529 | 537.4 | 537.2 | 541.2 | 527.7 | 573 | 539.2 | 561.5 | 549.3 | 542.4 | 547.8 | 593 | 596 | 571 | 596 | 541.2 | 539 | 588 | 590 | 528 | 590 | 534 | 499.3 | 586.1 | 584 | 584 | 569 | 532.2 | 536 | 536.5 | 522.8 | 529.1 | 541.3 | 599 | 588 | 590 | 534 | 534.4 | 567 | 529 | 524.2 | 539.9 | 532.8 | 524.9 | 523.2 | 523.9 | 532.3 | 531 | 526 | 546 | 562.1 | 536 | 523 | 600.4 | 532.1 | 470 | 521 | 539 | 542.7 | 532 | 538 | 533 | 540.7 | 610.8 | 523.2 | 601 | 598.2 | 524 | 604.2 | 580.1 | 581.3 | 590 | 593 | 531 | 524 | 582 | 587 | 602.9 | 532.6 | 538.6 | 556.4 | 574.5 | 533.7 | 535.4 | 589 | 524 | 535.6 | 587.5 | 602 | 572 | 587.3 | 567 | 480 | 572 | 562 | 563 | 568 | 559.8 | 539 | 591.3 | 588.7 | 531.5 | 574.8 | 523 | 582 | 545.4 | 431 | 591 | 590 | 578 | 529 | 614.6 | 529 | 535 | 540.7 | 524 | 538.7 | 529 | 534 | 590 | 519.6 | 603.9 | 531 | 581 | 552.9 | 535.4 | 529 | 532.8 | 545.3 | 547.3 | 549.9 | 591.2 | 546 | 583 | 492.2 | 524 | 523.5 | 592.6 | 519 | 569.6 | 578 | 590 | 549 | 579.2 | 583 | 545 | 538 | 551 | 495 | 529 | 537 | 527 | 525 | 513.8 | 526 | 435.5 | 520.4 |  |  | 0 | 381.2 | 531 |  | 571 | 534 | 527 | 536 | 536 | 527.2 | 485 | 539.4 | 522.8 | 533.8 | 527.3 | 540.5 | 590 | 617.5 | 472 | 451 | 390 | 333.4 | 413 | 473.7 | 558.4 | 597.5 | 568.4 | 573 | 564.5 | 574.5 | 597.6 | 585.9 | 513 | 551.2 | 528 | 538 | 497 |  | 734 | 562 | 198 | 525 | 509 |  |  | 512 | 538 | 543 | 511.7 | 487 | 27.91 | 32.27 | 0.185 | 4.7 | 0.2 | 2.61 | 2.41 |  |  | 88101780.953 | 283573.584 | 61006685.813 | 63324.216 | 88798717.359 | 189026.628 | 64609100.658 | 58500.056 | 333617364.81 | 90456.444 | 36319.653 | 8.941 | 34343.261 | 12.884 | 33920.943 | 23.27 | 26991.007 | 28.544 | 131303.317 | 95.681 | 70641.089 | 131207.636 | 13.15 | 2.61 | 2.41 | 27.91 | 32.27 | 0.185 | 4.7 | 132771
2025-07-02 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:14 | 18:38 | 934 | 952 | 877 | 878 | 940 | 869 | 876 | 875 | 865 | 905 | 896 | 888 | 837 | 822 | 882 | 879 | 881 | 881 | 962 | 962 | 892 | 889 | 937 | 1007 | 964 | 958 | 950 | 989 | 991 | 947 | 958 | 996 | 813 | 1101 | 877 | 985 | 886 | 870 | 846 | 871 | 846 | 839 | 854 | 855 | 860 | 864 | 932 | 858 | 893 | 877 | 851 | 865 | 988 | 968 | 914 | 984 | 956 | 790 | 956 | 964 | 859 | 964 | 801 | 798 | 933 | 940 | 942 | 906 | 865 | 869 | 868 | 849 | 839 | 848 | 959 | 947 | 934 | 852 | 865 | 909 | 836 | 863 | 865 | 863 | 841 | 850 | 841 | 855 | 839 | 844.5 | 881 | 901 | 812 | 852 | 958 | 865 | 788 | 853 | 846 | 853 | 852 | 862 | 842 | 854 | 963 | 778 | 967 | 949 | 875 | 978 | 945 | 935 | 978 | 979 | 879 | 843 | 947 | 942 | 967 | 866 | 878 | 905 | 929 | 867 | 872 | 949 | 849 | 843 | 964 | 939 | 903 | 947 | 924 | 798 | 902 | 897 | 903 | 918 | 904 | 857 | 955 | 938 | 849 | 923 | 845 | 948 | 851 | 793 | 944 | 953 | 945 | 861 | 971 | 854 | 847 | 842 | 845 | 873 | 851 | 851 | 959 | 840 | 950 | 934 | 950 | 871 | 846 | 971 | 831 | 886 | 897 | 882 | 965 | 887 | 901 | 834 | 857 | 831 | 943 | 851 | 907 | 945 | 952 | 878 | 938 | 972 | 872 | 887 | 867 | 911 | 839 | 829.8 | 757 | 831 | 831 | 807 | 702 | 833 |  |  | 407 | 609 | 869 |  | 937 | 846 | 851 | 841 | 854 | 842 | 849 | 869 | 848 | 854 | 851 | 866 | 968 | 964 | 747 | 761 | 632 | 531 | 666 | 755 | 883 | 961 | 910 | 917 | 902 | 909 | 962 | 944 | 819 | 875 | 809 | 857 | 791 |  | 1201 | 921 | 321 | 857 | 816 |  |  | 801 | 861 | 863 | 809 | 771 | 30.38 | 37.35 | 1.48 | 7.1 | 1.2 | 4.34 | 4.07 |  |  | 88159467.883 | 283582.525 | 61061901.317 | 63337.1 | 88855694.683 | 189049.898 | 64652310.868 | 58528.6 | 333830099.275 | 90552.125 | 57686.93 | 8.941 | 55215.504 | 12.884 | 56977.324 | 23.27 | 43210.21 | 28.544 | 212734.465 | 95.681 | 112880.609 | 212638.784 | 13.4 | 4.34 | 4.07 | 30.38 | 37.35 | 1.48 | 7.1 | 213894.3
2025-07-03 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:16 | 18:38 | 1036 | 1059 | 978 | 975 | 1054 | 973 | 956 | 951 | 964 | 1017 | 962 | 955 | 935 | 890 | 976 | 973 | 968 | 967 | 1053 | 1053 | 978 | 978 | 1032 | 1106 | 1062 | 1052 | 1045 | 1088 | 1091 | 1040 | 1046 | 1051 | 902 | 1223 | 957 | 1064 | 929 | 928 | 933 | 964 | 936 | 933.5 | 940 | 945 | 951 | 957 | 1039 | 954 | 988 | 971 | 951 | 963 | 1106 | 1084 | 1004 | 1081 | 1063 | 949 | 1092 | 1106 | 967 | 1062 | 954 | 901 | 1032 | 1044 | 1047 | 1008 | 954 | 963 | 960 | 936 | 970 | 951 | 1064 | 1075 | 1081 | 949 | 954 | 1045 | 971 | 943 | 962 | 950 | 930 | 942 | 927 | 945 | 933 | 929 | 971 | 1010 | 964 | 935 | 1087 | 961 | 933 | 953 | 957 | 949 | 961 | 957 | 947 | 946 | 1067 | 951 | 1084 | 1034.8 | 968 | 1092 | 1048 | 1024 | 1044 | 1055 | 945 | 929 | 1042 | 1044 | 1093 | 968 | 977 | 1015 | 1037 | 957 | 964 | 1054 | 933 | 943 | 1060.2 | 1070.7 | 1023 | 1032.2 | 1040.2 | 857 | 1001 | 1012.7 | 994 | 1028 | 986 | 952 | 1009 | 1023.6 | 958.6 | 1032 | 925.6 | 1038.6 | 961.2 | 821 | 1022.2 | 1034 | 1031 | 953 | 1072 | 957 | 951 | 943 | 946 | 939 | 943 | 928 | 1045 | 934 | 1056 | 939 | 1061 | 965 | 798 | 898 | 923 | 969 | 988 | 967 | 1045 | 959 | 1033 | 923 | 919 | 919 | 1034 | 924 | 1010 | 1034 | 1031 | 989 | 998 | 1033 | 974 | 965 | 990 | 996 | 932 | 934 | 934 | 927 | 935 | 945 | 793 | 946 |  |  | 867 | 687 | 965 |  | 1035 | 934 | 931 | 931 | 946 | 961 | 956 | 953 | 964 | 935 | 964 | 952 | 1049 | 1087 | 831 | 825 | 701 | 590 | 728 | 855 | 1020 | 1066 | 1032 | 1037 | 1002 | 1025 | 1065 | 1085 | 901 | 980 | 901 | 935 | 864 |  | 1302 | 1004 | 356 | 934 | 901 |  |  | 875 | 956 | 944 | 897 | 842 | 31.07 | 39.16 | 2.32 | 5.7 |  | 4.77 | 4.56 |  |  | 88223510.201 | 283591.466 | 61123420.148 | 63349.984 | 88917345.921 | 189073.168 | 64701872.208 | 58557.144 | 334066544.056 | 90647.806 | 64042.318 | 8.941 | 61518.831 | 12.884 | 61651.238 | 23.27 | 49561.34 | 28.544 | 236444.781 | 95.681 | 125539.324 | 236349.1 | 13.3667 | 4.77 | 4.56 | 31.07 | 39.16 | 2.32 | 5.7 | 237266.1
2025-07-04 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:15 | 18:36 | 954 | 961 | 876 | 888 | 954 | 881 | 885 | 883 | 891 | 901 | 872 | 875 | 875.3 | 801 | 860 | 866 | 879 | 890 | 952 | 949 | 882 | 874 | 965 | 1012 | 966 | 978 | 971 | 990 | 1011.6 | 968.3 | 992 | 996 | 829.5 | 1101 | 858.9 | 954.3 | 801 | 871 | 851.1 | 884.2 | 867 | 876 | 852.4 | 855.9 | 866.2 | 876.5 | 954.7 | 872.8 | 910.1 | 897 | 885.3 | 889.1 | 993 | 999.3 | 933.6 | 990 | 956 | 859 | 1007.3 | 995 | 881 | 965 | 856 | 818 | 951.1 | 946.2 | 956 | 924.1 | 859.3 | 867.4 | 872.2 | 854.9 | 876.6 | 867.5 | 968.6 | 949 | 973.6 | 863 | 855.5 | 937.5 | 875.5 | 861 | 868.5 | 855.7 | 842.5 | 855.9 | 844.5 | 867.5 | 856 | 854 | 909 | 912 | 874.9 | 854 | 965 | 858.8 | 848 | 881.8 | 868.3 | 871 | 882.5 | 865.9 | 873.7 | 858.6 | 957.9 | 851 | 977.4 | 948 | 861.5 | 958 | 915.2 | 946.1 | 982 | 984.8 | 876.5 | 845 | 943 | 953 | 971 | 851.3 | 861.8 | 883.5 | 918.5 | 841.5 | 846.3 | 965.8 | 809 | 851 | 945.2 | 939.5 | 883.6 | 922.9 | 933.7 | 798 | 924 | 921.4 | 901 | 934 | 901 | 875.7 | 929.6 | 919.3 | 877.7 | 943 | 846.5 | 933.6 | 853 | 794.5 | 919.7 | 936.1 | 944 | 864.2 | 962.2 | 867.5 | 854.8 | 846.5 | 855.5 | 847 | 851 | 849 | 961 | 853.4 | 967.3 | 944.5 | 1008.3 | 884.6 | 845 | 963.2 | 861.1 | 893.1 | 895.5 | 888.7 | 959 | 919.1 | 935 | 844 | 841.8 | 851 | 934.4 | 838.5 | 932 | 954 | 958.1 | 867 | 934.1 | 966.9 | 897.2 | 887.8 | 890 | 912 | 842 | 841 | 838 | 845 | 836.3 | 842 | 718.5 | 841.6 |  |  | 764.4 | 609 | 863 |  | 934 | 845 | 849 | 855 | 856 | 851 | 847 | 866.8 | 857.8 | 861 | 863.8 | 884.6 | 962 | 956 | 761 | 751 | 654 | 554 | 671 | 764.1 | 912.3 | 976.2 | 921 | 935 | 922.2 | 925.5 | 972.6 | 965 | 823 | 891 | 844 | 869 | 810 |  | 1181 | 941 | 321 | 854 | 834 |  |  | 801 | 878 | 888 | 823 | 790 | 30.97 | 40.04 | 1.49 | 7.5 |  | 4.55 | 4.15 |  |  | 88282690.988 | 283600.407 | 61178438.591 | 63362.868 | 88973969.421 | 189096.438 | 64745685.766 | 58585.688 | 334281509.689 | 90743.487 | 59180.787 | 8.941 | 55018.443 | 12.884 | 56623.5 | 23.27 | 43813.558 | 28.544 | 214965.633 | 95.681 | 114177.405 | 214869.952 | 13.35 | 4.55 | 4.15 | 30.97 | 40.04 | 1.49 | 7.5 | 216167.6
2025-07-05 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:29 | 18:42 | 1150.1 | 1170.7 | 1077.3 | 1072.9 | 1161.3 | 1069.9 | 1073 | 1077.5 | 1036.3 | 1119.9 | 1087.9 | 1085.2 | 1049 | 1013.2 | 1074.1 | 1073.8 | 1047 | 1047.1 | 1137.5 | 1140.1 | 1070.5 | 1080.3 | 1144.2 | 1219.5 | 1153.5 | 1150.9 | 1149.8 | 1202.3 | 1203.2 | 1162.5 | 1195.5 | 1203.8 | 994.8 | 1354 | 1032.7 | 1147.2 | 1020 | 1023 | 1015.2 | 1012 | 1026 | 1012 | 1021.8 | 1034.8 | 1041.3 | 1055.6 | 1142.9 | 1040.5 | 1104.8 | 1090.2 | 1062.2 | 1069.3 | 1226.6 | 1192.5 | 1133 | 1227.9 | 1112 | 1077.4 | 1194.3 | 1208.7 | 1055.8 | 1206.9 | 1065.4 | 990 | 1171 | 1176 | 1175 | 1169 | 1046 | 1054 | 1049 | 1043 | 1049 | 1090 | 1197 | 1193 | 1222 | 1090 | 1091 | 1184 | 1078 | 1101 | 1083 | 1083 | 1070.9 | 1087.8 | 1073.9 | 1075 | 1047 | 1043 | 1140.3 | 1121 | 1114.5 | 1100.9 | 1231 | 1112.3 | 1062 | 1128.9 | 1109.8 | 1115.3 | 1132.9 | 1114.2 | 1129.4 | 1114.5 | 1237.5 | 1100 | 1273 | 1255.5 | 1101.9 | 1252.1 | 1199.9 | 1193.7 | 1247 | 1246 | 1119.8 | 1063 | 1194 | 1204.1 | 1254.8 | 1119.2 | 1113.6 | 1169.1 | 1213.3 | 1090.8 | 1099.5 | 1267 | 1021 | 1009 | 1135.8 | 1135 | 1098 | 1098.9 | 1113 | 934 | 1095 | 1112 | 1097 | 1124.7 | 1071 | 1023 | 1104.4 | 1119 | 1034.4 | 1101 | 1011 | 1114 | 1027.7 | 931 | 1106 | 1110 | 1101 | 1033 | 1162.6 | 1032 | 1023 | 1034.6 | 1019 | 1026.6 | 1060.8 | 1039.5 | 1172.4 | 1034 | 1165 | 1171 | 1190.9 | 1074 | 1056 | 1181 | 1057 | 1074.9 | 1074 | 1082 | 1176 | 1099.7 | 1143 | 1016 | 1035 | 1033 | 1165 | 1067 | 1132 | 1172 | 1174 | 1135.9 | 1120.6 | 1168 | 1091.5 | 1076 | 1023 | 1045 | 1063.3 | 1092 | 1065 | 1045 | 1090.9 | 1045 | 916.4 | 1090.6 |  |  | 962.8 | 764 | 1067 |  | 1159 | 1053 | 1057 | 1080.1 | 1091.9 | 1102.5 | 1098.3 | 1136.7 | 1114.7 | 1074.6 | 1109.7 | 1124.1 | 1185 | 1275.2 | 956 | 959 | 821 | 682 | 855.2 | 1010.3 | 1189.9 | 1299.2 | 1245.3 | 1224.6 | 1201 | 1251.5 | 1288.7 | 1292.8 | 1058.5 | 1157 | 1044.3 | 1101.8 | 1020.2 |  | 1500.5 | 1167.6 | 409 | 1100.8 | 1066.8 |  |  | 1004 | 1064 | 1103 | 1012 | 945.5 | 31.55 | 42.78 | 1.29 | 4.3 |  | 5.37 | 5.13 |  |  | 88353150.305 | 283609.348 | 61249233.387 | 63375.752 | 89042191.268 | 189119.708 | 64803443.715 | 58614.232 | 334547631.737 | 90839.168 | 70459.317 | 8.941 | 70794.796 | 12.884 | 68221.847 | 23.27 | 57757.949 | 28.544 | 266122.048 | 95.681 | 141232.288 | 266026.367 | 13.2167 | 5.37 | 5.13 | 31.55 | 42.78 | 1.29 | 4.3 | 267586.7
2025-07-06 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:15 | 18:27 | 991.3 | 1012.5 | 936.5 | 935.7 | 1003.6 | 925 | 932.6 | 935.2 | 962.2 | 967.9 | 939 | 946.3 | 937 | 873.7 | 928.4 | 923.3 | 925.6 | 923.2 | 1002.8 | 1002.9 | 930.5 | 929.5 | 991 | 1051 | 1012.8 | 1003.9 | 996.8 | 1039.473 | 1046.5 | 1036.2 | 1035.5 | 1045.2 | 882 | 1172 | 917.1 | 1018.8 | 925.8 | 912 | 909 | 913.5 | 915 | 921 | 919 | 929 | 924 | 909.5 | 991 | 925 | 956 | 957 | 925 | 917.3 | 1058.3 | 1026.8 | 991 | 1050.3 | 1058.4 | 942 | 1045.8 | 1058.3 | 917.3 | 1055.4 | 922 | 831 | 1032.2 | 1029.5 | 1037.6 | 1014.4 | 922.3 | 942.3 | 949.8 | 937.7 | 948 | 950.9 | 1080.8 | 1060.7 | 1086.6 | 949.1 | 928.1 | 1019.3 | 921 | 957 | 930.2 | 914.9 | 926 | 932 | 939.8 | 932.4 | 940 | 929.9 | 978.2 | 1023.6 | 963 | 943 | 1058.7 | 943.4 | 909.4 | 964.6 | 957.6 | 939 | 931 | 932 | 945 | 957.8 | 1075.3 | 911 | 1073 | 1075.5 | 950 | 1074.6 | 1027.6 | 1033.6 | 1079.6 | 1076.7 | 955.3 | 923 | 1025 | 1031 | 1076.4 | 949 | 950.6 | 1015.7 | 1036.7 | 926.2 | 938.6 | 1061 | 919 | 925 | 1037.8 | 1043.1 | 991 | 1022 | 1014 | 877.9 | 1016 | 986.7 | 981 | 1024 | 990 | 951 | 1016.9 | 1008.8 | 960 | 1032 | 938.2 | 1020 | 934 | 871 | 989 | 1019 | 1032 | 954 | 1080.4 | 959 | 956.2 | 952.4 | 957.3 | 937.5 | 924.6 | 906.6 | 1022.1 | 925 | 1021 | 1031 | 1046.2 | 943 | 945 | 1029 | 899.7 | 945 | 939 | 951 | 1031.1 | 953.5 | 1029 | 939 | 922 | 915 | 1021 | 926 | 1009 | 1012 | 1029 | 978 | 1005 | 1029 | 953.8 | 959.2 | 957.2 | 1012 | 931 | 937 | 851 | 925 | 942 | 927 | 767.6 | 919.1 |  |  | 838 | 650 | 939 |  | 1034 | 922.5 | 924 | 916.9 | 922.1 | 943.7 | 928.3 | 939 | 944 | 923 | 937.8 | 941 | 1039 | 1099 | 839 | 842 | 717 | 596 | 715 | 838.8 | 1005.8 | 1051 | 1030.7 | 1015.5 | 990 | 1021 | 1077.2 | 1063 | 901 | 953.6 | 911 | 923 | 847 |  | 1250.5 | 1009 | 351 | 923 | 877.9 |  |  | 863 | 931 | 945 | 901 | 831 | 32.64 | 41.48 | 1.41 | 3.9 |  | 4.72 | 4.5 |  |  | 88414777.733 | 283618.289 | 61310077.476 | 63388.636 | 89103661.517 | 189142.978 | 64852126.609 | 58642.776 | 334779897.943 | 90934.849 | 61627.428 | 8.941 | 60844.089 | 12.884 | 61470.249 | 23.27 | 48682.894 | 28.544 | 232266.206 | 95.681 | 122449.692 | 232170.525 | 13.2 | 4.72 | 4.5 | 32.64 | 41.48 | 1.41 | 3.9 | 233878.073
2025-07-07 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:21 | 18:50 | 1031 | 1022 | 953 | 949 | 1034 | 939 | 944 | 947 | 990 | 990 | 957 | 961 | 938 | 887 | 938 | 941 | 938 | 937 | 1023 | 1021 | 941 | 944 | 1006 | 1064 | 1024 | 1023 | 1011 | 1054 | 1056 | 1052 | 1048 | 1059 | 892.4 | 1201 | 928.7 | 1041 | 950.6 | 941 | 955 | 938.8 | 941 | 954 | 951 | 939 | 946 | 949 | 1010.1 | 933.2 | 977 | 971 | 948 | 940.7 | 1081 | 1052.9 | 1021 | 1081 | 1070 | 951 | 1055 | 1065 | 942.5 | 1061 | 935 | 867 | 1049.6 | 1043.5 | 1056.7 | 1034.6 | 958.6 | 956.8 | 965.9 | 961.5 | 972.9 | 962.4 | 1074.7 | 1053.9 | 1084.6 | 949.4 | 932.8 | 1046.5 | 936 | 967.9 | 936.4 | 944 | 949 | 956 | 950.2 | 954.6 | 955.7 | 951.9 | 996.9 | 1045.4 | 951 | 954 | 1080.2 | 951.1 | 950.2 | 972.4 | 959.5 | 963.2 | 953 | 960.7 | 951 | 958.2 | 1068.1 | 956 | 1090 | 1044 | 945.5 | 1074.4 | 1023.9 | 1042.4 | 1095.9 | 1086.1 | 961.1 | 957.4 | 1047 | 1061 | 1078.3 | 947.1 | 944.3 | 1053 | 1074.8 | 971.5 | 930.1 | 1096.9 | 955 | 939 | 1055 | 1051 | 1012 | 1025.4 | 1022.9 | 885.6 | 1020 | 1010 | 1009.1 | 1042.5 | 1010 | 975.1 | 1024 | 1011 | 955.1 | 1053.2 | 934 | 1035.2 | 954.4 | 888 | 1032 | 1050.1 | 1059.1 | 972.2 | 1059.1 | 972.9 | 956.7 | 947.3 | 941 | 931.3 | 949.1 | 933.6 | 1042.3 | 939 | 1045 | 1052 | 1067.8 | 1002 | 943 | 1040 | 926.8 | 967.1 | 973 | 958.6 | 1078.5 | 990.8 | 1045 | 934 | 941 | 956 | 1051 | 952 | 1044 | 1049 | 1036 | 999.8 | 1023 | 1044 | 963.4 | 984.2 | 987.3 | 1016 | 942 | 932 | 939 | 954 | 932 | 936 | 781 | 934 |  |  | 820 | 680 | 954 |  | 1026 | 956 | 934 | 949 | 935 | 937.7 | 933 | 964.7 | 936 | 935 | 976.5 | 966.4 | 1101 | 1111.1 | 854 | 854.7 | 735.7 | 601 | 734 | 850.6 | 1010 | 1090.9 | 1048.6 | 1024.2 | 1056.1 | 1021 | 1087.8 | 1078.3 | 912 | 989.7 | 923 | 938 | 901 |  | 1301 | 1021 | 363 | 936 | 902.4 |  |  | 887 | 940 | 956 | 909 | 844.7 | 30.51 | 37.51 | 1.91 | 4.3 |  | 4.55 | 4.44 |  |  | 88478645.112 | 283627.23 | 61371584.592 | 63401.52 | 89165988.592 | 189166.248 | 64901337.613 | 58671.32 | 335016401.227 | 91030.53 | 63867.379 | 8.941 | 61507.116 | 12.884 | 62327.075 | 23.27 | 49211.004 | 28.544 | 236503.284 | 95.681 | 125352.67 | 236407.603 | 13.4833 | 4.55 | 4.44 | 30.51 | 37.51 | 1.91 | 4.3 | 238029.5
2025-07-08 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:19 | 18:44 | 1423 | 1443 | 1323 | 1339 | 1433 | 1309 | 1311.9 | 1290 | 1390 | 1391 | 1334 | 1325 | 1331 | 1195 | 1327 | 1321.2 | 1319 | 1323 | 1422 | 1427 | 1310 | 1290 | 1421 | 1490 | 1390 | 1388 | 1390 | 1449 | 1451 | 1444 | 1439 | 1435 | 1244 | 1623 | 1296 | 1424.7 | 1323.7 | 1321 | 1311 | 1297.5 | 1285 | 1296 | 1285 | 1290.1 | 1281 | 1285.5 | 1391.1 | 1290 | 1340 | 1323 | 1281 | 1286.3 | 1454 | 1442.7 | 1378.1 | 1441 | 1439 | 1311 | 1457 | 1441 | 1309.5 | 1505.6 | 1275 | 1201 | 1390 | 1384 | 1401 | 1407 | 1290 | 1295 | 1291 | 1294 | 1321 | 1290 | 1451 | 1457.1 | 1438 | 1287 | 1304.8 | 1400 | 1270.5 | 1311 | 1293.6 | 1291 | 1267 | 1296 | 1307.8 | 1281 | 1311.6 | 1312.8 | 1360.5 | 1401 | 1319 | 1289 | 1472.3 | 1281 | 1295 | 1290 | 1297 | 1284 | 1293 | 1299 | 1278 | 1293 | 1458.8 | 1290 | 1481 | 1452 | 1299.6 | 1474.1 | 1401.4 | 1424.3 | 1471.2 | 1479.1 | 1321.5 | 1315.4 | 1432 | 1423 | 1468.3 | 1300.3 | 1290.9 | 1422 | 1453.7 | 1297 | 1271.4 | 1423 | 1285 | 1267.5 | 1439 | 1438 | 1378.2 | 1423.2 | 1423.3 | 1233 | 1421 | 1389 | 1371 | 1409 | 1388 | 1332.6 | 1424.5 | 1373.2 | 1331.5 | 1432 | 1296.3 | 1421.1 | 1307.5 | 1201 | 1378 | 1434.1 | 1447.7 | 1327.6 | 1449.6 | 1327.8 | 1308.5 | 1299.5 | 1290 | 1315.4 | 1301 | 1315.3 | 1461 | 1270.4 | 1420.5 | 1450.8 | 1501.1 | 1324.6 | 1271 | 1438.3 | 1303.2 | 1351.5 | 1334.5 | 1339.1 | 1480 | 1368.6 | 1477.8 | 1271.8 | 1252.7 | 1266 | 1421 | 1276 | 1367 | 1414 | 1418.8 | 1431 | 1378.4 | 1417.8 | 1351.6 | 1351 | 1321 | 1390 | 1256 | 1265 | 1261 | 1266 | 1261.9 | 1259 | 1064 | 1266 |  |  | 1159 | 921 | 1289 |  | 1401 | 1271 | 1276 | 1278 | 1281 | 1278 | 1273 | 1326.5 | 1279.3 | 1281 | 1280.3 | 1291 | 1431 | 1502.8 | 1151 | 1159 | 998.2 | 821 | 1001 | 1156.3 | 1383.1 | 1483.5 | 1416.9 | 1396.7 | 1390 | 1432 | 1439 | 1432 | 1255 | 1324 | 1275 | 1323.1 | 1190 |  | 1780 | 1419 | 490 | 1321 | 1256 |  |  | 1201 | 1271 | 1311 | 1275 | 1182 | 34.05 | 43.94 | 1.76 | 6.5 |  | 6.66 | 6.3 |  |  | 88567201.418 | 283636.171 | 61455212.684 | 63414.404 | 89252319.721 | 189189.518 | 64967375.267 | 58699.864 | 335340446.602 | 91126.211 | 88556.306 | 8.941 | 83628.092 | 12.884 | 86331.129 | 23.27 | 66037.654 | 28.544 | 324045.375 | 95.681 | 172162.573 | 323949.694 | 13.4167 | 6.66 | 6.3 | 34.05 | 43.94 | 1.76 | 6.5 | 325117.4
2025-07-09 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:21 | 17:32 | 896.2 | 912.7 | 847.1 | 821.8 | 911.9 | 838.4 | 831 | 829 | 877.5 | 883.2 | 837 | 826 | 846.2 | 781 | 849.5 | 836 | 841.8 | 845.1 | 918.7 | 920.1 | 833 | 836 | 918 | 934 | 918 | 923.5 | 918.5 | 955.1 | 955.7 | 951.9 | 953.8 | 955.5 | 777 | 1051 | 812.6 | 931 | 834 | 828 | 829 | 821 | 833 | 829 | 841 | 812.1 | 837 | 828 | 896 | 829 | 851 | 859 | 837 | 829 | 953 | 919 | 891 | 957.8 | 933 | 841 | 945 | 941 | 821.2 | 962.3 | 835 | 771 | 916.6 | 914.1 | 924 | 903.9 | 843.7 | 840.6 | 845.9 | 842.5 | 827 | 847.2 | 931 | 929 | 937 | 834 | 840.1 | 901 | 832 | 831 | 843.6 | 833 | 841 | 839 | 827.5 | 832.2 | 838.8 | 833.3 | 870.9 | 912 | 838 | 838 | 942 | 839.2 | 840 | 829 | 845 | 845.5 | 839 | 846 | 843 | 844.8 | 930.2 | 829.5 | 952.7 | 912 | 826.1 | 933.8 | 889.4 | 910.7 | 955.8 | 947.9 | 840.5 | 832 | 912 | 921 | 938.4 | 822.4 | 818.9 | 919 | 934.1 | 839 | 824 | 947.8 | 829 | 833 | 915.5 | 914.8 | 892 | 905.4 | 906.5 | 784.9 | 909 | 882.6 | 891 | 901 | 890 | 855.3 | 906 | 893.4 | 841 | 931.8 | 822.5 | 914.1 | 842.5 | 780.7 | 885.9 | 921.6 | 921 | 852.1 | 923.6 | 854.5 | 840 | 834.5 | 843.5 | 841.6 | 843.8 | 830.3 | 918.9 | 823 | 911 | 909 | 948.7 | 841.1 | 827 | 920.4 | 819.9 | 855.9 | 843.5 | 846.7 | 940.3 | 849.1 | 931.7 | 829 | 809 | 835 | 907 | 837 | 898 | 911 | 909 | 881 | 891 | 912 | 845.8 | 844 | 854.9 | 878 | 829 | 821 | 836 | 831 | 829 | 839 | 681 | 809 |  |  | 747 | 587 | 829 |  | 901 | 819 | 824 | 833 | 835 | 825 | 821 | 839.6 | 821 | 831 | 834 | 852.9 | 919 | 965.9 | 724 | 743.9 | 638.1 | 524 | 643 | 738.8 | 879.4 | 943.4 | 905.5 | 883.2 | 885.8 | 921.5 | 941.1 | 926.1 | 798 | 854 | 791 | 819 | 765 |  | 1156 | 891 | 321 | 816 | 791 |  |  | 767 | 814 | 846 | 791 | 740.1 | 31.93 | 39.1 | 2.24 | 7.1 |  | 4.07 | 3.86 |  |  | 88622789.601 | 283645.112 | 61509254.043 | 63427.288 | 89307397.672 | 189212.788 | 65009921.548 | 58728.408 | 335547445.895 | 91221.892 | 55588.183 | 8.941 | 54041.359 | 12.884 | 55077.951 | 23.27 | 42546.281 | 28.544 | 206999.293 | 95.681 | 109607.717 | 206903.612 | 12.1833 | 4.07 | 3.86 | 31.93 | 39.1 | 2.24 | 7.1 | 208916.3
2025-07-10 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:27 | 18:31 | 499.7 | 504 | 470.7 | 472.9 | 500.1 | 468 | 470.1 | 471.3 | 486.8 | 493 | 475.7 | 474.7 | 477.1 | 441.4 | 476.9 | 481 | 477.7 | 479.5 | 516.2 | 521 | 468.5 | 467.1 | 520.2 | 515.9 | 507.3 | 512.8 | 521.6 | 517.9 | 526.7 | 521.8 | 527.2 | 529 | 446.9 | 590.9 | 467.1 | 515 | 463.6 | 467.7 | 468.2 | 465 | 473.6 | 477 | 473 | 475.7 | 462.7 | 472.4 | 498.2 | 464.6 | 483.2 | 480.8 | 464.4 | 467.4 | 520.6 | 522.6 | 500.2 | 525.2 | 521.3 | 470.2 | 521.3 | 521.7 | 465.3 | 535.3 | 471.6 | 421.4 | 509.8 | 514.9 | 514.2 | 515.4 | 472.5 | 470.6 | 470.1 | 470.8 | 473.5 | 472.2 | 522.6 | 525 | 526.8 | 467.3 | 463.5 | 518.6 | 470.1 | 477.1 | 473.3 | 473.5 | 468.5 | 470.2 | 473.9 | 476.2 | 471 | 469.6 | 497 | 518.5 | 467.7 | 480.2 | 540.7 | 462.5 | 462.7 | 469.6 | 468.6 | 463.5 | 470.1 | 479.1 | 460.6 | 471.6 | 530.9 | 461.7 | 525 | 535 | 467.3 | 526.9 | 511.5 | 510.2 | 537.4 | 529.6 | 466.1 | 461.2 | 521.2 | 526.5 | 524 | 478.8 | 469.4 | 523.5 | 528.3 | 468.6 | 461.8 | 521.3 | 461.2 | 476.8 | 521.4 | 518.9 | 506.5 | 509.7 | 507.1 | 421.3 | 493.1 | 493.5 | 506.7 | 492 | 491.7 | 474 | 502.6 | 511 | 467.2 | 520.4 | 467.1 | 525.4 | 461.2 | 427.3 | 508.7 | 509.7 | 512.2 | 471 | 521 | 475.4 | 473.3 | 475.2 | 468.1 | 461.8 | 463.2 | 456.8 | 518.8 | 461 | 523 | 517 | 528.1 | 485.8 | 462.1 | 511.3 | 462.5 | 480.3 | 494.1 | 478.4 | 515 | 480.6 | 529.4 | 458.5 | 457 | 458.4 | 516.8 | 455 | 513 | 517.6 | 511.1 | 488.4 | 514.1 | 514 | 476 | 445 | 485 | 509 | 467 | 461 | 471 | 458 | 463 | 465 | 393 | 458.5 |  |  | 422.9 | 333.8 | 473.8 |  | 512 | 467 | 464 | 466 | 468 | 463 | 465 | 469 | 468 | 471 | 463 | 476.5 | 525 | 551.7 | 401.7 | 418.7 | 364.6 | 295.7 | 363.7 | 424.4 | 498.9 | 535 | 501.2 | 501.7 | 529.9 | 507.4 | 523.7 | 528 | 444 | 491 | 457 | 465.4 | 428 |  | 634.8 | 516.2 | 172.9 | 476.3 | 449 |  |  | 430 | 456 | 471.4 | 444 | 423 | 27.48 | 31.37 | 1.28 | 6.1 |  | 2.41 | 2.21 |  |  | 88654468.041 | 283654.053 | 61539532.993 | 63440.172 | 89337150.978 | 189236.058 | 65034076.732 | 58756.952 | 335663069.843 | 91317.573 | 31678.44 | 8.941 | 30278.95 | 12.884 | 29753.306 | 23.27 | 24155.184 | 28.544 | 115623.948 | 95.681 | 61935.565 | 115528.267 | 13.0667 | 2.41 | 2.21 | 27.48 | 31.37 | 1.28 | 6.1 | 117443.3
2025-07-11 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:13 | 18:45 | 1299.5 | 1323.8 | 1219.9 | 1221 | 1316 | 1212.2 | 1212.7 | 1219 | 1264.3 | 1251.4 | 1212.7 | 1215 | 1219 | 1123 | 1211.1 | 1131 | 1215 | 1223 | 1311 | 1314 | 1217 | 1212 | 1319 | 1341.3 | 1322 | 1317 | 1322 | 1337 | 1335 | 1339 | 1344 | 1338 | 1143 | 1429.6 | 1195.3 | 1330.87 | 1221 | 1209 | 1211 | 1195.9 | 1196.6 | 1203.3 | 1209.7 | 1199 | 1218 | 1221 | 1291 | 1211 | 1243 | 1244 | 1189 | 1195 | 1370.1 | 1335 | 1289 | 1362 | 1371 | 1224.8 | 1371 | 1371 | 1201.2 | 1359 | 1194.9 | 1100.3 | 1351 | 1354 | 1361 | 1335.6 | 1283.2 | 1286.7 | 1280.7 | 1267.5 | 1212 | 1280.6 | 1437.3 | 1425 | 1448.9 | 1286.7 | 1286.9 | 1399.3 | 1266.1 | 1280.5 | 1267.7 | 1237 | 1263.5 | 1275.2 | 1243.9 | 1235.9 | 1249 | 1239.5 | 1275.7 | 1343.5 | 1231 | 1227 | 1392.3 | 1229 | 1235 | 1225 | 1240 | 1230 | 1228 | 1219 | 1215 | 1211 | 1385.6 | 1230 | 1381 | 1380.5 | 1255.8 | 1414.5 | 1341 | 1369.2 | 1406.3 | 1423.3 | 1212 | 1255.9 | 1331.7 | 1343 | 1391.2 | 1241.3 | 1228.8 | 1342 | 1372 | 1199.8 | 1226.8 | 1403.8 | 1143 | 1138.4 | 1291 | 1289 | 1234 | 1252 | 1256 | 1044 | 1219 | 1224 | 1212 | 1228 | 1199 | 1142 | 1256 | 1213 | 1142 | 1229 | 1132 | 1256 | 1156 | 1055 | 1242 | 1239 | 1244 | 1121 | 1132 | 1129 | 1125 | 1121 | 1134 | 1127 | 1221 | 1218 | 1343 | 1177.8 | 1321 | 1342.8 | 1361 | 1246.7 | 1221 | 1332 | 1213 | 1268.4 | 1263.6 | 1276.2 | 1301.6 | 1281 | 1381 | 1194.6 | 1198 | 1212 | 1334 | 1196 | 1281 | 1323 | 1329 | 1260 | 1284 | 1324 | 1251 | 1284.8 | 1171 | 1212 | 1212 | 1194 | 1204 | 1197 | 1201.1 | 1223 | 994 | 1206.1 |  |  | 1104.1 | 801 | 1221 |  | 1319 | 1210 | 1230.1 | 1197 | 1198.3 | 1193.2 | 1201 | 1221 | 1131 | 1201 | 1198 | 1241 | 1340.5 | 1429.6 | 1051 | 1071 | 929 | 771 | 952.9 | 1101 | 1294 | 1381 | 1331 | 1327 | 1298 | 1325 | 1381 | 1375 | 1167 | 1251 | 1167 | 1217.7 | 1136.8 |  | 1600.1 | 1301 | 455 | 1218.8 | 1171 |  |  | 1109 | 1178 | 1212 | 1181 | 1109 | 30.53 | 43.25 | 1.6 | 7.7 |  | 6.47 | 6.17 |  |  | 88734485.731 | 283662.994 | 61619742.604 | 63453.056 | 89416165.477 | 189259.328 | 65096725.501 | 58785.496 | 335964631.299 | 91413.254 | 80017.69 | 8.941 | 80209.611 | 12.884 | 79014.499 | 23.27 | 62648.769 | 28.544 | 301561.456 | 95.681 | 160205.476 | 301465.775 | 13.5333 | 6.47 | 6.17 | 30.53 | 43.25 | 1.6 | 7.7 | 302424.37
2025-07-12 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:16 | 18:27 | 861.7 | 859.1 | 798 | 793 | 857 | 791 | 788 | 771 | 801 | 810 | 784 | 789 | 793 | 732 | 785 | 785.8 | 788.8 | 784 | 848.6 | 832 | 777 | 788 | 856 | 861 | 843 | 839 | 838 | 871 | 891 | 886 | 892 | 882 | 743 | 984.8 | 781 | 856 | 789 | 786 | 789 | 796 | 785 | 776 | 778 | 791 | 772 | 781 | 826 | 784 | 801 | 805.5 | 789 | 781 | 877.9 | 861 | 842 | 902.1 | 895.1 | 798 | 874.7 | 875.5 | 789 | 854.2 | 781 | 701 | 848 | 851 | 849 | 856.8 | 809.8 | 813.6 | 806.7 | 796.5 | 798 | 808.9 | 909.4 | 906.5 | 909.8 | 800.3 | 788.5 | 870.5 | 781 | 793.2 | 778.8 | 797.2 | 779.9 | 798.2 | 782.3 | 779.6 | 800.3 | 794.3 | 817.6 | 867.4 | 781 | 801.5 | 892.5 | 793.7 | 787 | 791 | 788 | 793 | 794 | 783 | 794 | 794 | 871 | 778 | 889.9 | 855.5 | 787 | 908.1 | 846 | 873 | 894.4 | 892.3 | 800.1 | 791.5 | 861 | 859 | 866 | 776 | 769.3 | 867 | 863.5 | 781 | 784 | 892.5 | 781 | 786 | 861 | 867 | 829 | 834 | 837 | 712.3 | 852.1 | 823 | 829 | 848.6 | 807 | 781 | 832 | 828.2 | 778 | 834 | 789.7 | 834 | 789 | 712 | 854 | 845 | 849 | 784 | 866 | 781 | 791 | 793.3 | 791 | 785.1 | 788.8 | 783.3 | 855.4 | 781 | 866 | 855.8 | 859 | 796.3 | 786 | 860 | 768.1 | 793 | 790.1 | 792.5 | 864 | 787 | 876.8 | 781 | 789 | 794 | 863 | 778 | 839 | 856 | 867 | 794 | 829 | 862 | 797 | 803 | 797.7 | 819 | 778.9 | 794 | 789 | 784 | 782 | 796.1 | 634 | 789 |  |  | 702.89 | 555 | 793 |  | 848 | 791 | 786.8 | 793 | 797 | 780.5 | 802 | 803.3 | 780 | 792 | 797 | 785 | 878 | 934.8 | 680 | 698 | 597 | 498 | 610.2 | 716.9 | 832 | 888 | 851 | 855.6 | 834 | 839 | 871 | 894.4 | 739 | 819.6 | 756 | 772.4 | 728.7 |  | 1050 | 833 | 293 | 785.5 | 764.1 |  |  | 723 | 760 | 781 | 742 | 692 | 29.65 | 36.39 | 1.47 | 11.3 | 0.5 | 4.09 | 3.83 |  |  | 88786555.421 | 283671.935 | 61670838.051 | 63465.94 | 89466698.705 | 189282.598 | 65137845.104 | 58814.04 | 336159261.162 | 91508.935 | 52069.69 | 8.941 | 51095.447 | 12.884 | 50533.228 | 23.27 | 41119.603 | 28.544 | 194629.863 | 95.681 | 103143.312 | 194534.182 | 13.1833 | 4.09 | 3.83 | 29.65 | 36.39 | 1.47 | 11.3 | 196348.49
2025-07-13 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:31 | 18:29 | 810 | 807 | 738 | 741 | 803.9 | 737.6 | 735 | 737 | 770.3 | 775.3 | 734 | 741 | 745.2 | 682 | 730 | 723 | 729.9 | 737.5 | 800.5 | 802.4 | 734 | 712.6 | 790 | 810 | 790 | 802.2 | 798.3 | 828.3 | 826.8 | 827.1 | 834.2 | 825.2 | 677.1 | 920 | 721 | 810 | 731.2 | 710 | 721 | 728 | 724 | 730 | 721 | 710 | 729 | 723.3 | 792 | 713.5 | 751 | 755 | 722 | 719.5 | 822 | 808.5 | 777 | 821 | 830.5 | 733.5 | 819 | 824 | 723.5 | 826.6 | 725.6 | 657 | 818.9 | 815.2 | 814.2 | 804.5 | 750.5 | 747 | 750.1 | 746.6 | 763.6 | 754.2 | 845.6 | 837.5 | 848.6 | 747.6 | 739.5 | 820.5 | 741.5 | 751.2 | 729 | 753.8 | 738.7 | 749 | 742 | 737.3 | 748.5 | 741.2 | 750.5 | 811.4 | 756.7 | 731.5 | 842 | 722 | 728 | 721 | 726 | 727 | 721 | 733 | 732 | 719 | 823.1 | 732.1 | 809.9 | 829.5 | 728 | 830.6 | 785.5 | 791.6 | 822 | 824 | 720 | 732.4 | 807.8 | 812 | 833 | 730.6 | 734.5 | 819 | 824 | 728.6 | 712.7 | 822.5 | 719.6 | 722 | 811 | 804.9 | 770 | 797 | 806.6 | 685 | 780 | 774.7 | 771 | 781 | 759 | 736 | 792.6 | 783.6 | 736.5 | 793.7 | 725 | 802.2 | 740 | 660 | 808.7 | 790 | 791 | 728 | 815.4 | 723 | 733 | 736.6 | 733.4 | 743.6 | 726 | 720 | 799 | 723 | 811 | 801 | 813.4 | 741 | 739 | 790 | 715.4 | 735 | 755 | 737.7 | 792 | 739 | 799.1 | 721 | 723 | 729 | 801 | 721 | 775 | 801 | 809 | 752.3 | 771 | 791 | 736 | 734 | 743 | 776 | 716.5 | 713.4 | 723 | 725 | 708.7 | 719 | 600 | 723 |  |  | 651.4 | 521 | 735.6 |  | 790.2 | 721 | 736.5 | 724 | 729 | 720.5 | 725 | 731 | 721 | 719 | 729 | 722 | 812 | 864.5 | 634 | 641 | 550 | 467 | 571 | 659.7 | 771 | 821 | 778 | 787.7 | 778 | 779 | 841.2 | 829 | 701 | 756.4 | 701 | 729 | 667 |  | 989 | 774.5 | 279.5 | 721.4 | 696 |  |  | 674 | 721 | 733 | 701 | 662 | 29.58 | 34.35 | 1.14 | 4.1 |  | 3.56 | 3.52 |  |  | 88835350.561 | 283680.876 | 61718777.906 | 63478.824 | 89513905.592 | 189305.868 | 65176117.939 | 58842.584 | 336341275.968 | 91604.616 | 48795.14 | 8.941 | 47939.855 | 12.884 | 47206.887 | 23.27 | 38272.835 | 28.544 | 182014.806 | 95.681 | 96713.17 | 181919.125 | 12.9667 | 3.56 | 3.52 | 29.58 | 34.35 | 1.14 | 4.1 | 182953.6
2025-07-14 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:24 | 18:39 | 1067.2 | 1092.3 | 1011.1 | 1004.6 | 1084.5 | 998.5 | 1008.5 | 1016.7 | 1046.3 | 1052 | 998 | 994 | 1010.3 | 917 | 1012.2 | 1009.2 | 990.5 | 999.4 | 1077.2 | 1084.8 | 1014.3 | 972.4 | 1090 | 1121 | 1081 | 1090.6 | 1085.6 | 1128.3 | 1099.6 | 1100.2 | 1125.5 | 1135.5 | 940.1 | 1232.6 | 972.9 | 1109 | 984 | 971 | 978 | 986.9 | 975 | 983 | 981 | 988 | 990 | 982 | 1058.5 | 980.7 | 1012 | 1015.5 | 984 | 980.7 | 1139 | 1103.6 | 1069 | 1121 | 1125.2 | 990 | 1121 | 1127 | 998.9 | 1136.5 | 985 | 901 | 1101 | 1119.5 | 1109 | 1104.4 | 1035.3 | 1035.4 | 1042.1 | 1039.1 | 1032 | 1038.4 | 1168.6 | 1151.1 | 1174.7 | 1038.2 | 1033.6 | 1131 | 1020.6 | 1031.3 | 1039.8 | 1052.87 | 1034.7 | 1046.5 | 1038.1 | 1033.5 | 1039 | 1037.6 | 1067.6 | 1128.2 | 1036.5 | 1029 | 1159.9 | 1019.5 | 1032.6 | 989 | 991 | 983 | 980 | 995 | 984 | 1026.2 | 1111.2 | 983 | 1110.2 | 1099 | 1004.1 | 1128.5 | 1071.1 | 1093.1 | 1136.2 | 1126.1 | 991 | 1004.8 | 1096.9 | 1131 | 1110.4 | 1008.6 | 1014.6 | 1102 | 1113.1 | 975.41 | 992.4 | 1134.3 | 1003.6 | 974.4 | 1131.1 | 1120.6 | 1060.5 | 1093.1 | 1090.6 | 901 | 1093 | 1061.6 | 1050.4 | 1061 | 1043 | 1012.5 | 1092.8 | 1083.3 | 1011.8 | 1094.7 | 987.7 | 1089 | 991 | 925 | 1090 | 1101 | 1090.8 | 1021 | 1106.6 | 981 | 985 | 981 | 990 | 980 | 976 | 991.8 | 1091.8 | 970.2 | 1088 | 1090.5 | 1117.6 | 1020.5 | 976.3 | 1086.8 | 980.5 | 1017.1 | 1007.3 | 1011.4 | 1096.8 | 1037.3 | 1114.2 | 980.1 | 973.5 | 977.8 | 1109 | 981 | 1052 | 1087 | 1096 | 1037.3 | 1051.1 | 1091.4 | 1016.6 | 1019 | 1012.3 | 1071 | 999.1 | 985.1 | 981 | 978 | 985.5 | 974.3 | 815.4 | 990 |  |  | 912 | 714.8 | 1010.7 |  | 1073.1 | 981.3 | 1022.4 | 982.6 | 983.4 | 979.7 | 988.9 | 981 | 985.5 | 979 | 1000.6 | 986 | 1105.5 | 1188.8 | 828 | 871 | 751 | 629 | 772 | 902.8 | 1059.5 | 1133.8 | 1090 | 1084.9 | 1055.5 | 1081 | 1123 | 1138.3 | 945 | 1042.4 | 963.5 | 990.2 | 920.3 |  | 1330 | 1061 | 380 | 988.4 | 939 |  |  | 912 | 951 | 990 | 951 | 901 | 29.93 | 37.7 | 4.92 | 9.3 |  | 4.98 | 4.91 |  |  | 88901648.079 | 283689.817 | 61784411.924 | 63491.708 | 89579196.273 | 189329.138 | 65228511.671 | 58871.128 | 336590668.94 | 91700.297 | 66297.518 | 8.941 | 65634.018 | 12.884 | 65290.681 | 23.27 | 52393.732 | 28.544 | 249392.972 | 95.681 | 131909.711 | 249297.291 | 13.25 | 4.98 | 4.91 | 29.93 | 37.7 | 4.92 | 9.3 | 250120.88
2025-07-15 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:09 | 18:39 | 947.2 | 951 | 880 | 861 | 965.2 | 892.1 | 881 | 879 | 930.4 | 933.5 | 874 | 891 | 894 | 801 | 890 | 901.3 | 894.1 | 871 | 972.4 | 951 | 888 | 871.1 | 957 | 1001 | 951 | 954 | 949.1 | 990 | 969.6 | 981 | 1003 | 990 | 824.3 | 1078 | 855.1 | 972 | 858.8 | 861.2 | 867.5 | 861.9 | 868.7 | 869 | 864 | 861 | 897.9 | 898.6 | 951 | 856.9 | 899.8 | 898.6 | 867 | 879 | 1009.4 | 962.8 | 928.7 | 997.2 | 987 | 856 | 990 | 1021.8 | 871.8 | 1005 | 855.1 | 802.9 | 969.7 | 963.8 | 976.6 | 952.9 | 895.2 | 889.6 | 900.9 | 897 | 865.8 | 896.5 | 1019.9 | 1001.6 | 1021.1 | 901.2 | 899.1 | 982.1 | 907.1 | 867.6 | 906.2 | 917.3 | 904.5 | 908.9 | 896.4 | 893.2 | 901.1 | 896.9 | 921.5 | 973.4 | 861 | 871 | 998.3 | 880.4 | 891.4 | 896.9 | 896.6 | 888.7 | 900 | 892.1 | 869 | 891.7 | 968.7 | 859 | 981 | 978 | 869.8 | 970.7 | 939 | 951.5 | 990.1 | 971.8 | 885 | 868.7 | 957.8 | 961 | 981 | 863.4 | 874.6 | 975.8 | 973 | 862.7 | 864 | 980.9 | 881.9 | 879 | 995.6 | 986.7 | 933.9 | 962.4 | 980.3 | 805.7 | 956 | 939.7 | 924.5 | 958.1 | 901 | 890 | 962.7 | 947.2 | 888 | 950.7 | 867 | 965.7 | 888.9 | 825.6 | 960.5 | 969.5 | 977.7 | 898.5 | 971 | 898.9 | 887.3 | 878.1 | 887.1 | 881.5 | 877 | 881 | 989.2 | 873 | 951.9 | 985.6 | 998 | 920.3 | 871 | 961 | 894.2 | 881 | 918.3 | 918.7 | 977 | 880.4 | 1009.1 | 858.9 | 861.7 | 867 | 959 | 869 | 955 | 965 | 955.5 | 901 | 918.6 | 958 | 906.6 | 901 | 896.8 | 923 | 851.9 | 855 | 877 | 858 | 866 | 872 | 720 | 881 |  |  | 775.6 | 626 | 891 |  | 949 | 867 | 870.6 | 859 | 871 | 864 | 879 | 890 | 874.3 | 860.8 | 869 | 906.9 | 980 | 1018.5 | 758 | 768 | 671.4 | 554.3 | 674 | 778.4 | 932.4 | 997.3 | 955.8 | 930 | 936.5 | 961.5 | 994.3 | 976.2 | 829 | 902.1 | 847 | 881 | 795.1 |  | 1191 | 934 | 331.1 | 873 | 825.3 |  |  | 801 | 854 | 788 | 839 | 784 | 30.41 | 39.15 | 2.63 | 6.1 |  | 4.41 | 4.21 |  |  | 88960403.509 | 283698.758 | 61841455.326 | 63504.592 | 89637589.055 | 189352.408 | 65273672.295 | 58899.672 | 336809868.235 | 91795.978 | 58755.43 | 8.941 | 57043.402 | 12.884 | 58392.782 | 23.27 | 45160.624 | 28.544 | 219199.295 | 95.681 | 115777.007 | 219103.614 | 13.5 | 4.41 | 4.21 | 30.41 | 39.15 | 2.63 | 6.1 | 220029.5
2025-07-16 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:22 | 18:41 | 797.6 | 789 | 727 | 733.2 | 806.7 | 744.8 | 736.2 | 730.6 | 761 | 782.9 | 726 | 744 | 727 | 671 | 737.7 | 735.8 | 741.4 | 734 | 799.9 | 809.7 | 734.1 | 727.8 | 790 | 819 | 795 | 795.6 | 784.8 | 844.9 | 806.8 | 840.1 | 845.5 | 836.5 | 688 | 919 | 725 | 812 | 736.2 | 741 | 738 | 732 | 745 | 732 | 729 | 717.4 | 757.8 | 758.4 | 791 | 720.2 | 756 | 755 | 723 | 718.4 | 839.4 | 823 | 791 | 835.8 | 841.9 | 757.9 | 834.9 | 837.7 | 731.3 | 829.1 | 735 | 661 | 823 | 820 | 820.1 | 797.8 | 757.7 | 758.1 | 755.7 | 748.7 | 735 | 721 | 832 | 847.1 | 842 | 739 | 752.7 | 809 | 751.8 | 761.4 | 751.6 | 762.5 | 747.8 | 756 | 741.6 | 740.1 | 746.3 | 743.7 | 766.2 | 812.7 | 736.1 | 734.5 | 835.5 | 751.6 | 754.6 | 744 | 741 | 732 | 725 | 739 | 745 | 750 | 828.1 | 729 | 812 | 812.5 | 745 | 840.2 | 791.3 | 812.4 | 846.5 | 836.7 | 728.6 | 745.3 | 814 | 834 | 828.6 | 748 | 728 | 808 | 825.8 | 723 | 724.7 | 844.8 | 718.1 | 723 | 829.2 | 811 | 783.9 | 807.1 | 815.7 | 671 | 790 | 783 | 780.6 | 801 | 779 | 743 | 805.6 | 789.3 | 751 | 793 | 724 | 811.1 | 748.4 | 678 | 813 | 797.7 | 789 | 736 | 814.5 | 743 | 741 | 750.7 | 744 | 738 | 731 | 725 | 797.6 | 726 | 809 | 804 | 840.9 | 749.4 | 737.5 | 813 | 713.2 | 748 | 750.6 | 749.6 | 801 | 747 | 817.3 | 737 | 727.9 | 734 | 819 | 732.4 | 775 | 821 | 807 | 772.5 | 775 | 813 | 741.2 | 753.4 | 745 | 798 | 734 | 726 | 739 | 735 | 734.9 | 723 | 601 | 734 |  |  | 656 | 523 | 734 |  | 794 | 728 | 746.4 | 724 | 725.6 | 737 | 725 | 740 | 719.4 | 734.1 | 729.1 | 741 | 810.2 | 855 | 634 | 644 | 561.5 | 455.5 | 567.5 | 664.1 | 771 | 836 | 807.6 | 785.6 | 756 | 814.5 | 823 | 822 | 714 | 756 | 713 | 734 | 691 |  | 1000.5 | 790 | 274 | 729 | 701 |  |  | 666.5 | 709 | 665 | 701 | 656 | 29.38 | 36.95 | 1.39 | 6.5 |  | 3.65 | 3.55 |  |  | 89009374.667 | 283707.699 | 61889621.133 | 63517.476 | 89685651.485 | 189375.678 | 65311941.907 | 58928.216 | 336993168.642 | 91891.659 | 48971.158 | 8.941 | 48165.807 | 12.884 | 48062.43 | 23.27 | 38269.612 | 28.544 | 183300.407 | 95.681 | 97115.14 | 183204.726 | 13.3167 | 3.65 | 3.55 | 29.38 | 36.95 | 1.39 | 6.5 | 184352.8
2025-07-17 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:24 | 18:25 | 796.9 | 798 | 735 | 744 | 811.8 | 751 | 744 | 751 | 767 | 791.9 | 740 | 756 | 735 | 687 | 748 | 755 | 753.5 | 752 | 818.6 | 827.7 | 750.7 | 748.4 | 824.1 | 843.8 | 815 | 830.7 | 799.7 | 854.4 | 827.5 | 852.5 | 847.6 | 845.8 | 701.8 | 935.1 | 739.2 | 825 | 750.9 | 749 | 745 | 748.3 | 755 | 742 | 739 | 733.6 | 769.6 | 768 | 801 | 736.4 | 767 | 762.3 | 735 | 739 | 839.1 | 825 | 801 | 838.9 | 851 | 774 | 852 | 858.4 | 739.8 | 843.8 | 744 | 678.9 | 823.7 | 821 | 825.2 | 806.6 | 764.7 | 765.6 | 767.5 | 764.4 | 755.2 | 759.4 | 852 | 864.9 | 860 | 765 | 770.2 | 840.7 | 768 | 765 | 771.4 | 772.7 | 754 | 765 | 754.6 | 751.5 | 763.5 | 757.7 | 775.4 | 821.7 | 762.2 | 747.5 | 842.7 | 754.3 | 764.6 | 763.1 | 745.4 | 753.2 | 762.9 | 761.6 | 759.8 | 765 | 840.2 | 737.6 | 829.8 | 823.6 | 755.4 | 846.6 | 812 | 817 | 857 | 844 | 751.8 | 751.1 | 826.8 | 849.6 | 838.7 | 751.1 | 733.8 | 829.7 | 829.6 | 737.5 | 732.7 | 849.7 | 741.6 | 747.7 | 835.3 | 826.3 | 796.5 | 816.2 | 829.2 | 677.7 | 795.5 | 787.6 | 789 | 804 | 791 | 751.2 | 816.3 | 800.8 | 756.4 | 802.3 | 733 | 817 | 761.3 | 681 | 820 | 801 | 796 | 746.1 | 824.3 | 756.1 | 766.7 | 758.4 | 754.4 | 758.7 | 747.6 | 736.7 | 816.8 | 747 | 819.6 | 817.3 | 854.9 | 772.1 | 749.9 | 821.6 | 729.7 | 758 | 770.8 | 774.3 | 822 | 757 | 835.2 | 747 | 738.7 | 745 | 833 | 751 | 789.5 | 836.6 | 827 | 792.7 | 790.7 | 823 | 757.6 | 769 | 753 | 814 | 751.7 | 744.7 | 758.8 | 756.5 | 769.1 | 745 | 621 | 779.1 |  |  | 667.8 | 535 | 749 |  | 812 | 747 | 770.4 | 744 | 741 | 754.8 | 733.4 | 756.7 | 738.8 | 755 | 743 | 776.6 | 827 | 864.4 | 648.8 | 656 | 564.1 | 484.8 | 581.2 | 664.2 | 793.9 | 844.9 | 816.7 | 801.1 | 801.1 | 823 | 843.7 | 828.8 | 733.3 | 768.8 | 723.4 | 754.4 | 709 |  | 995.6 | 810.1 | 281 | 742.2 | 714.1 |  |  | 688.1 | 729 | 682.2 | 721.1 | 674.1 | 29.54 | 38.29 | 0.78 | 4.9 |  | 3.67 | 3.55 |  |  | 89059212.706 | 283716.64 | 61938214.608 | 63530.36 | 89734693.704 | 189398.948 | 65350923.465 | 58956.76 | 337179476.796 | 91987.34 | 49838.039 | 8.941 | 48593.475 | 12.884 | 49042.219 | 23.27 | 38981.558 | 28.544 | 186308.154 | 95.681 | 98409.689 | 186212.473 | 13.0167 | 3.67 | 3.55 | 29.54 | 38.29 | 0.78 | 4.9 | 187729.2
2025-07-18 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:33 | 18:25 | 335 | 341 | 314.6 | 311 | 339 | 309 | 311.8 | 314 | 324 | 324 | 318 | 308.1 | 306 | 287 | 306 | 311.5 | 306 | 316.7 | 331 | 335 | 309 | 315.5 | 336.1 | 355 | 338 | 332.6 | 342.7 | 343.6 | 352.8 | 349.8 | 352.5 | 357.1 | 297.6 | 389.7 | 308.4 | 348.1 | 307.7 | 311.2 | 313.2 | 312.9 | 307.8 | 315.2 | 308.3 | 310.8 | 311.2 | 306.7 | 335.6 | 309.5 | 321 | 329 | 317.5 | 310.7 | 351 | 352.8 | 339 | 350.2 | 347.7 | 310.2 | 353.4 | 357.8 | 317.1 | 347.6 | 311.2 | 273.1 | 347.8 | 346.1 | 348.6 | 340.3 | 317.3 | 316.8 | 320.8 | 317.6 | 327.8 | 320 | 367.3 | 362.3 | 367.2 | 322.3 | 315.6 | 352.8 | 320.3 | 325.7 | 319.7 | 320.2 | 312.9 | 323.4 | 314.4 | 315.2 | 319.6 | 317 | 326.8 | 346.6 | 325.8 | 322.6 | 358.7 | 312.8 | 319 | 318.8 | 321.4 | 313.5 | 318.6 | 317.7 | 323 | 315.7 | 348.6 | 312.1 | 351 | 342.1 | 313 | 349.2 | 335.3 | 342.2 | 360.2 | 353.7 | 318.3 | 307.3 | 347.1 | 348.1 | 347.2 | 308.8 | 304.5 | 346.9 | 350.8 | 306.3 | 311 | 350.4 | 305.3 | 308.7 | 347.6 | 344.3 | 345.6 | 335.8 | 343.2 | 293 | 347.7 | 330.9 | 329.5 | 346.2 | 337.1 | 318.6 | 337 | 332.1 | 314.6 | 347.3 | 312.1 | 340.1 | 310.5 | 287.1 | 336 | 340.1 | 343.8 | 313.1 | 348.1 | 312.2 | 310.5 | 306.8 | 309 | 311.2 | 311.1 | 306.8 | 341.2 | 312.1 | 343.5 | 339.5 | 351.6 | 319 | 307.6 | 339.3 | 302.7 | 314.6 | 323 | 327 | 346.6 | 328 | 342.1 | 311.2 | 314.2 | 307.6 | 351.2 | 308 | 338 | 345 | 342 | 319.2 | 334 | 346 | 327 | 321 | 318.9 | 341.2 | 316.1 | 305.3 | 314.2 | 319.4 | 311.1 | 308 | 254 | 322 |  |  | 275 | 221 | 315.8 |  | 338.7 | 307.8 | 320.7 | 306.9 | 312 | 319 | 321 | 321.4 | 320 | 322.4 | 314 | 321.3 | 349 | 351.6 | 267 | 276.3 | 235.8 | 198.7 | 245 | 281 | 325 | 345.6 | 335.2 | 335 | 332.3 | 339.9 | 345.9 | 353.1 | 298.6 | 321 | 301 | 317 | 289 |  | 415 | 339 | 116 | 312 | 307 |  |  | 288.7 | 301 | 279 | 302 | 282.2 | 26.7 | 35.9 | 1.21 | 7.8 |  | 1.57 | 1.41 |  |  | 89080585.051 | 283725.581 | 61958966.394 | 63543.244 | 89754674.656 | 189422.218 | 65367160.619 | 58985.304 | 337257621.94 | 92083.021 | 21372.345 | 8.941 | 20751.786 | 12.884 | 19980.952 | 23.27 | 16237.154 | 28.544 | 78145.144 | 95.681 | 42102.306 | 78049.463 | 12.8667 | 1.57 | 1.41 | 26.7 | 35.9 | 1.21 | 7.8 | 78405.8
2025-07-19 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:15 | 18:38 | 1251 | 1276 | 1180 | 1175 | 1267 | 1171 | 1178 | 1182 | 1201 | 1212 | 1182 | 1169 | 1169 | 1071 | 1174 | 1180 | 1173 | 1184 | 1265 | 1271 | 1165 | 1170.7 | 1275 | 1319.7 | 1269 | 1262.1 | 1259 | 1319 | 1311.8 | 1315 | 1300.6 | 1320.4 | 1101 | 1451 | 1170.6 | 1291 | 1155 | 1164 | 1161 | 1156 | 1159 | 1163 | 1159.8 | 1163 | 1174 | 1169 | 1262.2 | 1159 | 1212 | 1209 | 1163.5 | 1169 | 1321 | 1316.4 | 1264 | 1318.8 | 1326 | 1156 | 1314 | 1329.6 | 1172.1 | 1322 | 1164 | 1051 | 1290 | 1299 | 1304 | 1310.1 | 1167 | 1174 | 1169 | 1176 | 1181 | 1077 | 1324 | 1333 | 1329 | 1190 | 1181 | 1302 | 1190 | 1200 | 1190 | 1184 | 1181 | 1172 | 1090 | 1174 | 1183 | 1189 | 1227 | 1314 | 1176 | 1187 | 1335.6 | 1168 | 1171.2 | 1182.6 | 1164.6 | 1172.5 | 1185.7 | 1169.7 | 1166.7 | 1173.5 | 1298.4 | 1166 | 1301 | 1301 | 1191.7 | 1330.7 | 1249.6 | 1278.3 | 1320.3 | 1306.9 | 1201.6 | 1194.1 | 1301 | 1200.3 | 1292.8 | 1204.2 | 1197.5 | 1298 | 1302 | 1161 | 1161.9 | 1313.9 | 1167 | 1160 | 1325.7 | 1309.7 | 1253.7 | 1283.6 | 1290 | 1101 | 1290 | 1261.1 | 1230.4 | 1280 | 1264 | 1190 | 1278.6 | 1259 | 1167 | 1291 | 1156.2 | 1288.3 | 1169 | 1090 | 1285.4 | 1267 | 1273 | 1190 | 1299.7 | 1169 | 1174.6 | 1168 | 1173 | 1169 | 1177 | 1172.2 | 1312.6 | 1174.6 | 1277 | 1303.5 | 1323 | 1212 | 1140.7 | 1282 | 1166 | 1183 | 1209 | 1225 | 1282 | 1191 | 1301 | 1160.7 | 1134 | 1144 | 1267 | 1134 | 1221 | 1265 | 1269 | 1221.1 | 1240.7 | 1277 | 1200.7 | 1189 | 1209.9 | 1233 | 1156 | 1163.2 | 1159.5 | 1171.2 | 1162.1 | 1152.9 | 970.1 | 1149 |  |  | 1050 | 841 | 1176 |  | 1204 | 1159 | 1171 | 1176 | 1168 | 1181.2 | 1174 | 1170 | 1181 | 1161.8 | 1171.1 | 1180.2 | 1321.1 | 1329 | 1000 | 1021 | 870 | 724 | 910 | 1032 | 1224 | 1322 | 1267 | 1281 | 1221 | 1265 | 1321 | 1321 | 1107 | 1218 | 1110 | 1176.2 | 1091 |  | 1554 | 1234.7 | 436 | 1173 | 1145.2 |  |  | 1070 | 1122 | 1034 | 1101 | 955 | 30.63 | 42.45 | 2.31 | 5.7 |  |  | 5.81 |  |  | 89160578.553 | 283734.522 | 62036183.614 | 63556.128 | 89832801.551 | 189445.488 | 65423608.067 | 59013.848 | 337549193.171 | 92178.702 | 79993.502 | 8.941 | 77217.22 | 12.884 | 78126.895 | 23.27 | 56447.448 | 28.544 | 291571.231 | 95.681 | 157188.897 | 291475.55 | 13.3833 | 0 | 5.81 | 30.63 | 42.45 | 2.31 | 5.7 | 292631.9
2025-07-20 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:25 | 18:37 | 1421 | 1424 | 1312 | 1320 | 1434.2 | 1312 | 1323 | 1321 | 1344.2 | 1369 | 1312 | 1315 | 1327 | 1178 | 1282 | 1307 | 1300 | 1321 | 1432.4 | 1432 | 1301 | 1313.4 | 1400 | 1487 | 1444 | 1432 | 1405.7 | 1486.8 | 1427.5 | 1482.5 | 1467 | 1474.2 | 1219.1 | 1633.4 | 1263.4 | 1421 | 1315.6 | 1275 | 1275 | 1282.7 | 1272 | 1289 | 1264 | 1285 | 1280 | 1301 | 1378 | 1270 | 1322 | 1320 | 1269 | 1289.5 | 1424 | 1437.6 | 1381 | 1482 | 1476.7 | 1304.5 | 1483.5 | 1488.3 | 1304.2 | 1429 | 1274 | 1178 | 1432 | 1440.1 | 1434 | 1421.7 | 1302 | 1309 | 1301 | 1312 | 1310 | 1322 | 1485.6 | 1479.4 | 1472 | 1321 | 1319 | 1432 | 1325 | 1321 | 1328 | 1303 | 1289 | 1297.8 | 1307 | 1311 | 1328 | 1315 | 1368.1 | 1423 | 1290 | 1310 | 1495.9 | 1310 | 1305 | 1312 | 1303 | 1320.7 | 1300 | 1287 | 1304 | 1296 | 1421 | 1271 | 1429 | 1411 | 1301.4 | 1440.3 | 1371 | 1395.6 | 1428.9 | 1416.7 | 1323.7 | 1300.7 | 1410 | 1423 | 1434 | 1316.7 | 1319.6 | 1429 | 1439 | 1268 | 1273 | 1424 | 1271 | 1277 | 1425 | 1434 | 1381 | 1389 | 1378 | 1184 | 1374 | 1371.2 | 1380.8 | 1366 | 1322.7 | 1288 | 1367 | 1371 | 1281 | 1377 | 1277 | 1365 | 1271 | 1172 | 1374 | 1380.8 | 1369 | 1278 | 1423 | 1277 | 1267 | 1264.5 | 1281 | 1270 | 1301 | 1305 | 1420.4 | 1266.5 | 1418 | 1404.8 | 1475.8 | 1336.9 | 1267 | 1409 | 1290 | 1309 | 1350.9 | 1352.5 | 1415 | 1321 | 1452.4 | 1273 | 1274 | 1270 | 1429 | 1255 | 1355 | 1407 | 1424 | 1354 | 1371 | 1412 | 1312.7 | 1335 | 1311.6 | 1359 | 1282 | 1307.1 | 1255 | 1298.2 | 1301 | 1248.7 | 1053.6 | 1302 |  |  | 1139 | 924 | 1305.9 |  | 1388.9 | 1297 | 1301.6 | 1289.7 | 1288.7 | 1282 | 1289 | 1278 | 1299 | 1291 | 1273.7 | 1301 | 1433.5 | 1479.6 | 1101 | 1143 | 967 | 801 | 990.3 | 1163 | 1364 | 1478.6 | 1408 | 1380.1 | 1409.6 | 1417.7 | 1470.1 | 1432.4 | 1247.1 | 1323.1 | 1255 | 1278 | 1188.9 |  | 1701 | 1374 | 490 | 1277 | 1254 |  |  | 1205 | 1270 | 1139 | 1234 | 1155 | 31.33 | 44.09 | 2.44 | 5.7 |  |  | 6.19 |  |  | 89247304.297 | 283743.463 | 62119877.386 | 63569.012 | 89917631.181 | 189468.758 | 65490845.845 | 59042.392 | 337871388.134 | 92274.383 | 86725.744 | 8.941 | 83693.772 | 12.884 | 84829.63 | 23.27 | 67237.778 | 28.544 | 322194.963 | 95.681 | 170397.691 | 322099.282 | 13.2 | 0 | 6.19 | 31.33 | 44.09 | 2.44 | 5.7 | 323299.9
2025-07-21 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:50 | 18:36 | 810 | 832 | 764 | 757 | 821 | 750 | 764 | 771 | 787 | 790.1 | 765 | 747 | 763 | 690 | 762.6 | 757.9 | 736.6 | 761.2 | 815.2 | 824.9 | 747 | 758 | 809 | 844 | 816 | 814 | 791 | 854.8 | 818.5 | 855.6 | 819 | 843 | 701.4 | 933 | 746.4 | 832 | 740.9 | 734 | 730 | 742.2 | 731 | 752.5 | 739 | 752.2 | 744 | 749 | 798 | 734 | 767 | 771 | 727 | 729 | 841 | 817.9 | 798 | 849.8 | 849.9 | 739 | 843 | 839 | 732.9 | 841 | 753 | 690 | 833 | 829.4 | 837.1 | 819.9 | 765.2 | 762.9 | 765.9 | 764 | 780 | 771.4 | 870.8 | 860.1 | 871.1 | 767 | 760.8 | 819.9 | 759.8 | 746 | 766 | 745.6 | 761.1 | 739 | 751.1 | 747.9 | 763.6 | 758.8 | 786.4 | 829.7 | 732 | 744 | 854.5 | 760.7 | 759.3 | 750.8 | 764.3 | 754.5 | 765.7 | 766.9 | 750.6 | 764.8 | 828.7 | 752.2 | 821.4 | 831 | 734.7 | 825.5 | 789.8 | 815 | 851 | 852.6 | 758.5 | 759.9 | 817.2 | 835 | 837 | 753.3 | 743.4 | 861.2 | 851.8 | 744 | 739 | 852 | 751 | 747 | 845 | 821 | 791.5 | 815.7 | 810.3 | 680 | 790 | 790.7 | 809 | 792.3 | 789 | 743 | 815.8 | 800.2 | 757.8 | 788 | 733 | 820.9 | 752.2 | 696.6 | 823.8 | 810.4 | 809 | 756 | 819.7 | 759 | 763.4 | 751.1 | 763.5 | 762.8 | 738.7 | 742 | 815.6 | 719 | 813 | 810 | 844 | 761 | 721 | 809 | 739.7 | 754 | 763.5 | 766 | 809 | 757 | 841.6 | 724 | 725 | 721 | 809 | 724 | 790 | 829 | 841 | 782.8 | 780.1 | 810 | 760 | 754 | 759.4 | 809 | 747.9 | 753.4 | 736.3 | 751.9 | 755 | 735 | 608.4 | 742 |  |  | 647.1 | 529 | 748 |  | 801 | 741 | 758.4 | 761.9 | 768 | 755.5 | 763.9 | 776.3 | 773.9 | 743.6 | 744 | 773.9 | 836.4 | 843.4 | 646 | 662 | 556.2 | 463 | 581 | 662.5 | 784.1 | 843.5 | 820.1 | 804.2 | 770 | 810.1 | 843.5 | 824.6 | 723.9 | 758.1 | 719.7 | 733 | 694.6 |  | 1005 | 801 | 287 | 739 | 728 |  |  | 690 | 731 | 654 | 709 | 687.7 | 31.33 | 38.57 | 1.33 | 3.9 |  |  | 3.4 |  |  | 89296740.341 | 283752.404 | 62168929.232 | 63581.896 | 89966282.038 | 189492.028 | 65529909.921 | 59070.936 | 338057477.186 | 92370.064 | 49436.044 | 8.941 | 49051.846 | 12.884 | 48650.857 | 23.27 | 39064.076 | 28.544 | 186089.052 | 95.681 | 98466.065 | 185993.371 | 12.7667 | 0 | 3.4 | 31.33 | 38.57 | 1.33 | 3.9 | 187263.7
2025-07-22 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:26 | 18:32 | 1291 | 1288.2 | 1186.5 | 1191 | 1295 | 1193 | 1229 | 1225 | 1243 | 1232 | 1244 | 1201.4 | 1224 | 1127 | 1224 | 1214.8 | 1212 | 1233 | 1322 | 1318 | 1226 | 1197 | 1331 | 1383 | 1327 | 1339 | 1289.7 | 1387.1 | 1338 | 1366 | 1339 | 1352 | 1136 | 1532 | 1194 | 1343 | 1221 | 1201 | 1196 | 1201 | 1205 | 1206 | 1201 | 1203 | 1198 | 1214 | 1301 | 1221 | 1247 | 1238 | 1190.3 | 1209 | 1388.8 | 1338.5 | 1291 | 1347.8 | 1361 | 1212 | 1341 | 1355 | 1199 | 1355 | 1196 | 1101 | 1333.6 | 1330.8 | 1342 | 1320.2 | 1234 | 1228 | 1239 | 1231 | 1234 | 1241 | 1396 | 1382 | 1392.1 | 1244 | 1241 | 1332 | 1224 | 1233 | 1223 | 1238 | 1242 | 1225 | 1234.9 | 1234.4 | 1231 | 1237.5 | 1262.7 | 1314.3 | 1219 | 1214 | 1348.5 | 1204 | 1210 | 1197 | 1201 | 1215 | 1202 | 1196 | 1208 | 1211 | 1358.8 | 1197 | 1361 | 1325.5 | 1208.7 | 1338 | 1286 | 1323 | 1351 | 1359 | 1234 | 1202.1 | 1333 | 1333 | 1327 | 1207 | 1203 | 1352.1 | 1364.3 | 1208 | 1217 | 1366.1 | 1211.2 | 1212 | 1339 | 1345 | 1315 | 1312 | 1301 | 1115 | 1301 | 1280 | 1285 | 1275 | 1245 | 1201 | 1302 | 1291 | 1216 | 1324 | 1191.3 | 1324 | 1213 | 1120 | 1329 | 1325 | 1326 | 1200 | 1370 | 1228 | 1206 | 1209 | 1201 | 1194 | 1190 | 1182 | 1317 | 1182 | 1325 | 1313 | 1361 | 1234 | 1206 | 1321 | 1191 | 1227.3 | 1231 | 1232 | 1334 | 1219 | 1351 | 1181 | 1178 | 1180 | 1323 | 1171 | 1267 | 1312 | 1321 | 1271 | 1280 | 1221 | 1219.5 | 1220 | 1224 | 1293 | 1191 | 1214.2 | 1203 | 1215 | 1221 | 1209 | 1021 | 1215 |  |  | 1049.3 | 854 | 1219 |  | 1321 | 1214 | 1216 | 1220.3 | 1202 | 1238 | 1213 | 1238 | 1231 | 1207 | 1218.9 | 1237 | 1333 | 1379.1 | 1044 | 1069 | 901 | 760 | 932 | 1072.3 | 1252.3 | 1376.4 | 1321.6 | 1291 | 1289 | 1325.5 | 1377.6 | 1333.6 | 1156 | 1231.5 | 1143 | 1190 | 1099.41 |  | 1601 | 1276 | 456 | 1212 | 1143 |  |  | 1124 | 1181 | 1065 | 1167 | 1071 | 32.95 | 48.46 | 1.66 | 6.9 |  |  | 5.81 |  |  | 89376458.593 | 283761.345 | 62247578.787 | 63594.78 | 90046789.695 | 189515.298 | 65592254.87 | 59099.48 | 338358429.854 | 92465.745 | 79718.252 | 8.941 | 78649.555 | 12.884 | 80507.657 | 23.27 | 62344.949 | 28.544 | 300952.668 | 95.681 | 158345.982 | 300856.987 | 13.1 | 0 | 5.81 | 32.95 | 48.46 | 1.66 | 6.9 | 302267.01
2025-07-23 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:27 | 18:33 | 481 | 486 | 444 | 441 | 486.6 | 451 | 452.7 | 448 | 460 | 473 | 450 | 449 | 457.5 | 404 | 449.1 | 451 | 454 | 449.6 | 494 | 487.1 | 453.6 | 456 | 493.6 | 511.2 | 492.9 | 487.7 | 490 | 503 | 501 | 512.2 | 505 | 507 | 421 | 556 | 451 | 509 | 450 | 448 | 458 | 459 | 443 | 457 | 451 | 446 | 448 | 452 | 481 | 448 | 463 | 468 | 455.3 | 452 | 512.4 | 503 | 486 | 500.1 | 511.4 | 449 | 511 | 507 | 451 | 498 | 447 | 401 | 491 | 497.4 | 500.1 | 488.4 | 457.3 | 458.4 | 461.1 | 455.6 | 447 | 461.5 | 512.6 | 497 | 513.4 | 456.8 | 449.4 | 486 | 452.2 | 458 | 455.9 | 457 | 446.8 | 451 | 445.1 | 445.3 | 454.8 | 452 | 465.3 | 492.6 | 447 | 454 | 507 | 451.7 | 447 | 451 | 449 | 449 | 453.2 | 456.7 | 451 | 451.9 | 501 | 449 | 498 | 497 | 445 | 501 | 476 | 494.2 | 496 | 507.1 | 452.4 | 441.9 | 503 | 508 | 497.1 | 446 | 453 | 501 | 503 | 451 | 453 | 501 | 448 | 453 | 497.3 | 492 | 478.6 | 477.4 | 483.8 | 412.2 | 471 | 474 | 472 | 484.5 | 471 | 441 | 478.6 | 489 | 454 | 495.1 | 455 | 476 | 445.2 | 414.2 | 488.4 | 491.7 | 473 | 446 | 497 | 453 | 453.6 | 445.6 | 454.4 | 452.74 | 443 | 444.8 | 497 | 448 | 492 | 494 | 502 | 452 | 441 | 490 | 445 | 466 | 453 | 464 | 501 | 461 | 497.7 | 439 | 444 | 447 | 503 | 442 | 484 | 495 | 488 | 461.6 | 476 | 487 | 461 | 451 | 455.2 | 474 | 455 | 447.2 | 447 | 451 | 448 | 444 | 381 | 451 |  |  | 377.4 | 315 | 461 |  | 497 | 444 | 448 | 455.5 | 458 | 449 | 451.2 | 452 | 465.5 | 456 | 449 | 462.5 | 503 | 515.3 | 391 | 387 | 332.1 | 284 | 350 | 397.2 | 471.6 | 514.1 | 487.9 | 482 | 475.5 | 485 | 501 | 497 | 424 | 461 | 439 | 446 | 411.4 |  | 612 | 481 | 167 | 452 | 432 |  |  | 416 | 445 | 395 | 432 | 412.5 | 29.49 | 32.13 | 1.64 | 5.3 |  |  | 2.1 |  |  | 89405617.291 | 283770.286 | 62277022.662 | 63607.664 | 90075838.802 | 189538.568 | 65615621.783 | 59128.024 | 338469279.863 | 92561.426 | 29158.698 | 8.941 | 29443.875 | 12.884 | 29049.107 | 23.27 | 23366.913 | 28.544 | 110850.009 | 95.681 | 58580.748 | 110754.328 | 13.1 | 0 | 2.1 | 29.49 | 32.13 | 1.64 | 5.3 | 112397.24
2025-07-24 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-25 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-26 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-27 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-28 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-29 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-30 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-31 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-01 | 2026 | 2025 |  |  | Aug-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-02 | 2026 | 2025 |  |  | Aug-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-03 | 2026 | 2025 |  |  | Aug-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Formulas:
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 12 | 0 |  | 0 |  | 35.4677 | 50.0389 | 2.5105 | 5.7 | [9 empty] | 0 |  |  |  | 66.75 | 6.6839 | 346441.9355 | 77.65% | 21.62% | 99.5% | 99.5%
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 12 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 100% |  |  | 100% |  |  |  |  | 21.45% | 0 | 343623.8886 | 61.9293 | 343561.9593 | 66.75 | 6.6839 | 346441.9355 | 77.65% | 21.62% | 99.5% | 99.5% | [9 empty] | 66.755
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 12 | 0 |  | 7.31 |  | 30.32 | 40.28 | 1.71 | 6.3 | 100% |  |  | 100% |  |  | 70.41% |  | 21.45% | 364093.2 | 343623.8886 | 61.9293 | 343561.9593 | 66.75 | 6.6839 | 346441.9355 | 77.65% | 21.62% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 7.18 |  | 25.08 | 40.95 | 1.76 | 5.3 | 99.99% |  |  | 100% |  |  | 71.69% |  | 21.45% | 354559 | 343623.8886 | 61.9293 | 343561.9593 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.87 |  | 26.5 | 39.7 | 1.9 | 5.9 | 99.79% |  |  | 100% |  |  | 72.98% |  | 20.89% | 341179 | 334708.37 | 58.016 | 334650.354 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 0 |  | 25.78 | 32 | 2.63 | 5.3 | 99.56% |  |  | 100% |  |  |  |  | 18.92% | 305040 | 303117.53 | 59.618 | 303057.912 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.1 |  | 35.1 | 50.1 | 1.5 | 4.3 | 100% |  |  | 100% |  |  | 77.97% |  | 19.82% | 318035 | 317553.665 | 61.857 | 317491.808 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.9 |  | 37.8 | 58.63 | 1.48 | 7.5 | 100% |  |  | 100% |  |  | 84.59% |  | 20.79% | 336772.2 | 333180.32 | 55.638 | 333124.682 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.92 |  | 39.3 | 47.4 | 1.2 | 5.33 | 100% |  |  | 100% |  |  | 71.24% |  | 20.54% | 331522.2 | 329112.576 | 55.361 | 329057.215 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.5257 |  | 41.9 | 51.1 | 1.1 | 3.13 | 99.98% |  |  | 100% |  |  | 72.85% |  | 19.81% | 324271 | 317387.001 | 54.398 | 317332.603 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.0578 |  | 43.9 | 51.1 | 1.1 | 3.13 | 99.72% |  |  | 100% |  |  | 73.87% |  | 18.65% | 315636 | 298762.742 | 57.574 | 298705.168 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.6268 |  | 39.9 | 50.1 | 1.1 | 3.4 | 100% |  |  | 100% |  |  | 75.08% |  | 17.6% | 289705 | 282018.859 | 38.081 | 281980.778 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 4.36 |  | 34.9 | 49 | 3 | 5 | 99.96% |  |  | 100% |  |  | 75.19% |  | 13.66% | 223694 | 218866.4 | 30.36 | 218836.04 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 4.88 |  | 36.6 | 55.86 | 2.52 | 13.1 | 100% |  |  | 100% |  |  | 78.29% |  | 15.92% | 257651 | 255074.896 | 62.053 | 255012.843 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.15 |  | 29.88 | 43.21 | 1.3 | 6.1 | 99.74% |  |  | 100% |  |  | 77.44% |  | 19.84% | 321089 | 317952.483 | 55.075 | 317897.408 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.14 |  | 31.82 | 40.8 | 3.02 | 7.1 | 99.85% |  |  | 100% |  |  | 81.2% |  | 20.77% | 335292 | 332864.4 | 60.962 | 332803.438 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.51 |  | 32.37 | 45.01 | 1.79 | 6.1 | 99.73% |  |  | 100% |  |  | 76.08% |  | 20.64% | 333086 | 330638.835 | 55.409 | 330583.426 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.23 |  | 32.7 | 43.6 | 1.6 | 6.5 | 99.99% |  |  | 100% |  |  | 76.67% |  | 19.9% | 326506 | 318888.957 | 53.177 | 318835.78 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.27 |  | 34.09 | 46.02 | 1.33 | 6.1 | 100% |  |  | 100% |  |  | 76.29% |  | 19.93% | 323020 | 319338.93 | 54.629 | 319284.301 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.11 |  | 35.7 | 46 | 0.6 | 6.78 | 100% |  |  | 100% |  |  | 75.56% |  | 19.24% | 314197 | 308209.27 | 60.571 | 308148.699 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.95 |  | 35.61 | 47.4 | 1.3 | 5.1 | 100% |  |  | 100% |  |  | 75.62% |  | 18.75% | 305558 | 300377.401 | 57.568 | 300319.833 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.87 |  | 35.4 | 46.4 | 1.2 | 5.3 | 99.63% |  |  | 100% |  |  | 75.46% | 0% | 18.46% | 312642 | 295745.199 | 72.432 | 295672.767 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.7 |  | 35.9 | 47.6 | 1.6 | 5.1 | 100% |  |  | 100% |  |  | 72.02% |  | 20.11% | 327345 | 322154.968 | 55.847 | 322099.121 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.75 |  | 37.4 | 47.37 | 2.08 | 5.4 | 99.65% |  |  | 100% |  |  | 71.15% |  | 20.01% | 328589 | 320631.049 | 59.061 | 320571.988 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 7.08 |  | 37.9 | 46.08 | 1.93 | 5.1 | 99.68% |  |  | 100% |  |  | 72.39% |  | 21.36% | 347261 | 342184.731 | 53.875 | 342130.856 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 7.22 |  | 38 | 46.1 | 2 | 5.3 | 99.68% |  |  | 100% |  |  | 72.85% |  | 21.92% | 355743 | 351160.163 | 54.826 | 351105.337 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 7.18 |  | 36.5 | 45.1 | 2.47 | 8.3 | 99.54% |  |  | 100% |  |  | 72.38% |  | 21.65% | 351420 | 346943.965 | 58.132 | 346885.833 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 7.1 |  | 37.08 | 47.02 | 1.4 | 6.5 | 99.47% |  |  | 100% |  |  | 69.54% |  | 20.57% | 335649 | 329619.258 | 51.72 | 329567.538 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.34 |  | 36.9 | 43.37 | 1.8 | 9.9 | 100% |  |  | 100% |  |  | 73.1% |  | 16.27% | 266123 | 260616.1 | 41.865 | 260574.235 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.5 |  | 38 | 45.8 | 1.9 | 6.1 | 94.93% |  |  | 100% |  |  | 73.17% |  | 16.77% | 274076 | 268672.384 | 58.871 | 268613.513 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.2 |  | 38.9724 | 45.8338 | 2.2649 | 5.9 | 99.92% |  |  | 100% |  |  | 73.78% |  | 19.06% | 306127.9 | 305402.761 | 61 | 305341.761 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.38 |  | 40 | 46 | 2.1 | 5.1 | 99.9% |  |  | 100% |  |  | 73.79% |  | 19.62% | 316090 | 314307.9307 | 54.003 | 314253.9277 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.29 |  | 35.51 | 43.47 | 2.54 | 6.7 | 99.9% |  |  | 100% |  |  | 73.11% |  | 19.16% | 308834.9 | 307007.4493 | 43.615 | 306963.8343 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 0 |  | 6.3 |  | 34.64 | 42.7 | 3.78 | 7.5 | 100% |  |  | 100% |  |  | 70.46% |  | 18.5% | 298175.2 | 296343.885 | 22.985 | 296320.9 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 0 |  | 4.16 |  | 26.59 | 33.02 | 3.03 | 7.7 | 99.95% |  |  | 100% |  |  | 75.68% |  | 13.12% | 211112 | 210230.583 | 81.52 | 210149.063 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 0 |  | 5.85 |  | 27 | 31 | 3.1 | 5.9 | 99.84% |  |  | 100% |  |  | 74.98% |  | 18.28% | 293330 | 292856.136 | 59.17 | 292796.966 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 0 |  | 6.49 |  | 33.65 | 43.22 | 1.9 | 7.5 | 99.87% |  |  | 100% |  |  | 74.05% |  | 20.02% | 322757 | 320844.417 | 64.162 | 320780.255 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 0 |  | 4.14 |  | 27.91 | 34.01 | 2.69 | 9.1 | 99.71% |  |  | 100% |  |  | 76.47% |  | 13.19% | 212087.7 | 211396.792 | 63.762 | 211333.03 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 12.25 | 0 |  | 6.31 |  | 30.59 | 43.32 | 1.89 | 5.1 | 99.57% |  |  | 100% |  |  | 75.86% |  | 19.95% | 321279.5 | 319633.678 | 103.308 | 319530.37 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 12.5667 | 0 |  | 5.46 |  | 26.11 | 40.91 | 2.1 | 4.9 | 73.28% |  |  | 100% |  |  | 55.99% |  | 12.74% | 213164.2 | 204058.977 | 2.116 | 204056.861 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 12.45 | 0 |  | 6.54 |  | 31.23 | 40.22 | 2.05 | 7.9 | 98.05% |  |  | 100% |  |  | 69.67% |  | 18.99% | 302578 | 304228.486 | 66.532 | 304161.954 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 12.15 | 0 |  | 6.68 |  | 32.39 | 43.99 | 1.81 | 7.1 | 99.59% |  |  | 100% |  |  | 73.52% |  | 20.46% | 328786 | 327888.986 | 53.566 | 327835.42 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 12.0833 | 0 |  | 5.78 |  | 29.02 | 40.1 | 1.6 | 5.4 | 99.62% |  |  | 100% |  |  | 73.67% |  | 17.74% | 283650.6625 | 284293.991 | 47.886 | 284246.105 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 12.45 | 0 |  | 6.7 |  | 31.8 | 43.4 | 1.5 | 4.8 | 99.89% |  |  | 100% |  |  | 75.16% |  | 20.98% | 338732 | 336183.752 | 63.231 | 336120.521 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 12.3167 | 0 |  | 6.85 |  | 35.13 | 43.88 | 1.88 | 7.3 | 99.98% |  |  | 100% |  |  | 75.16% |  | 21.45% | 345699 | 343701.784 | 61.428 | 343640.356 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 12.45 | 0 |  | 5.73 |  | 34.36 | 42.16 | 1.65 | 11.7 | 99.49% |  |  | 100% |  |  | 75.05% |  | 17.92% | 286967.7 | 287098.603 | 65.958 | 287032.645 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 12.9167 | 0 |  | 6.95 |  | 38.2 | 45.38 | 2.6 | 7.1 | 99.64% |  |  | 100% |  |  | 75.03% |  | 21.73% | 201945 | 348122.386 | 66.671 | 348055.715 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 12.9 | 0 |  | 6.81 |  | 38.52 | 46.82 | 2.05 | 5.8 | 99.94% |  |  | 100% |  |  | 74.49% |  | 21.14% | 334705.4 | 338665.544 | 60.012 | 338605.532 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 13.15 | 0 |  | 5.56 |  | 37.78 | 42.3 | 2.3 | 11.3 | 99.97% |  |  | 100% |  |  | 75.32% |  | 17.45% | 292468 | 279612.765 | 60.495 | 279552.27 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 12.9667 | 0 |  | 4.84 |  | 34.4 | 42 | 2.7 | 19.29 | 99.96% |  |  | 100% |  |  | 76.27% |  | 15.38% | 254893 | 246466.213 | 72.164 | 246394.049 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 13.15 | 0 |  | 6.4 |  | 32.3 | 41.68 | 1.14 | 4.7 | 99.66% |  |  | 100% |  |  | 76.6% |  | 20.43% | 332920 | 327298.332 | 54.8 | 327243.532 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 13.2167 | 0 |  | 6.27 |  | 36.2 | 40 | 1.1 | 4.2 | 99.62% |  |  | 100% |  |  | 77.25% |  | 20.18% | 324288 | 323348.624 | 55.371 | 323293.253 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 13.2 | 0 |  | 6.27 |  | 36.2 | 38.23 | 1.3 | 6.3 | 99.94% |  |  | 100% |  |  | 76.72% |  | 20.04% | 323147 | 321187.681 | 90.846 | 321096.835 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 13.1833 | 0 |  | 5.79 |  | 35.5 | 28 | 1.1 | 4.3 | 99.99% |  |  | 100% |  |  | 76.26% |  | 18.4% | 297837.6 | 294810.933 | 87.974 | 294722.959 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 13.2167 | 6.88 |  | 6.41 |  | 33.8 | 43.42 | 3.64 | 8.3 | 99.96% |  |  | 100% |  |  | 75.84% |  | 20.26% | 327534.8 | 324586.013 | 90.849 | 324495.164 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 13.2667 | 6.9 |  | 6.38 |  | 34.93 | 46.23 | 3.32 | 7.1 | 99.98% |  |  | 100% |  |  | 75.88% |  | 20.17% | 326090.97 | 323230.815 | 100.849 | 323129.966 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 13.2333 | 6.17 |  | 5.67 |  | 35.89 | 44.51 | 4.63 | 7.7 | 99.77% |  |  | 100% |  |  | 76.14% |  | 17.99% | 290997.7 | 288274.486 | 120.849 | 288153.637 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 12.7667 | 6.76 |  | 6.25 |  | 36.28 | 44.75 | 2.4 | 6.5 | 99.87% |  |  | 100% |  |  | 79.48% |  | 20.7% | 333824.3 | 331724.974 | 160.849 | 331564.125 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 13.2833 | 5.25 |  | 4.81 |  | 32.47 | 39.01 | 3.18 | 8.3 | 99.66% |  |  | 100% |  |  | 79.8% |  | 15.99% | 258237.06 | 256383.486 | 160.849 | 256222.637 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 13.35 | 6.45 |  | 5.98 |  | 34.17 | 39.27 | 1.95 | 5.7 | 99.93% |  |  | 100% |  |  | 77.18% |  | 19.23% | 311840.2 | 308223.809 | 158.849 | 308064.96 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 13.4167 | 6.79 |  | 6.28 |  | 36.79 | 48.09 | 1.97 | 4.9 | 65.94% |  |  | 100% |  |  | 50.45% |  | 13.2% | 212537.6 | 211625.783 | 159.849 | 211465.934 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 13.1667 | 5.38 |  | 4.87 |  | 35.73 | 41.95 | 2.07 | 9.69 | 86.27% |  |  | 100% |  |  | 66.65% |  | 13.53% | 218430.9 | 216832.746 | 161.849 | 216670.897 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 13.0167 | 5.85 |  | 5.34 |  | 36.45 | 45.55 | 2.33 | 7.9 | 100% |  |  | 100% |  |  | 77.05% |  | 17.14% | 277904.9 | 274797.158 | 161.849 | 274635.309 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 13.1833 | 5.3 |  | 4.85 |  | 33.5 | 42 | 3.1 | 8.3 | 99.72% |  |  | 100% |  |  | 76.48% |  | 15.46% | 251303.79 | 247759.346 | 159.812 | 247599.534 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 13.3167 | 4.91 |  | 4.4 |  | 31.9 | 40.8 | 3.4 | 6.2 | 99.77% |  |  | 100% |  |  | 77.97% |  | 14.29% | 229035.1 | 229145.811 | 156.812 | 228988.999 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 12.6833 | 5.82 |  | 5.25 |  | 32.2 | 41.3 | 3.2 | 4.8 | 94.53% |  |  | 100% |  |  | 73.47% |  | 16.07% | 259288.99 | 257628.344 | 156.812 | 257471.532 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 13.2333 | 5.12 |  | 4.62 |  | 32.1 | 40.8 | 2.8 | 7.1 | 94.13% |  |  | 100% |  |  | 74.85% |  | 14.41% | 231929.06 | 230994.357 | 156.812 | 230837.545 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 13.3833 | 5.74 |  | 5.18 |  | 36.4 | 48 | 3.1 | 6.3 | 99.5% |  |  | 100% |  |  | 78.8% |  | 17.01% | 273632.5 | 272636.06 | 156.812 | 272479.248 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 13.5 | 6.7 |  | 6.3 |  | 36.8 | 52.03 | 3.2 | 8.3 | 95.71% |  |  | 100% |  |  | 74.99% |  | 19.69% | 317965 | 315512.697 | 154.875 | 315357.822 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 13.45 | 6.6 |  | 6.32 |  | 30.8 | 50.3 | 31.1 | 8.5 | 100% |  |  | 100% |  |  | 75.41% |  | 19.86% | 319248 | 318269.456 | 156.271 | 318113.185 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 13.4833 | 6.98 |  | 6.78 |  | 31.9 | 52.8 | 3.9 | 6.4 | 99.74% |  |  | 100% |  |  | 74.75% |  | 21.12% | 340883 | 338445.266 | 155.681 | 338289.585 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 13.4667 | 6.9 |  | 6.38 |  | 38.8 | 45.5 | 1.23 | 6.3 | 99.89% |  |  | 100% |  |  | 77.59% |  | 20.63% | 332985.59 | 330587.652 | 155.681 | 330431.971 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 13.4667 | 7.2 |  | 6.66 |  | 40.38 | 45.99 | 2.41 | 7.7 | 99.85% |  |  | 100% |  |  | 75.64% |  | 20.99% | 338140.4 | 336393.986 | 146.681 | 336247.305 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 13.4833 | 7.54 |  | 7.03 |  | 41.33 | 46.5 | 3.21 | 8.7 | 99.96% |  |  | 100% |  |  | 76.27% |  | 22.34% | 359956.5 | 358052.207 | 146.681 | 357905.526 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 13.45 | 7.17 |  | 6.59 |  | 40.35 | 47.76 | 2.22 | 5.5 | 100% |  |  | 100% |  |  | 76.48% |  | 21% | 338030.77 | 336579.164 | 146.681 | 336432.483 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 13.4333 | 6.58 |  | 6.05 |  | 39.97 | 49.84 | 2.3 | 5.5 | 100% |  |  | 100% |  |  | 76.02% |  | 19.16% | 309854.97 | 307152.908 | 146.681 | 307006.227 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 11.3833 | 5.96 |  | 5.45 |  | 39.42 | 48.96 | 3.4 | 12.9 | 100% |  |  | 100% |  |  | 76.09% |  | 17.28% | 279024.1 | 276945.719 | 146.681 | 276799.038 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 13.5833 | 6.54 |  | 6.01 |  | 37.79 | 49.04 | 1.63 | 4.9 | 99.99% |  |  | 100% |  |  | 76.05% |  | 19.04% | 307007.4 | 305232.082 | 146.681 | 305085.401 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 13.2333 | 4.87 |  | 4.49 |  | 34.83 | 42.57 | 3.24 | 10.7 | 99.78% |  |  | 100% |  |  | 76.17% |  | 14.25% | 229066.5 | 228426.298 | 146.681 | 228279.617 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 11.6667 | 6.29 |  | 5.78 |  | 32.82 | 40.29 | 3.89 | 8.5 | 99.58% |  |  | 100% |  |  | 78.46% |  | 18.89% | 303505.1 | 302835.605 | 143.681 | 302691.924 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 10.8833 | 4.44 |  | 3.98 |  | 33.67 | 42.05 | 2.77 | 8.9 | 100% |  |  | 100% |  |  | 79.43% |  | 13.17% | 212042.5 | 211172.845 | 143.681 | 211029.164 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 13.4667 | 5.32 |  | 4.96 |  | 31.72 | 42.78 | 1.64 | 5.1 | 99.56% |  |  | 100% |  |  | 78.39% |  | 16.2% | 261299.05 | 259670.743 | 135.681 | 259535.062 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 12.4333 | 4.53 |  | 4.17 |  | 30.22 | 39.34 | 3.06 | 9.5 | 99.98% |  |  | 100% |  |  | 81.17% |  | 14.1% | 227578.3 | 226079.287 | 135.681 | 225943.606 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 13.25 | 2.53 |  | 2.4 |  | 28.91 | 32.29 | 0.946 | 5.7 | 96.01% |  |  | 100% |  |  | 79.62% |  | 7.962% | 128207.03 | 127693.287 | 135.681 | 127557.606 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 13.5 | 5.62 |  | 5.19 |  | 31.15 | 42.22 | 1.35 | 6.1 | 98.93% |  |  | 100% |  |  | 76.07% |  | 16.45% | 264314.4 | 263653.358 | 133.681 | 263519.677 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 13.2167 | 5.81 |  | 5.3 |  | 33.23 | 41.42 | 1.87 | 4.9 | 99.87% |  |  | 100% |  |  | 79.53% |  | 17.56% | 282611.15 | 281490.64 | 133.681 | 281356.959 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 13.3 | 4.95 |  | 4.58 |  | 30.76 | 41.42 | 1.21 | 6.5 | 99.31% |  |  | 100% |  |  | 78.06% |  | 14.9% | 239843.7 | 238787.797 | 133.681 | 238654.116 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 13.3333 | 6.96 |  | 6.44 |  | 33.08 | 45.26 | 1.88 | 5.5 | 99.71% |  |  | 100% |  |  | 75.97% |  | 20.38% | 329656.49 | 326685.442 | 133.681 | 326551.761 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 13.65 | 6.57 |  | 6.18 |  | 33.46 | 42.64 | 3.12 | 7.5 | 99.86% |  |  | 100% |  |  | 78.29% |  | 20.16% | 324493.01 | 323091.37 | 120.681 | 322970.689 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 13.4333 | 6.68 |  | 6.3 |  | 34.28 | 42.05 | 4.04 | 8.1 | 99.96% |  |  | 100% |  |  | 76.9% |  | 20.19% | 325151.3 | 323519.832 | 116.681 | 323403.151 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 12.8833 | 6.01 |  | 5.64 |  | 31.5 | 41.46 | 2.01 | 6.7 | 99.37% |  |  | 100% |  |  | 76.06% |  | 17.87% | 287351.88 | 286457.904 | 105.681 | 286352.223 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 13.05 | 5.07 |  | 4.65 |  | 30.91 | 41.13 | 1.51 | 9.7 | 99.06% |  |  | 100% |  |  | 76.14% |  | 14.75% | 238197.7 | 236444.405 | 105.681 | 236338.724 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 13.1833 | 4.19 |  | 3.89 |  | 30.09 | 37.22 | 2.43 | 9.3 | 99.29% |  |  | 100% |  |  | 80.51% |  | 13.05% | 210024.2 | 209152.788 | 105.681 | 209047.107 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 13.05 | 3.23 |  | 3.03 |  | 29.64 | 35.33 | 1.69 | 4.3 | 99.32% |  |  | 100% |  |  | 81.73% |  | 10.32% | 166212.4 | 165401.16 | 95.681 | 165305.479 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | 13.15 | 2.61 |  | 2.41 |  | 27.91 | 32.27 | 0.185 | 4.7 | 98.74% |  |  | 100% |  |  | 81.56% |  | 8.19% | 132771 | 131303.317 | 95.681 | 131207.636 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | 13.4 | 4.34 |  | 4.07 |  | 30.38 | 37.35 | 1.48 | 7.1 | 99.5% |  |  | 100% |  |  | 78.27% |  | 13.27% | 213894.3 | 212734.465 | 95.681 | 212638.784 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | 13.3667 | 4.77 |  | 4.56 |  | 31.07 | 39.16 | 2.32 | 5.7 | 99.78% |  |  | 100% |  |  | 77.65% |  | 14.75% | 237266.1 | 236444.781 | 95.681 | 236349.1 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | 13.35 | 4.55 |  | 4.15 |  | 30.97 | 40.04 | 1.49 | 7.5 | 99.93% |  |  | 100% |  |  | 77.57% |  | 13.41% | 216167.6 | 214965.633 | 95.681 | 214869.952 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | 13.2167 | 5.37 |  | 5.13 |  | 31.55 | 42.78 | 1.29 | 4.3 | 98.88% |  |  | 100% |  |  | 77.69% |  | 16.61% | 267586.7 | 266122.048 | 95.681 | 266026.367 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | 13.2 | 4.72 |  | 4.5 |  | 32.64 | 41.48 | 1.41 | 3.9 | 99.97% |  |  | 100% |  |  | 77.29% |  | 14.49% | 233878.073 | 232266.206 | 95.681 | 232170.525 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | 13.4833 | 4.55 |  | 4.44 |  | 30.51 | 37.51 | 1.91 | 4.3 | 99.76% |  |  | 100% |  |  | 79.77% |  | 14.76% | 238029.5 | 236503.284 | 95.681 | 236407.603 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | 13.4167 | 6.66 |  | 6.3 |  | 34.05 | 43.94 | 1.76 | 6.5 | 100% |  |  | 100% |  |  | 77.03% |  | 20.22% | 325117.4 | 324045.375 | 95.681 | 323949.694 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | 12.1833 | 4.07 |  | 3.86 |  | 31.93 | 39.1 | 2.24 | 7.1 | 100% |  |  | 100% |  |  | 80.3% |  | 12.92% | 208916.3 | 206999.293 | 95.681 | 206903.612 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | 13.0667 | 2.41 |  | 2.21 |  | 27.48 | 31.37 | 1.28 | 6.1 | 100% |  |  | 100% |  |  | 78.31% |  | 7.212% | 117443.3 | 115623.948 | 95.681 | 115528.267 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | 13.5333 | 6.47 |  | 6.17 |  | 30.53 | 43.25 | 1.6 | 7.7 | 98.59% |  |  | 100% |  |  | 73.2% |  | 18.82% | 302424.37 | 301561.456 | 95.681 | 301465.775 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | 13.1833 | 4.09 |  | 3.83 |  | 29.65 | 36.39 | 1.47 | 11.3 | 99.81% |  |  | 100% |  |  | 76.09% |  | 12.14% | 196348.49 | 194629.863 | 95.681 | 194534.182 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | 12.9667 | 3.56 |  | 3.52 |  | 29.58 | 34.35 | 1.14 | 4.1 | 100% |  |  | 100% |  |  | 77.43% |  | 11.36% | 182953.6 | 182014.806 | 95.681 | 181919.125 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | 13.25 | 4.98 |  | 4.91 |  | 29.93 | 37.7 | 4.92 | 9.3 | 100% |  |  | 100% |  |  | 76.06% |  | 15.56% | 250120.88 | 249392.972 | 95.681 | 249297.291 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | 13.5 | 4.41 |  | 4.21 |  | 30.41 | 39.15 | 2.63 | 6.1 | 99.96% |  |  | 100% |  |  | 77.97% |  | 13.68% | 220029.5 | 219199.295 | 95.681 | 219103.614 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | 13.3167 | 3.65 |  | 3.55 |  | 29.38 | 36.95 | 1.39 | 6.5 | 99.94% |  |  | 100% |  |  | 77.31% |  | 11.44% | 184352.8 | 183300.407 | 95.681 | 183204.726 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | 13.0167 | 3.67 |  | 3.55 |  | 29.54 | 38.29 | 0.78 | 4.9 | 99.94% |  |  | 100% |  |  | 78.58% |  | 11.62% | 187729.2 | 186308.154 | 95.681 | 186212.473 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | 12.8667 | 1.57 |  | 1.41 |  | 26.7 | 35.9 | 1.21 | 7.8 | 99.94% |  |  | 100% |  |  | 82.93% |  | 4.872% | 78405.8 | 78145.144 | 95.681 | 78049.463 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | 13.3833 | 0 |  | 5.81 |  | 30.63 | 42.45 | 2.31 | 5.7 | 99.78% |  |  | 100% |  |  | 75.16% |  | 18.19% | 292631.9 | 291571.231 | 95.681 | 291475.55 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | 13.2 | 0 |  | 6.19 |  | 31.33 | 44.09 | 2.44 | 5.7 | 99.9% |  |  | 100% |  |  | 77.96% |  | 20.11% | 323299.9 | 322194.963 | 95.681 | 322099.282 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | 12.7667 | 0 |  | 3.4 |  | 31.33 | 38.57 | 1.33 | 3.9 | 99.89% |  |  | 100% |  |  | 81.95% |  | 11.61% | 187263.7 | 186089.052 | 95.681 | 185993.371 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | 13.1 | 0 |  | 5.81 |  | 32.95 | 48.46 | 1.66 | 6.9 | 99.86% |  |  | 100% |  |  | 77.58% |  | 18.78% | 302267.01 | 300952.668 | 95.681 | 300856.987 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | 13.1 | 0 |  | 2.1 |  | 29.49 | 32.13 | 1.64 | 5.3 | 99.87% |  |  | 100% |  |  | 79.01% |  | 6.914% | 112397.24 | 110850.009 | 95.681 | 110754.328 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Modelling New
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | CC*Bugt (MTD) | CC*Bugt (YTD) | Capacity | 66.755
1 | April | 4 | 2024-04-01 | 2024 | FY25 | 30 | 200.3 | 206.6 |  | 29.1001 |  | 10502 | 66.755 | 76.15% | 6.8867 | 0 | 0 | 0 | 350.0667 | 0 | 0 | 21.85% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
2 | May | 5 | 2024-05-01 | 2024 | FY25 | 31 | 197.9 | 191.7 |  | 33.4 |  | 9693 | 66.755 | 75.74% | 6.1839 | 0 | 0 | 0 | 312.6774 | 0 | 0 | 19.52% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
3 | June | 6 | 2024-06-01 | 2024 | FY25 | 30 | 165.8 | 157.1 |  | 34.8001 |  | 7976.9 | 66.755 | 76.06% | 5.2367 | 0 | 0 | 0 | 265.8967 | 0 | 0 | 16.6% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
4 | July | 7 | 2024-07-01 | 2024 | FY25 | 31 | 141.9 | 135 |  | 33.0999 |  | 6950.5 | 66.755 | 77.13% | 4.3548 | 0 | 0 | 0 | 224.2097 | 0 | 0 | 13.99% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
5 | August | 8 | 2024-08-01 | 2024 | FY25 | 31 | 145 | 143.9 |  | 31.8 |  | 7459 | 66.755 | 77.65% | 4.6419 | 0 | 0 | 0 | 240.6129 | 0 | 0 | 15.02% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
6 | September | 9 | 2024-09-01 | 2024 | FY25 | 30 | 153 | 163.3 |  | 31.1999 |  | 8419.6 | 66.755 | 77.24% | 5.4433 | 0 | 0 | 0 | 280.6533 | 0 | 0 | 17.52% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
7 | October | 10 | 2024-10-01 | 2024 | FY25 | 31 | 153.5 | 177.1 |  | 27.1001 |  | 9198.8 | 66.755 | 77.81% | 5.7129 | 0 | 0 | 0 | 296.7355 | 0 | 0 | 18.52% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
8 | November | 11 | 2024-11-01 | 2024 | FY25 | 30 | 117.4 | 144.5 |  | 20.9 |  | 7717.8 | 66.755 | 80.01% | 4.8167 | 0 | 0 | 0 | 257.26 | 0 | 0 | 16.06% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
9 | December | 12 | 2024-12-01 | 2024 | FY25 | 31 | 103.2 | 132.4 |  | 15.8915 |  | 7215.2 | 66.755 | 81.64% | 4.271 | 0 | 0 | 0 | 232.7484 | 0 | 0 | 14.53% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
10 | January | 1 | 2025-01-01 | 2025 | FY25 | 31 | 102.5 | 127.5 |  | 14.3999 |  | 6983 | 66.755 | 82.04% | 4.1129 | 0 | 0 | 0 | 225.2581 | 0 | 0 | 14.06% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
11 | February | 2 | 2025-02-01 | 2025 | FY25 | 28 | 134.2 | 162.2 |  | 17.8001 |  | 8614.6 | 66.755 | 79.56% | 5.7929 | 0 | 0 | 0 | 307.6643 | 0 | 0 | 19.2% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
12 | March | 3 | 2025-03-01 | 2025 | FY25 | 31 | 185.4 | 207.2 |  | 23.6002 |  | 10739.7 | 66.755 | 77.65% | 6.6839 | 3 | 20.0516 | 20.0516 | 346.4419 | 1039.3258 | 1039.3258 | 21.62% | 2.093% | 21.62% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
13 | April | 4 | 2025-04-01 | 2025 | FY26 | 30 | 167.2997 | 206.6 |  | 29.1001 |  | 10495.2627 | 66.755 | 76.1% | 6.8867 | 30 | 206.6 | 206.6 | 349.8421 | 10495.2627 | 10495.2627 | 21.84% | 21.84% | 21.84% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
14 | May | 5 | 2025-05-01 | 2025 | FY26 | 31 | 203.1012 | 191.7 |  | 33.4 |  | 9688.8168 | 66.755 | 75.71% | 6.1839 | 31 | 191.7 | 398.3 | 312.5425 | 9688.8168 | 20184.0795 | 19.51% | 19.51% | 20.65% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
15 | June | 6 | 2025-06-01 | 2025 | FY26 | 30 | 165.8 | 157.1 |  | 34.8001 |  | 7971.775 | 66.755 | 76.01% | 5.2367 | 30 | 157.1 | 555.4 | 265.7258 | 7971.775 | 28155.8545 | 16.59% | 16.59% | 19.31% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
16 | July | 7 | 2025-07-01 | 2025 | FY26 | 31 | 141.9 | 135 |  | 33.0999 |  | 6947.4741 | 66.755 | 77.09% | 4.3548 | 23 | 100.1613 | 655.5613 | 224.1121 | 5154.5775 | 33310.432 | 13.99% | 10.38% | 18.24% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
17 | August | 8 | 2025-08-01 | 2025 | FY26 | 31 | 145 | 143.9 |  | 31.8 |  | 7455.8025 | 66.755 | 77.62% | 4.6419 | 0 | 0 | 655.5613 | 240.5098 | 0 | 33310.432 | 15.01% | 0% | 18.24% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
18 | September | 9 | 2025-09-01 | 2025 | FY26 | 30 | 153 | 163.3 |  | 31.1999 |  | 8414.1736 | 66.755 | 77.19% | 5.4433 | 0 | 0 | 655.5613 | 280.4725 | 0 | 33310.432 | 17.51% | 0% | 18.24% |  | 66.755 |  |  |  | 99.5% | 99.5%
19 | October | 10 | 2025-10-01 | 2025 | FY26 | 31 | 153.5 | 177.1 |  | 27.1001 |  | 9194.8209 | 66.755 | 77.78% | 5.7129 | 0 | 0 | 655.5613 | 296.6071 | 0 | 33310.432 | 18.51% | 0% | 18.24% |  | 66.755 |  |  |  | 99.5% | 99.5%
20 | November | 11 | 2025-11-01 | 2025 | FY26 | 30 | 117.4 | 144.5 |  | 20.9 |  | 7712.8332 | 66.755 | 79.96% | 4.8167 | 0 | 0 | 655.5613 | 257.0944 | 0 | 33310.432 | 16.05% | 0% | 18.24% |  | 66.755 |  |  |  | 99.5% | 99.5%
21 | December | 12 | 2025-12-01 | 2025 | FY26 | 31 | 103.2 | 132.4 |  | 15.8915 |  | 7212.1488 | 66.755 | 81.6% | 4.271 | 0 | 0 | 655.5613 | 232.65 | 0 | 33310.432 | 14.52% | 0% | 18.24% |  | 66.755 |  |  |  | 99.5% | 99.5%
22 | January | 1 | 2026-01-01 | 2026 | FY26 | 31 | 102.5 | 127.5 |  | 14.3999 |  | 6979.9612 | 66.755 | 82.01% | 4.1129 | 0 | 0 | 655.5613 | 225.16 | 0 | 33310.432 | 14.05% | 0% | 18.24% |  | 66.755 |  |  |  | 99.5% | 99.5%
23 | February | 2 | 2026-02-01 | 2026 | FY26 | 28 | 134.2 | 162.2 |  | 17.8001 |  | 8661.6493 | 66.755 | 80% | 5.7929 | 0 | 0 | 655.5613 | 309.3446 | 0 | 33310.432 | 19.31% | 0% | 18.24% |  | 66.755 |  |  |  | 99.5% | 99.5%
24 | March | 3 | 2026-03-01 | 2026 | FY26 | 31 | 185.4 | 207.2 |  | 23.6002 |  | 10735.0943 | 66.755 | 77.61% | 6.6839 | 0 | 0 | 655.5613 | 346.2934 | 0 | 33310.432 | 21.61% | 0% | 18.24% |  | 66.755 |  |  |  | 99.5% | 99.5%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## Basic Data (hidden)
Equipment | Affected DC Capacity | Plant Equivalent Weightage | Fault Category Plant BD sheet | IS Number | LT Number | String Type | Equipment | Inverter Number | Status | Plant capacity | LT Number
BLK1INV1 | 289.25 | 0.4333% | Module | BLK1 | ACCB1 | Str_Typ1(445*50) | Tx | INV1 | Open | 66750 | LT1
BLK1INV2 | 289.25 | 0.4333% | Cables | BLK2 | ACCB2 | Str_Typ2 (330*60) | MVP | INV2 | Close |  | LT2
BLK1INV3 | 267 | 0.4% | String Fuses | BLK3 | ACCB3 | Str_Typ3(335*60) | Aux_Tx | INV3
BLK1INV4 | 267 | 0.4% | ACCB | BLK4 | ACCB4 | Str_Typ4(440*60) | MCR_MVP_IC_1 | INV4
BLK1INV5 | 289.25 | 0.4333% | Inverter | BLK5 | ACCB5 |  | MCR_MVP_IC_2 | INV5
BLK1INV6 | 267 | 0.4% | IDT | BLK6 | ACCB6 |  | MCR_MVP_IC_3 | INV6
BLK1INV7 | 267 | 0.4% | PTR | BLK7 | ACCB7 |  | MCR_MVP_IC_4 | INV7
BLK1INV8 | 267 | 0.4% | MV Panel | BLK8 | ACCB8 |  | MCR_MVP_OG | INV8
BLK1INV9 | 278.125 | 0.4167% | Metering System Plant |  |  |  | PWR_Tx | INV9
BLK1INV10 | 278.125 | 0.4167% | Grid System |  |  |  | Line_Bay1 | INV10
BLK1INV11 | 267 | 0.4% | Metering System Grid |  |  |  |  | INV11
BLK1INV12 | 267 | 0.4% | WMS |  |  |  |  | INV12
BLK1INV13 | 267 | 0.4% | MMS |  |  |  |  | INV13
BLK1INV14 | 244.75 | 0.3667% | Battery Charger_MCR |  |  |  |  | INV14
BLK1INV15 | 267 | 0.4% | IC_UPS |  |  |  |  | INV15
BLK1INV16 | 267 | 0.4% | IC_Auxiliary Tranformer |  |  |  |  | INV16
BLK1INV17 | 267 | 0.4% | IC_Auxiliary DB |  |  |  |  | INV17
BLK1INV18 | 267 | 0.4% | IC_SCADA Panel |  |  |  |  | INV18
BLK1INV19 | 289.25 | 0.4333% | Connectors |  |  |  |  | INV19
BLK1INV20 | 289.25 | 0.4333% | LT Panel |  |  |  |  | INV20
BLK1INV21 | 267 | 0.4% | SS |  |  |  |  | INV21
BLK1INV22 | 267 | 0.4% | Force Majeure |  |  |  |  | INV22
BLK1INV23 | 289.25 | 0.4333% | [5 empty] | INV23
BLK1INV24 | 300.375 | 0.45% | [5 empty] | INV24
BLK1INV25 | 289.25 | 0.4333% | [5 empty] | INV25
BLK1INV26 | 289.25 | 0.4333% | [5 empty] | INV26
BLK1INV27 | 289.25 | 0.4333% | [5 empty] | INV27
BLK1INV28 | 300.375 | 0.45% | [5 empty] | INV28
BLK1INV29 | 300.375 | 0.45% | [5 empty] | INV29
BLK1INV30 | 300.375 | 0.45% | [5 empty] | INV30
BLK1INV31 | 300.375 | 0.45% | [5 empty] | INV31
BLK1INV32 | 300.375 | 0.45% | [5 empty] | INV31
BLK2INV1 | 300.375 | 0.45% | [5 empty] | INV32
BLK2INV2 | 222.5 | 0.3333% | [5 empty] | All_Inv
BLK2INV3 | 111.25 | 0.1667%
BLK2INV4 | 267 | 0.4%
BLK2INV5 | 267 | 0.4%
BLK2INV6 | 267 | 0.4%
BLK2INV7 | 267 | 0.4%
BLK2INV8 | 267 | 0.4%
BLK2INV9 | 267 | 0.4%
BLK2INV10 | 267 | 0.4%
BLK2INV11 | 267 | 0.4%
BLK2INV12 | 267 | 0.4%
BLK2INV13 | 267 | 0.4%
BLK2INV14 | 267 | 0.4%
BLK2INV15 | 267 | 0.4%
BLK2INV16 | 289.25 | 0.4333%
BLK2INV17 | 267 | 0.4%
BLK2INV18 | 278.125 | 0.4167%
BLK2INV19 | 278.125 | 0.4167%
BLK2INV20 | 267 | 0.4%
BLK2INV21 | 267 | 0.4%
BLK2INV22 | 300.375 | 0.45%
BLK2INV23 | 300.375 | 0.45%
BLK2INV24 | 289.25 | 0.4333%
BLK2INV25 | 300.375 | 0.45%
BLK2INV26 | 300.375 | 0.45%
BLK2INV27 | 267 | 0.4%
BLK2INV28 | 300.375 | 0.45%
BLK2INV29 | 300.375 | 0.45%
BLK2INV30 | 267 | 0.4%
BLK2INV31 | 267 | 0.4%
BLK2INV32 | 239.25 | 0.3584%
BLK3INV1 | 267 | 0.4%
BLK3INV2 | 289.25 | 0.4333%
BLK3INV3 | 289.25 | 0.4333%
BLK3INV4 | 289.25 | 0.4333%
BLK3INV5 | 289.25 | 0.4333%
BLK3INV6 | 267 | 0.4%
BLK3INV7 | 267 | 0.4%
BLK3INV8 | 267 | 0.4%
BLK3INV9 | 267 | 0.4%
BLK3INV10 | 267 | 0.4%
BLK3INV11 | 267 | 0.4%
BLK3INV12 | 300.375 | 0.45%
BLK3INV13 | 300.375 | 0.45%
BLK3INV14 | 300.375 | 0.45%
BLK3INV15 | 267 | 0.4%
BLK3INV16 | 267 | 0.4%
BLK3INV17 | 289.25 | 0.4333%
BLK3INV18 | 267 | 0.4%
BLK3INV19 | 267 | 0.4%
BLK3INV20 | 267 | 0.4%
BLK3INV21 | 267 | 0.4%
BLK3INV22 | 267 | 0.4%
BLK3INV23 | 267 | 0.4%
BLK3INV24 | 267 | 0.4%
BLK3INV25 | 267 | 0.4%
BLK3INV26 | 267 | 0.4%
BLK3INV27 | 267 | 0.4%
BLK3INV28 | 278.125 | 0.4167%
BLK3INV29 | 289.25 | 0.4333%
BLK3INV30 | 267 | 0.4%
BLK3INV31 | 267 | 0.4%
BLK4INV1 | 300.375 | 0.45%
BLK4INV2 | 267 | 0.4%
BLK4INV3 | 267 | 0.4%
BLK4INV4 | 267 | 0.4%
BLK4INV5 | 267 | 0.4%
BLK4INV6 | 267 | 0.4%
BLK4INV7 | 267 | 0.4%
BLK4INV8 | 267 | 0.4%
BLK4INV9 | 267 | 0.4%
BLK4INV10 | 267 | 0.4%
BLK4INV11 | 300.375 | 0.45%
BLK4INV12 | 267 | 0.4%
BLK4INV13 | 300.375 | 0.45%
BLK4INV14 | 267 | 0.4%
BLK4INV15 | 267 | 0.4%
BLK4INV16 | 300.375 | 0.45%
BLK4INV17 | 289.25 | 0.4333%
BLK4INV18 | 289.25 | 0.4333%
BLK4INV19 | 300.375 | 0.45%
BLK4INV20 | 300.375 | 0.45%
BLK4INV21 | 267 | 0.4%
BLK4INV22 | 267 | 0.4%
BLK4INV23 | 267 | 0.4%
BLK4INV24 | 300.375 | 0.45%
BLK4INV25 | 300.375 | 0.45%
BLK4INV26 | 267 | 0.4%
BLK4INV27 | 267 | 0.4%
BLK4INV28 | 300.375 | 0.45%
BLK4INV29 | 300.375 | 0.45%
BLK4INV30 | 267 | 0.4%
BLK4INV31 | 267 | 0.4%
BLK5INV1 | 300.375 | 0.45%
BLK5INV2 | 267 | 0.4%
BLK5INV3 | 267 | 0.4%
BLK5INV4 | 300.375 | 0.45%
BLK5INV5 | 300.375 | 0.45%
BLK5INV6 | 289.25 | 0.4333%
BLK5INV7 | 289.25 | 0.4333%
BLK5INV8 | 289.25 | 0.4333%
BLK5INV9 | 244.75 | 0.3667%
BLK5INV10 | 286 | 0.4285%
BLK5INV11 | 286 | 0.4285%
BLK5INV12 | 286 | 0.4285%
BLK5INV13 | 286 | 0.4285%
BLK5INV14 | 278.125 | 0.4167%
BLK5INV15 | 267 | 0.4%
BLK5INV16 | 289.25 | 0.4333%
BLK5INV17 | 289.25 | 0.4333%
BLK5INV18 | 267 | 0.4%
BLK5INV19 | 289.25 | 0.4333%
BLK5INV20 | 267 | 0.4%
BLK5INV21 | 289.25 | 0.4333%
BLK5INV22 | 267 | 0.4%
BLK5INV23 | 244.75 | 0.3667%
BLK5INV24 | 267 | 0.4%
BLK5INV25 | 267 | 0.4%
BLK5INV26 | 289.25 | 0.4333%
BLK5INV27 | 267 | 0.4%
BLK5INV28 | 300.375 | 0.45%
BLK5INV29 | 267 | 0.4%
BLK5INV30 | 267 | 0.4%
BLK5INV31 | 267 | 0.4%
BLK5INV32 | 267 | 0.4%
BLK6INV1 | 267 | 0.4%
BLK6INV2 | 264 | 0.3955%
BLK6INV3 | 264 | 0.3955%
BLK6INV4 | 297 | 0.4449%
BLK6INV5 | 264 | 0.3955%
BLK6INV6 | 297 | 0.4449%
BLK6INV7 | 297 | 0.4449%
BLK6INV8 | 297 | 0.4449%
BLK6INV9 | 275 | 0.412%
BLK6INV10 | 264 | 0.3955%
BLK6INV11 | 297 | 0.4449%
BLK6INV12 | 264 | 0.3955%
BLK6INV13 | 275 | 0.412%
BLK6INV14 | 275 | 0.412%
BLK6INV15 | 275 | 0.412%
BLK6INV16 | 297 | 0.4449%
BLK6INV17 | 275 | 0.412%
BLK6INV18 | 297 | 0.4449%
BLK6INV19 | 264 | 0.3955%
BLK6INV20 | 264 | 0.3955%
BLK6INV21 | 264 | 0.3955%
BLK6INV22 | 297 | 0.4449%
BLK6INV23 | 264 | 0.3955%
BLK6INV24 | 286 | 0.4285%
BLK6INV25 | 297 | 0.4449%
BLK6INV26 | 297 | 0.4449%
BLK6INV27 | 275 | 0.412%
BLK6INV28 | 286 | 0.4285%
BLK6INV29 | 297 | 0.4449%
BLK6INV30 | 275 | 0.412%
BLK6INV31 | 275 | 0.412%
BLK6INV32 | 275 | 0.412%
BLK7INV1 | 286 | 0.4285%
BLK7INV2 | 264 | 0.3955%
BLK7INV3 | 264 | 0.3955%
BLK7INV4 | 264 | 0.3955%
BLK7INV5 | 264 | 0.3955%
BLK7INV6 | 264 | 0.3955%
BLK7INV7 | 264 | 0.3955%
BLK7INV8 | 220 | 0.3296%
BLK7INV9 | 264 | 0.3955%
BLK7INV10 | 257.4 | 0.3856%
BLK7INV11 | 190.35 | 0.2852%
BLK7INV12 | 270.6 | 0.4054%
BLK7INV13 | 244.75 | 0.3667%
BLK7INV14 | 267 | 0.4%
BLK7INV15 | 267 | 0.4%
BLK7INV16 | 267 | 0.4%
BLK7INV17 | 267 | 0.4%
BLK7INV18 | 267 | 0.4%
BLK7INV19 | 267 | 0.4%
BLK7INV20 | 267 | 0.4%
BLK7INV21 | 267 | 0.4%
BLK7INV22 | 267 | 0.4%
BLK7INV23 | 267 | 0.4%
BLK7INV24 | 267 | 0.4%
BLK7INV25 | 300.375 | 0.45%
BLK7INV26 | 300.375 | 0.45%
BLK7INV27 | 267 | 0.4%
BLK7INV28 | 267 | 0.4%
BLK7INV29 | 267 | 0.4%
BLK7INV30 | 267 | 0.4%
BLK7INV31 | 267 | 0.4%
BLK7INV32 | 159.5 | 0.239%
BLK8INV1 | 267 | 0.4%
BLK8INV2 | 198 | 0.2966%
BLK8INV3 | 188.1 | 0.2818%
BLK8INV4 | 278.125 | 0.4167%
BLK8INV5 | 300.375 | 0.45%
BLK8INV6 | 289.25 | 0.4333%
BLK8INV7 | 289.25 | 0.4333%
BLK8INV8 | 267 | 0.4%
BLK8INV9 | 289.25 | 0.4333%
BLK8INV10 | 300.375 | 0.45%
BLK8INV11 | 300.375 | 0.45%
BLK8INV12 | 257.4 | 0.3856%
BLK8INV13 | 277.2 | 0.4153%
BLK8INV14 | 257.4 | 0.3856%
BLK8INV15 | 267.3 | 0.4004%
BLK8INV16 | 188.1 | 0.2818%
BLK8INV17 | 178 | 0.2667%
BLK8INV18 | 222.5 | 0.3333%
BLK8INV19 | 287.1 | 0.4301%
BLK8INV20 | 257.4 | 0.3856%
BLK8INV21 | 267.3 | 0.4004%
BLK8INV22 | 257.4 | 0.3856%
BLK8INV23 | 271.35 | 0.4065%
BLK8INV24 | 271.35 | 0.4065%
BLK8INV25 | 261.3 | 0.3915%
BLK8INV26 | 271.35 | 0.4065%
BLK8INV27 | 291.45 | 0.4366%
BLK8INV28 | 257.4 | 0.3856%
BLK1LT1 | 4338.75 | 6.5%
BLK1LT2 | 4605.75 | 6.9%
BLK2LT1 | 4094 | 6.133%
BLK2LT2 | 4249.75 | 6.367%
BLK3LT1 | 4483.375 | 6.717%
BLK3LT2 | 4071.75 | 6.1%
BLK4LT1 | 4394.375 | 6.583%
BLK4LT2 | 4260.875 | 6.383%
BLK5LT1 | 4514.875 | 6.764%
BLK5LT2 | 4349.875 | 6.517%
BLK6LT1 | 4477 | 6.707%
BLK6LT2 | 4499 | 6.74%
BLK7LT1 | 3298.1 | 4.941%
BLK7LT2 | 4071.75 | 6.1%
BLK8LT1 | 3947.5 | 5.914%
BLK8LT2 | 3093.9 | 4.635%
BLK1LT1ACCB1 | 578.5 | 0.8667%
BLK1LT1ACCB2 | 534 | 0.8%
BLK1LT1ACCB3 | 556.25 | 0.8333%
BLK1LT1ACCB4 | 534 | 0.8%
BLK1LT1ACCB5 | 556.25 | 0.8333%
BLK1LT1ACCB6 | 534 | 0.8%
BLK1LT1ACCB7 | 511.75 | 0.7667%
BLK1LT1ACCB8 | 534 | 0.8%
BLK1LT2ACCB1 | 534 | 0.8%
BLK1LT2ACCB2 | 578.5 | 0.8667%
BLK1LT2ACCB3 | 534 | 0.8%
BLK1LT2ACCB4 | 589.625 | 0.8833%
BLK1LT2ACCB5 | 578.5 | 0.8667%
BLK1LT2ACCB6 | 589.625 | 0.8833%
BLK1LT2ACCB7 | 600.75 | 0.9%
BLK1LT2ACCB8 | 600.75 | 0.9%
BLK2LT1ACCB1 | 333.75 | 0.5%
BLK2LT1ACCB2 | 534 | 0.8%
BLK2LT1ACCB3 | 534 | 0.8%
BLK2LT1ACCB4 | 534 | 0.8%
BLK2LT1ACCB5 | 534 | 0.8%
BLK2LT1ACCB6 | 534 | 0.8%
BLK2LT1ACCB7 | 534 | 0.8%
BLK2LT1ACCB8 | 556.25 | 0.8333%
BLK2LT2ACCB1 | 556.25 | 0.8333%
BLK2LT2ACCB2 | 534 | 0.8%
BLK2LT2ACCB3 | 600.75 | 0.9%
BLK2LT2ACCB4 | 589.625 | 0.8833%
BLK2LT2ACCB5 | 567.375 | 0.85%
BLK2LT2ACCB6 | 600.75 | 0.9%
BLK2LT2ACCB7 | 534 | 0.8%
BLK2LT2ACCB8 | 267 | 0.4%
BLK3LT1ACCB1 | 578.5 | 0.8667%
BLK3LT1ACCB2 | 556.25 | 0.8333%
BLK3LT1ACCB3 | 534 | 0.8%
BLK3LT1ACCB4 | 534 | 0.8%
BLK3LT1ACCB5 | 567.375 | 0.85%
BLK3LT1ACCB6 | 600.75 | 0.9%
BLK3LT1ACCB7 | 534 | 0.8%
BLK3LT1ACCB8 | 578.5 | 0.8667%
BLK3LT2ACCB1 | 534 | 0.8%
BLK3LT2ACCB2 | 534 | 0.8%
BLK3LT2ACCB3 | 534 | 0.8%
BLK3LT2ACCB4 | 534 | 0.8%
BLK3LT2ACCB5 | 545.125 | 0.8167%
BLK3LT2ACCB6 | 556.25 | 0.8333%
BLK3LT2ACCB7 | 567.375 | 0.85%
BLK3LT2ACCB8 | 267 | 0.4%
BLK4LT1ACCB1 | 534 | 0.8%
BLK4LT1ACCB2 | 534 | 0.8%
BLK4LT1ACCB3 | 534 | 0.8%
BLK4LT1ACCB4 | 534 | 0.8%
BLK4LT1ACCB5 | 567.375 | 0.85%
BLK4LT1ACCB6 | 567.375 | 0.85%
BLK4LT1ACCB7 | 534 | 0.8%
BLK4LT1ACCB8 | 589.625 | 0.8833%
BLK4LT2ACCB1 | 589.625 | 0.8833%
BLK4LT2ACCB2 | 567.375 | 0.85%
BLK4LT2ACCB3 | 534 | 0.8%
BLK4LT2ACCB4 | 600.75 | 0.9%
BLK4LT2ACCB5 | 534 | 0.8%
BLK4LT2ACCB6 | 600.75 | 0.9%
BLK4LT2ACCB7 | 534 | 0.8%
BLK4LT2ACCB8 | 300.375 | 0.45%
BLK5LT1ACCB1 | 534 | 0.8%
BLK5LT1ACCB2 | 600.75 | 0.9%
BLK5LT1ACCB3 | 578.5 | 0.8667%
BLK5LT1ACCB4 | 534 | 0.8%
BLK5LT1ACCB5 | 572 | 0.8569%
BLK5LT1ACCB6 | 572 | 0.8569%
BLK5LT1ACCB7 | 545.125 | 0.8167%
BLK5LT1ACCB8 | 578.5 | 0.8667%
BLK5LT2ACCB1 | 556.25 | 0.8333%
BLK5LT2ACCB2 | 556.25 | 0.8333%
BLK5LT2ACCB3 | 511.75 | 0.7667%
BLK5LT2ACCB4 | 534 | 0.8%
BLK5LT2ACCB5 | 556.25 | 0.8333%
BLK5LT2ACCB6 | 567.375 | 0.85%
BLK5LT2ACCB7 | 534 | 0.8%
BLK5LT2ACCB8 | 534 | 0.8%
BLK6LT1ACCB1 | 528 | 0.791%
BLK6LT1ACCB2 | 561 | 0.8404%
BLK6LT1ACCB3 | 594 | 0.8899%
BLK6LT1ACCB4 | 572 | 0.8569%
BLK6LT1ACCB5 | 561 | 0.8404%
BLK6LT1ACCB6 | 539 | 0.8075%
BLK6LT1ACCB7 | 550 | 0.824%
BLK6LT1ACCB8 | 572 | 0.8569%
BLK6LT2ACCB1 | 561 | 0.8404%
BLK6LT2ACCB2 | 528 | 0.791%
BLK6LT2ACCB3 | 561 | 0.8404%
BLK6LT2ACCB4 | 583 | 0.8734%
BLK6LT2ACCB5 | 572 | 0.8569%
BLK6LT2ACCB6 | 583 | 0.8734%
BLK6LT2ACCB7 | 550 | 0.824%
BLK6LT2ACCB8 | 561 | 0.8404%
BLK7LT1ACCB1 | 528 | 0.791%
BLK7LT1ACCB2 | 528 | 0.791%
BLK7LT1ACCB3 | 528 | 0.791%
BLK7LT1ACCB4 | 484 | 0.7251%
BLK7LT1ACCB5 |  | 0%
BLK7LT1ACCB6 | 447.75 | 0.6708%
BLK7LT1ACCB7 | 270.5 | 0.4052%
BLK7LT1ACCB8 | 511.75 | 0.7667%
BLK7LT2ACCB1 | 534 | 0.8%
BLK7LT2ACCB2 | 534 | 0.8%
BLK7LT2ACCB3 | 534 | 0.8%
BLK7LT2ACCB4 | 534 | 0.8%
BLK7LT2ACCB5 | 534 | 0.8%
BLK7LT2ACCB6 | 600.75 | 0.9%
BLK7LT2ACCB7 | 534 | 0.8%
BLK7LT2ACCB8 | 267 | 0.4%
BLK8LT1ACCB1 | 386.1 | 0.5784%
BLK8LT1ACCB2 | 578.5 | 0.8667%
BLK8LT1ACCB3 | 578.5 | 0.8667%
BLK8LT1ACCB4 | 556.25 | 0.8333%
BLK8LT1ACCB5 | 600.75 | 0.9%
BLK8LT1ACCB6 | 534.6 | 0.8009%
BLK8LT1ACCB7 | 524.7 | 0.7861%
BLK8LT1ACCB8 | 188.1 | 0.2818%
BLK8LT2ACCB1 | 400.5 | 0.6%
BLK8LT2ACCB2 | 544.5 | 0.8157%
BLK8LT2ACCB3 | 524.7 | 0.7861%
BLK8LT2ACCB4 | 542.7 | 0.813%
BLK8LT2ACCB5 | 532.65 | 0.798%
BLK8LT2ACCB6 | 548.85 | 0.8222%
BLK1TX | 8944.5 | 13.4%
BLK2TX | 8343.75 | 12.5%
BLK3TX | 8555.125 | 12.82%
BLK4TX | 8655.25 | 12.97%
BLK5TX | 8864.75 | 13.28%
BLK6TX | 8976 | 13.45%
BLK7TX | 7369.85 | 11.04%
BLK8TX | 7041.4 | 10.55%
MCR_MVP_IC_1 | 17288.25 | 25.9%
MCR_MVP_IC_2 | 17210.375 | 25.78%
MCR_MVP_IC_3 | 17840.75 | 26.73%
MCR_MVP_IC_4 | 14411.25 | 21.59%
MCR_MVP_OG | 66750.25 | 100%
PWR_TX | 66750.25 | 100%
132KV_OC | 66750.25 | 100%
Line_Bay1 | 66750.25 | 100%
Str_Typ1(445*50) | 22.25 | 0.03333%
Str_Typ2 (330*60) | 19.8 | 0.02966%
Str_Typ3(335*60) | 20.1 | 0.03011%
Str_Typ4(440*60) | 22 | 0.03296%
BLK1MVP | 8944.5 | 13.4%
BLK2MVP | 8343.75 | 12.5%
BLK3MVP | 8555.125 | 12.82%
BLK4MVP | 8655.25 | 12.97%
BLK5MVP | 8864.75 | 13.28%
BLK6MVP | 8976 | 13.45%
BLK7MVP | 7369.85 | 11.04%
BLK8MVP | 7041.4 | 10.55%
BLK1Aux_Tx | 8944.5 | 13.4%
BLK2Aux_Tx | 8343.75 | 12.5%
BLK3Aux_Tx | 8555.125 | 12.82%
BLK4Aux_Tx | 8655.25 | 12.97%
BLK5Aux_Tx | 8864.75 | 13.28%
BLK6Aux_Tx | 8976 | 13.45%
BLK7Aux_Tx | 7369.85 | 11.04%
BLK8Aux_Tx | 7041.4 | 10.55%
All_Inv | 66750.25 | 100%

## GA
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
Sr. No. | Date | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Breakdown Description | Fault Time | Work Completion time on fault | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(kWh/m2) | Approximate Energy Loss (KWh)
1 |  | 1900 | 1900 | Year-2 | Year-2 | 1899-12-31 | 31 | 0:00 | 0:00 | 0 |  | 0 | 0% |  |  |  | 0 |  |  | 0
2 |  | 1900 | 1900 | Year-2 | Year-2 | 1899-12-31 | 31 | 0:00 | 0:00 | 0 |  | 0 | 0% |  |  |  | 0 |  |  | 0
3 |  | 1900 | 1900 | Year-2 | Year-2 | 1899-12-31 | 31 | 0:00 | 0:00 | 0 |  | 0 | 0% |  |  |  | 0 |  |  | 0
4 |  | 1900 | 1900 | Year-2 | Year-2 | 1899-12-31 | 31 | 0:00 | 0:00 | 0 |  | 0 | 0% |  |  |  | 0 |  |  | 0
[6 empty] | 1899-12-31 | [10 empty] | 0 |  |  | 0
[6 empty] | 1899-12-31 | [10 empty] | 0 |  |  | 0
[6 empty] | 1899-12-31 | [10 empty] | 0 |  |  | 0
Formulas:
Month Year = GA[[#This Row],[Date]]-DAY(GA[[#This Row],[Date]])+1
Days = DAY(EOMONTH(GA[[#This Row],[Month Year]],0))

## PA
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  |  | 12 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Sr. No. | Date | Financial Year | Calendar Year | 9 | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Inverter Station Number (if Bd in filed) | LT Number (If breakdwon in Below LT Panel) | ACCB Number (If BD below ACCB) | Inverter number (If Inv or Str BD) | String Type(If String BD, No other filed to be inserted) | Equipment (If any BD above LT panel) | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Fault Category | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgement Time | Work Start time on Fault | Work Completion time on fault | Acknow. time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(kWh/m2) | Approximate Energy Loss (KWh) | PTW No. | Job Card No.
1 | 2025-04-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 4249.75 | 6.367% |  |  | I/C trip in overcurrent | 11:41 | 11:41 | 11:44 | 11:44 | 0 | 0.05 | 0.05 | 0.05 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.0031833 | 0.015 | 48.5103
2 | 2025-04-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 300.375 | 0.45% | Inverter |  | I/C trip in overcurrent | 17:53 | 17:53 | 18:05 | 18:05 | 0 | 0.2 | 0.2 | 0.2 | Inverter trip in ground fault | closed | 0.0009 | 0.01 | 2.2858
3 | 2025-04-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 300.375 | 0.45% | Inverter |  | Ground Fault | 5:51 | 5:51 | 18:04 | 18:04 | 0 | 12.2167 | 12.2167 | 12.2167 | Inverter trip in ground fault | closed | 0.054975 | 3.05 | 697.1766
4 | 2025-04-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 300.375 | 0.45% | Inverter |  | Ground Fault | 5:53 | 5:53 | 10:11 | 12:46 | 0 | 4.3 | 6.8833 | 6.8833 | The inverter tripped due to a ground fault. After performing IR testing, we found a cable fault. Once the cable was repaired, the inverter was successfully charged | closed | 0.030975 | 2.2 | 502.8815
5 | 2025-04-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK5 |  |  | INV2 |  |  | BLK5INV2 | 267 | 0.4% | Inverter |  | Precautionry shutdown | 10:11 | 10:11 | 10:11 | 12:46 | 0 | 0 | 2.5833 | 2.5833 | The inverter tripped due to a ground fault. After performing IR testing, we found a cable fault. Once the cable was repaired, the inverter was successfully charged | closed | 0.010333 | 4.1 | 833.0562
6 | 2025-04-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 267 | 6.367% | LT Panel |  | ACB Triped in overcurrent | 11:27 | 11:27 | 11:35 | 11:50 | 0 | 0.13333 | 0.38333 | 0.38333 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.024406 | 0.328 | 66.6445
7 | 2025-04-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 240 | 6.367% | LT Panel |  | ACB Triped in overcurrent | 11:50 | 11:50 | 11:55 | 12:20 | 0 | 0.083333 | 0.5 | 0.5 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.031833 | 0.348 | 63.5579
8 | 2025-04-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV23 |  |  | BLK2INV23 | 300.375 | 0.45% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:55 | 11:50 | 14:00 | 14:00 | -0.083333 | 2.0833 | 2.0833 | 2.0833 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0.009375 | 1.8 | 411.4485
9 | 2025-04-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV12 |  |  | BLK2INV12 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:55 | 11:50 | 14:00 | 14:00 | -0.083333 | 2.0833 | 2.0833 | 2.0833 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0.0083333 | 1.8 | 365.732
10 | 2025-04-10 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 267 | 6.367% |  |  |  | 11:40 | 11:40 | 11:45 | 12:00 | 0 | 0.083333 | 0.33333 | 0.33333 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.021222 | 0.23 | 46.7324
11 | 2025-04-10 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK8 | LT2 |  |  |  |  | BLK8LT2 | 240 | 4.635% | LT Panel |  |  | 12:05 | 12:05 | 12:10 | 12:30 | 0 | 0.083333 | 0.41667 | 0.41667 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.019313 | 0.24 | 43.833
12 | 2025-04-12 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 267 | 6.367% | LT Panel |  | I/C trip in overcurrent | 12:45 | 12:45 | 12:50 | 13:20 | 0 | 0.083333 | 0.58333 | 0.58333 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.037139 | 2.13 | 432.7829
13 | 2025-04-12 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 240 | 6.367% | LT Panel |  | I/C trip in overcurrent | 11:44 | 11:44 | 11:49 | 12:20 | 0 | 0.083333 | 0.6 | 0.6 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.0382 | 2.11 | 385.3656
14 | 2025-04-13 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 507 | 6.367% | LT Panel |  | I/C trip in overcurrent | 10:58 | 10:58 | 11:10 | 11:20 | 0 | 0.2 | 0.36667 | 0.36667 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.023344 | 1.32 | 509.2852
15 | 2025-04-14 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 507 | 6.367% | LT Panel |  | I/C trip in overcurrent | 11:30 | 11:30 | 11:30 | 14:00 | 0 | 0 | 2.5 | 2.5 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0 | 2.3 | 887.3909
16 | 2025-04-15 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 507 | 6.367% | LT Panel |  | I/C trip in overcurrent | 10:49 | 10:49 | 10:59 | 11:00 | 5 | 0.16667 | 0.18333 | 0.18333 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0 | 0.1 | 38.5822
17 | 2025-04-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:10 | 11:05 | 14:00 | 14:00 | -0.083333 | 2.8333 | 2.8333 | 2.8333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.83 | 575.012
18 | 2025-04-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:10 | 11:05 | 14:00 | 14:00 | -0.083333 | 2.8333 | 2.8333 | 2.8333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.83 | 516.8647
19 | 2025-04-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:10 | 11:05 | 14:00 | 14:00 | -0.083333 | 2.8333 | 2.8333 | 2.8333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.95 | 599.3941
20 | 2025-04-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:10 | 11:05 | 14:00 | 14:00 | -0.083333 | 2.8333 | 2.8333 | 2.8333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.95 | 538.7812
[18 empty] | #N/A | [8 empty] | 0 | 0 | 0 | 0 |  | closed |  |  | 0
1724 | 2025-04-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 10:55 | 10:50 | 13:55 | 13:55 | -0.083333 | 3 | 3 | 3 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.82 | 572.9801
1725 | 2025-04-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 10:55 | 10:50 | 13:55 | 13:55 | -0.083333 | 3 | 3 | 3 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.82 | 515.0383
1726 | 2025-04-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 10:43 | 10:43 | 14:00 | 14:00 | 0 | 3.2833 | 3.2833 | 3.2833 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.89 | 587.203
1727 | 2025-04-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 10:43 | 10:43 | 14:00 | 14:00 | 0 | 3.2833 | 3.2833 | 3.2833 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.89 | 527.823
1728 | 2025-04-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:10 | 11:10 | 14:10 | 14:10 | 0 | 3 | 3 | 3 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted…..12 Times LT2 Trip Some ratio changes on Breaker | closed | 0 | 2.83 | 575.012
1729 | 2025-04-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:10 | 11:10 | 14:10 | 14:10 | 0 | 3 | 3 | 3 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted…..12 Times LT2 Trip Some ratio changes on Breaker | closed | 0 | 2.83 | 516.8647
1730 | 2025-04-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV30 |  |  | BLK2INV30 | 240 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:20 | 11:20 | 14:10 | 14:10 | 0 | 2.8333 | 2.8333 | 2.8333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted…..12 Times LT2 Trip Some ratio changes on Breaker | closed | 0 | 2.72 | 496.7746
1731 | 2025-04-25 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:00 | 11:00 | 13:20 | 13:20 | 0 | 2.3333 | 2.3333 | 2.3333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted….. | closed | 0 | 2.31 | 421.8931
1732 | 2025-04-25 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:00 | 11:00 | 13:20 | 13:20 | 0 | 2.3333 | 2.3333 | 2.3333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted….. | closed | 0 | 2.31 | 469.3561
1733 | 2025-04-25 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | All_Inv |  |  | BLK2All_Inv | 4605 |  | Inverter |  | All inverter Tripped LT2 | 12:18 | 12:18 | 12:32 | 12:32 | 0 | 0.23333 | 0.23333 | 0.23333 | All inverter Tripped LT2 | closed | 0 | 0.25 | 876.0902
1734 | 2025-04-27 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK1 |  |  | All_Inv |  |  | BLK1All_Inv | 4381 |  | IDT |  | IDT tripped due to overcurrent | 11:30 | 11:30 | 11:42 | 11:42 | 0 | 0.2 | 0.2 | 0.2 | IDT tripped due to overcurrent | closed | 0 | 2.12 | 7067.866
1735 | 2025-04-27 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | All_Inv |  |  | BLK2All_Inv | 4520 |  | IDT |  | IDT tripped due to overcurrent | 11:30 | 11:30 | 11:42 | 11:42 | 0 | 0.2 | 0.2 | 0.2 | IDT tripped due to overcurrent | closed | 0 | 2.12 | 7292.1147
1735 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV5 |  |  | BLK8INV5 | 22.25 | 0.45% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 9:00 | 9:30 | 0 | 0 | 0.5 | 0.5 | Found inv string open, connected & rectified | closed | 0 | 0.555 | 9.3973
1736 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV10 |  |  | BLK8INV10 | 9.9 | 0.45% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 9:35 | 9:55 | 0 | 0.58333 | 0.91667 | 0.91667 | Found inv string open, connected & rectified | closed | 0 | 0.64 | 4.8216
1738 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV11 |  |  | BLK8INV11 | 9.9 | 0.45% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 10:10 | 10:25 | 0 | 1.1667 | 1.4167 | 1.4167 | Found inv string open, connected & rectified | closed | 0 | 0.724 | 5.4545
1739 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV12 |  |  | BLK8INV12 | 9.9 | 0.3856% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 10:30 | 10:40 | 0 | 1.5 | 1.6667 | 1.6667 | Found inv string open, connected & rectified | closed | 0 | 0.752 | 5.6654
1740 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV13 |  |  | BLK8INV13 | 9.9 | 0.4153% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 10:45 | 11:00 | 0 | 1.75 | 2 | 2 | Found inv string open, connected & rectified | closed | 0 | 0.776 | 5.8462
1741 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK3 |  |  | INV6 |  |  | BLK3INV6 | 11.13 | 0.4% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 11:10 | 11:20 | 0 | 2.1667 | 2.3333 | 2.3333 | Found inv string open, connected & rectified | closed | 0 | 0.798 | 6.7589
1742 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK3 |  |  | INV20 |  |  | BLK3INV20 | 11.13 | 0.4% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 11:25 | 11:35 | 0 | 2.4167 | 2.5833 | 2.5833 | Found inv string open, connected & rectified | closed | 0 | 0.814 | 6.8944
1743 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK1 |  |  | INV17 |  |  | BLK1INV17 | 11.13 | 0.4% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 11:50 | 12:00 | 0 | 2.8333 | 3 | 3 | Found inv string open, connected & rectified | closed | 0 | 0.839 | 7.1062
1744 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK1 |  |  | INV18 |  |  | BLK1INV18 | 11.13 | 0.4% | String Fuses |  | Replaced the fuse and rectified | 9:00 | 9:00 | 12:05 | 12:15 | 0 | 3.0833 | 3.25 | 3.25 | Replaced the fuse and rectified | closed | 0 | 6.3 | 53.3599
1745 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK3 |  |  | INV32 |  |  | BLK3INV32 | 31.9 |  | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 12:05 | 12:00 | 0 | 3.0833 | 3 | 3 | Replaced the fuse and rectified | closed | 0 | 6.3 | 152.9362
1746 | 2025-04-29 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 66.75 | 0.3955% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 10:30 | 10:30 | 0 | 1.5 | 1.5 | 1.5 | DC cable damage caused by tractor movement. The cable was replaced with a new one | closed | 0 | 0.7 | 35.5573
1747 | 2025-04-29 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 22.25 | 0.3955% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 11:30 | 11:30 | 0 | 2.5 | 2.5 | 2.5 | DC cable damage caused by tractor movement. The cables were replaced with new ones. | closed | 0 | 2.1 | 35.5573
1748 | 2025-04-29 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK1 |  |  | INV24 |  |  | BLK1INV24 | 22.25 | 0.45% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 17:30 | 17:30 | 0 | 8.5 | 8.5 | 8.5 | Cable Damged due to tractor movement | closed | 0 | 6.7 | 113.4446
1749 | 2025-04-29 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV28 |  |  | BLK2INV28 | 22.5 | 0.45% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 12:30 | 12:30 | 0 | 3.5 | 3.5 | 3.5 | Due to a short circuit caused by tractor movement. The cable was replaced with a new one. | closed | 0 | 3.1 | 53.0791
1750 | 2025-04-29 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV3 |  |  | BLK2INV3 | 22.5 | 0.1667% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 13:30 | 13:30 | 0 | 4.5 | 4.5 | 4.5 | Cable Damge due to grass cutting activitysame replaced | closed | 0 | 4.1 | 70.2014
1751 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK6 |  |  | INV7 |  |  | BLK6INV7 | 88 | 0.4449% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 10:00 | 11:00 | 0 | 1 | 2 | 2 | Cable Damge due to grass cutting activitysame replaced | closed | 0 | 0.8 | 53.5737
1752 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 22 | 0.4449% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 11:15 | 11:30 | 0 | 2.25 | 2.5 | 2.5 | Cable Damge due to grass cutting activitysame replaced | closed | 0 | 1 | 16.7418
1753 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 22.25 | 0.45% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 11:35 | 11:50 | 0 | 2.5833 | 2.8333 | 2.8333 | Cable Damge due to grass cutting activitysame replaced | closed | 0 | 1.5 | 25.3981
1754 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK6 |  |  | INV8 |  |  | BLK6INV8 | 22 | 0.4449% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 11:55 | 12:10 | 0 | 2.9167 | 3.1667 | 3.1667 | Cable Damge due to grass cutting activitysame replaced | closed | 0 | 1.7 | 28.461
1755 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK6 |  |  | INV15 |  |  | BLK6INV15 | 22 | 0.412% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 12:15 | 12:30 | 0 | 3.25 | 3.5 | 3.5 | Cable Damge due to grass cutting activitysame replaced | closed | 0 | 2 | 33.4836
1756 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV24 |  |  | BLK2INV24 | 44.5 | 0.4333% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 16:05 | 16:25 | 0 | 7.0833 | 7.4167 | 7.4167 | Cable Damge due to grass cutting activitysame replaced | closed | 0 | 4.6 | 155.7747
1757 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK3 |  |  | INV12 |  |  | BLK3INV12 | 300.38 | 0.45% | Inverter |  | inv tripped on system fault | 7:14 | 7:18 | 11:00 | 12:45 | 0.066667 | 3.7667 | 5.5167 | 5.5167 | Inv Fault System Shudown | closed | 0 | 0.3 | 68.5759
1758 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.2 | 0.45% | Cables |  | cable short | 7:18 | 9:00 | 12:00 | 12:15 | 1.7 | 4.7 | 4.95 | 4.95 | Cable Damge due to grass cutting activity same replaced | closed | 0 | 0.293 | 4.9499
1759 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV7 |  |  | BLK8INV7 | 22.2 | 0.4333% | Cables |  | cable short | 7:18 | 9:00 | 12:18 | 12:28 | 1.7 | 5 | 5.1667 | 5.1667 | Cable Damge due to grass cutting activity same replaced | closed | 0 | 0.317 | 5.3554
1760 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV8 |  |  | BLK8INV8 | 22.2 | 0.4% | Cables |  | mc4 open | 7:18 | 9:00 | 12:35 | 12:50 | 1.7 | 5.2833 | 5.5333 | 5.5333 | MC4 Open FOUND rectified | closed | 0 | 0.326 | 5.5074
1761 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV10 |  |  | BLK8INV10 | 22.2 | 0.45% | Cables |  | cable short | 7:18 | 9:00 | 13:00 | 13:10 | 1.7 | 5.7 | 5.8667 | 5.8667 | Cable Damge due to grass cutting activity same replaced | closed | 0 | 0.326 | 5.5074
1762 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV11 |  |  | BLK8INV11 | 22.2 | 0.45% | Cables |  | cable cut | 7:18 | 9:00 | 13:15 | 13:25 | 1.7 | 5.95 | 6.1167 | 6.1167 | Cable Damge due to grass cutting activity same replaced | closed | 0 | 0.325 | 5.4905
1763 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV21 |  |  | BLK2INV21 | 22.2 | 0.4% | Connectors |  | Open Found and rectified | 7:20 | 9:00 | 11:15 | 11:15 | 1.6667 | 3.9167 | 3.9167 | 3.9167 | MC4 Found open condition | closed | 0 | 2.3 | 38.8562
1764 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK1 |  |  | INV15 |  |  | BLK1INV15 | 22.2 | 0.4% | Connectors |  | Open Found and rectified | 7:20 | 9:00 | 11:45 | 11:45 | 1.6667 | 4.4167 | 4.4167 | 4.4167 | MC4 Found open condition | closed | 0 | 3.5 | 59.129
1765 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV17 |  |  | BLK2INV17 | 22.2 | 0.4% | Connectors |  | Opend Found MC4 Rectified | 7:20 | 9:00 | 13:10 | 13:10 | 1.6667 | 5.8333 | 5.8333 | 5.8333 | MC4 Found opend condition | closed | 0 | 3.1 | 52.3714
1766 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV18 |  |  | BLK2INV18 | 44.5 | 0.4167% | Connectors |  | two string found Opend Found MC4 Rectified | 7:20 | 9:00 | 15:30 | 15:30 | 1.6667 | 8.1667 | 8.1667 | 8.1667 | 2 MC4 Found OPEN Condition | closed | 0 | 4.1 | 138.8427
1767 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 22.2 | 0.4167% | Connectors |  | Opend Found MC4 Rectified | 7:20 | 9:00 | 16:25 | 16:25 | 1.6667 | 9.0833 | 9.0833 | 9.0833 | MC4 Found opend condition | closed | 0 | 4.9 | 82.7805
1768 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV6 |  |  | BLK8INV6 | 22.2 | 0.4333% | Connectors |  | Opend Found MC4 Rectified | 7:20 | 9:00 | 17:46 | 17:46 | 1.6667 | 10.4333 | 10.4333 | 10.4333 | MC4 Found opend condition | closed | 0 | 5.3 | 89.5381
1769 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 4008 | 5.914% | LT Panel |  | Tripped due to overcurrent fault | 12:50 | 12:52 | 13:00 | 13:00 | 0.033333 | 0.16667 | 0.16667 | 0.16667 | Reset & Started | closed | 0 | 0.122 | 370.2136
1770 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV27 |  |  | BLK8INV27 | 22.2 | 0.4366% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 9:30 | 9:40 | 3.7333 | 4.2333 | 4.4 | 4.4 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.9 | 15.1273
1771 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.2 | 0.3856% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 9:50 | 10:00 | 3.7333 | 4.5667 | 4.7333 | 4.7333 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.08 | 1.3446
1772 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.2 | 0.3856% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 10:10 | 10:15 | 3.7333 | 4.9 | 4.9833 | 4.9833 | MC4 tightned | closed | 0 | 0.107 | 1.7985
1773 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.2 | 0.3856% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 10:20 | 10:25 | 3.7333 | 5.0667 | 5.15 | 5.15 | MC4 tightned | closed | 0 | 0.12 | 2.017
1774 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.2 | 0.3856% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 10:30 | 10:40 | 3.7333 | 5.2333 | 5.4 | 5.4 | MC4 tightned | closed | 0 | 0.11 | 1.8489
1775 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.2 | 0.3856% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 10:50 | 11:00 | 3.7333 | 5.5667 | 5.7333 | 5.7333 | MC4 tightned | closed | 0 | 0.12 | 2.017
1776 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV17 |  |  | BLK8INV17 | 22.2 | 0.2667% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 11:10 | 11:20 | 3.7333 | 5.9 | 6.0667 | 6.0667 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.11 | 1.8489
1777 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV3 |  |  | BLK8INV3 | 22.2 | 0.2818% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 11:40 | 11:50 | 3.7333 | 6.4 | 6.5667 | 6.5667 | MC4 tightned | closed | 0 | 0.9 | 15.1273
1778 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 22.2 | 0.4301% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 12:00 | 12:10 | 3.7333 | 6.7333 | 6.9 | 6.9 | 3 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.14 | 2.3531
1779 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 22.2 | 0.4301% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 12:20 | 12:30 | 3.7333 | 7.0667 | 7.2333 | 7.2333 | 2 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.13 | 2.185
1780 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV4 |  |  | BLK8INV4 | 22.2 | 0.4167% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 12:35 | 12:40 | 3.7333 | 7.3167 | 7.4 | 7.4 | MC4 tightned | closed | 0 | 0.13 | 2.185
1781 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK3 |  |  | INV6 |  |  | BLK3INV6 | 267 | 0.4% | Inverter |  | inv tripped on system fault | 14:20 | 14:20 | 16:00 | 16:30 | 0 | 1.6667 | 2.1667 | 2.1667 | Inv Fault System Shudown | closed | 0 | 0.131 | 26.4818
1782 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK4 |  |  | INV17 |  |  | BLK4INV17 | 289.25 | 0.4333% | Inverter |  | inv tripped on system fault | 14:20 | 14:20 | 15:40 | 16:10 | 0 | 1.3333 | 1.8333 | 1.8333 | Inv Fault System Shudown | closed | 0 | 0.8228 | 180.1907
1783 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK7 |  |  | INV12 |  |  | BLK7INV12 | 190.35 | 0.4054% | Inverter |  | inv tripped on system fault | 14:20 | 14:20 | 15:50 | 16:20 | 0 | 1.5 | 2 | 2 | One nos of MC4 connector replaced with new one | closed | 0 | 0.11194 | 16.1325
1784 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK6 |  |  | INV20 |  |  | BLK6INV20 | 264 | 0.3955% | Inverter |  | inv tripped on system fault | 14:20 | 14:20 | 15:30 | 16:10 | 0 | 1.1667 | 1.8333 | 1.8333 | One nos of MC4 connector replaced with new one | closed | 0 | 0.8227 | 164.4411
1785 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK5 |  |  | INV27 |  |  | BLK5INV27 | 300.38 | 0.4% | Inverter |  | inv tripped on system fault | 14:20 | 14:20 | 15:25 | 16:08 | 0 | 1.0833 | 1.8 | 1.8 | Inv Fault System Shudown | closed | 0 | 0.7578 | 172.3417
1786 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK5 |  |  | INV13 |  |  | BLK5INV13 | 22.25 | 0.4285% | Connectors |  | Found MC4 connector faulty condition | 9:00 | 9:00 | 9:30 | 9:40 | 0 | 0.5 | 0.66667 | 0.66667 | MC4 tightned | closed | 0 | 0.623 | 10.495
1787 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK5 |  |  | INV17 |  |  | BLK5INV17 | 22.25 | 0.4333% | Connectors |  | Found MC4 connector faulty condition | 9:00 | 9:00 | 9:50 | 10:00 | 0 | 0.83333 | 1 | 1 | MC4 tightned | closed | 0 | 0.651 | 10.9667
1788 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK5 |  |  | INV12 |  |  | BLK5INV12 | 22.25 | 0.4285% | Connectors |  | Found MC4 connector faulty condition | 9:00 | 9:00 | 10:10 | 10:20 | 0 | 1.1667 | 1.3333 | 1.3333 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.666 | 11.2194
1789 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK3 |  |  | INV6 |  |  | BLK3INV6 | 22.25 | 0.4% | Connectors |  | Found MC4 connector faulty condition | 9:00 | 9:00 | 10:30 | 10:40 | 0 | 1.5 | 1.6667 | 1.6667 | MC4 tightned | closed | 0 | 0.663 | 11.1688
1790 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK7 |  |  | INV28 |  |  | BLK7INV28 | 22.25 | 0.4% | Connectors |  | Found MC4 connector faulty condition | 9:00 | 9:00 | 10:50 | 11:00 | 0 | 1.8333 | 2 | 2 | 2 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.695 | 11.7079
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK2 |  |  | MVP |  |  | BLK2MVP | 4349.2 | 12.5% | IDT |  | IDT tripped on over current fault | 10:44 | 10:44 | 10:54 | 10:54 | 0 | 0.16667 | 0.16667 | 0.16667 | Normally check the all parameters & charge the idt | closed | 0 | 0.146 | 480.7586
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK2 |  |  | MVP |  |  | BLK2MVP | 4489 | 12.5% | IDT |  | IDT tripped on over current fault | 10:44 | 10:44 | 10:54 | 10:54 | 0 | 0.16667 | 0.16667 | 0.16667 | Normally check the all parameters & charge the idt | closed | 0 | 0.146 | 496.212
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV4 |  |  | BLK6INV4 | 22 | 0.4449% | Connectors |  | Found MC4 connector faulty condition | 9:00 | 9:00 | 9:45 | 9:55 | 0 | 0.75 | 0.91667 | 0.91667 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.0512 | 0.85282
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV14 |  |  | BLK6INV14 | 22 | 0.412% | Connectors |  | Found MC4 connectors open condition | 9:00 | 9:00 | 10:00 | 10:10 | 0 | 1 | 1.1667 | 1.1667 | MC4 tightned | closed | 0 | 0.69 | 11.4931
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV18 |  |  | BLK6INV18 | 22 | 0.4449% | Connectors |  | Found MC4 connector faulty condition | 9:00 | 9:00 | 10:15 | 10:25 | 0 | 1.25 | 1.4167 | 1.4167 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.82 | 13.6584
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV20 |  |  | BLK6INV20 | 22 | 0.3955% | Connectors |  | Found Y connector shorted | 9:00 | 9:00 | 10:35 | 10:45 | 0 | 1.5833 | 1.75 | 1.75 | 1Nos y connector used | closed | 0 | 0.1 | 1.6657
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV23 |  |  | BLK6INV23 | 22 | 0.3955% | Connectors |  | Found Y connector shorted & MC4 1Pair | 9:00 | 9:00 | 10:50 | 11:00 | 0 | 1.8333 | 2 | 2 | 1 pair of mc4 connectors & 1NOs of Y connector | closed | 0 | 1.22 | 20.3211
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV26 |  |  | BLK6INV26 | 22 | 0.4449% | Connectors |  | Found MC4 connectors open condition | 9:00 | 9:00 | 11:10 | 11:20 | 0 | 2.1667 | 2.3333 | 2.3333 | mc4 tightned | closed | 0 | 1.43 | 23.819
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV27 |  |  | BLK6INV27 | 22 | 0.412% | Connectors |  | Found Y connector shorted | 9:00 | 9:00 | 11:25 | 11:35 | 0 | 2.4167 | 2.5833 | 2.5833 | 1Nos y connector used | closed | 0 | 1.65 | 27.4835
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK7 |  |  | INV4 |  |  | BLK7INV4 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 9:00 | 9:00 | 11:50 | 12:00 | 0 | 2.8333 | 3 | 3 | mc4 tightned | closed | 0 | 2.069 | 34.4626
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 257.4 | 0.2852% | Inverter |  | Inv tripped on excessive leakage current fault | 14:30 | 14:30 | 14:40 | 15:26 | 0 | 0.16667 | 0.93333 | 0.93333 | 1Nos of y connector used & reset the fault after got the password | closed | 0 | 0.571 | 111.278
1791 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 22.25 | 0.4% | Connectors |  | MC4 found open condition | 9:00 | 9:00 | 12:10 | 12:20 | 0 | 3.1667 | 3.3333 | 3.3333 | mc4 tightned | closed | 0 | 2.388 | 40.2281
1792 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK7 |  |  | INV15 |  |  | BLK7INV15 | 247.5 | 0.4% | Inverter |  | Inverter tripped due to ground fault | 9:00 | 9:00 | 9:30 | 9:42 | 0 | 0.5 | 0.7 | 0.7 | Checked all string one by one and found one string was grounded and after rectified the same charge the Inverter | closed | 0 | 0.622 | 116.5549
1793 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV10 |  |  | BLK7INV10 | 22 | 0.3856% | Connectors |  | MC4 found open condition | 0.375 | 9:00 | 9:30 | 9:44 | 0 | 0.5 | 0.73333 | 0.73333 | mc4 tightned | closed | 0 | 0.1688 | 2.8116
1794 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV25 |  |  | BLK7INV25 | 22 | 0.45% | Connectors |  | Found MC4 connector faulty condition | 0.375 | 9:00 | 9:30 | 10:01 | 0 | 0.5 | 1.0167 | 1.0167 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.2 | 3.3313
1795 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV17 |  |  | BLK7INV17 | 22 | 0.4% | Connectors |  | Found Y connector shorted |  |  |  | 10:18 | 0 | 0 | 10.3 | 10.3 | 1Nos y connector used and 1 nos of 15A fuse replaced with new one | closed | 0 | 0.1987 | 3.3097
1796 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 22 | 0.3955% | Connectors |  | MC4 found open condition |  |  |  | 10:33 | 0 | 0 | 10.55 | 10.55 | mc4 tightned | closed | 0 | 0.21 | 3.4979
1797 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV5 |  |  | BLK7INV5 | 22 | 0.3955% | Connectors |  | MC4 found open condition |  |  |  | 11:10 | 0 | 0 | 11.1667 | 11.1667 | mc4 tightned | closed | 0 | 0.191 | 3.1814
1798 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV16 |  |  | BLK7INV16 | 22 | 0.4% | Connectors |  | MC4 found open condition |  |  |  | 11:22 | 0 | 0 | 11.3667 | 11.3667 | mc4 tightned | closed | 0 | 0.214 | 3.5645
1799 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK3 |  |  | INV6 |  |  | BLK3INV6 | 22 | 0.4% | Connectors |  | Found Y connector shorted |  |  |  | 11:38 | 0 | 0 | 11.6333 | 11.6333 | 1Nos y connector used and 1 nos of 15A fuse replaced with new one | closed | 0 | 0.22 | 3.6645
1800 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22 | 0.45% | Connectors |  | Found Y connector shorted |  |  |  | 12:14 | 0 | 0 | 12.2333 | 12.2333 | 1Nos y connector used and 1 nos of 15A fuse replaced with new one | closed | 0 | 0.218 | 3.6311
1801 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | POWER TRAFO |  |  | 132KV_OC |  |  | POWER TRAFO132KV_OC | 67300 |  | Power Trafo |  | Tripped on REF HV Earth Fault | 13:13 | 13:13 | 13:30 | 18:30 | 0 | 0.28333 | 5.2833 | 5.2833 | Checked all Parameter & Testing than charged the Power trafo | closed | 0 | 1.46 | 74393.1161
1802 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:40 | 12.45 | BLK2 |  |  | MVP |  |  | BLK2MVP | 7500 | 12.5% | IDT |  | Tripped on Over current | 11:10 | 11:10 | 11:15 | 11:20 | 0 | 0.083333 | 0.16667 | 0.16667 | Checked all parameter & charged the IDT | closed | 0 | 0.193 | 1095.9315
1803 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:40 | 12.45 | BLK1 |  |  | MVP |  |  | BLK1MVP | 7500 | 13.4% | IDT |  | Tripped on Over current | 11:22 | 11:22 | 11:30 | 11:34 | 0 | 0.13333 | 0.2 | 0.2 | Checked all parameter & charged the IDT | closed | 0 | 0.182 | 1033.4691
1804 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:40 | 12.45 |  |  |  | MVP |  |  | MVP | 7500 |  | IDT |  | Tripped on Over current | 11:22 | 11:22 | 11:25 | 11:40 | 0 | 0.05 | 0.3 | 0.3 | Checked all parameter & charged the IDT | closed | 0 | 0.17 | 965.3282
1805 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:40 | 12.45 |  |  |  | MVP |  |  | MVP | 7500 |  | IDT |  | Tripped on Over current | 11:22 | 11:22 | 11:28 | 11:46 | 0 | 0.1 | 0.4 | 0.4 | Checked all parameter & charged the IDT | closed | 0 | 0.173 | 982.3635
1806 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:40 | 12.45 |  |  |  | MVP |  |  | MVP | 7500 |  | IDT |  | Tripped on Over current | 12:45 | 12:45 | 12:51 | 12:55 | 0 | 0.1 | 0.16667 | 0.16667 | Checked all parameter & charged the IDT | closed | 0 | 0.16 | 908.5442
1807 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:40 | 12.45 |  |  |  | MVP |  |  | MVP | 7500 |  | IDT |  | Tripped on Over current | 12:53 | 12:55 | 13:05 | 13:08 | 0.033333 | 0.2 | 0.25 | 0.25 | Checked all parameter & charged the IDT | closed | 0 | 0.153 | 868.7954
1808 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:40 | 12.45 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 247.5 | 0.3333% | Inverter |  | Manually shutdown | 12:45 | 12:45 | 13:45 | 14:00 | 0 | 1 | 1.25 | 1.25 | Manually tripped | closed | 0.0041667 | 1.1 | 206.126
1809 | 2025-05-09 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:15 | 18:24 | 12.15 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 22 | 0.4167% | Connectors |  | MC4 found open condition | 6:15 | 12:00 | 12:02 | 12:09 | 5.75 | 5.7833 | 5.9 | 5.9 | mc4 tightned | closed | 0.024583 | 3.33 | 55.4666
1810 | 2025-05-09 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:15 | 18:24 | 12.15 | BLK1 |  |  | INV13 |  |  | BLK1INV13 | 22 | 0.4% | Connectors |  | Found MC4 connector faulty condition | 6:15 | 12:00 | 12:14 | 12:18 | 5.75 | 5.9833 | 6.05 | 6.05 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0.0242 | 3.36 | 55.9663
1811 | 2025-05-09 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:15 | 18:24 | 12.15 | BLK3 |  |  | INV10 |  |  | BLK3INV10 | 12 | 0.4% | Connectors |  | MC4 found open condition | 6:15 | 12:10 | 12:30 | 12:36 | 5.9167 | 6.25 | 6.35 | 6.35 | mc4 tightned | closed | 0.0254 | 3.4 | 30.8905
1812 | 2025-05-09 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:15 | 18:24 | 12.15 | BLK1 | LT2 |  |  |  |  | BLK1LT2 | 4605.75 | 6.9% | LT Panel |  | Tripped on Over current | 11:07 | 11:07 | 11:14 | 11:18 | 0 | 0.11667 | 0.18333 | 0.18333 | Checked all parameter & charged the breaker | closed | 0.01265 | 0.18 | 627.6791
1813 | 2025-05-09 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:15 | 18:24 | 12.15 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 4008.13 | 5.914% | LT Panel |  | Tripped on Over current | 11:31 | 11:31 | 11:38 | 11:42 | 0 | 0.11667 | 0.18333 | 0.18333 | Checked all parameter & charged the breaker | closed | 0.010842 | 0.196 | 594.7887
1814 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 4008.13 | 5.914% | LT Panel |  | Tripped on Over current | 12:17 | 12:17 | 12:22 | 12:25 | 0 | 0.083333 | 0.13333 | 0.13333 | Checked all parameter & charged the breaker | closed | 0.0078851 | 0.16 | 485.5418
1815 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 6:05 | 6:05 | 15:25 | 15:30 | 0 | 9.3333 | 9.4167 | 9.4167 | 1 nos of +ve & -ve MC4 connector replaced with new one and 60 mtr cable replaced with new one | closed | 0.037243 | 4.17 | 69.4582
1816 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 6:05 | 6:05 | 15:35 | 15:40 | 0 | 9.5 | 9.5833 | 9.5833 | 1 nos of +ve & -ve MC4 connector replaced with new one and 60 mtr cable replaced with new one | closed | 0.037903 | 4.2 | 69.9579
1817 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 6:05 | 6:05 | 15:52 | 15:56 | 0 | 9.7833 | 9.85 | 9.85 | 1 nos of +ve & -ve MC4 connector replaced with new one and 60 mtr cable replaced with new one | closed | 0.038957 | 4.12 | 68.6254
1818 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 6:05 | 6:05 | 16:00 | 16:10 | 0 | 9.9167 | 10.0833 | 10.0833 | 1 nos of +ve & -ve MC4 connector replaced with new one and 60 mtr cable replaced with new one | closed | 0.03988 | 4.66 | 77.62
1819 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK6 |  |  | INV8 |  |  | BLK6INV8 | 22 | 0.4449% | Connectors |  | MC4 found open condition | 6:05 | 6:05 | 16:05 | 16:13 | 0 | 10 | 10.1333 | 10.1333 | 1 nos of +ve & -ve MC4 connector replaced with new one and 60 mtr cable replaced with new one | closed | 0 | 4.73 | 78.7859
1820 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 22 | 0.4301% | Connectors |  | Theft cable | 6:05 | 6:05 | 16:45 | 16:50 | 0 | 10.6667 | 10.75 | 10.75 | 290 meter cable used ,2 pair MC4 connecter ,2 15A fuse replaced with new one | closed | 0.046237 | 4.23 | 70.4576
1821 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 22 | 0.4301% | Connectors |  | Theft cable | 6:05 | 6:05 | 17:00 | 17:20 | 0 | 10.9167 | 11.25 | 11.25 | 276 meter cable used ,2 pair MC4 connecter ,2 15A fuse replaced with new one | closed | 0.048388 | 4.77 | 79.4522
1822 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 22 | 0.4301% | Connectors |  | Theft cable | 6:05 | 6:05 | 17:28 | 17:34 | 0 | 11.3833 | 11.4833 | 11.4833 | 260 meter cable used ,2 pair MC4 connecter ,2 15A fuse replaced with new one | closed | 0.049391 | 4.87 | 81.1179
1823 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK1 |  |  | INV8 |  |  | BLK1INV8 | 22 | 0.4% | Connectors |  | MC4 found open condition | 5:48 | 5:48 | 11:30 | 11:40 | 0 | 5.7 | 5.8667 | 5.8667 | mc4 tightned | closed | 0 | 2.12 | 35.3121
1824 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK2 |  |  | INV15 |  |  | BLK2INV15 | 22 | 0.4% | Connectors |  | MC4 found open condition | 5:48 | 5:48 | 11:31 | 11:50 | 0 | 5.7167 | 6.0333 | 6.0333 | mc4 tightned | closed | 0.024133 | 2.48 | 41.3085
1825 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK2 |  |  | INV28 |  |  | BLK2INV28 | 22 | 0.45% | Connectors |  | MC4 found open condition | 5:48 | 5:48 | 11:40 | 11:55 | 0 | 5.8667 | 6.1167 | 6.1167 | mc4 tightned | closed | 0.027525 | 2.31 | 38.4768
1826 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK7 |  |  | INV4 |  |  | BLK7INV4 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 5:48 | 5:48 | 12:00 | 12:28 | 0 | 6.2 | 6.6667 | 6.6667 | mc4 tightned | closed | 0.026367 | 2.6 | 43.3073
1827 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK7 |  |  | INV26 |  |  | BLK7INV26 | 22 | 0.45% | Connectors |  | MC4 found open condition | 5:48 | 5:48 | 12:10 | 12:40 | 0 | 6.3667 | 6.8667 | 6.8667 | mc4 tightned | closed | 0.0309 | 2.23 | 37.1443
1828 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | Theft cable | 5:48 | 5:48 | 16:05 | 16:20 | 0 | 10.2833 | 10.5333 | 10.5333 | St-13 120 mtr cables, 2 pair of MC4 connecter replaced with new one | closed | 0.04166 | 2.44 | 40.6422
1829 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | Theft cable | 5:48 | 5:48 | 16:05 | 16:20 | 0 | 10.2833 | 10.5333 | 10.5333 | St-14 120 mtr cables, 2 pair of MC4 connecter replaced with new one | closed | 0.04166 | 2.78 | 46.3055
1830 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | Theft cable | 5:48 | 5:48 | 16:05 | 16:20 | 0 | 10.2833 | 10.5333 | 10.5333 | St-15 120 mtr cables, 2 pair of MC4 connecter replaced with new one | closed | 0.04166 | 2.54 | 42.3079
1831 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK7 |  |  | INV32 |  |  | BLK7INV32 | 22 | 0.239% | Connectors |  | I nos of string cable fired by short circuited | 11:02 | 11:02 | 12:45 | 17:20 | 0 | 1.7167 | 6.3 | 6.3 | St-4 ,50 mtr cables, 2 pair of MC4 connecter replaced with new one | closed | 0 | 2.64 | 43.9735
1832 | 2025-05-12 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:32 | 12.3167 | BLK2 |  |  | INV11 |  |  | BLK2INV11 | 22 | 0.4% | Connectors |  | Mc4 connecter found open | 6:13 | 6:13 | 9:00 | 9:31 | 0 | 2.7833 | 3.3 | 3.3 | mc4 tightned | closed | 0.0132 | 0.694 | 11.5597
1833 | 2025-05-12 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:32 | 12.3167 | BLK3 |  |  | INV31 |  |  | BLK3INV31 | 22 | 0.4% | Connectors |  | String cable found faulty | 6:13 | 6:13 | 10:11 | 10:23 | 0 | 3.9667 | 4.1667 | 4.1667 | mc4 tightned | closed | 0.016667 | 1.47 | 24.4853
1834 | 2025-05-12 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:32 | 12.3167 | BLK6 |  |  | INV8 |  |  | BLK6INV8 | 22 | 0.4449% | Inverter |  | Inverter tripped due to system fault | 9:59 | 9:59 | 11:00 | 11:18 | 0 | 1.0167 | 1.3167 | 1.3167 | After checking all parameter restart the inverter | closed | 0.0058584 | 1.13 | 18.822
1835 | 2025-05-12 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:32 | 12.3167 | BLK8 |  |  | INV15 |  |  | BLK8INV15 | 22 | 0.4004% | Connectors |  | S7-17 half string found grounded | 6:13 | 16:30 |  |  | 10.2833 | -6.2167 | -6.2167 | -6.2167 | today will closed this fault | closed | -0.024895 |  | 0
1836 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:03 | 18:30 | 12.45 | BLK4 |  |  | INV1 |  |  | BLK4INV1 | 22 | 0.45% | Connectors |  | MC4 found open condition | 6:03 | 6:03 | 9:15 | 9:21 | 0 | 3.2 | 3.3 | 3.3 | mc4 tightned | closed | 0.01485 | 0.788 | 13.1254
1837 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:03 | 18:30 | 12.45 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 22 | 0.45% | Connectors |  | Y connecter faulty | 6:03 | 6:03 | 13:10 | 13:23 | 0 | 7.1167 | 7.3333 | 7.3333 | Y connecter burrnt & 2 nos of Mc4 replaced with new one | closed | 0.033 | 3.62 | 60.2971
1838 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:03 | 18:30 | 12.45 | BLK5 |  |  | INV19 |  |  | BLK5INV19 | 22 | 0.4333% | Connectors |  | MC4 found open condition | 6:03 | 6:03 | 13:20 | 13:26 | 0 | 7.2833 | 7.3833 | 7.3833 | mc4 tightned | closed | 0.031994 | 3.71 | 61.7962
1839 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:03 | 18:30 | 12.45 | BLK5 |  |  | INV17 |  |  | BLK5INV17 | 22 | 0.4333% | Connectors |  | MC4 found open condition | 6:03 | 6:03 | 13:15 | 13:31 | 0 | 7.2 | 7.4667 | 7.4667 | mc4 tightned | closed | 0.032356 | 3.61 | 60.1305
1840 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:03 | 18:30 | 12.45 | BLK5 |  |  | INV4 |  |  | BLK5INV4 | 22 | 0.45% | Connectors |  | MC4 found open condition | 6:03 | 6:03 | 15:25 | 15:32 | 0 | 9.3667 | 9.4833 | 9.4833 | One nos of MC4 connector replaced with new one | closed | 0.042675 | 5.51 | 91.7781
1841 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:03 | 18:30 | 12.45 | BLK1 |  |  | MVP |  |  | BLK1MVP | 4338 | 13.4% | LT Panel |  | Tripped on Over current | 10:10 | 10:10 | 10:15 | 10:34 | 0 | 0.083333 | 0.4 | 0.4 | Tripped due to over current | closed | 0.0536 | 0.33 | 1083.8478
1842 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:03 | 18:30 | 12.45 | BLK8 |  |  | INV15 |  |  | BLK8INV15 | 22 | 0.4004% | Connectors |  | S7-17 half string found grounded |  |  |  |  | 0 | 0 | 0 | 0 | today will closed this fault | closed | 0 | 6.7 | 111.5995
1842 | 2025-05-14 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:02 | 18:33 | 12.5167 | BLK1 |  |  | MVP |  |  | BLK1MVP | 4338 | 13.4% | LT Panel |  | Tripped on Over current | 11:30 | 11:30 | 11:35 | 11:40 | 0 | 0.083333 | 0.16667 | 0.16667 | Tripped due to over current | closed | 0.022333 | 0.38 | 1248.0672
1843 | 2025-05-15 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:40 | 18:34 | 12.9 | BLK3 |  |  | INV12 |  |  | BLK3INV12 | 22.25 | 0.45% | Connectors |  | MC4 found open condition | 5:40 | 9:00 | 9:40 | 9:58 | 3.3333 | 4 | 4.3 | 4.3 | mc4 tightned | closed | 0.01935 | 0.342 | 5.7613
1844 | 2025-05-15 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:40 | 18:34 | 12.9 | BLK8 |  |  | INV24 |  |  | BLK8INV24 | 19.1 | 0.4065% | String |  | Pending for verification | 5:40 | 9:00 | 18:52 | 18:52 | 3.3333 | 13.2 | 13.2 | 13.2 | Pending for verification | closed | 0.05366 | 6.81 | 98.4794
1845 | 2025-05-15 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:40 | 18:34 | 12.9 | BLK8 |  |  | INV15 |  |  | BLK8INV15 | 19.1 | 0.4004% | String |  | mc4 Connector Found open | 5:15 | 9:00 | 18:52 | 18:52 | 3.75 | 13.6167 | 13.6167 | 13.6167 | String cable found faulty | closed | 0.054528 | 6.81 | 98.4794
1850 | 2025-05-16 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:24 | 13.15 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 19.1 | 0.2852% | String |  | mc4 Connector Found open | 5:15 | 12:15 | 12:15 | 12:15 | 7 | 7 | 7 | 7 | String Found open restored immidiate | closed | 0.019962 | 2.3 | 33.2603
1851 | 16-May-25 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:24 | 13.15 | BLK7 |  |  | INV12 |  |  | BLK7INV12 | 19.1 | 0.4054% | String |  | mc4 Connector Found open | 5:15 | 13:10 | 13:10 | 13:10 | 7.9167 | 7.9167 | 7.9167 | 7.9167 | String Found open restored immidiate | closed | 0.032094 | 3.1 | 44.8291
1852 | 2025-05-17 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:27 | 18:25 | 12.9667 | BLK4 |  |  | INV31 |  |  | BLK4INV31 | 19.1 | 0.4% | String |  | mc4 Connector Found open | 5:27 | 10:55 | 10:55 | 10:55 | 5.4667 | 5.4667 | 5.4667 | 5.4667 | String Found open restored immidiate | closed | 0.021867 | 0.8 | 11.5688
1853 | 2025-05-17 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:27 | 18:25 | 12.9667 | BLK4 |  |  | INV16 |  |  | BLK4INV16 | 19.1 | 0.45% | String |  | mc4 Connector Found open | 5:27 | 11:13 | 11:13 | 11:13 | 5.7667 | 5.7667 | 5.7667 | 5.7667 | String Found open restored immidiate | closed | 0.02595 | 1.2 | 17.3532
1854 | 2025-05-17 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:27 | 18:25 | 12.9667 | BLK8 |  |  | INV7 |  |  | BLK8INV7 | 19.1 | 0.4333% | String |  | mc4 Connector Found open | 5:27 | 18:08 | 18:08 | 18:08 | 12.6833 | 12.6833 | 12.6833 | 12.6833 | String Found open restored immidiate | closed | 0.054961 | 4.2 | 60.7362
| 2025-05-18 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:23 | 13.15 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 19.1 | 0.3955% | String |  | Y Connector found open same replaced after avrifying load | 5:14 | 12:22 | 12:22 | 12:22 | 7.1333 | 7.1333 | 7.1333 | 7.1333 | String Found open restored immidiate | closed | 0.028213 | 5.1 | 73.7511
1856 | 2025-05-18 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:23 | 13.15 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 22.25 | 0.4449% | String |  | String cut by grass cutting machine same is restored after applying 2 nos Positive and Negative MC4 Connectore | 16:39 | 18:30 | 18:30 | 18:30 | 1.85 | 1.85 | 1.85 | 1.85 | String Found open restored immidiate | closed | 0.0082315 | 0.3 | 5.0538
1857 | 2025-05-18 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:23 | 13.15 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 19.1 | 0.3955% | String |  | Mc4 Connector found open same is restored after varifying the load | 5:14 | 10:05 | 10:05 | 10:05 | 4.85 | 4.85 | 4.85 | 4.85 | String Found open restored immidiate | closed | 0.019182 | 2.3 | 33.2603
1842 | 2025-05-18 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:23 | 13.15 | BLK8 |  |  | All_Inv |  |  | BLK8All_Inv | 4338 |  | LT Panel |  | Tripped on Over current | 12:54 | 12:54 | 13:04 | 13:04 | 0 | 0.16667 | 0.16667 | 0.16667 | Tripped due to over current | closed |  | 0.31 | 1018.1601
1859 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK1 |  |  | INV15 |  |  | BLK1INV15 | 19.1 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 10:15 | 10:15 | 10:15 | 5.0167 | 5.0167 | 5.0167 | 5.0167 | mc4 Connector Found open | closed | 0.020067 | 2.3 | 33.2603
1860 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK1 |  |  | INV21 |  |  | BLK1INV21 | 19.1 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 10:21 | 10:21 | 10:21 | 5.1167 | 5.1167 | 5.1167 | 5.1167 | mc4 Connector Found open | closed | 0.020467 | 2.32 | 33.5495
1861 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK3 |  |  | INV10 |  |  | BLK3INV10 | 19.1 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 10:33 | 10:33 | 10:33 | 5.3167 | 5.3167 | 5.3167 | 5.3167 | mc4 Connector Found open | closed | 0.021267 | 2.38 | 34.4172
1862 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK4 |  |  | INV9 |  |  | BLK4INV9 | 22.25 | 0.4% | String |  | Y Connectoor Fuse was failure | 5:14 | 10:48 | 10:48 | 10:48 | 5.5667 | 5.5667 | 5.5667 | 5.5667 |  | closed | 0.022267 | 2.38 | 40.0933
1863 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK2 |  |  | INV11 |  |  | BLK2INV11 | 22.25 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 10:57 | 10:57 | 10:57 | 5.7167 | 5.7167 | 5.7167 | 5.7167 | mc4 Connector Found open | closed | 0.022867 | 2.34 | 39.4195
1864 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK2 |  |  | INV13 |  |  | BLK2INV13 | 19.1 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 11:20 | 11:20 | 11:20 | 6.1 | 6.1 | 6.1 | 6.1 | mc4 Connector Found open | closed | 0.0244 | 2.45 | 35.4294
1865 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK2 |  |  | INV10 |  |  | BLK2INV10 | 22.25 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 11:28 | 11:28 | 11:28 | 6.2333 | 6.2333 | 6.2333 | 6.2333 | mc4 Connector Found open | closed | 0.024933 | 2.45 | 41.2725
1866 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:26 | 13.2 | BLK8 |  |  | MVP |  |  | BLK8MVP | 4338 | 10.55% | LT Panel |  | Tripped on Over current | 11:45 | 11:45 | 11:50 | 11:50 | 0 | 0.083333 | 0.083333 | 0.083333 | Tripped on Over current | closed | 0.0087908 | 0.3 | 985.3162
1867 | 2025-05-20 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:26 | 13.2 | BLK6 |  |  | INV17 |  |  | BLK6INV17 | 22.25 | 0.412% | String |  | Yconnector Fuse burn | 5:14 | 11:14 | 11:14 | 11:14 | 6 | 6 | 6 | 6 | Y Connectoor Fuse was failure | closed | 0.024719 | 2.3 | 38.7456
1868 | 2025-05-20 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:26 | 13.2 | BLK7 |  |  | INV2 |  |  | BLK7INV2 | 22.25 | 0.3955% | String |  | mc4 Connector Found open | 5:14 | 12:30 | 12:30 | 12:30 | 7.2667 | 7.2667 | 7.2667 | 7.2667 | mc4 Connector Found open | closed | 0.02874 | 2.4 | 40.4302
1869 | 2025-05-20 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:26 | 13.2 | BLK8 |  |  | INV9 |  |  | BLK8INV9 | 22.25 | 0.4333% | String |  | Yconnector Fuse burn | 5:14 | 17:09 | 17:09 | 17:09 | 11.9167 | 11.9167 | 11.9167 | 11.9167 | Y Connectoor Fuse was failure | closed | 0.051639 | 3.4 | 57.2761
1870 | 2025-05-20 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:26 | 13.2 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.25 | 0.3856% | String |  | 1 module replaced | 5:14 | 15:40 | 15:40 | 15:40 | 10.4333 | 10.4333 | 10.4333 | 10.4333 | Module replaced | closed | 0.040233 | 4 | 67.3837
1871 | 2025-05-21 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:27 | 13.1833 | BLK8 |  |  | INV14 |  |  | BLK8INV14 | 22.25 | 0.3856% | String |  | Yconnector Fuse burn | 5:14 | 10:10 | 10:10 | 10:10 | 4.9333 | 4.9333 | 4.9333 | 4.9333 | Y Connectoor Fuse was failure | closed | 0.019024 | 1 | 16.8459
1872 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK3 |  |  | INV16 |  |  | BLK3INV16 | 22.25 | 0.4% | String |  | module fixing | 5:16 | 8:00 | 9:50 | 10:08 | 2.7333 | 4.5667 | 4.8667 | 4.8667 | module fixing, tighten & string rectification | closed | 0.019467 | 0.347 | 5.8455
1873 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK3 |  |  | INV13 |  |  | BLK3INV13 | 22.25 | 0.45% | String |  | module fixing | 5:16 | 8:00 | 10:10 | 10:30 | 2.7333 | 4.9 | 5.2333 | 5.2333 | module fixing, tighten & string rectification | closed | 0.02355 | 0.347 | 5.8455
1874 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK3 |  |  | INV12 |  |  | BLK3INV12 | 22.25 | 0.45% | String |  | module fixing | 5:16 | 8:00 | 10:35 | 10:45 | 2.7333 | 5.3167 | 5.4833 | 5.4833 | module fixing, tighten & string rectification | closed | 0.024675 | 0.375 | 6.3172
1875 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 22.25 | 0.45% | String |  | module fixing | 5:16 | 8:00 | 10:10 | 10:40 | 2.7333 | 4.9 | 5.4 | 5.4 | module fixing, tighten & string rectification | closed | 0.0243 | 0.396 | 6.671
1876 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK5 |  |  | INV15 |  |  | BLK5INV15 | 22.25 | 0.4% | String |  | module fixing | 5:16 | 8:00 | 15:52 | 16:20 | 2.7333 | 10.6 | 11.0667 | 11.0667 | module fixing, tighten & string rectification | closed | 0.044267 | 0.389 | 6.5531
1877 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK5 |  |  | INV22 |  |  | BLK5INV22 | 22.25 | 0.4% | String |  | module fixing | 5:16 | 8:00 | 15:40 | 16:10 | 2.7333 | 10.4 | 10.9 | 10.9 | module fixing, tighten & string rectification | closed | 0.0436 | 0.585 | 9.8549
1878 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 22.25 | 0.3955% | String |  | module fixing | 5:16 | 8:00 | 12:15 | 12:30 | 2.7333 | 6.9833 | 7.2333 | 7.2333 | module fixing, tighten & string rectification | closed | 0.028608 | 0.582 | 9.8043
1879 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK7 |  |  | INV12 |  |  | BLK7INV12 | 20.1 | 0.4054% | String |  | module fixing | 5:16 | 8:00 | 12:35 | 12:50 | 2.7333 | 7.3167 | 7.5667 | 7.5667 | module fixing, tighten & string rectification | closed | 0.030675 | 0.506 | 7.7004
1880 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK7 |  |  | INV13 |  |  | BLK7INV13 | 20.1 | 0.3667% | String |  | module fixing | 5:16 | 8:00 | 12:00 | 12:17 | 2.7333 | 6.7333 | 7.0167 | 7.0167 | module fixing, tighten & string rectification | closed | 0.025728 | 0.535 | 8.1417
1881 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV2 |  |  | BLK8INV2 | 19.1 | 0.2966% | String |  | module fixing | 5:16 | 8:00 | 10:50 | 11:11 | 2.7333 | 5.5667 | 5.9167 | 5.9167 | module fixing, tighten & string rectification | closed | 0.017551 | 0.43 | 6.2182
1882 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV2 |  |  | BLK8INV2 | 19.1 | 0.2966% | String |  | module fixing | 5:16 | 8:00 | 10:50 | 11:22 | 2.7333 | 5.5667 | 6.1 | 6.1 | module fixing, tighten & string rectification | closed | 0.018094 | 0.444 | 6.4207
1883 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV2 |  |  | BLK8INV2 | 19.1 | 0.2966% | String |  | module fixing | 5:16 | 8:00 | 10:50 | 11:35 | 2.7333 | 5.5667 | 6.3167 | 6.3167 | module fixing, tighten & string rectification | closed | 0.018737 | 0.46 | 6.6521
1884 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV17 |  |  | BLK8INV17 | 31.9 | 0.2667% | String |  | module fixing | 5:16 | 8:00 | 11:00 | 11:22 | 2.7333 | 5.7333 | 6.1 | 6.1 | module fixing, tighten & string rectification | closed | 0.016267 | 0.444 | 10.7235
1885 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV24 |  |  | BLK8INV24 | 31.9 | 0.4065% | String |  | module fixing | 5:16 | 8:00 | 11:15 | 11:30 | 2.7333 | 5.9833 | 6.2333 | 6.2333 | module fixing, tighten & string rectification | closed | 0.02534 | 0.454 | 10.9651
1886 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV24 |  |  | BLK8INV24 | 31.9 | 0.4065% | String |  | module fixing | 5:16 | 8:00 | 11:15 | 11:40 | 2.7333 | 5.9833 | 6.4 | 6.4 | module fixing, tighten & string rectification | closed | 0.026017 | 0.465 | 11.2307
1887 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 20.1 | 0.3856% | String |  | module fixing | 5:16 | 8:00 | 11:20 | 11:40 | 2.7333 | 6.0667 | 6.4 | 6.4 | module fixing, tighten & string rectification | closed | 0.02468 | 0.465 | 7.0764
1888 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:13 | 18:29 | 13.2667 | BLK2 |  |  | INV10 |  |  | BLK2INV10 | 22.25 | 0.4% | String |  | 2 fuse was fused which was replaced with a new one & restored | 5:13 | 8:00 | 10:50 | 11:05 | 2.7833 | 5.6167 | 5.8667 | 5.8667 | fuse replaced with a new one & connect the same | closed | 0.023467 | 0.405 | 6.8226
1889 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:13 | 18:29 | 13.2667 | BLK3 |  |  | INV7 |  |  | BLK3INV7 | 22.25 | 0.4% | String |  | mc4 open so rectify & connect the same | 5:13 | 8:00 | 11:00 | 11:20 | 2.7833 | 5.7833 | 6.1167 | 6.1167 | mc4 Connector Found open | closed | 0.024467 | 0.424 | 7.1427
1890 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:13 | 18:29 | 13.2667 | BLK1 |  |  | INV28 |  |  | BLK1INV28 | 22.25 | 0.45% | String |  | mc4 open so rectify & connect the same | 5:13 | 8:00 | 11:35 | 11:50 | 2.7833 | 6.3667 | 6.6167 | 6.6167 | mc4 Connector Found open | closed | 0.029775 | 0.462 | 7.7828
1891 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:13 | 18:29 | 13.2667 | BLK5 |  |  | INV15 |  |  | BLK5INV15 | 22.25 | 0.4% | String |  | module fixing | 5:13 | 8:00 | 12:10 | 13:01 | 2.7833 | 6.95 | 7.8 | 7.8 | module fixing, tighten & string rectification | closed | 0.0312 | 0.533 | 8.9789
1892 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:13 | 18:29 | 13.2667 | BLK6 |  |  | INV12 |  |  | BLK6INV12 | 22.25 | 0.3955% | String |  | mc4 open so rectify & connect the same | 5:13 | 8:00 | 17:20 | 17:40 | 2.7833 | 12.1167 | 12.45 | 12.45 | mc4 open so rectify & connect the same | closed | 0.04924 | 0.629 | 10.5961
1893 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:13 | 18:29 | 13.2667 | BLK6 |  |  | INV8 |  |  | BLK6INV8 | 22.25 | 0.4449% | String |  | String cable found faulty | 5:13 | 8:00 | 17:05 | 17:25 | 2.7833 | 11.8667 | 12.2 | 12.2 | String cable found faulty | closed | 0.054283 | 0.631 | 10.6298
1894 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:13 | 18:29 | 13.2667 | BLK6 |  |  | INV14 |  |  | BLK6INV14 | 22.25 | 0.412% | String |  | mc4 open so rectify & connect the same | 5:13 | 8:00 | 17:30 | 17:45 | 2.7833 | 12.2833 | 12.5333 | 12.5333 | mc4 open so rectify & connect the same | closed | 0.051635 | 0.633 | 10.6635
1895 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK6 |  |  | INV26 |  |  | BLK6INV26 | 22.25 | 0.4449% | MCCB |  | Inv MCCB (250Amp) flash-over replaced with a new one & restore | 5:15 | 5:15 | 10:40 | 11:46 | 0 | 5.4167 | 6.5167 | 6.5167 | Inv MCCB (250Amp) flash-over replaced with a new one & restore | closed | 0.028996 | 2.16 | 36.3872
1896 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK6 |  |  | INV25 |  |  | BLK6INV25 | 22.25 | 0.4449% | MCCB |  | Manually shutdown taken for restoretion work of inv 26 | 5:15 | 10:38 | 10:38 | 11:40 | 5.3833 | 5.3833 | 6.4167 | 6.4167 | Manually shutdown taken for restoretion work of inv 26 | closed | 0.028551 | 0.608 | 10.2423
1897 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK3 |  |  | INV29 |  |  | BLK3INV29 | 22.25 | 0.4333% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 9:00 | 15:15 | 15:28 | 3.75 | 10 | 10.2167 | 10.2167 | MC4 Connector found open Same is restored after verfying the load | closed | 0.044272 | 4.987 | 84.0106
1898 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK3 |  |  | INV24 |  |  | BLK3INV24 | 22.25 | 0.4% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 9:00 | 15:15 | 15:32 | 3.75 | 10 | 10.2833 | 10.2833 | MC4 Connector found open Same is restored after verfying the load | closed | 0.041133 | 5.081 | 85.5941
1899 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK2 |  |  | INV24 |  |  | BLK2INV24 | 22.25 | 0.4333% | String |  | Found Fuse burn replace with a new one & restore the same | 5:15 | 9:00 | 15:30 | 15:53 | 3.75 | 10.25 | 10.6333 | 10.6333 | Found Fuse burn replace with a new one & restore the same | closed | 0.046078 | 5.123 | 86.3017
1900 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK7 |  |  | INV5 |  |  | BLK7INV5 | 22.25 | 0.3955% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 9:00 | 16:25 | 16:40 | 3.75 | 11.1667 | 11.4167 | 11.4167 | MC4 Connector found open Same is restored after verfying the load | closed | 0.045154 | 5.325 | 89.7045
1901 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK7 |  |  | INV2 |  |  | BLK7INV2 | 22.25 | 0.3955% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 9:00 | 16:20 | 16:47 | 3.75 | 11.0833 | 11.5333 | 11.5333 | MC4 Connector found open Same is restored after verfying the load | closed | 0.045615 | 5.416 | 91.2375
1902 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | String |  | Found Fuse burn replace with a new one & restore the same | 5:15 | 9:00 | 16:50 | 17:12 | 3.75 | 11.5833 | 11.95 | 11.95 | Found Fuse burn replace with a new one & restore the same | closed | 0.053775 | 5.44 | 91.6418
1903 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK4 |  |  | INV31 |  |  | BLK4INV31 | 22.25 | 0.4% | String |  | Found Fuse burn replace with a new one & restore the same | 5:15 | 9:00 | 17:15 | 17:35 | 3.75 | 12 | 12.3333 | 12.3333 | Found Fuse burn replace with a new one & restore the same | closed | 0.049333 | 5.61 | 94.5056
1904 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK4 |  |  | INV24 |  |  | BLK4INV24 | 22.25 | 0.45% | String |  | Found MC4 Faulty | 5:45 | 9:00 | 11:20 | 11:36 | 3.25 | 5.5833 | 5.85 | 5.85 | 1Pair of MC4 connector replaced with new one | closed | 0.026325 | 2.53 | 42.6202
1905 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK2 |  |  | INV20 |  |  | BLK2INV20 | 44.5 | 0.4% | String |  | Found MC4 Faulty | 5:45 | 9:00 | 10:10 | 10:38 | 3.25 | 4.4167 | 4.8833 | 4.8833 | 1 No of MC4, 1 pcs of Y connector & 1 pair of Fuse replaced with new one | closed | 0.019533 | 1.75 | 58.9607
1906 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 22.25 | 0.3955% | String |  | Found MC4 Faulty | 5:45 | 9:00 | 11:30 | 11:56 | 3.25 | 5.75 | 6.1833 | 6.1833 | 1Pair of MC4 connector replaced with new one | closed | 0.024455 | 2.82 | 47.5055
1907 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 11.5 | 0.3955% | String |  | module displaced | 5:45 | 9:00 | 15:15 | 15:36 | 3.25 | 9.5 | 9.85 | 9.85 | Fixed with same | closed | 0.038957 | 5.76 | 50.1516
1908 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK8 |  |  | INV2 |  |  | BLK8INV2 | 9.5 | 0.2966% | String |  | module displaced | 5:45 | 9:00 | 15:20 | 15:41 | 3.25 | 9.5833 | 9.9333 | 9.9333 | Fixed with same | closed | 0.029465 | 5.77 | 41.5015
1909 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK8 |  |  | INV24 |  |  | BLK8INV24 | 15.75 | 0.4065% | String |  | module displaced | 5:45 | 9:00 | 15:25 | 15:44 | 3.25 | 9.6667 | 9.9833 | 9.9833 | Fixed with same | closed | 0.040584 | 5.77 | 68.8052
1910 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 11.25 | 0.45% | String |  | module displaced | 5:45 | 9:00 | 9:50 | 10:10 | 3.25 | 4.0833 | 4.4167 | 4.4167 | Fixed with same | closed | 0.019875 | 1.25 | 10.647
1911 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK5 |  |  | INV12 |  |  | BLK5INV12 | 286 | 0.4285% | Inverter |  | Module flyout due to yesterday wind strom impact , same is restored | 5:45 | 9:00 | 6:45 | 7:05 | 3.25 | 1 | 1.3333 | 1.3333 | Reset & Started | closed | 0.0057129 | 0.201 | 43.5238
1912 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 267 | 0.4% | Inverter |  | Module flyout due to yesterday wind strom impact , same is restored | 7:20 | 9:00 | 7:20 | 7:40 | 1.6667 | 0 | 0.33333 | 0.33333 | Reset & Started | closed | 0.0013333 | 0.349 | 70.5507
1913 | 2025-05-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:31 | 13.2833 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 3947.5 | 5.914% | LT Panel |  | LT1 trippedon over current fault | 10:28 | 10:28 | 10:33 | 10:40 | 0 | 0.083333 | 0.2 | 0.2 | Check the all parmeter & charged | closed | 0.011828 | 0.113 | 337.7267
1914 | 2025-05-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:31 | 13.2833 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 267 | 0.4% | Inverter |  | Inverter tripped on excessive leakage current fault | 11:30 | 11:30 | 11:35 | 12:14 | 0 | 0.083333 | 0.73333 | 0.73333 | Reset & Started | closed | 0.0029333 | 0.393 | 79.4454
1915 | 2025-05-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:31 | 13.2833 | BLK5 |  |  | INV23 |  |  | BLK5INV23 | 22.25 | 0.3667% | String |  | Module flyout due to day before yesterday wind strom impact , same is restored | 5:14 | 9:00 | 12:05 | 12:40 | 3.7667 | 6.85 | 7.4333 | 7.4333 | Fixed with same | closed | 0.027256 | 2.319 | 39.0657
1916 | 2025-05-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:31 | 13.2833 | BLK1 |  |  | INV17 |  |  | BLK1INV17 | 22.25 | 0.4% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:14 | 9:00 | 12:35 | 13:00 | 3.7667 | 7.35 | 7.7667 | 7.7667 | MC4 Connector found open Same is restored after verfying the load | closed | 0.031067 | 2.46 | 41.441
1917 | 2025-05-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:31 | 13.2833 | BLK1 | LT2 |  |  |  |  | BLK1LT2 | 4605.75 | 6.9% | LT Panel |  | LT1 trippedon over current fault | 13:18 | 13:18 | 13:29 | 13:29 | 0 | 0.18333 | 0.18333 | 0.18333 | Check the all parmeter & charged | closed | 0.01265 | 0.111 | 387.0688
1918 | 2025-05-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:10 | 18:31 | 13.35 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 22.25 | 0.45% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 9:00 | 16:25 | 16:25 | 3.75 | 11.1667 | 11.1667 | 11.1667 | MC4 Connector found open Same is restored after verfying the load | closed | 0.05025 | 5 | 84.2296
1919 | 2025-05-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:10 | 18:31 | 13.35 | BLK5 |  |  | INV2 |  |  | BLK5INV2 | 22.25 | 0.4% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 9:00 | 16:09 | 16:09 | 3.75 | 10.9 | 10.9 | 10.9 | MC4 Connector found open Same is restored after verfying the load | closed | 0.0436 | 4.3 | 72.4375
1920 | 2025-05-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:10 | 18:31 | 13.35 | BLK5 |  |  | INV32 |  |  | BLK5INV32 | 22.25 | 0.4% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 9:00 | 15:50 | 15:50 | 3.75 | 10.5833 | 10.5833 | 10.5833 | MC4 Connector found open Same is restored after verfying the load | closed | 0.042333 | 4.2 | 70.7529
1921 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK1 | LT1 |  |  |  |  | BLK1LT1 | 4338.75 | 6.5% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:00 | 13:10 |  |  |  |  | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0 | 1.746 | 5735.5319
1922 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK1 | LT2 |  |  |  |  | BLK1LT2 | 4605.75 | 6.9% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:00 | 13:10 |  |  |  |  | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0 | 1.746 | 6088.4877
1923 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK2 | LT1 |  |  |  |  | BLK2LT1 | 4094 | 6.133% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:00 | 13:10 | 0 | 1.8167 | 1.9833 | 1.9833 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.12164 | 1.746 | 5411.989
1924 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 4249.75 | 6.367% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:00 | 13:10 | 0 | 1.8167 | 1.9833 | 1.9833 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.12627 | 1.746 | 5617.8799
1925 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK3 | LT1 |  |  |  |  | BLK3LT1 | 4483.375 | 6.717% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:05 | 13:13 | 0 | 1.9 | 2.0333 | 2.0333 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.13657 | 1.791 | 6079.4667
1926 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK3 | LT2 |  |  |  |  | BLK3LT2 | 4071.75 | 6.1% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:05 | 13:13 | 0 | 1.9 | 2.0333 | 2.0333 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.12403 | 1.791 | 5521.3022
1927 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK4 | LT1 |  |  |  |  | BLK4LT1 | 4394.375 | 6.583% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:05 | 13:13 | 0 | 1.9 | 2.0333 | 2.0333 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.13386 | 1.791 | 5958.7825
1928 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK4 | LT2 |  |  |  |  | BLK4LT2 | 4260.875 | 6.383% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:05 | 13:13 | 0 | 1.9 | 2.0333 | 2.0333 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.12979 | 1.791 | 5777.7562
1929 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK7 | LT1 |  |  |  |  | BLK7LT1 | 3298.1 | 4.941% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:12 | 13:17 | 0 | 2.0167 | 2.1 | 2.1 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.10376 | 1.725 | 4307.4252
1930 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK7 | LT2 |  |  |  |  | BLK7LT2 | 4071.75 | 6.1% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:12 | 13:17 | 0 | 2.0167 | 2.1 | 2.1 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.1281 | 1.725 | 5317.8372
1931 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 3947.5 | 5.914% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:12 | 13:17 | 0 | 2.0167 | 2.1 | 2.1 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.12419 | 1.725 | 5155.5626
1932 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK8 | LT2 |  |  |  |  | BLK8LT2 | 3093.9 | 4.635% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:12 | 13:17 | 0 | 2.0167 | 2.1 | 2.1 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.097336 | 1.725 | 4040.7334
1933 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK5 | LT1 |  |  |  |  | BLK5LT1 | 4514.875 | 6.764% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 15:30 | 15:39 | 0 | 4.3167 | 4.4667 | 4.4667 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.30212 | 2.152 | 7356.1881
1934 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK5 | LT2 |  |  |  |  | BLK5LT2 | 4349.875 | 6.517% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 15:30 | 15:39 | 0 | 4.3167 | 4.4667 | 4.4667 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.29108 | 2.152 | 7087.3499
1935 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK6 | LT1 |  |  |  |  | BLK6LT1 | 4477 | 6.707% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 18:31 | 18:31 | 0 | 7.3333 | 7.3333 | 7.3333 | Jointing work in progress, It will be restored after joint work. | closed | 0.49186 | 4.381 | 14849.9564
1936 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK6 | LT2 |  |  |  |  | BLK6LT2 | 4499 | 6.74% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 18:31 | 18:31 | 0 | 7.3333 | 7.3333 | 7.3333 | Jointing work in progress, It will be restored after joint work. | closed | 0.49427 | 4.381 | 14922.9291
1937 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 22.25 | 0.3333% | string |  | Inverter was tripped due to excessive leakage current, | 13:15 | 13:15 | 13:20 | 12:42 | 0 | 0.083333 | -0.55 | -0.55 | we have physically checked all parameter of this inverter & string's then we found that string no-2 MC4 Connector Positive & negative was failure same is restored after replaced it new one. | closed | -0.0018333 | 0.398 | 6.7047
1938 | 2025-05-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:09 | 18:19 | 13.1667 | BLK5 | LT1 |  |  |  |  | BLK5LT1 | 4514.875 | 6.764% | LT Panel |  | HT Cables jointing work has been done of Block-6 O/G Cable, we have to take manually shutdown of incommer-3(Connected Block 5&6) for take load of Block which is connected to block -5 | 13:20 | 13:20 | 13:40 | 13:56 | 0 | 0.33333 | 0.6 | 0.6 | After connected the load of block-6 to block -5, checked the all parameters then charged the Block 5 | closed | 0.040583 | 0.456 | 1558.7462
1939 | 2025-05-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:09 | 18:19 | 13.1667 | BLK5 | LT2 |  |  |  |  | BLK5LT2 | 4349.875 | 6.517% | LT Panel |  | HT Cables jointing work has been done of Block-6 O/G Cable, we have to take manually shutdown of incommer-3(Connected Block 5&6) for take load of Block which is connected to block -5 | 13:20 | 13:20 | 13:40 | 13:56 | 0 | 0.33333 | 0.6 | 0.6 | After connected the load of block-6 to block -5, checked the all parameters then charged the Block 5 | closed | 0.0391 | 0.456 | 1501.7805
1940 | 2025-05-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:09 | 18:19 | 13.1667 | BLK6 | LT1 |  |  |  |  | BLK6LT1 | 4477 | 6.707% | LT Panel |  | HT Cable jointing work | 5:09 | 5:09 | 14:00 | 14:13 | 0 | 8.85 | 9.0667 | 9.0667 | after checking all the parameter & visual inspection of block 6 we charge the ICR | closed | 0.60811 | 4.47 | 15151.6332
1941 | 2025-05-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:09 | 18:19 | 13.1667 | BLK6 | LT2 |  |  |  |  | BLK6LT2 | 4499 | 6.74% | LT Panel |  | HT Cable jointing work | 5:09 | 5:09 | 14:00 | 14:13 | 0 | 8.85 | 9.0667 | 9.0667 | after checking all the parameter & visual inspection of block 6 we charge the ICR | closed | 0.6111 | 4.47 | 15226.0884
1942 | 2025-05-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:09 | 18:19 | 13.1667 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 3947.5 | 5.914% | LT Panel |  | LT-1 was in breakdown under over current | 13:42 | 13:50 | 14:35 | 14:48 | 0.13333 | 0.88333 | 1.1 | 1.1 | after checking all the parameter & visual inspection of block 8 LT-1 we charge it. | closed | 0.065052 | 0.345 | 1031.1125
1943 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK6 | LT2 |  |  |  |  | BLK6LT2 | 22.25 | 6.74% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 1930:00 | 10:30 | 10:30 | 1924.75 | 5.25 | 5.25 | 5.25 | MC4 Connector found open Same is restored after verfying the load | closed | 0.35385 | 2.2 | 37.061
1944 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK6 | LT2 |  |  |  |  | BLK6LT2 | 22.25 | 6.74% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 1930:00 | 11:00 | 11:00 | 1924.75 | 5.75 | 5.75 | 5.75 | MC4 Connector found open Same is restored after verfying the load | closed | 0.38755 | 2.1 | 35.3764
1945 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK6 | LT2 |  |  |  |  | BLK6LT2 | 22.25 | 6.74% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 1930:00 | 11:05 | 11:05 | 1924.75 | 5.8333 | 5.8333 | 5.8333 | MC4 Connector found open Same is restored after verfying the load | closed | 0.39317 | 2.1 | 35.3764
1946 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK1 | LT1 |  |  |  |  | BLK1LT1 | 22.25 | 6.5% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 1930:00 | 14:28 | 14:28 | 1924.75 | 9.2167 | 9.2167 | 9.2167 | MC4 Connector found open Same is restored after verfying the load | closed | 0.59908 | 4.3 | 72.4375
1947 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK1 | LT1 |  |  |  |  | BLK1LT1 | 22.25 | 6.5% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 1930:00 | 14:38 | 14:38 | 1924.75 | 9.3833 | 9.3833 | 9.3833 | MC4 Connector found open Same is restored after verfying the load | closed | 0.60992 | 4.4 | 74.1221
1948 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 22.25 | 6.367% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 1930:00 | 14:53 | 14:53 | 1924.75 | 9.6333 | 9.6333 | 9.6333 | MC4 Connector found open Same is restored after verfying the load | closed | 0.61332 | 4.5 | 75.8067
1949 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 22.25 | 6.367% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 1930:00 | 15:38 | 15:38 | 1924.75 | 10.3833 | 10.3833 | 10.3833 | MC4 Connector found open Same is restored after verfying the load | closed | 0.66107 | 5 | 84.2296
1950 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK8 | LT2 |  |  |  |  | BLK8LT2 | 67.25 | 4.635% | string |  | Block8 Inv No 28 3 nos String add after replaced all faulty module(Jakson-335wp),Now Inverter isrunning with total 12.5 String | 5:15 | 1930:00 | 16:40 | 16:40 | 1924.75 | 11.4167 | 11.4167 | 11.4167 | Block8 Inv No 28 3 nos String add after replaced all faulty module(Jakson-335wp),Now Inverter isrunning with total 12.5 String | closed | 0.52917 | 5.3 | 269.8566
1951 | 2025-06-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:33 | 13.3167 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 267 | 0.3955% | Inverter |  | Inv 6 Under breakdown due to insulation fault | 5:14 | 10:00 | 9:32 | 9:32 | 4.7667 | 4.3 | 4.3 | 4.3 | Inv 6 Under breakdown due to insulation fault | closed | 0.017007 | 2.1 | 426.2119
1952 | 2025-06-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:33 | 13.3167 | BLK6 |  |  | INV24 |  |  | BLK6INV24 | 22.3 | 0.4285% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:14 | 10:00 | 10:20 | 10:20 | 4.7667 | 5.1 | 5.1 | 5.1 | MC4 Connector found open Same is restored after verfying the load | closed | 0.021852 | 1.3 | 22.0365
1953 | 2025-06-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:33 | 13.3167 | BLK8 |  |  | INV14 |  |  | BLK8INV14 | 22.3 | 0.3856% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:14 | 10:00 | 10:38 | 10:38 | 4.7667 | 5.4 | 5.4 | 5.4 | MC4 Connector found open Same is restored after verfying the load | closed | 0.020823 | 1.4 | 23.7317
1954 | 2025-06-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:33 | 13.3167 | BLK2 |  |  | INV29 |  |  | BLK2INV29 | 22.3 | 0.45% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:14 | 10:00 | 11:20 | 11:20 | 4.7667 | 6.1 | 6.1 | 6.1 | MC4 Connector found open Same is restored after verfying the load | closed | 0.02745 | 1.5 | 25.4268
1955 | 2025-06-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:33 | 13.3167 | BLK8 |  |  | INV26 |  |  | BLK8INV26 | 22.3 | 0.4065% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:14 | 10:00 | 2:45 | 2:45 | 4.7667 | -2.4833 | -2.4833 | -2.4833 | MC4 Connector found open Same is restored after verfying the load | closed | -0.010095 | 1.4 | 23.7317
1956 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:36 | 11:36 | 11:36 | 11:46 | 0 | 0 | 0.16667 | 0.16667 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.022333 | 0.3 | 2039.7285
1957 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8909 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:36 | 11:36 | 11:46 | 11:46 | 0 | 0.16667 | 0.16667 | 0.16667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.022134 | 0.3 | 2031.633
1958 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8944.5 | 13.45% | IDT |  | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:38 | 11:38 | 11:48 | 11:48 | 0 | 0.16667 | 0.16667 | 0.16667 | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.022412 | 0.3 | 2039.7285
1959 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:38 | 11:38 | 11:53 | 11:53 | 0 | 0.25 | 0.25 | 0.25 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.0335 | 0.4 | 2719.638
1960 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:24 | 12:24 | 12:31 | 12:31 | 0 | 0.11667 | 0.11667 | 0.11667 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.014583 | 0.28 | 1887.9113
1961 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:24 | 12:24 | 12:35 | 12:35 | 0 | 0.18333 | 0.18333 | 0.18333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.024348 | 0.29 | 1978.6815
1963 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8909.25 | 13.45% | IDT |  | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:24 | 12:24 | 12:38 | 12:38 | 0 | 0.23333 | 0.23333 | 0.23333 | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.031377 | 0.31 | 2099.413
1964 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK5 |  |  | INV20 |  |  | BLK5INV20 | 22.5 | 0.4% | string |  | Found Fuse, Y- connector & MC4 burn replace with a new one & restore the same | 12:24 | 12:24 | 12:40 | 12:40 | 0 | 0.26667 | 0.26667 | 0.26667 | Found Fuse, Y- connector & MC4 burn replace with a new one & restore the same | closed | 0.0010667 | 0.31 | 5.302
1965 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 22.5 | 0.45% | string |  | MC4 connector melted causes failure so replaced it with new one | 5:15 | 9:00 | 15:06 | 15:06 | 3.75 | 9.85 | 9.85 | 9.85 | MC4 connector melted causes failure so replaced it with new one | closed | 0.044325 | 5.1 | 87.2264
1966 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:11 | 11:26 | 11:17 | 11:17 | 0.25 | 0.1 |  |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0 | 0.35 | 2359.8892
1967 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:20 | 11:25 | 11:25 | 11:25 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011067 | 0.21 | 1432.8383
1968 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:48 | 12:00 | 11:55 | 11:55 | 0.2 | 0.11667 | 0.11667 | 0.11667 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.014583 | 0.21 | 1415.9335
1969 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:48 | 11:56 | 11:55 | 11:55 | 0.13333 | 0.11667 | 0.11667 | 0.11667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.015494 | 0.21 | 1432.8383
1970 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:09 | 12:22 | 12:15 | 12:15 | 0.21667 | 0.1 | 0.1 | 0.1 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.0134 | 0.15 | 1019.8643
1971 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:09 | 12:20 | 12:15 | 12:15 | 0.18333 | 0.1 | 0.1 | 0.1 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.0125 | 0.15 | 1011.3811
1972 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:15 | 12:21 | 12:22 | 12:22 | 0.1 | 0.11667 | 0.11667 | 0.11667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.015494 | 0.16 | 1091.6863
1973 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:28 | 12:34 | 12:35 | 12:35 | 0.1 | 0.11667 | 0.11667 | 0.11667 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.014583 | 0.16 | 1078.8065
1974 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:29 | 12:36 | 12:35 | 12:35 | 0.11667 | 0.1 | 0.1 | 0.1 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.013281 | 0.14 | 955.2255
1975 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8976 | 13.45% | IDT |  | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:29 | 12:38 | 12:35 | 12:35 | 0.15 | 0.1 | 0.1 | 0.1 | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.013447 | 0.145 | 989.3407
1976 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK7 | LT1 |  |  |  |  | BLK7LT1 | 4071.75 | 4.941% | LT Panel |  | Block-7 LT1 tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:25 | 12:32 | 12:35 | 12:35 | 0.11667 | 0.16667 | 0.16667 | 0.16667 | Block-7 LT1 tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.008235 | 0.13 | 402.3644
1977 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK1 |  |  | INV1 |  |  | BLK1INV1 | 289.25 | 0.4333% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 12:17 | 13:12 | 12:24 | 12:24 | 0.91667 | 0.11667 | 0.11667 | 0.11667 | As per O2 Team, instruction we have taken manually shutdown for active power control | closed | 0.00050556 | 0.44 | 96.7433
1978 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK1 |  |  | INV2 |  |  | BLK1INV2 | 289.25 | 0.4333% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 12:17 | 13:12 | 12:24 | 12:24 | 0.91667 | 0.11667 | 0.11667 | 0.11667 | As per O2 Team, instruction we have taken manually shutdown for active power control | closed | 0.00050556 | 0.44 | 96.7433
1979 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK1 |  |  | INV3 |  |  | BLK1INV3 | 289.25 | 0.4% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 12:17 | 13:13 | 12:24 | 12:24 | 0.93333 | 0.11667 | 0.11667 | 0.11667 | As per O2 Team, instruction we have taken manually shutdown for active power control | closed | 0.00046667 | 0.44 | 96.7433
1980 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | INV1 |  |  | BLK2INV1 | 243.275 | 0.45% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 12:16 | 12:59 | 12:24 | 12:24 | 0.71667 | 0.13333 | 0.13333 | 0.13333 | As per O2 Team, instruction we have taken manually shutdown for active power control | closed | 0.0006 | 0.46 | 85.0649
1981 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 334.55 | 0.3333% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 12:16 | 13:05 | 12:24 | 12:24 | 0.81667 | 0.13333 | 0.13333 | 0.13333 | As per O2 Team, instruction we have taken manually shutdown for active power control | closed | 0.00044444 | 0.46 | 116.9806
1982 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | INV16 |  |  | BLK5INV16 | 289.25 | 0.4333% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 12:20 | 13:10 | 12:24 | 12:24 | 0.83333 | 0.066667 | 0.066667 | 0.066667 | As per O2 Team, instruction we have taken manually shutdown for active power control | closed | 0.00028889 | 0.31 | 68.1601
1983 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | INV22 |  |  | BLK5INV22 | 244.75 | 0.4% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 12:20 | 13:10 | 12:24 | 12:24 | 0.83333 | 0.066667 | 0.066667 | 0.066667 | As per O2 Team, instruction we have taken manually shutdown for active power control | closed | 0.00026667 | 0.31 | 57.6739
1984 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK8 |  |  | INV24 |  |  | BLK8INV24 | 31.9 | 0.4065% | String |  | MC4 Connector found melted, Same is restored after verfying the load | 5:19 | 9:00 | 10:31 | 10:31 | 3.6833 | 5.2 | 5.2 | 5.2 | MC4 Connector found melted, Same is restored after verfying the load | closed | 0.021139 | 1.28 | 31.0381
1985 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK8 |  |  | INV15 |  |  | BLK8INV15 | 20.1 | 0.4004% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:19 | 9:00 | 10:45 | 10:45 | 3.6833 | 5.4333 | 5.4333 | 5.4333 | MC4 Connector found open Same is restored after verfying the load | closed | 0.021758 | 1.41 | 21.5432
1986 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK8 |  |  | INV21 |  |  | BLK8INV21 | 20.1 | 0.4004% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:19 | 9:00 | 11:00 | 11:00 | 3.6833 | 5.6833 | 5.6833 | 5.6833 | MC4 Connector found open Same is restored after verfying the load | closed | 0.022759 | 1.56 | 23.835
1987 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK8 |  |  | INV10 |  |  | BLK8INV10 | 20.1 | 0.45% | String |  | MC4 Connector found melted, Same is restored after verfying the load | 5:19 | 9:00 | 15:15 | 15:15 | 3.6833 | 9.9333 | 9.9333 | 9.9333 | MC4 Connector found melted, Same is restored after verfying the load | closed | 0.0447 | 3.7 | 56.5318
1988 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK8 |  |  | INV18 |  |  | BLK8INV18 | 20.1 | 0.3333% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:19 | 9:00 | 15:30 | 15:30 | 3.6833 | 10.1833 | 10.1833 | 10.1833 | MC4 Connector found open Same is restored after verfying the load | closed | 0.033944 | 3.76 | 57.4485
1989 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 22.25 | 0.3955% | String |  | Y connector & fuse failure so replaced it with new one | 5:19 | 9:00 | 15:45 | 15:45 | 3.6833 | 10.4333 | 10.4333 | 10.4333 | Y connector & fuse failure so replaced it with new one | closed | 0.041264 | 3.82 | 64.6083
1990 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 22.25 | 0.3955% | String |  | MC4 Connector found melted, Same is restored after verfying the load | 5:19 | 9:00 | 16:10 | 16:10 | 3.6833 | 10.85 | 10.85 | 10.85 | MC4 Connector found melted, Same is restored after verfying the load | closed | 0.042912 | 3.92 | 66.2996
1991 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK3 |  |  | INV28 |  |  | BLK3INV28 | 22.25 | 0.4167% | sTring |  | Y connector & fuse failure so replaced it with new one | 5:19 | 9:00 | 16:20 | 16:20 | 3.6833 | 11.0167 | 11.0167 | 11.0167 | Y connector & fuse failure so replaced it with new one | closed | 0.045903 | 3.95 | 66.807
1992 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK4 |  |  | INV4 |  |  | BLK4INV4 | 22.25 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:19 | 9:00 | 16:35 | 16:35 | 3.6833 | 11.2667 | 11.2667 | 11.2667 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.045067 | 4.01 | 67.8218
1993 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | INV8 |  |  | BLK5INV8 | 22.25 | 0.4333% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:19 | 9:00 | 16:55 | 16:55 | 3.6833 | 11.6 | 11.6 | 11.6 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.050267 | 4.07 | 68.8366
1994 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | INV21 |  |  | BLK5INV21 | 22.25 | 0.4333% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:19 | 9:00 | 17:10 | 17:10 | 3.6833 | 11.85 | 11.85 | 11.85 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.05135 | 4.11 | 69.5131
1995 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK2 |  |  | mvp |  |  | BLK2mvp | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:13 | 11:13 | 11:15 | 11:18 | 0 | 0.033333 | 0.083333 | 0.083333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.010417 | 0.065 | 438.2651
1996 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | mvp |  |  | BLK5mvp | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:12 | 11:12 | 11:14 | 11:17 | 0 | 0.033333 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011067 | 0.064 | 436.6745
1997 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | INV32 |  |  | BLK5INV32 | 22.23 | 0.4% | String |  | Y connector, fuse & mc4 failure | 5:10 | 9:00 | 11:55 | 12:10 | 3.8333 | 6.75 | 7 | 7 | Y connector, fuse & mc4 failure so replaced it with new one | closed | 0.028 | 2.061 | 34.8267
1998 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | INV29 |  |  | BLK5INV29 | 22.23 | 0.4% | String |  | MC4 Connector found melted | 5:10 | 9:00 | 12:10 | 12:25 | 3.8333 | 7 | 7.25 | 7.25 | MC4 Connector found melted, Same is restored after verfying the load | closed | 0.029 | 2.21 | 37.3445
1999 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | INV30 |  |  | BLK5INV30 | 22.23 | 0.4% | String |  | MC4 Connecto found open | 5:10 | 9:00 | 12:25 | 12:45 | 3.8333 | 7.25 | 7.5833 | 7.5833 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.030333 | 2.38 | 40.2172
2000 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | INV28 |  |  | BLK5INV28 | 22.23 | 0.45% | String |  | MC4 Connecto found open | 5:10 | 9:00 | 12:45 | 13:05 | 3.8333 | 7.5833 | 7.9167 | 7.9167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.035625 | 2.54 | 42.9208
2001 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | INV31 |  |  | BLK5INV31 | 22.23 | 0.4% | String |  | MC4 Connecto found open | 5:10 | 9:00 | 14:50 | 15:10 | 3.8333 | 9.6667 | 10 | 10 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.04 | 3.84 | 64.8882
2002 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | INV12 |  |  | BLK5INV12 | 22.23 | 0.4285% | String |  | MC4 Connecto found open | 5:10 | 9:00 | 15:10 | 15:30 | 3.8333 | 10 | 10.3333 | 10.3333 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.044275 | 4.08 | 68.9437
2003 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 22.23 | 0.45% | String |  | Found 1 fuse failure | 5:10 | 9:00 | 15:25 | 15:45 | 3.8333 | 10.25 | 10.5833 | 10.5833 | Found 1 fuse failure so replaced it with new one | closed | 0.047625 | 4.22 | 71.3094
2004 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 267 | 0.4% | String |  | Inverter frequently shutdown on fault of excessive leakage current | 8:00 | 8:00 | 8:15 | 9:41 | 0 | 0.25 | 1.6833 | 1.6833 | Inverter frequently shutdown on fault of excessive leakage current after reset the fault & verify all parameter charge the inverter | closed | 0.0067333 | 0.65 | 131.9227
2005 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 | 18:36 | 13.5 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:44 | 12:44 | 12:46 | 12:57 | 0 | 0.033333 | 0.21667 | 0.21667 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.029033 | 0.38 | 2583.6561
2006 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:44 | 12:44 | 12:46 | 12:55 | 0 | 0.033333 | 0.18333 | 0.18333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.022917 | 0.38 | 2562.1654
2007 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:44 | 12:44 | 12:46 | 12:51 | 0 | 0.033333 | 0.11667 | 0.11667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.015494 | 0.28 | 1910.4511
2008 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8976 | 13.45% | IDT |  | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:44 | 12:44 | 12:46 | 12:50 | 0 | 0.033333 | 0.1 | 0.1 | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.013447 | 0.26 | 1773.9903
2009 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 13:04 | 13:04 | 13:06 | 13:19 | 0 | 0.033333 | 0.25 | 0.25 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.03125 | 0.28 | 1887.9113
2010 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 13:12 | 13:12 | 13:14 | 13:17 | 0 | 0.033333 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011067 | 0.25 | 1705.7599
2011 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK7 |  |  | MVP |  |  | BLK7MVP | 8870.1 | 11.04% | IDT |  | Block-7 LT1 tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:40 | 12:40 | 12:42 | 12:50 | 0 | 0.033333 | 0.16667 | 0.16667 | Block-7 LT1 tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.018402 | 0.22 | 1483.3589
2012 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK1 |  |  | INV1 |  |  | BLK1INV1 | 289.25 | 0.4333% | Inverter |  | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | 10:39 | 10:55 | 10:55 | 10:55 | 0.26667 | 0.26667 | 0.26667 | 0.26667 | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | closed | 0.0011556 | 0.31 | 68.1601
2013 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK2 |  |  | INV29 |  |  | BLK2INV29 | 267 | 0.45% | Inverter |  | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | 10:39 | 10:55 | 10:55 | 10:55 | 0.26667 | 0.26667 | 0.26667 | 0.26667 | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | closed | 0.0012 | 0.31 | 62.917
2014 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK2 |  |  | INV30 |  |  | BLK2INV30 | 298 | 0.4% | Inverter |  | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | 10:39 | 10:55 | 10:55 | 10:55 | 0.26667 | 0.26667 | 0.26667 | 0.26667 | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | closed | 0.0010667 | 0.31 | 70.222
2015 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK3 |  |  | INV17 |  |  | BLK3INV17 | 22.5 | 0.4333% | String |  | MC4 Connecto found open Same is restored after verfying the load | 9:00 | 10:55 | 10:55 | 10:55 | 1.9167 | 1.9167 | 1.9167 | 1.9167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.0083056 | 0.33 | 5.6441
2016 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK4 |  |  | INV21 |  |  | BLK4INV21 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 9:00 | 15:10 | 15:10 | 15:10 | 6.1667 | 6.1667 | 6.1667 | 6.1667 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.024667 | 0.64 | 10.9461
2017 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 9:00 | 15:30 | 15:30 | 15:30 | 6.5 | 6.5 | 6.5 | 6.5 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.026 | 0.61 | 10.433
2018 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 9:00 | 15:50 | 15:50 | 15:50 | 6.8333 | 6.8333 | 6.8333 | 6.8333 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.027333 | 0.62 | 10.604
2019 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK1 |  |  | INV31 |  |  | BLK1INV31 | 22.5 | 0.45% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:07 | 15:45 | 15:45 | 16:08 | 10.6333 | 10.6333 | 11.0167 | 11.0167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.049575 | 5.23 | 89.4498
2020 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK1 |  |  | INV8 |  |  | BLK1INV8 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:07 | 16:20 | 16:20 | 16:27 | 11.2167 | 11.2167 | 11.3333 | 11.3333 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.045333 | 5.32 | 90.9891
2021 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK1 |  |  | INV8 |  |  | BLK1INV8 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:07 | 16:10 | 16:10 | 16:29 | 11.05 | 11.05 | 11.3667 | 11.3667 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.045467 | 5.41 | 92.5284
2022 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 22.5 | 0.45% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:07 | 16:10 | 16:10 | 16:43 | 11.05 | 11.05 | 11.6 | 11.6 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.0522 | 5.46 | 93.3835
2023 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK2 |  |  | INV20 |  |  | BLK2INV20 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:07 | 16:20 | 16:20 | 16:47 | 11.2167 | 11.2167 | 11.6667 | 11.6667 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.046667 | 5.51 | 94.2387
2024 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK2 |  |  | INV17 |  |  | BLK2INV17 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:07 | 16:32 | 16:32 | 16:52 | 11.4167 | 11.4167 | 11.75 | 11.75 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.047 | 5.59 | 95.6069
2025 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK2 |  |  | INV18 |  |  | BLK2INV18 | 22.5 | 0.4167% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:07 | 16:44 | 16:44 | 16:56 | 11.6167 | 11.6167 | 11.8167 | 11.8167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.049236 | 6.12 | 104.6716
2026 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK2 |  |  | INV16 |  |  | BLK2INV16 | 22.5 | 0.4333% | String |  | MC4 connector failure | 5:07 | 16:56 | 16:56 | 17:08 | 11.8167 | 11.8167 | 12.0167 | 12.0167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.052072 | 6.18 | 105.6978
2027 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 22.5 | 0.3333% | String |  | MC4 connector failure | 5:07 | 17:00 | 17:00 | 17:13 | 11.8833 | 11.8833 | 12.1 | 12.1 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.040333 | 6.26 | 107.0661
2028 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK3 |  |  | INV24 |  |  | BLK3INV24 | 22.5 | 0.4% | String |  | MC4 Connecto found open | 5:08 | 10:11 | 10:11 | 10:25 | 5.05 | 5.05 | 5.2833 | 5.2833 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.021133 | 0.95 | 16.248
2029 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 22.5 | 0.3955% | String |  | MC4 Connecto found open | 5:08 | 10:20 | 10:20 | 10:45 | 5.2 | 5.2 | 5.6167 | 5.6167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.022214 | 1.2 | 20.5238
2030 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 22.5 | 0.3955% | String |  | MC4 Connecto found open | 5:08 | 11:02 | 11:02 | 11:10 | 5.9 | 5.9 | 6.0333 | 6.0333 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.023862 | 1.47 | 25.1417
2031 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK8 |  |  | INV10 |  |  | BLK8INV10 | 22.5 | 0.45% | String |  | MC4 Connecto found open | 5:08 | 11:02 | 11:02 | 11:30 | 5.9 | 5.9 | 6.3667 | 6.3667 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.02865 | 1.88 | 32.154
2032 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 22.5 | 0.4% | String |  | Y connector & fuse failure so replaced it with new one | 5:08 | 11:55 | 11:55 | 12:10 | 6.7833 | 6.7833 | 7.0333 | 7.0333 | Y connector & fuse failure so replaced it with new one | closed | 0.028133 | 2.29 | 39.1663
2033 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 22.5 | 0.4% | String |  | Y connector & fuse failure so replaced it with new one | 5:08 | 11:55 | 11:55 | 12:20 | 6.7833 | 6.7833 | 7.2 | 7.2 | Y connector & fuse failure so replaced it with new one | closed | 0.0288 | 2.77 | 47.3759
2034 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK1 |  |  | INV31 |  |  | BLK1INV31 | 22.25 | 0.45% | String |  | MC4 Connecto found open | 5:08 | 9:00 | 16:10 | 16:20 | 3.8667 | 11.0333 | 11.2 | 11.2 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.0504 | 5.88 | 99.4495
2035 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 22.25 | 0.45% | String |  | MC4 Connecto found open | 5:08 | 9:00 | 16:40 | 16:55 | 3.8667 | 11.5333 | 11.7833 | 11.7833 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.053025 | 5.88 | 99.4495
2036 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 22.25 | 0.45% | String |  | MC4 Connecto found open | 5:08 | 9:00 | 9:00 | 9:45 | 3.8667 | 3.8667 | 4.6167 | 4.6167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.020775 | 1.19 | 20.1267
2037 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 22.25 | 0.45% | String |  | MC4 Connecto found open | 5:08 | 9:20 | 9:20 | 9:55 | 4.2 | 4.2 | 4.7833 | 4.7833 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.021525 | 1.22 | 20.6341
2038 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK5 |  |  | INV2 |  |  | BLK5INV2 | 22.25 | 0.4% | String |  | MC4 Connecto found open | 5:08 | 10:00 | 10:00 | 10:15 | 4.8667 | 4.8667 | 5.1167 | 5.1167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.020467 | 1.78 | 30.1054
2039 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 22.25 | 0.45% | String |  | MC4 Connecto found open | 5:08 | 10:10 | 10:10 | 10:35 | 5.0333 | 5.0333 | 5.45 | 5.45 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.024525 | 2.76 | 46.6804
2040 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK5 |  |  | INV12 |  |  | BLK5INV12 | 22.25 | 0.4285% | String |  | MC4 Connecto found open | 5:08 | 11:00 | 11:00 | 11:10 | 5.8667 | 5.8667 | 6.0333 | 6.0333 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.025851 | 2.98 | 50.4013
2041 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK4 |  |  | INV1 |  |  | BLK4INV1 | 22.25 | 0.45% | String |  | During String current measurement activity we have observed that String-12 is grounded | 5:08 | 12:05 | 12:05 | 12:15 | 6.95 | 6.95 | 7.1167 | 7.1167 | During String current measurement activity we have observed that String-12 is grounded, so replaced with new one. | closed | 0.032025 | 3.55 | 60.0418
2042 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK3 |  |  | INV24 |  |  | BLK3INV24 | 22.25 | 0.4% | String |  | MC4 Connector melted | 5:08 | 15:05 | 15:05 | 15:10 | 9.95 | 9.95 | 10.0333 | 10.0333 | MC4 Connector melted so replace it with new one | closed | 0.040133 | 5.11 | 86.4263
2043 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK2 |  |  | INV3 |  |  | BLK2INV3 | 22.25 | 0.1667% | String |  | fuse failure | 5:08 | 15:10 | 15:10 | 15:30 | 10.0333 | 10.0333 | 10.3667 | 10.3667 | fuse failure so replaced it with new one | closed | 0.017278 | 5.45 | 92.1768
2044 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK2 |  |  | INV17 |  |  | BLK2INV17 | 22.25 | 0.4% | String |  | MC4 Connector found open | 5:08 | 15:20 | 15:20 | 15:55 | 10.2 | 10.2 | 10.7833 | 10.7833 | MC4 Connecto found open Same is restored after verfying the load[@[Action taken]] | closed | 0.043133 | 6.11 | 103.3395
2045 | 2025-06-10 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:09 | 18:38 | 13.4833 | BLK8 |  |  | INV26 |  |  | BLK8INV26 | 271.35 | 0.4065% | Inverter |  | Inv Shut down on the fault of 47 (Relay Card Faulty) | 8:55 | 9:00 | 9:35 | 11:25 | 0.083333 | 0.66667 | 2.5 | 2.5 | after discussion with OEM we replaced the Inv with a new one | closed | 0.010163 | 0.746 | 153.8735
2046 | 2025-06-14 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:43 | 13.5833 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 264 | 0.3955% | Inverter |  | INVERTER SHUT DOWN on fault of excessive leakage current, restore | 7:45 | 7:50 | 8:05 | 8:22 | 0.083333 | 0.33333 | 0.61667 | 0.61667 | after checking the all strin found string no 4 &11 floating is not ok, after rectification connected the string & restore | closed | 0.002439 | 0.186 | 37.326
2047 | 2025-06-15 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 18:29 | 13.2333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:25 | 12:25 | 12:27 | 12:29 | 0 | 0.033333 | 0.066667 | 0.066667 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.0083333 | 0.0371 | 250.1483
2048 | 2025-06-15 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 18:29 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:24 | 12:24 | 12:28 | 12:29 | 0 | 0.066667 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011067 | 0.0371 | 253.1348
2049 | 2025-06-16 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:13 | 17:53 | 11.6667 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:52 | 12:52 | 12:56 | 12:57 | 0 | 0.066667 | 0.083333 | 0.083333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.010417 | 0.075 | 505.6905
2050 | 2025-06-16 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 18:29 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:55 | 11:55 | 11:58 | 11:59 | 0 | 0.05 | 0.066667 | 0.066667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.0088537 | 0.112 | 764.1804
2051 | 2025-06-18 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 | 18:34 | 13.4667 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:47 | 11:47 | 11:52 | 11:52 | 0 | 0.083333 | 0.083333 | 0.083333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.010417 | 0.101 | 640.5864
2052 | 2025-06-18 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 | 18:34 | 13.4667 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:54 | 12:54 | 12:58 | 12:58 | 0 | 0.066667 | 0.066667 | 0.066667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.0088537 | 0.069 | 464.9547
2053 | 2025-06-18 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 | 18:34 | 13.4667 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 22.25 | 0.3333% | Inverter |  | Inv tripped on fault of string back fedded current | 11:52 | 11:52 | 12:00 | 12:26 | 0 | 0.13333 | 0.56667 | 0.56667 | we have physically checked all parameter of this inverter & string's then we found that all string are healthy same is store. | closed | 0.0018889 | 0.559 | 9.4545
2054 | 2025-06-18 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 | 18:34 | 13.4667 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 267 | 0.4% | Inverter |  | INV tripped on fault of excessive leakage current | 10:00 | 10:02 | 10:10 | 10:30 | 0.033333 | 0.16667 | 0.5 | 0.5 | we have physically checked all parameter of this inverter & string's then we found that string no-4,9,11 MC4 Connector Positive & negative was failure same is restored after replaced it new one. | closed | 0.002 | 0.219 | 44.4478
2055 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:24 | 17:50 | 12.4333 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 267 | 0.4% | Inverter |  | INV tripped on fault of excessive leakage current | 8:08 | 8:10 | 8:20 | 9:03 | 0.033333 | 0.2 | 0.91667 | 0.91667 | we have physically checked all parameter of this inverter & string's then we found that string no-6,10, MC4 Connector Positive & negative was failure same is restored after replaced it new one. | closed | 0.0036667 | 0.217 | 44.0419
2056 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:24 | 17:50 | 12.4333 | BLK4 |  |  | MVP |  |  | BLK4MVP | 8655.25 | 12.97% | IDT |  | B-4 IDT tripped due to 2 Nos. of 500Amp MCCb failure after generation | 17:04 | 17:04 | 8:20 | 22:06 | 0 | -8.7333 | 5.0333 | 5.0333 | after checking the all parameters & verifying the load charge the IDT | closed | 0.65266 | 0 | 0
2057 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:24 | 17:50 | 12.4333 | BLK4 | LT1 | ACCB1 |  |  |  | BLK4LT1ACCB1 | 534 | 0.8% | ACCB |  | B-4 IDT tripped due to 2 Nos. of 500Amp MCCb failure after generation | 17:04 | 17:04 | 8:20 |  | 0 | -8.7333 | -17.0667 | -17.0667 | MCCB meggaring value is not good | closed | -0.13653 | 0 | 0
2058 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:24 | 17:50 | 12.4333 | BLK4 | LT1 | ACCB2 |  |  |  | BLK4LT1ACCB2 | 534 | 0.8% | ACCB |  | B-4 IDT tripped due to 2 Nos. of 500Amp MCCb failure after generation | 17:04 | 17:04 | 8:20 | 22:39 | 0 | -8.7333 | 5.5833 | 5.5833 | After checking the all paramerters & meggaring the MCCB & found MCCB Healthy same is restore | closed | 0.044667 | 0 | 0
2059 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:24 | 17:50 | 12.4333 | BLK4 | LT1 | ACCB5 |  |  |  | BLK4LT1ACCB5 | 567.375 | 0.85% | ACCB |  | B-4 IDT tripped due to 2 Nos. of 500Amp MCCb failure after generation | 17:04 | 17:04 | 8:20 | 22:39 | 0 | -8.7333 | 5.5833 | 5.5833 | MCCB meggaring value is not good | closed | 0.047458 | 0 | 0
2060 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:24 | 17:50 | 12.4333 | BLK4 | LT1 | ACCB6 |  |  |  | BLK4LT1ACCB6 | 567.375 | 0.85% | ACCB |  | B-4 IDT tripped due to 2 Nos. of 500Amp MCCb failure after generation | 17:04 | 17:04 | 8:20 | 11:30 | 0 | -8.7333 | -5.5667 | -5.5667 | After checking the all paramerters & meggaring the MCCB & found MCCB Healthy same is restore | closed | -0.047317 | 0 | 0
2061 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV1 |  |  | BLK4INV1 | 300.375 | 0.45% | Inverter |  | Due to Block-4 Inverter failure this impact 500 Amp MCCB of this inverter also failure. | 5:45 | 5:45 | 18:45 | 20:00 | 0 | 13 | 14.25 | 14.25 | It will be restored after rectification of MCCB or Replacment of MCCB. | closed | 0.064125 | 2.4 | 547.9868
2062 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | Due to Block-4 Inverter failure this impact 500 Amp MCCB of this inverter also failure. | 5:45 | 5:45 | 18:45 | 20:00 | 0 | 13 | 14.25 | 14.25 | It will be restored after rectification of MCCB or Replacment of MCCB. | closed | 0.057 | 2.4 | 487.0994
2063 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV11 |  |  | BLK4INV11 | 300.375 | 0.45% | Inverter |  | Block-4 Inverter No-11 IGBT Failure , it was restored after MCCB replacment work. | 5:45 | 5:45 |  |  | 0 | -5.75 | -5.75 | -5.75 | Block-4 Inverter No-11 IGBT Failure , it was restored after MCCB replacment work. | closed | -0.025875 | 2.4 | 547.9868
2064 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV12 |  |  | BLK4INV12 | 267 | 0.4% | Inverter |  | Due to Block-4 Inverter failure this impact 500 Amp MCCB of this inverter also failure. | 5:45 | 5:45 |  |  | 0 | -5.75 | -5.75 | -5.75 | It will be restored after rectification of MCCB or Replacment of MCCB. | closed | -0.023 | 2.4 | 487.0994
2065 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 267 | 0.4% | string |  | As per observation we observed that String no -13 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 5:45 | 7:35 | 10:30 | 10:45 | 1.8333 | 4.75 | 5 | 5 | During VOC we got string no 13 DC cable shorted so isolated the string & charge | closed | 0.02 | 0.64 | 129.8932
2066 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 300.375 | 0.45% | string |  | As per observation we observed that String no -13 &14 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 5:45 | 7:35 | 10:50 | 11:10 | 1.8333 | 5.0833 | 5.4167 | 5.4167 | During VOC we got string no 13 & 14 DC cable shorted so isolated the string & charge | closed | 0.024375 | 0.827 | 188.8271
2067 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 278.125 | 0.4167% | string |  | As per observation we observed that String no -9 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 5:45 | 7:35 | 11:45 | 12:06 | 1.8333 | 6 | 6.35 | 6.35 | During VOC we got string np 9 faulty so isolated this string & charge | closed | 0.026458 | 1.26 | 266.3825
2068 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK1 |  |  | INV18 |  |  | BLK1INV18 | 267 | 0.4% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 8:55 | 9:19 | 1.8333 | 3.1667 | 3.5667 | 3.5667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.014267 | 0.236 | 47.8981
2069 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 300.375 | 0.45% | string |  | As per observation we observed that String no -13 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 5:45 | 7:35 | 11:15 | 11:42 | 1.8333 | 5.5 | 5.95 | 5.95 | As per observation we observed that String no -13 was grounded due to this inverter was in breakdown on exxcusive leakage current. | closed | 0.026775 | 1.03 | 235.1777
2070 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 222.5 | 0.3333% | string |  | As per observation we observed that String no -5 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 5:45 | 7:35 | 11:30 | 11:56 | 1.8333 | 5.75 | 6.1833 | 6.1833 | As per observation we observed that String no -5 was grounded due to this inverter was in breakdown on exxcusive leakage current. | closed | 0.020611 | 1.51 | 255.3889
2071 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK2 |  |  | INV9 |  |  | BLK2INV9 | 267 | 0.4% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:00 | 9:24 | 1.8333 | 3.25 | 3.65 | 3.65 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.0146 | 0.267 | 54.1898
2072 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK2 |  |  | INV15 |  |  | BLK2INV15 | 267 | 0.4% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 8:40 | 9:10 | 1.8333 | 2.9167 | 3.4167 | 3.4167 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.013667 | 0.203 | 41.2005
2073 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK2 |  |  | INV18 |  |  | BLK2INV18 | 278.125 | 0.4167% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 10:35 | 11:04 | 1.8333 | 4.8333 | 5.3167 | 5.3167 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.022153 | 0.781 | 165.1148
2074 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 239.25 | 0.3584% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 8:50 | 9:16 | 1.8333 | 3.0833 | 3.5167 | 3.5167 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.012605 | 0.222 | 40.3738
2075 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK3 |  |  | INV18 |  |  | BLK3INV18 | 267 | 0.4% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:05 | 9:32 | 1.8333 | 3.3333 | 3.7833 | 3.7833 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.015133 | 0.314 | 63.7288
2076 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK5 |  |  | INV4 |  |  | BLK5INV4 | 300.375 | 0.45% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 11:15 | 11:40 | 1.8333 | 5.5 | 5.9167 | 5.9167 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.026625 | 1.021 | 233.1227
2077 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK5 |  |  | INV26 |  |  | BLK5INV26 | 289.25 | 0.4333% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:20 | 9:43 | 1.8333 | 3.5833 | 3.9667 | 3.9667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.017189 | 0.361 | 79.3735
2078 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 297 | 0.4449% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 8:35 | 9:00 | 1.8333 | 2.8333 | 3.25 | 3.25 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.014461 | 0.189 | 42.6691
2079 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV9 |  |  | BLK6INV9 | 275 | 0.412% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:05 | 9:25 | 1.8333 | 3.3333 | 3.6667 | 3.6667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.015106 | 0.27 | 56.4406
2080 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 264 | 0.3955% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:30 | 9:55 | 1.8333 | 3.75 | 4.1667 | 4.1667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.016479 | 0.414 | 83.0805
2081 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV11 |  |  | BLK6INV11 | 297 | 0.4449% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 10:00 | 10:30 | 1.8333 | 4.25 | 4.75 | 4.75 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.021135 | 0.527 | 118.9768
2082 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV15 |  |  | BLK6INV15 | 275 | 0.412% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 10:40 | 11:02 | 1.8333 | 4.9167 | 5.2833 | 5.2833 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.021767 | 0.766 | 160.124
2083 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV16 |  |  | BLK6INV16 | 297 | 0.4449% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 10:30 | 10:50 | 1.8333 | 4.75 | 5.0833 | 5.0833 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.022618 | 0.663 | 149.6804
2084 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV23 |  |  | BLK6INV23 | 264 | 0.3955% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:30 | 9:49 | 1.8333 | 3.75 | 4.0667 | 4.0667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.016084 | 0.388 | 77.8629
2085 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV24 |  |  | BLK6INV24 | 286 | 0.4285% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:45 | 10:16 | 1.8333 | 4 | 4.5167 | 4.5167 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.019352 | 0.475 | 103.2654
2086 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV31 |  |  | BLK6INV31 | 275 | 0.412% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:30 | 9:54 | 1.8333 | 3.75 | 4.15 | 4.15 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.017097 | 0.411 | 85.9151
2087 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV32 |  |  | BLK6INV32 | 275 | 0.412% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:34 | 10:03 | 1.8333 | 3.8167 | 4.3 | 4.3 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.017715 | 0.432 | 90.3049
2088 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 264 | 0.3955% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 10:00 | 10:23 | 1.8333 | 4.25 | 4.6333 | 4.6333 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.018325 | 0.499 | 100.1381
2089 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK7 |  |  | INV26 |  |  | BLK7INV26 | 300.375 | 0.45% | string |  | As per observation we observed that String no -1,10 & 12 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 5:45 | 7:35 | 10:45 | 11:10 | 1.8333 | 5 | 5.4167 | 5.4167 | As per observation we observed that String no -1,10 & 12 was grounded due to this inverter was in breakdown on exxcusive leakage current. | closed | 0.024375 | 0.826 | 188.5988
2090 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:45 | 7:35 |  | 18:42 | 1.8333 | -5.75 | 12.95 | 12.95 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0518 | 2.4 | 21.8921
2091 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:45 | 7:35 |  | 18:42 | 1.8333 | -5.75 | 12.95 | 12.95 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.058275 | 2.4 | 40.5916
2092 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:45 | 7:35 |  | 18:42 | 1.8333 | -5.75 | 12.95 | 12.95 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.058275 | 2.4 | 21.8921
2093 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 22.25 | 0.4167% | string |  | 1 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | 5:45 | 7:35 | 11:50 | 12:10 | 1.8333 | 6.0833 | 6.4167 | 6.4167 | 1 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | closed | 0.026736 | 1.303 | 22.0379
2094 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 22.25 | 0.3333% | string |  | 1 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | 5:45 | 7:35 | 11:50 | 12:10 | 1.8333 | 6.0833 | 6.4167 | 6.4167 | 1 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | closed | 0.021389 | 1.303 | 22.0379
2095 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK7 |  |  | INV26 |  |  | BLK7INV26 | 66.75 | 0.45% | string |  | 3 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | 5:45 | 7:35 | 11:05 | 11:30 | 1.8333 | 5.3333 | 5.75 | 5.75 | 3 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | closed | 0.025875 | 0.951 | 48.2533
2096 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK3 |  |  | INV16 |  |  | BLK3INV16 | 267 | 0.4% | Inverter |  | During morning after few time of plant start Block-3 inverter-16 Shut down on fault of ecxcessive leakage current, When Done VOC we got that String NO. 8 yconnector & fuse was failure so replace it with new one, restore | 7:10 | 7:15 | 9:02 | 9:27 | 0.083333 | 1.8667 | 2.2833 | 2.2833 | During morning after few time of plant start Block-3 inverter-16 Shut down on fault of ecxcessive leakage current, When Done VOC we got that String NO. 8 yconnector & fuse was failure so replace it with new one, restore | closed | 0.0091333 | 0.585 | 118.7305
2097 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK4 |  |  | INV12 |  |  | BLK4INV12 | 267 | 0.4% | Inverter |  | During morning after few time of plant start Block-4 inverter-12 shut down on fault of ecxcessive leakage current, When Done VOC we got that String NO. 13 MC4 connector & fuse was failure so replace it with new one, restore | 5:23 | 5:25 | 9:00 | 9:23 | 0.033333 | 3.6167 | 4 | 4 | During morning after few time of plant start Block-4 inverter-12 shut down on fault of ecxcessive leakage current, When Done VOC we got that String NO. 13 MC4 connector & fuse was failure so replace it with new one, restore | closed | 0.016 | 0.911 | 184.8948
2098 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK6 |  |  | INV15 |  |  | BLK6INV15 | 275 | 0.412% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 7:00 | 7:10 | 7:35 | 8:06 | 0.16667 | 0.58333 | 1.1 | 1.1 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0045318 | 0.341 | 71.2824
2099 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK4 |  |  | INV11 |  |  | BLK4INV11 | 300.375 | 0.45% | Inverter |  | Restoretion of Inverter & 250 Amp MCCB, after verifying the all parameter connect the same | 5:23 | 5:25 | 8:45 | 9:13 | 0.033333 | 3.3667 | 3.8333 | 3.8333 | Restoretion of Inverter & 250 Amp MCCB, after verifying the all parameter connect the same | closed | 0.01725 | 0.834 | 190.4254
2100 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:05 | 12:06 | 12:07 | 12:10 | 0.016667 | 0.033333 | 0.083333 | 0.083333 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011167 | 0.102 | 693.5077
2101 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:02 | 12:03 | 12:06 | 12:07 | 0.016667 | 0.066667 | 0.083333 | 0.083333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.010417 | 0.104 | 659.6137
2102 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:15 | 12:16 | 12:19 | 12:20 | 0.016667 | 0.066667 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011067 | 0.112 | 754.7091
2103 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:45 | 5:45 |  | 18:29 | 0 | -5.75 | 12.7333 | 12.7333 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.050933 | 5.19 | 47.3417
2104 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:45 | 5:45 |  | 18:29 | 0 | -5.75 | 12.7333 | 12.7333 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0573 | 5.19 | 87.7794
2105 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:45 | 5:45 |  | 18:29 | 0 | -5.75 | 12.7333 | 12.7333 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0573 | 5.19 | 47.3417
2106 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK2 |  |  | INV15 |  |  | BLK2INV15 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 6:59 | 7:05 | 7:20 | 8:15 | 0.1 | 0.35 | 1.2667 | 1.2667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.0050667 | 0.42 | 85.2424
2107 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK5 |  |  | INV20 |  |  | BLK5INV20 | 22.25 | 0.4% | string |  | During morining string checking we got that 1 string MC4 connector open, same restore | 4:59 | 9:00 | 9:50 | 10:10 | 4.0167 | 4.85 | 5.1833 | 5.1833 | During morining string checking we got that 1 string MC4 connector open, same restore | closed | 0.020733 | 1.135 | 19.1965
2108 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK6 |  |  | INV32 |  |  | BLK6INV32 | 22.25 | 0.412% | string |  | During morining string checking we got that 1 string MC4 connector open, same restore | 4:59 | 9:00 | 10:00 | 10:30 | 4.0167 | 5.0167 | 5.5167 | 5.5167 | During morining string checking we got that 1 string MC4 connector open, same restore | closed | 0.022728 | 1.219 | 20.6172
2109 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK4 |  |  | INV17 |  |  | BLK4INV17 | 22.25 | 0.4333% | string |  | Morning string checking found that String no 9 , Y connector, fuse & MC4 connector melted | 4:59 | 9:00 | 10:25 | 10:45 | 4.0167 | 5.4333 | 5.7667 | 5.7667 | Morning string checking found that String no 9 , Y connector, fuse & MC4 connector melted, so replace it with new one, restored | closed | 0.024989 | 1.663 | 28.1266
2110 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK4 |  |  | INV12 |  |  | BLK4INV12 | 12 | 0.4% | string |  | Morning string checking found that String no 13 MC4 connector melted | 4:59 | 9:00 | 10:33 | 10:50 | 4.0167 | 5.5667 | 5.85 | 5.85 | Morning string checking found that String no 13 MC4 connector melted, same is replace it with new one, restored | closed | 0.0234 | 1.717 | 15.662
2111 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 4:59 |  |  | 18:12 | -4.9833 | -4.9833 | 13.2167 | 13.2167 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.052867 | 5.3 | 48.3451
2112 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 4:59 |  |  | 18:12 | -4.9833 | -4.9833 | 13.2167 | 13.2167 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.059475 | 5.3 | 89.6398
2113 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 4:59 |  |  | 18:12 | -4.9833 | -4.9833 | 13.2167 | 13.2167 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.059475 | 5.3 | 48.3451
2114 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 278.125 | 0.4167% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 7:30 | 8:15 | 1.4167 | 2 | 2.75 | 2.75 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.011458 | 0.222 | 46.9341
2115 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK2 |  |  | INV15 |  |  | BLK2INV15 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 8:00 | 8:30 | 1.4167 | 2.5 | 3 | 3 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.012 | 0.293 | 59.4667
2116 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK2 |  |  | INV18 |  |  | BLK2INV18 | 278.125 | 0.4167% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 8:15 | 8:45 | 1.4167 | 2.75 | 3.25 | 3.25 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.013542 | 0.37 | 78.2234
2117 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | During morning after few time of plant start Block-4 inverter-2 shut down on fault of ecxcessive leakage current & fault 47, When Done VOC we got that String NO. 12 MC4 connector & fuse was failure so replace it with new one & also share Log file of Inverter to OEm after got permission from OEM reset it, restore | 5:30 | 6:55 | 10:30 | 11:00 | 1.4167 | 5 | 5.5 | 5.5 | During morning after few time of plant start Block-4 inverter-2 shut down on fault of ecxcessive leakage current & fault 47, When Done VOC we got that String NO. 12 MC4 connector & fuse was failure so replace it with new one & also share Log file of Inverter to OEm after got permission from OEM reset it, restore | closed | 0.022 | 1.656 | 336.0986
2118 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK4 |  |  | INV22 |  |  | BLK4INV22 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 8:05 | 8:25 | 1.4167 | 2.5833 | 2.9167 | 2.9167 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.011667 | 0.269 | 54.5957
2119 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK6 |  |  | INV5 |  |  | BLK6INV5 | 264 | 0.3955% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 7:15 | 7:45 | 1.4167 | 1.75 | 2.25 | 2.25 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0088989 | 0.132 | 26.4894
2120 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 297 | 0.4449% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 8:45 | 9:15 | 1.4167 | 3.25 | 3.75 | 3.75 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.016685 | 0.564 | 127.33
2121 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 264 | 0.3955% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 9:00 | 9:25 | 1.4167 | 3.5 | 3.9167 | 3.9167 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.015491 | 0.639 | 128.233
2122 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK6 |  |  | INV31 |  |  | BLK6INV31 | 275 | 0.412% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 7:40 | 8:10 | 1.4167 | 2.1667 | 2.6667 | 2.6667 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.010986 | 0.203 | 42.435
2123 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK7 |  |  | INV12 |  |  | BLK7INV12 | 270.6 | 0.4054% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 8:10 | 8:35 | 1.4167 | 2.6667 | 3.0833 | 3.0833 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0125 | 0.319 | 65.6166
2124 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK7 |  |  | INV17 |  |  | BLK7INV17 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 8:50 | 9:15 | 1.4167 | 3.3333 | 3.75 | 3.75 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.015 | 0.563 | 114.2654
2125 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK5 |  |  | INV11 |  |  | BLK5INV11 | 286 | 0.4285% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 11:00 | 11:30 | 1.4167 | 5.5 | 6 | 6 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.025708 | 1.881 | 408.9309
2126 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:30 |  |  | 18:30 | -5.5 | -5.5 | 13 | 13 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.052 | 4.58 | 41.7774
2127 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.3 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:30 |  |  | 18:30 | -5.5 | -5.5 | 13 | 13 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0585 | 4.58 | 77.6364
2128 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:30 |  |  | 18:30 | -5.5 | -5.5 | 13 | 13 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0585 | 4.58 | 41.7774
2129 | 2025-06-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:11 | 18:31 | 13.3333 | Blk4 |  |  | INV13 |  |  | Blk4INV13 | 300.375 | 0.45% | Inverter |  | Block-4 inverter 13 failure on fault of 1616 & 21 in morning, after sharing the log file to OEM, inverter has been replaced with spare one | 5:11 | 6:00 | 12:00 | 12:49 | 0.81667 | 6.8167 | 7.6333 | 7.6333 | Block-4 inverter 13 failure on fault of 1616 & 21 in morning, after sharing the log file to OEM, inverter has been replaced with spare one | closed | 0.03435 | 3.4 | 776.3146
2130 | 2025-06-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:11 | 18:31 | 13.3333 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:11 |  |  | 18:31 | -5.1833 | -5.1833 | 13.3333 | 13.3333 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.053333 | 6.46 | 58.9263
2131 | 2025-06-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:11 | 18:31 | 13.3333 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:11 |  |  | 18:31 | -5.1833 | -5.1833 | 13.3333 | 13.3333 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.06 | 6.46 | 109.2591
2132 | 2025-06-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:11 | 18:50 | 13.65 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:11 |  |  | 18:50 | -5.1833 | -5.1833 | 13.65 | 13.65 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0546 | 6.18 | 56.3722
2133 | 2025-06-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:11 | 18:50 | 13.65 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:11 |  |  | 18:50 | -5.1833 | -5.1833 | 13.65 | 13.65 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.061425 | 6.18 | 104.5234
2134 | 2025-06-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:40 | 13.4333 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:14 |  |  | 18:40 | -5.2333 | -5.2333 | 13.4333 | 13.4333 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.053733 | 6.3 | 57.4668
2135 | 2025-06-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:40 | 13.4333 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:14 |  |  | 18:40 | -5.2333 | -5.2333 | 13.4333 | 13.4333 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.06045 | 6.3 | 106.553
2136 | 2025-06-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:40 | 13.4333 | BLK4 |  |  | INV11 |  |  | BLK4INV11 | 300.375 | 0.45% | Inverter |  | As per obsservation we found that Block-4 Inverter11 running with derating generation, after Discussion with Oem & sharing Log file to OEM, they instructed to change control card, After changing the Control card now its under observation | 16:15 | 16:15 | 16:30 | 18:05 | 0 | 0.25 | 1.8333 | 1.8333 | As per obsservation we found that Block-4 Inverter11 running with derating generation, after Discussion with Oem & sharing Log file to OEM, they instructed to change control card, After changing the Control card now its under observation | closed | 0.00825 | 0.513 | 117.1322
2137 | 2025-06-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 |  |  | 0 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:14 |  |  | 18:40 | -5.2333 | -5.2333 | 13.4333 | 13.4333 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.053733 | 6.3 | 57.4668
2138 | 2025-06-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 |  |  | 0 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:14 |  |  | 18:40 | -5.2333 | -5.2333 | 13.4333 | 13.4333 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.06045 | 6.3 | 58.664
2139 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:48 | 18:41 | 12.8833 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | Inverter |  | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | 5:48 | 7:00 | 9:30 | 18:41 | 1.2 | 3.7 | 12.8833 | 12.8833 | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | closed | 0.036739 | 5.64 | 816.0693
2140 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:48 | 18:41 | 12.8833 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | Inverter shutdown in morining on fault of excessive leakage current, after removing the faulty string inverter fault reset, restore | 5:48 | 7:00 | 9:10 | 9:35 | 1.2 | 3.3667 | 3.7833 | 3.7833 | Inverter shutdown in morining on fault of excessive leakage current, after removing the faulty string inverter fault reset, restore | closed | 0.015133 | 1.025 | 208.032
2141 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:48 | 18:41 | 12.8833 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | 17:45 | 17:45 | 17:50 | 18:41 | 0 | 0.083333 | 0.93333 | 0.93333 | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | closed | 0.0037333 | 0.0961 | 19.5043
2142 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:48 | 18:41 | 12.8833 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:48 |  |  | 18:41 | -5.8 | -5.8 | 12.8833 | 12.8833 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.051533 | 5.64 | 51.4464
2143 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:48 | 18:41 | 12.8833 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:48 |  |  | 18:41 | -5.8 | -5.8 | 12.8833 | 12.8833 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.057975 | 5.64 | 95.3903
2144 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:48 | 18:41 | 12.8833 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:37 | 12:37 | 12:41 | 12:42 | 0 | 0.066667 | 0.083333 | 0.083333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.010417 | 0.097 | 615.2166
2145 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:26 |  |  | 18:29 | -5.4333 | -5.4333 | 13.05 | 13.05 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0522 | 4.65 | 42.416
2146 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:26 |  |  | 18:29 | -5.4333 | -5.4333 | 13.05 | 13.05 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.058725 | 4.65 | 78.6462
2147 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 300.375 | 0.45% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:26 | 6:10 | 7:15 | 7:35 | 0.73333 | 1.8167 | 2.15 | 2.15 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.009675 | 0.189 | 43.154
2148 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK5 |  |  | INV14 |  |  | BLK5INV14 | 278.125 | 0.4167% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:26 | 6:10 | 7:25 | 7:45 | 0.73333 | 1.9833 | 2.3167 | 2.3167 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0096528 | 0.232 | 49.0482
2149 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK6 |  |  | INV32 |  |  | BLK6INV32 | 275 | 0.412% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:26 | 6:10 | 7:40 | 8:10 | 0.73333 | 2.2333 | 2.7333 | 2.7333 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.011261 | 0.351 | 73.3728
2150 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK6 |  |  | INV16 |  |  | BLK6INV16 | 297 | 0.4449% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:26 | 6:10 | 8:10 | 8:30 | 0.73333 | 2.7333 | 3.0667 | 3.0667 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.013645 | 0.489 | 110.3978
2151 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK2 |  |  | INV7 |  |  | BLK2INV7 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:26 | 6:10 | 8:25 | 8:45 | 0.73333 | 2.9833 | 3.3167 | 3.3167 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.013267 | 0.455 | 92.3459
2152 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK3 |  |  | INV30 |  |  | BLK3INV30 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:26 | 6:10 | 6:55 | 7:20 | 0.73333 | 1.4833 | 1.9 | 1.9 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0076 | 0.132 | 26.7905
2153 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK7 |  |  | INV19 |  |  | BLK7INV19 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:26 | 6:10 | 8:45 | 9:10 | 0.73333 | 3.3167 | 3.7333 | 3.7333 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.014933 | 0.589 | 119.5423
2154 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | 5:26 |  |  | 18:29 | -5.4333 | -5.4333 | 13.05 | 13.05 | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | closed | 0.0522 | 4.65 | 943.755
2155 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | Inverter |  | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | 5:26 |  |  | 18:29 | -5.4333 | -5.4333 | 13.05 | 13.05 | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | closed | 0.037214 | 4.65 | 672.8231
2156 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | 5:18 |  |  | 18:29 | -5.3 | -5.3 | 13.1833 | 13.1833 | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | closed | 0.052733 | 3.89 | 789.5069
2157 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | Inverter |  | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | 5:18 |  |  | 18:29 | -5.3 | -5.3 | 13.1833 | 13.1833 | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | closed | 0.037595 | 3.89 | 562.8563
2158 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | String |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:18 |  |  | 18:29 | -5.3 | -5.3 | 13.1833 | 13.1833 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.052733 | 3.89 | 35.4835
2159 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | String |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:18 |  |  | 18:29 | -5.3 | -5.3 | 13.1833 | 13.1833 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.059325 | 3.89 | 65.7922
2160 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 22.25 | 0.45% | String |  | During String current measurement activity we have observed that String-1 MC4 connector was melted so replace it with spare one. | 6:40 | 7:00 | 7:45 | 8:15 | 0.33333 | 1.0833 | 1.5833 | 1.5833 | During String current measurement activity we have observed that String-1 MC4 connector was melted so replace it with spare one. | closed | 0.007125 | 0.207 | 3.501
2161 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | String |  | During String current measurement activity we have observed that String-10 MC4 connector was melted so replace it with spare one. | 6:40 | 7:00 | 8:15 | 8:40 | 0.33333 | 1.5833 | 2 | 2 | During String current measurement activity we have observed that String-10 MC4 connector was melted so replace it with spare one. | closed | 0.0079101 | 0.379 | 6.3381
2162 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK6 |  |  | INV16 |  |  | BLK6INV16 | 22 | 0.4449% | String |  | During String current measurement activity we have observed that String-5 MC4 connector was melted so replace it with spare one. | 6:40 | 7:00 | 8:40 | 9:00 | 0.33333 | 2 | 2.3333 | 2.3333 | During String current measurement activity we have observed that String-5 MC4 connector was melted so replace it with spare one. | closed | 0.010382 | 0.547 | 9.1476
2163 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK2 |  |  | INV12 |  |  | BLK2INV12 | 22.25 | 0.4% | String |  | During String current measurement activity we have observed that String No.-6 MC4 connector was melted so replace it with spare one. | 6:40 | 7:00 | 9:10 | 9:30 | 0.33333 | 2.5 | 2.8333 | 2.8333 | During String current measurement activity we have observed that String No.-6 MC4 connector was melted so replace it with spare one. | closed | 0.011333 | 0.788 | 13.3276
2164 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | String |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:20 |  |  | 18:23 | -5.3333 | -5.3333 | 13.05 | 13.05 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0522 | 3.09 | 28.1861
2165 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | String |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:20 |  |  | 18:23 | -5.3333 | -5.3333 | 13.05 | 13.05 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.058725 | 3.09 | 28.1861
2166 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | inverter |  | Inverter IGBT was failure so replace it with spare one | 5:20 | 3:55 | 4:05 | 4:46 | -1.4167 | -1.25 | -0.56667 | -0.56667 | Inverter IGBT was failure so replace it with spare one | closed | -0.0022667 | 2.79 | 566.253
2167 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | inverter |  | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | 5:20 |  |  | 18:23 | -5.3333 | -5.3333 | 13.05 | 13.05 | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | closed | 0.037214 | 3.09 | 447.1018
2168 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | String |  | String no. 13 load shifted to string no. 14 & string no. 6 splited to 2 half string, now restore | 5:20 | 7:00 | 7:10 | 7:25 | 1.6667 | 1.8333 | 2.0833 | 2.0833 | String no. 13 load shifted to string no. 14 & string no. 6 splited to 2 half string, now restore | closed | 0.009375 | 0.075 | 0.68413
2169 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK6 |  |  | INV31 |  |  | BLK6INV31 | 275 | 0.412% | String |  | During string monitoring found string no. 1 shows ground fault, rectified now restore | 5:20 | 7:00 | 7:35 | 7:55 | 1.6667 | 2.25 | 2.5833 | 2.5833 | During string monitoring found string no. 1 shows ground fault, rectified now restore | closed | 0.010643 | 0.121 | 25.2937
2170 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 44 | 0.3955% | String |  | During string monitoring found string no. 3& 6 in ground fault now rectified & restore | 5:20 | 7:00 | 8:10 | 8:30 | 1.6667 | 2.8333 | 3.1667 | 3.1667 | During string monitoring found string no. 3& 6 in ground fault now rectified & restore | closed | 0.012524 | 0.178 | 5.9534
2171 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK2 |  |  | INV15 |  |  | BLK2INV15 | 22 | 0.4% | String |  | During string monitoring found string no. 12 in ground fault now rectified & restore | 5:20 | 7:00 | 8:40 | 8:55 | 1.6667 | 3.3333 | 3.5833 | 3.5833 | During string monitoring found string no. 12 in ground fault now rectified & restore | closed | 0.014333 | 0.221 | 3.6958
2172 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK2 |  |  | INV17 |  |  | BLK2INV17 | 22 | 0.4% | String |  | during string monitoring found string no. 7 MC4 connector open, now restore | 5:20 | 7:00 | 9:10 | 9:20 | 1.6667 | 3.8333 | 4 | 4 | during string monitoring found string no. 7 MC4 connector open, now restore | closed | 0.016 | 0.3 | 5.0169
2173 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK2 |  |  | INV18 |  |  | BLK2INV18 | 22 | 0.4167% | String |  | during string monitoring found string no. 3 MC4 connector open, now restore | 5:20 | 7:00 | 9:25 | 9:35 | 1.6667 | 4.0833 | 4.25 | 4.25 | during string monitoring found string no. 3 MC4 connector open, now restore | closed | 0.017708 | 0.342 | 5.7193
2174 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK3 |  |  | INV30 |  |  | BLK3INV30 | 22.25 | 0.4% | String |  | during string monitoring found string no. 1 MC4 connector melted so replace it with spare one, now restore | 5:20 | 7:00 | 10:00 | 10:25 | 1.6667 | 4.6667 | 5.0833 | 5.0833 | during string monitoring found string no. 1 MC4 connector melted so replace it with spare one, now restore | closed | 0.020333 | 0.39 | 6.5961
2175 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK5 |  |  | INV3 |  |  | BLK5INV3 | 44.5 | 0.4% | String |  | during string monitoring found string no. 9on ground fault while string no.12 Fuse & y connector melted so replace it with spare one, now restore | 5:20 | 7:00 | 10:40 | 11:00 | 1.6667 | 5.3333 | 5.6667 | 5.6667 | during string monitoring found string no. 9on ground fault while string no.12 Fuse & y connector melted so replace it with spare one, now restore | closed | 0.022667 | 0.514 | 17.3867
2176 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:34 | 18:43 | 13.15 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 264 | 0.3955% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 8:10 | 8:10 | 11:00 | 11:30 | 0 | 2.8333 | 3.3333 | 3.3333 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.013184 | 0.975 | 195.6607
2177 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:34 | 18:43 | 13.15 | BLK6 |  |  | INV32 |  |  | BLK6INV32 | 275 | 0.412% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:34 | 5:34 | 9:00 | 9:30 | 0 | 3.4333 | 3.9333 | 3.9333 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.016205 | 0.751 | 156.9884
2178 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:34 | 18:43 | 13.15 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 297 | 0.4449% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:34 | 5:34 | 8:55 | 9:15 | 0 | 3.35 | 3.6833 | 3.6833 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.016389 | 0.699 | 157.8079
2179 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:34 | 18:43 | 13.15 | BLK6 |  |  | INV18 |  |  | BLK6INV18 | 297 | 0.4449% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:34 | 5:34 | 9:40 | 10:02 | 0 | 4.1 | 4.4667 | 4.4667 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.019874 | 0.834 | 188.2858
2180 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:34 | 18:43 | 13.15 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:34 | 5:34 | 10:00 | 10:27 | 0 | 4.4333 | 4.8833 | 4.8833 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.019533 | 0.927 | 188.1421
2181 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:34 | 18:43 | 13.15 | BLK2 |  |  | INV25 |  |  | BLK2INV25 | 300.375 | 0.45% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:34 | 5:34 | 8:40 | 8:55 | 0 | 3.1 | 3.35 | 3.35 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.015075 | 0.569 | 129.9185
2182 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:34 | 18:43 | 13.15 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 278.125 | 0.4167% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:34 | 5:34 | 8:00 | 8:27 | 0 | 2.4333 | 2.8833 | 2.8833 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.012014 | 0.398 | 84.143
2183 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:34 | 18:43 | 13.15 | BLK5 |  |  | INV22 |  |  | BLK5INV22 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:34 | 5:34 | 8:40 | 9:09 | 0 | 3.1 | 3.5833 | 3.5833 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.014333 | 0.66 | 133.9523
2184 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:34 | 18:43 | 13.15 | BLK7 |  |  | INV21 |  |  | BLK7INV21 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 10:30 | 10:35 | 10:40 | 11:04 | 0.083333 | 0.16667 | 0.56667 | 0.56667 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0022667 | 0.241 | 48.9129
2185 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:34 | 18:43 | 13.15 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | Inverter |  | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | 10:55 | 10:55 | 11:00 | 11:31 | 0 | 0.083333 | 0.6 | 0.6 | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | closed | 0.001711 | 2.41 | 348.7105
2186 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:34 | 18:43 | 13.15 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:34 | 5:34 |  | 18:43 | 0 | -5.5667 | 13.15 | 13.15 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0526 | 2.41 | 21.9833
2187 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:34 | 18:43 | 13.15 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:34 | 5:34 |  | 18:43 | 0 | -5.5667 | 13.15 | 13.15 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.059175 | 2.41 | 21.9833
2188 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK2 |  |  | INV26 |  |  | BLK2INV26 | 300.375 | 0.45% | inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:14 | 6:00 | 7:45 | 8:20 | 0.76667 | 2.5167 | 3.1 | 3.1 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.01395 | 0.345 | 78.7731
2189 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK6 |  |  | INV17 |  |  | BLK6INV17 | 275 | 0.412% | inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:14 | 6:00 | 8:35 | 8:55 | 0.76667 | 3.35 | 3.6833 | 3.6833 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.015175 | 0.456 | 95.3219
2190 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 264 | 0.3955% | inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:14 | 6:00 | 7:00 | 7:30 | 0.76667 | 1.7667 | 2.2667 | 2.2667 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0089648 | 0.147 | 29.4996
2191 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 264 | 0.3955% | inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:14 | 6:00 | 7:40 | 8:03 | 0.76667 | 2.4333 | 2.8167 | 2.8167 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.01114 | 0.204 | 40.9382
2192 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | inverter |  | During morning after few time of plant start Block-2 inverter-31 shutdown on excessive lekage current, When we got Voc found that String NO. 3,6,9 MC4 connector & fuse was failure so replace it with new one , restore | 5:14 | 6:00 | 9:45 | 10:10 | 0.76667 | 4.5167 | 4.9333 | 4.9333 | During morning after few time of plant start Block-2 inverter-31 shutdown on excessive lekage current, When we got Voc found that String NO. 3,6,9 MC4 connector & fuse was failure so replace it with new one , restore | closed | 0.019733 | 0.698 | 141.6647
2193 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | inverter |  | During morning after few time of plant start Block-4 inverter-2 shutdown on excessive lekage current, When we got Voc found that String NO. 2,5 MC4 connector & fuse was failure so replace it with new one , restore | 5:14 | 6:00 | 10:15 | 10:40 | 0.76667 | 5.0167 | 5.4333 | 5.4333 | During morning after few time of plant start Block-4 inverter-2 shutdown on excessive lekage current, When we got Voc found that String NO. 2,5 MC4 connector & fuse was failure so replace it with new one , restore | closed | 0.021733 | 0.891 | 180.8356
2194 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK4 |  |  | INV11 |  |  | BLK4INV11 | 300.375 | 0.45% | inverter |  | During string monitoring we found that Block-4 Inverter-11 String-6 mc4 connector open, connected the same, restore | 5:14 | 6:00 | 10:50 | 11:10 | 0.76667 | 5.6 | 5.9333 | 5.9333 | During string monitoring we found that Block-4 Inverter-11 String-6 mc4 connector open, connected the same, restore | closed | 0.0267 | 0.563 | 128.5486
2195 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK3 |  |  | INV29 |  |  | BLK3INV29 | 289.25 | 0.4333% | inverter |  | During morning after few time of plant start Block-3 inverter-29 , When we got Voc found that String NO. 1,5 MC4 connector was failure so replace it with new one , restore | 5:14 | 6:00 | 8:55 | 9:20 | 0.76667 | 3.6833 | 4.1 | 4.1 | During morning after few time of plant start Block-3 inverter-29 , When we got Voc found that String NO. 1,5 MC4 connector was failure so replace it with new one , restore | closed | 0.017767 | 0.363 | 79.8133
2196 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | inverter |  | Inverter restoration work completed | 5:14 | 5:14 | 10:30 | 10:56 | 0 | 5.2667 | 5.7 | 5.7 | Inverter restoration work completed | closed | 0.016255 | 1.56 | 225.7213
2197 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:14 | 5:14 |  | 18:38 | 0 | -5.2333 | 13.4 | 13.4 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0536 | 4.07 | 37.1254
2198 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:14 | 5:14 |  | 18:38 | 0 | -5.2333 | 13.4 | 13.4 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0603 | 4.07 | 37.1254
2199 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:38 | 13.3667 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:16 |  |  | 18:38 | -5.2667 | -5.2667 | 13.3667 | 13.3667 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.053467 | 4.56 | 41.595
2200 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:38 | 13.3667 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:16 |  |  | 18:38 | -5.2667 | -5.2667 | 13.3667 | 13.3667 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.06015 | 4.56 | 41.595
2201 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:38 | 13.3667 | BLK5 |  |  | INV22 |  |  | BLK5INV22 | 267 | 0.4% | inverter |  | During morning after few time of plant start Block-5 inverter-22 shutdown on PV reverse current alarm , When we got Voc found that String NO. 7 Y connector was failure, so isolate it and charge the inverter | 5:16 | 6:00 | 6:30 | 7:01 | 0.73333 | 1.2333 | 1.75 | 1.75 | During morning after few time of plant start Block-5 inverter-22 shutdown on PV reverse current alarm , When we got Voc found that String NO. 7 Y connector was failure, so isolate it and charge the inverter | closed | 0.007 | 0.064 | 12.9893
2202 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:38 | 13.3667 | BLK5 |  |  | INV22 |  |  | BLK5INV22 | 22.25 | 0.4% | string |  | String NO. 7 Y connector was melted so replace it with spare one,restore | 5:16 | 6:00 | 9:30 | 10:00 | 0.73333 | 4.2333 | 4.7333 | 4.7333 | String NO. 7 Y connector was melted so replace it with spare one,restore | closed | 0.018933 | 0.909 | 15.3741
2203 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:38 | 13.3667 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 297 | 0.4449% | inverter |  | During morning after few time of plant start Block-6 inverter-6 shutdown on low system isulation alarm , When we got Voc found that String NO. 1,3,6,10,11 was failure, so isolate it and charge the inverter | 5:16 | 6:00 | 7:15 | 7:35 | 0.73333 | 1.9833 | 2.3167 | 2.3167 | During morning after few time of plant start Block-6 inverter-6 shutdown on low system isulation alarm , When we got Voc found that String NO. 1,3,6,10,11 was failure, so isolate it and charge the inverter | closed | 0.010308 | 0.13 | 29.3491
2204 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:38 | 13.3667 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 110 | 0.4449% | string |  | String NO. 1,,3,6,10,11 MC4 Fuse & Y connector was melted so replace it with spare one, restore | 5:16 | 6:00 | 9:00 | 9:30 | 0.73333 | 3.7333 | 4.2333 | 4.2333 | String NO. 1,,3,6,10,11 MC4 Fuse & Y connector was melted so replace it with spare one, restore | closed | 0.018836 | 0.713 | 59.618
2205 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:38 | 13.3667 | BLK6 |  |  | INV9 |  |  | BLK6INV9 | 275 | 0.412% | inverter |  | During morning after few time of plant start Block-6 inverter-9 shutdown on low system isulation alarm , When we got Voc found that String NO. 3,4,5,7 was failure, so isolate it and charge the inverter | 5:16 | 6:00 | 7:45 | 8:15 | 0.73333 | 2.4833 | 2.9833 | 2.9833 | During morning after few time of plant start Block-6 inverter-9 shutdown on low system isulation alarm , When we got Voc found that String NO. 3,4,5,7 was failure, so isolate it and charge the inverter | closed | 0.012291 | 0.278 | 58.1129
2206 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:38 | 13.3667 | BLK6 |  |  | INV9 |  |  | BLK6INV9 | 88 | 0.412% | string |  | String NO. 3,4,5,7 MC4 Fuse & Y connector was melted so replace it with spare one, restore | 5:16 | 6:00 | 9:45 | 10:15 | 0.73333 | 4.4833 | 4.9833 | 4.9833 | String NO. 3,4,5,7 MC4 Fuse & Y connector was melted so replace it with spare one, restore | closed | 0.020531 | 1.069 | 71.5081
2207 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:38 | 13.3667 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 264 | 0.3955% | inverter |  | During morning after few time of plant start Block-6 inverter-10 shutdown on low system isulation alarm , When we got Voc found that String NO. 1,3,4,7 was failure, so isolate it and charge the inverter | 5:16 | 6:00 | 8:25 | 8:45 | 0.73333 | 3.15 | 3.4833 | 3.4833 | During morning after few time of plant start Block-6 inverter-10 shutdown on low system isulation alarm , When we got Voc found that String NO. 1,3,4,7 was failure, so isolate it and charge the inverter | closed | 0.013777 | 0.476 | 95.5226
2208 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:38 | 13.3667 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 88 | 0.3955% | string |  | String NO. 1,3,4,7 MC4 Fuse & Y connector was melted so replace it with spare one, restore | 5:16 | 6:00 | 10:25 | 10:45 | 0.73333 | 5.15 | 5.4833 | 5.4833 | String NO. 1,3,4,7 MC4 Fuse & Y connector was melted so replace it with spare one, restore | closed | 0.021687 | 1.444 | 96.5928
2209 | 2025-07-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:36 | 13.35 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:16 |  |  |  | -5.2667 | -5.2667 | -5.2667 | -5.2667 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | -0.021067 | 4.21 | 38.4024
2210 | 2025-07-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:36 | 13.35 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:16 |  |  |  | -5.2667 | -5.2667 | -5.2667 | -5.2667 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | -0.0237 | 4.21 | 38.4024
2211 | 2025-07-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:36 | 13.35 | BLK5 |  |  | INV4 |  |  | BLK5INV4 | 22.25 | 0.45% | string |  | String no 3 MC4 was melted so replace it with spare one | 5:16 | 7:00 | 9:55 | 10:20 | 1.7333 | 4.65 | 5.0667 | 5.0667 | String no 3 MC4 was melted so replace it with spare one | closed | 0.0228 | 1.29 | 21.818
2212 | 2025-07-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:36 | 13.35 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 22.25 | 0.45% | string |  | String no 8 MC4 was melted so replace it with spare one | 5:16 | 7:00 | 8:45 | 9:15 | 1.7333 | 3.4833 | 3.9833 | 3.9833 | String no 8 MC4 was melted so replace it with spare one | closed | 0.017925 | 0.78 | 13.1923
2213 | 2025-07-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:36 | 13.35 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 22.25 | 0.45% | string |  | String no 8 Y connector, fuse & MC4 was melted so replace it with spare one | 5:16 | 7:00 | 9:20 | 9:45 | 1.7333 | 4.0667 | 4.4833 | 4.4833 | String no 8 Y connector, fuse & MC4 was melted so replace it with spare one | closed | 0.020175 | 1.014 | 17.15
2214 | 2025-07-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:36 | 13.35 | BLK2 |  |  | INV5 |  |  | BLK2INV5 | 22.25 | 0.4% | string |  | String no 7 MC4 was melted so replace it with spare one | 5:16 | 7:00 | 10:15 | 10:40 | 1.7333 | 4.9833 | 5.4 | 5.4 | String no 7 MC4 was melted so replace it with spare one | closed | 0.0216 | 1.588 | 26.8581
2215 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:29 |  |  | 18:42 | -5.4833 | -5.4833 | 13.2167 | 13.2167 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.052867 | 5.13 | 46.7944
2216 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:29 |  |  | 18:42 | -5.4833 | -5.4833 | 13.2167 | 13.2167 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.059475 | 5.13 | 46.7944
2217 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK2 |  |  | INV25 |  |  | BLK2INV25 | 66.75 | 0.45% | string |  | String no 1,4,7 MC4 was melted so replace it with spare one | 5:29 | 6:00 | 8:00 | 8:20 | 0.51667 | 2.5167 | 2.85 | 2.85 | String no 1,4,7 MC4 was melted so replace it with spare one | closed | 0.012825 | 0.346 | 17.5559
2218 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK3 |  |  | INV28 |  |  | BLK3INV28 | 22.25 | 0.4167% | string |  | String no 5 on ground fault, rectified | 5:29 | 6:00 | 8:25 | 8:35 | 0.51667 | 2.9333 | 3.1 | 3.1 | String no 5 on ground fault, rectified | closed | 0.012917 | 0.656 | 11.095
2219 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK1 |  |  | INV30 |  |  | BLK1INV30 | 22.25 | 0.45% | string |  | During string monitoring we found that string no 2 MC4 connector open so connect it & restore | 5:29 | 6:00 | 8:50 | 9:10 | 0.51667 | 3.35 | 3.6833 | 3.6833 | During string monitoring we found that string no 2 MC4 connector open so connect it & restore | closed | 0.016575 | 0.753 | 12.7356
2220 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK6 |  |  | INV31 |  |  | BLK6INV31 | 44 | 0.412% | string |  | String no.4 & 6 on ground fault due to MC4 Connector & Y-connector was melted, rectified | 5:29 | 6:00 | 9:20 | 9:40 | 0.51667 | 3.85 | 4.1833 | 4.1833 | String no.4 & 6 on ground fault due to MC4 Connector & Y-connector was melted, rectified | closed | 0.017235 | 1.221 | 40.8379
2221 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK6 |  |  | INV32 |  |  | BLK6INV32 | 110 | 0.412% | string |  | String no.1,6,10,11 & 12 on ground fault due to MC4 Connector was melted, rectified | 5:29 | 6:00 | 9:50 | 10:10 | 0.51667 | 4.35 | 4.6833 | 4.6833 | String no.1,6,10,11 & 12 on ground fault due to MC4 Connector was melted, rectified | closed | 0.019295 | 1.345 | 112.4631
2222 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK6 |  |  | INV18 |  |  | BLK6INV18 | 22 | 0.4449% | string |  | During string monitoring we found that string no 5 MC4 connector was melted so replace it with spare one & restore | 5:29 | 6:00 | 10:20 | 10:45 | 0.51667 | 4.85 | 5.2667 | 5.2667 | During string monitoring we found that string no 5 MC4 connector was melted so replace it with spare one & restore | closed | 0.023434 | 1.456 | 24.3489
2223 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK6 |  |  | INV17 |  |  | BLK6INV17 | 22 | 0.412% | string |  | During string monitoring we found that string no 6 MC4 connector was melted so replace it with spare one & restore | 5:29 | 6:00 | 10:55 | 11:20 | 0.51667 | 5.4333 | 5.85 | 5.85 | During string monitoring we found that string no 6 MC4 connector was melted so replace it with spare one & restore | closed | 0.024101 | 1.657 | 27.7102
2224 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:10 | 12:10 | 12:14 | 12:15 | 0 | 0.066667 | 0.083333 | 0.083333 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011167 | 0.106 | 720.7041
2225 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:10 | 12:10 | 12:16 | 12:17 | 0 | 0.1 | 0.11667 | 0.11667 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.014583 | 0.14 | 887.9415
2226 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:10 | 12:10 | 12:17 | 12:18 | 0 | 0.11667 | 0.13333 | 0.13333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.017707 | 0.159 | 1071.4173
2227 | 2025-07-06 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:27 | 13.2 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 264 | 0.3955% | inverter |  | Inverter shutdown on fault of excessive leakage current, after identify the string, isolate the string & charge the inverter | 5:15 | 6:10 | 7:10 | 7:30 | 0.91667 | 1.9167 | 2.25 | 2.25 | Inverter shutdown on fault of excessive leakage current, after identify the string, isolate the string & charge the inverter | closed | 0.0088989 | 0.156 | 31.3057
2228 | 2025-07-06 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:27 | 13.2 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 22.25 | 0.3955% | string |  | during VOC we found that sring no 9 in ground fault so rectify it & connect to the inverter, restore | 5:15 | 6:10 | 7:45 | 8:15 | 0.91667 | 2.5 | 3 | 3 | during VOC we found that sring no 9 in ground fault so rectify it & connect to the inverter, restore | closed | 0.011865 | 0.37 | 6.2579
2229 | 2025-07-06 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:27 | 13.2 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | String 13 cable failure so for minimize the generation lost its load is connected with string no 14 while string no 5 seprated to 2v half string & connected to inverter | 5:15 | 5:15 | 10:10 | 10:53 | 0 | 4.9167 | 5.6333 | 5.6333 | String 13 cable failure so for minimize the generation lost its load is connected with string no 14 while string no 5 seprated to 2v half string & connected to inverter | closed | 0.022533 | 1.564 | 14.2664
2230 | 2025-07-06 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:27 | 13.2 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | string |  | String 14 cable failure so for minimize the generation lost its load is connected with string no 15 while string no 6 seprated to 2v half string & connected to inverter | 5:15 | 5:15 | 11:10 | 11:40 | 0 | 5.9167 | 6.4167 | 6.4167 | String 14 cable failure so for minimize the generation lost its load is connected with string no 15 while string no 6 seprated to 2v half string & connected to inverter | closed | 0.028875 | 2.241 | 20.4418
2231 | 2025-07-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:19 | 18:44 | 13.4167 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:18 | 12:18 | 12:22 | 12:23 | 0 | 0.066667 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011067 | 0.085 | 572.7703
2232 | 2025-07-10 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:27 | 18:31 | 13.0667 | BLK6 |  |  | INV30 |  |  | BLK6INV30 | 22 | 0.412% | inverter |  | String no.12 on ground fault due to MC4 Connector & Y-connector was melted, rectified | 7:15 | 7:15 | 8:15 | 8:40 | 0 | 1 | 1.4167 | 1.4167 | String no.12 on ground fault due to MC4 Connector & Y-connector was melted, rectified (Due to rain rectification work delayed) | closed | 0.0058365 | 0.262 | 4.3815
2233 | 2025-07-11 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:13 | 18:45 | 13.5333 | BLK6 |  |  | INV15 |  |  | BLK6INV15 | 22 | 0.412% | string |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:13 | 6:10 | 7:30 | 8:10 | 0.95 | 2.2833 | 2.95 | 2.95 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.012154 | 0.392 | 6.5555
2234 | 2025-07-11 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:13 | 18:45 | 13.5333 | BLK6 |  |  | INV31 |  |  | BLK6INV31 | 44 | 0.412% | string |  | String no.4& 6 on ground fault due to MC4 Connector & Y-connector was melted, rectified | 5:13 | 6:10 | 8:15 | 8:30 | 0.95 | 3.0333 | 3.2833 | 3.2833 | String no.4& 6 on ground fault due to MC4 Connector & Y-connector was melted, rectified | closed | 0.013527 | 0.539 | 18.0275
2235 | 2025-07-11 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:13 | 18:45 | 13.5333 | BLK7 |  |  | INV23 |  |  | BLK7INV23 | 22.25 | 0.4% | string |  | String no.3 on ground fault due to MC4 Connector was melted, rectified | 5:13 | 6:10 | 8:45 | 9:10 | 0.95 | 3.5333 | 3.95 | 3.95 | String no.3 on ground fault due to MC4 Connector was melted, rectified | closed | 0.0158 | 0.927 | 15.6785
2236 | 2025-07-11 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:13 | 18:45 | 13.5333 | BLK7 |  |  | INV12 |  |  | BLK7INV12 | 20 | 0.4054% | string |  | String no.12 on ground fault due to MC4 Connector was melted, rectified | 5:13 | 6:10 | 9:15 | 9:35 | 0.95 | 4.0333 | 4.3667 | 4.3667 | String no.12 on ground fault due to MC4 Connector was melted, rectified | closed | 0.017702 | 1.068 | 16.2366
2237 | 2025-07-11 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:13 | 18:45 | 13.5333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 10:34 | 10:34 | 10:37 | 10:41 | 0 | 0.05 | 0.11667 | 0.11667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.015494 | 0.135 | 909.694
2238 | 2025-07-11 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:13 | 18:45 | 13.5333 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 10:34 | 10:34 | 10:37 | 10:39 | 0 | 0.05 | 0.083333 | 0.083333 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011167 | 0.11 | 747.9005
2239 | 2025-07-11 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:13 | 18:45 | 13.5333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:00 | 12:00 | 12:04 | 12:05 | 0 | 0.066667 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011067 | 0.101 | 680.5858
2240 | 2025-07-11 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:13 | 18:45 | 13.5333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:00 | 12:00 | 12:07 | 12:08 | 0 | 0.11667 | 0.13333 | 0.13333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.016667 | 0.139 | 881.5991
2241 | 2025-07-11 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:13 | 18:45 | 13.5333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:27 | 12:27 | 12:29 | 12:31 | 0 | 0.033333 | 0.066667 | 0.066667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.0088537 | 0.082 | 552.5548
2242 | 2025-07-11 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:13 | 18:45 | 13.5333 | BLK1 |  |  | INV16 |  |  | BLK1INV16 | 267 | 0.4% | Inverter |  | Inverter Shows starting up mode so we have to check all the string after checking the string we got all string are accurate so we Off the Inverter as well as ACCB, Then Charge, Restore | 12:45 | 12:50 | 12:55 | 13:30 | 0.083333 | 0.16667 | 0.75 | 0.75 | Inverter Shows starting up mode so we have to check all the string after checking the string we got all string are accurate so we Off the Inverter as well as ACCB, Then Charge, Restore | closed | 0.003 | 0.741 | 150.3919
2243 | 2025-07-11 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:13 | 18:45 | 13.5333 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 222.5 | 0.3333% | Inverter |  | Inverter tripped after the IDT tripping as inverter not bootup auto,(we have to Manually trip the inverter & ACCB from to Charge the Inverter) | 12:07 | 12:07 | 12:10 | 12:35 | 0 | 0.05 | 0.46667 | 0.46667 | Inverter tripped after the IDT tripping as inverter not bootup auto,(we have to Manually trip the inverter & ACCB from to Charge the Inverter) | closed | 0.0015556 | 0.409 | 69.1749
2244 | 2025-07-11 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:13 | 18:45 | 13.5333 | BLK5 |  |  | INV27 |  |  | BLK5INV27 | 267 | 0.4% | Inverter |  | Inverter tripped after the IDT tripping as inverter not bootup auto, so we share the logfile to OEM after getting the instruction from the OEM we Manually trip the inverter & ACCB & than Charge the Inverter) | 12:29 | 12:35 | 12:50 | 1:45 | 0.1 | 0.35 | -10.7333 | -10.7333 | Inverter tripped after the IDT tripping as inverter not bootup auto, so we share the logfile to OEM after getting the instruction from the OEM we Manually trip the inverter & ACCB & than Charge the Inverter) | closed | -0.042933 | 1.342 | 272.3697
2245 | 2025-07-12 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:27 | 13.1833 | BLK3 |  |  | INV27 |  |  | BLK3INV27 | 267 | 0.4% | Inverter |  | Inverter no 27 shutdown on fault of excessive leakage current so we isolate the all string & found that St no 13 on ground fault so we rectify & connect the same | 16:35 | 16:40 | 16:50 | 17:20 | 0.083333 | 0.25 | 0.75 | 0.75 | Inverter no 27 shutdown on fault of excessive leakage current so we isolate the all string & found that St no 13 on ground fault so we rectify & connect the same | closed | 0.003 | 0.009 | 1.8266
2246 | 2025-07-12 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:27 | 13.1833 | BLK3 |  |  | INV30 |  |  | BLK3INV30 | 267 | 0.4% | Inverter |  | Inverter no 30 shutdown on fault of excessive leakage current so we isolate the all string & found that St no 1 on ground fault so we rectify & connect the same | 16:35 | 16:40 | 16:55 | 17:25 | 0.083333 | 0.33333 | 0.83333 | 0.83333 | Inverter no 30 shutdown on fault of excessive leakage current so we isolate the all string & found that St no 1 on ground fault so we rectify & connect the same | closed | 0.0033333 | 0.011 | 2.2325
2247 | 2025-07-12 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:27 | 13.1833 | BLK5 |  |  | INV26 |  |  | BLK5INV26 | 289.25 | 0.4333% | Inverter |  | Inverter no 26 shutdown on fault of excessive leakage current so we isolate the all string & found that St no 1 on ground fault so we rectify & connect the same | 16:35 | 16:40 | 17:25 | 17:45 | 0.083333 | 0.83333 | 1.1667 | 1.1667 | Inverter no 26 shutdown on fault of excessive leakage current so we isolate the all string & found that St no 1 on ground fault so we rectify & connect the same | closed | 0.0050556 | 0.017 | 3.7378
2248 | 2025-07-12 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:27 | 13.1833 | BLK8 |  |  | INV10 |  |  | BLK8INV10 | 300.375 | 0.45% | Inverter |  | Inverter no 10 shutdown on fault of excessive leakage current so we isolate the all string & found that St no 7 on ground fault so we rectify & connect the same | 16:35 | 16:40 | 17:30 | 17:50 | 0.083333 | 0.91667 | 1.25 | 1.25 | Inverter no 10 shutdown on fault of excessive leakage current so we isolate the all string & found that St no 7 on ground fault so we rectify & connect the same | closed | 0.005625 | 0.019 | 4.3382
2249 | 2025-07-12 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:27 | 13.1833 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:19 | 12:19 | 12:21 | 12:21 | 0 | 0.033333 | 0.033333 | 0.033333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.0044268 | 0.054 | 363.8776
2250 | 2025-07-12 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:27 | 13.1833 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | Inverter |  | To control unneceesary tripping of IDT all inverter active power limit set to 68% | 12:22 | 12:22 | 12:22 | 13:30 | 0 | 0 | 1.1333 | 1.1333 | To control unneceesary tripping of IDT all inverter active power limit set to 68% | closed | 0.15051 |  | 0
2251 | 2025-07-12 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:27 | 13.1833 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | Inverter |  | To control unneceesary tripping of IDT all inverter active power limit set to 68% | 12:22 | 12:22 | 12:22 | 13:30 | 0 | 0 | 1.1333 | 1.1333 | To control unneceesary tripping of IDT all inverter active power limit set to 68% | closed | 0.15187 |  | 0
2252 | 2025-07-12 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:27 | 13.1833 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | Inverter |  | To control unneceesary tripping of IDT all inverter active power limit set to 68% | 12:22 | 12:22 | 12:22 | 13:30 | 0 | 0 | 1.1333 | 1.1333 | To control unneceesary tripping of IDT all inverter active power limit set to 68% | closed | 0.14167 |  | 0
2253 | 2025-07-12 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:16 | 18:27 | 13.1833 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8976 | 13.45% | Inverter |  | To control unneceesary tripping of IDT all inverter active power limit set to 68% | 12:22 | 12:22 | 12:22 | 13:30 | 0 | 0 | 1.1333 | 1.1333 | To control unneceesary tripping of IDT all inverter active power limit set to 68% | closed | 0.1524 |  | 0
2254 | 2025-07-13 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:24 | 18:39 | 13.25 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | Inverter |  | To control unneceesary tripping of IDT all inverter active power limit set to 60% | 11:25 | 11:25 | 11:25 | 14:15 | 0 | 0 | 2.8333 | 2.8333 | To control unneceesary tripping of IDT all inverter active power limit set to 60% | closed | 0.37628 |  | 0
2255 | 2025-07-13 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:24 | 18:39 | 13.25 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | Inverter |  | To control unneceesary tripping of IDT all inverter active power limit set to 60% | 11:25 | 11:25 | 11:25 | 14:15 | 0 | 0 | 2.8333 | 2.8333 | To control unneceesary tripping of IDT all inverter active power limit set to 60% | closed | 0.37628 |  | 0
2256 | 2025-07-13 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:24 | 18:39 | 13.25 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | Inverter |  | To control unneceesary tripping of IDT all inverter active power limit set to 60% | 11:25 | 11:25 | 11:25 | 14:15 | 0 | 0 | 2.8333 | 2.8333 | To control unneceesary tripping of IDT all inverter active power limit set to 60% | closed | 0.37967 |  | 0
2257 | 2025-07-13 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:24 | 18:39 | 13.25 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | Inverter |  | To control unneceesary tripping of IDT all inverter active power limit set to 60% | 11:25 | 11:25 | 11:25 | 14:15 | 0 | 0 | 2.8333 | 2.8333 | To control unneceesary tripping of IDT all inverter active power limit set to 60% | closed | 0.35417 |  | 0
2258 | 2025-07-13 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:24 | 18:39 | 13.25 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8976 | 13.45% | Inverter |  | To control unneceesary tripping of IDT all inverter active power limit set to 60% | 11:25 | 11:25 | 11:25 | 14:15 | 0 | 0 | 2.8333 | 2.8333 | To control unneceesary tripping of IDT all inverter active power limit set to 60% | closed | 0.381 |  | 0
2259 | 2025-07-15 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:09 | 18:39 | 13.5 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | Inverter |  | To control unneceesary tripping of IDT all inverter active power limit set to 75% | 11:10 | 11:10 | 11:10 | 13:30 | 0 | 0 | 2.3333 | 2.3333 | To control unneceesary tripping of IDT all inverter active power limit set to 75% | closed | 0.30988 |  | 0
2260 | 2025-07-15 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:09 | 18:39 | 13.5 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | Inverter |  | To control unneceesary tripping of IDT all inverter active power limit set to 75% | 11:10 | 11:10 | 11:10 | 13:30 | 0 | 0 | 2.3333 | 2.3333 | To control unneceesary tripping of IDT all inverter active power limit set to 75% | closed | 0.31267 |  | 0
2261 | 2025-07-15 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:09 | 18:39 | 13.5 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | Inverter |  | To control unneceesary tripping of IDT all inverter active power limit set to 75% | 11:10 | 11:10 | 11:10 | 13:30 | 0 | 0 | 2.3333 | 2.3333 | To control unneceesary tripping of IDT all inverter active power limit set to 75% | closed | 0.29167 |  | 0
2262 | 2025-07-15 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:09 | 18:39 | 13.5 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8976 | 13.45% | Inverter |  | To control unneceesary tripping of IDT all inverter active power limit set to 78% | 11:10 | 11:10 | 11:10 | 13:30 | 0 | 0 | 2.3333 | 2.3333 | To control unneceesary tripping of IDT all inverter active power limit set to 78% | closed | 0.31377 |  | 0
2263 | 2025-07-15 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:09 | 18:39 | 13.5 | BLK8 |  |  | INV26 |  |  | BLK8INV26 | 40.2 | 0.4065% | String |  | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | 10:00 | 10:00 | 10:00 | 18:39 | 0 | 0 |  | 8.65 | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | open | 0.035164 | 3.06 | 93.5067
2263 | 2025-07-16 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:22 | 18:41 | 13.3167 | BLK8 |  |  | INV26 |  |  | BLK8INV26 | 40.2 | 0.4065% | String |  | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | 5:22 | 5:22 | 5:22 | 18:41 | 0 | 0 |  | 13.3167 | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | open | 0.054134 | 3.55 | 108.4799
2264 | 2025-07-17 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:24 | 18:25 | 13.0167 | BLK8 |  |  | INV26 |  |  | BLK8INV26 | 40.2 | 0.4065% | String |  | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | 5:24 | 5:24 | 5:24 | 18:25 | 0 | 0 |  | 13.0167 | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | open | 0.052915 | 3.55 | 108.4799
2265 | 2025-07-18 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:33 | 18:25 | 12.8667 | BLK8 |  |  | INV26 |  |  | BLK8INV26 | 40.2 | 0.4065% | String |  | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | 5:33 | 5:33 | 5:33 | 18:25 | 0 | 0 |  | 12.8667 | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | open | 0.052305 | 1.41 | 43.0864
2266 | 2025-07-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:38 | 13.3833 | BLK8 |  |  | INV26 |  |  | BLK8INV26 | 40 | 0.4065% | String |  | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | 5:15 | 5:15 | 5:15 | 18:38 | 0 | 0 |  | 13.3833 | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | open | 0.054406 | 5.84 | 177.5693
2267 | 2025-07-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:38 | 13.3833 | BLK3 |  |  | INV10 |  |  | BLK3INV10 | 267 | 0.4% | String |  | Inverter no 10 shutdown on fault of excessive leakage current so we isolate the all string & found that St no 10 on ground fault so we rectify & connect the same | 5:15 | 7:00 | 7:05 | 7:25 | 1.75 | 1.8333 | 2.1667 | 2.1667 | Inverter no 10 shutdown on fault of excessive leakage current so we isolate the all string & found that St no 10 on ground fault so we rectify & connect the same | closed | 0.0086667 | 0.166 | 33.691
2268 | 2025-07-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:38 | 13.3833 | BLK3 |  |  | INV23 |  |  | BLK3INV23 | 267 | 0.4% | String |  | During string monitoring found that inverter 23 st 7 shows 0 Amp current so we check in field & found that Fuse & Y Connector melted so replace it with spare one, restore | 5:15 | 7:00 | 7:35 | 8:00 | 1.75 | 2.3333 | 2.75 | 2.75 | During string monitoring found that inverter 23 st 7 shows 0 Amp current so we check in field & found that Fuse & Y Connector melted so replace it with spare one, restore | closed | 0.011 | 0.338 | 68.5998
2269 | 2025-07-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:38 | 13.3833 | BLK4 |  |  | INV23 |  |  | BLK4INV23 | 300.375 | 0.4% | String |  | Inverter no 23 shutdown on fault of excessive leakage current so we isolate the all string & found that St no 9 on ground fault (Yconnector melted)so we rectify & connect the same | 5:15 | 7:00 | 8:10 | 8:35 | 1.75 | 2.9167 | 3.3333 | 3.3333 | Inverter no 23 shutdown on fault of excessive leakage current so we isolate the all string & found that St no 9 on ground fault so we rectify & connect the same | closed | 0.013333 | 0.563 | 128.5486
2270 | 2025-07-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:38 | 13.3833 | BLK7 |  |  | INV15 |  |  | BLK7INV15 | 292.6 | 0.4% | String |  | Inverter no 15 shutdown on fault of excessive leakage current so we isolate the all string & found that St no 12 (DC cable punctured) on ground fault so we rectify & connect the same | 5:15 | 7:00 | 8:40 | 9:05 | 1.75 | 3.4167 | 3.8333 | 3.8333 | Inverter no 15 shutdown on fault of excessive leakage current so we isolate the all string & found that St no 12 on ground fault so we rectify & connect the same | closed | 0.015333 | 0.788 | 175.2652
2271 | 2025-07-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:38 | 13.3833 | BLK8 |  |  | INV13 |  |  | BLK8INV13 | 20.1 | 0.4153% | String |  | Inverter 13 string no 11 fuse was failure so replace it with spare one | 5:15 | 7:00 | 10:10 | 10:30 | 1.75 | 4.9167 | 5.25 | 5.25 | Inverter 13 string no 11 fuse was failure so replace it with spare one | closed | 0.021802 | 1.525 | 23.3003
2272 | 2025-07-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:15 | 18:38 | 13.3833 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 44.5 | 0.3856% | String |  | Inverter no 28 string no1 & 3 was on ground fault so (Fuse failure)replace it with spare one | 5:15 | 7:00 | 9:30 | 10:00 | 1.75 | 4.25 | 4.75 | 4.75 | Inverter no 28 string no1 & 3 was on ground fault so replace it with spare one(as this inverter not communicated with scada so we got late information) | closed | 0.018317 | 1.224 | 41.4034
2273 | 2025-07-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:25 | 18:38 | 13.2167 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 40.2 | 0.3856% | String |  | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | 5:25 | 5:25 | 5:25 | 18:38 | 0 | 0 |  | 13.2167 | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | open | 0.050966 | 6.19 | 189.1524
2274 | 2025-07-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:25 | 18:38 | 13.2167 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 40.2 | 0.4301% | String |  | Block-8 Inverter 19 string no 5 & 8 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | 10:10 | 10:10 | 10:10 | 18:38 | 0 | 0 |  | 8.4667 | Block-8 Inverter 19 string no 5 & 8 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | open | 0.036416 | 4.67 | 142.7046
2275 | 2025-07-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:25 | 18:38 | 13.2167 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | Inverter |  | To control unnecessary tripping of IDT all inverter active power limit set to 6600kW | 11:10 | 11:10 | 11:10 | 13:45 | 0 | 0 | 2.5833 | 2.5833 | To control unneceesary tripping of IDT all inverter active power limit set to 6600kW | closed | 0.34617 |  | 0
2276 | 2025-07-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:25 | 18:38 | 13.2167 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | Inverter |  | To control unnecessary tripping of IDT all inverter active power limit set to 6600kW | 11:10 | 11:10 | 11:10 | 13:45 | 0 | 0 | 2.5833 | 2.5833 | To control unneceesary tripping of IDT all inverter active power limit set to 6600kW | closed | 0.32292 |  | 0
2277 | 2025-07-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:25 | 18:38 | 13.2167 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | Inverter |  | To control unnecessary tripping of IDT all inverter active power limit set to 6650kW | 11:10 | 11:10 | 11:10 | 13:45 | 0 | 0 | 2.5833 | 2.5833 | To control unneceesary tripping of IDT all inverter active power limit set to 6650kW | closed | 0.34308 |  | 0
2278 | 2025-07-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:25 | 18:38 | 13.2167 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8976 | 13.45% | Inverter |  | To control unnecessary tripping of IDT all inverter active power limit set to 6700kW | 11:10 | 11:10 | 11:10 | 13:45 | 0 | 0 | 2.5833 | 2.5833 | To control unneceesary tripping of IDT all inverter active power limit set to 6700kW | closed | 0.34739 |  | 0
2279 | 2025-07-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:50 | 18:38 | 12.8 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 40.2 | 0.3856% | String |  | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | 5:50 | 5:50 | 5:50 | 18:38 | 0 | 0 |  | 12.8 | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | open | 0.049359 | 3.4 | 103.8963
2280 | 2025-07-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:50 | 18:38 | 12.8 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 40.2 | 0.4301% | String |  | Block-8 Inverter 19 string no 5 & 8 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | 5:50 | 5:50 | 5:50 | 18:38 | 0 | 0 |  | 12.8 | Block-8 Inverter 19 string no 5 & 8 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | open | 0.055054 | 3.4 | 103.8963
2281 | 2025-07-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:26 | 18:32 | 13.1 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 40.2 | 0.3856% | String |  | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | 5:32 | 5:32 | 5:32 | 18:26 | 0 | 0 |  | 12.9 | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | open | 0.049745 | 5.81 | 177.5404
2282 | 2025-07-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:26 | 18:32 | 13.1 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 40.2 | 0.4301% | String |  | Block-8 Inverter 19 string no 5 & 8 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | 5:32 | 5:32 | 5:32 | 18:26 | 0 | 0 |  | 12.9 | Block-8 Inverter 19 string no 5 & 8 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | open | 0.055484 | 5.81 | 177.5404
2283 | 2025-07-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:26 | 18:32 | 13.1 | BLK6 |  |  | INV28 |  |  | BLK6INV28 | 286 | 0.4285% | Inverter |  | Inverter tripped on fault of excessive leakage current, when we check the VOC of the string we found that String no 13 VOC is not accurate, found Y connector burnt replace it with spare one | 7:25 | 7:30 | 7:45 | 8:15 | 0.083333 | 0.33333 | 0.83333 | 0.83333 | Inverter tripped on fault of excessive leakage current, when we check the VOC of the string we found that String no 13 VOC is not accurate, found Y connector burnt replace it with spare one | closed | 0.0035705 | 0.239 | 51.9588
2284 | 2025-07-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:27 | 18:33 | 13.1 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 40.2 | 0.3856% | string |  | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | 5:27 | 5:27 | 5:27 | 18:33 | 0 | 0 |  | 13.1 | Block-8 Inverter 26 string no 10 & 12 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | open | 0.050516 | 2.1 | 64.1712
2285 | 2025-07-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:27 | 18:33 | 13.1 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 40.2 | 0.4301% | string |  | Block-8 Inverter 19 string no 5 & 8 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | 5:27 | 5:27 | 5:27 | 18:33 | 0 | 0 |  | 13.1 | Block-8 Inverter 19 string no 5 & 8 isolated from the inverter as O2 Power management Team instructed to dismantle the MMS to control water of river | open | 0.056345 | 2.1 | 64.1712
2286 | 2025-07-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:27 | 18:33 | 13.1 | BLK6 |  |  | INV9 |  |  | BLK6INV9 | 22 | 0.412% | string |  | Durig string monitoring we found that string no 7 MC4 open, after verifying the load connect the same | 8:00 | 8:00 | 9:00 | 9:15 | 0 | 1 | 1.25 | 1.25 | Durig string monitoring we found that string no 7 MC4 open, after verifying the load connect the same | closed | 0.0051498 | 0.102 | 1.7058
2287 | 2025-07-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:27 | 18:33 | 13.1 | BLK6 |  |  | INV24 |  |  | BLK6INV24 | 11 | 0.4285% | string |  | Durig string monitoring we found that string no 4 fuse failure (1 Nos.), after verifying the load connect the same | 8:00 | 8:00 | 16:30 | 17:00 | 0 | 8.5 | 9 | 9 | Durig string monitoring we found that string no 4 fuse failure (1 Nos.), after verifying the load connect the same | closed | 0.038562 | 2.1 | 17.5593
Formulas:
Days = DAY(EOMONTH(PA[[#This Row],[Date]], 0))
Days = DAY(EOMONTH(PA!$[Date], 0))

## Inv_SY_B
| 289.25 | 289.25 | 267 | 267 | 289.25 | 267 | 267 | 267 | 278.125 | 278.125 | 267 | 267 | 267 | 244.75 | 267 | 267 | 267 | 267 | 289.25 | 289.25 | 267 | 267 | 289.25 | 300.375 | 289.25 | 289.25 | 289.25 | 300.375 | 300.375 | 300.375 | 300.375 | 300.375 | 254.4 | 334.55 | 267 | 298.9 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 289.25 | 267 | 278.125 | 278.125 | 267 | 267 | 300.375 | 300.375 | 289.25 | 300.375 | 300.375 | 267 | 300.375 | 300.375 | 267 | 298.9 | 267 | 239.25 | 289.25 | 289.25 | 289.25 | 289.25 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 300.375 | 300.375 | 267 | 267 | 289.25 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 278.125 | 289.25 | 267 | 267 | 300.375 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 267 | 300.375 | 298.9 | 267 | 300.375 | 289.25 | 289.25 | 300.375 | 300.375 | 267 | 267 | 298.9 | 300.375 | 300.375 | 267 | 267 | 300.375 | 300.375 | 267 | 267 | 300.375 | 267 | 267 | 300.375 | 300.375 | 289.25 | 289.25 | 289.25 | 244.75 | 286 | 286 | 286 | 286 | 278.125 | 267 | 289.25 | 289.25 | 267 | 289.25 | 267 | 289.25 | 267 | 244.75 | 289.25 | 289.25 | 289.25 | 267 | 300.375 | 267 | 267 | 267 | 267 | 267 | 264 | 264 | 297 | 264 | 297 | 297 | 297 | 275 | 264 | 297 | 264 | 275 | 275 | 275 | 297 | 275 | 297 | 264 | 264 | 264 | 297 | 264 | 286 | 297 | 297 | 275 | 286 | 297 | 275 | 275 | 275 | 286 | 264 | 264 | 264 | 264 | 264 | 264 | 220 | 264 | 0 | 0 | 227.4 | 190.35 | 270.6 | 0 | 292.6 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 300.375 | 223.3 | 223.3 | 191.4 | 159.5 | 207.9 | 239.8 | 278.125 | 300.375 | 289.25 | 289.25 | 278.125 | 289.25 | 300.375 | 300.375 | 257.4 | 277.2 | 257.4 | 267.3 | 247.5 | 0 | 353.3 | 287.1 | 100.5 | 267.3 | 257.4 | 0 | 0 | 239.25 | 255.2 | 230.15 | 257.4 | 241.2 | 66958.55
| 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 | 237 | 238 | 239 | 240 | 241 | 242 | 243 | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261
Date | BLK1_INV1 | BLK1_INV2 | BLK1_INV3 | BLK1_INV4 | BLK1_INV5 | BLK1_INV6 | BLK1_INV7 | BLK1_INV8 | BLK1_INV9 | BLK1_INV10 | BLK1_INV11 | BLK1_INV12 | BLK1_INV13 | BLK1_INV14 | BLK1_INV15 | BLK1_INV16 | BLK1_INV17 | BLK1_INV18 | BLK1_INV19 | BLK1_INV20 | BLK1_INV21 | BLK1_INV22 | BLK1_INV23 | BLK1_INV24 | BLK1_INV25 | BLK1_INV26 | BLK1_INV27 | BLK1_INV28 | BLK1_INV29 | BLK1_INV30 | BLK1_INV31 | BLK1_INV32 | BLK2_INV1 | BLK2_INV2 | BLK2_INV3 | BLK2_INV4 | BLK2_INV5 | BLK2_INV6 | BLK2_INV7 | BLK2_INV8 | BLK2_INV9 | BLK2_INV10 | BLK2_INV11 | BLK2_INV12 | BLK2_INV13 | BLK2_INV14 | BLK2_INV15 | BLK2_INV16 | BLK2_INV17 | BLK2_INV18 | BLK2_INV19 | BLK2_INV20 | BLK2_INV21 | BLK2_INV22 | BLK2_INV23 | BLK2_INV24 | BLK2_INV25 | BLK2_INV26 | BLK2_INV27 | BLK2_INV28 | BLK2_INV29 | BLK2_INV30 | BLK2_INV31 | BLK2_INV32 | BLK3_INV1 | BLK3_INV2 | BLK3_INV3 | BLK3_INV4 | BLK3_INV5 | BLK3_INV6 | BLK3_INV7 | BLK3_INV8 | BLK3_INV9 | BLK3_INV10 | BLK3_INV11 | BLK3_INV12 | BLK3_INV13 | BLK3_INV14 | BLK3_INV15 | BLK3_INV16 | BLK3_INV17 | BLK3_INV18 | BLK3_INV19 | BLK3_INV20 | BLK3_INV21 | BLK3_INV22 | BLK3_INV23 | BLK3_INV24 | BLK3_INV25 | BLK3_INV26 | BLK3_INV27 | BLK3_INV28 | BLK3_INV29 | BLK3_INV30 | BLK3_INV31 | BLK4_INV1 | BLK4_INV2 | BLK4_INV3 | BLK4_INV4 | BLK4_INV5 | BLK4_INV6 | BLK4_INV7 | BLK4_INV8 | BLK4_INV9 | BLK4_INV10 | BLK4_INV11 | BLK4_INV12 | BLK4_INV13 | BLK4_INV14 | BLK4_INV15 | BLK4_INV16 | BLK4_INV17 | BLK4_INV18 | BLK4_INV19 | BLK4_INV20 | BLK4_INV21 | BLK4_INV22 | BLK4_INV23 | BLK4_INV24 | BLK4_INV25 | BLK4_INV26 | BLK4_INV27 | BLK4_INV28 | BLK4_INV29 | BLK4_INV30 | BLK4_INV31 | BLK5_INV1 | BLK5_INV2 | BLK5_INV3 | BLK5_INV4 | BLK5_INV5 | BLK5_INV6 | BLK5_INV7 | BLK5_INV8 | BLK5_INV9 | BLK5_INV10 | BLK5_INV11 | BLK5_INV12 | BLK5_INV13 | BLK5_INV14 | BLK5_INV15 | BLK5_INV16 | BLK5_INV17 | BLK5_INV18 | BLK5_INV19 | BLK5_INV20 | BLK5_INV21 | BLK5_INV22 | BLK5_INV23 | BLK5_INV24 | BLK5_INV25 | BLK5_INV26 | BLK5_INV27 | BLK5_INV28 | BLK5_INV29 | BLK5_INV30 | BLK5_INV31 | BLK5_INV32 | BLK6_INV1 | BLK6_INV2 | BLK6_INV3 | BLK6_INV4 | BLK6_INV5 | BLK6_INV6 | BLK6_INV7 | BLK6_INV8 | BLK6_INV9 | BLK6_INV10 | BLK6_INV11 | BLK6_INV12 | BLK6_INV13 | BLK6_INV14 | BLK6_INV15 | BLK6_INV16 | BLK6_INV17 | BLK6_INV18 | BLK6_INV19 | BLK6_INV20 | BLK6_INV21 | BLK6_INV22 | BLK6_INV23 | BLK6_INV24 | BLK6_INV25 | BLK6_INV26 | BLK6_INV27 | BLK6_INV28 | BLK6_INV29 | BLK6_INV30 | BLK6_INV31 | BLK6_INV32 | BLK7_INV1 | BLK7_INV2 | BLK7_INV3 | BLK7_INV4 | BLK7_INV5 | BLK7_INV6 | BLK7_INV7 | BLK7_INV8 | BLK7_INV9 | BLK7_INV10 | BLK7_INV11 | BLK7_INV12 | BLK7_INV13 | BLK7_INV14 | BLK7_INV15 | BLK7_INV16 | BLK7_INV17 | BLK7_INV18 | BLK7_INV19 | BLK7_INV20 | BLK7_INV21 | BLK7_INV22 | BLK7_INV23 | BLK7_INV24 | BLK7_INV25 | BLK7_INV26 | BLK7_INV27 | BLK7_INV28 | BLK7_INV29 | BLK7_INV30 | BLK7_INV31 | BLK7_INV32 | BLK8_INV1 | BLK8_INV2 | BLK8_INV3 | BLK8_INV4 | BLK8_INV5 | BLK8_INV6 | BLK8_INV7 | BLK8_INV8 | BLK8_INV9 | BLK8_INV10 | BLK8_INV11 | BLK8_INV12 | BLK8_INV13 | BLK8_INV14 | BLK8_INV15 | BLK8_INV16 | BLK8_INV17 | BLK8_INV18 | BLK8_INV19 | BLK8_INV20 | BLK8_INV21 | BLK8_INV22 | BLK8_INV23 | BLK8_INV24 | BLK8_INV25 | BLK8_INV26 | BLK8_INV27 | BLK8_INV28 | Plnat
2025-06-22 | 4.2541 | 4.2458 | 4.2288 | 4.2479 | 4.2213 | 4.2734 | 4.2622 | 4.2884 | 4.2787 | 4.2787 | 4.221 | 4.2959 | 4.1772 | 4.2737 | 4.2809 | 4.1199 | 4.2472 | 4.3165 | 4.3077 | 4.2558 | 4.2434 | 4.2509 | 4.2417 | 4.2613 | 4.2558 | 4.2835 | 4.2652 | 4.278 | 4.3213 | 4.1248 | 4.1798 | 3.9883 | 4.2846 | 4.1232 | 4.3101 | 4.2824 | 4.3228 | 4.2539 | 4.3112 | 4.2959 | 4.236 | 4.2532 | 4.2472 | 4.1985 | 4.2996 | 4.2285 | 4.1521 | 4.2734 | 4.1931 | 3.9673 | 4.3146 | 4.309 | 4.3313 | 4.2946 | 4.2714 | 4.2547 | 4.2314 | 4.2397 | 4.228 | 4.2946 | 4.2622 | 4.3158 | 4.2963 | 4.3887 | 4.2489 | 4.2558 | 4.308 | 4.2016 | 4.2397 | 4.2551 | 4.2659 | 4.2472 | 4.1985 | 4.2888 | 4.228 | 4.268 | 4.2757 | 4.2899 | 4.2798 | 4.3274 | 4.236 | 4.2288 | 4.2524 | 4.3056 | 4.3109 | 4.2925 | 4.2839 | 4.2835 | 4.2094 | 4.1768 | 4.2057 | 4.1452 | 4.236 | 4.2221 | 4.241 | 4.2659 | 4.2401 | 4.221 | 4.2925 | 4.2816 | 4.2509 | 4.2824 | 4.2472 | 4.2011 | 4.2687 | 4.2528 | 4.0682 | 4.2392 | 4.2944 | 4.2247 | 4.2244 | 3.9758 | 4.2234 | 4.252 | 4.3026 | 4.2745 | 4.1285 | 4.1558 | 4.1861 | 4.203 | 4.2903 | 3.9497 | 3.8665 | 4.2442 | 4.2809 | 4.245 | 4.2801 | 4.2693 | 4.1315 | 4.2121 | 4.2506 | 4.1521 | 4.2911 | 4.2942 | 4.2622 | 4.3042 | 4.3042 | 4.2797 | 4.2427 | 4.1236 | 4.2648 | 4.1957 | 4.2397 | 4.2662 | 4.2547 | 3.9713 | 4.1985 | 4.2533 | 4.2742 | 4.26 | 4.2627 | 4.297 | 4.2873 | 4.2476 | 4.2506 | 4.2277 | 4.2513 | 4.279 | 4.2792 | 4.2909 | 4.2458 | 4.2121 | 4.2212 | 4.2508 | 4.2121 | 4.3138 | 4.2189 | 4.2189 | 4.1742 | 4.192 | 4.1876 | 4.2015 | 4.2626 | 4.1895 | 4.2694 | 4.1705 | 4.2413 | 4.2697 | 4.3098 | 4.3091 | 4.1902 | 4.2061 | 4.2785 | 4.2909 | 4.278 | 4.2811 | 4.2182 | 4.2545 | 4.2767 | 3.993 | 4.1288 | 4.2083 | 4.2538 | 4.1705 | 4.1523 | 4.2322 | 4.2518 | 4.2587 |  |  | 4.4899 | 4.208 | 4.2166 |  | 4.1432 | 4.1985 | 4.1558 | 4.2011 | 4.1648 | 4.1427 | 4.2045 | 4.2 | 4.2288 | 4.1929 | 4.2266 | 4.1551 | 4.227 | 4.3223 | 4.3439 | 4.2991 | 4.3521 | 4.3135 | 4.1919 | 4.1747 | 4.1341 | 4.1608 | 4.1431 | 4.1822 | 4.1546 | 4.1901 | 4.1395 | 4.16 | 4.2778 | 4.1681 | 4.2863 | 4.2312 | 4.2747 |  | 4.246 | 4.2598 | 4.1891 | 4.1489 | 4.1608 |  |  | 4.3469 | 4.3143 | 4.9663 | 4.1608 | 4.2745 | 4.2377
2025-06-23 | 3.6889 | 3.6418 | 3.6629 | 3.6446 | 3.6273 | 3.6476 | 3.6427 | 3.6446 | 3.3496 | 3.6426 | 3.6742 | 3.6936 | 3.6745 | 3.6404 | 3.6262 | 3.6247 | 3.6161 | 3.7386 | 3.6142 | 3.6086 | 3.63 | 3.6404 | 3.6166 | 3.6604 | 3.6564 | 3.6242 | 3.6615 | 3.6225 | 3.6548 | 3.6328 | 3.6921 | 3.3625 | 3.6761 | 3.6826 | 3.6345 | 3.5831 | 3.6581 | 3.7116 | 3.6749 | 3.6625 | 3.6045 | 3.7075 | 3.7419 | 3.7251 | 3.6532 | 3.6682 | 3.2878 | 3.5921 | 3.6315 | 3.2755 | 3.6315 | 3.6442 | 3.6288 | 3.6335 | 3.5751 | 3.6621 | 3.6604 | 3.6326 | 3.6201 | 3.6767 | 3.6558 | 3.6132 | 3.6457 | 3.72 | 3.638 | 3.6557 | 3.6093 | 3.5889 | 3.6554 | 3.6483 | 3.6532 | 3.6221 | 3.5993 | 3.5993 | 3.5955 | 3.6571 | 3.5888 | 3.6813 | 3.6442 | 3.7058 | 3.6727 | 3.6176 | 3.6479 | 3.7041 | 3.6352 | 3.6446 | 3.6513 | 3.6285 | 3.5809 | 3.5419 | 3.5951 | 3.516 | 3.5768 | 3.588 | 3.5655 | 3.5884 | 2.7903 | 3.6899 | 3.5805 | 3.5955 | 3.633 | 3.588 | 3.5618 | 3.5453 | 3.5955 | 3.5618 | 3.5955 | 3.6112 | 3.5618 | 3.5256 | 3.6135 | 3.6398 | 3.5622 | 3.5323 | 3.5618 | 3.6105 | 3.2352 | 3.6288 | 3.5256 | 3.6536 | 3.5805 | 3.461 | 3.3828 | 3.5618 | 3.6217 | 3.6255 | 3.521 | 3.6109 | 3.5955 | 3.4823 | 3.5575 | 3.5239 | 3.6111 | 3.5138 | 3.5664 | 3.6038 | 3.0409 | 3.5979 | 3.5596 | 3.4981 | 3.5941 | 3.5277 | 3.6045 | 3.6024 | 3.5453 | 3.6093 | 3.6142 | 3.5792 | 3.6764 | 3.6667 | 3.6232 | 3.6375 | 3.5988 | 3.6045 | 3.6479 | 3.6037 | 3.6146 | 3.5693 | 3.6337 | 3.5951 | 3.6347 | 3.4883 | 3.3313 | 3.3273 | 3.532 | 3.6145 | 3.5606 | 3.3421 | 3.5606 | 3.5098 | 3.6058 | 3.5222 | 3.569 | 3.5636 | 3.6236 | 3.614 | 3.5644 | 3.5769 | 3.5744 | 3.6023 | 3.5664 | 3.5051 | 3.6061 | 3.6 | 3.5822 | 3.6118 | 3.5309 | 3.6033 | 3.3455 | 3.5315 | 3.5989 | 3.5447 | 3.5644 | 3.567 | 3.6235 | 3.5265 | 3.5455 | 3.5265 |  |  | 3.7819 | 3.2356 | 3.524 |  | 3.6408 | 3.5337 | 3.3757 | 3.5255 | 3.594 | 3.6247 | 3.6592 | 3.6558 | 3.5243 | 3.6483 | 3.6614 | 3.5243 | 3.5955 | 3.6621 | 3.717 | 3.6677 | 3.6468 | 3.7053 | 3.5642 | 3.6163 | 3.7124 | 3.6658 | 3.6353 | 3.6812 | 3.7131 | 3.7082 | 3.6977 | 3.6375 | 3.6581 | 3.539 | 3.6127 | 3.5226 | 3.5418 |  | 3.6824 | 3.5528 | 3.7015 | 3.4942 | 3.5043 |  |  | 3.9415 | 3.7226 | 4.1886 | 3.4887 | 3.5705 | 3.5962
2025-06-24 | 4.8927 | 5.0137 | 5.0404 | 4.97 | 4.9649 | 5.0124 | 5.0101 | 5.0345 | 5.0013 | 5.0333 | 5.0974 | 5.0861 | 4.8202 | 5.1718 | 5.024 | 5.021 | 4.9801 | 4.9689 | 4.9787 | 4.9777 | 5.0288 | 5.0521 | 4.9148 | 5.049 | 5.0586 | 5.0143 | 4.8716 | 4.9711 | 5.0254 | 4.8439 | 4.8456 | 4.831 | 4.945 | 5.0776 | 4.9105 | 4.9455 | 4.8067 | 4.8397 | 4.9326 | 4.9798 | 4.8955 | 4.8783 | 4.9667 | 4.9322 | 5.0004 | 5.0221 | 4.8709 | 4.9225 | 4.9377 | 4.8719 | 4.9884 | 4.9831 | 5.058 | 4.9911 | 4.9141 | 5.0071 | 4.9994 | 5.0082 | 4.9375 | 5.0054 | 4.9933 | 5.0335 | 4.9801 | 5.3889 | 5.0237 | 4.9787 | 5.0202 | 4.8619 | 4.9742 | 4.9652 | 4.97 | 4.9337 | 5.061 | 4.9517 | 4.9661 | 4.8613 | 4.9934 | 4.9775 | 4.9382 | 5.0009 | 5.0281 | 5.0438 | 4.9727 | 5.0213 | 4.9798 | 4.9993 | 4.9876 | 4.9809 | 4.8757 | 4.8457 | 4.8629 | 4.8443 | 5.0494 | 4.8715 | 4.9385 | 4.909 | 4.824 | 5.0483 | 4.9273 | 4.9996 | 5.1026 | 4.9573 | 4.9914 | 4.9067 | 4.9988 | 4.8596 | 5.1156 | 2.4975 | 5.0382 | 4.9774 | 5.0031 | 4.9615 | 4.9608 | 4.9971 | 5.0491 | 5.0315 | 4.8394 | 4.9478 | 4.9538 | 4.9981 | 5.0663 | 4.7527 | 4.6464 | 5.0109 | 4.9034 | 4.9235 | 4.9116 | 4.8404 | 4.9455 | 4.9012 | 4.875 | 4.808 | 4.8944 | 4.9075 | 5.0441 | 4.814 | 4.9755 | 5.0196 | 4.9715 | 4.9401 | 4.8754 | 4.8477 | 4.9258 | 4.9825 | 4.8071 | 4.8971 | 4.8386 | 4.9397 | 4.8885 | 4.874 | 4.9805 | 4.9195 | 4.9238 | 4.9154 | 4.8277 | 4.8356 | 4.8037 | 4.8816 | 5.0269 | 4.936 | 4.9795 | 4.8564 | 4.8687 | 4.8727 | 4.8956 | 4.9651 | 4.8966 | 4.9067 | 4.8788 | 4.8244 | 4.972 | 4.8636 | 4.862 | 4.9836 | 4.9842 | 4.9583 | 4.9682 | 4.8773 | 4.9013 | 5.0576 | 4.857 | 4.8926 | 4.8519 | 5.1636 | 5.0035 | 4.9657 | 4.9873 | 4.9091 | 4.8502 | 4.9301 | 4.9936 | 4.9587 | 4.8409 | 4.9322 | 4.9693 | 4.8527 | 5.0145 | 4.8864 |  |  | 5.1715 | 4.8385 | 4.8485 |  | 4.892 | 4.8581 | 4.8831 | 4.8824 | 4.9648 | 4.9727 | 5.0034 | 5.0041 | 4.9955 | 4.8281 | 4.9633 | 5 | 4.9615 | 4.9858 | 5.1232 | 4.9306 | 4.9321 | 5.0219 | 4.9264 | 4.8595 | 4.9762 | 4.9848 | 4.9386 | 4.922 | 5.0175 | 4.9628 | 4.9598 | 4.9149 | 4.8368 | 4.8308 | 4.8271 | 4.9502 | 4.9661 |  | 5.0977 | 4.8805 | 5.2189 | 4.8672 | 4.831 |  |  | 5.4378 | 5.0047 | 5.6528 | 4.8302 | 4.886 | 4.9439
2025-06-25 | 4.8356 | 4.8443 | 4.9667 | 4.9622 | 4.9158 | 4.9378 | 4.9539 | 4.8734 | 4.9111 | 4.9219 | 4.9142 | 4.9049 | 4.7345 | 4.8629 | 4.9322 | 4.927 | 4.9064 | 4.8846 | 4.874 | 4.8961 | 4.9483 | 4.9502 | 4.8353 | 4.9548 | 4.9649 | 4.9044 | 4.7402 | 4.8769 | 4.9005 | 4.7314 | 4.7457 | 4.7191 | 4.934 | 4.8516 | 4.8603 | 4.8953 | 4.9045 | 4.7993 | 4.8801 | 4.9614 | 4.8453 | 4.8015 | 4.8933 | 4.8528 | 4.9311 | 4.9363 | 4.8799 | 4.8708 | 4.8762 | 4.7227 | 4.9184 | 4.9101 | 4.8929 | 4.9202 | 4.7976 | 4.8846 | 4.8742 | 4.8678 | 4.8922 | 4.8759 | 4.9449 | 4.8906 | 4.9202 | 5.261 | 4.9414 | 4.8992 | 4.9587 | 4.8121 | 4.9157 | 4.8963 | 4.9157 | 4.8678 | 4.9404 | 4.9165 | 4.9538 | 4.8516 | 4.9605 | 4.9232 | 4.8715 | 4.9611 | 4.9476 | 4.8727 | 4.8906 | 4.9517 | 4.8824 | 4.9064 | 4.8996 | 4.8895 | 4.7858 | 4.7468 | 4.8068 | 4.7589 | 4.9816 | 4.8356 | 4.8849 | 4.8667 | 4.8813 | 4.9685 | 4.9079 | 4.9356 | 4.9479 | 4.8798 | 4.9255 | 4.8734 | 4.9445 | 4.8318 | 4.9615 | 4.7313 | 4.903 | 4.8879 | 4.9141 | 4.911 | 4.8476 | 4.8812 | 4.9596 | 4.7461 | 4.7461 | 4.8533 | 4.8832 | 4.9311 | 4.9404 | 4.6795 | 4.5546 | 4.9311 | 4.8322 | 4.8842 | 4.8322 | 4.8438 | 4.7068 | 4.821 | 4.8474 | 4.8035 | 4.8232 | 4.9164 | 4.899 | 4.8049 | 4.8605 | 4.9413 | 4.8694 | 4.7648 | 4.7772 | 4.7426 | 4.8813 | 4.8439 | 4.736 | 4.8152 | 4.797 | 4.8936 | 4.8498 | 4.8913 | 4.8439 | 4.8622 | 4.9488 | 4.8655 | 4.776 | 4.767 | 4.767 | 4.8648 | 4.8322 | 4.7409 | 4.764 | 4.7523 | 4.7407 | 4.7104 | 4.8559 | 4.7902 | 4.7394 | 4.8199 | 4.7898 | 4.7764 | 4.7913 | 4.7746 | 4.7623 | 4.8415 | 4.7751 | 4.7795 | 4.825 | 4.8087 | 4.7529 | 4.8663 | 4.7524 | 4.7253 | 4.8569 | 4.9535 | 4.8136 | 4.7771 | 4.8498 | 4.8378 | 4.8145 | 4.7399 | 4.8458 | 4.7413 | 4.7898 | 4.7879 | 4.9027 | 4.8027 | 4.8691 | 4.8864 |  |  | 5.1645 | 4.7386 | 4.813 |  | 4.8452 | 4.7644 | 4.8232 | 4.7607 | 4.8809 | 4.903 | 4.9476 | 4.9543 | 4.8318 | 4.7622 | 4.9345 | 4.8315 | 4.9352 | 5.0497 | 5.1679 | 5.0291 | 5.0522 | 4.9467 | 4.81 | 4.7631 | 4.9129 | 4.8706 | 4.7917 | 4.7934 | 4.942 | 4.8211 | 4.8633 | 4.7654 | 4.7552 | 4.7662 | 4.7436 | 4.7437 | 4.8667 |  | 5.0637 | 4.7638 | 5.005 | 4.7759 | 4.7809 |  |  | 5.2723 | 4.9177 | 5.705 | 4.7883 | 4.9362 | 4.8661
2025-06-26 | 4.8885 | 4.92 | 5.0157 | 5.0034 | 4.9352 | 4.9742 | 4.9449 | 4.9648 | 4.923 | 4.9395 | 5.006 | 4.9727 | 4.8303 | 4.952 | 4.8996 | 4.8921 | 4.861 | 4.8386 | 4.8318 | 4.847 | 4.9064 | 4.9161 | 4.7965 | 4.9002 | 4.902 | 4.8446 | 4.735 | 4.808 | 4.84 | 4.808 | 4.7387 | 4.7767 | 4.9033 | 5.0052 | 4.8345 | 4.8598 | 4.8693 | 4.7625 | 4.8375 | 4.9243 | 4.8139 | 4.7689 | 4.8457 | 4.8056 | 4.8993 | 4.9255 | 4.8916 | 4.8412 | 4.914 | 4.7507 | 4.9453 | 4.9341 | 4.8999 | 4.9215 | 4.7665 | 4.8979 | 4.8586 | 4.9315 | 4.8556 | 4.9072 | 4.9067 | 4.9512 | 4.897 | 5.3007 | 4.9276 | 4.8792 | 4.9428 | 4.8263 | 4.9094 | 4.8828 | 4.9199 | 4.8805 | 4.8775 | 4.873 | 4.8496 | 4.772 | 4.8952 | 4.873 | 4.8337 | 4.8868 | 4.9056 | 4.9266 | 4.8734 | 4.9247 | 4.8592 | 4.8955 | 4.9034 | 4.9052 | 4.7955 | 4.7678 | 4.827 | 4.7765 | 4.9674 | 4.9195 | 4.8593 | 4.833 | 4.8228 | 4.9464 | 4.8521 | 4.8985 | 4.9109 | 4.8303 | 4.8794 | 4.8191 | 4.8416 | 4.5749 | 4.9705 | 4.8026 | 4.921 | 4.8446 | 4.8515 | 4.8965 | 4.8649 | 4.8856 | 4.9367 | 4.7607 | 4.8019 | 4.7647 | 4.8087 | 4.9071 | 4.9678 | 4.6642 | 4.5057 | 4.8865 | 4.903 | 4.8866 | 4.83 | 4.8255 | 4.7644 | 4.8216 | 4.8107 | 4.8114 | 4.8277 | 4.9128 | 4.857 | 4.8014 | 4.8888 | 4.8993 | 4.8582 | 4.8697 | 4.7965 | 4.7748 | 4.9004 | 4.9286 | 4.7633 | 4.8283 | 4.7966 | 4.8813 | 4.7865 | 4.8532 | 4.8764 | 4.8131 | 4.9125 | 4.8311 | 4.7513 | 4.7869 | 4.7449 | 4.8318 | 4.8848 | 4.8148 | 4.8185 | 4.7943 | 4.7848 | 4.829 | 4.8455 | 4.804 | 4.7936 | 4.8859 | 4.8485 | 4.9273 | 4.8836 | 4.8415 | 4.7865 | 4.8767 | 4.7845 | 4.8148 | 4.8174 | 4.8902 | 4.8185 | 4.928 | 4.8409 | 4.7862 | 4.7492 | 4.9858 | 4.8885 | 4.8306 | 4.8873 | 4.8876 | 4.8705 | 4.7941 | 4.8932 | 4.8689 | 4.8716 | 4.8845 | 4.8864 | 4.8409 | 4.8636 | 4.9284 |  |  | 5.1935 | 4.8106 | 4.8141 |  | 4.9306 | 4.8161 | 4.8367 | 4.8 | 4.8727 | 4.8532 | 4.9854 | 4.9554 | 4.873 | 4.8315 | 4.9139 | 4.9622 | 4.9382 | 5.05 | 5.1545 | 5.0766 | 5.0914 | 5.0094 | 4.8066 | 4.9041 | 4.9316 | 4.9162 | 4.8781 | 4.8729 | 4.9298 | 4.9151 | 4.9844 | 4.9265 | 4.8221 | 4.8618 | 4.7933 | 4.8253 | 4.8117 |  | 5.0977 | 4.7948 | 5.1065 | 4.7729 | 4.7883 |  |  | 5.2706 | 5.0102 | 5.7402 | 4.7622 | 5.0004 | 4.8764
2025-06-27 | 4.4543 | 4.4636 | 4.4569 | 4.4981 | 4.4944 | 4.485 | 4.4255 | 4.4873 | 4.3222 | 4.3506 | 4.4573 | 4.4895 | 4.2873 | 4.3309 | 4.4442 | 4.461 | 4.4232 | 4.4176 | 4.3271 | 4.3357 | 4.373 | 4.3888 | 4.3488 | 4.3316 | 4.3831 | 4.3755 | 4.223 | 4.4038 | 4.3865 | 4.2277 | 4.2131 | 4.2517 | 4.3333 | 4.3539 | 4.2801 | 4.2673 | 4.3131 | 4.2322 | 4.303 | 4.3921 | 4.2719 | 4.2438 | 4.309 | 4.2708 | 4.3682 | 4.3843 | 4.1901 | 4.3307 | 4.3865 | 4.1988 | 4.3861 | 4.3933 | 4.3316 | 4.3735 | 4.1901 | 4.3319 | 4.3685 | 4.4157 | 4.3239 | 4.3466 | 4.3723 | 4.3874 | 4.3431 | 4.604 | 4.3526 | 4.3761 | 4.3969 | 4.3264 | 4.3165 | 4.3243 | 4.3517 | 4.3884 | 4.3659 | 4.3558 | 4.3436 | 4.285 | 4.3273 | 4.385 | 4.3742 | 4.3658 | 4.3577 | 4.3356 | 4.3813 | 4.394 | 4.3794 | 4.3401 | 4.3401 | 4.3221 | 4.3251 | 4.2805 | 4.3017 | 4.2385 | 4.3708 | 4.3655 | 4.3832 | 4.3858 | 2.864 | 4.3918 | 4.3831 | 4.3738 | 4.3539 | 4.3936 | 4.424 | 4.2236 | 4.3452 | 4.415 | 4.3772 | 4.2081 | 4.3888 | 4.3829 | 4.4007 | 4.3519 | 4.3472 | 4.3972 | 4.3154 | 4.206 | 4.1957 | 4.2467 | 4.268 | 4.403 | 4.4487 | 4.1155 | 4.0866 | 4.3236 | 4.3592 | 4.2547 | 4.3221 | 4.2734 | 4.2184 | 4.2247 | 4.2116 | 4.2555 | 4.2655 | 4.3375 | 4.3014 | 4.2378 | 4.2857 | 4.2657 | 4.2416 | 4.2239 | 4.261 | 4.2216 | 4.2266 | 4.2545 | 4.2363 | 4.2562 | 4.2363 | 4.2272 | 4.2576 | 4.2199 | 4.2392 | 4.2064 | 4.271 | 4.2127 | 4.2363 | 4.2139 | 4.2903 | 4.2715 | 4.3216 | 4.2402 | 4.2525 | 4.2856 | 4.2185 | 4.2249 | 4.3145 | 4.2767 | 4.2788 | 4.2 | 4.2928 | 4.2633 | 4.2695 | 4.2044 | 4.2532 | 4.3004 | 4.2226 | 4.2519 | 4.2932 | 4.2466 | 4.2138 | 4.3189 | 4.2378 | 4.2226 | 4.2576 | 4.4211 | 4.2892 | 4.2673 | 4.3011 | 4.3033 | 4.356 | 4.2308 | 4.2883 | 4.3023 | 4.2466 | 4.3117 | 4.2845 | 4.2163 | 4.3459 | 4.258 |  |  | 0.00043975 | 4.238 | 4.2458 |  | 4.3681 | 4.3404 | 4.3861 | 4.2258 | 4.3861 | 4.3457 | 4.3734 | 4.4 | 4.3251 | 4.239 | 4.3116 | 4.3311 | 4.4018 | 4.4964 | 4.5862 | 4.5678 | 4.5517 | 4.3962 | 4.265 | 4.3424 | 4.489 | 4.4155 | 4.363 | 4.3834 | 4.5142 | 4.4425 | 4.3955 | 4.3246 | 4.2389 | 4.2828 | 4.2774 | 4.2705 | 4.2493 |  | 4.5896 | 4.2532 | 4.3363 | 4.2353 | 4.2409 |  |  | 4.6859 | 4.4773 | 5.1345 | 4.3551 | 4.3744 | 4.3234
2025-06-28 | 3.6273 | 3.6968 | 3.5996 | 3.6094 | 3.6923 | 3.6854 | 3.7101 | 3.7101 | 3.6642 | 3.6825 | 3.6285 | 3.7375 | 3.5184 | 3.5877 | 3.6828 | 3.6483 | 3.6618 | 3.6562 | 3.6384 | 3.6498 | 3.5622 | 3.5948 | 3.5481 | 3.6418 | 3.5768 | 3.6249 | 3.5029 | 3.5592 | 3.5918 | 3.5396 | 3.5659 | 3.4996 | 3.546 | 3.5905 | 3.6375 | 3.5129 | 3.6375 | 3.618 | 3.2622 | 3.6498 | 3.6554 | 3.6427 | 3.6375 | 3.6165 | 3.6 | 3.5835 | 3.5609 | 3.6247 | 3.584 | 3.4981 | 3.6375 | 3.6509 | 3.6395 | 3.6578 | 3.5367 | 3.6624 | 3.6741 | 3.2667 | 3.5845 | 3.6328 | 3.7142 | 3.5296 | 3.6914 | 3.7701 | 3.6664 | 3.5997 | 3.6515 | 3.6045 | 3.6464 | 3.6094 | 3.6217 | 3.6745 | 3.6307 | 3.5794 | 3.5712 | 3.5992 | 3.6311 | 3.6322 | 3.6453 | 3.6681 | 3.5873 | 3.6375 | 3.6674 | 3.6213 | 3.6712 | 3.6187 | 3.5813 | 3.664 | 3.6345 | 3.585 | 3.5847 | 3.5215 | 3.6 | 3.1985 | 3.6648 | 3.6506 | 0 | 3.6408 | 3.588 | 3.5738 | 3.6127 | 3.564 | 3.5933 | 3.5592 | 3.5655 | 3.6217 | 3.6078 | 3.5172 | 3.5202 | 3.6787 | 3.5678 | 3.5236 | 3.5219 | 3.5672 | 3.6213 | 3.5809 | 3.5504 | 3.5089 | 3.5619 | 3.5738 | 3.6225 | 3.3258 | 3.3458 | 3.5805 | 3.5243 | 3.5256 | 3.5805 | 3.5431 | 3.6288 | 3.5968 | 3.3089 | 3.6204 | 3.6716 | 3.6977 | 3.729 | 3.5647 | 3.7248 | 3.7073 | 3.6915 | 3.2813 | 3.6283 | 3.5495 | 3.6704 | 3.7134 | 3.5659 | 3.638 | 3.6105 | 3.6903 | 3.6145 | 3.6557 | 3.6536 | 3.5873 | 3.5762 | 3.5532 | 3.5419 | 3.5581 | 3.624 | 3.6985 | 3.6663 | 3.5625 | 3.6461 | 3.5152 | 3.537 | 3.5168 | 3.6394 | 3.5778 | 3.5712 | 3.5189 | 3.539 | 3.4909 | 3.5971 | 3.5251 | 3.5441 | 3.248 | 3.5966 | 3.6333 | 3.6932 | 3.6545 | 3.6074 | 3.6212 | 3.5385 | 3.5562 | 3.536 | 3.6727 | 3.5703 | 3.6418 | 3.5564 | 3.6 | 3.5015 | 3.2605 | 3.5811 | 3.6633 | 3.6333 | 3.6799 | 3.6208 | 3.5795 | 3.6159 | 3.5966 |  |  | 0 | 3.5787 | 3.5432 |  | 3.5338 | 3.6371 | 3.5805 | 3.5921 | 3.2127 | 3.6749 | 3.6191 | 3.6483 | 3.5461 | 3.5835 | 3.5517 | 3.5543 | 3.5372 | 3.8052 | 3.811 | 3.7662 | 3.767 | 3.6991 | 3.5676 | 3.543 | 3.6185 | 3.5868 | 3.5073 | 3.5111 | 3.6728 | 3.5765 | 3.5562 | 3.5892 | 3.6173 | 3.6515 | 3.5315 | 3.5488 | 3.5511 |  | 3.807 | 3.5563 | 3.607 | 3.4942 | 3.5431 |  |  | 3.7659 | 3.7461 | 4.2494 | 3.5264 | 3.6111 | 3.5984
2025-06-29 | 3.1564 | 3.2221 | 3.2285 | 3.2172 | 3.2083 | 3.2097 | 3.2247 | 3.236 | 3.2072 | 3.2216 | 3.206 | 3.1453 | 3.1423 | 3.2972 | 3.2172 | 3.188 | 3.191 | 3.1873 | 3.1979 | 3.2083 | 3.1798 | 3.2285 | 3.1392 | 3.226 | 3.115 | 3.2118 | 3.1184 | 3.1893 | 3.216 | 3.1434 | 3.1694 | 3.0535 | 3.1486 | 3.2049 | 3.1798 | 3.2051 | 3.206 | 3.1049 | 3.161 | 3.221 | 3.1311 | 3.124 | 3.1685 | 3.0682 | 3.1948 | 3.206 | 3.115 | 3.1685 | 3.1712 | 3.0964 | 3.1835 | 3.1985 | 3.2393 | 3.1993 | 3.1623 | 3.1777 | 3.2 | 3.1712 | 3.196 | 3.1074 | 3.206 | 3.2519 | 3.2397 | 3.2936 | 3.191 | 3.1772 | 3.2083 | 3.0908 | 3.1648 | 3.176 | 3.191 | 3.1386 | 3.1423 | 3.1723 | 3.2127 | 3.1727 | 3.2193 | 3.1798 | 3.1648 | 3.2152 | 3.1985 | 3.221 | 3.1685 | 3.191 | 3.1386 | 3.176 | 3.1461 | 3.1573 | 3.1453 | 3.1243 | 3.1612 | 3.115 | 3.2135 | 3.1131 | 3.1561 | 3.161 | 0 | 3.1723 | 3.191 | 3.1423 | 3.1199 | 3.2022 | 3.1311 | 3.191 | 3.2127 | 3.1498 | 3.2726 | 3.187 | 3.1573 | 3.186 | 3.1841 | 3.1841 | 3.1104 | 3.0885 | 3.221 | 3.1341 | 3.1623 | 3.0995 | 3.166 | 3.1948 | 3.1262 | 2.9929 | 2.9397 | 3.1985 | 3.1041 | 3.1893 | 3.1172 | 3.1449 | 3.1045 | 3.1817 | 3.1208 | 3.1689 | 3.1896 | 3.1297 | 3.1434 | 3.1479 | 3.1217 | 3.1573 | 3.1317 | 3.2247 | 3.1775 | 3.1288 | 3.1685 | 3.257 | 3.1127 | 3.1997 | 3.1764 | 3.2196 | 3.1841 | 3.2643 | 3.2294 | 3.2397 | 3.1667 | 3.1648 | 3.1921 | 3.1491 | 3.206 | 3.2629 | 3.2121 | 3.1364 | 3.1785 | 3.0985 | 3.1481 | 3.1044 | 3.2054 | 3.16 | 3.1288 | 3.0168 | 3.1644 | 3.0953 | 3.1418 | 3.1487 | 3.1616 | 2.9818 | 3.1303 | 3.1591 | 3.2045 | 3.1212 | 3.1178 | 3.2008 | 3.1913 | 3.1347 | 3.1212 | 3.1709 | 3.1213 | 3.2054 | 3.168 | 3.148 | 3.1425 | 3.1538 | 3.1098 | 3.1598 | 3.192 | 3.1629 | 3.1591 | 3.1402 | 3.1318 | 3.1174 |  |  | 0 | 3.1573 | 3.1633 |  | 3.1664 | 3.1798 | 3.1674 | 3.1449 | 3.1494 | 3.1599 | 3.1311 | 3.1787 | 3.1449 | 3.1704 | 3.191 | 3.1169 | 3.1997 | 3.3325 | 3.3686 | 3.3094 | 3.2863 | 3.348 | 3.1025 | 3.1276 | 3.1101 | 3.1893 | 3.115 | 3.1115 | 3.2288 | 3.229 | 3.1794 | 3.1208 | 3.1119 | 3.1241 | 3.143 | 3.1511 | 3.1604 |  | 3.315 | 3.1682 | 3.204 | 3.1238 | 3.1197 |  |  | 3.2936 | 3.3346 | 3.6715 | 3.143 | 3.1497 | 3.1726
2025-06-30 | 2.5549 | 2.5307 | 2.5356 | 2.5206 | 2.5169 | 2.5243 | 2.5356 | 2.5431 | 2.5204 | 2.5312 | 2.588 | 2.5693 | 2.5506 | 2.5904 | 2.5243 | 2.5206 | 2.5094 | 2.4944 | 2.5238 | 2.5134 | 2.5243 | 2.5318 | 2.5203 | 2.5402 | 2.5341 | 2.5099 | 2.5411 | 2.5135 | 2.5235 | 2.5335 | 2.5268 | 2.5069 | 2.5511 | 2.5826 | 2.4794 | 2.4891 | 2.5206 | 2.4869 | 2.4419 | 2.5169 | 2.5206 | 2.4569 | 2.573 | 2.5318 | 2.5618 | 2.5206 | 2.3578 | 2.5311 | 2.3766 | 2.3694 | 2.4869 | 2.5393 | 2.5002 | 2.5435 | 2.4996 | 2.5402 | 2.5468 | 2.5468 | 2.5169 | 2.5501 | 2.5094 | 2.5694 | 2.5206 | 2.6082 | 2.5134 | 2.503 | 2.5169 | 2.5376 | 2.4794 | 2.4869 | 2.5243 | 2.5131 | 2.5581 | 2.5431 | 2.5561 | 2.5002 | 2.5368 | 2.5056 | 2.527 | 2.5272 | 2.5019 | 2.5206 | 2.4831 | 2.5056 | 2.5243 | 2.4532 | 2.5506 | 2.4532 | 2.4569 | 2.4944 | 2.4493 | 2.4996 | 2.4981 | 2.3745 | 2.5169 | 2.4794 | 0.1779 | 2.5318 | 2.5581 | 2.5169 | 2.4637 | 2.5644 | 2.464 | 2.4981 | 2.5135 | 2.427 | 2.5412 | 2.4724 | 2.5131 | 2.5169 | 2.5134 | 2.5687 | 2.5169 | 2.5235 | 2.5169 | 2.5206 | 2.5159 | 2.437 | 2.5135 | 2.5206 | 2.4517 | 2.3571 | 2.4203 | 2.5019 | 2.5056 | 2.5102 | 2.5243 | 2.5618 | 2.4003 | 2.5668 | 2.5549 | 2.5756 | 2.5549 | 2.5005 | 2.5245 | 2.521 | 2.486 | 2.549 | 2.5276 | 2.5543 | 2.4844 | 2.4719 | 2.5581 | 2.4512 | 2.5543 | 2.4588 | 2.491 | 2.5303 | 2.5549 | 2.5376 | 2.5545 | 2.5401 | 2.5342 | 2.5442 | 2.5045 | 2.5618 | 2.5094 | 2.5655 | 2.5038 | 2.5367 | 2.4815 | 2.4583 | 2.5387 | 2.4478 | 2.4613 | 2.4582 | 2.553 | 2.3603 | 2.4659 | 2.4764 | 2.5382 | 2.4691 | 2.4882 | 2.4291 | 2.4882 | 2.472 | 2.4773 | 2.4803 | 2.4377 | 2.4659 | 2.5315 | 2.4613 | 2.4377 | 2.4469 | 2.486 | 2.4781 | 2.5164 | 2.5236 | 2.3455 | 2.451 | 2.4879 | 2.4432 | 2.4848 | 2.4697 | 2.4811 | 2.4939 | 2.4727 | 2.5 |  |  | 0 | 2.4355 | 2.4242 |  | 2.488 | 2.5543 | 2.4464 | 2.4494 | 2.5655 | 2.4981 | 2.5019 | 2.4648 | 2.5094 | 2.4588 | 2.4906 | 2.4757 | 2.5268 | 2.5768 | 2.6288 | 2.5661 | 2.581 | 2.5956 | 2.4242 | 2.4812 | 2.5312 | 2.5335 | 2.5307 | 2.4927 | 2.5636 | 2.5549 | 2.5268 | 2.5135 | 2.4825 | 2.4387 | 2.4981 | 2.4916 | 2.4727 |  | 2.6436 | 2.4695 | 2.5075 | 2.4729 | 2.4631 |  |  | 2.6708 | 2.6567 | 2.972 | 2.4709 | 2.4917 | 2.5
2025-07-01 | 2.0342 | 2.0709 | 2.0757 | 2.0652 | 2.0646 | 2.0629 | 2.0734 | 2.0794 | 1.8013 | 1.9524 | 2.1202 | 2.1064 | 1.9783 | 2.1263 | 2.0704 | 2.0712 | 2.0506 | 2.0427 | 2.0709 | 2.0674 | 2.0734 | 2.0861 | 2.0304 | 2.1047 | 2.093 | 2.0785 | 2.066 | 2.0737 | 2.0954 | 2.0058 | 2.0481 | 2.0375 | 2.0346 | 2.0625 | 2.039 | 1.9739 | 2.0075 | 1.9517 | 1.9925 | 2.0105 | 1.97 | 1.9813 | 2.0127 | 2.012 | 2.027 | 1.9764 | 1.981 | 2.0195 | 2.0189 | 1.975 | 2.0315 | 2.0517 | 1.9742 | 1.9842 | 1.9741 | 1.9842 | 1.8017 | 2.0187 | 1.9576 | 1.9642 | 1.9775 | 1.9739 | 2 | 2.0869 | 2.0263 | 2.019 | 2.019 | 1.9672 | 1.9933 | 2.0075 | 2.0094 | 1.9581 | 1.9816 | 2.0273 | 1.9942 | 1.9576 | 1.9642 | 2 | 2.0015 | 1.9602 | 1.9813 | 1.9633 | 2.0221 | 1.9955 | 1.9659 | 1.9596 | 1.9622 | 1.9936 | 1.9888 | 1.97 | 1.9631 | 1.9433 | 2.0075 | 1.9588 | 1.9988 | 1.9929 | 1.7603 | 1.9513 | 2.0187 | 2.0326 | 1.9925 | 2.015 | 1.9963 | 2.0251 | 2.0335 | 1.9596 | 2.0008 | 2.0013 | 1.9625 | 2.0115 | 2.0055 | 2.0097 | 1.9642 | 1.9742 | 1.9888 | 1.9625 | 1.9471 | 1.9542 | 2.0072 | 1.9948 | 2.0172 | 1.8524 | 1.9126 | 1.9989 | 2.0052 | 1.9609 | 1.9625 | 2.006 | 1.9559 | 2.0042 | 1.9775 | 2.0304 | 1.9602 | 1.9612 | 2 | 1.965 | 1.9685 | 1.986 | 2.0128 | 2.0187 | 2.0443 | 2.0353 | 1.9906 | 1.9872 | 1.9588 | 2.0121 | 2.0427 | 1.761 | 2.0432 | 2.0398 | 1.9983 | 1.9813 | 2.0461 | 1.9813 | 2.0037 | 2.0251 | 1.9625 | 2.0176 | 2.0038 | 2.0227 | 1.9865 | 1.9682 | 2.0333 | 1.7879 | 1.9562 | 2.0105 | 2.028 | 1.7811 | 2.0182 | 1.9829 | 1.9902 | 1.9996 | 1.9906 | 1.9855 | 1.963 | 1.8644 | 1.9848 | 1.983 | 1.9953 | 1.9659 | 1.9916 | 1.9461 | 1.9865 | 1.9964 | 2.0252 | 1.963 | 1.9818 | 1.9564 | 2.0036 | 1.7308 | 2.0038 | 2.0341 | 1.9962 | 1.9886 | 1.9462 | 1.9924 | 1.9795 | 1.9712 |  |  | 0 | 2.0026 | 1.9623 |  | 1.9515 | 2 | 1.9738 | 2.0075 | 2.0075 | 1.9745 | 1.8165 | 2.0202 | 1.9581 | 1.9993 | 1.9749 | 2.0243 | 1.9642 | 2.0558 | 2.1137 | 2.0197 | 2.0376 | 2.0903 | 1.9865 | 1.9754 | 2.0077 | 1.9892 | 1.9651 | 1.981 | 2.0297 | 1.9862 | 1.9895 | 1.9506 | 1.993 | 1.9885 | 2.0513 | 2.0127 | 2.0081 |  | 2.0776 | 1.9575 | 1.9701 | 1.9641 | 1.9775 |  |  | 2.14 | 2.1082 | 2.3593 | 1.988 | 2.0191 | 1.9976
2025-07-02 | 3.229 | 3.2913 | 3.2846 | 3.2884 | 3.2498 | 3.2547 | 3.2809 | 3.2772 | 3.1101 | 3.2539 | 3.3558 | 3.3258 | 3.1348 | 3.3585 | 3.3034 | 3.2921 | 3.2996 | 3.2996 | 3.3258 | 3.3258 | 3.3408 | 3.3296 | 3.2394 | 3.3525 | 3.3328 | 3.312 | 3.2844 | 3.2926 | 3.2992 | 3.1527 | 3.1893 | 3.3159 | 3.1958 | 3.291 | 3.2846 | 3.2954 | 3.3184 | 3.2584 | 3.1685 | 3.2622 | 3.1685 | 3.1423 | 3.1985 | 3.2022 | 3.221 | 3.236 | 3.2221 | 3.2135 | 3.2108 | 3.1533 | 3.1873 | 3.2397 | 3.2892 | 3.2226 | 3.1599 | 3.2759 | 3.1827 | 2.9588 | 3.1827 | 3.2093 | 3.2172 | 3.2252 | 3 | 3.3354 | 3.2256 | 3.2498 | 3.2567 | 3.1322 | 3.2397 | 3.2547 | 3.2509 | 3.1798 | 3.1423 | 3.176 | 3.1927 | 3.1527 | 3.1094 | 3.191 | 3.2397 | 3.1426 | 3.1311 | 3.2322 | 3.2397 | 3.2322 | 3.1498 | 3.1835 | 3.1498 | 3.2022 | 3.1423 | 3.1629 | 3.1676 | 3.115 | 3.0412 | 3.191 | 3.1893 | 3.2397 | 2.9513 | 3.1948 | 3.1685 | 3.1948 | 3.191 | 3.2285 | 3.1536 | 3.1985 | 3.206 | 2.9139 | 3.2193 | 3.175 | 3.2772 | 3.2559 | 3.2671 | 3.2325 | 3.2559 | 3.2593 | 3.2921 | 3.1573 | 3.1683 | 3.1361 | 3.2193 | 3.2434 | 3.2884 | 3.0129 | 3.0928 | 3.2472 | 3.2659 | 3.1594 | 3.1798 | 3.1573 | 3.2093 | 3.1261 | 3.1219 | 3.274 | 3.1945 | 3.2605 | 3.1538 | 3.1364 | 3.1573 | 3.2098 | 3.2503 | 3.2097 | 3.3016 | 3.2429 | 3.1798 | 3.191 | 3.1648 | 3.2774 | 3.1873 | 3.24 | 3.2636 | 3.2947 | 3.2671 | 3.2247 | 3.2326 | 3.1985 | 3.1723 | 3.1536 | 3.1648 | 3.2697 | 3.2235 | 3.2235 | 3.229 | 3.1818 | 3.1987 | 3.1448 | 3.1987 | 3.1673 | 3.2045 | 3.2694 | 3.1477 | 3.2218 | 3.2618 | 3.2073 | 3.2492 | 3.2255 | 3.0337 | 3.1591 | 3.2462 | 3.1477 | 3.1751 | 3.2235 | 3.1713 | 3.1818 | 3.2054 | 3.1927 | 3.2797 | 3.2727 | 3.1709 | 3.2255 | 3.1527 | 3.1853 | 3.178 | 3.1432 | 2.8674 | 3.1477 | 3.1477 | 3.0568 | 3.1909 | 3.1553 |  |  | 1.7898 | 3.1994 | 3.2114 |  | 3.2023 | 3.1685 | 3.1873 | 3.1498 | 3.1985 | 3.1536 | 3.1798 | 3.2547 | 3.176 | 3.1985 | 3.1873 | 3.2434 | 3.2226 | 3.2093 | 3.3453 | 3.408 | 3.302 | 3.3292 | 3.2035 | 3.1485 | 3.1748 | 3.1993 | 3.1461 | 3.1703 | 3.2431 | 3.1426 | 3.2027 | 3.1427 | 3.1818 | 3.1566 | 3.143 | 3.2061 | 3.196 |  | 3.3994 | 3.2079 | 3.194 | 3.2061 | 3.1702 |  |  | 3.348 | 3.3738 | 3.7497 | 3.143 | 3.1965 | 3.2055
2025-07-03 | 3.5817 | 3.6612 | 3.6629 | 3.6517 | 3.6439 | 3.6442 | 3.5805 | 3.5618 | 3.4661 | 3.6566 | 3.603 | 3.5768 | 3.5019 | 3.6364 | 3.6554 | 3.6442 | 3.6255 | 3.6217 | 3.6404 | 3.6404 | 3.6629 | 3.6629 | 3.5678 | 3.6821 | 3.6716 | 3.637 | 3.6128 | 3.6221 | 3.6321 | 3.4623 | 3.4823 | 3.499 | 3.5456 | 3.6557 | 3.5843 | 3.5597 | 3.4794 | 3.4757 | 3.4944 | 3.6105 | 3.5056 | 3.4963 | 3.5206 | 3.5393 | 3.5618 | 3.5843 | 3.592 | 3.573 | 3.5524 | 3.4912 | 3.5618 | 3.6067 | 3.6821 | 3.6088 | 3.471 | 3.5988 | 3.5389 | 3.5543 | 3.6355 | 3.6821 | 3.6217 | 3.553 | 3.573 | 3.7659 | 3.5678 | 3.6093 | 3.6197 | 3.4849 | 3.573 | 3.6067 | 3.5955 | 3.5056 | 3.633 | 3.5618 | 3.5422 | 3.5789 | 3.5988 | 3.5543 | 3.573 | 3.6128 | 3.6367 | 3.5318 | 3.603 | 3.5581 | 3.4831 | 3.5281 | 3.4719 | 3.5393 | 3.4944 | 3.4794 | 3.4912 | 3.4918 | 3.6105 | 3.5019 | 3.6188 | 3.5993 | 3.4944 | 3.5693 | 3.5843 | 3.5543 | 3.5993 | 3.5843 | 3.5468 | 3.5431 | 3.5522 | 3.5618 | 3.6088 | 3.462 | 3.6255 | 3.6355 | 3.6232 | 3.5402 | 3.4757 | 3.5123 | 3.5393 | 3.4794 | 3.4861 | 3.4757 | 3.6388 | 3.6255 | 3.6592 | 3.3791 | 3.4524 | 3.5843 | 3.6105 | 3.5089 | 3.4944 | 3.5318 | 3.5296 | 3.5645 | 3.5367 | 3.5685 | 3.5962 | 3.5015 | 3.5 | 3.5409 | 3.4755 | 3.5944 | 3.5452 | 3.5655 | 3.4883 | 3.5388 | 3.5903 | 3.5678 | 3.4667 | 3.5907 | 3.6 | 3.3544 | 3.534 | 3.5748 | 3.5644 | 3.5693 | 3.5689 | 3.5843 | 3.5618 | 3.5318 | 3.5431 | 3.5169 | 3.572 | 3.5152 | 3.5185 | 3.5379 | 3.5556 | 3.1616 | 3.5724 | 3.5091 | 3.0227 | 3.0236 | 3.4962 | 3.5236 | 3.5927 | 3.5164 | 3.5185 | 3.4873 | 3.4781 | 3.4962 | 3.4811 | 3.4811 | 3.4815 | 3.5 | 3.5315 | 3.4815 | 3.4714 | 3.5964 | 3.4895 | 3.4781 | 3.5418 | 3.5091 | 3.6 | 3.4825 | 3.5303 | 3.5379 | 3.5379 | 3.5114 | 3.5417 | 3.5795 | 3.6045 | 3.5833 |  |  | 3.8127 | 3.6091 | 3.5661 |  | 3.5373 | 3.4981 | 3.4869 | 3.4869 | 3.5431 | 3.5993 | 3.5805 | 3.5693 | 3.6105 | 3.5019 | 3.6105 | 3.5655 | 3.4923 | 3.6188 | 3.7215 | 3.6946 | 3.6625 | 3.6991 | 3.5017 | 3.5655 | 3.6674 | 3.5489 | 3.5678 | 3.5851 | 3.6027 | 3.5436 | 3.5456 | 3.6122 | 3.5004 | 3.5354 | 3.5004 | 3.4979 | 3.4909 |  | 3.6853 | 3.497 | 3.5423 | 3.4942 | 3.5004 |  |  | 3.6573 | 3.7461 | 4.1017 | 3.4848 | 3.4909 | 3.5575
2025-07-04 | 3.2982 | 3.3224 | 3.2809 | 3.3258 | 3.2982 | 3.2996 | 3.3146 | 3.3071 | 3.2036 | 3.2396 | 3.2659 | 3.2772 | 3.2783 | 3.2727 | 3.221 | 3.2434 | 3.2921 | 3.3333 | 3.2913 | 3.2809 | 3.3034 | 3.2734 | 3.3362 | 3.3691 | 3.3397 | 3.3812 | 3.357 | 3.2959 | 3.3678 | 3.2236 | 3.3025 | 3.3159 | 3.2606 | 3.291 | 3.2169 | 3.1927 | 3 | 3.2622 | 3.1876 | 3.3116 | 3.2472 | 3.2809 | 3.1925 | 3.2056 | 3.2442 | 3.2828 | 3.3006 | 3.2689 | 3.2723 | 3.2252 | 3.3157 | 3.33 | 3.3059 | 3.3268 | 3.2277 | 3.2959 | 3.1827 | 3.2172 | 3.3535 | 3.3125 | 3.2996 | 3.2285 | 3.206 | 3.419 | 3.2882 | 3.2712 | 3.3051 | 3.1948 | 3.2184 | 3.2487 | 3.2667 | 3.2019 | 3.2831 | 3.2491 | 3.2246 | 3.1594 | 3.2413 | 3.2322 | 3.2041 | 3.2411 | 3.279 | 3.2247 | 3.2528 | 3.2049 | 3.1554 | 3.2056 | 3.1629 | 3.2491 | 3.206 | 3.1985 | 3.2683 | 3.153 | 3.2768 | 3.1985 | 3.2127 | 3.2165 | 3.176 | 3.3026 | 3.2521 | 3.2622 | 3.3052 | 3.2431 | 3.2723 | 3.2157 | 3.189 | 3.1873 | 3.2539 | 3.1716 | 3.2266 | 3.1893 | 3.164 | 3.2709 | 3.2692 | 3.2786 | 3.2828 | 3.1648 | 3.1549 | 3.1727 | 3.2326 | 3.1884 | 3.2277 | 2.9413 | 3.0578 | 3.1517 | 3.1697 | 3.2153 | 3.03 | 3.1873 | 3.1467 | 3.1278 | 3.0548 | 3.1907 | 3.228 | 3.2605 | 3.2308 | 3.2217 | 3.1503 | 3.2657 | 3.2396 | 3.2798 | 3.2138 | 3.1782 | 3.2873 | 3.2602 | 3.1704 | 3.2277 | 3.1948 | 3.2462 | 3.1796 | 3.2363 | 3.2636 | 3.2367 | 3.2033 | 3.2491 | 3.2015 | 3.1704 | 3.2041 | 3.1723 | 3.2235 | 3.2159 | 3.2357 | 3.2326 | 3.2569 | 3.1801 | 3.3949 | 3.2167 | 3.2008 | 3.2431 | 3.2617 | 3.2476 | 3.2564 | 3.2316 | 3.229 | 3.3422 | 3.1481 | 3.197 | 3.1886 | 3.2235 | 3.1461 | 3.1761 | 3.2587 | 3.2121 | 3.2259 | 3.1527 | 3.2661 | 3.2556 | 3.2625 | 3.2284 | 3.2364 | 3.1888 | 3.1894 | 3.1856 | 3.1742 | 3.2008 | 3.1678 | 3.1894 | 3.2659 | 3.1879 |  |  | 3.3615 | 3.1994 | 3.1892 |  | 3.1921 | 3.1648 | 3.1798 | 3.2022 | 3.206 | 3.1873 | 3.1723 | 3.2464 | 3.2127 | 3.2247 | 3.2352 | 3.3131 | 3.2027 | 3.1827 | 3.408 | 3.3632 | 3.4169 | 3.4734 | 3.2275 | 3.1864 | 3.2802 | 3.2499 | 3.1841 | 3.2325 | 3.3158 | 3.1997 | 3.238 | 3.2127 | 3.1974 | 3.2143 | 3.2789 | 3.251 | 3.2727 |  | 3.3428 | 3.2776 | 3.194 | 3.1949 | 3.2401 |  |  | 3.348 | 3.4404 | 3.8584 | 3.1974 | 3.2753 | 3.2413
2025-07-05 | 3.9761 | 4.0474 | 4.0348 | 4.0184 | 4.0149 | 4.0071 | 4.0187 | 4.0356 | 3.726 | 4.0266 | 4.0745 | 4.0644 | 3.9288 | 4.1397 | 4.0228 | 4.0217 | 3.9213 | 3.9217 | 3.9326 | 3.9416 | 4.0094 | 4.0461 | 3.9557 | 4.0599 | 3.9879 | 3.9789 | 3.9751 | 4.0027 | 4.0057 | 3.8702 | 3.98 | 4.0077 | 3.9104 | 4.0472 | 3.8678 | 3.8381 | 3.8202 | 3.8315 | 3.8022 | 3.7903 | 3.8427 | 3.7903 | 3.827 | 3.8757 | 3.9 | 3.9536 | 3.9513 | 3.897 | 3.9723 | 3.9198 | 3.9783 | 4.0049 | 4.0836 | 3.97 | 3.917 | 4.0879 | 3.702 | 4.0352 | 3.976 | 4.024 | 3.9543 | 4.0378 | 3.9903 | 4.1379 | 4.0484 | 4.0657 | 4.0622 | 4.0415 | 3.9176 | 3.9476 | 3.9288 | 3.9064 | 3.9288 | 4.0824 | 3.985 | 3.9717 | 4.0682 | 4.0824 | 4.0861 | 4.0933 | 4.0375 | 4.1236 | 4.0562 | 4.0562 | 4.0109 | 4.0742 | 4.0221 | 4.0262 | 3.9213 | 3.9064 | 4.1 | 3.8755 | 4.1742 | 4.1232 | 4.0982 | 4.1659 | 3.9775 | 4.2281 | 4.1566 | 4.1772 | 4.2431 | 4.173 | 4.23 | 4.1742 | 4.1199 | 4.1199 | 4.238 | 4.2004 | 4.127 | 4.1685 | 4.1483 | 4.1269 | 4.1515 | 4.1481 | 4.194 | 3.9813 | 3.9946 | 4.0087 | 4.1774 | 4.1918 | 4.1708 | 3.8921 | 4.0393 | 4.0854 | 4.118 | 4.2181 | 3.824 | 3.779 | 3.7813 | 3.7786 | 3.796 | 3.7991 | 3.8479 | 3.8161 | 3.8287 | 3.8881 | 3.8357 | 3.9325 | 3.8508 | 3.8315 | 3.8182 | 3.8686 | 3.8742 | 3.8064 | 3.7865 | 3.8513 | 3.8491 | 3.8039 | 3.8237 | 3.8375 | 3.8064 | 3.8689 | 3.8705 | 3.8652 | 3.8315 | 3.8749 | 3.8165 | 3.8449 | 4.0182 | 3.9375 | 3.9475 | 3.9167 | 3.9226 | 3.9428 | 4.0098 | 3.9055 | 4 | 3.9764 | 4.0038 | 3.9087 | 3.9055 | 3.9345 | 3.9596 | 3.9989 | 3.8485 | 3.8485 | 3.9205 | 3.9129 | 3.9226 | 4.0417 | 3.958 | 3.9461 | 3.9529 | 4.1305 | 3.9182 | 3.9327 | 3.9691 | 3.9127 | 3.72 | 3.6538 | 4.0277 | 4.1364 | 4.0341 | 3.9583 | 4.1322 | 3.9583 | 4.1655 | 4.1311 |  |  | 4.2339 | 4.0137 | 3.9431 |  | 3.961 | 3.9438 | 3.9588 | 4.0453 | 4.0895 | 4.1292 | 4.1135 | 4.2573 | 4.1749 | 4.0247 | 4.1562 | 4.2101 | 3.9451 | 4.2454 | 4.2812 | 4.2947 | 4.2894 | 4.2759 | 4.1135 | 4.2131 | 4.2783 | 4.3253 | 4.3053 | 4.2337 | 4.3182 | 4.3267 | 4.2903 | 4.304 | 4.1123 | 4.1739 | 4.0571 | 4.122 | 4.122 |  | 4.2471 | 4.0669 | 4.0697 | 4.1182 | 4.1445 |  |  | 4.1964 | 4.1693 | 4.7925 | 3.9316 | 3.92 | 4.0131
2025-07-06 | 3.4271 | 3.5004 | 3.5075 | 3.5045 | 3.4697 | 3.4644 | 3.4929 | 3.5026 | 3.4596 | 3.4801 | 3.5169 | 3.5442 | 3.5094 | 3.5698 | 3.4772 | 3.4581 | 3.4667 | 3.4577 | 3.4669 | 3.4672 | 3.485 | 3.4813 | 3.4261 | 3.499 | 3.5015 | 3.4707 | 3.4462 | 3.4606 | 3.484 | 3.4497 | 3.4474 | 3.4797 | 3.467 | 3.5032 | 3.4348 | 3.4085 | 3.4674 | 3.4157 | 3.4045 | 3.4213 | 3.427 | 3.4494 | 3.4419 | 3.4794 | 3.4607 | 3.4064 | 3.4261 | 3.4644 | 3.4373 | 3.4409 | 3.4644 | 3.4356 | 3.5233 | 3.4184 | 3.4261 | 3.4966 | 3.5236 | 3.5281 | 3.4816 | 3.5233 | 3.4356 | 3.5309 | 3.4532 | 3.4734 | 3.5685 | 3.5592 | 3.5872 | 3.507 | 3.4543 | 3.5292 | 3.5573 | 3.512 | 3.5506 | 3.5614 | 3.5982 | 3.5313 | 3.6175 | 3.5547 | 3.476 | 3.5239 | 3.4494 | 3.5843 | 3.4839 | 3.4266 | 3.4682 | 3.4906 | 3.5199 | 3.4921 | 3.5206 | 3.4828 | 3.5171 | 3.5388 | 3.6067 | 3.5318 | 3.5246 | 3.5333 | 3.406 | 3.6127 | 3.5865 | 3.5169 | 3.4869 | 3.4906 | 3.5393 | 3.5873 | 3.5799 | 3.412 | 3.5722 | 3.5982 | 3.5581 | 3.5775 | 3.5526 | 3.5734 | 3.5942 | 3.5845 | 3.5779 | 3.4569 | 3.4292 | 3.4324 | 3.5835 | 3.5543 | 3.5603 | 3.3814 | 3.4514 | 3.4689 | 3.5154 | 3.5323 | 3.4419 | 3.4644 | 3.455 | 3.4727 | 3.4261 | 3.5333 | 3.5056 | 3.5869 | 3.5524 | 3.45 | 3.4301 | 3.5804 | 3.5596 | 3.5618 | 3.5156 | 3.4876 | 3.5955 | 3.5678 | 3.5139 | 3.5264 | 3.4981 | 3.5587 | 3.4192 | 3.5229 | 3.5678 | 3.573 | 3.5968 | 3.5918 | 3.5813 | 3.567 | 3.5854 | 3.5112 | 3.5023 | 3.4341 | 3.4414 | 3.5038 | 3.4377 | 3.4714 | 3.5226 | 3.4291 | 3.5795 | 3.4646 | 3.408 | 3.4364 | 3.4145 | 3.4582 | 3.4717 | 3.4673 | 3.4646 | 3.5568 | 3.4924 | 3.4659 | 3.4377 | 3.5076 | 3.528 | 3.4074 | 3.4646 | 3.5564 | 3.514 | 3.4646 | 3.4684 | 3.488 | 3.4807 | 3.5385 | 3.5265 | 3.5492 | 3.2235 | 3.5038 | 3.5682 | 3.5114 | 3.4891 | 3.4814 |  |  | 3.6851 | 3.4148 | 3.4701 |  | 3.5338 | 3.4551 | 3.4607 | 3.4341 | 3.4536 | 3.5345 | 3.4768 | 3.5169 | 3.5356 | 3.4569 | 3.5124 | 3.5243 | 3.459 | 3.6588 | 3.7573 | 3.7707 | 3.7461 | 3.7367 | 3.4392 | 3.4979 | 3.6164 | 3.499 | 3.5634 | 3.5108 | 3.5596 | 3.5298 | 3.5862 | 3.5389 | 3.5004 | 3.4401 | 3.5392 | 3.453 | 3.4222 |  | 3.5395 | 3.5145 | 3.4925 | 3.453 | 3.4106 |  |  | 3.6071 | 3.6481 | 4.106 | 3.5004 | 3.4453 | 3.5069
2025-07-07 | 3.5644 | 3.5333 | 3.5693 | 3.5543 | 3.5748 | 3.5169 | 3.5356 | 3.5468 | 3.5596 | 3.5596 | 3.5843 | 3.5993 | 3.5131 | 3.6241 | 3.5131 | 3.5243 | 3.5131 | 3.5094 | 3.5367 | 3.5298 | 3.5243 | 3.5356 | 3.478 | 3.5422 | 3.5402 | 3.5367 | 3.4952 | 3.5089 | 3.5156 | 3.5023 | 3.489 | 3.5256 | 3.5079 | 3.5899 | 3.4783 | 3.4828 | 3.5603 | 3.5243 | 3.5768 | 3.5161 | 3.5243 | 3.573 | 3.5618 | 3.5169 | 3.5431 | 3.5543 | 3.4921 | 3.4951 | 3.5128 | 3.4912 | 3.5506 | 3.5232 | 3.5988 | 3.5053 | 3.5298 | 3.5988 | 3.5622 | 3.5618 | 3.5123 | 3.5456 | 3.53 | 3.5497 | 3.5019 | 3.6238 | 3.6287 | 3.6076 | 3.6532 | 3.5768 | 3.5903 | 3.5835 | 3.6176 | 3.6011 | 3.6438 | 3.6045 | 3.5779 | 3.5086 | 3.6108 | 3.5558 | 3.4936 | 3.618 | 3.5056 | 3.6251 | 3.5071 | 3.5356 | 3.5543 | 3.5805 | 3.5588 | 3.5753 | 3.5794 | 3.5652 | 3.5844 | 3.6142 | 3.5618 | 3.573 | 3.5962 | 3.5622 | 3.5588 | 3.6419 | 3.5936 | 3.6075 | 3.5693 | 3.5981 | 3.5618 | 3.5888 | 3.5559 | 3.5805 | 3.6288 | 3.4928 | 3.5412 | 3.5769 | 3.5398 | 3.6038 | 3.6484 | 3.6158 | 3.5996 | 3.5858 | 3.5028 | 3.5323 | 3.5898 | 3.5472 | 3.5367 | 3.5056 | 3.5782 | 3.6386 | 3.4835 | 3.6518 | 3.5768 | 3.5169 | 3.5123 | 3.499 | 3.4987 | 3.545 | 3.5364 | 3.6184 | 3.5664 | 3.5315 | 3.5283 | 3.6451 | 3.6315 | 3.6521 | 3.5402 | 3.4952 | 3.5772 | 3.6411 | 3.4981 | 3.5789 | 3.5745 | 3.6282 | 3.5678 | 3.6304 | 3.6615 | 3.6412 | 3.5259 | 3.6438 | 3.5831 | 3.5479 | 3.5243 | 3.488 | 3.5951 | 3.5364 | 3.5094 | 3.5568 | 3.5185 | 3.5421 | 3.5953 | 3.6436 | 3.572 | 3.5017 | 3.5106 | 3.5167 | 3.5382 | 3.4858 | 3.6313 | 3.6029 | 3.5185 | 3.5379 | 3.5644 | 3.6212 | 3.5387 | 3.6061 | 3.6503 | 3.532 | 3.4882 | 3.6356 | 3.5769 | 3.5152 | 3.5033 | 3.5789 | 3.5902 | 3.5524 | 3.5682 | 3.5303 | 3.5568 | 3.6136 | 3.5303 | 3.5455 | 3.55 | 3.5379 |  |  | 3.606 | 3.5724 | 3.5255 |  | 3.5065 | 3.5805 | 3.4981 | 3.5543 | 3.5019 | 3.512 | 3.4944 | 3.6131 | 3.5056 | 3.5019 | 3.6573 | 3.6195 | 3.6654 | 3.699 | 3.8245 | 3.8276 | 3.8438 | 3.768 | 3.5305 | 3.5471 | 3.6315 | 3.6318 | 3.6252 | 3.5409 | 3.7972 | 3.5298 | 3.6215 | 3.5898 | 3.5431 | 3.5703 | 3.5859 | 3.5092 | 3.6404 |  | 3.6824 | 3.5563 | 3.6119 | 3.5017 | 3.5058 |  |  | 3.7074 | 3.6834 | 4.1538 | 3.5315 | 3.5021 | 3.5694
2025-07-08 | 4.9196 | 4.9888 | 4.9551 | 5.015 | 4.9542 | 4.9026 | 4.9135 | 4.8315 | 4.9978 | 5.0013 | 4.9963 | 4.9625 | 4.985 | 4.8825 | 4.97 | 4.9483 | 4.9401 | 4.9551 | 4.9162 | 4.9334 | 4.9064 | 4.8315 | 4.9127 | 4.9605 | 4.8055 | 4.7986 | 4.8055 | 4.824 | 4.8306 | 4.8073 | 4.7907 | 4.7774 | 4.8899 | 4.8513 | 4.8539 | 4.7665 | 4.9577 | 4.9476 | 4.9101 | 4.8596 | 4.8127 | 4.8539 | 4.8127 | 4.8318 | 4.7978 | 4.8146 | 4.8093 | 4.8315 | 4.818 | 4.7569 | 4.7978 | 4.8176 | 4.8406 | 4.803 | 4.7644 | 4.7973 | 4.7907 | 4.9101 | 4.8506 | 4.7973 | 4.9045 | 5.0371 | 4.7753 | 5.0199 | 4.8055 | 4.7848 | 4.8436 | 4.8643 | 4.8315 | 4.8502 | 4.8352 | 4.8464 | 4.9476 | 4.8315 | 4.8306 | 4.8509 | 4.7873 | 4.8202 | 4.8869 | 4.8401 | 4.7584 | 4.9101 | 4.8449 | 4.8352 | 4.7453 | 4.8539 | 4.8981 | 4.7978 | 4.9124 | 4.9169 | 4.8917 | 4.8436 | 4.9401 | 4.8277 | 4.9015 | 4.7978 | 4.8502 | 4.8315 | 4.8577 | 4.809 | 4.8427 | 4.8652 | 4.7865 | 4.8427 | 4.8566 | 4.8315 | 4.9305 | 4.8578 | 4.8674 | 4.9075 | 4.8449 | 4.9241 | 4.8979 | 4.9242 | 4.9494 | 4.9266 | 4.7909 | 4.7374 | 4.8882 | 4.87 | 4.8348 | 4.7341 | 4.8396 | 4.8577 | 4.7618 | 4.7374 | 4.8127 | 4.7472 | 4.7907 | 4.7873 | 4.7647 | 4.9203 | 4.9207 | 5.0378 | 4.9685 | 4.8566 | 4.7937 | 4.9266 | 4.9906 | 4.991 | 4.9248 | 4.7475 | 4.9869 | 4.9507 | 4.8551 | 4.9131 | 4.897 | 4.907 | 4.764 | 4.958 | 5.005 | 4.9723 | 4.826 | 4.973 | 4.9007 | 4.867 | 4.8315 | 4.9266 | 4.928 | 4.9822 | 4.9192 | 4.8121 | 4.7828 | 4.8848 | 5.0542 | 4.8167 | 4.8144 | 4.8428 | 4.9364 | 4.9145 | 4.8527 | 4.8695 | 4.9832 | 4.9767 | 4.9758 | 4.8174 | 4.7451 | 4.7955 | 4.7845 | 4.8333 | 4.7797 | 4.7609 | 4.7771 | 5.2036 | 4.8196 | 4.7737 | 4.9149 | 4.9127 | 4.8036 | 4.8601 | 4.7576 | 4.7917 | 4.7765 | 4.7955 | 4.7799 | 4.7689 | 4.8364 | 4.7955 |  |  | 5.0967 | 4.8385 | 4.7635 |  | 4.7881 | 4.7603 | 4.779 | 4.7865 | 4.7978 | 4.7865 | 4.7678 | 4.9682 | 4.7914 | 4.7978 | 4.7951 | 4.8352 | 4.764 | 5.0031 | 5.1545 | 5.1903 | 5.2153 | 5.1473 | 4.8148 | 4.8219 | 4.9729 | 4.9388 | 4.8985 | 4.8287 | 4.9978 | 4.9507 | 4.7907 | 4.7674 | 4.8757 | 4.7763 | 4.9534 | 4.9499 | 4.8081 |  | 5.0382 | 4.9425 | 4.8756 | 4.942 | 4.8796 |  |  | 5.0199 | 4.9804 | 5.6963 | 4.9534 | 4.9005 | 4.8754
2025-07-09 | 3.0984 | 3.1554 | 3.1727 | 3.0779 | 3.1526 | 3.1401 | 3.1124 | 3.1049 | 3.1551 | 3.1756 | 3.1348 | 3.0936 | 3.1693 | 3.191 | 3.1816 | 3.1311 | 3.1528 | 3.1652 | 3.1761 | 3.181 | 3.1199 | 3.1311 | 3.1737 | 3.1094 | 3.1737 | 3.1927 | 3.1755 | 3.1797 | 3.1817 | 3.169 | 3.1754 | 3.181 | 3.0542 | 3.1415 | 3.0434 | 3.1148 | 3.1236 | 3.1011 | 3.1049 | 3.0749 | 3.1199 | 3.1049 | 3.1498 | 3.0416 | 3.1348 | 3.1011 | 3.0977 | 3.1049 | 3.0598 | 3.0885 | 3.1348 | 3.1049 | 3.1727 | 3.0595 | 3.0804 | 3.1887 | 3.1061 | 3.1498 | 3.1461 | 3.1328 | 3.0757 | 3.2195 | 3.1273 | 3.2226 | 3.1689 | 3.1602 | 3.1945 | 3.125 | 3.1599 | 3.1483 | 3.1682 | 3.1554 | 3.0974 | 3.173 | 3.0995 | 3.0928 | 3.1194 | 3.1236 | 3.1464 | 3.115 | 3.1161 | 3.1124 | 3.1596 | 3.1199 | 3.1498 | 3.1423 | 3.0993 | 3.1169 | 3.1416 | 3.121 | 3.1313 | 3.153 | 3.1386 | 3.1386 | 3.1361 | 3.1431 | 3.1461 | 3.1049 | 3.1648 | 3.1667 | 3.1423 | 3.1685 | 3.1573 | 3.164 | 3.0968 | 3.1067 | 3.1717 | 3.0512 | 3.094 | 3.1088 | 3.0748 | 3.1485 | 3.182 | 3.1557 | 3.1479 | 3.1161 | 3.0512 | 3.0662 | 3.1241 | 3.0801 | 3.067 | 3.0595 | 3.1098 | 3.1423 | 3.0861 | 3.1554 | 3.1049 | 3.1199 | 3.0479 | 3.0455 | 3.0838 | 3.1302 | 3.134 | 3.2069 | 3.1783 | 3.086 | 3.1154 | 3.1503 | 3.2 | 3.2034 | 3.1322 | 3.0887 | 3.1498 | 3.2214 | 3.0805 | 3.1602 | 3.1554 | 3.1898 | 3.0627 | 3.1862 | 3.1841 | 3.1914 | 3.0748 | 3.2004 | 3.1461 | 3.1255 | 3.1592 | 3.1521 | 3.1962 | 3.1451 | 3.0939 | 3.1174 | 3.0673 | 3.0606 | 3.1943 | 3.0585 | 3.1326 | 3.099 | 3.1057 | 3.1124 | 3.0673 | 3.0789 | 3.166 | 3.0876 | 3.137 | 3.1402 | 3.0644 | 3.1629 | 3.0539 | 3.1705 | 3.1399 | 3.0673 | 3.0606 | 3.2036 | 3.1154 | 3.0707 | 3.0756 | 3.0691 | 3.1087 | 3.0699 | 3.1402 | 3.1098 | 3.1667 | 3.1477 | 3.1402 | 3.178 | 3.0955 | 3.0644 |  |  | 3.285 | 3.0838 | 3.0636 |  | 3.0793 | 3.0674 | 3.0861 | 3.1199 | 3.1273 | 3.0899 | 3.0749 | 3.1446 | 3.0749 | 3.1124 | 3.1236 | 3.1944 | 3.0595 | 3.2156 | 3.2423 | 3.3314 | 3.3339 | 3.2853 | 3.0928 | 3.0809 | 3.1619 | 3.1407 | 3.1305 | 3.0534 | 3.1849 | 3.1858 | 3.1331 | 3.0831 | 3.1002 | 3.0808 | 3.073 | 3.064 | 3.0909 |  | 3.272 | 3.1034 | 3.194 | 3.0527 | 3.073 |  |  | 3.2059 | 3.1897 | 3.6759 | 3.073 | 3.0684 | 3.1327
2025-07-10 | 1.7276 | 1.7424 | 1.7629 | 1.7712 | 1.729 | 1.7528 | 1.7607 | 1.7652 | 1.7503 | 1.7726 | 1.7816 | 1.7779 | 1.7869 | 1.8035 | 1.7861 | 1.8015 | 1.7891 | 1.7959 | 1.7846 | 1.8012 | 1.7547 | 1.7494 | 1.7984 | 1.7175 | 1.7538 | 1.7729 | 1.8033 | 1.7242 | 1.7535 | 1.7372 | 1.7551 | 1.7611 | 1.7567 | 1.7663 | 1.7494 | 1.723 | 1.7363 | 1.7517 | 1.7536 | 1.7416 | 1.7738 | 1.7865 | 1.7715 | 1.7816 | 1.733 | 1.7693 | 1.7224 | 1.7401 | 1.7373 | 1.7287 | 1.7393 | 1.7506 | 1.7332 | 1.7398 | 1.7293 | 1.7485 | 1.7355 | 1.761 | 1.7355 | 1.7368 | 1.7427 | 1.7909 | 1.7663 | 1.7613 | 1.7625 | 1.7801 | 1.7777 | 1.7818 | 1.7697 | 1.7625 | 1.7607 | 1.7633 | 1.7734 | 1.7685 | 1.7398 | 1.7478 | 1.7538 | 1.7502 | 1.736 | 1.7929 | 1.7607 | 1.7869 | 1.7727 | 1.7734 | 1.7547 | 1.761 | 1.7749 | 1.7835 | 1.764 | 1.7588 | 1.787 | 1.7926 | 1.7517 | 1.7985 | 1.8001 | 1.7322 | 1.733 | 1.7588 | 1.7551 | 1.736 | 1.7607 | 1.7944 | 1.7251 | 1.7663 | 1.7675 | 1.7292 | 1.7478 | 1.7899 | 1.7502 | 1.7541 | 1.7684 | 1.7639 | 1.7891 | 1.7631 | 1.7457 | 1.7273 | 1.7437 | 1.7528 | 1.7445 | 1.7933 | 1.7581 | 1.7428 | 1.7588 | 1.7551 | 1.7296 | 1.7355 | 1.7273 | 1.7858 | 1.7358 | 1.7275 | 1.7511 | 1.7621 | 1.7532 | 1.7213 | 1.7241 | 1.7255 | 1.7717 | 1.7203 | 1.7679 | 1.7753 | 1.7376 | 1.7666 | 1.7498 | 1.7991 | 1.7494 | 1.8164 | 1.7273 | 1.7459 | 1.7587 | 1.7621 | 1.7708 | 1.764 | 1.7345 | 1.7805 | 1.7727 | 1.7798 | 1.7532 | 1.7296 | 1.7545 | 1.7303 | 1.7468 | 1.7462 | 1.7609 | 1.7407 | 1.7781 | 1.7665 | 1.7504 | 1.7215 | 1.7519 | 1.7465 | 1.7967 | 1.7396 | 1.734 | 1.7476 | 1.7825 | 1.7367 | 1.7311 | 1.7364 | 1.7401 | 1.7235 | 1.7937 | 1.7428 | 1.7209 | 1.776 | 1.7976 | 1.7306 | 1.7309 | 1.6182 | 1.7636 | 1.7797 | 1.7689 | 1.7462 | 1.7841 | 1.7348 | 1.7538 | 1.7614 | 1.7864 | 1.7367 |  |  | 1.8597 | 1.7536 | 1.7509 |  | 1.7498 | 1.7491 | 1.7378 | 1.7453 | 1.7528 | 1.7341 | 1.7416 | 1.7566 | 1.7528 | 1.764 | 1.7341 | 1.7846 | 1.7478 | 1.8367 | 1.7989 | 1.8751 | 1.9049 | 1.8539 | 1.7494 | 1.7698 | 1.7938 | 1.7811 | 1.7328 | 1.7345 | 1.9053 | 1.7542 | 1.7435 | 1.7578 | 1.7249 | 1.7713 | 1.7754 | 1.7411 | 1.7293 |  | 1.7968 | 1.798 | 1.7204 | 1.7819 | 1.7444 |  |  | 1.7973 | 1.7868 | 2.0482 | 1.7249 | 1.7537 | 1.761
2025-07-11 | 4.4927 | 4.5767 | 4.5689 | 4.573 | 4.5497 | 4.5401 | 4.5419 | 4.5655 | 4.5458 | 4.4994 | 4.5419 | 4.5506 | 4.5655 | 4.5884 | 4.536 | 4.236 | 4.5506 | 4.5805 | 4.5324 | 4.5428 | 4.5581 | 4.5393 | 4.5601 | 4.4654 | 4.5704 | 4.5532 | 4.5704 | 4.4511 | 4.4444 | 4.4578 | 4.4744 | 4.4544 | 4.4929 | 4.2732 | 4.4768 | 4.4526 | 4.573 | 4.5281 | 4.5356 | 4.479 | 4.4816 | 4.5067 | 4.5307 | 4.4906 | 4.5618 | 4.573 | 4.4633 | 4.5356 | 4.4692 | 4.4728 | 4.4532 | 4.4757 | 4.5613 | 4.4444 | 4.4564 | 4.5343 | 4.5643 | 4.5873 | 4.5643 | 4.5643 | 4.4989 | 4.5467 | 4.4753 | 4.599 | 4.6707 | 4.6811 | 4.7053 | 4.6175 | 4.806 | 4.8191 | 4.7966 | 4.7472 | 4.5393 | 4.7963 | 4.785 | 4.7441 | 4.8236 | 4.8191 | 4.8199 | 4.8377 | 4.7419 | 4.7959 | 4.7479 | 4.633 | 4.7322 | 4.776 | 4.6588 | 4.6288 | 4.6779 | 4.6423 | 4.5868 | 4.6448 | 4.6105 | 4.5955 | 4.6352 | 4.603 | 4.6255 | 4.588 | 4.6442 | 4.6067 | 4.5993 | 4.5655 | 4.5506 | 4.5356 | 4.6129 | 4.6067 | 4.5976 | 4.6186 | 4.7034 | 4.7091 | 4.6361 | 4.7336 | 4.6818 | 4.7384 | 4.5393 | 4.7037 | 4.4553 | 4.4711 | 4.6315 | 4.6491 | 4.6022 | 4.4677 | 4.5676 | 4.4936 | 4.5948 | 4.6735 | 4.2809 | 4.2637 | 4.298 | 4.2913 | 4.2662 | 4.3284 | 4.3423 | 4.2656 | 4.2622 | 4.2797 | 4.2378 | 4.2937 | 4.311 | 4.2772 | 4.3423 | 4.1936 | 4.2772 | 4.2489 | 4.2397 | 4.3423 | 4.3296 | 4.3105 | 4.2939 | 4.2835 | 4.3008 | 4.1985 | 3.7686 | 4.2285 | 4.2135 | 4.1985 | 4.2472 | 4.221 | 4.625 | 4.6136 | 4.5219 | 4.4614 | 4.4478 | 4.5212 | 4.5825 | 4.5335 | 4.625 | 4.4848 | 4.5947 | 4.6124 | 4.5949 | 4.6407 | 4.3825 | 4.6582 | 4.6498 | 4.525 | 4.5379 | 4.5909 | 4.4916 | 4.5303 | 4.479 | 4.4545 | 4.4747 | 4.5818 | 4.4895 | 4.4579 | 4.5491 | 4.672 | 4.2582 | 4.2378 | 4.5909 | 4.5227 | 4.5606 | 4.5341 | 4.5496 | 4.6326 | 4.5182 | 4.5686 |  |  | 4.8553 | 4.208 | 4.5122 |  | 4.5079 | 4.5318 | 4.6071 | 4.4831 | 4.488 | 4.4689 | 4.4981 | 4.573 | 4.236 | 4.4981 | 4.4869 | 4.6479 | 4.4628 | 4.7594 | 4.7067 | 4.7962 | 4.8537 | 4.8339 | 4.5835 | 4.5913 | 4.6526 | 4.5976 | 4.6016 | 4.5877 | 4.667 | 4.5808 | 4.5976 | 4.5776 | 4.5338 | 4.513 | 4.5338 | 4.5556 | 4.5931 |  | 4.529 | 4.5315 | 4.5274 | 4.5597 | 4.5493 |  |  | 4.6353 | 4.616 | 5.2661 | 4.5882 | 4.5978 | 4.5354
2025-07-12 | 2.9791 | 2.9701 | 2.9888 | 2.97 | 2.9628 | 2.9625 | 2.9513 | 2.8876 | 2.88 | 2.9124 | 2.9363 | 2.9551 | 2.97 | 2.9908 | 2.9401 | 2.9431 | 2.9543 | 2.9363 | 2.9338 | 2.8764 | 2.9101 | 2.9513 | 2.9594 | 2.8664 | 2.9144 | 2.9006 | 2.8971 | 2.8997 | 2.9663 | 2.9496 | 2.9696 | 2.9363 | 2.9206 | 2.9437 | 2.9251 | 2.8638 | 2.9551 | 2.9438 | 2.9551 | 2.9813 | 2.9401 | 2.9064 | 2.9139 | 2.9625 | 2.8914 | 2.9251 | 2.8557 | 2.9363 | 2.88 | 2.8962 | 2.9551 | 2.9251 | 2.9227 | 2.8664 | 2.911 | 3.0032 | 2.9799 | 2.9888 | 2.912 | 2.9147 | 2.9551 | 2.8578 | 2.9251 | 2.93 | 2.9317 | 2.9421 | 2.9352 | 2.9621 | 3.033 | 3.0472 | 3.0213 | 2.9831 | 2.9888 | 3.0296 | 3.0275 | 3.0179 | 3.0289 | 2.9974 | 2.9532 | 3.0095 | 2.9251 | 2.9708 | 2.9169 | 2.9858 | 2.921 | 2.9895 | 2.93 | 2.9199 | 2.9974 | 2.9749 | 2.9397 | 2.9988 | 2.9251 | 3.0019 | 2.9713 | 2.9727 | 2.9476 | 2.9625 | 2.9513 | 2.97 | 2.9738 | 2.9326 | 2.9738 | 2.9738 | 2.8997 | 2.9139 | 2.9626 | 2.8622 | 2.9476 | 3.0232 | 2.9248 | 3.0182 | 2.9776 | 2.9706 | 2.9966 | 2.9644 | 2.8806 | 2.8598 | 2.8831 | 2.9064 | 2.8813 | 2.8864 | 2.8747 | 2.9251 | 2.9363 | 2.9713 | 2.9251 | 2.9438 | 2.8664 | 2.8864 | 2.866 | 2.8833 | 2.8937 | 2.9103 | 2.9794 | 2.8776 | 2.8986 | 2.9671 | 2.9016 | 2.9251 | 2.8764 | 2.8633 | 2.9139 | 2.8833 | 2.9577 | 2.8833 | 2.9551 | 2.9091 | 2.9525 | 2.9213 | 2.9352 | 2.9363 | 2.8831 | 2.9251 | 2.9625 | 2.9712 | 2.9625 | 2.9404 | 2.9879 | 2.967 | 2.8801 | 2.9583 | 2.9158 | 2.8815 | 2.8923 | 2.8956 | 2.9773 | 2.8956 | 2.9095 | 2.8836 | 2.8731 | 2.8818 | 2.9091 | 2.8618 | 2.9522 | 2.9583 | 2.9886 | 3.0076 | 2.9057 | 2.947 | 2.9336 | 2.8822 | 2.9192 | 2.8873 | 2.8986 | 2.9024 | 2.8982 | 2.92 | 2.9007 | 2.8636 | 2.9504 | 3.0076 | 2.9886 | 2.9697 | 2.9621 | 3.0155 | 2.8818 | 2.9886 |  |  | 3.091 | 2.9157 | 2.9305 |  | 2.8982 | 2.9625 | 2.9468 | 2.97 | 2.985 | 2.9232 | 3.0037 | 3.0086 | 2.9213 | 2.9663 | 2.985 | 2.9401 | 2.923 | 3.1121 | 3.0452 | 3.1258 | 3.1191 | 3.1223 | 2.9351 | 2.9896 | 2.9915 | 2.9563 | 2.9421 | 2.958 | 2.9987 | 2.9006 | 2.8997 | 2.9776 | 2.871 | 2.9567 | 2.9371 | 2.8896 | 2.9442 |  | 2.972 | 2.9014 | 2.9154 | 2.9386 | 2.9685 |  |  | 3.0219 | 2.9781 | 3.3934 | 2.8827 | 2.869 | 2.9446
2025-07-13 | 2.8003 | 2.79 | 2.764 | 2.7753 | 2.7793 | 2.7625 | 2.7528 | 2.7603 | 2.7696 | 2.7876 | 2.7491 | 2.7753 | 2.791 | 2.7865 | 2.7341 | 2.7079 | 2.7337 | 2.7622 | 2.7675 | 2.7741 | 2.7491 | 2.6689 | 2.7312 | 2.6966 | 2.7312 | 2.7734 | 2.7599 | 2.7576 | 2.7526 | 2.7536 | 2.7772 | 2.7472 | 2.6616 | 2.75 | 2.7004 | 2.7099 | 2.7386 | 2.6592 | 2.7004 | 2.7266 | 2.7116 | 2.7341 | 2.7004 | 2.6592 | 2.7303 | 2.709 | 2.7381 | 2.6723 | 2.7002 | 2.7146 | 2.7041 | 2.6948 | 2.7366 | 2.6916 | 2.6863 | 2.7333 | 2.7649 | 2.7472 | 2.7266 | 2.7432 | 2.7097 | 2.7655 | 2.7176 | 2.7461 | 2.8311 | 2.8183 | 2.8149 | 2.7813 | 2.8109 | 2.7978 | 2.8094 | 2.7963 | 2.8599 | 2.8247 | 2.8151 | 2.7882 | 2.8251 | 2.8 | 2.7697 | 2.8366 | 2.7772 | 2.8135 | 2.7303 | 2.8232 | 2.7667 | 2.8052 | 2.779 | 2.7614 | 2.8034 | 2.776 | 2.6984 | 2.8052 | 2.8341 | 2.7397 | 2.8032 | 2.7041 | 2.7266 | 2.7004 | 2.7191 | 2.7228 | 2.7004 | 2.7453 | 2.7416 | 2.6929 | 2.7402 | 2.7419 | 2.6963 | 2.7752 | 2.7266 | 2.7652 | 2.7156 | 2.7367 | 2.7366 | 2.7432 | 2.6966 | 2.7431 | 2.7026 | 2.7033 | 2.7732 | 2.7363 | 2.7509 | 2.7266 | 2.7432 | 2.7288 | 2.6693 | 2.7382 | 2.6951 | 2.7041 | 2.7 | 2.6797 | 2.6621 | 2.7554 | 2.7886 | 2.7988 | 2.7273 | 2.7087 | 2.6958 | 2.7308 | 2.729 | 2.7566 | 2.7402 | 2.7091 | 2.7584 | 2.744 | 2.7154 | 2.7734 | 2.7715 | 2.6966 | 2.7959 | 2.7312 | 2.7347 | 2.7266 | 2.7146 | 2.7079 | 2.7453 | 2.7588 | 2.7468 | 2.785 | 2.75 | 2.7273 | 2.6902 | 2.7386 | 2.7306 | 2.697 | 2.7387 | 2.6945 | 2.7992 | 2.6599 | 2.7098 | 2.6727 | 2.7455 | 2.6825 | 2.6667 | 2.6873 | 2.6906 | 2.7311 | 2.7386 | 2.7614 | 2.697 | 2.7311 | 2.7098 | 2.697 | 2.7239 | 2.7356 | 2.6958 | 2.6633 | 2.6764 | 2.6691 | 2.7018 | 2.7133 | 2.714 | 2.7023 | 2.7386 | 2.7462 | 2.6845 | 2.7235 | 2.7273 | 2.7386 |  |  | 2.8646 | 2.7371 | 2.7184 |  | 2.7006 | 2.7004 | 2.7584 | 2.7116 | 2.7303 | 2.6985 | 2.7154 | 2.7378 | 2.7004 | 2.6929 | 2.7303 | 2.7041 | 2.7033 | 2.8781 | 2.8392 | 2.8706 | 2.8736 | 2.9279 | 2.7465 | 2.751 | 2.7721 | 2.7333 | 2.6897 | 2.7232 | 2.7973 | 2.6932 | 2.8005 | 2.7599 | 2.7234 | 2.7287 | 2.7234 | 2.7273 | 2.6949 |  | 2.7993 | 2.6977 | 2.7811 | 2.6988 | 2.704 |  |  | 2.8171 | 2.8252 | 3.1849 | 2.7234 | 2.7446 | 2.7433
2025-07-14 | 3.6895 | 3.7763 | 3.7869 | 3.7625 | 3.7494 | 3.7397 | 3.7772 | 3.8079 | 3.762 | 3.7825 | 3.7378 | 3.7228 | 3.7839 | 3.7467 | 3.791 | 3.7798 | 3.7097 | 3.7431 | 3.7241 | 3.7504 | 3.7989 | 3.6419 | 3.7684 | 3.732 | 3.7373 | 3.7704 | 3.7532 | 3.7563 | 3.6608 | 3.6628 | 3.747 | 3.7803 | 3.6954 | 3.6844 | 3.6438 | 3.7103 | 3.6854 | 3.6367 | 3.6629 | 3.6963 | 3.6517 | 3.6816 | 3.6742 | 3.7004 | 3.7079 | 3.6779 | 3.6595 | 3.673 | 3.6387 | 3.6512 | 3.6854 | 3.673 | 3.7919 | 3.6741 | 3.6958 | 3.732 | 3.746 | 3.7079 | 3.732 | 3.752 | 3.7412 | 3.8023 | 3.6891 | 3.7659 | 3.8064 | 3.8704 | 3.8341 | 3.8182 | 3.8775 | 3.8779 | 3.903 | 3.8918 | 3.8652 | 3.8891 | 3.8905 | 3.8322 | 3.9108 | 3.8884 | 3.8712 | 3.9101 | 3.8225 | 3.8625 | 3.8944 | 3.9433 | 3.8753 | 3.9195 | 3.888 | 3.8708 | 3.8914 | 3.8861 | 3.8386 | 3.9004 | 3.882 | 3.8539 | 3.8615 | 3.8184 | 3.8674 | 3.7041 | 3.7116 | 3.6816 | 3.6704 | 3.7266 | 3.6854 | 3.8434 | 3.6994 | 3.6816 | 3.696 | 3.6768 | 3.7607 | 3.757 | 3.703 | 3.7791 | 3.7826 | 3.749 | 3.7116 | 3.7633 | 3.6698 | 3.7653 | 3.6967 | 3.7775 | 3.8 | 3.6687 | 3.7057 | 3.6532 | 3.7169 | 3.7763 | 3.7588 | 3.6494 | 3.7656 | 3.7307 | 3.6664 | 3.7791 | 3.7704 | 3.6813 | 3.8217 | 3.7119 | 3.6727 | 3.7098 | 3.7501 | 3.7921 | 3.778 | 3.7452 | 3.7895 | 3.7846 | 3.6993 | 3.7649 | 3.7116 | 3.7794 | 3.7684 | 3.8064 | 3.7711 | 3.824 | 3.6841 | 3.6742 | 3.6891 | 3.6742 | 3.7079 | 3.6704 | 3.697 | 3.7568 | 3.6761 | 3.675 | 3.6633 | 3.6717 | 3.763 | 3.7109 | 3.6981 | 3.6593 | 3.714 | 3.6985 | 3.6629 | 3.6778 | 3.6929 | 3.772 | 3.7515 | 3.7125 | 3.6875 | 3.7038 | 3.734 | 3.7159 | 3.6783 | 3.6599 | 3.6902 | 3.772 | 3.6752 | 3.6747 | 3.6967 | 3.7055 | 3.6811 | 3.7448 | 3.7845 | 3.7314 | 3.7159 | 3.7045 | 3.733 | 3.6905 | 3.7064 | 3.75 |  |  | 4.0106 | 3.7552 | 3.735 |  | 3.6675 | 3.6753 | 3.8292 | 3.6801 | 3.6831 | 3.6693 | 3.7037 | 3.6742 | 3.691 | 3.6667 | 3.7476 | 3.6929 | 3.6804 | 3.9577 | 3.708 | 3.9006 | 3.9237 | 3.9436 | 3.7133 | 3.7648 | 3.8094 | 3.7746 | 3.7684 | 3.7507 | 3.7951 | 3.7373 | 3.7387 | 3.7896 | 3.6713 | 3.7605 | 3.7432 | 3.7045 | 3.7184 |  | 3.7645 | 3.6956 | 3.7811 | 3.6977 | 3.648 |  |  | 3.8119 | 3.7265 | 4.3015 | 3.6946 | 3.7355 | 3.7502
2025-07-15 | 3.2747 | 3.2878 | 3.2959 | 3.2247 | 3.3369 | 3.3412 | 3.2996 | 3.2921 | 3.3453 | 3.3564 | 3.2734 | 3.3371 | 3.3483 | 3.2727 | 3.3333 | 3.3757 | 3.3487 | 3.2622 | 3.3618 | 3.2878 | 3.3258 | 3.2625 | 3.3086 | 3.3325 | 3.2878 | 3.2982 | 3.2812 | 3.2959 | 3.228 | 3.2659 | 3.3392 | 3.2959 | 3.2402 | 3.2222 | 3.2026 | 3.2519 | 3.2165 | 3.2255 | 3.2491 | 3.2281 | 3.2536 | 3.2547 | 3.236 | 3.2247 | 3.3629 | 3.3655 | 3.2878 | 3.2094 | 3.2352 | 3.2309 | 3.2472 | 3.2921 | 3.3605 | 3.2053 | 3.2107 | 3.3199 | 3.2859 | 3.206 | 3.2959 | 3.4017 | 3.2652 | 3.3623 | 3.2026 | 3.3559 | 3.3525 | 3.3321 | 3.3763 | 3.2944 | 3.3528 | 3.3318 | 3.3742 | 3.3596 | 3.2427 | 3.3577 | 3.3954 | 3.3345 | 3.3994 | 3.3753 | 3.3674 | 3.3953 | 3.3974 | 3.2494 | 3.394 | 3.4356 | 3.3876 | 3.4041 | 3.3573 | 3.3453 | 3.3749 | 3.3592 | 3.3133 | 3.3653 | 3.2247 | 3.2622 | 3.3235 | 3.2974 | 3.3386 | 3.3592 | 3.3581 | 3.3285 | 3.3708 | 3.3412 | 3.2547 | 3.3397 | 3.225 | 3.2172 | 3.2659 | 3.272 | 3.2577 | 3.2316 | 3.2463 | 3.2895 | 3.2962 | 3.2353 | 3.3146 | 3.2536 | 3.2044 | 3.1993 | 3.2659 | 3.2337 | 3.2757 | 3.2486 | 3.2393 | 3.2311 | 3.236 | 3.2656 | 3.303 | 3.2921 | 3.3145 | 3.2849 | 3.2287 | 3.3272 | 3.3891 | 3.2919 | 3.3427 | 3.2857 | 3.2325 | 3.35 | 3.2396 | 3.3333 | 3.3283 | 3.2747 | 3.3258 | 3.2868 | 3.2472 | 3.3386 | 3.3292 | 3.3732 | 3.3207 | 3.3518 | 3.3801 | 3.3652 | 3.2326 | 3.3667 | 3.3232 | 3.2888 | 3.3225 | 3.3015 | 3.322 | 3.3371 | 3.3306 | 3.3068 | 3.2051 | 3.3185 | 3.3603 | 3.3465 | 3.2992 | 3.2357 | 3.3871 | 3.2036 | 3.3393 | 3.3407 | 3.2896 | 3.2015 | 3.3976 | 3.2534 | 3.264 | 3.2841 | 3.229 | 3.2917 | 3.3392 | 3.2492 | 3.2172 | 3.2764 | 3.2119 | 3.2256 | 3.2967 | 3.2764 | 3.2611 | 3.2273 | 3.2269 | 3.2386 | 3.322 | 3.25 | 3.2803 | 3.303 | 3.2727 | 3.3371 |  |  | 3.4107 | 3.2887 | 3.2927 |  | 3.2433 | 3.2472 | 3.2607 | 3.2172 | 3.2622 | 3.236 | 3.2921 | 3.3333 | 3.2745 | 3.224 | 3.2547 | 3.3966 | 3.2626 | 3.3908 | 3.3945 | 3.4393 | 3.5078 | 3.4752 | 3.2419 | 3.246 | 3.3524 | 3.3202 | 3.3044 | 3.2152 | 3.3672 | 3.3241 | 3.3102 | 3.2499 | 3.2207 | 3.2543 | 3.2906 | 3.2959 | 3.2125 |  | 3.3711 | 3.2532 | 3.2945 | 3.266 | 3.2063 |  |  | 3.348 | 3.3464 | 3.4239 | 3.2595 | 3.2504 | 3.2988
2025-07-16 | 2.7575 | 2.7277 | 2.7228 | 2.7461 | 2.7889 | 2.7895 | 2.7573 | 2.7363 | 2.7362 | 2.8149 | 2.7191 | 2.7865 | 2.7228 | 2.7416 | 2.7629 | 2.7558 | 2.7768 | 2.7491 | 2.7654 | 2.7993 | 2.7494 | 2.7258 | 2.7312 | 2.7266 | 2.7485 | 2.7506 | 2.7132 | 2.8128 | 2.686 | 2.7968 | 2.8148 | 2.7849 | 2.7044 | 2.747 | 2.7154 | 2.7166 | 2.7573 | 2.7753 | 2.764 | 2.7416 | 2.7903 | 2.7416 | 2.7303 | 2.6869 | 2.8382 | 2.8404 | 2.7347 | 2.6974 | 2.7182 | 2.7146 | 2.7079 | 2.6906 | 2.7945 | 2.7399 | 2.7347 | 2.7825 | 2.8028 | 2.8386 | 2.7795 | 2.7888 | 2.739 | 2.7738 | 2.7528 | 2.7628 | 2.8453 | 2.8349 | 2.8353 | 2.7582 | 2.8378 | 2.8393 | 2.8303 | 2.8041 | 2.7528 | 2.7004 | 2.7699 | 2.8201 | 2.8032 | 2.7678 | 2.8191 | 2.7969 | 2.8157 | 2.8517 | 2.815 | 2.8558 | 2.8007 | 2.8315 | 2.7775 | 2.7719 | 2.7951 | 2.7854 | 2.7549 | 2.8097 | 2.7569 | 2.7509 | 2.7815 | 2.815 | 2.8262 | 2.7865 | 2.7753 | 2.7416 | 2.7154 | 2.7678 | 2.7903 | 2.809 | 2.7569 | 2.7303 | 2.7033 | 2.7183 | 2.7903 | 2.7972 | 2.7357 | 2.8086 | 2.8181 | 2.7855 | 2.7288 | 2.7914 | 2.7233 | 2.7765 | 2.7586 | 2.8015 | 2.7266 | 2.69 | 2.7492 | 2.7079 | 2.7142 | 2.8125 | 2.6895 | 2.7079 | 2.7605 | 2.7 | 2.7101 | 2.7903 | 2.8201 | 2.7416 | 2.7622 | 2.7378 | 2.7294 | 2.8007 | 2.8009 | 2.7828 | 2.7851 | 2.7288 | 2.8127 | 2.7416 | 2.7116 | 2.8041 | 2.803 | 2.7702 | 2.8107 | 2.7578 | 2.7277 | 2.7566 | 2.7116 | 2.7828 | 2.7753 | 2.8116 | 2.7865 | 2.764 | 2.7689 | 2.7462 | 2.6855 | 2.75 | 2.7239 | 2.7071 | 2.8313 | 2.7251 | 2.7936 | 2.7374 | 2.7015 | 2.72 | 2.7295 | 2.7258 | 2.697 | 2.7164 | 2.7519 | 2.7917 | 2.7572 | 2.7803 | 2.7576 | 2.7742 | 2.7098 | 2.7643 | 2.7172 | 2.8091 | 2.7098 | 2.7374 | 2.6953 | 2.7396 | 2.7091 | 2.7902 | 2.7803 | 2.75 | 2.7992 | 2.7841 | 2.7837 | 2.7386 | 2.7318 | 2.7803 |  |  | 2.8848 | 2.7476 | 2.7125 |  | 2.7136 | 2.7266 | 2.7955 | 2.7116 | 2.7176 | 2.7603 | 2.7154 | 2.7715 | 2.6944 | 2.7494 | 2.7307 | 2.7753 | 2.6973 | 2.8464 | 2.8392 | 2.884 | 2.9336 | 2.8558 | 2.7297 | 2.7694 | 2.7721 | 2.7832 | 2.792 | 2.716 | 2.7182 | 2.8159 | 2.7399 | 2.7366 | 2.7739 | 2.7273 | 2.77 | 2.746 | 2.7919 |  | 2.8319 | 2.7517 | 2.7264 | 2.7273 | 2.7234 |  |  | 2.7858 | 2.7782 | 2.8894 | 2.7234 | 2.7197 | 2.7637
2025-07-17 | 2.7551 | 2.7589 | 2.7528 | 2.7865 | 2.8066 | 2.8127 | 2.7865 | 2.8127 | 2.7578 | 2.8473 | 2.7715 | 2.8315 | 2.7528 | 2.8069 | 2.8015 | 2.8277 | 2.8221 | 2.8165 | 2.8301 | 2.8615 | 2.8116 | 2.803 | 2.8491 | 2.8092 | 2.8176 | 2.8719 | 2.7647 | 2.8444 | 2.7549 | 2.8381 | 2.8218 | 2.8158 | 2.7586 | 2.7951 | 2.7685 | 2.7601 | 2.8124 | 2.8052 | 2.7903 | 2.8026 | 2.8277 | 2.779 | 2.7678 | 2.7476 | 2.8824 | 2.8764 | 2.7692 | 2.7581 | 2.7578 | 2.7409 | 2.7528 | 2.7678 | 2.7935 | 2.7466 | 2.7692 | 2.7928 | 2.8331 | 2.8989 | 2.8365 | 2.8578 | 2.7708 | 2.823 | 2.7865 | 2.8376 | 2.8477 | 2.8384 | 2.8529 | 2.7886 | 2.864 | 2.8674 | 2.8745 | 2.8629 | 2.8285 | 2.8442 | 2.8365 | 2.8794 | 2.8631 | 2.8652 | 2.8846 | 2.9065 | 2.8764 | 2.8652 | 2.8891 | 2.894 | 2.824 | 2.8652 | 2.8262 | 2.8146 | 2.8596 | 2.8378 | 2.788 | 2.8408 | 2.8547 | 2.7996 | 2.8055 | 2.8251 | 2.8637 | 2.8581 | 2.7918 | 2.821 | 2.8573 | 2.8524 | 2.8457 | 2.8652 | 2.7972 | 2.7625 | 2.7625 | 2.7554 | 2.8292 | 2.8185 | 2.8073 | 2.8245 | 2.8531 | 2.8098 | 2.8157 | 2.8131 | 2.7661 | 2.8285 | 2.7922 | 2.8131 | 2.7483 | 2.7622 | 2.7619 | 2.7622 | 2.7442 | 2.8288 | 2.7775 | 2.8004 | 2.7809 | 2.7509 | 2.7537 | 2.8218 | 2.8667 | 2.7689 | 2.7815 | 2.7538 | 2.7587 | 2.8112 | 2.844 | 2.8135 | 2.8221 | 2.7685 | 2.833 | 2.7737 | 2.7453 | 2.8245 | 2.8513 | 2.7824 | 2.8349 | 2.7692 | 2.7519 | 2.7944 | 2.7442 | 2.8318 | 2.8715 | 2.8404 | 2.8255 | 2.8416 | 2.8318 | 2.7905 | 2.7502 | 2.8295 | 2.7596 | 2.7519 | 2.8785 | 2.8076 | 2.8405 | 2.7663 | 2.764 | 2.7564 | 2.8029 | 2.8156 | 2.7677 | 2.7527 | 2.8121 | 2.8295 | 2.7981 | 2.822 | 2.8047 | 2.8447 | 2.7605 | 2.8168 | 2.7845 | 2.8825 | 2.7647 | 2.771 | 2.7549 | 2.7964 | 2.7382 | 2.8462 | 2.8473 | 2.8208 | 2.8742 | 2.8655 | 2.9133 | 2.822 | 2.8227 | 2.9511 |  |  | 2.9367 | 2.8106 | 2.7679 |  | 2.7751 | 2.7978 | 2.8854 | 2.7865 | 2.7753 | 2.827 | 2.7468 | 2.8341 | 2.767 | 2.8277 | 2.7828 | 2.9086 | 2.7532 | 2.8777 | 2.9055 | 2.9378 | 2.9472 | 3.0395 | 2.7956 | 2.7698 | 2.8545 | 2.8128 | 2.8235 | 2.7696 | 2.8804 | 2.8453 | 2.8088 | 2.7592 | 2.8489 | 2.7734 | 2.8104 | 2.8223 | 2.8646 |  | 2.818 | 2.8217 | 2.796 | 2.7767 | 2.7743 |  |  | 2.8761 | 2.8566 | 2.9642 | 2.8015 | 2.7948 | 2.8151
2025-07-18 | 1.1582 | 1.1789 | 1.1783 | 1.1648 | 1.172 | 1.1573 | 1.1678 | 1.176 | 1.1649 | 1.1649 | 1.191 | 1.1539 | 1.1461 | 1.1726 | 1.1461 | 1.1667 | 1.1461 | 1.1861 | 1.1443 | 1.1582 | 1.1573 | 1.1816 | 1.162 | 1.1819 | 1.1685 | 1.1499 | 1.1848 | 1.1439 | 1.1745 | 1.1645 | 1.1735 | 1.1888 | 1.1698 | 1.1648 | 1.1551 | 1.1646 | 1.1524 | 1.1655 | 1.173 | 1.1719 | 1.1528 | 1.1805 | 1.1547 | 1.164 | 1.1655 | 1.1487 | 1.1602 | 1.1592 | 1.1542 | 1.1829 | 1.1891 | 1.1637 | 1.1685 | 1.1745 | 1.172 | 1.1659 | 1.1576 | 1.1618 | 1.1765 | 1.1912 | 1.1876 | 1.1629 | 1.1655 | 1.1415 | 1.2024 | 1.1965 | 1.2052 | 1.1765 | 1.1884 | 1.1865 | 1.2015 | 1.1895 | 1.2277 | 1.1985 | 1.2228 | 1.2062 | 1.2225 | 1.2071 | 1.182 | 1.2197 | 1.1996 | 1.2199 | 1.1974 | 1.1993 | 1.1719 | 1.2112 | 1.1775 | 1.1805 | 1.197 | 1.1873 | 1.175 | 1.1983 | 1.2202 | 1.2082 | 1.1942 | 1.1715 | 1.1948 | 1.194 | 1.2037 | 1.1742 | 1.1933 | 1.1899 | 1.2097 | 1.1824 | 1.1605 | 1.1689 | 1.1685 | 1.1445 | 1.1723 | 1.1625 | 1.1592 | 1.1831 | 1.1992 | 1.1775 | 1.1921 | 1.1509 | 1.1613 | 1.1589 | 1.1559 | 1.1566 | 1.1404 | 1.1549 | 1.1679 | 1.1472 | 1.1648 | 1.1665 | 1.1434 | 1.1562 | 1.1572 | 1.1462 | 1.1948 | 1.1609 | 1.1865 | 1.1971 | 1.2157 | 1.157 | 1.1521 | 1.2105 | 1.212 | 1.1933 | 1.1651 | 1.1481 | 1.1783 | 1.2007 | 1.1689 | 1.1758 | 1.1629 | 1.173 | 1.1616 | 1.1758 | 1.1886 | 1.1727 | 1.1589 | 1.1693 | 1.1629 | 1.1491 | 1.1573 | 1.1655 | 1.1784 | 1.1621 | 1.1488 | 1.1822 | 1.1566 | 1.1431 | 1.1838 | 1.16 | 1.1652 | 1.1424 | 1.1466 | 1.144 | 1.1745 | 1.1891 | 1.167 | 1.1927 | 1.1519 | 1.1788 | 1.1902 | 1.1652 | 1.1825 | 1.1667 | 1.1818 | 1.1616 | 1.1515 | 1.1607 | 1.1678 | 1.165 | 1.1891 | 1.1673 | 1.1596 | 1.193 | 1.1973 | 1.1564 | 1.1902 | 1.2098 | 1.1784 | 1.1667 | 1.1545 | 1.2197 |  |  | 1.2093 | 1.161 | 1.167 |  | 1.1576 | 1.1528 | 1.2011 | 1.1494 | 1.1685 | 1.1948 | 1.2022 | 1.2037 | 1.1985 | 1.2075 | 1.176 | 1.2034 | 1.1619 | 1.1705 | 1.1957 | 1.2373 | 1.232 | 1.2458 | 1.1785 | 1.1718 | 1.1685 | 1.1506 | 1.1589 | 1.1582 | 1.1948 | 1.1751 | 1.1516 | 1.1755 | 1.1601 | 1.158 | 1.1694 | 1.1859 | 1.1677 |  | 1.1746 | 1.1808 | 1.1542 | 1.1672 | 1.1927 |  |  | 1.2067 | 1.1795 | 1.2123 | 1.1733 | 1.17 | 1.1756
2025-07-19 | 4.325 | 4.4114 | 4.4195 | 4.4007 | 4.3803 | 4.3858 | 4.412 | 4.427 | 4.3182 | 4.3578 | 4.427 | 4.3783 | 4.3783 | 4.3759 | 4.397 | 4.4195 | 4.3933 | 4.4345 | 4.3734 | 4.3941 | 4.3633 | 4.3846 | 4.408 | 4.3935 | 4.3872 | 4.3634 | 4.3526 | 4.3912 | 4.3672 | 4.3779 | 4.3299 | 4.3958 | 4.3278 | 4.3372 | 4.3843 | 4.3192 | 4.3258 | 4.3596 | 4.3483 | 4.3296 | 4.3408 | 4.3558 | 4.3438 | 4.3558 | 4.397 | 4.3783 | 4.3637 | 4.3408 | 4.3578 | 4.347 | 4.3577 | 4.3783 | 4.3978 | 4.3825 | 4.3699 | 4.3905 | 4.4145 | 4.3296 | 4.3745 | 4.4265 | 4.3899 | 4.4229 | 4.3596 | 4.3929 | 4.4598 | 4.4909 | 4.5082 | 4.5293 | 4.3708 | 4.397 | 4.3783 | 4.4045 | 4.4232 | 4.0337 | 4.4078 | 4.4378 | 4.4245 | 4.4569 | 4.4232 | 4.5013 | 4.4569 | 4.4944 | 4.4569 | 4.4345 | 4.4232 | 4.3895 | 4.0824 | 4.397 | 4.4307 | 4.4532 | 4.4117 | 4.5428 | 4.4045 | 4.4457 | 4.4464 | 4.3745 | 4.3865 | 4.4292 | 4.3618 | 4.3914 | 4.4408 | 4.3809 | 4.3697 | 4.3951 | 4.3226 | 4.367 | 4.3313 | 4.3526 | 4.4633 | 4.4301 | 4.3201 | 4.4194 | 4.3955 | 4.3509 | 4.5004 | 4.4723 | 4.3526 | 3.996 | 4.304 | 4.5101 | 4.485 | 4.3213 | 4.3346 | 4.3483 | 4.3517 | 4.3742 | 4.3708 | 4.3446 | 4.4135 | 4.3602 | 4.3343 | 4.4377 | 4.4598 | 4.4985 | 4.5105 | 4.4094 | 4.3021 | 4.4755 | 4.5447 | 4.4569 | 4.4204 | 4.3526 | 4.3708 | 4.4633 | 4.3303 | 4.4539 | 4.3783 | 4.4535 | 4.4439 | 4.3803 | 4.401 | 4.4569 | 4.3269 | 4.3783 | 4.3993 | 4.3745 | 4.3933 | 4.3783 | 4.4583 | 4.4402 | 4.4195 | 4.4492 | 4.2997 | 4.3889 | 4.4545 | 4.4073 | 4.3208 | 4.3165 | 4.4167 | 4.3018 | 4.3964 | 4.4545 | 4.3165 | 4.3309 | 4.3805 | 4.3966 | 4.2955 | 4.3333 | 4.266 | 4.2955 | 4.2692 | 4.2593 | 4.2727 | 4.4404 | 4.3381 | 4.2997 | 4.3662 | 4.3236 | 4.3996 | 4.3112 | 4.3788 | 4.4061 | 4.392 | 4.4364 | 4.4019 | 4.367 | 4.4095 | 4.3523 |  |  | 4.6174 | 4.4182 | 4.3459 |  | 4.1148 | 4.3408 | 4.3858 | 4.4045 | 4.3745 | 4.424 | 4.397 | 4.382 | 4.4232 | 4.3513 | 4.3861 | 4.4202 | 4.3982 | 4.4245 | 4.4783 | 4.5723 | 4.5455 | 4.5392 | 4.3771 | 4.3036 | 4.4009 | 4.4012 | 4.3803 | 4.4287 | 4.3901 | 4.3734 | 4.3978 | 4.3978 | 4.3007 | 4.3939 | 4.3124 | 4.4003 | 4.4081 |  | 4.3985 | 4.3006 | 4.3383 | 4.3883 | 4.4491 |  |  | 4.4723 | 4.3966 | 4.4927 | 4.2774 | 3.9594 | 4.3874
2025-07-20 | 4.9127 | 4.9231 | 4.9139 | 4.9438 | 4.9583 | 4.9139 | 4.9551 | 4.9476 | 4.8331 | 4.9222 | 4.9139 | 4.9251 | 4.97 | 4.8131 | 4.8015 | 4.8951 | 4.8689 | 4.9476 | 4.9521 | 4.9507 | 4.8727 | 4.9191 | 4.8401 | 4.9505 | 4.9922 | 4.9507 | 4.8598 | 4.9498 | 4.7524 | 4.9355 | 4.8839 | 4.9079 | 4.7921 | 4.8824 | 4.7318 | 4.7541 | 4.9273 | 4.7753 | 4.7753 | 4.8041 | 4.764 | 4.8277 | 4.7341 | 4.8127 | 4.794 | 4.8727 | 4.764 | 4.7566 | 4.7533 | 4.7461 | 4.7528 | 4.8296 | 4.7407 | 4.786 | 4.7744 | 4.9338 | 4.9162 | 4.8858 | 4.9388 | 4.9548 | 4.8846 | 4.7809 | 4.7715 | 4.9237 | 4.9507 | 4.9787 | 4.9576 | 4.9151 | 4.8764 | 4.9026 | 4.8727 | 4.9139 | 4.9064 | 4.9513 | 4.9458 | 4.9252 | 4.9005 | 4.9476 | 4.9401 | 4.9507 | 4.9625 | 4.9476 | 4.9738 | 4.8801 | 4.8277 | 4.8607 | 4.8951 | 4.9101 | 4.9738 | 4.9251 | 4.919 | 4.9196 | 4.8315 | 4.9064 | 4.9801 | 4.9064 | 4.8876 | 4.9139 | 4.8801 | 4.9464 | 4.8689 | 4.8202 | 4.8839 | 4.8539 | 4.7308 | 4.7603 | 4.7574 | 4.7206 | 4.8742 | 4.795 | 4.7398 | 4.8249 | 4.7571 | 4.7164 | 4.9577 | 4.8715 | 4.7173 | 4.7374 | 4.774 | 4.9315 | 4.9423 | 4.7574 | 4.7907 | 4.7491 | 4.7678 | 4.7407 | 4.7603 | 4.7828 | 4.7441 | 4.774 | 4.7744 | 4.8021 | 4.764 | 4.8376 | 4.8042 | 4.7944 | 4.828 | 4.7762 | 4.7558 | 4.824 | 4.726 | 4.7398 | 4.7978 | 4.7606 | 4.7828 | 4.7191 | 4.7603 | 4.7886 | 4.7502 | 4.7737 | 4.7329 | 4.7865 | 4.7374 | 4.7828 | 4.7453 | 4.736 | 4.7978 | 4.7566 | 4.928 | 4.9432 | 4.7825 | 4.7973 | 4.7744 | 4.73 | 4.969 | 4.8615 | 4.7992 | 4.7441 | 4.8864 | 4.76 | 4.9124 | 4.9182 | 4.7643 | 4.8036 | 4.8902 | 4.822 | 4.8258 | 4.8106 | 4.8114 | 4.7538 | 4.7378 | 4.7374 | 4.7946 | 4.9236 | 4.7937 | 4.7542 | 4.7735 | 4.8545 | 4.7695 | 4.7517 | 4.8561 | 4.9511 | 4.7538 | 4.9174 | 4.928 | 4.7299 | 4.7891 | 4.9318 |  |  | 5.0088 | 4.8542 | 4.8259 |  | 4.7468 | 4.8577 | 4.8749 | 4.8303 | 4.8266 | 4.8015 | 4.8277 | 4.7865 | 4.8652 | 4.8352 | 4.7704 | 4.8727 | 4.7724 | 4.9258 | 4.9306 | 5.1187 | 5.0522 | 5.0219 | 4.7633 | 4.8499 | 4.9043 | 4.9225 | 4.8678 | 4.7713 | 5.0682 | 4.9013 | 4.8942 | 4.7687 | 4.845 | 4.7731 | 4.8757 | 4.7811 | 4.8036 |  | 4.8146 | 4.7858 | 4.8756 | 4.7774 | 4.8718 |  |  | 5.0366 | 4.9765 | 4.9489 | 4.7941 | 4.7886 | 4.8475
2025-07-21 | 2.8003 | 2.8764 | 2.8614 | 2.8352 | 2.8384 | 2.809 | 2.8614 | 2.8876 | 2.8297 | 2.8408 | 2.8652 | 2.7978 | 2.8577 | 2.8192 | 2.8562 | 2.8386 | 2.7588 | 2.8509 | 2.8183 | 2.8519 | 2.7978 | 2.839 | 2.7969 | 2.8098 | 2.8211 | 2.8142 | 2.7347 | 2.8458 | 2.7249 | 2.8484 | 2.7266 | 2.8065 | 2.7571 | 2.7888 | 2.7955 | 2.7835 | 2.7749 | 2.7491 | 2.7341 | 2.7798 | 2.7378 | 2.8184 | 2.7678 | 2.8172 | 2.7865 | 2.8052 | 2.7589 | 2.7491 | 2.7578 | 2.7721 | 2.7228 | 2.7303 | 2.7998 | 2.7229 | 2.7589 | 2.8291 | 2.8295 | 2.7678 | 2.8065 | 2.7932 | 2.7449 | 2.8137 | 2.8202 | 2.884 | 2.8799 | 2.8674 | 2.894 | 2.8346 | 2.8659 | 2.8573 | 2.8685 | 2.8614 | 2.9213 | 2.8891 | 2.899 | 2.8634 | 2.9 | 2.8727 | 2.8494 | 2.8346 | 2.8457 | 2.794 | 2.8689 | 2.7925 | 2.8506 | 2.7678 | 2.8131 | 2.8011 | 2.8599 | 2.8419 | 2.8275 | 2.8685 | 2.7416 | 2.7865 | 2.8448 | 2.8491 | 2.8438 | 2.812 | 2.8625 | 2.8258 | 2.8678 | 2.8723 | 2.8112 | 2.8644 | 2.7589 | 2.8172 | 2.7346 | 2.7802 | 2.7517 | 2.7482 | 2.7305 | 2.8176 | 2.8331 | 2.8385 | 2.8408 | 2.8461 | 2.734 | 2.7799 | 2.7865 | 2.8213 | 2.7843 | 2.8671 | 2.8358 | 2.7865 | 2.7678 | 2.8365 | 2.8127 | 2.7978 | 2.8132 | 2.7333 | 2.7364 | 2.8201 | 2.8014 | 2.7783 | 2.7622 | 2.7647 | 2.8287 | 2.7703 | 2.8369 | 2.7828 | 2.8204 | 2.7665 | 2.8382 | 2.7243 | 2.7453 | 2.838 | 2.8172 | 2.8462 | 2.8481 | 2.8017 | 2.7969 | 2.8315 | 2.7289 | 2.8427 | 2.8592 | 2.8131 | 2.8596 | 2.8569 | 2.7981 | 2.8106 | 2.7461 | 2.7235 | 2.7374 | 2.7273 | 2.8418 | 2.7673 | 2.7311 | 2.7239 | 2.8019 | 2.7418 | 2.7764 | 2.7855 | 2.7239 | 2.7527 | 2.8337 | 2.7424 | 2.7462 | 2.7311 | 2.7239 | 2.7424 | 2.7622 | 2.7912 | 2.8316 | 2.8465 | 2.7276 | 2.7273 | 2.7636 | 2.7418 | 2.7615 | 2.8287 | 2.833 | 2.8538 | 2.789 | 2.8481 | 2.8598 | 2.7841 | 2.7655 | 2.8106 |  |  | 2.8456 | 2.7791 | 2.7642 |  | 2.7375 | 2.7753 | 2.8404 | 2.8536 | 2.8764 | 2.8296 | 2.861 | 2.9075 | 2.8985 | 2.785 | 2.7865 | 2.8985 | 2.7845 | 2.8078 | 2.893 | 2.9646 | 2.906 | 2.9028 | 2.7946 | 2.7627 | 2.8192 | 2.8082 | 2.8353 | 2.7803 | 2.7685 | 2.8007 | 2.8082 | 2.7452 | 2.8124 | 2.7348 | 2.796 | 2.7422 | 2.8065 |  | 2.8446 | 2.79 | 2.8557 | 2.7647 | 2.8283 |  |  | 2.884 | 2.8644 | 2.8416 | 2.7545 | 2.8512 | 2.8078
2025-07-22 | 4.4633 | 4.4536 | 4.4438 | 4.4607 | 4.4771 | 4.4682 | 4.603 | 4.588 | 4.4692 | 4.4297 | 4.6592 | 4.4996 | 4.5843 | 4.6047 | 4.5843 | 4.5498 | 4.5393 | 4.618 | 4.5704 | 4.5566 | 4.5918 | 4.4831 | 4.6016 | 4.6042 | 4.5877 | 4.6292 | 4.4588 | 4.6179 | 4.4544 | 4.5476 | 4.4578 | 4.501 | 4.4654 | 4.5793 | 4.4719 | 4.4931 | 4.573 | 4.4981 | 4.4794 | 4.4981 | 4.5131 | 4.5169 | 4.4981 | 4.5056 | 4.4869 | 4.5468 | 4.4978 | 4.573 | 4.4836 | 4.4512 | 4.4581 | 4.5281 | 4.6236 | 4.4561 | 4.4633 | 4.4871 | 4.531 | 4.5393 | 4.4644 | 4.511 | 4.4906 | 4.5333 | 4.4794 | 4.6019 | 4.6105 | 4.6009 | 4.6396 | 4.5642 | 4.6217 | 4.5993 | 4.6404 | 4.6105 | 4.6217 | 4.6479 | 4.6475 | 4.6009 | 4.6345 | 4.6592 | 4.6479 | 4.605 | 4.5843 | 4.618 | 4.5805 | 4.6367 | 4.6517 | 4.588 | 4.6251 | 4.6232 | 4.6105 | 4.6348 | 4.54 | 4.5438 | 4.5655 | 4.5468 | 4.4894 | 4.5094 | 4.5318 | 4.4831 | 4.4981 | 4.5506 | 4.5019 | 4.4794 | 4.5243 | 4.5356 | 4.5237 | 4.4831 | 4.531 | 4.4346 | 4.527 | 4.4544 | 4.446 | 4.5739 | 4.4977 | 4.5243 | 4.6217 | 4.5022 | 4.4597 | 4.4378 | 4.4178 | 4.5206 | 4.5056 | 4.5014 | 4.542 | 4.5243 | 4.5581 | 4.548 | 4.5363 | 4.5393 | 4.4578 | 4.4777 | 4.5462 | 4.5359 | 4.4978 | 4.5557 | 4.549 | 4.4755 | 4.493 | 4.458 | 4.4764 | 4.4981 | 4.5013 | 4.4633 | 4.5543 | 4.5774 | 4.4618 | 4.5774 | 4.5431 | 4.5761 | 4.5946 | 4.5808 | 4.5843 | 4.4944 | 4.561 | 4.5993 | 4.5169 | 4.5281 | 4.4981 | 4.4719 | 4.5076 | 4.4773 | 4.4343 | 4.4773 | 4.4613 | 4.4209 | 4.5825 | 4.4873 | 4.5682 | 4.4478 | 4.5114 | 4.4629 | 4.4764 | 4.48 | 4.4916 | 4.4327 | 4.5488 | 4.4735 | 4.4621 | 4.4697 | 4.4545 | 4.4356 | 4.4301 | 4.4175 | 4.4478 | 4.6218 | 4.4755 | 4.1111 | 4.4345 | 4.4364 | 4.4509 | 4.521 | 4.5114 | 4.5992 | 4.5568 | 4.6023 | 4.625 | 4.5795 | 4.6409 | 4.6023 |  |  | 4.6143 | 4.4865 | 4.5048 |  | 4.5147 | 4.5468 | 4.5543 | 4.5704 | 4.5019 | 4.6367 | 4.5431 | 4.6367 | 4.6105 | 4.5206 | 4.5652 | 4.633 | 4.4378 | 4.5913 | 4.6753 | 4.7873 | 4.7074 | 4.7649 | 4.4829 | 4.4716 | 4.5027 | 4.5823 | 4.5691 | 4.4633 | 4.6346 | 4.5825 | 4.5863 | 4.4398 | 4.4911 | 4.4426 | 4.4406 | 4.4519 | 4.4421 |  | 4.5316 | 4.4444 | 4.5373 | 4.5342 | 4.4406 |  |  | 4.698 | 4.6277 | 4.6274 | 4.5338 | 4.4403 | 4.5324
2025-07-23 | 1.6629 | 1.6802 | 1.6629 | 1.6517 | 1.6823 | 1.6891 | 1.6955 | 1.6779 | 1.6539 | 1.7007 | 1.6854 | 1.6816 | 1.7135 | 1.6507 | 1.682 | 1.6891 | 1.7004 | 1.6839 | 1.7079 | 1.684 | 1.6989 | 1.7079 | 1.7065 | 1.7019 | 1.7041 | 1.6861 | 1.694 | 1.6746 | 1.6679 | 1.7052 | 1.6812 | 1.6879 | 1.6549 | 1.6619 | 1.6891 | 1.7029 | 1.6854 | 1.6779 | 1.7154 | 1.7191 | 1.6592 | 1.7116 | 1.6891 | 1.6704 | 1.6779 | 1.6929 | 1.6629 | 1.6779 | 1.6647 | 1.6827 | 1.7052 | 1.6929 | 1.7059 | 1.6746 | 1.6802 | 1.6649 | 1.7025 | 1.6816 | 1.7012 | 1.6879 | 1.6891 | 1.6661 | 1.6742 | 1.6761 | 1.6975 | 1.7196 | 1.729 | 1.6885 | 1.7127 | 1.7169 | 1.727 | 1.7064 | 1.6742 | 1.7285 | 1.7065 | 1.6546 | 1.7092 | 1.7109 | 1.6831 | 1.6802 | 1.6936 | 1.7154 | 1.7075 | 1.7116 | 1.6734 | 1.6891 | 1.667 | 1.6678 | 1.7034 | 1.6929 | 1.673 | 1.703 | 1.6742 | 1.7004 | 1.6879 | 1.6918 | 1.6742 | 1.6891 | 1.6816 | 1.6816 | 1.6974 | 1.7105 | 1.6891 | 1.6925 | 1.6679 | 1.6816 | 1.6579 | 1.6628 | 1.6667 | 1.6679 | 1.6456 | 1.7086 | 1.6513 | 1.6882 | 1.6944 | 1.6551 | 1.6828 | 1.6912 | 1.6549 | 1.6704 | 1.6966 | 1.6679 | 1.6746 | 1.6891 | 1.6966 | 1.6679 | 1.6779 | 1.6966 | 1.6556 | 1.638 | 1.6546 | 1.6505 | 1.6726 | 1.6842 | 1.6469 | 1.6573 | 1.6503 | 1.6941 | 1.6935 | 1.6517 | 1.6546 | 1.6906 | 1.7004 | 1.7117 | 1.7041 | 1.6456 | 1.6674 | 1.6923 | 1.6885 | 1.6999 | 1.6353 | 1.6704 | 1.6546 | 1.6966 | 1.6989 | 1.6689 | 1.7019 | 1.6957 | 1.678 | 1.6848 | 1.6734 | 1.697 | 1.6566 | 1.6633 | 1.6902 | 1.6436 | 1.6705 | 1.6498 | 1.6856 | 1.6945 | 1.6473 | 1.6873 | 1.6869 | 1.6764 | 1.6758 | 1.6629 | 1.6818 | 1.6932 | 1.6936 | 1.6742 | 1.6923 | 1.6667 | 1.6431 | 1.6785 | 1.6643 | 1.6397 | 1.6764 | 1.64 | 1.6553 | 1.6573 | 1.7235 | 1.6939 | 1.6932 | 1.7083 | 1.697 | 1.6818 | 1.7318 | 1.7083 |  |  | 1.6596 | 1.6548 | 1.7036 |  | 1.6986 | 1.6629 | 1.6779 | 1.706 | 1.7154 | 1.6816 | 1.6899 | 1.6929 | 1.7434 | 1.7079 | 1.6816 | 1.7322 | 1.6746 | 1.7155 | 1.751 | 1.7331 | 1.7351 | 1.7806 | 1.6835 | 1.6564 | 1.6956 | 1.7115 | 1.6868 | 1.6664 | 1.7097 | 1.6768 | 1.6679 | 1.6546 | 1.6472 | 1.6631 | 1.7055 | 1.6685 | 1.6622 |  | 1.7322 | 1.6754 | 1.6617 | 1.691 | 1.6783 |  |  | 1.7388 | 1.7437 | 1.7163 | 1.6783 | 1.7102 | 1.6852
2025-07-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-08-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-08-04
2025-08-05
2025-08-06
2025-08-07
2025-08-08
2025-08-09
2025-08-10
Formulas:
Date = [Date, row above]+1

## Inv_SY
| 289.25 | 289.25 | 267 | 267 | 289.25 | 267 | 267 | 267 | 278.125 | 278.125 | 267 | 267 | 267 | 244.75 | 267 | 267 | 267 | 267 | 289.25 | 289.25 | 267 | 267 | 289.25 | 300.375 | 289.25 | 289.25 | 289.25 | 300.375 | 300.375 | 300.375 | 300.375 | 300.375 | 254.4 | 334.55 | 267 | 298.9 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 289.25 | 267 | 278.125 | 278.125 | 267 | 267 | 300.375 | 300.375 | 289.25 | 300.375 | 300.375 | 267 | 300.375 | 300.375 | 267 | 298.9 | 267 | 239.25 | 289.25 | 289.25 | 289.25 | 289.25 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 300.375 | 300.375 | 267 | 267 | 289.25 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 278.125 | 289.25 | 267 | 267 | 300.375 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 267 | 300.375 | 298.9 | 267 | 300.375 | 289.25 | 289.25 | 300.375 | 300.375 | 267 | 267 | 298.9 | 300.375 | 300.375 | 267 | 267 | 300.375 | 300.375 | 267 | 267 | 300.375 | 267 | 267 | 300.375 | 300.375 | 289.25 | 289.25 | 289.25 | 244.75 | 286 | 286 | 286 | 286 | 278.125 | 267 | 289.25 | 289.25 | 267 | 289.25 | 267 | 289.25 | 267 | 244.75 | 289.25 | 289.25 | 289.25 | 267 | 300.375 | 267 | 267 | 267 | 267 | 267 | 264 | 264 | 297 | 264 | 297 | 297 | 297 | 275 | 264 | 297 | 264 | 275 | 275 | 275 | 297 | 275 | 297 | 264 | 264 | 264 | 297 | 264 | 286 | 297 | 297 | 275 | 286 | 297 | 275 | 275 | 275 | 286 | 264 | 264 | 264 | 264 | 264 | 264 | 220 | 264 | 0 | 0 | 227.4 | 190.35 | 270.6 | 0 | 292.6 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 300.375 | 223.3 | 223.3 | 191.4 | 159.5 | 207.9 | 239.8 | 278.125 | 300.375 | 289.25 | 289.25 | 278.125 | 289.25 | 300.38 | 300.375 | 257.4 | 277.2 | 257.4 | 267.3 | 247.5 | 0 | 353.2 | 287.1 | 100.5 | 267.3 | 257.4 | 0 | 0 | 239.25 | 255.2 | 230.15 | 257.4 | 241.2 | 66958.455
Date | BLK1_INV1 | BLK1_INV2 | BLK1_INV3 | BLK1_INV4 | BLK1_INV5 | BLK1_INV6 | BLK1_INV7 | BLK1_INV8 | BLK1_INV9 | BLK1_INV10 | BLK1_INV11 | BLK1_INV12 | BLK1_INV13 | BLK1_INV14 | BLK1_INV15 | BLK1_INV16 | BLK1_INV17 | BLK1_INV18 | BLK1_INV19 | BLK1_INV20 | BLK1_INV21 | BLK1_INV22 | BLK1_INV23 | BLK1_INV24 | BLK1_INV25 | BLK1_INV26 | BLK1_INV27 | BLK1_INV28 | BLK1_INV29 | BLK1_INV30 | BLK1_INV31 | BLK1_INV32 | BLK2_INV1 | BLK2_INV2 | BLK2_INV3 | BLK2_INV4 | BLK2_INV5 | BLK2_INV6 | BLK2_INV7 | BLK2_INV8 | BLK2_INV9 | BLK2_INV10 | BLK2_INV11 | BLK2_INV12 | BLK2_INV13 | BLK2_INV14 | BLK2_INV15 | BLK2_INV16 | BLK2_INV17 | BLK2_INV18 | BLK2_INV19 | BLK2_INV20 | BLK2_INV21 | BLK2_INV22 | BLK2_INV23 | BLK2_INV24 | BLK2_INV25 | BLK2_INV26 | BLK2_INV27 | BLK2_INV28 | BLK2_INV29 | BLK2_INV30 | BLK2_INV31 | BLK2_INV32 | BLK3_INV1 | BLK3_INV2 | BLK3_INV3 | BLK3_INV4 | BLK3_INV5 | BLK3_INV6 | BLK3_INV7 | BLK3_INV8 | BLK3_INV9 | BLK3_INV10 | BLK3_INV11 | BLK3_INV12 | BLK3_INV13 | BLK3_INV14 | BLK3_INV15 | BLK3_INV16 | BLK3_INV17 | BLK3_INV18 | BLK3_INV19 | BLK3_INV20 | BLK3_INV21 | BLK3_INV22 | BLK3_INV23 | BLK3_INV24 | BLK3_INV25 | BLK3_INV26 | BLK3_INV27 | BLK3_INV28 | BLK3_INV29 | BLK3_INV30 | BLK3_INV31 | BLK4_INV1 | BLK4_INV2 | BLK4_INV3 | BLK4_INV4 | BLK4_INV5 | BLK4_INV6 | BLK4_INV7 | BLK4_INV8 | BLK4_INV9 | BLK4_INV10 | BLK4_INV11 | BLK4_INV12 | BLK4_INV13 | BLK4_INV14 | BLK4_INV15 | BLK4_INV16 | BLK4_INV17 | BLK4_INV18 | BLK4_INV19 | BLK4_INV20 | BLK4_INV21 | BLK4_INV22 | BLK4_INV23 | BLK4_INV24 | BLK4_INV25 | BLK4_INV26 | BLK4_INV27 | BLK4_INV28 | BLK4_INV29 | BLK4_INV30 | BLK4_INV31 | BLK5_INV1 | BLK5_INV2 | BLK5_INV3 | BLK5_INV4 | BLK5_INV5 | BLK5_INV6 | BLK5_INV7 | BLK5_INV8 | BLK5_INV9 | BLK5_INV10 | BLK5_INV11 | BLK5_INV12 | BLK5_INV13 | BLK5_INV14 | BLK5_INV15 | BLK5_INV16 | BLK5_INV17 | BLK5_INV18 | BLK5_INV19 | BLK5_INV20 | BLK5_INV21 | BLK5_INV22 | BLK5_INV23 | BLK5_INV24 | BLK5_INV25 | BLK5_INV26 | BLK5_INV27 | BLK5_INV28 | BLK5_INV29 | BLK5_INV30 | BLK5_INV31 | BLK5_INV32 | BLK6_INV1 | BLK6_INV2 | BLK6_INV3 | BLK6_INV4 | BLK6_INV5 | BLK6_INV6 | BLK6_INV7 | BLK6_INV8 | BLK6_INV9 | BLK6_INV10 | BLK6_INV11 | BLK6_INV12 | BLK6_INV13 | BLK6_INV14 | BLK6_INV15 | BLK6_INV16 | BLK6_INV17 | BLK6_INV18 | BLK6_INV19 | BLK6_INV20 | BLK6_INV21 | BLK6_INV22 | BLK6_INV23 | BLK6_INV24 | BLK6_INV25 | BLK6_INV26 | BLK6_INV27 | BLK6_INV28 | BLK6_INV29 | BLK6_INV30 | BLK6_INV31 | BLK6_INV32 | BLK7_INV1 | BLK7_INV2 | BLK7_INV3 | BLK7_INV4 | BLK7_INV5 | BLK7_INV6 | BLK7_INV7 | BLK7_INV8 | BLK7_INV9 | BLK7_INV10 | BLK7_INV11 | BLK7_INV12 | BLK7_INV13 | BLK7_INV14 | BLK7_INV15 | BLK7_INV16 | BLK7_INV17 | BLK7_INV18 | BLK7_INV19 | BLK7_INV20 | BLK7_INV21 | BLK7_INV22 | BLK7_INV23 | BLK7_INV24 | BLK7_INV25 | BLK7_INV26 | BLK7_INV27 | BLK7_INV28 | BLK7_INV29 | BLK7_INV30 | BLK7_INV31 | BLK7_INV32 | BLK8_INV1 | BLK8_INV2 | BLK8_INV3 | BLK8_INV4 | BLK8_INV5 | BLK8_INV6 | BLK8_INV7 | BLK8_INV8 | BLK8_INV9 | BLK8_INV10 | BLK8_INV11 | BLK8_INV12 | BLK8_INV13 | BLK8_INV14 | BLK8_INV15 | BLK8_INV16 | BLK8_INV17 | BLK8_INV18 | BLK8_INV19 | BLK8_INV20 | BLK8_INV21 | BLK8_INV22 | BLK8_INV23 | BLK8_INV24 | BLK8_INV25 | BLK8_INV26 | BLK8_INV27 | BLK8_INV28
2025-06-22 | 0.3864% | 0.1907% | -0.2098% | 0.241% | -0.3886% | 0.8419% | 0.5768% | 1.195% | 0.9657% | 0.9657% | -0.3954% | 1.372% | -1.429% | 0.85% | 1.019% | -2.782% | 0.2233% | 1.858% | 1.651% | 0.4272% | 0.1349% | 0.3117% | 0.09275% | 0.5572% | 0.4272% | 1.08% | 0.6475% | 0.95% | 1.971% | -2.664% | -1.368% | -5.885% | 1.106% | -2.704% | 1.708% | 1.053% | 2.009% | 0.3824% | 1.735% | 1.372% | -0.04186% | 0.3647% | 0.2233% | -0.9257% | 1.461% | -0.2186% | -2.02% | 0.8419% | -1.054% | -6.382% | 1.814% | 1.682% | 2.207% | 1.343% | 0.7944% | 0.4% | -0.1499% | 0.04652% | -0.2284% | 1.343% | 0.5768% | 1.843% | 1.381% | 3.563% | 0.2641% | 0.4272% | 1.659% | -0.8536% | 0.04652% | 0.4089% | 0.6652% | 0.2233% | -0.9257% | 1.204% | -0.2284% | 0.7143% | 0.895% | 1.231% | 0.9922% | 2.116% | -0.04186% | -0.2098% | 0.347% | 1.602% | 1.726% | 1.293% | 1.089% | 1.081% | -0.6694% | -1.438% | -0.7567% | -2.183% | -0.04186% | -0.3689% | 0.07795% | 0.6652% | 0.05536% | -0.3954% | 1.293% | 1.036% | 0.3117% | 1.054% | 0.2233% | -0.8638% | 0.73% | 0.3559% | -3.999% | 0.03496% | 1.337% | -0.307% | -0.3152% | -6.181% | -0.3384% | 0.3372% | 1.531% | 0.8685% | -2.578% | -1.933% | -1.218% | -0.8196% | 1.24% | -6.796% | -8.76% | 0.1526% | 1.019% | 0.1722% | 1.001% | 0.7447% | -2.507% | -0.6055% | 0.3049% | -2.02% | 1.259% | 1.332% | 0.5784% | 1.568% | 1.568% | 0.9909% | 0.1172% | -2.693% | 0.6394% | -0.9923% | 0.04652% | 0.672% | 0.4% | -6.287% | -0.9257% | 0.3679% | 0.8596% | 0.5251% | 0.5904% | 1.399% | 1.17% | 0.2321% | 0.3028% | -0.2363% | 0.3205% | 0.9745% | 0.9778% | 1.255% | 0.1903% | -0.6043% | -0.3898% | 0.3094% | -0.6043% | 1.796% | -0.4434% | -0.4454% | -1.498% | -1.079% | -1.182% | -0.856% | 0.5875% | -1.139% | 0.7464% | -1.588% | 0.08399% | 0.7544% | 1.7% | 1.684% | -1.121% | -0.7473% | 0.9609% | 1.255% | 0.9496% | 1.025% | -0.4613% | 0.3968% | 0.9203% | -5.775% | -2.571% | -0.6937% | 0.379% | -1.588% | -2.017% | -0.1305% | 0.3325% | 0.4952% |  |  | 5.95% | -0.7006% | -0.4996% |  | -2.231% | -0.9257% | -1.933% | -0.8638% | -1.721% | -2.243% | -0.7843% | -0.8903% | -0.2098% | -1.058% | -0.2628% | -1.951% | -0.252% | 1.995% | 2.506% | 1.449% | 2.7% | 1.788% | -1.081% | -1.487% | -2.445% | -1.815% | -2.232% | -1.31% | -1.961% | -1.123% | -2.318% | -1.835% | 0.9451% | -1.643% | 1.147% | -0.154% | 0.8735% |  | 0.1944% | 0.5218% | -1.149% | -2.096% | -1.814% |  |  | 2.577% | 1.806% | 17.19% | -1.814% | 0.8668%
2025-06-23 | 2.577% | 1.27% | 1.856% | 1.346% | 0.8658% | 1.429% | 1.294% | 1.346% | -6.857% | 1.291% | 2.168% | 2.71% | 2.179% | 1.231% | 0.8353% | 0.7937% | 0.5541% | 3.96% | 0.5005% | 0.3466% | 0.9395% | 1.231% | 0.5678% | 1.787% | 1.673% | 0.7793% | 1.818% | 0.7312% | 1.629% | 1.018% | 2.666% | -6.499% | 2.222% | 2.402% | 1.064% | -0.3626% | 1.721% | 3.21% | 2.189% | 1.846% | 0.2313% | 3.095% | 4.053% | 3.585% | 1.585% | 2.002% | -8.575% | -0.1124% | 0.9811% | -8.917% | 0.9811% | 1.335% | 0.9071% | 1.037% | -0.5859% | 1.833% | 1.787% | 1.012% | 0.6664% | 2.24% | 1.658% | 0.4747% | 1.377% | 3.442% | 1.164% | 1.654% | 0.3659% | -0.2013% | 1.648% | 1.45% | 1.585% | 0.7208% | 0.08547% | 0.08547% | -0.01867% | 1.694% | -0.2038% | 2.366% | 1.335% | 3.048% | 2.127% | 0.5958% | 1.439% | 3.002% | 1.085% | 1.346% | 1.533% | 0.8978% | -0.4248% | -1.508% | -0.02867% | -2.23% | -0.5394% | -0.227% | -0.8519% | -0.2166% | -22.41% | 2.606% | -0.4353% | -0.01867% | 1.023% | -0.227% | -0.956% | -1.414% | -0.01867% | -0.956% | -0.01867% | 0.4189% | -0.956% | -1.963% | 0.4812% | 1.212% | -0.9444% | -1.778% | -0.956% | 0.3979% | -10.04% | 0.9071% | -1.963% | 1.596% | -0.4353% | -3.759% | -5.934% | -0.956% | 0.7104% | 0.8145% | -2.091% | 0.4083% | -0.01867% | -3.166% | -1.076% | -2.009% | 0.4139% | -2.291% | -0.8271% | 0.2133% | -15.44% | 0.04797% | -1.018% | -2.727% | -0.05713% | -1.903% | 0.2313% | 0.1736% | -1.414% | 0.3659% | 0.5021% | -0.4731% | 2.231% | 1.962% | 0.7504% | 1.148% | 0.0739% | 0.2313% | 1.439% | 0.2105% | 0.5125% | -0.7477% | 1.044% | -0.03063% | 1.071% | -3.001% | -7.365% | -7.478% | -1.785% | 0.5108% | -0.9891% | -7.066% | -0.9891% | -2.401% | 0.2681% | -2.058% | -0.7551% | -0.9049% | 0.7617% | 0.496% | -0.8838% | -0.5362% | -0.6053% | 0.1695% | -0.8271% | -2.534% | 0.2748% | 0.1063% | -0.3896% | 0.434% | -1.815% | 0.1973% | -6.972% | -1.799% | 0.0747% | -1.432% | -0.8838% | -0.8101% | 0.7594% | -1.937% | -1.41% | -1.937% |  |  | 5.164% | -10.03% | -2.006% |  | 1.241% | -1.737% | -6.132% | -1.966% | -0.06033% | 0.7937% | 1.752% | 1.658% | -1.997% | 1.45% | 1.814% | -1.997% | -0.01867% | 1.833% | 3.359% | 1.989% | 1.408% | 3.035% | -0.8888% | 0.5609% | 3.231% | 1.935% | 1.087% | 2.365% | 3.251% | 3.115% | 2.823% | 1.148% | 1.722% | -1.591% | 0.4585% | -2.045% | -1.512% |  | 2.398% | -1.207% | 2.929% | -2.836% | -2.556% |  |  | 9.602% | 3.515% | 16.47% | -2.988% | -0.7145%
2025-06-24 | -1.037% | 1.411% | 1.953% | 0.5285% | 0.4248% | 1.385% | 1.339% | 1.832% | 1.162% | 1.809% | 3.104% | 2.877% | -2.502% | 4.61% | 1.619% | 1.559% | 0.7331% | 0.5058% | 0.7045% | 0.6835% | 1.718% | 2.188% | -0.5892% | 2.126% | 2.32% | 1.425% | -1.463% | 0.5504% | 1.648% | -2.022% | -1.988% | -2.285% | 0.02147% | 2.704% | -0.676% | 0.03155% | -2.774% | -2.108% | -0.229% | 0.7255% | -0.979% | -1.327% | 0.4604% | -0.2366% | 1.142% | 1.582% | -1.477% | -0.4336% | -0.1254% | -1.456% | 0.8997% | 0.7937% | 2.308% | 0.9545% | -0.6031% | 1.278% | 1.123% | 1.301% | -0.1297% | 1.244% | 0.9982% | 1.811% | 0.7331% | 9.001% | 1.614% | 0.7045% | 1.544% | -1.659% | 0.6119% | 0.4301% | 0.5285% | -0.2063% | 2.369% | 0.1573% | 0.4494% | -1.672% | 1.002% | 0.68% | -0.1154% | 1.152% | 1.703% | 2.021% | 0.5816% | 1.566% | 0.7255% | 1.119% | 0.8846% | 0.7482% | -1.381% | -1.987% | -1.638% | -2.016% | 2.135% | -1.464% | -0.1095% | -0.7063% | -2.426% | 2.112% | -0.3351% | 1.127% | 3.21% | 0.271% | 0.9603% | -0.7517% | 1.109% | -1.706% | 3.473% | -49.48% | 1.907% | 0.6784% | 1.197% | 0.3549% | 0.3417% | 1.076% | 2.127% | 1.771% | -2.114% | 0.07905% | 0.2003% | 1.097% | 2.475% | -3.867% | -6.018% | 1.354% | -0.8199% | -0.4125% | -0.6533% | -2.093% | 0.03191% | -0.8637% | -1.393% | -2.75% | -1.002% | -0.7373% | 2.026% | -2.628% | 0.6395% | 1.531% | 0.5582% | -0.07751% | -1.386% | -1.946% | -0.3654% | 0.7814% | -2.767% | -0.9458% | -2.131% | -0.0844% | -1.121% | -1.414% | 0.7395% | -0.4942% | -0.4058% | -0.5775% | -2.35% | -2.191% | -2.835% | -1.259% | 1.679% | -0.1602% | 0.7192% | -1.769% | -1.521% | -1.44% | -0.9766% | 0.4285% | -0.9571% | -0.7519% | -1.317% | -2.418% | 0.5682% | -1.624% | -1.658% | 0.8036% | 0.8145% | 0.2918% | 0.491% | -1.348% | -0.8609% | 2.299% | -1.758% | -1.038% | -1.862% | 4.444% | 1.205% | 0.4399% | 0.8772% | -0.7042% | -1.896% | -0.2799% | 1.004% | 0.2995% | -2.083% | -0.2369% | 0.514% | -1.846% | 1.429% | -1.164% |  |  | 4.604% | -2.133% | -1.93% |  | -1.05% | -1.737% | -1.229% | -1.244% | 0.4225% | 0.5816% | 1.203% | 1.218% | 1.044% | -2.343% | 0.3922% | 1.135% | 0.3551% | 0.8467% | 3.626% | -0.2694% | -0.2392% | 1.578% | -0.354% | -1.708% | 0.6528% | 0.8265% | -0.1067% | -0.4423% | 1.489% | 0.3829% | 0.3215% | -0.5876% | -2.166% | -2.288% | -2.362% | 0.1282% | 0.4481% |  | 3.11% | -1.282% | 5.562% | -1.552% | -2.284% |  |  | 9.99% | 1.23% | 14.34% | -2.299% | -1.172%
2025-06-25 | -0.6261% | -0.4485% | 2.067% | 1.975% | 1.022% | 1.475% | 1.805% | 0.1507% | 0.9253% | 1.147% | 0.9896% | 0.7972% | -2.705% | -0.06484% | 1.359% | 1.251% | 0.828% | 0.3816% | 0.1625% | 0.6172% | 1.69% | 1.729% | -0.6332% | 1.823% | 2.031% | 0.7877% | -2.587% | 0.2225% | 0.7083% | -2.767% | -2.473% | -3.02% | 1.395% | -0.2977% | -0.1187% | 0.6002% | 0.7895% | -1.373% | 0.2892% | 1.959% | -0.4266% | -1.327% | 0.5586% | -0.2727% | 1.336% | 1.444% | 0.2833% | 0.09679% | 0.2085% | -2.947% | 1.074% | 0.905% | 0.5509% | 1.112% | -1.408% | 0.3799% | 0.1678% | 0.03521% | 0.5372% | 0.202% | 1.621% | 0.5039% | 1.113% | 8.116% | 1.548% | 0.6812% | 1.903% | -1.109% | 1.02% | 0.6202% | 1.02% | 0.03521% | 1.528% | 1.036% | 1.803% | -0.2975% | 1.94% | 1.174% | 0.1122% | 1.953% | 1.675% | 0.1353% | 0.5047% | 1.759% | 0.3354% | 0.828% | 0.6894% | 0.4816% | -1.65% | -2.451% | -1.218% | -2.203% | 2.375% | -0.6267% | 0.3867% | 0.01212% | 0.3123% | 2.106% | 0.8588% | 1.428% | 1.682% | 0.2815% | 1.221% | 0.1507% | 1.611% | -0.7037% | 1.96% | -2.769% | 0.7587% | 0.4483% | 0.9867% | 0.9227% | -0.3796% | 0.3114% | 1.921% | -2.466% | -2.466% | -0.2633% | 0.3525% | 1.336% | 1.528% | -3.835% | -6.4% | 1.336% | -0.696% | 0.373% | -0.696% | -0.4574% | -3.274% | -0.9269% | -0.3846% | -1.287% | -0.8819% | 1.035% | 0.6756% | -1.257% | -0.1148% | 1.545% | 0.06816% | -2.081% | -1.827% | -2.537% | 0.3123% | -0.4556% | -2.674% | -1.045% | -1.419% | 0.5649% | -0.3348% | 0.5177% | -0.4556% | -0.08024% | 1.7% | -0.01097% | -1.85% | -2.035% | -2.035% | -0.02636% | -0.6962% | -2.572% | -2.098% | -2.339% | -2.576% | -3.198% | -0.2093% | -1.56% | -2.603% | -0.9497% | -1.568% | -1.844% | -1.537% | -1.88% | -2.133% | -0.506% | -1.87% | -1.778% | -0.8441% | -1.179% | -2.327% | 0.00434% | -2.335% | -2.894% | -0.1885% | 1.796% | -1.078% | -1.828% | -0.3341% | -0.5807% | -1.059% | -2.594% | -0.416% | -2.564% | -1.568% | -1.607% | 0.7516% | -1.303% | 0.06194% | 0.4169% |  |  | 6.132% | -2.619% | -1.091% |  | -0.4294% | -2.089% | -0.8807% | -2.166% | 0.3046% | 0.7587% | 1.675% | 1.813% | -0.7037% | -2.135% | 1.405% | -0.7114% | 1.42% | 3.773% | 6.203% | 3.35% | 3.826% | 1.657% | -1.152% | -2.115% | 0.9622% | 0.09251% | -1.528% | -1.493% | 1.561% | -0.9245% | -0.058% | -2.069% | -2.278% | -2.052% | -2.517% | -2.514% | 0.01212% |  | 4.061% | -2.101% | 2.854% | -1.853% | -1.751% |  |  | 8.348% | 1.061% | 17.24% | -1.599% | 1.44%
2025-06-26 | 0.2475% | 0.8927% | 2.857% | 2.603% | 1.205% | 2.004% | 1.405% | 1.812% | 0.9542% | 1.293% | 2.657% | 1.973% | -0.9453% | 1.549% | 0.4756% | 0.322% | -0.3155% | -0.7763% | -0.9152% | -0.6032% | 0.6138% | 0.8135% | -1.638% | 0.4875% | 0.524% | -0.6528% | -2.9% | -1.404% | -0.7482% | -1.404% | -2.824% | -2.045% | 0.551% | 2.641% | -0.8608% | -0.3407% | -0.1465% | -2.335% | -0.7994% | 0.9825% | -1.283% | -2.205% | -0.6304% | -1.452% | 0.4679% | 1.006% | 0.3114% | -0.7226% | 0.7699% | -2.578% | 1.413% | 1.182% | 0.4807% | 0.9245% | -2.255% | 0.4398% | -0.3658% | 1.128% | -0.4273% | 0.6309% | 0.6215% | 1.532% | 0.4218% | 8.701% | 1.049% | 0.05612% | 1.361% | -1.029% | 0.6753% | 0.13% | 0.8903% | 0.08389% | 0.02245% | -0.06972% | -0.5502% | -2.141% | 0.3851% | -0.06972% | -0.8762% | 0.2121% | 0.5985% | 1.029% | -0.06204% | 0.9902% | -0.3539% | 0.3911% | 0.5524% | 0.5908% | -1.66% | -2.228% | -1.014% | -2.049% | 1.866% | 0.8827% | -0.3522% | -0.8915% | -1.099% | 1.436% | -0.4998% | 0.4526% | 0.706% | -0.9453% | 0.06085% | -1.176% | -0.714% | -6.183% | 1.928% | -1.514% | 0.9134% | -0.6526% | -0.511% | 0.4106% | -0.2361% | 0.1872% | 1.236% | -2.374% | -1.528% | -2.291% | -1.39% | 0.6292% | 1.873% | -4.353% | -7.603% | 0.2068% | 0.5447% | 0.2076% | -0.953% | -1.045% | -2.298% | -1.124% | -1.348% | -1.333% | -1% | 0.7451% | -0.3987% | -1.539% | 0.2538% | 0.4689% | -0.3729% | -0.1388% | -1.638% | -2.085% | 0.491% | 1.07% | -2.32% | -0.9861% | -1.637% | 0.09995% | -1.844% | -0.4756% | -0.0005923% | -1.299% | 0.7401% | -0.9299% | -2.566% | -1.836% | -2.696% | -0.9146% | 0.1726% | -1.264% | -1.188% | -1.684% | -1.878% | -0.9736% | -0.6353% | -1.485% | -1.699% | 0.1933% | -0.5731% | 1.043% | 0.1477% | -0.7173% | -1.844% | 0.006027% | -1.885% | -1.264% | -1.21% | 0.2813% | -1.188% | 1.058% | -0.7285% | -1.85% | -2.61% | 2.243% | 0.2467% | -0.9391% | 0.2223% | 0.2297% | -0.1207% | -1.689% | 0.3435% | -0.1537% | -0.0993% | 0.1648% | 0.2036% | -0.7285% | -0.2624% | 1.066% |  |  | 6.502% | -1.35% | -1.278% |  | 1.111% | -1.237% | -0.8147% | -1.567% | -0.0774% | -0.4768% | 2.234% | 1.62% | -0.06972% | -0.9222% | 0.7675% | 1.758% | 1.266% | 3.56% | 5.702% | 4.104% | 4.409% | 2.727% | -1.431% | 0.5671% | 1.131% | 0.8152% | 0.03486% | -0.07149% | 1.094% | 0.7934% | 2.215% | 1.027% | -1.115% | -0.2994% | -1.704% | -1.049% | -1.327% |  | 4.536% | -1.673% | 4.717% | -2.123% | -1.808% |  |  | 8.084% | 2.743% | 17.71% | -2.342% | 2.542%
2025-06-27 | 3.027% | 3.243% | 3.089% | 4.041% | 3.955% | 3.738% | 2.361% | 3.79% | -0.02875% | 0.6282% | 3.097% | 3.842% | -0.8358% | 0.1746% | 2.794% | 3.184% | 2.309% | 2.179% | 0.08449% | 0.2844% | 1.148% | 1.512% | 0.5883% | 0.1893% | 1.38% | 1.204% | -2.322% | 1.86% | 1.46% | -2.213% | -2.552% | -1.659% | 0.2298% | 0.7057% | -1% | -1.297% | -0.238% | -2.109% | -0.4719% | 1.59% | -1.191% | -1.841% | -0.3333% | -1.217% | 1.035% | 1.408% | -3.082% | 0.1691% | 1.46% | -2.881% | 1.451% | 1.616% | 0.1893% | 1.16% | -3.082% | 0.197% | 1.044% | 2.136% | 0.01222% | 0.5358% | 1.131% | 1.481% | 0.455% | 6.49% | 0.6762% | 1.22% | 1.7% | 0.06849% | -0.1601% | 0.02185% | 0.6542% | 1.503% | 0.9834% | 0.7495% | 0.4665% | -0.8887% | 0.08922% | 1.425% | 1.174% | 0.9801% | 0.7928% | 0.2817% | 1.339% | 1.633% | 1.295% | 0.3857% | 0.3857% | -0.03013% | 0.03917% | -0.9917% | -0.5028% | -1.963% | 1.096% | 0.9748% | 1.383% | 1.443% | -33.75% | 1.581% | 1.382% | 1.165% | 0.7062% | 1.624% | 2.326% | -2.308% | 0.505% | 2.118% | 1.244% | -2.667% | 1.512% | 1.375% | 1.788% | 0.6602% | 0.5512% | 1.706% | -0.1861% | -2.716% | -2.953% | -1.774% | -1.281% | 1.841% | 2.898% | -4.808% | -5.478% | 0.00452% | 0.8275% | -1.589% | -0.03013% | -1.156% | -2.429% | -2.282% | -2.586% | -1.571% | -1.339% | 0.3258% | -0.5089% | -1.981% | -0.8728% | -1.334% | -1.892% | -2.302% | -1.443% | -2.354% | -2.239% | -1.595% | -2.014% | -1.555% | -2.014% | -2.226% | -1.523% | -2.394% | -1.947% | -2.707% | -1.212% | -2.56% | -2.014% | -2.534% | -0.7665% | -1.2% | -0.04185% | -1.926% | -1.639% | -0.8742% | -2.426% | -2.278% | -0.2064% | -1.08% | -1.032% | -2.854% | -0.7077% | -1.391% | -1.248% | -2.753% | -1.624% | -0.5328% | -2.332% | -1.654% | -0.6989% | -1.777% | -2.535% | -0.1032% | -1.981% | -2.332% | -1.523% | 2.26% | -0.792% | -1.297% | -0.516% | -0.4655% | 0.754% | -2.143% | -0.8128% | -0.4887% | -1.777% | -0.2696% | -0.9005% | -2.477% | 0.5206% | -1.514% |  |  | -99.99% | -1.976% | -1.796% |  | 1.033% | 0.3944% | 1.451% | -2.256% | 1.451% | 0.5156% | 1.157% | 1.772% | 0.03917% | -1.953% | -0.2727% | 0.1778% | 1.814% | 4.001% | 6.079% | 5.654% | 5.281% | 1.685% | -1.35% | 0.4387% | 3.83% | 2.13% | 0.9161% | 1.388% | 4.412% | 2.755% | 1.668% | 0.02762% | -1.954% | -0.9384% | -1.064% | -1.224% | -1.714% |  | 6.157% | -1.623% | 0.2988% | -2.037% | -1.909% |  |  | 8.384% | 3.559% | 18.76% | 0.733% | 1.179%
2025-06-28 | 0.8036% | 2.735% | 0.03415% | 0.3048% | 2.61% | 2.418% | 3.105% | 3.105% | 1.828% | 2.338% | 0.8356% | 3.864% | -2.224% | -0.2961% | 2.345% | 1.387% | 1.762% | 1.606% | 1.111% | 1.428% | -1.007% | -0.1012% | -1.397% | 1.206% | -0.5991% | 0.7363% | -2.655% | -1.089% | -0.1821% | -1.635% | -0.9037% | -2.745% | -1.456% | -0.2196% | 1.085% | -2.376% | 1.085% | 0.5442% | -9.344% | 1.429% | 1.585% | 1.231% | 1.085% | 0.5025% | 0.04456% | -0.4134% | -1.041% | 0.7315% | -0.4001% | -2.788% | 1.085% | 1.46% | 1.141% | 1.65% | -1.714% | 1.779% | 2.103% | -9.219% | -0.3856% | 0.9559% | 3.219% | -1.912% | 2.584% | 4.772% | 1.889% | 0.03496% | 1.476% | 0.1695% | 1.335% | 0.3048% | 0.6482% | 2.116% | 0.898% | -0.5279% | -0.7557% | 0.02143% | 0.9096% | 0.9397% | 1.304% | 1.937% | -0.3093% | 1.085% | 1.918% | 0.6378% | 2.022% | 0.565% | -0.4759% | 1.824% | 1.002% | -0.3718% | -0.3801% | -2.136% | 0.04456% | -11.11% | 1.844% | 1.45% | -100% | 1.179% | -0.2885% | -0.684% | 0.3984% | -0.9546% | -0.1428% | -1.09% | -0.913% | 0.6482% | 0.262% | -2.256% | -2.172% | 2.233% | -0.8489% | -2.079% | -2.125% | -0.8667% | 0.6378% | -0.4863% | -1.335% | -2.486% | -1.015% | -0.684% | 0.6691% | -7.574% | -7.019% | -0.4967% | -2.058% | -2.023% | -0.4967% | -1.537% | 0.8448% | -0.04333% | -8.045% | 0.6114% | 2.033% | 2.758% | 3.63% | -0.9368% | 3.513% | 3.028% | 2.588% | -8.813% | 0.8324% | -1.358% | 2.001% | 3.196% | -0.9026% | 1.101% | 0.336% | 2.554% | 0.4481% | 1.591% | 1.534% | -0.3093% | -0.6169% | -1.256% | -1.569% | -1.121% | 0.7107% | 2.782% | 1.887% | -0.9976% | 1.326% | -2.313% | -1.705% | -2.267% | 1.139% | -0.5719% | -0.7555% | -2.21% | -1.65% | -2.987% | -0.03628% | -2.037% | -1.509% | -9.738% | -0.04901% | 0.9709% | 2.634% | 1.56% | 0.2504% | 0.6341% | -1.666% | -1.172% | -1.733% | 2.066% | -0.7814% | 1.205% | -1.168% | 0.04456% | -2.694% | -9.39% | -0.4818% | 1.803% | 0.9709% | 2.266% | 0.6235% | -0.5239% | 0.4867% | -0.05018% |  |  | -100% | -0.5482% | -1.533% |  | -1.794% | 1.075% | -0.4967% | -0.174% | -10.72% | 2.126% | 0.5754% | 1.387% | -1.454% | -0.4134% | -1.298% | -1.225% | -1.699% | 5.748% | 5.909% | 4.664% | 4.685% | 2.797% | -0.8564% | -1.541% | 0.5591% | -0.3209% | -2.53% | -2.425% | 2.068% | -0.6088% | -1.172% | -0.2561% | 0.5261% | 1.476% | -1.86% | -1.378% | -1.314% |  | 5.796% | -1.171% | 0.2381% | -2.896% | -1.536% |  |  | 4.656% | 4.104% | 18.09% | -2% | 0.3533%
2025-06-29 | -0.5088% | 1.562% | 1.761% | 1.407% | 1.126% | 1.171% | 1.643% | 1.998% | 1.091% | 1.544% | 1.053% | -0.8593% | -0.9537% | 3.929% | 1.407% | 0.4865% | 0.581% | 0.4629% | 0.7989% | 1.126% | 0.2268% | 1.761% | -1.054% | 1.683% | -1.816% | 1.235% | -1.707% | 0.5285% | 1.368% | -0.9196% | -0.1011% | -3.753% | -0.7563% | 1.019% | 0.2268% | 1.025% | 1.053% | -2.134% | -0.3635% | 1.525% | -1.308% | -1.532% | -0.1274% | -3.291% | 0.699% | 1.053% | -1.816% | -0.1274% | -0.04236% | -2.4% | 0.3449% | 0.8171% | 2.103% | 0.8433% | -0.3235% | 0.1612% | 0.8643% | -0.04472% | 0.7384% | -2.053% | 1.053% | 2.501% | 2.116% | 3.815% | 0.581% | 0.1451% | 1.126% | -2.579% | -0.2454% | 0.1088% | 0.581% | -1.072% | -0.9537% | -0.009302% | 1.263% | 0.003815% | 1.473% | 0.2268% | -0.2454% | 1.344% | 0.8171% | 1.525% | -0.1274% | 0.581% | -1.072% | 0.1088% | -0.8357% | -0.4815% | -0.8593% | -1.52% | -0.3597% | -1.816% | 1.289% | -1.875% | -0.5209% | -0.3635% | -100% | -0.009302% | 0.581% | -0.9537% | -1.662% | 0.9351% | -1.308% | 0.581% | 1.263% | -0.7176% | 3.152% | 0.4551% | -0.4815% | 0.4236% | 0.363% | 0.363% | -1.958% | -2.651% | 1.525% | -1.213% | -0.3252% | -2.305% | -0.2061% | 0.699% | -1.461% | -5.663% | -7.342% | 0.8171% | -2.158% | 0.5285% | -1.745% | -0.8711% | -2.147% | 0.2871% | -1.631% | -0.1165% | 0.5374% | -1.351% | -0.9211% | -0.7778% | -1.604% | -0.4803% | -1.289% | 1.643% | 0.156% | -1.381% | -0.1274% | 2.662% | -1.886% | 0.8534% | 0.1206% | 1.482% | 0.363% | 2.891% | 1.791% | 2.116% | -0.1851% | -0.2454% | 0.6164% | -0.7412% | 1.053% | 2.848% | 1.246% | -1.142% | 0.1851% | -2.335% | -0.7701% | -2.15% | 1.034% | -0.3965% | -1.38% | -4.909% | -0.258% | -2.437% | -0.9696% | -0.7518% | -0.3456% | -6.013% | -1.333% | -0.4252% | 1.008% | -1.619% | -1.725% | 0.8882% | 0.5888% | -1.195% | -1.619% | -0.05266% | -1.615% | 1.034% | -0.1444% | -0.7748% | -0.9467% | -0.5905% | -1.977% | -0.4013% | 0.6136% | -0.3058% | -0.4252% | -1.022% | -1.285% | -1.739% |  |  | -100% | -0.4803% | -0.2912% |  | -0.1936% | 0.2268% | -0.1628% | -0.8711% | -0.7294% | -0.3989% | -1.308% | 0.1914% | -0.8711% | -0.06833% | 0.581% | -1.756% | 0.8538% | 5.041% | 6.177% | 4.314% | 3.585% | 5.528% | -2.21% | -1.418% | -1.969% | 0.5285% | -1.816% | -1.925% | 1.771% | 1.78% | 0.2137% | -1.633% | -1.913% | -1.528% | -0.9334% | -0.6757% | -0.3838% |  | 4.49% | -0.137% | 0.9897% | -1.537% | -1.668% |  |  | 3.815% | 5.108% | 15.73% | -0.9334% | -0.7222%
2025-06-30 | 2.195% | 1.227% | 1.423% | 0.8239% | 0.6741% | 0.9737% | 1.423% | 1.723% | 0.8179% | 1.249% | 3.521% | 2.771% | 2.022% | 3.616% | 0.9737% | 0.8239% | 0.3745% | -0.2248% | 0.9507% | 0.5358% | 0.9737% | 1.273% | 0.8124% | 1.606% | 1.366% | 0.3975% | 1.642% | 0.5409% | 0.9404% | 1.34% | 1.074% | 0.2746% | 2.044% | 3.303% | -0.824% | -0.435% | 0.8239% | -0.5244% | -2.322% | 0.6741% | 0.8239% | -1.723% | 2.921% | 1.273% | 2.472% | 0.8239% | -5.687% | 1.243% | -4.935% | -5.223% | -0.5244% | 1.573% | 0.008256% | 1.739% | -0.01735% | 1.606% | 1.873% | 1.873% | 0.6741% | 2.006% | 0.3745% | 2.777% | 0.8239% | 4.326% | 0.5358% | 0.1209% | 0.6741% | 1.504% | -0.824% | -0.5244% | 0.9737% | 0.5243% | 2.322% | 1.723% | 2.245% | 0.008256% | 1.473% | 0.2247% | 1.079% | 1.089% | 0.07484% | 0.8239% | -0.6742% | 0.2247% | 0.9737% | -1.873% | 2.022% | -1.873% | -1.723% | -0.2248% | -2.03% | -0.01735% | -0.07497% | -5.019% | 0.6741% | -0.824% | -92.88% | 1.273% | 2.322% | 0.6741% | -1.453% | 2.577% | -1.438% | -0.07497% | 0.5409% | -2.921% | 1.646% | -1.104% | 0.5243% | 0.6741% | 0.5358% | 2.748% | 0.6741% | 0.9404% | 0.6741% | 0.8239% | 0.6356% | -2.522% | 0.5409% | 0.8239% | -1.933% | -5.718% | -3.188% | 0.07484% | 0.2247% | 0.4078% | 0.9737% | 2.472% | -3.987% | 2.672% | 2.195% | 3.025% | 2.195% | 0.02036% | 0.979% | 0.8391% | -0.5595% | 1.958% | 1.106% | 2.172% | -0.6258% | -1.124% | 2.322% | -1.953% | 2.172% | -1.649% | -0.3596% | 1.213% | 2.195% | 1.504% | 2.181% | 1.603% | 1.367% | 1.768% | 0.1797% | 2.472% | 0.3745% | 2.622% | 0.1514% | 1.47% | -0.7408% | -1.667% | 1.549% | -2.088% | -1.549% | -1.673% | 2.121% | -5.589% | -1.364% | -0.9455% | 1.527% | -1.236% | -0.4714% | -2.836% | -0.4714% | -1.121% | -0.9092% | -0.7879% | -2.492% | -1.364% | 1.259% | -1.549% | -2.492% | -2.124% | -0.5595% | -0.8755% | 0.6545% | 0.9454% | -6.182% | -1.958% | -0.4849% | -2.273% | -0.6061% | -1.212% | -0.7576% | -0.2425% | -1.091% | -6.708e-05% |  |  | -100% | -2.58% | -3.03% |  | -0.4785% | 2.172% | -2.142% | -2.023% | 2.622% | -0.07497% | 0.07484% | -1.408% | 0.3745% | -1.648% | -0.3746% | -0.9738% | 1.074% | 3.071% | 5.15% | 2.642% | 3.239% | 3.824% | -3.03% | -0.7507% | 1.249% | 1.34% | 1.227% | -0.2939% | 2.544% | 2.195% | 1.074% | 0.5409% | -0.6994% | -2.453% | -0.07777% | -0.3368% | -1.091% |  | 5.746% | -1.219% | 0.2984% | -1.085% | -1.476% |  |  | 6.834% | 6.27% | 18.88% | -1.166% | -0.3317%
2025-07-01 | 1.834% | 3.668% | 3.908% | 3.383% | 3.357% | 3.27% | 3.795% | 4.095% | -9.824% | -2.265% | 6.139% | 5.445% | -0.9671% | 6.44% | 3.645% | 3.683% | 2.651% | 2.258% | 3.668% | 3.495% | 3.795% | 4.433% | 1.643% | 5.362% | 4.776% | 4.049% | 3.426% | 3.812% | 4.895% | 0.412% | 2.529% | 1.995% | 1.852% | 3.248% | 2.07% | -1.186% | 0.4953% | -2.298% | -0.2547% | 0.6453% | -1.38% | -0.8172% | 0.7578% | 0.7203% | 1.47% | -1.061% | -0.8316% | 1.095% | 1.065% | -1.131% | 1.695% | 2.708% | -1.171% | -0.6713% | -1.178% | -0.6713% | -9.804% | 1.058% | -2.005% | -1.671% | -1.005% | -1.186% | 0.1203% | 4.472% | 1.436% | 1.072% | 1.072% | -1.524% | -0.2172% | 0.4953% | 0.589% | -1.98% | -0.7984% | 1.489% | -0.1714% | -2.005% | -1.671% | 0.1203% | 0.1953% | -1.87% | -0.8172% | -1.717% | 1.226% | -0.1047% | -1.586% | -1.905% | -1.773% | -0.1984% | -0.4422% | -1.38% | -1.725% | -2.718% | 0.4953% | -1.942% | 0.06197% | -0.2359% | -11.88% | -2.317% | 1.058% | 1.751% | -0.2547% | 0.8703% | -0.06719% | 1.376% | 1.795% | -1.905% | 0.162% | 0.1873% | -1.755% | 0.6953% | 0.3972% | 0.6049% | -1.671% | -1.171% | -0.4422% | -1.755% | -2.526% | -2.171% | 0.4786% | -0.1422% | 0.9828% | -7.271% | -4.254% | 0.06405% | 0.3828% | -1.838% | -1.755% | 0.4203% | -2.088% | 0.3286% | -1.005% | 1.643% | -1.87% | -1.823% | 0.1203% | -1.63% | -1.455% | -0.5798% | 0.7593% | 1.058% | 2.336% | 1.886% | -0.3484% | -0.5201% | -1.942% | 0.726% | 2.258% | -11.85% | 2.284% | 2.111% | 0.03376% | -0.8172% | 2.429% | -0.8172% | 0.3078% | 1.376% | -1.755% | 1.002% | 0.3099% | 1.258% | -0.5539% | -1.473% | 1.789% | -10.5% | -2.071% | 0.6482% | 1.524% | -10.84% | 1.03% | -0.7353% | -0.3712% | 0.1021% | -0.3516% | -0.6078% | -1.734% | -6.668% | -0.6382% | -0.733% | -0.1157% | -1.586% | -0.2998% | -2.577% | -0.5539% | -0.06174% | 1.381% | -1.734% | -0.7899% | -2.064% | 0.3023% | -13.36% | 0.3099% | 1.827% | -0.06932% | -0.4486% | -2.572% | -0.2589% | -0.9037% | -1.321% |  |  | -100% | 0.2518% | -1.767% |  | -2.309% | 0.1203% | -1.192% | 0.4953% | 0.4953% | -1.155% | -9.067% | 1.133% | -1.98% | 0.0828% | -1.136% | 1.339% | -1.671% | 2.912% | 5.815% | 1.107% | 2.003% | 4.64% | -0.5539% | -1.111% | 0.5073% | -0.4213% | -1.628% | -0.8316% | 1.605% | -0.572% | -0.4047% | -2.355% | -0.2298% | -0.4576% | 2.687% | 0.7571% | 0.5248% |  | 4.003% | -2.007% | -1.374% | -1.678% | -1.008% |  |  | 7.13% | 5.534% | 18.11% | -0.4826% | 1.075%
2025-07-02 | 0.7339% | 2.675% | 2.469% | 2.585% | 1.381% | 1.534% | 2.352% | 2.235% | -2.976% | 1.51% | 4.688% | 3.754% | -2.205% | 4.773% | 3.053% | 2.702% | 2.936% | 2.936% | 3.754% | 3.754% | 4.221% | 3.871% | 1.057% | 4.585% | 3.969% | 3.322% | 2.46% | 2.715% | 2.923% | -1.647% | -0.5044% | 3.442% | -0.3045% | 2.666% | 2.469% | 2.805% | 3.52% | 1.651% | -1.154% | 1.767% | -1.154% | -1.971% | -0.2188% | -0.1019% | 0.4823% | 0.9496% | 0.5182% | 0.2486% | 0.1645% | -1.63% | -0.5693% | 1.066% | 2.611% | 0.5342% | -1.423% | 2.196% | -0.7121% | -7.697% | -0.7121% | 0.1188% | 0.3654% | 0.6128% | -6.411% | 4.053% | 0.6261% | 1.381% | 1.597% | -2.286% | 1.066% | 1.534% | 1.417% | -0.803% | -1.971% | -0.9198% | -0.4005% | -1.647% | -2.997% | -0.4525% | 1.066% | -1.962% | -2.322% | 0.8328% | 1.066% | 0.8328% | -1.738% | -0.6861% | -1.738% | -0.1019% | -1.971% | -1.329% | -1.182% | -2.825% | -5.126% | -0.4525% | -0.5044% | 1.066% | -7.93% | -0.3356% | -1.154% | -0.3356% | -0.4525% | 0.7159% | -1.621% | -0.2188% | 0.0149% | -9.099% | 0.4303% | -0.9527% | 2.235% | 1.573% | 1.92% | 0.8418% | 1.573% | 1.677% | 2.702% | -1.504% | -1.161% | -2.166% | 0.4303% | 1.183% | 2.585% | -6.009% | -3.516% | 1.3% | 1.884% | -1.439% | -0.803% | -1.504% | 0.1188% | -2.478% | -2.61% | 2.136% | -0.3446% | 1.714% | -1.612% | -2.157% | -1.503% | 0.1334% | 1.398% | 0.1317% | 2.999% | 1.165% | -0.803% | -0.4525% | -1.27% | 2.244% | -0.5693% | 1.077% | 1.812% | 2.783% | 1.92% | 0.5991% | 0.8458% | -0.2188% | -1.037% | -1.621% | -1.27% | 2.001% | 0.5606% | 0.5606% | 0.7313% | -0.7393% | -0.2141% | -1.895% | -0.2141% | -1.193% | -0.03025% | 1.992% | -1.803% | 0.5086% | 1.756% | 0.05483% | 1.362% | 0.622% | -5.361% | -1.448% | 1.27% | -1.803% | -0.9493% | 0.5606% | -1.066% | -0.7393% | -0.003986% | -0.3989% | 2.315% | 2.097% | -1.08% | 0.622% | -1.647% | -0.6302% | -0.8574% | -1.945% | -10.55% | -1.803% | -1.803% | -4.639% | -0.4556% | -1.566% |  |  | -44.17% | -0.1917% | 0.183% |  | -0.09955% | -1.154% | -0.5693% | -1.738% | -0.2188% | -1.621% | -0.803% | 1.534% | -0.9198% | -0.2188% | -0.5693% | 1.183% | 0.5342% | 0.1188% | 4.36% | 6.316% | 3.01% | 3.857% | -0.06401% | -1.78% | -0.9572% | -0.1928% | -1.855% | -1.1% | 1.174% | -1.962% | -0.08896% | -1.958% | -0.7393% | -1.527% | -1.951% | 0.01936% | -0.2981% |  | 6.048% | 0.0757% | -0.3583% | 0.01936% | -1.103% |  |  | 4.444% | 5.251% | 16.98% | -1.951% | -0.2807%
2025-07-03 | 0.6791% | 2.914% | 2.963% | 2.647% | 2.428% | 2.436% | 0.6467% | 0.1203% | -2.571% | 2.786% | 1.278% | 0.5414% | -1.564% | 2.216% | 2.752% | 2.436% | 1.91% | 1.805% | 2.331% | 2.331% | 2.963% | 2.963% | 0.2904% | 3.501% | 3.206% | 2.234% | 1.554% | 1.816% | 2.097% | -2.675% | -2.114% | -1.646% | -0.3351% | 2.759% | 0.752% | 0.06189% | -2.196% | -2.301% | -1.775% | 1.489% | -1.459% | -1.722% | -1.038% | -0.5113% | 0.1203% | 0.752% | 0.9707% | 0.4362% | -0.145% | -1.863% | 0.1203% | 1.384% | 3.501% | 1.442% | -2.431% | 1.161% | -0.523% | -0.09023% | 2.191% | 3.501% | 1.805% | -0.1262% | 0.4362% | 5.859% | 0.2904% | 1.457% | 1.748% | -2.042% | 0.4362% | 1.384% | 1.068% | -1.459% | 2.121% | 0.1203% | -0.4295% | 0.5999% | 1.161% | -0.09023% | 0.4362% | 1.554% | 2.226% | -0.7219% | 1.278% | 0.01505% | -2.091% | -0.8272% | -2.406% | -0.5113% | -1.775% | -2.196% | -1.863% | -1.848% | 1.489% | -1.564% | 1.723% | 1.173% | -1.775% | 0.3309% | 0.752% | -0.09023% | 1.173% | 0.752% | -0.3008% | -0.4061% | -0.1487% | 0.1203% | 1.442% | -2.684% | 1.91% | 2.191% | 1.845% | -0.4871% | -2.301% | -1.272% | -0.5113% | -2.196% | -2.007% | -2.301% | 2.284% | 1.91% | 2.858% | -5.015% | -2.956% | 0.752% | 1.489% | -1.365% | -1.775% | -0.7219% | -0.7851% | 0.1975% | -0.5842% | 0.3098% | 1.087% | -1.574% | -1.617% | -0.4668% | -2.305% | 1.037% | -0.3471% | 0.2256% | -1.945% | -0.5259% | 0.9204% | 0.2904% | -2.554% | 0.9318% | 1.194% | -5.708% | -0.662% | 0.4848% | 0.1932% | 0.3309% | 0.3192% | 0.752% | 0.1203% | -0.7219% | -0.4061% | -1.143% | 0.4063% | -1.191% | -1.096% | -0.552% | -0.05514% | -11.13% | 0.4181% | -1.361% | -15.03% | -15.01% | -1.723% | -0.9524% | 0.9897% | -1.157% | -1.096% | -1.975% | -2.232% | -1.723% | -2.149% | -2.149% | -2.137% | -1.617% | -0.7322% | -2.137% | -2.421% | 1.092% | -1.912% | -2.232% | -0.4413% | -1.361% | 1.194% | -2.108% | -0.765% | -0.552% | -0.552% | -1.297% | -0.4455% | 0.6192% | 1.322% | 0.7257% |  |  | 7.172% | 1.451% | 0.2426% |  | -0.5696% | -1.669% | -1.985% | -1.985% | -0.4061% | 1.173% | 0.6467% | 0.3309% | 1.489% | -1.564% | 1.489% | 0.2256% | -1.833% | 1.723% | 4.608% | 3.853% | 2.951% | 3.979% | -1.569% | 0.2236% | 3.089% | -0.2423% | 0.2904% | 0.7763% | 1.27% | -0.3899% | -0.3359% | 1.536% | -1.606% | -0.623% | -1.606% | -1.675% | -1.872% |  | 3.591% | -1.7% | -0.4281% | -1.78% | -1.606% |  |  | 2.804% | 5.3% | 15.3% | -2.043% | -1.873%
2025-07-04 | 1.755% | 2.502% | 1.222% | 2.609% | 1.755% | 1.8% | 2.262% | 2.031% | -1.163% | -0.05358% | 0.7599% | 1.107% | 1.141% | 0.97% | -0.6267% | 0.06659% | 1.569% | 2.84% | 1.542% | 1.222% | 1.915% | 0.991% | 2.929% | 3.944% | 3.035% | 4.315% | 3.569% | 1.684% | 3.903% | -0.5445% | 1.89% | 2.301% | 0.5962% | 1.533% | -0.7538% | -1.499% | -7.444% | 0.6443% | -1.655% | 2.17% | 0.1821% | 1.222% | -1.505% | -1.1% | 0.0897% | 1.28% | 1.83% | 0.8523% | 0.9559% | -0.4973% | 2.297% | 2.736% | 1.992% | 2.64% | -0.4205% | 1.684% | -1.808% | -0.7423% | 3.461% | 2.198% | 1.8% | -0.3944% | -1.089% | 5.483% | 1.446% | 0.9234% | 1.969% | -1.434% | -0.7076% | 0.2284% | 0.783% | -1.216% | 1.291% | 0.2399% | -0.5137% | -2.527% | -0.0001718% | -0.2801% | -1.147% | -0.004517% | 1.164% | -0.5112% | 0.3555% | -1.124% | -2.649% | -1.1% | -2.418% | 0.2399% | -1.089% | -1.32% | 0.8338% | -2.724% | 1.095% | -1.32% | -0.8835% | -0.7654% | -2.013% | 1.892% | 0.3324% | 0.6443% | 1.973% | 0.05504% | 0.9563% | -0.7885% | -1.613% | -1.667% | 0.3901% | -2.149% | -0.4534% | -1.602% | -2.383% | 0.9128% | 0.8626% | 1.15% | 1.28% | -2.36% | -2.665% | -2.116% | -0.2672% | -1.632% | -0.4187% | -9.254% | -5.66% | -2.764% | -2.21% | -0.8013% | -6.52% | -1.667% | -2.917% | -3.503% | -5.754% | -1.562% | -0.4098% | 0.5918% | -0.3245% | -0.605% | -2.806% | 0.7542% | -0.05358% | 1.187% | -0.8471% | -1.946% | 1.419% | 0.5821% | -2.187% | -0.4205% | -1.436% | 0.1506% | -1.903% | -0.1538% | 0.6888% | -0.1414% | -1.171% | 0.2399% | -1.228% | -2.187% | -1.147% | -2.129% | -0.5492% | -0.783% | -0.1727% | -0.2688% | 0.4818% | -1.887% | 4.741% | -0.7577% | -1.25% | 0.05585% | 0.6311% | 0.1959% | 0.4651% | -0.2978% | -0.3804% | 3.113% | -2.874% | -1.367% | -1.624% | -0.5492% | -2.936% | -2.01% | 0.5385% | -0.8998% | -0.4739% | -2.732% | 0.765% | 0.4402% | 0.6559% | -0.3987% | -0.1519% | -1.619% | -1.601% | -1.718% | -2.068% | -1.25% | -2.267% | -1.601% | 0.7596% | -1.648% |  |  | 3.708% | -1.293% | -1.607% |  | -1.518% | -2.36% | -1.898% | -1.204% | -1.089% | -1.667% | -2.129% | 0.159% | -0.8809% | -0.5112% | -0.1876% | 2.216% | -1.192% | -1.808% | 5.143% | 3.761% | 5.419% | 7.16% | -0.425% | -1.693% | 1.2% | 0.2669% | -1.764% | -0.2712% | 2.298% | -1.284% | -0.1029% | -0.8835% | -1.355% | -0.8331% | 1.162% | 0.3005% | 0.97% |  | 3.131% | 1.12% | -1.458% | -1.431% | -0.03684% |  |  | 3.291% | 6.144% | 19.04% | -1.355% | 1.049%
2025-07-05 | -0.9209% | 0.8538% | 0.5415% | 0.1309% | 0.04399% | -0.1491% | 0.1402% | 0.5602% | -7.154% | 0.3366% | 1.531% | 1.279% | -2.1% | 3.156% | 0.2429% | 0.2149% | -2.286% | -2.277% | -2.006% | -1.782% | -0.09313% | 0.8215% | -1.429% | 1.167% | -0.628% | -0.8519% | -0.9467% | -0.2601% | -0.1854% | -3.562% | -0.8242% | -0.1356% | -2.56% | 0.8504% | -3.621% | -4.361% | -4.806% | -4.526% | -5.254% | -5.553% | -4.246% | -5.553% | -4.638% | -3.425% | -2.818% | -1.484% | -1.541% | -2.893% | -1.016% | -2.324% | -0.8677% | -0.2051% | 1.756% | -1.073% | -2.394% | 1.864% | -7.751% | 0.5508% | -0.9237% | 0.2708% | -1.465% | 0.6156% | -0.5691% | 3.111% | 0.8796% | 1.31% | 1.224% | 0.7073% | -2.38% | -1.633% | -2.1% | -2.66% | -2.1% | 1.727% | -0.6998% | -1.032% | 1.374% | 1.727% | 1.82% | 2% | 0.6068% | 2.753% | 1.073% | 1.073% | -0.0558% | 1.521% | 0.2242% | 0.3268% | -2.286% | -2.66% | 2.164% | -3.428% | 4.013% | 2.744% | 2.121% | 3.808% | -0.8864% | 5.357% | 3.575% | 4.088% | 5.73% | 3.985% | 5.404% | 4.013% | 2.66% | 2.66% | 5.605% | 4.667% | 2.837% | 3.871% | 3.369% | 2.835% | 3.448% | 3.365% | 4.508% | -0.7931% | -0.4598% | -0.1108% | 4.095% | 4.452% | 3.929% | -3.014% | 0.6525% | 1.801% | 2.613% | 5.107% | -4.713% | -5.833% | -5.777% | -5.843% | -5.409% | -5.332% | -4.117% | -4.908% | -4.596% | -3.115% | -4.421% | -2.008% | -4.045% | -4.526% | -4.858% | -3.6% | -3.462% | -5.151% | -5.646% | -4.031% | -4.088% | -5.213% | -4.72% | -4.375% | -5.151% | -3.593% | -3.553% | -3.686% | -4.526% | -3.444% | -4.899% | -4.19% | 0.1266% | -1.884% | -1.635% | -2.403% | -2.256% | -1.753% | -0.08313% | -2.682% | -0.3264% | -0.9137% | -0.2321% | -2.601% | -2.682% | -1.957% | -1.333% | -0.3536% | -4.102% | -4.102% | -2.309% | -2.497% | -2.256% | 0.7118% | -1.372% | -1.669% | -1.501% | 2.927% | -2.365% | -2.004% | -1.097% | -2.501% | -7.304% | -8.952% | 0.3626% | 3.072% | 0.523% | -1.365% | 2.968% | -1.365% | 3.796% | 2.939% |  |  | 5.503% | 0.01392% | -1.745% |  | -1.297% | -1.726% | -1.353% | 0.8028% | 1.904% | 2.893% | 2.501% | 6.085% | 4.032% | 0.2895% | 3.565% | 4.909% | -1.695% | 5.788% | 6.682% | 7.016% | 6.886% | 6.548% | 2.502% | 4.984% | 6.608% | 7.779% | 7.28% | 5.497% | 7.603% | 7.815% | 6.907% | 7.248% | 2.471% | 4.006% | 1.097% | 2.713% | 2.714% |  | 5.831% | 1.34% | 1.409% | 2.619% | 3.275% |  |  | 4.569% | 3.892% | 19.42% | -2.03% | -2.32%
2025-07-06 | -2.273% | -0.1834% | 0.01786% | -0.06758% | -1.061% | -1.21% | -0.3987% | -0.121% | -1.348% | -0.7635% | 0.2849% | 1.064% | 0.07126% | 1.794% | -0.8472% | -1.392% | -1.146% | -1.403% | -1.14% | -1.13% | -0.6229% | -0.7297% | -2.303% | -0.2254% | -0.1538% | -1.031% | -1.731% | -1.32% | -0.6526% | -1.63% | -1.697% | -0.776% | -1.137% | -0.1041% | -2.054% | -2.805% | -1.125% | -2.599% | -2.919% | -2.439% | -2.278% | -1.638% | -1.851% | -0.7831% | -1.317% | -2.866% | -2.303% | -1.21% | -1.984% | -1.881% | -1.21% | -2.033% | 0.4676% | -2.523% | -2.303% | -0.2919% | 0.4771% | 0.6053% | -0.7191% | 0.4676% | -2.033% | 0.6867% | -1.531% | -0.9556% | 1.759% | 1.493% | 2.291% | 0.003894% | -1.499% | 0.6373% | 1.438% | 0.146% | 1.246% | 1.556% | 2.604% | 0.6954% | 3.154% | 1.364% | -0.8793% | 0.487% | -1.638% | 2.207% | -0.655% | -2.289% | -1.104% | -0.4627% | 0.3703% | -0.42% | 0.3917% | -0.687% | 0.2925% | 0.9109% | 2.848% | 0.7121% | 0.5056% | 0.7548% | -2.876% | 3.019% | 2.271% | 0.2849% | -0.5695% | -0.4627% | 0.9257% | 2.293% | 2.081% | -2.706% | 1.863% | 2.604% | 1.46% | 2.015% | 1.305% | 1.897% | 2.49% | 2.214% | 2.026% | -1.424% | -2.213% | -2.124% | 2.186% | 1.353% | 1.524% | -3.577% | -1.583% | -1.082% | 0.2421% | 0.7239% | -1.851% | -1.21% | -1.479% | -0.9754% | -2.303% | 0.7531% | -0.03554% | 2.283% | 1.3% | -1.622% | -2.19% | 2.097% | 1.502% | 1.566% | 0.2504% | -0.5482% | 2.528% | 1.739% | 0.1994% | 0.556% | -0.2491% | 1.479% | -2.5% | 0.4574% | 1.739% | 1.887% | 2.566% | 2.421% | 2.122% | 1.716% | 2.239% | 0.1247% | -0.1309% | -2.075% | -1.866% | -0.08773% | -1.972% | -1.012% | 0.4475% | -2.218% | 2.073% | -1.204% | -2.82% | -2.01% | -2.633% | -1.388% | -1.002% | -1.129% | -1.204% | 1.424% | -0.4118% | -1.168% | -1.972% | 0.02029% | 0.6019% | -2.836% | -1.204% | 1.411% | 0.2031% | -1.204% | -1.098% | -0.5379% | -0.7453% | 0.901% | 0.5604% | 1.208% | -8.081% | -0.08773% | 1.748% | 0.1283% | -0.5068% | -0.725% |  |  | 5.084% | -2.626% | -1.049% |  | 0.7691% | -1.477% | -1.317% | -2.075% | -1.52% | 0.7868% | -0.8579% | 0.2849% | 0.8189% | -1.424% | 0.1567% | 0.4985% | -1.365% | 4.331% | 7.141% | 7.524% | 6.821% | 6.553% | -1.931% | -0.2552% | 3.122% | -0.2254% | 1.611% | 0.1123% | 1.502% | 0.6546% | 2.262% | 0.9138% | -0.1847% | -1.903% | 0.9232% | -1.535% | -2.414% |  | 0.9302% | 0.2164% | -0.4085% | -1.535% | -2.744% |  |  | 2.858% | 4.028% | 17.09% | -0.1847% | -1.756%
2025-07-07 | -0.1406% | -1.012% | -0.003432% | -0.4231% | 0.1499% | -1.472% | -0.9478% | -0.633% | -0.2762% | -0.2762% | 0.4163% | 0.836% | -1.577% | 1.532% | -1.577% | -1.263% | -1.577% | -1.682% | -0.9155% | -1.109% | -1.263% | -0.9478% | -2.562% | -0.7612% | -0.8186% | -0.9155% | -2.078% | -1.694% | -1.507% | -1.88% | -2.254% | -1.228% | -1.724% | 0.5739% | -2.553% | -2.427% | -0.2553% | -1.263% | 0.2064% | -1.493% | -1.263% | 0.1015% | -0.2133% | -1.472% | -0.7379% | -0.4231% | -2.165% | -2.081% | -1.586% | -2.19% | -0.5281% | -1.294% | 0.8243% | -1.797% | -1.109% | 0.8243% | -0.2016% | -0.2133% | -1.601% | -0.668% | -1.105% | -0.5527% | -1.892% | 1.524% | 1.661% | 1.07% | 2.349% | 0.208% | 0.5842% | 0.3953% | 1.35% | 0.8885% | 2.085% | 0.9829% | 0.2367% | -1.703% | 1.16% | -0.3812% | -2.123% | 1.361% | -1.787% | 1.56% | -1.745% | -0.9478% | -0.4231% | 0.3114% | -0.2972% | 0.1645% | 0.2799% | -0.1189% | 0.4188% | 1.254% | -0.2133% | 0.1015% | 0.7497% | -0.2028% | -0.2972% | 2.032% | 0.6786% | 1.067% | -0.003432% | 0.8045% | -0.2133% | 0.5422% | -0.3788% | 0.3114% | 1.664% | -2.146% | -0.7904% | 0.2088% | -0.8283% | 0.9635% | 2.214% | 1.3% | 0.8465% | 0.4583% | -1.865% | -1.041% | 0.5725% | -0.6225% | -0.9163% | -1.787% | 0.2461% | 1.938% | -2.406% | 2.307% | 0.2064% | -1.472% | -1.601% | -1.974% | -1.981% | -0.683% | -0.9252% | 1.372% | -0.08341% | -1.063% | -1.151% | 2.121% | 1.738% | 2.315% | -0.8186% | -2.078% | 0.2169% | 2.01% | -1.997% | 0.2662% | 0.1435% | 1.647% | -0.04379% | 1.709% | 2.581% | 2.011% | -1.218% | 2.085% | 0.3848% | -0.6015% | -1.263% | -2.28% | 0.719% | -0.9258% | -1.68% | -0.3528% | -1.426% | -0.7655% | 0.7249% | 2.079% | 0.07169% | -1.897% | -1.647% | -1.476% | -0.8749% | -2.342% | 1.734% | 0.9385% | -1.426% | -0.8834% | -0.1406% | 1.451% | -0.8598% | 1.027% | 2.268% | -1.048% | -2.275% | 1.855% | 0.2105% | -1.52% | -1.853% | 0.2661% | 0.5819% | -0.4752% | -0.03443% | -1.096% | -0.3528% | 1.239% | -1.096% | -0.6712% | -0.5438% | -0.8834% |  |  | 1.025% | 0.08281% | -1.23% |  | -1.763% | 0.3114% | -1.997% | -0.4231% | -1.892% | -1.609% | -2.102% | 1.224% | -1.787% | -1.892% | 2.462% | 1.403% | 2.69% | 3.632% | 7.145% | 7.233% | 7.687% | 5.564% | -1.089% | -0.6244% | 1.738% | 1.748% | 1.564% | -0.7993% | 6.382% | -1.109% | 1.459% | 0.5725% | -0.7365% | 0.02621% | 0.4608% | -1.688% | 1.989% |  | 3.166% | -0.3687% | 1.191% | -1.897% | -1.781% |  |  | 3.866% | 3.193% | 16.37% | -1.063% | -1.887%
2025-07-08 | 0.906% | 2.324% | 1.633% | 2.862% | 1.615% | 0.5573% | 0.7801% | -0.9022% | 2.509% | 2.582% | 2.478% | 1.786% | 2.247% | 0.1453% | 1.94% | 1.495% | 1.326% | 1.633% | 0.8351% | 1.19% | 0.6342% | -0.9022% | 0.7642% | 1.744% | -1.434% | -1.576% | -1.434% | -1.056% | -0.9193% | -1.397% | -1.739% | -2.012% | 0.2972% | -0.4955% | -0.4413% | -2.235% | 1.687% | 1.479% | 0.711% | -0.3261% | -1.286% | -0.4413% | -1.286% | -0.8946% | -1.594% | -1.248% | -1.356% | -0.9022% | -1.179% | -2.432% | -1.594% | -1.186% | -0.7145% | -1.486% | -2.278% | -1.602% | -1.739% | 0.711% | -0.5096% | -1.602% | 0.5957% | 3.316% | -2.055% | 2.962% | -1.434% | -1.86% | -0.6541% | -0.2286% | -0.9022% | -0.5181% | -0.8254% | -0.595% | 1.479% | -0.9022% | -0.9193% | -0.5028% | -1.807% | -1.133% | 0.2347% | -0.725% | -2.4% | 0.711% | -0.6257% | -0.8254% | -2.669% | -0.4413% | 0.4652% | -1.594% | 0.7571% | 0.8493% | 0.333% | -0.6541% | 1.326% | -0.9791% | 0.5351% | -1.594% | -0.5181% | -0.9022% | -0.3645% | -1.363% | -0.6718% | -0.2109% | -1.824% | -0.6718% | -0.3867% | -0.9022% | 1.129% | -0.3618% | -0.1648% | 0.6581% | -0.6257% | 0.9982% | 0.46% | 0.9995% | 1.518% | 1.049% | -1.734% | -2.831% | 0.262% | -0.111% | -0.8331% | -2.9% | -0.7349% | -0.3645% | -2.331% | -2.831% | -1.286% | -2.631% | -1.739% | -1.807% | -2.271% | 0.9202% | 0.9273% | 3.33% | 1.909% | -0.3857% | -1.677% | 1.049% | 2.361% | 2.37% | 1.012% | -2.625% | 2.286% | 1.544% | -0.4183% | 0.7712% | 0.4421% | 0.6481% | -2.285% | 1.693% | 2.657% | 1.986% | -1.015% | 2.002% | 0.5189% | -0.1725% | -0.9022% | 1.049% | 1.078% | 2.189% | 0.8972% | -1.299% | -1.9% | 0.1928% | 3.667% | -1.204% | -1.252% | -0.6705% | 1.249% | 0.8019% | -0.466% | -0.123% | 2.209% | 2.077% | 2.057% | -1.19% | -2.674% | -1.641% | -1.865% | -0.8638% | -1.963% | -2.349% | -2.017% | 6.731% | -1.146% | -2.086% | 0.8094% | 0.7646% | -1.473% | -0.314% | -2.418% | -1.718% | -2.029% | -1.641% | -1.959% | -2.185% | -0.8017% | -1.641% |  |  | 4.539% | -0.7588% | -2.296% |  | -1.791% | -2.362% | -1.978% | -1.824% | -1.594% | -1.824% | -2.208% | 1.902% | -1.724% | -1.594% | -1.647% | -0.8254% | -2.285% | 2.618% | 5.724% | 6.458% | 6.97% | 5.577% | -1.244% | -1.098% | 2% | 1.3% | 0.4734% | -0.959% | 2.509% | 1.544% | -1.739% | -2.217% | 0.004733% | -2.033% | 1.598% | 1.526% | -1.382% |  | 3.338% | 1.376% | 0.003544% | 1.365% | 0.08442% |  |  | 2.962% | 2.153% | 16.84% | 1.598% | 0.5138%
2025-07-09 | -1.095% | 0.7259% | 1.277% | -1.748% | 0.6376% | 0.2367% | -0.6481% | -0.8872% | 0.7149% | 1.369% | 0.06928% | -1.246% | 1.169% | 1.863% | 1.564% | -0.05028% | 0.6432% | 1.038% | 1.388% | 1.543% | -0.409% | -0.05028% | 1.311% | -0.7411% | 1.311% | 1.918% | 1.366% | 1.501% | 1.565% | 1.161% | 1.363% | 1.544% | -2.503% | 0.2832% | -2.848% | -0.5716% | -0.2894% | -1.007% | -0.8872% | -1.844% | -0.409% | -0.8872% | 0.5475% | -2.908% | 0.06928% | -1.007% | -1.117% | -0.8872% | -2.327% | -1.408% | 0.06928% | -0.8872% | 1.278% | -2.335% | -1.669% | 1.788% | -0.8473% | 0.5475% | 0.4279% | 0.002856% | -1.82% | 2.771% | -0.1698% | 2.87% | 1.156% | 0.8804% | 1.973% | -0.2453% | 0.8703% | 0.4997% | 1.133% | 0.7268% | -1.126% | 1.289% | -1.06% | -1.272% | -0.4222% | -0.2894% | 0.4399% | -0.5653% | -0.5285% | -0.6481% | 0.8584% | -0.409% | 0.5475% | 0.3084% | -1.067% | -0.5046% | 0.2845% | -0.3731% | -0.04263% | 0.6487% | 0.1888% | 0.1888% | 0.1091% | 0.3323% | 0.4279% | -0.8872% | 1.026% | 1.086% | 0.3084% | 1.145% | 0.7866% | 1.002% | -1.145% | -0.8274% | 1.246% | -2.601% | -1.234% | -0.7623% | -1.845% | 0.5052% | 1.576% | 0.7361% | 0.4877% | -0.5285% | -2.601% | -2.123% | -0.2735% | -1.676% | -2.095% | -2.335% | -0.7304% | 0.3084% | -1.485% | 0.7255% | -0.8872% | -0.409% | -2.707% | -2.781% | -1.559% | -0.07971% | 0.04169% | 2.371% | 1.458% | -1.489% | -0.5515% | 0.5646% | 2.15% | 2.257% | -0.01349% | -1.404% | 0.5475% | 2.834% | -1.664% | 0.8804% | 0.7268% | 1.824% | -2.232% | 1.708% | 1.642% | 1.875% | -1.846% | 2.162% | 0.4279% | -0.2296% | 0.8464% | 0.6192% | 2.029% | 0.3963% | -1.236% | -0.4864% | -2.085% | -2.3% | 1.967% | -2.366% | -0.002729% | -1.075% | -0.8612% | -0.6479% | -2.087% | -1.716% | 1.064% | -1.437% | 0.1397% | 0.2391% | -2.179% | 0.9646% | -2.515% | 1.206% | 0.2298% | -2.085% | -2.3% | 2.266% | -0.5515% | -1.978% | -1.82% | -2.029% | -0.764% | -2.002% | 0.2391% | -0.7282% | 1.086% | 0.4809% | 0.2391% | 1.448% | -1.188% | -2.179% |  |  | 4.862% | -1.56% | -2.206% |  | -1.704% | -2.083% | -1.485% | -0.409% | -0.1698% | -1.365% | -1.844% | 0.3801% | -1.844% | -0.6481% | -0.2894% | 1.97% | -2.335% | 2.649% | 3.499% | 6.344% | 6.422% | 4.871% | -1.271% | -1.652% | 0.933% | 0.2579% | -0.06867% | -2.53% | 1.668% | 1.697% | 0.01348% | -1.581% | -1.035% | -1.655% | -1.903% | -2.193% | -1.333% |  | 4.448% | -0.9325% | 1.959% | -2.551% | -1.903% |  |  | 2.336% | 1.819% | 17.34% | -1.903% | -2.051%
2025-07-10 | -1.896% | -1.052% | 0.1112% | 0.5791% | -1.818% | -0.463% | -0.01639% | 0.2388% | -0.606% | 0.66% | 1.175% | 0.962% | 1.472% | 2.414% | 1.43% | 2.302% | 1.6% | 1.983% | 1.343% | 2.286% | -0.3567% | -0.6544% | 2.128% | -2.467% | -0.4041% | 0.6757% | 2.403% | -2.089% | -0.4252% | -1.352% | -0.3307% | 0.009608% | -0.2431% | 0.3004% | -0.6544% | -2.157% | -1.399% | -0.5268% | -0.4205% | -1.101% | 0.728% | 1.451% | 0.6004% | 1.175% | -1.59% | 0.4728% | -2.191% | -1.186% | -1.341% | -1.831% | -1.229% | -0.5906% | -1.578% | -1.2% | -1.798% | -0.7088% | -1.446% | 0.004881% | -1.446% | -1.37% | -1.037% | 1.7% | 0.3026% | 0.02128% | 0.08668% | 1.088% | 0.9505% | 1.186% | 0.4941% | 0.08996% | -0.01639% | 0.1325% | 0.7067% | 0.4303% | -1.2% | -0.7466% | -0.4063% | -0.6119% | -1.42% | 1.814% | -0.01639% | 1.472% | 0.6642% | 0.7067% | -0.3567% | 0.004881% | 0.7918% | 1.281% | 0.175% | -0.1227% | 1.477% | 1.795% | -0.5268% | 2.132% | 2.222% | -1.633% | -1.59% | -0.1227% | -0.3354% | -1.42% | -0.01639% | 1.898% | -2.037% | 0.3026% | 0.3688% | -1.803% | -0.7466% | 1.643% | -0.6119% | -0.3874% | 0.4204% | 0.1652% | 1.598% | 0.123% | -0.8671% | -1.909% | -0.9788% | -0.463% | -0.9357% | 1.834% | -0.1653% | -1.03% | -0.1227% | -0.3354% | -1.782% | -1.446% | -1.909% | 1.409% | -1.427% | -1.9% | -0.5612% | 0.06705% | -0.4434% | -2.25% | -2.092% | -2.012% | 0.6085% | -2.31% | 0.3945% | 0.8131% | -1.327% | 0.3223% | -0.6332% | 2.168% | -0.6544% | 3.149% | -1.909% | -0.8575% | -0.1293% | 0.06705% | 0.5579% | 0.175% | -1.503% | 1.111% | 0.6642% | 1.068% | -0.4418% | -1.782% | -0.3644% | -1.741% | -0.8042% | -0.8376% | -0.001134% | -1.148% | 0.974% | 0.317% | -0.601% | -2.238% | -0.515% | -0.8187% | 2.031% | -1.211% | -1.531% | -0.7568% | 1.223% | -1.375% | -1.698% | -1.397% | -1.187% | -2.128% | 1.859% | -1.034% | -2.276% | 0.8539% | 2.078% | -1.722% | -1.707% | -8.108% | 0.1518% | 1.065% | 0.453% | -0.8376% | 1.313% | -1.483% | -0.4074% | 0.02277% | 1.442% | -1.375% |  |  | 5.608% | -0.4174% | -0.5701% |  | -0.6322% | -0.6757% | -1.314% | -0.8884% | -0.463% | -1.526% | -1.101% | -0.2503% | -0.463% | 0.175% | -1.526% | 1.345% | -0.7466% | 4.301% | 2.156% | 6.479% | 8.174% | 5.279% | -0.6567% | 0.5023% | 1.865% | 1.144% | -1.602% | -1.504% | 8.194% | -0.3845% | -0.9924% | -0.1794% | -2.046% | 0.5861% | 0.8225% | -1.127% | -1.798% |  | 2.034% | 2.102% | -2.304% | 1.189% | -0.9424% |  |  | 2.063% | 1.469% | 16.31% | -2.046% | -0.4106%
2025-07-11 | -0.9422% | 0.9101% | 0.7393% | 0.8301% | 0.3156% | 0.1034% | 0.1447% | 0.6649% | 0.2296% | -0.7931% | 0.1447% | 0.3346% | 0.6649% | 1.168% | 0.01255% | -6.602% | 0.3346% | 0.9952% | -0.06559% | 0.1631% | 0.4998% | 0.08687% | 0.5442% | -1.543% | 0.7729% | 0.3918% | 0.7729% | -1.858% | -2.005% | -1.712% | -1.345% | -1.785% | -0.9362% | -5.781% | -1.292% | -1.826% | 0.8301% | -0.1609% | 0.00429% | -1.243% | -1.185% | -0.6316% | -0.1031% | -0.9867% | 0.5823% | 0.8301% | -1.59% | 0.00429% | -1.459% | -1.38% | -1.812% | -1.317% | 0.5713% | -2.005% | -1.743% | -0.02324% | 0.6374% | 1.144% | 0.6374% | 0.6374% | -0.805% | 0.2488% | -1.325% | 1.402% | 2.984% | 3.212% | 3.746% | 1.81% | 5.967% | 6.256% | 5.76% | 4.67% | 0.08687% | 5.752% | 5.504% | 4.601% | 6.356% | 6.256% | 6.272% | 6.665% | 4.554% | 5.744% | 4.687% | 2.151% | 4.34% | 5.306% | 2.721% | 2.061% | 3.142% | 2.358% | 1.133% | 2.412% | 1.656% | 1.326% | 2.201% | 1.491% | 1.986% | 1.16% | 2.399% | 1.573% | 1.408% | 0.6649% | 0.3346% | 0.00429% | 1.709% | 1.573% | 1.371% | 1.835% | 3.704% | 3.83% | 2.221% | 4.371% | 3.229% | 4.476% | 0.08687% | 3.712% | -1.765% | -1.418% | 2.12% | 2.506% | 1.474% | -1.491% | 0.7108% | -0.9206% | 1.309% | 3.045% | -5.611% | -5.991% | -5.235% | -5.382% | -5.935% | -4.563% | -4.258% | -5.949% | -6.023% | -5.637% | -6.562% | -5.329% | -4.947% | -5.694% | -4.258% | -7.536% | -5.694% | -6.316% | -6.52% | -4.258% | -4.538% | -4.958% | -5.325% | -5.554% | -5.173% | -7.428% | -16.91% | -6.767% | -7.098% | -7.428% | -6.354% | -6.932% | 1.976% | 1.725% | -0.2977% | -1.632% | -1.931% | -0.3125% | 1.039% | -0.04259% | 1.976% | -1.114% | 1.308% | 1.697% | 1.312% | 2.323% | -3.371% | 2.708% | 2.523% | -0.229% | 0.05496% | 1.224% | -0.9658% | -0.1121% | -1.243% | -1.782% | -1.337% | 1.024% | -1.012% | -1.708% | 0.3022% | 3.012% | -6.112% | -6.562% | 1.224% | -0.2791% | 0.5561% | -0.02855% | 0.3139% | 2.143% | -0.3793% | 0.7315% |  |  | 7.054% | -7.218% | -0.5113% |  | -0.6069% | -0.07829% | 1.582% | -1.152% | -1.044% | -1.466% | -0.8215% | 0.8301% | -6.602% | -0.8215% | -1.069% | 2.482% | -1.601% | 4.939% | 3.777% | 5.751% | 7.019% | 6.581% | 1.06% | 1.233% | 2.584% | 1.371% | 1.459% | 1.154% | 2.901% | 1.002% | 1.371% | 0.931% | -0.03498% | -0.4939% | -0.03498% | 0.4447% | 1.273% |  | -0.1405% | -0.08519% | -0.1769% | 0.5355% | 0.3077% |  |  | 2.203% | 1.777% | 16.11% | 1.164% | 1.377%
2025-07-12 | 1.171% | 0.8659% | 1.5% | 0.8639% | 0.6193% | 0.6095% | 0.228% | -1.934% | -2.194% | -1.095% | -0.2808% | 0.3552% | 0.8639% | 1.569% | -0.1536% | -0.05185% | 0.3297% | -0.2808% | -0.3669% | -2.316% | -1.171% | 0.228% | 0.5019% | -2.655% | -1.024% | -1.494% | -1.611% | -1.524% | 0.7367% | 0.1714% | 0.8498% | -0.2808% | -0.8151% | -0.032% | -0.6624% | -2.743% | 0.3552% | -0.02642% | 0.3552% | 1.246% | -0.1536% | -1.298% | -1.044% | 0.6095% | -1.807% | -0.6624% | -3.02% | -0.2808% | -2.194% | -1.644% | 0.3552% | -0.6624% | -0.7443% | -2.655% | -1.142% | 1.992% | 1.2% | 1.5% | -1.106% | -1.016% | 0.3552% | -2.947% | -0.6624% | -0.4961% | -0.4373% | -0.08512% | -0.3199% | 0.5959% | 3.001% | 3.484% | 2.606% | 1.309% | 1.5% | 2.886% | 2.817% | 2.489% | 2.862% | 1.792% | 0.2916% | 2.204% | -0.6624% | 0.8894% | -0.9422% | 1.398% | -0.8023% | 1.525% | -0.497% | -0.8404% | 1.792% | 1.029% | -0.1668% | 1.84% | -0.6624% | 1.945% | 0.9063% | 0.953% | 0.1008% | 0.6095% | 0.228% | 0.8639% | 0.9911% | -0.408% | 0.9911% | 0.9911% | -1.524% | -1.044% | 0.6124% | -2.8% | 0.1008% | 2.67% | -0.6722% | 2.498% | 1.121% | 0.8837% | 1.767% | 0.6731% | -2.175% | -2.881% | -2.09% | -1.298% | -2.151% | -1.977% | -2.372% | -0.6624% | -0.2808% | 0.9063% | -0.6624% | -0.02642% | -2.655% | -1.977% | -2.668% | -2.081% | -1.729% | -1.164% | 1.181% | -2.275% | -1.562% | 0.7653% | -1.461% | -0.6624% | -2.316% | -2.762% | -1.044% | -2.081% | 0.4442% | -2.081% | 0.3552% | -1.206% | 0.2671% | -0.7896% | -0.3199% | -0.2808% | -2.09% | -0.6624% | 0.6095% | 0.9021% | 0.6095% | -0.1409% | 1.47% | 0.7623% | -2.189% | 0.4665% | -0.9771% | -2.143% | -1.778% | -1.663% | 1.11% | -1.663% | -1.193% | -2.07% | -2.428% | -2.132% | -1.206% | -2.811% | 0.2578% | 0.4665% | 1.496% | 2.139% | -1.32% | 0.08054% | -0.3746% | -2.121% | -0.8628% | -1.947% | -1.562% | -1.435% | -1.576% | -0.8354% | -1.49% | -2.749% | 0.1963% | 2.139% | 1.496% | 0.8524% | 0.5951% | 2.409% | -2.132% | 1.496% |  |  | 4.971% | -0.982% | -0.4779% |  | -1.577% | 0.6095% | 0.07534% | 0.8639% | 1.373% | -0.726% | 2.009% | 2.174% | -0.7896% | 0.7367% | 1.373% | -0.1536% | -0.733% | 5.689% | 3.418% | 6.155% | 5.927% | 6.033% | -0.3237% | 1.527% | 1.591% | 0.3976% | -0.08512% | 0.455% | 1.836% | -1.494% | -1.524% | 1.121% | -2.499% | 0.4113% | -0.2559% | -1.867% | -0.01208% |  | 0.9299% | -1.466% | -0.9908% | -0.2021% | 0.8128% |  |  | 2.627% | 1.136% | 15.24% | -2.103% | -2.568%
2025-07-13 | 2.079% | 1.701% | 0.7562% | 1.166% | 1.311% | 0.7016% | 0.3466% | 0.6197% | 0.9594% | 1.615% | 0.2101% | 1.166% | 1.739% | 1.575% | -0.336% | -1.292% | -0.3497% | 0.6879% | 0.8822% | 1.122% | 0.2101% | -2.712% | -0.441% | -1.701% | -0.441% | 1.096% | 0.605% | 0.5196% | 0.3375% | 0.3739% | 1.236% | 0.1434% | -2.98% | 0.2429% | -1.565% | -1.216% | -0.1722% | -3.067% | -1.565% | -0.6091% | -1.155% | -0.336% | -1.565% | -3.067% | -0.4725% | -1.251% | -0.189% | -2.589% | -1.57% | -1.046% | -1.428% | -1.77% | -0.245% | -1.883% | -2.079% | -0.3663% | 0.7865% | 0.1418% | -0.6091% | -0.002278% | -1.223% | 0.8083% | -0.9367% | 0.1014% | 3.201% | 2.735% | 2.609% | 1.386% | 2.463% | 1.985% | 2.408% | 1.93% | 4.251% | 2.968% | 2.619% | 1.636% | 2.983% | 2.067% | 0.961% | 3.403% | 1.234% | 2.558% | -0.4725% | 2.913% | 0.8518% | 2.258% | 1.302% | 0.6606% | 2.19% | 1.193% | -1.636% | 2.256% | 3.309% | -0.1312% | 2.182% | -1.428% | -0.6091% | -1.565% | -0.8821% | -0.7456% | -1.565% | 0.07357% | -0.06296% | -1.838% | -0.1115% | -0.0493% | -1.713% | 1.162% | -0.6091% | 0.7987% | -1.008% | -0.2394% | -0.245% | -0.002278% | -1.701% | -0.008345% | -1.484% | -1.459% | 1.09% | -0.2541% | 0.2784% | -0.6091% | -0.002278% | -0.5271% | -2.698% | -0.1843% | -1.756% | -1.428% | -1.58% | -2.32% | -2.962% | 0.4411% | 1.651% | 2.022% | -0.5842% | -1.26% | -1.731% | -0.4568% | -0.5217% | 0.4831% | -0.1134% | -1.248% | 0.5514% | 0.02526% | -1.019% | 1.096% | 1.029% | -1.701% | 1.916% | -0.441% | -0.315% | -0.6091% | -1.046% | -1.292% | 0.07357% | 0.5651% | 0.1282% | 1.521% | 0.2442% | -0.5842% | -1.934% | -0.17% | -0.4615% | -1.689% | -0.1669% | -1.777% | 2.039% | -3.039% | -1.219% | -2.573% | 0.07853% | -2.215% | -2.793% | -2.042% | -1.922% | -0.4462% | -0.17% | 0.6585% | -1.689% | -0.4462% | -1.222% | -1.689% | -0.707% | -0.2794% | -1.731% | -2.916% | -2.44% | -2.705% | -1.512% | -1.094% | -1.068% | -1.496% | -0.17% | 0.1062% | -2.145% | -0.7223% | -0.5842% | -0.17% |  |  | 4.42% | -0.2273% | -0.9075% |  | -1.556% | -1.565% | 0.5514% | -1.155% | -0.4725% | -1.633% | -1.019% | -0.1995% | -1.565% | -1.838% | -0.4725% | -1.428% | -1.459% | 4.913% | 3.497% | 4.64% | 4.748% | 6.729% | 0.1171% | 0.2822% | 1.051% | -0.3663% | -1.953% | -0.7309% | 1.969% | -1.827% | 2.085% | 0.6045% | -0.7259% | -0.5316% | -0.7259% | -0.5842% | -1.762% |  | 2.042% | -1.663% | 1.378% | -1.621% | -1.434% |  |  | 2.692% | 2.987% | 16.1% | -0.7259% | 0.04776%
2025-07-14 | -1.618% | 0.6956% | 0.9776% | 0.3284% | -0.02343% | -0.2808% | 0.7179% | 1.537% | 0.3132% | 0.8597% | -0.3307% | -0.7302% | 0.8977% | -0.09467% | 1.087% | 0.7878% | -1.08% | -0.1909% | -0.6964% | 0.004222% | 1.297% | -2.887% | 0.4836% | -0.4861% | -0.3461% | 0.5389% | 0.07797% | 0.162% | -2.386% | -2.333% | -0.0866% | 0.8011% | -1.463% | -1.757% | -2.837% | -1.066% | -1.729% | -3.027% | -2.328% | -1.439% | -2.628% | -1.829% | -2.028% | -1.329% | -1.13% | -1.929% | -2.42% | -2.058% | -2.975% | -2.64% | -1.729% | -2.058% | 1.112% | -2.031% | -1.452% | -0.4861% | -0.1132% | -1.13% | -0.4861% | 0.04656% | -0.2408% | 1.388% | -1.629% | 0.4188% | 1.498% | 3.203% | 2.235% | 1.811% | 3.394% | 3.404% | 4.073% | 3.774% | 3.065% | 3.704% | 3.739% | 2.186% | 4.281% | 3.684% | 3.225% | 4.263% | 1.926% | 2.995% | 3.844% | 5.149% | 3.334% | 4.513% | 3.674% | 3.215% | 3.764% | 3.624% | 2.355% | 4.005% | 3.514% | 2.765% | 2.967% | 1.816% | 3.125% | -1.23% | -1.03% | -1.829% | -2.128% | -0.6303% | -1.729% | 2.486% | -1.356% | -1.829% | -1.445% | -1.958% | 0.2785% | 0.1797% | -1.259% | 0.7694% | 0.8633% | -0.03334% | -1.03% | 0.3484% | -2.145% | 0.4016% | -1.427% | 0.7279% | 1.327% | -2.173% | -1.187% | -2.587% | -0.89% | 0.6946% | 0.2285% | -2.688% | 0.4105% | -0.5216% | -2.236% | 0.7694% | 0.5389% | -1.838% | 1.905% | -1.022% | -2.067% | -1.078% | -0.003153% | 1.117% | 0.7417% | -0.1341% | 1.047% | 0.9169% | -1.359% | 0.3914% | -1.03% | 0.7769% | 0.4836% | 1.498% | 0.5573% | 1.966% | -1.764% | -2.028% | -1.629% | -2.028% | -1.13% | -2.128% | -1.42% | 0.1757% | -1.977% | -2.006% | -2.318% | -2.094% | 0.3395% | -1.049% | -1.39% | -2.426% | -0.9657% | -1.378% | -2.328% | -1.931% | -1.528% | 0.5805% | 0.03425% | -1.006% | -1.673% | -1.238% | -0.4326% | -0.9152% | -1.917% | -2.408% | -1.6% | 0.5805% | -2.001% | -2.013% | -1.427% | -1.194% | -1.844% | -0.146% | 0.913% | -0.5011% | -0.9152% | -1.218% | -0.4607% | -1.592% | -1.17% | -0.006149% |  |  | 6.942% | 0.1322% | -0.4052% |  | -2.207% | -1.999% | 2.106% | -1.869% | -1.789% | -2.158% | -1.24% | -2.028% | -1.579% | -2.228% | -0.07106% | -1.529% | -1.862% | 5.533% | -1.126% | 4.009% | 4.626% | 5.155% | -0.9841% | 0.3886% | 1.579% | 0.6502% | 0.4836% | 0.01344% | 1.195% | -0.3461% | -0.3085% | 1.05% | -2.104% | 0.2728% | -0.1874% | -1.221% | -0.8492% |  | 0.3807% | -1.457% | 0.823% | -1.4% | -2.725% |  |  | 1.645% | -0.6331% | 14.7% | -1.482% | -0.3931%
2025-07-15 | -0.7325% | -0.3343% | -0.08976% | -2.247% | 1.154% | 1.284% | 0.02378% | -0.2033% | 1.407% | 1.745% | -0.771% | 1.159% | 1.5% | -0.7916% | 1.046% | 2.329% | 1.511% | -1.112% | 1.908% | -0.3343% | 0.8185% | -1.1% | 0.2945% | 1.02% | -0.3343% | -0.01989% | -0.5334% | -0.08976% | -2.149% | -0.998% | 1.222% | -0.08976% | -1.778% | -2.322% | -2.917% | -1.422% | -2.497% | -2.224% | -1.509% | -2.145% | -1.373% | -1.339% | -1.906% | -2.247% | 1.943% | 2.022% | -0.3343% | -2.712% | -1.928% | -2.059% | -1.566% | -0.2033% | 1.868% | -2.835% | -2.671% | 0.6369% | -0.3925% | -2.815% | -0.08976% | 3.119% | -1.021% | 1.925% | -2.917% | 1.73% | 1.625% | 1.007% | 2.349% | -0.1352% | 1.636% | 1% | 2.283% | 1.84% | -1.702% | 1.784% | 2.928% | 1.081% | 3.049% | 2.317% | 2.079% | 2.925% | 2.987% | -1.498% | 2.885% | 4.145% | 2.692% | 3.191% | 1.772% | 1.409% | 2.306% | 1.829% | 0.437% | 2.013% | -2.247% | -1.112% | 0.7479% | -0.04434% | 1.205% | 1.829% | 1.795% | 0.898% | 2.181% | 1.284% | -1.339% | 1.239% | -2.239% | -2.474% | -0.998% | -0.8137% | -1.248% | -2.038% | -1.592% | -0.2819% | -0.07967% | -1.926% | 0.4779% | -1.373% | -2.862% | -3.016% | -0.998% | -1.974% | -0.7028% | -1.523% | -1.805% | -2.054% | -1.906% | -1.008% | 0.126% | -0.2033% | 0.4754% | -0.4228% | -2.126% | 0.8604% | 2.736% | -0.2095% | 1.328% | -0.3994% | -2.011% | 1.551% | -1.797% | 1.046% | 0.8919% | -0.7325% | 0.8185% | -0.3657% | -1.566% | 1.206% | 0.9207% | 2.255% | 0.6613% | 1.605% | 2.464% | 2.011% | -2.007% | 2.056% | 0.739% | -0.3055% | 0.7163% | 0.08054% | 0.7011% | 1.16% | 0.9639% | 0.2418% | -2.843% | 0.5965% | 1.862% | 1.446% | 0.01216% | -1.914% | 2.676% | -2.886% | 1.226% | 1.27% | -0.2813% | -2.952% | 2.995% | -1.377% | -1.056% | -0.4471% | -2.118% | -0.2175% | 1.222% | -1.506% | -2.476% | -0.6814% | -2.636% | -2.221% | -0.06408% | -0.6814% | -1.144% | -2.17% | -2.181% | -1.825% | 0.7011% | -1.481% | -0.562% | 0.127% | -0.7916% | 1.16% |  |  | 3.392% | -0.3081% | -0.1867% |  | -1.683% | -1.566% | -1.157% | -2.474% | -1.112% | -1.906% | -0.2033% | 1.046% | -0.7369% | -2.27% | -1.339% | 2.964% | -1.099% | 2.786% | 2.901% | 4.258% | 6.335% | 5.347% | -1.725% | -1.601% | 1.625% | 0.647% | 0.1688% | -2.535% | 2.072% | 0.7661% | 0.3442% | -1.482% | -2.37% | -1.349% | -0.2499% | -0.08848% | -2.617% |  | 2.19% | -1.383% | -0.1308% | -0.9957% | -2.805% |  |  | 1.489% | 1.442% | 3.79% | -1.192% | -1.468%
2025-07-16 | -0.2255% | -1.301% | -1.479% | -0.6383% | 0.9129% | 0.9337% | -0.2317% | -0.9906% | -0.9961% | 1.853% | -1.614% | 0.8253% | -1.479% | -0.8009% | -0.02847% | -0.286% | 0.4729% | -0.5299% | 0.06223% | 1.288% | -0.5163% | -1.37% | -1.176% | -1.343% | -0.5507% | -0.4757% | -1.827% | 1.777% | -2.813% | 1.199% | 1.849% | 0.7651% | -2.146% | -0.6055% | -1.75% | -1.704% | -0.2317% | 0.4187% | 0.01219% | -0.8009% | 0.9608% | -0.8009% | -1.207% | -2.779% | 2.695% | 2.777% | -1.051% | -2.4% | -1.647% | -1.777% | -2.021% | -2.644% | 1.114% | -0.8611% | -1.051% | 0.6807% | 1.416% | 2.709% | 0.5723% | 0.9096% | -0.8958% | 0.3665% | -0.3944% | -0.03284% | 2.952% | 2.577% | 2.589% | -0.2005% | 2.682% | 2.736% | 2.411% | 1.462% | -0.3944% | -2.292% | 0.223% | 2.042% | 1.428% | 0.1477% | 2.004% | 1.201% | 1.882% | 3.183% | 1.855% | 3.332% | 1.34% | 2.452% | 0.5001% | 0.2968% | 1.137% | 0.7846% | -0.3196% | 1.663% | -0.2453% | -0.4621% | 0.6446% | 1.855% | 2.262% | 0.8253% | 0.4187% | -0.8009% | -1.75% | 0.1477% | 0.9608% | 1.638% | -0.2468% | -1.207% | -2.186% | -1.643% | 0.9608% | 1.211% | -1.014% | 1.626% | 1.97% | 0.7892% | -1.262% | 1.001% | -1.461% | 0.4639% | -0.1866% | 1.367% | -1.343% | -2.668% | -0.5239% | -2.021% | -1.79% | 1.765% | -2.685% | -2.021% | -0.1143% | -2.307% | -1.939% | 0.9629% | 2.039% | -0.8009% | -0.0532% | -0.9388% | -1.242% | 1.338% | 1.346% | 0.6898% | 0.7753% | -1.264% | 1.774% | -0.8009% | -1.885% | 1.463% | 1.422% | 0.2339% | 1.701% | -0.213% | -1.301% | -0.2588% | -1.885% | 0.6898% | 0.4187% | 1.733% | 0.8253% | 0.01219% | 0.1893% | -0.6331% | -2.829% | -0.496% | -1.44% | -2.049% | 2.446% | -1.397% | 1.08% | -0.9529% | -2.25% | -1.582% | -1.239% | -1.371% | -2.415% | -1.713% | -0.429% | 1.012% | -0.2356% | 0.6005% | -0.2219% | 0.3812% | -1.951% | 0.02177% | -1.684% | 1.642% | -1.951% | -0.9529% | -2.476% | -0.871% | -1.976% | 0.9589% | 0.6005% | -0.496% | 1.286% | 0.7375% | 0.7238% | -0.9072% | -1.154% | 0.6005% |  |  | 4.381% | -0.5839% | -1.853% |  | -1.813% | -1.343% | 1.151% | -1.885% | -1.668% | -0.1233% | -1.75% | 0.2832% | -2.508% | -0.5163% | -1.194% | 0.4187% | -2.403% | 2.994% | 2.733% | 4.353% | 6.149% | 3.332% | -1.231% | 0.2056% | 0.3049% | 0.7048% | 1.025% | -1.727% | -1.647% | 1.889% | -0.8611% | -0.9816% | 0.3685% | -1.318% | 0.2279% | -0.6415% | 1.021% |  | 2.466% | -0.4361% | -1.351% | -1.318% | -1.459% |  |  | 0.799% | 0.5248% | 4.549% | -1.459% | -1.591%
2025-07-17 | -2.132% | -1.997% | -2.212% | -1.014% | -0.3022% | -0.08318% | -1.014% | -0.08318% | -2.036% | 1.144% | -1.547% | 0.582% | -2.212% | -0.2888% | -0.4823% | 0.449% | 0.2494% | 0.04986% | 0.5329% | 1.65% | -0.1231% | -0.4291% | 1.208% | -0.2103% | 0.0908% | 2.019% | -1.788% | 1.043% | -2.138% | 0.8186% | 0.2391% | 0.02621% | -2.004% | -0.7097% | -1.653% | -1.952% | -0.09649% | -0.3493% | -0.8815% | -0.4424% | 0.449% | -1.281% | -1.68% | -2.398% | 2.391% | 2.179% | -1.629% | -2.026% | -2.036% | -2.637% | -2.212% | -1.68% | -0.7661% | -2.434% | -1.629% | -0.7898% | 0.6412% | 2.977% | 0.7594% | 1.516% | -1.573% | 0.2821% | -1.014% | 0.8008% | 1.159% | 0.8277% | 1.343% | -0.9408% | 1.74% | 1.859% | 2.112% | 1.7% | 0.4756% | 1.034% | 0.7594% | 2.285% | 1.706% | 1.779% | 2.471% | 3.247% | 2.179% | 1.779% | 2.631% | 2.804% | 0.316% | 1.779% | 0.3958% | -0.01666% | 1.58% | 0.8082% | -0.9634% | 0.9136% | 1.407% | -0.5488% | -0.3404% | 0.3559% | 1.726% | 1.527% | -0.8282% | 0.2095% | 1.5% | 1.327% | 1.088% | 1.779% | -0.6361% | -1.866% | -1.866% | -2.119% | 0.5022% | 0.1208% | -0.2776% | 0.3364% | 1.351% | -0.1867% | 0.02326% | -0.06988% | -1.738% | 0.4756% | -0.8135% | -0.06988% | -2.372% | -1.878% | -1.89% | -1.879% | -2.518% | 0.4874% | -1.334% | -0.5222% | -1.216% | -2.28% | -2.181% | 0.2382% | 1.835% | -1.639% | -1.194% | -2.175% | -2.001% | -0.1381% | 1.029% | -0.05657% | 0.2505% | -1.653% | 0.6353% | -1.469% | -2.478% | 0.3364% | 1.287% | -1.16% | 0.7049% | -1.629% | -2.243% | -0.7351% | -2.516% | 0.5953% | 2.006% | 0.9014% | 0.3692% | 0.9413% | 0.5947% | -0.8719% | -2.306% | 0.514% | -1.971% | -2.246% | 2.251% | -0.2643% | 0.9042% | -1.732% | -1.814% | -2.086% | -0.4322% | 0.01992% | -1.684% | -2.215% | -0.105% | 0.514% | -0.6028% | 0.2449% | -0.3681% | 1.052% | -1.939% | 0.0625% | -1.086% | 2.397% | -1.79% | -1.564% | -2.137% | -0.6647% | -2.732% | 1.104% | 1.146% | 0.2045% | 2.102% | 1.792% | 3.488% | 0.2449% | 0.2718% | 4.833% |  |  | 4.32% | -0.1586% | -1.675% |  | -1.419% | -0.6154% | 2.498% | -1.014% | -1.414% | 0.4224% | -2.425% | 0.6752% | -1.706% | 0.449% | -1.148% | 3.323% | -2.197% | 2.226% | 3.212% | 4.358% | 4.695% | 7.972% | -0.6927% | -1.608% | 1.399% | -0.08022% | 0.2996% | -1.616% | 2.319% | 1.073% | -0.2221% | -1.984% | 1.201% | -1.479% | -0.1657% | 0.2565% | 1.761% |  | 0.1039% | 0.2341% | -0.6769% | -1.365% | -1.449% |  |  | 2.167% | 1.474% | 5.296% | -0.4831% | -0.7211%
2025-07-18 | -1.48% | 0.2842% | 0.2303% | -0.9167% | -0.304% | -1.554% | -0.6618% | 0.0391% | -0.9039% | -0.9039% | 1.313% | -1.841% | -2.51% | -0.2505% | -2.51% | -0.7574% | -2.51% | 0.8993% | -2.657% | -1.48% | -1.554% | 0.517% | -1.157% | 0.5347% | -0.5981% | -2.186% | 0.7841% | -2.694% | -0.08834% | -0.9379% | -0.1733% | 1.129% | -0.4899% | -0.9121% | -1.745% | -0.9329% | -1.968% | -0.853% | -0.2158% | -0.3114% | -1.936% | 0.4214% | -1.777% | -0.9804% | -0.853% | -2.287% | -1.304% | -1.395% | -1.821% | 0.6253% | 1.154% | -1.012% | -0.5981% | -0.08834% | -0.304% | -0.8246% | -1.533% | -1.172% | 0.08158% | 1.328% | 1.027% | -1.075% | -0.853% | -2.9% | 2.284% | 1.784% | 2.519% | 0.07831% | 1.09% | 0.9312% | 2.206% | 1.186% | 4.436% | 1.951% | 4.018% | 2.602% | 3.99% | 2.683% | 0.5489% | 3.754% | 2.046% | 3.767% | 1.855% | 2.014% | -0.3114% | 3.034% | 0.1665% | 0.4214% | 1.823% | 0.9949% | -0.04756% | 1.931% | 3.799% | 2.779% | 1.583% | -0.3432% | 1.632% | 1.568% | 2.397% | -0.1202% | 1.505% | 1.218% | 2.906% | 0.5807% | -1.278% | -0.5662% | -0.5981% | -2.64% | -0.2795% | -1.108% | -1.392% | 0.6371% | 2.007% | 0.1665% | 1.409% | -2.095% | -1.217% | -1.419% | -1.674% | -1.618% | -2.988% | -1.759% | -0.6547% | -2.414% | -0.9167% | -0.768% | -2.733% | -1.649% | -1.561% | -2.496% | 1.637% | -1.245% | 0.9312% | 1.835% | 3.417% | -1.58% | -1.997% | 2.97% | 3.103% | 1.505% | -0.8922% | -2.333% | 0.2303% | 2.137% | -0.5662% | 0.0195% | -1.076% | -0.2158% | -1.186% | 0.0195% | 1.108% | -0.2476% | -1.419% | -0.5344% | -1.076% | -2.255% | -1.554% | -0.853% | 0.2415% | -1.144% | -2.275% | 0.5637% | -1.617% | -2.762% | 0.7033% | -1.324% | -0.8863% | -2.82% | -2.465% | -2.686% | -0.08718% | 1.15% | -0.7287% | 1.459% | -2.018% | 0.2737% | 1.24% | -0.8863% | 0.5888% | -0.7574% | 0.5315% | -1.187% | -2.046% | -1.263% | -0.6582% | -0.9006% | 1.15% | -0.7058% | -1.355% | 1.483% | 1.853% | -1.627% | 1.24% | 2.916% | 0.2415% | -0.7574% | -1.788% | 3.754% |  |  | 2.871% | -1.238% | -0.726% |  | -1.533% | -1.936% | 2.174% | -2.223% | -0.5981% | 1.632% | 2.269% | 2.397% | 1.951% | 2.715% | 0.0391% | 2.365% | -1.164% | -0.4282% | 1.712% | 5.255% | 4.798% | 5.971% | 0.2451% | -0.3199% | -0.5981% | -2.127% | -1.422% | -1.48% | 1.635% | -0.03932% | -2.042% | -0.003378% | -1.319% | -1.494% | -0.5261% | 0.8815% | -0.6715% |  | -0.07921% | 0.4426% | -1.815% | -0.7097% | 1.457% |  |  | 2.647% | 0.3315% | 3.12% | -0.1956% | -0.4752%
2025-07-19 | -1.422% | 0.5476% | 0.7314% | 0.3046% | -0.1616% | -0.03685% | 0.5607% | 0.9022% | -1.577% | -0.6754% | 0.9022% | -0.2076% | -0.2076% | -0.2619% | 0.2192% | 0.7314% | 0.1339% | 1.073% | -0.3192% | 0.1536% | -0.549% | -0.06246% | 0.4688% | 0.1396% | -0.004016% | -0.5477% | -0.792% | 0.08646% | -0.4599% | -0.2171% | -1.31% | 0.1927% | -1.357% | -1.145% | -0.07099% | -1.555% | -1.403% | -0.6344% | -0.8905% | -1.317% | -1.061% | -0.7198% | -0.9929% | -0.7198% | 0.2192% | -0.2076% | -0.5398% | -1.061% | -0.6754% | -0.9212% | -0.6771% | -0.2076% | 0.2382% | -0.1108% | -0.398% | 0.07128% | 0.6176% | -1.317% | -0.2929% | 0.8908% | 0.05705% | 0.8091% | -0.6344% | 0.1256% | 1.651% | 2.36% | 2.754% | 3.235% | -0.3783% | 0.2192% | -0.2076% | 0.39% | 0.8168% | -8.061% | 0.4659% | 1.149% | 0.8453% | 1.585% | 0.8168% | 2.596% | 1.585% | 2.439% | 1.585% | 1.073% | 0.8168% | 0.04852% | -6.951% | 0.2192% | 0.9875% | 1.5% | 0.5539% | 3.542% | 0.39% | 1.329% | 1.346% | -0.2929% | -0.01978% | 0.9534% | -0.5832% | 0.0912% | 1.218% | -0.1478% | -0.4039% | 0.1766% | -1.477% | -0.4637% | -1.279% | -0.7922% | 1.73% | 0.9743% | -1.533% | 0.7288% | 0.1851% | -0.8317% | 2.575% | 1.935% | -0.7922% | -8.921% | -1.902% | 2.797% | 2.225% | -1.507% | -1.204% | -0.8905% | -0.8137% | -0.3005% | -0.3783% | -0.9759% | 0.5949% | -0.6192% | -1.21% | 1.146% | 1.651% | 2.532% | 2.806% | 0.5027% | -1.944% | 2.009% | 3.586% | 1.585% | 0.7525% | -0.792% | -0.3783% | 1.73% | -1.3% | 1.517% | -0.2076% | 1.507% | 1.288% | -0.1616% | 0.3112% | 1.585% | -1.378% | -0.2076% | 0.2705% | -0.2929% | 0.1339% | -0.2076% | 1.617% | 1.203% | 0.7326% | 1.41% | -1.999% | 0.03429% | 1.531% | 0.4533% | -1.517% | -1.616% | 0.6674% | -1.95% | 0.2047% | 1.531% | -1.616% | -1.287% | -0.1576% | 0.2098% | -2.095% | -1.232% | -2.767% | -2.095% | -2.693% | -2.92% | -2.613% | 1.208% | -1.123% | -1.999% | -0.4833% | -1.453% | 0.2793% | -1.737% | -0.1959% | 0.4257% | 0.1062% | 1.116% | 0.3307% | -0.4636% | 0.5051% | -0.8003% |  |  | 5.243% | 0.7018% | -0.9456% |  | -6.212% | -1.061% | -0.03685% | 0.39% | -0.2929% | 0.8339% | 0.2192% | -0.1222% | 0.8168% | -0.8222% | -0.02831% | 0.7485% | 0.2458% | 0.8453% | 2.072% | 4.215% | 3.603% | 3.46% | -0.2343% | -1.91% | 0.308% | 0.3141% | -0.1616% | 0.9416% | 0.06218% | -0.3192% | 0.2382% | 0.2382% | -1.976% | 0.1494% | -1.71% | 0.2944% | 0.4717% |  | 0.254% | -1.978% | -1.119% | 0.0215% | 1.407% |  |  | 1.936% | 0.2089% | 2.401% | -2.507% | -9.756%
2025-07-20 | 1.344% | 1.558% | 1.368% | 1.986% | 2.286% | 1.368% | 2.218% | 2.064% | -0.2982% | 1.541% | 1.368% | 1.6% | 2.527% | -0.7108% | -0.9496% | 0.9819% | 0.4411% | 2.064% | 2.157% | 2.129% | 0.5183% | 1.476% | -0.1532% | 2.124% | 2.985% | 2.129% | 0.2533% | 2.11% | -1.963% | 1.815% | 0.7501% | 1.245% | -1.144% | 0.7189% | -2.387% | -1.927% | 1.646% | -1.49% | -1.49% | -0.8956% | -1.722% | -0.4088% | -2.34% | -0.7179% | -1.104% | 0.5183% | -1.722% | -1.877% | -1.945% | -2.093% | -1.954% | -0.3702% | -2.203% | -1.269% | -1.508% | 1.78% | 1.416% | 0.7888% | 1.883% | 2.213% | 0.7656% | -1.375% | -1.568% | 1.572% | 2.129% | 2.707% | 2.272% | 1.394% | 0.5956% | 1.136% | 0.5183% | 1.368% | 1.214% | 2.141% | 2.028% | 1.602% | 1.094% | 2.064% | 1.909% | 2.129% | 2.373% | 2.064% | 2.604% | 0.6729% | -0.4088% | 0.2711% | 0.9819% | 1.291% | 2.604% | 1.6% | 1.475% | 1.487% | -0.3315% | 1.214% | 2.735% | 1.214% | 0.8274% | 1.368% | 0.6729% | 2.04% | 0.4411% | -0.5633% | 0.7501% | 0.132% | -2.409% | -1.8% | -1.86% | -2.618% | 0.5492% | -1.084% | -2.221% | -0.467% | -1.866% | -2.704% | 2.272% | 0.4952% | -2.687% | -2.272% | -1.516% | 1.731% | 1.955% | -1.86% | -1.173% | -2.031% | -1.645% | -2.203% | -1.8% | -1.336% | -2.134% | -1.516% | -1.508% | -0.9378% | -1.722% | -0.2051% | -0.894% | -1.096% | -0.4035% | -1.471% | -1.893% | -0.4861% | -2.507% | -2.221% | -1.027% | -1.794% | -1.336% | -2.649% | -1.8% | -1.217% | -2.008% | -1.523% | -2.364% | -1.259% | -2.272% | -1.336% | -2.109% | -2.302% | -1.027% | -1.877% | 1.661% | 1.973% | -1.342% | -1.035% | -1.508% | -2.425% | 2.506% | 0.2872% | -0.9962% | -2.134% | 0.8011% | -1.806% | 1.337% | 1.457% | -1.717% | -0.9055% | 0.8809% | -0.5273% | -0.4492% | -0.7618% | -0.7444% | -1.934% | -2.264% | -2.272% | -1.092% | 1.57% | -1.11% | -1.925% | -1.528% | 0.1447% | -1.611% | -1.976% | 0.1759% | 2.137% | -1.934% | 1.442% | 1.661% | -2.426% | -1.206% | 1.739% |  |  | 3.327% | 0.1379% | -0.4454% |  | -2.079% | 0.2093% | 0.5647% | -0.3547% | -0.432% | -0.9496% | -0.4088% | -1.259% | 0.3638% | -0.2543% | -1.591% | 0.5183% | -1.551% | 1.615% | 1.713% | 5.593% | 4.223% | 3.598% | -1.737% | 0.04832% | 1.17% | 1.547% | 0.4173% | -1.572% | 4.553% | 1.109% | 0.963% | -1.626% | -0.05248% | -1.536% | 0.5807% | -1.37% | -0.9055% |  | -0.6793% | -1.274% | 0.5795% | -1.447% | 0.5005% |  |  | 3.9% | 2.66% | 2.092% | -1.102% | -1.217%
2025-07-21 | -0.2654% | 2.443% | 1.91% | 0.9761% | 1.089% | 0.0424% | 1.91% | 2.844% | 0.7787% | 1.176% | 2.043% | -0.3578% | 1.776% | 0.4062% | 1.723% | 1.096% | -1.745% | 1.536% | 0.3749% | 1.569% | -0.3578% | 1.11% | -0.3885% | 0.07205% | 0.4734% | 0.2271% | -2.605% | 1.353% | -2.951% | 1.447% | -2.892% | -0.04652% | -1.806% | -0.6759% | -0.4378% | -0.864% | -1.171% | -2.092% | -2.625% | -0.998% | -2.492% | 0.3759% | -1.425% | 0.3359% | -0.7579% | -0.09099% | -1.743% | -2.092% | -1.782% | -1.27% | -3.026% | -2.759% | -0.2837% | -3.023% | -1.743% | 0.7597% | 0.7716% | -1.425% | -0.04652% | -0.5208% | -2.239% | 0.2084% | 0.4426% | 2.714% | 2.567% | 2.123% | 3.071% | 0.9536% | 2.07% | 1.763% | 2.163% | 1.91% | 4.044% | 2.897% | 3.25% | 1.981% | 3.285% | 2.31% | 1.483% | 0.9536% | 1.35% | -0.4912% | 2.177% | -0.5445% | 1.523% | -1.425% | 0.1891% | -0.2377% | 1.857% | 1.216% | 0.7019% | 2.16% | -2.359% | -0.7579% | 1.317% | 1.47% | 1.283% | 0.1491% | 1.95% | 0.6427% | 2.137% | 2.297% | 0.1224% | 2.017% | -1.742% | 0.3359% | -2.608% | -0.9831% | -1.998% | -2.121% | -2.753% | 0.3502% | 0.902% | 1.092% | 1.176% | 1.363% | -2.627% | -0.9951% | -0.7579% | 0.4826% | -0.838% | 2.111% | 0.9969% | -0.7579% | -1.425% | 1.021% | 0.1758% | -0.3578% | 0.1906% | -2.655% | -2.543% | 0.4364% | -0.2285% | -1.049% | -1.623% | -1.535% | 0.7434% | -1.336% | 1.035% | -0.8913% | 0.4487% | -1.472% | 1.083% | -2.974% | -2.225% | 1.077% | 0.3359% | 1.367% | 1.434% | -0.2162% | -0.3885% | 0.8427% | -2.809% | 1.243% | 1.83% | 0.1891% | 1.843% | 1.75% | -0.3452% | 0.1% | -2.196% | -3.003% | -2.508% | -2.868% | 1.209% | -1.443% | -2.733% | -2.988% | -0.2103% | -2.35% | -1.12% | -0.7958% | -2.988% | -1.961% | 0.9214% | -2.328% | -2.193% | -2.733% | -2.988% | -2.328% | -1.623% | -0.5895% | 0.8495% | 1.38% | -2.855% | -2.868% | -1.573% | -2.35% | -1.651% | 0.7434% | 0.8959% | 1.638% | -0.669% | 1.436% | 1.854% | -0.8443% | -1.508% | 0.1% |  |  | 1.348% | -1.022% | -1.552% |  | -2.503% | -1.158% | 1.163% | 1.63% | 2.443% | 0.776% | 1.897% | 3.551% | 3.23% | -0.8113% | -0.7579% | 3.23% | -0.8291% | 0.0009058% | 3.033% | 5.585% | 3.496% | 3.384% | -0.4696% | -1.605% | 0.4074% | 0.01276% | 0.9782% | -0.9796% | -1.398% | -0.2531% | 0.01276% | -2.228% | 0.1623% | -2.598% | -0.4189% | -2.335% | -0.04749% |  | 1.311% | -0.635% | 1.707% | -1.536% | 0.7296% |  |  | 2.714% | 2.017% | 1.205% | -1.899% | 1.544%
2025-07-22 | -1.525% | -1.738% | -1.954% | -1.582% | -1.22% | -1.417% | 1.558% | 1.228% | -1.393% | -2.266% | 2.798% | -0.7225% | 1.145% | 1.596% | 1.145% | 0.3848% | 0.1535% | 1.889% | 0.84% | 0.5348% | 1.31% | -1.086% | 1.526% | 1.586% | 1.221% | 2.137% | -1.624% | 1.887% | -1.72% | 0.3371% | -1.646% | -0.6913% | -1.477% | 1.035% | -1.334% | -0.8655% | 0.8972% | -0.7555% | -1.169% | -0.7555% | -0.425% | -0.3424% | -0.7555% | -0.5903% | -1.003% | 0.3187% | -0.7619% | 0.8972% | -1.076% | -1.79% | -1.64% | -0.09445% | 2.012% | -1.683% | -1.525% | -0.9998% | -0.03018% | 0.1535% | -1.499% | -0.4709% | -0.9208% | 0.02025% | -1.169% | 1.534% | 1.725% | 1.511% | 2.366% | 0.7027% | 1.971% | 1.476% | 2.385% | 1.724% | 1.971% | 2.55% | 2.541% | 1.512% | 2.254% | 2.798% | 2.55% | 1.603% | 1.145% | 1.889% | 1.062% | 2.302% | 2.632% | 1.228% | 2.046% | 2.004% | 1.724% | 2.261% | 0.1693% | 0.2526% | 0.7319% | 0.3187% | -0.9483% | -0.5076% | -0.01182% | -1.086% | -0.7555% | 0.4014% | -0.6729% | -1.169% | -0.1771% | 0.07082% | -0.1918% | -1.086% | -0.03018% | -2.157% | -0.1192% | -1.72% | -1.906% | 0.9162% | -0.7647% | -0.1771% | 1.971% | -0.6646% | -1.604% | -2.087% | -2.528% | -0.2597% | -0.5903% | -0.6839% | 0.2122% | -0.1771% | 0.5666% | 0.3444% | 0.08734% | 0.1535% | -1.646% | -1.205% | 0.306% | 0.07717% | -0.7619% | 0.514% | 0.3658% | -1.254% | -0.8685% | -1.64% | -1.235% | -0.7555% | -0.6856% | -1.525% | 0.484% | 0.9925% | -1.557% | 0.9925% | 0.2361% | 0.9648% | 1.374% | 1.069% | 1.145% | -0.8382% | 0.6309% | 1.476% | -0.3424% | -0.09445% | -0.7555% | -1.334% | -0.5471% | -1.216% | -2.163% | -1.216% | -1.569% | -2.46% | 1.106% | -0.995% | 0.7901% | -1.866% | -0.4635% | -1.533% | -1.236% | -1.155% | -0.8999% | -2.198% | 0.363% | -1.299% | -1.55% | -1.383% | -1.717% | -2.135% | -2.257% | -2.534% | -1.866% | 1.974% | -1.254% | -9.294% | -2.158% | -2.118% | -1.797% | -0.2513% | -0.4635% | 1.475% | 0.5394% | 1.542% | 2.044% | 1.041% | 2.395% | 1.542% |  |  | 1.808% | -1.013% | -0.6082% |  | -0.39% | 0.3187% | 0.484% | 0.8393% | -0.6729% | 2.302% | 0.2361% | 2.302% | 1.724% | -0.2597% | 0.7236% | 2.219% | -2.087% | 1.299% | 3.154% | 5.624% | 3.862% | 5.13% | -1.091% | -1.34% | -0.6557% | 1.101% | 0.8094% | -1.525% | 2.256% | 1.107% | 1.189% | -2.043% | -0.9114% | -1.98% | -2.026% | -1.775% | -1.993% |  | -0.0179% | -1.94% | 0.109% | 0.04104% | -2.026% |  |  | 3.655% | 2.104% | 2.097% | 0.03152% | -2.031%
2025-07-23 | -1.319% | -0.2935% | -1.319% | -1.986% | -0.1704% | 0.2365% | 0.6144% | -0.4302% | -1.853% | 0.9211% | 0.01428% | -0.208% | 1.681% | -2.047% | -0.1857% | 0.2365% | 0.9033% | -0.07462% | 1.348% | -0.06778% | 0.8144% | 1.348% | 1.266% | 0.9922% | 1.122% | 0.05532% | 0.5272% | -0.6278% | -1.023% | 1.19% | -0.2327% | 0.1625% | -1.797% | -1.378% | 0.2365% | 1.054% | 0.01428% | -0.4302% | 1.792% | 2.015% | -1.541% | 1.57% | 0.2365% | -0.8747% | -0.4302% | 0.4588% | -1.319% | -0.4302% | -1.213% | -0.1457% | 1.192% | 0.4588% | 1.229% | -0.6278% | -0.2935% | -1.201% | 1.032% | -0.208% | 0.9527% | 0.1625% | 0.2365% | -1.13% | -0.6525% | -0.5389% | 0.7323% | 2.045% | 2.599% | 0.1989% | 1.637% | 1.881% | 2.481% | 1.259% | -0.6525% | 2.57% | 1.269% | -1.813% | 1.427% | 1.526% | -0.1191% | -0.2935% | 0.5032% | 1.792% | 1.326% | 1.57% | -0.6969% | 0.2365% | -1.075% | -1.03% | 1.081% | 0.4588% | -0.7218% | 1.061% | -0.6525% | 0.9033% | 0.1625% | 0.3921% | -0.6525% | 0.2365% | -0.208% | -0.208% | 0.7255% | 1.503% | 0.2365% | 0.4366% | -1.023% | -0.208% | -1.616% | -1.329% | -1.097% | -1.023% | -2.345% | 1.389% | -2.011% | 0.1822% | 0.5477% | -1.786% | -0.1374% | 0.36% | -1.793% | -0.8747% | 0.681% | -1.023% | -0.6278% | 0.2365% | 0.681% | -1.023% | -0.4302% | 0.681% | -1.754% | -2.801% | -1.812% | -2.058% | -0.7448% | -0.05845% | -2.273% | -1.65% | -2.065% | 0.5283% | 0.4944% | -1.986% | -1.812% | 0.322% | 0.9033% | 1.573% | 1.126% | -2.345% | -1.053% | 0.4265% | 0.1989% | 0.8759% | -2.961% | -0.8747% | -1.813% | 0.681% | 0.8144% | -0.9636% | 0.9922% | 0.6233% | -0.4226% | -0.01804% | -0.6974% | 0.7013% | -1.696% | -1.297% | 0.3016% | -2.464% | -0.8722% | -2.096% | 0.02691% | 0.5574% | -2.248% | 0.1258% | 0.1018% | -0.5216% | -0.5575% | -1.322% | -0.1979% | 0.4765% | 0.5014% | -0.6474% | 0.4246% | -1.097% | -2.496% | -0.3921% | -1.235% | -2.695% | -0.5216% | -2.679% | -1.773% | -1.65% | 2.275% | 0.5214% | 0.4765% | 1.376% | 0.7013% | -0.1979% | 2.769% | 1.376% |  |  | -1.515% | -1.798% | 1.096% |  | 0.7959% | -1.319% | -0.4302% | 1.237% | 1.792% | -0.208% | 0.281% | 0.4588% | 3.459% | 1.348% | -0.208% | 2.792% | -0.6278% | 1.802% | 3.908% | 2.845% | 2.965% | 5.662% | -0.09797% | -1.707% | 0.6224% | 1.565% | 0.09635% | -1.114% | 1.454% | -0.4986% | -1.023% | -1.813% | -2.25% | -1.311% | 1.208% | -0.986% | -1.361% |  | 2.794% | -0.5803% | -1.392% | 0.346% | -0.4054% |  |  | 3.182% | 3.476% | 1.847% | -0.4054% | 1.486%
2025-07-24
2025-07-25
2025-07-26
2025-07-27
2025-07-28
2025-07-29
2025-07-30
2025-07-31
2025-08-01
2025-08-02
2025-08-03
2025-08-04
2025-08-05
2025-08-06
2025-08-07
2025-08-08
2025-08-09
2025-08-10
2025-08-11
2025-08-12
2025-08-13
2025-08-14
2025-08-15
2025-08-16
2025-08-17
2025-08-18
2025-08-19
Formulas:
Date = [Date, row above]+1